## Slide 1: ERCOT RMR Study for Luminant NSO
Jay Teixeira

## Slide 2: Luminant – Notice of Suspension of Operations
On February 5, 2009 Luminant submitted Notice of Suspension of Operations (NSO) for:
Name | MW | Bus | County | Group | Initial Need | Final Need
Tradinghouse Unit 1 | 563 | 3403 | McLennan | 1 |  | 
Morgan Creek Unit 5 | 137 | 1037 | Mitchell | 1 |  | 
Permian Basin 5 | 114 | 1007 | Ward | 1 | X | X
Sweetwater Cogen Unit 1 | 30 | 1416 | Nolan | 1 |  | 
Sweetwater CT1 | 72 | 1417 | Nolan | 1 |  | 
Sweetwater CT2 | 68 | 1418 | Nolan | 1 |  | 
Sweetwater CT3 | 61 | 1419 | Nolan | 1 |  | 
North Lake 1 | 156 | 2381 | Dallas | 1 |  | 
North Lake 2 | 181 | 2382 | Dallas | 1 |  | 
North Lake 3 | 329 | 2383 | Dallas | 1 |  | 
Permian Basin 6 | 515 | 1008 | Ward | 2 | X | X
Decordova SES Unit 1 | 779 | 1889 | Hood | 2 | X | 
Lake Creek SES Unit 1 | 75 | 3416 | McLennan | 2 |  | 
Lake Creek SES Unit 2 | 222 | 3417 | McLennan | 2 |  | 

## Slide 3: Study Methodology
The units were grouped and analyzed in two group based on the proposed suspension dates
  Group 1: May 2009
  Group 2: September 2009
Analysis was done to determine if absence of the units violated any planning criteria as outlined in the Operating Guides
  Transfer study performed using MUST
  Voltage Stability study performed using VSAT
Study results were reviewed and verified by Operations Staff

## Slide 4: Study Assumptions – Initial Determination
The following study assumptions were used:
  2009 summer peak case (SSWG DSA December 2008 Update) used for Group 1 units
    All Group 1 units turned off
    All Group 2 units were available (unless otherwise specified)
    All wind generation was turned off
  2010 summer peak case (SSWG DSB December 2008 Update) used for Group 2 units
    All Group 1 and 2 units were turned off
    All wind generation was turned off
  For each unit a second scenario was modeled where a nearby unit was modeled as unavailable; for some units a third scenario was modeled where a different nearby unit was modeled as unavailable [to meet Operating Guide 5 requirements]

## Slide 5: Study Assumptions – Final Determination
The following study assumptions were used:
  2009 summer peak case (SSWG DSA December 2008 Update) used for Group Permian 5 determination
    Permian 6 and Decordova considered available
    All wind generation was turned off
  2010 summer peak case (SSWG DSB December 2008 Update) used for Group 2 units
    Permian Basin 5 not available
    Permian 6 and Decordova not available when other was studied
    All wind generation was turned off
  For each unit a second scenario was modeled where a nearby unit was modeled as unavailable; for some units a third scenario was modeled where a different nearby unit was modeled as unavailable [to meet Operating Guide 5 requirements]

## Slide 6: Wind Level Analysis – Initial and Final Determination
No Wind Justification
  190 hours when all wind generation in ERCOT was less than 70 MW total
  92 hours when all wind generation in ERCOT was less than 30 MW total
  21 hours when all wind generation in ERCOT was less than 10 MW
  1 hour when all wind generation in ERCOT was 0 MW
  Summer of 2008 only – June to September
  Using Hourly Settlement Quality Metering Data
  Installed capacity 5906 MW

## Slide 7: Historical Wind Output 4/10/06 to 4/15/09
Normalized over three year period

## Slide 8: Summer 2008 Wind Levels Percentage
Range of wind generation in summer 2008 (MW) | Cumulative percentage of hours in summer
0 and <100 | 8.54%
101 and <200 | 15.64%
201 and <300 | 21.17%
301 and <400 | 25.41%
401 and <500 | 30.12%
501 and <600 | 34.12%
601 and <700 | 37.64%
701 and <800 | 40.30%
801 and <900 | 43.37%
901 and <1000 | 46.86%
1001 and <1100 | 49.56%
1101 and <1200 | 53.21%

## Slide 9: Additional Studies with 300 MW Wind
Assumptions for wind units with shift factor magnitude similar in magnitude to PB SES units
  Negative shift factor (unloads line) – not guaranteed to be available so assumed not available
  Positive shift factor (loads line) – subject to OOM down so assumed not available
  Remaining wind units in North and West zones scaled to 300 and 414 MW
Results mostly similar to No Wind Studies

## Slide 10: Alternatives Considered
Considered SPS or RAP actions to eliminate need for RMR
  Opening a segment of Lamesa to Ackerly 69 kV line
  Odessa to Quail Switch and Longshore 345 kV double circuit
  Series Reactors on Odessa Autos

## Slide 11: Exit Strategy based on No Wind
Permian Basin 5 and Permian Basin 6 will be needed to provide RMR services until the upgrades of the
  Odessa EHV auto-transformer (Oncor adding to TPIT)
  Ackerly Vealmoor – Ackerly 69kV line (RPG submitted) - RAP Proposed but causes another overload
After the retirement of Permian Basin 5, Permian Basin 6 will be needed to provide RMR services to resolve post-contingency overloads of the
  Big Spring SS – Big Spring West
  Olefin Switch to Rexene Nylon Tap 138 kV lines (not necessary with 300 MW wind assumption) – RAP Proposed
  The remaining Lamesa - Ackerly 69kV line segments (RPG submitted) – RAP Proposed but causes another overload

## Slide 12
Questions?