| OGRR Number | 165 | OGRR Title | Update Unit Telemetry Requirement |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Approved Request for Withdrawal |
| Date of Decision |  | May 14, 2009 |  |  |
| Operating Guide Sections Requiring Revision |  | 3.1.3.1 Operating Obligations Attachment 8A: ERCOT Data Sets |  |  |
| Proposed Effective Date |  | Upon system implementation of Protocol Revision Request (PRR) 590. |  |  |
| Revision Description |  | This Operating Guide Revision Request (OGRR) proposes to add a requirement for Qualified Scheduling Entities (QSEs) to submit Real Time Automatic Generation Control (AGC) status and ramp rate for all units in their portfolio. |  |  |
| Overall Market Benefit |  | ERCOT will have more data available to analyze whether or not QSEs are in compliance for Ancillary Services. |  |  |
| Overall Market Impact |  | Generation Resources will have to implement systems to send AGC status and ramp rate to ERCOT. |  |  |
| Consumer Impact |  | None. |  |  |
| Procedural History |  | - On 4/1/05, OGRR165 and the corresponding Impact Analysis were posted. - On 5/12/05, ERCOT comments were posted. - On 9/20/05, the Operating Guide Revisions Task Force (OGRTF) comments were posted. - On 10/18/05, a second set of OGRTF comments were posted. - On 11/16/05, the Operations Working Group (OWG) considered the OGRR165. - On 1/13/06, ROS considered the OGRR165. - On 10/29/08, OWG comments were posted. - On 11/13/08, ROS again considered OGRR165. - On 4/17/09, a Request for Withdrawal was posted. - On 4/24/09, OWG comments were posted. - On 5/14/09, ROS again considered OGRR165. |  |  |
| OWG Decision |  | On, 11/16/05, the OWG was in consensus to recommend approval of OGRR165 as revised by OWG. |  |  |
| Summary of OWG Discussion |  | On 11/16/05, the OWG was informed by the OGRTF that ERCOT has specified the ramp rate requirement as shown in the Operating Guide Attachment 8A revision shown below. |  |  |
| ROS Decision |  | On 11/16/05, the ROS unanimously voted to remand OGRR165 to OWG for clarification of the language surrounding the information that ERCOT is expecting to receive from QSEs, and the intended purpose of the information being submitted. All market segments were present for the vote. On 11/13/08, the ROS was in consensus to remand OGRR165 to the Performance, Disturbance, Compliance Working Group (PDCWG) for review. On 5/14/09, ROS unanimously voted to approve the Request for Withdrawal of OGRR165. All Market Segments were present for the vote. |  |  |
| Summary of ROS Discussion |  | On 11/16/05, the ROS discussed the feasibility of using instantaneous Resource ramp rates for compliance, operations, and analysis purposes and agreed that the intended purpose of that information was not clear. On 11/13/08, the ROS discussed the OWG comments to recommend that PDCWG review this OGRR. On 5/11/09, it was noted that this OGRR relates to obtaining unit specific ramp rate capabilities and given that we are headed into a nodal market, nodal design looks at individual units. There was also discussion regarding the related PRR and the language approved. ERCOT clarified that the language is currently boxed so not in effect. |  |  |

| Original Sponsor |  |
| --- | --- |
| Name | John Dumas |
| Company | ERCOT |
| Segment | Not applicable. |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Description |
| ERCOT 051205 | Changes Protocol language in Operating Guides to Protocol reference. |
| OGRTF 092005 | Combines Protocol reference. |
| OGRTF 101805 | Requests further specification of 'ramp rate' from ERCOT. |
| OWG 102908 | Recommends to ROS that OGRR165 be remanded to the PDCWG. |
| OWG 042409 | Endorsed the Request for Withdrawal. |

Revised Proposed Operating Guide Language

#### 3.1.3.1	Operating Obligations

Reference:  Protocols, Section 4.3.4, Operations of the Qualified Scheduling Entity

Scheduling Center Requirement.  A QSE shall maintain a 24-hour, seven-day-per-week scheduling center with qualified personnel for the purposes of communicating with ERCOT for scheduling purposes and for deploying the QSE’s Ancillary Services in Real Time.

QSE Representative.  Each QSE shall, for the duration of the Scheduling Process and settlement period for which the QSE has submitted schedules to ERCOT, designate a representative who shall be responsible for operational communications and who shall have sufficient authority to commit and bind the QSE.

A QSE shall maintain a 24-hour, seven-day-per-week scheduling center with qualified personnel for the purposes of communicating with ERCOT for scheduling purposes and for deploying the QSE’s Ancillary Services in Real Time.  Each QSE shall provide the ERCOT Control Area Authority (CAA) with its written backup control plan to continue operation in the event the QSE’s scheduling center becomes inoperable.

Each backup control plan shall be reviewed and updated annually and shall meet the following minimum requirements:

- Description of actions to be taken by QSE personnel to avoid placing a prolonged burden on ERCOT and other Market Participants.

- Description of specific functions and responsibilities to be performed to continue operations from an alternate location.

- Includes procedures and responsibilities for maintaining basic voice communications capabilities with ERCOT.

- Includes procedures for backup control function testing and the training of personnel.

As an option, the backup plan may include arrangements made with another entity to provide the minimum backup control functions in the event the QSE’s primary functions are interrupted.

Each QSE shall, for the duration of the scheduling process and settlement period for which the QSE has submitted schedules to ERCOT, designate an individual who shall be responsible for operational communications and who shall have sufficient authority to commit and bind the QSE.

Reference:  Protocols, Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision

Operating Period data will be used by ERCOT to monitor the reliability of the ERCOT System in Real Time, monitor compliance with Ancillary Service Obligations, perform historical analysis, and predict the short-term reliability of the ERCOT System using network analysis software.  Each TDSP, at its own expense, may obtain such Operating Period data from ERCOT or from QSEs.

(1)	A QSE representing a Generation Entity that has Generation Resources connected to a TDSP shall provide the following Real Time data to ERCOT for each individual generating unit at a Generation Resource plant location and ERCOT will make the data available to the Generation Resource’s host TDSP (at TDSP expense):

(a)	gross or net real power,

(b)	gross or net Reactive Power;

(c)	if gross quantities are provided, the plant auxiliary Load data will also be supplied;

(d)	status of switching devices in the plant switchyard not monitored by the TDSP affecting flows on the ERCOT System;

(e)	Frequency Bias of Portfolio Generation Resources under QSE operation;

(f)	any data mutually agreed by ERCOT and the QSE to adequately manage system reliability and monitor Ancillary Service Obligations;

(g)	generator breaker status;

(h)	High Operating Limit; and

(i)	Low Operating Limit.

[PRR590: Add items (j) and (k) upon system implementation:] (j) AGC status; and (k) ramp rate.

Refer to Attachment 8A for the generating unit ramp rate specification.

Reference:  Protocols, Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision

[PRR307: Revise Section 6.5.1.1(1) and 6.5.1.1(1) (c) & (g) as follows when system change implemented.] (1) A QSE representing a Generation Entity or a Competitive Retailer that has Resources connected to a TDSP shall provide the following Real Time data to ERCOT for each individual generating unit or LaaR capable of controllably reducing or increasing consumption under Dispatch control (similar to AGC) and that immediately respond proportionally to frequency changes (similar to generator governor action) at a Resource plant location and ERCOT will make the data available to the Resource’s host TDSP (at TDSP expense): (c) If gross quantities are provided, the plant auxiliary Load data will also be supplied as needed to determine the net output; (g) Resource breaker status;

[PRR590: Add paragraph (2) and renumber subsequent paragraphs upon system implementation:] (2) A QSE representing Uncontrollable Renewable Resources is exempt from the requirements of Section 6.5.1.1(1)(j) and (k).

(2)	Any QSE providing Responsive Reserve and/or Regulation must provide for communications equipment to receive ERCOT telemetered control deployments of service power.

(3)	Any QSE providing Regulation Service must provide appropriate Real Time feedback signals to report the control actions allocated to the QSEs Generation Resources.

(4)	Any QSE that represents a provider of Responsive Reserve, Non-Spinning Reserve, or Replacement Reserve using LaaR shall provide separate telemetry of the real power consumption of each LaaR providing the above Ancillary Services, the LaaR response to Dispatch Instructions for each LaaR, and the status of the breaker controlling that LaaR.  If LaaR is used as a Responsive Reserve Resource, the status of the high-set under frequency relay will also be telemetered.

[PRR307: Revise Section 6.5.1.1(3) and 6.5.1.1(4) as follows when system change implemented.] (3) Any QSE providing Regulation Service must provide appropriate Real Time feedback signals to report the control actions allocated to the QSEs Resources. (4) Any QSE that represents a provider of Responsive Reserve, Non-Spinning Reserve, or Replacement Reserve using interruptible Load as a Resource shall provide separate telemetry of the real power consumption of each interruptible Load providing the above Ancillary Services, the LaaR response to Dispatch Instructions for each LaaR, and the status of the breaker controlling that interruptible Load. If interruptible Load is used as a Responsive Reserve Resource, the status of the high-set under frequency relay will also be telemetered.

(5)	Any QSE that represents a qualified provider of Balancing Up Load (BUL) need not provide telemetry but rather shall provide an estimate in Real Time representing the real power interrupted in response to the deployment of Balancing Up Load.

(6)	Real Time data for reliability purposes must be accurate to within three percent (3%).  This telemetry may be provided from relaying accuracy instrumentation transformers.

[PRR590: Add paragraph (7) upon system implementation:] (7) A QSE representing a combined cycle plant may aggregate the AGC and ramp rate SCADA points for the individual units at a plant location into two distinct SCADA points (AGC and ramp rate) if the plant is configured to operate as such, i.e. gas turbine(s) and steam turbine(s) are controlled in aggregate from an AGC perspective.

Attachment 8A:	ERCOT Data Sets

| ACTION | DATA QUANTITY | PURPOSE | SUPPLIED BY | RECEIVED BY | FREQUENCY | MODE OF COMM. | FORMAT | PROTOCOLS REFERENCE / COMMENTS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Private Network Net Interchange Low Limit | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | For private networks, the low operating limit will reflect the minimum generation available at the point of interconnection to ERCOT. |
|  | Status of switching devices in the plant switchyard not monitored by the TDSP affecting flows on the ERCOT System | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Generating Unit Breaker Status | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Generating Unit High Operating Limit | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Generating Unit Low Operating Limit | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision |
| NOTE: Operating Period data from QSE units can be made available to the PGCs host TDSP on request. |  |  |  |  |  |  |  |  |

[OGRR165: Add the following two rows to the above table upon system implementation:] Generating Unit AGC Status; Real-Time Monitoring & Security Analysis; QSE; ERCOT; 10 sec; RTU/ ICCP; DNP 3.0; Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision. Generating Unit Ramp Rate; Real-Time Monitoring & Security Analysis; QSE; ERCOT; 10 sec; RTU/ ICCP; DNP 3.0; Protocols Section 6.5.1.1, Requirements for Operating Period Data for System Reliability and Ancillary Service Provision Generating Unit Ramp Rate is the current Up Ramp Rate in MW/min..