NMMS:

ERCOT Modeling Guidelines

Version 0.06

| Document Revisions |  |  |  |
| --- | --- | --- | --- |
| Date | Version | Description | Author(s) |
| 1/13/09 | 0.01 | Initial draft | Terry Nielsen |
| 1/29/09 | 0.02 | Updated rules, edited to support for draft release to NDWSG. | Terry Nielsen |
| 2/17/09 | 0.03 | Updated with section changes based upon NDSWG input and NMMS team input. Also updated to add draft completed section for switch. | Terry Nielsen, Keith Smith |
| 4/9/09 | 0.04 | Updated with sections for: SVC Substations Breakers Disconnectors Shunt Compensators Series Compensators Lines and ACLinesgements SCADA and ICCP data Transformers Modeling Objects | Terry Nielsen Including sections from ERCOT NMMS Team |
| 4/16/09 | 0.05 | Incorporate comments from internal review by MMS and EMS team. | Terry Nielsen Including updates from ERCOT NMMS Team |
| 5/6/2009 | 0.06 | Updates to loads, substations section. Incorporating comments from Market participants. | Kalidindi Raju Joel Koepke Nitika Mago Mario De La Garza Kimberly Boatright Kashia Thuerwaechter Neelima Bezwada Vamsi Madam Keith Smith Rochie Guiyab |

Table of Contents

1	OVERVIEW	15

1.1	Document Organization	15

1.1.1	Major Sections	15

1.1.2	Modeling Approach Subsection	15

1.1.3	Attribute	15

1.1.4	Linkage	15

1.1.5	Appendix A - Validation Rules for Required Fields	15

1.1.6	Appendix B - Validation Rules for Required Associations	15

1.1.7	Appendix C – Complex Validation Rules	16

1.1.8	Appendix D - Classes Not Allowed Subsection	16

1.1.9	Automatic Validation Performed by NMMS Based Upon Data Dictionary	16

1.1.10	Further Clarification on Interpreting Data Dictionary and How Data is used in NMMS IMM	16

1.1.11	Relevant reference documents:	18

2	PROJECT TRACKER AND COORDINATOR	19

2.1	PTC PROJECT	19

2.2	Network Operations model change Request	21

3	INFORMATION MODEL MANAGER	23

3.1	Create New Instance	24

3.2	Add Attributes	28

3.3	Add Links	29

3.4	Rename Instance	31

3.5	Delete Instance	32

4	IMM Tools	33

4.1	Templates	33

4.2	Auto Layout	33

5	Modeling Breakers	34

5.1	Modeling Approach	34

5.2	Attributes	34

5.3	Linkage	38

6	Modeling Disconnectors	39

6.1	Modeling Approach	39

6.2	Attributes	39

6.3	Linkage	43

7	Modeling Shunt Compensators	44

7.1	Modeling Approach	44

7.2	Attributes	44

7.3	Linkage	48

8	Modeling Series Compensators	49

8.1	Modeling Approach	49

8.2	Attributes	50

8.3	Linkage	52

9	Modeling Lines	53

9.1	Modeling Approach	53

9.2	Attributes	54

9.3	Linkage	55

10	Modeling ACLineSegment	56

10.1	Modeling Approach	56

10.2	Attributes	56

10.3	Linkage	58

11	Modeling Substation	60

11.1	Modeling Approach	60

11.2	Attributes	61

11.3	Linkage	63

12	Modeling Bay	64

12.1	Modeling Approach	64

12.2	Attributes	64

12.3	Linkage	66

13	Modeling SCADA	67

13.1	Modeling Approach for SCADA	67

13.1.1	Modeling Approach for MeasurementLocation	68

13.1.1.1	Linkage	68

13.1.2	Modeling Approach for a MeasurementGroup	69

13.1.2.1	Attributes	70

13.1.3	Modeling Approach for a Calculation	71

13.1.3.1	Attributes	71

13.1.3.2	Linkage	72

13.1.4	Modeling Approach for MeasurementArgument	72

13.1.4.1	Attributes	73

13.1.4.2	Linkage	73

13.1.5	Modeling Approach for ConstantArgument	74

13.1.5.1	Attributes	74

13.1.5.2	Linkage	75

13.1.6	Modeling Function and FunctionArguments	75

13.1.7	Modeling Approach for Analog and Discrete Measurement	76

13.1.7.1	Attributes	77

13.1.7.2	Linkage	78

13.1.8	Modeling Approach for SCADA AnalogValue and DiscreteValue	79

13.1.8.1	Attributes	79

13.1.8.2	Linkage	87

13.1.9	Modeling Approach for Auxiliary SCADA Lists	89

14	Modeling ICCP	91

14.1	Modeling Approach for ICCP	91

14.2	Modeling Approach for ICCP AnalogValue and DiscreteValue	92

14.2.1	Attributes	92

14.2.2	Linkage	92

14.3	Modeling Approach for MeasurementValueQuality	93

14.3.1	Attributes	93

14.3.2	Linkage	96

15	Modeling Ratings	98

15.1.1	Modeling Approach for Ratings	98

15.1.2	Modeling Approach for SCADA AnalogLimitSet	98

15.1.2.1	Attributes	99

15.1.2.2	Linkage	100

15.1.3	Modeling Approach for SCADA AnalogLimit	101

15.1.3.1	Attributes	101

15.1.3.2	Linkage	103

15.1.4	Modeling Approach for Ratings AnalogLimitSet	103

15.1.4.1	Attributes	104

15.1.4.2	Linkage	106

15.1.5	Modeling Approach for Ratings AnalogLimit	106

15.1.5.1	Attributes	106

15.1.5.2	Linkage	108

16	Modeling Transformers	110

16.1	Modeling Approach	110

16.2	Modeling approach for Powertransformer	110

16.2.1	Attributes	111

16.2.2	Linkage	114

16.3	Modeling approach for Transformerwinding	114

16.3.1	Attributes	115

16.3.2	Linkage	119

16.4	Modeling TapChanger	120

16.4.1	Attributes	120

16.4.2	Linkage	124

16.5	modeling approach for Transformerkluge	126

16.5.1	Attributes	126

16.5.2	Linkage	127

17	Modeling Load	128

17.1	Modeling Approach	128

17.2	Modeling Approach for CustomerLoad	128

17.2.1	Attributes	129

17.2.2	Linkage	133

17.3	Modeling Approach for StationSupply	133

17.3.1	Attributes	134

17.3.2	Linkage	138

17.4	Modeling Approach for ConformLoadGroup	138

17.4.1	Attributes	139

17.4.2	Linkage	140

17.5	Modeling Approach for ConformLoadSchedule	140

17.5.1	Attributes	140

17.5.2	Linkage	141

18	Modeling Curves	142

18.1	Modeling Approach	142

18.2	Attributes Curves	143

18.3	Linkage Curves	145

19	Modeling CurveData	146

19.1	Modeling Approach	146

19.2	Attributes	146

19.3	Linkage	147

20	Modeling RegularTimePoint	148

20.1	Modeling Approach	148

20.2	Attributes	148

20.3	Linkage	149

21	Modeling Terminal	150

21.1	Modeling Approach	150

21.2	Attributes	150

21.3	Linkage	152

22	Modeling ConnectivityNode	153

22.1	Modeling Approach	153

22.2	Attributes	153

22.3	Linkage	155

23	Modeling ElectricalBus	157

23.1	Modeling Approach	157

23.2	Attributes	158

23.3	Linkages	159

24	Modeling ConnectivityNodeGroup	161

24.1	Modeling Approach	161

24.2	Attributes	161

24.3	Linkage	163

25	Modeling Operatorship	164

25.1	Modeling Approach	164

25.2	Attributes	164

25.3	Linkage	165

26	Modeling OwnershareRating	166

26.1	Modeling Approach	166

26.2	Attributes	166

26.3	Linkage	167

Classes Only Modeled By ERCOT	168

27	Modeling BaseVoltage	169

27.1	Modeling Approach	169

27.2	Attributes	169

27.3	Linkage	170

28	Modeling Company	171

28.1	Modeling Approach	171

28.2	Attributes	171

28.3	Linkage	173

29	Modeling SubgeographicalRegion	174

29.1	Modeling Approach	174

29.2	Attributes	174

29.3	Linkage	175

30	Modeling Geographical Region	176

30.1	Modeling Approach	176

30.2	Attributes	176

30.3	Linkage	177

31	Modeling Market Objects	178

31.1	Modeling Approach for SettlementHUB	178

31.1.1	Attributes	179

31.1.2	Linkage	180

31.2	Modeling Approach for AggregateHUB	180

31.2.1	HB_HUBAVG	180

31.2.1.1	Attributes	180

31.2.1.2	Linkage	180

31.2.2	HB_BUSAVG	181

31.2.2.1	Attributes	181

31.2.2.2	Linkage	181

31.3	Modeling Approach for HUBBus	181

31.3.1.1	Attributes	182

31.3.1.2	Linkages	182

31.4	Modeling Approach for PricingVector	183

31.4.1	Attributes	184

31.4.2	Linkages	184

31.5	Modeling Approach for EPSMeter	185

31.5.1	Attributes	185

31.5.2	Linkages	185

31.6	Modeling Approach for ResourceNode	186

31.6.1	Attributes	187

31.6.2	Linkages	187

31.7	Modeling Approach for SettlementLoadZone	187

31.7.1	Attributes	188

31.7.2	Linkage	189

31.8	Modeling Approach for SettlementNOIELoadZone	189

31.8.1	Attributes	190

31.8.2	Linkages	191

32	Modeling Generation	192

32.1	Modeling Generating Unit	192

32.1.1	Modeling Approach for Resource Controller	192

32.1.1.1	Attributes	193

32.1.1.2	Linkage	194

32.1.2	Modeling Approach for Generating Unit	195

32.1.2.1	Attributes	196

32.1.2.2	Linkage	207

32.1.3	Modeling Approach for Synchronous Machine	208

32.1.3.1	Attributes	209

32.1.3.2	Linkage	214

32.2	Modeling Combined Cycle PLant	214

32.2.1	Modeling Approach for Combined Cycle Plant	215

32.2.1.1	Attributes	216

32.2.1.2	Linkage	218

32.2.2	Modeling Approach for Logical Configuration	218

32.2.2.1	Attributes	219

32.2.2.2	Linkage	220

32.2.3	Modeling Approach for Configuration	220

32.2.3.1	Attributes	221

32.2.3.2	Linkage	223

32.2.4	Modeling Approach for Trans State	223

32.2.4.1	Attributes	224

32.2.4.2	Linkage	225

32.2.5	Modeling Approach for Configuration Member	225

32.2.5.1	Attributes	226

32.2.5.2	Linkage	227

33	Modeling Controllable Load Resources and Load resources	228

33.1	Modeling Approach	228

33.2	Attributes	229

33.3	Linkage	233

34	Modeling Owner Share Limits	234

34.1.1	Modeling Approach	234

34.1.2	Attributes	234

34.1.3	Linkage	235

35	Modeling Flowgate Group	237

35.1	Modeling Approach	237

35.2	Attributes	238

35.3	Linkage	239

36	Modeling Flowgate Element	240

36.1	Modeling Approach	240

36.2	Attributes	240

36.3	Linkage	242

37	Modeling Ownership	243

37.1	Modeling Approach	243

37.2	Attributes	243

37.3	Linkage	244

38	Modeling DC Ties	245

38.1	Modeling Approach	245

38.2	Attributes	245

38.3	Linkage	246

39	Modeling Contingencies	247

39.1	Modeling Approach for contingency	247

39.1.1	Attributes	248

39.1.2	Linkage	250

39.2	Modeling Approach for Contingency Element	250

39.2.1	Attributes	251

39.2.2	Linkage	252

39.3	Modeling approach for Contingency Groups	252

39.3.1	Attributes	253

39.3.2	Linkage	254

39.4	Modeling approach for Contingency Group Members	254

39.4.1	Attributes	255

39.4.2	Linkage	256

40	Modeling Remedial Action Schemes (RAS)	257

40.1	Modeling Approach	257

40.2	Modeling Approach RAS	257

40.2.1	Attributes	259

40.2.2	Linkage	260

40.3	Modeling Approach RAS-Stage, Stage Trigger, Private Protective Actions	260

40.3.1	Attributes	260

40.3.2	Linkage for RAS-Stage	261

40.3.3	Linkage for RAS-Stage Trigger	261

40.3.4	Linkage for RAS- Private Protective Actions	262

40.4	Modeling Approach RAS-Protective Action ACLine Segment, Series   Compensator, Switch, and Transformer Winding	262

40.4.1	Attributes	262

40.4.2	Linkage	263

40.5	Modeling Approach RAS-Protective Action Analog, Energy Consumer, Station Reduction, and Synchronous Machine	263

40.5.1	Attributes	263

40.5.2	Linkage	264

40.6	Modeling Approach RAS-Protective Action and Protective Action Shared	265

40.6.1	Attributes	265

40.6.2	Linkage for RAS- Protective Action	266

40.6.3	Linkage for RAS- Protective Action Shared	266

40.7	Modeling Approach RAS- Trigger Condition	266

40.7.1	Attributes	266

40.7.2	Linkage	267

40.8	Modeling Approach RAS- Gate	267

40.8.1	Attributes	267

40.8.2	Linkage	269

40.9	Modeling Approach RAS- Gate Input Pin, Pin Branch Group, Pin Branch Group, Pin Gate, Pin Switch, Pin Trigger Condition, and Pin Voltage	269

40.9.1	Attributes	269

40.9.2	Linkage for RAS- Gate Input Pin	270

40.9.3	Links for RAS- Pin Branch Group	270

40.9.4	Links for RAS- Pin Gate	271

40.9.5	Linkage for RAS- Pin Switch	271

40.9.6	Linkage for RAS- Pin Trigger Condition	271

40.9.7	Linkage for RAS- Pin Voltage	271

40.10	Modeling Approach for RAS-Pin Flow	272

40.10.1	Attributes	272

40.10.2	Linkage	273

41	Modeling PrivateAreaNetworks	274

41.1	Modeling Approach	274

41.2	Attributes	274

41.3	Linkage	275

42	Modeling Branch Group	276

42.1	Modeling Approach	276

42.2	Attributes	276

42.3	Linkage	278

43	Modeling Branch Group Terminal	279

43.1	Modeling Approach	279

43.2	Attributes	279

43.3	Linkage	280

44	Modeling Endcap	281

44.1	Modeling Approach	281

44.2	Attributes	281

44.3	Linkage	283

45	Modeling Tiecorridor	284

45.1	Modeling Approach	284

45.2	Attributes	284

45.3	Linkage	285

46	Modeling PermissionArea	287

46.1	Modeling Approach	287

46.2	Attributes	287

46.3	Linkage	288

47	Modeling Approach for DayType	289

47.1	Modeling Approach	289

47.2	Attributes	289

47.3	Linkage	290

48	Modeling Approach for LoadType	291

48.1	Modeling Approach	291

48.2	Attributes	291

48.3	Linkage	292

49	Modeling Approach for SubLoadArea	293

49.1	Attributes	293

49.2	Linkage	294

50	Modeling Approach for Season	295

50.1	Modeling Approach	295

50.2	Attributes	295

50.3	Linkage	296

51	Modeling PseudoTerminal	297

51.1	Modeling Approach	297

51.2	Attributes	297

51.3	Linkage	299

52	Modeling Planning Objects	300

52.1	Modeling Approach for Planning Area	300

52.1.1	Attributes	300

52.1.2	Linkage	301

52.2	Modeling Approach for Planning Zones	301

52.2.1	Attributes	302

52.2.2	Linkage	303

52.3	Modeling Approach for SubcontrolArea	303

52.3.1	Attributes	304

52.3.2	Linkage	305

Appendix A - Validation Rules – Required Fields	307

Appendix B - Validation Rules – Required associations	330

Appendix C - Validation Rules – COMPLEX rules	333

Appendix D – Classes Not Allowed	343

FIGURES

Figure 1 - Project Summary Display	19

Figure 2 - Create New Project Display	20

Figure 3 - Edit Project Display	21

Figure 4 - Edit NOMCR Display	22

Figure 5 - IMM Main Screen	23

Figure 6 - ERCOT Texas Network	24

Figure 7 - Create New Instance	25

Figure 8 - Create New Substation	26

Figure 9 - General Edit Instance Screen	27

Figure 10 -  __SUB1 in Model Hierarchy	28

Figure 11 - Substation Attributes	29

Figure 12 - Substation Links	30

Figure 13 -  __SUB1 Links Populated	31

Figure 14 - Rename Substation	31

Figure 15 - Delete Substation	32

Figure 16 - Breaker	34

Figure 17 - Disconnector	39

Figure 18 - Shunt Compensator	44

Figure 19 - Series Compensator	49

Figure 20 - Location of Lines containing ACLineSegments	53

Figure 21 - Location of Lines containing SeriesCompensators	54

Figure 22 - ACLineSegment	56

Figure 23 - Substation	60

Figure 24 - Bay	64

Figure 25 - IMM hierarchical view for SCADA measurement.	68

Figure 26 - IMM hierarchical view of a load with multiple SCADA measurements.	69

Figure 27 - IMM hierarchical view of a calculation definition.	71

Figure 28 - IMM hierarchical view of a Function definition in the ERCOT model.	76

Figure 29 - IMM hierarchical view of ICCP-sourced measurements in the ERCOT model.	91

Figure 30 - IMM hierarchical view of SCADA limits in the ERCOT model.	99

Figure 31 - IMM hierarchical view of static ratings of a device in the ERCOT model.	104

Figure 32 - Hierarchy for PowerTransformer	111

Figure 33 - Hierarchy for TransformerWinding	115

Figure 34 - Hierarchy for TapChanger	120

Figure 35 - Hierarchy for TransformerKluge	126

Figure 36 - Modeled RampRateCurves with parent/child associations labeled.	143

Figure 37 - CurveData	146

Figure 38 - RegularTimePoint	148

Figure 40 - Terminal	150

Figure 41 - ConnectivityNode	153

Figure 42 - ElectricalBus	158

Figure 65 - Operatorship	164

Figure 78 - Hierarchy for OwnerShareRating	166

Figure 39 - BaseVoltage	169

Figure 43 - Company	171

Figure 44 - SubGeographicalRegion	174

Figure 45 - GeographicalRegion	176

Figure 46 - SettlementHub	179

Figure 47 - HubBus	182

Figure 48 - PricingVector	184

Figure 49 - ResourceNode	186

Figure 50 – Modeled Generating Unit with parent/child associations labeled.	192

Figure 51 – Modeled Resource Controller with parent/child association.	193

Figure 52 – Modeled Generating Unit with parent/child association.	195

Figure 53 – Modeled Synchronous Machine with parent/child association.	209

Figure 54 –Combined Cycle with parent/child associations labeled.	215

Figure 55 – Modeled Combined Cycle Plant with parent/child association labeled.	216

Figure 56 – Modeled Logical Configuration with parent/child association.	219

Figure 57 -- Modeled Configuration with parent/child associations labeled.	221

Figure 58 -- Modeled Trans State with parent/child associations labeled.	224

Figure 59 -- Modeled Configuration Member with parent/child associations labeled.	226

Figure 60 – Modeled Controllable Load Resource with parent/child associations labeled.	228

Figure 61 – Modeled Load Resource with parent/child associations labeled.	229

Figure 62 - FlowgateGroup	237

Figure 63 - FlowgateElement	240

Figure 64 - Ownership	243

Figure 66 - DcTie	245

Figure 67 - Hierarchy of Contingencies	248

Figure 68 - Hierarchy for Contingency Elements	251

Figure 69 - Hierarchy for Contingency Groups	253

Figure 70 - Hierarchy for Contingency Group Member	255

Figure 71 - RAS	258

Figure 72 - IMM hierarchical view of a PrivateAreaNetwork as modeled in the ERCOT model.	274

Figure 73 - BranchGroup	276

Figure 74 - BranchGroupTerminal	279

Figure 75 - EndCap	281

Figure 76 - TieCorridor	284

Figure 77 - Hierarchy for PermissionArea	287

Figure 79 - DayType	289

Figure 80 - LoadType	291

Figure 81 - SubLoadArea	293

Figure 82 - Season	295

Figure 83 - PseudoTerminal	297

Figure 84 - PlanningArea	300

Figure 85 - PlanningZone	302

Figure 86 - SubcontrolArea	304

# OVERVIEW

This document provides guidelines for the creation of Network Model changes that are to be submitted to ERCOT. The Network Model changes may be either created using the Information Model Management (IMM) editor component of the Network Model Management System (NMMS) or by submitting a file that is in Common Information Model (CIM) XML format.

## Document Organization

The document explains how to use the attributes, associations and classes defined in the ERCOT data dictionary. The classes are organized into two sections. Classes that can be modified by TDSP’s and classes that can be modeled by ERCOT only. Also there are appendices showing the validation rules and the list of classes that are not allowed.

### Major Sections

The document is broken down into major sections that map to a single CIM package or a subsection of a package. This breaks down the document into logical subsections that cover areas such as generation, loads, etc.

The major sections are divided into two groups, those that are anticipated to be submitted by TSPs and those that are maintained by ERCOT, but would appear in any ERCOT model files.

Introductory sections describing how to perform general modeling tasks are covered first before the detailed modeling approach subsections.

### Modeling Approach Subsection

These are documented, either class by class or as logical group in subsections titled “Modeling approach for <X>”. The modeling approach section will describe the approach a user should take for modeling this object type. It covers what associations and attributes are needed and how they should be defined. For more complex modeling concepts, it may include flowcharts or other diagrams necessary to explain the modeling approach.

### Attribute

All the attributes for each of the classes are listed in the Attributes subsection with the required attributes in Bold.

### Linkage

Linkage subsection lists all the required associations or links from the class that is being described, to other classes.

### Appendix A - Validation Rules for Required Fields

Appendix A lists all of the validation rules for attributes that must be defined for a specific class. It also lists any validation for attributes that must be within a specific value range.

### Appendix B - Validation Rules for Required Associations

Appendix B lists all of the validation rules for associations (links) that must be defined for a specific class.

### Appendix C – Complex Validation Rules

Appendix C lists all the validation rules that beyond the required attributes and links and could apply to more than one class at a time.  It also list all the validation rules that are more complex than required fields and range checks. These include validation rules that are conditional based upon certain conditions, involve associations with other attributes, and those that describe specific data relationships. The validation rule is explained descriptively and not in a formal language.

### Appendix D - Classes Not Allowed Subsection

If a particular CIM class is not used in the ERCOT systems and would potentially break the ERCOT model, the class will be listed in the subsection titled “Classes Not Allowed”. The complete lists of classes that are not used are listed in Appendix D.

The appendix of this document contains the complete listing of validation rules that run against each NMMS NOMCR submission. If any of these rules do not pass, the NOMCR will not be allowed to be submitted and the user must make the necessary corrections. These rules document any minimally required attributes, valid data ranges. The validation also ensures that the submission meets the cardinality defined in the latest ERCOT data dictionary.

### Automatic Validation Performed by NMMS Based Upon Data Dictionary

The list of validation rules does not include the validation that is automatically performed by NMMS for links between objects. These links are validated based upon the data dictionary definition of the cardinality between the associated objects. There are two cardinality definitions that are validated, the first is the CardinalityRoleA and the second CardinalityRoleB. CardinalityRoleA defines the number of objects of the first Class that may exist related to the second Class.

For instance, in the data dictionary, the link between ThermalGeneratingUnit to CombinedCyclePlant CardinalityRoleA has a value of “0..n”. This means that there may be anything between 0 and n ThermalGeneratingUnits associated with a CombinedCyclePlant. The same association has a CardinalityRoleB of “0..1” which means that there may be between 0 and 1 CombinedCyclePlants associated with a ThermalGeneratingUnit.

This validation performed by NMMS follows the inheritance tree and the same validation is done for all objects that inherit from the object which has the cardinality definition.

For instance, in the data dictionary, a GeneratingUnit has a link to a ResourceNode that has a CardinalityRoleA defined as 1..n. This means that validation would be performed checking that there are one or more GeneratingUnits associated with a ResourceNode. It also means that validation would be performed for HydroGeneratingUnit, ThermalGeneratingUnit, WindGeneratingUnit and NuclearGeneratingUnit because these classes inherit from GeneratingUnit. Note: that the cardinality is not defined explicitly for each inherited class.

### Further Clarification on Interpreting Data Dictionary and How Data is used in NMMS IMM

The rules used when dealing with associations/links may help with understanding these relationships. In general, the direction is defined in the data dictionary by the A and B (e.g. Class A and Class B, A --> B). The key, however, is that while the IMM UI uses the direction of the link to determine which side to display the links, the CIM/RDF export standard uses the cardinality to determine which side to export links.

Sample association definition:

| Class A | Cardinality A | Class B | Cardinality B | NMMS Label |
| --- | --- | --- | --- | --- |
| GeneratingUnit | 0..1 | DCTie | 1..1 | PartOfDCTie |

The NMMS IMM UI displays links in the direction A --> B.

By default the IMM UI instance editor will show links to instances of Class B on the Class A side. This means you will see links in the direction of A --> B. In the definition above, the IMM UI will show the link to DCTie on the "link tab" of the GeneratingUnit. If the user wishes to see the links in the opposite direction, they can do so by pressing the [Options] button and choosing the appropriate setting.

The NMMS RDF Export lists the links to the Class having lower cardinality under the Class having higher cardinality.

The CIM/RDF standard recommends that the side with the lower cardinality be exported under the side having higher cardinality. In case the cardinalities are equal, NMMS is implemented so that it export the links to Class B under the Class A instance.

This explains why the user sees an inconsistency between IMM UI and RDF export with the GeneratingUnit to DCTie relationship. IMM UI shows the links to DCTie (Class B) under the GeneratingUnit (Class A). However, RDF Export lists the links pointing to GeneratingUnit (cardinality 0-1) under the DCTie (cardinality 1-1).

The cardinality order is shown in the following table:

Cardinality Order (Least to Greatest)

0..1

1..1

0..n

1..n

Below is another example:

| Class A | Cardinality A | Class B | Cardinality B | NMMS Label |
| --- | --- | --- | --- | --- |
| ConductingEquipment | 0..n | BaseVoltage | 0..1 | BaseVoltage |
| SynchronousMachine | 0..1 | GeneratingUnit | 0..1 | GeneratingUnit |
| Reservoir | 0..1 | HydroPowerPlant | 0..n | Provides Water To(HydroPowerPlants) |

The links to BaseVoltage (lower cardinality) will be exported under ConductingEquipment (higher cardinality). Likewise, IMM UI will list the links to BaseVoltage (Class B) under the ConductingEquipment (Class A).

The links to GeneratingUnit (cardinality 0..1) will be exported under the SynchronousMachine (cardinality 0..1). Likewise, IMM UI will list the links to GeneratingUnit (Class B) under the SynchronousMachine (Class A). The links to Reservoir (lower cardinality) will be exported under HydroPowerPlant (higher cardinality). However, IMM UI will list the links to HydroPowerPlant (Class B) under the Reservoir (Class A).

### Relevant reference documents:

- ERCOT Data Dictionary.

- ERCOT Processes and Procedures.

- ERCOT Training documents.

# PROJECT TRACKER AND COORDINATOR

The Project Tracker and Coordinator (PTC) is the single entry point for Operations Model changes.  Modeling data and change requests are initially received in the PTC, where each submission is tracked through any corrections, resubmission, validation, testing and review.

Upon login to the PTC, the user will see that Project Summary screen shown below in Figure 1.  The Project Summary screen is the base display for the PTC and provides the user the ability to view, edit, and create both change requests and projects.

Figure 1 - Project Summary Display

## PTC PROJECT

A PTC project is a container that is used to group similar change requests.  It is a requirement that every change request belong to a project, even if it is the only change request in the project.  To create a new project the user will click the New Project button on the Project Summary Display screen.  The Create New Project screen shown below in Figure 2 will appear. The user must designate the project as a NOMCR (Network Operations Model Change Request) project or a SAMR (Special Action Model Request) project.  Required fields are marked with an asterisk.   For modeling purposes, we will only cover a NOMCR project.   After the required fields are populated, the project can be saved.

Figure 2 - Create New Project Display

Once a project is created, the Edit Project screen can be opened by clicking on the Project ID on the Project Summary Screen.  The Edit Project screen is shown below in Figure 3.  Here the user can make changes to the project, create a new change request, or edit an existing change request.

Figure 3 - Edit Project Display

## Network Operations model change Request

Transmission Service Providers (TSPs) will submit all types of modeling changes using a Network Operations Model Change Request (NOMCR).  These changes include topological changes, limit/rating changes, telemetry mapping, and telemetry definitions.  The NOMCR process is defined in the Nodal Protocols and outlines submission deadlines, formats, and procedures.

A new NOMCR can be created from the Project Summary Screen, the Create New Project Screen, or the Edit Project Screen.  Once a NOMCR is created, the Edit NOMCR screen shown in Figure 4 will appear.  All NOMCR information can be added/edited from this screen.

Figure 4 - Edit NOMCR Display

Once data is entered into the required fields in the Edit NOMCR screen, the user can make changes to the model.  The most common method for making changes to the model is by clicking the Launch Model Editor button on the Edit NOMCR screen, which will open the Information Model Manager (IMM).  Once model changes have been made in the IMM, the NOMCR must be validated and submitted for the model changes to be applied to the Network Operations Model.  Validation is performed by clicking the Validate IMM Data button.  If the model changes pass validation, the NOMCR can be submitted by clicking the Submit NOMCR.  If the model changes fail validation, an error message will appear in the bottom left corner of the screen on the status bar.  The validation errors can be viewed by clicking on the Validation Log button.  These errors must be corrected before the NOMCR can be submitted.

Another option for making changes to the model is importing a CIM XML file.   This can be done by clicking the Browse button next to the CIM XML data field in the Upload section of the Edit NOMCR screen.  Once a CIM XML file is selected, the file is imported by clicking the Import button next to the Browse button.  After the file is imported successfully, the NOMCR can be validated and submitted.

# INFORMATION MODEL MANAGER

The Information Model Manager (IMM) is the user interface used to add and modify data in the Network Operations Model database.  The IMM can be accessed by clicking the “Launch Model Editor” button on the Edit NOMCR screen seen in Figure 4.   The IMM, as shown below in Figure 5 will appear.

Figure 5 - IMM Main Screen

Market Participants will be responsible for maintaining only a small number of the instances that are seen in the IMM.  A majority of these instances will be in the IMM under the path Network/Ercot Texas Network.  Figure 6 shows the IMM model expanded to show the full ERCOT Texas Network.  The ERCOT Texas Network includes substations, AC lines, and series compensators, all of which will be modeled by the Market Participants.

Figure 6 - ERCOT Texas Network

This section will cover the process of making model changes in the IMM by creating and editing a generic device.  For simplicity purposes we will use a substation as an example at this time.  The modeling of more complex scenarios and devices will be covered later in the document.

## Create New Instance

In order to find where in the model hierarchy a device is modeled it is best to look at the section on Substations.  Here we see that a Substation is modeled under a WeatherZone.  To create a new substation right-click on weather zone and select New, as seen below in Figure 7.

Figure 7 - Create New Instance

The screen seen in Figure 8 will appear in the IMM prompting the user to select an instance type.  Select substation and click the Create Instance button.

Figure 8 - Create New Substation

Once the substation is created the General Edit Instance screen shown below in Figure 9 will appear.  A name must be entered for the instance before the instance can be saved in the model.  Upon saving the new instance, the substation will appear in the model hierarchy.

Figure 9 - General Edit Instance Screen

The updated model hierarchy with new substation __SUB1 is shown below in Figure 10.

Figure 10 -  __SUB1 in Model Hierarchy

## Add Attributes

Once the substation has been created and saved, attributes for the substation must be entered into the required attribute fields.  Required attributes for each device can be found in a table in the device section.  Looking at the section on Substations, it is found that the required attributes for a substation are forNetwork and forScada.  These fields must be populated for the model changes to pass IMM validation.

Many of the attribute fields are auto-populated by the IMM.  Figure 11 shows the attributes screen for a newly created substation.  The auto-populated fields are populated in this figure. The IMM will prevent data that is not of the correct data type or size from being saved in the model.

Figure 11 - Substation Attributes

## Add Links

As with attributes, for every device there are required link fields that must be populated for the model changes to pass the IMM validation.  The required links for a substation can be found in the table named required links in the substation section of this document.  Looking at this table, it is found that the required links for a substation are Ownership, Operatorship, and PermissionArea.  Figure 12 shows the links screen for a newly created Substation.

Figure 12 - Substation Links

Links cannot be manually entered into the value column.  All of the links must be added using the drag and drop method or the copy/paste method.  The path for all of the required links can be found in the Required Links table.  With the links screen shown in Figure 12 up in the IMM, navigate to the desired link in the IMM and left-click on the link holding down the mouse button.  Drag the selected link into the desired field and release the mouse button.  The value field will be populated with the link.  Save the change and move forward populating all of the required links in a similar manner.  The screen shot in Figure 13 shows the ERCOT_Operator and ERCOT_Owner links in the __SUB1 Operatorship and Ownership fields.

Figure 13 -  __SUB1 Links Populated

## Rename Instance

To rename an instance right-click on the instance and selecting Rename.  A popup screen will appear prompting the user to enter a new instance name.  This popup screen is shown in Figure 14.  After the name is entered and the user selects the OK button, the instance name will be updated in the model hierarchy.

Figure 14 - Rename Substation

## Delete Instance

To delete an instance right-click on the instance and select Delete.  The warning message shown in Figure 15 will appear.  If the instance or children of the instance are modified in a later job, the user will not be able to delete the instance.

Figure 15 - Delete Substation

# IMM Tools

## Templates

## Auto Layout

# Modeling Breakers

## Modeling Approach

The ERCOT CIM model defines a Breaker as a mechanical switching device capable of making, carrying, and breaking currents under normal circuit conditions and also making, carrying for a specified time, and breaking currents under specified abnormal circuit conditions e.g. those of short circuit.

A Breaker is modeled under a VoltageLevel in a Substation.  Two Terminals are modeled under the Breaker as connection points to the circuit.  SCADA values modeled under the Terminals provide the Open/Close status of the Breakers to the model.  Figure below shows a Breaker modeled in the IMM model hierarchy with parent/child associations labeled.    For more information on modeling SCADA values, refer to the section on ‘Modeling SCADA’.

Figure 16 - Breaker

## Attributes

The attributes for a Breaker are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| TEID | Transmission Element ID | Integer | Auto-populated |  |
| normalOpen | The attribute is used in cases when no Measurement for the status value is present. | Boolean | False |  |
| initiallyOpen | T = The initial breaker state for the online switching device model is open. | Boolean | False |  |
| inTransitTime | The transition time from open to close, in seconds. | Float | 0 |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Current Flow | Fault interrupting rating in amperes. | Float | None |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Enable Manual Switching | T = Enables manual switching capability for the device. | Boolean | True |  |
| Latitude | Latiitude coordinates. | Float | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Normal Open | The attribute is used in cases when no Measurement for the status value is present. If the Switch has a status measurment the Measurement.normalValue is expected to match with the Switch.normalOpen. | Boolean | False |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode | None |  |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| Remove | The equipment is removed from the network. | Boolean | False |  |
| Remove Enable | The equipment can be removed from the network. | Boolean | False |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Switch On Count | The switch on count since the switch was last reset or initialized. | Integer | None |  |
| Switch On Date | The date and time when the switch was last switched on. | Date/Time | None |  |
| Switch Operation Over | Over Limit Violation Switch Operation (Open/Close). | Boolean | None |  |
| Switch Operation Under | Under Limit Violation Switch Operation (Open/Close). | Boolean | None |  |
| Switched By Schedule | T = The switch will follow a switching schedule to change state in the network applications. | Boolean | False |  |
| Trigger Network Sequence | T = The switch will trigger the real?time network application sequence when the switch changes state in SCADA. | Boolean | False |  |
| Trip Lockout | Lockout after trip. | Boolean | None |  |
| Zero Impedance Branch? | Mark Switching devices that should be converted to Zero Impedance Branches in Connectivity Node to Bus Processing Option 1. | Boolean | False |  |

## Linkage

The required links for a Breaker are defined below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Disconnectors

## Modeling Approach

The ERCOT CIM model defines a Disconnector as manually operated or motor operated mechanical switching device used for changing the connections in a circuit, or for isolating a circuit or equipment from a source of power. It is required to open or close circuits when negligible current is broken or made.

A Disconnector is modeled under a VoltageLevel in a Substation.  Two Terminals are modeled under the Disconnector as connection points to the circuit.  SCADA values modeled under the Terminals provide the Open/Close status of the Breakers to the model.  Figure below shows a Disconnector modeled in the IMM model hierarchy with parent/child associations labeled.    For more information on modeling SCADA values, refer to the section on SCADA.

Figure 17 - Disconnector

## Attributes

The attributes for a Disconnector are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| normalOpen | The attribute is used in cases when no Measurement for the status value is present. | Boolean | False |  |
| initiallyOpen | T = The initial breaker state for the online switching device model is open. | Boolean | False |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Enable Manual Switching | T = Enables manual switching capability for the device. | Boolean | True |  |
| Latitude | Latiitude coordinates. | Float | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| Normal Open | The attribute is used in cases when no Measurement for the status value is present. If the Switch has a status measurment the Measurement.normalValue is expected to match with the Switch.normalOpen. | Boolean | False |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode | None |  |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| Remove | The equipment is removed from the network. | Boolean | False |  |
| Remove Enable | The equipment can be removed from the network. | Boolean | False |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Switch On Count | The switch on count since the switch was last reset or initialized. | Integer | None |  |
| Switch On Date | The date and time when the switch was last switched on. | Date/Time | None |  |
| Switched By Schedule | T = The switch will follow a switching schedule to change state in the network applications. | Boolean | False |  |
| Trigger Network Sequence | T = The switch will trigger the real?time network application sequence when the switch changes state in SCADA. | Boolean | False |  |
| Zero Impedance Branch? | Mark Switching devices that should be converted to Zero Impedance Branches in Connectivity Node to Bus Processing Option 1. | Boolean | False |  |

## Linkage

The required links for a Disconnector are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Shunt Compensators

## Modeling Approach

In the ERCOT CIM model, a ShuntCompensator is defined as a shunt capacitor or reactor or switchable bank of shunt capacitors or reactors. A section of a Shunt Compensator is an individual capacitor or reactor. Negative values for mVArPerSection and nominalMVAr indicate that the compensator is a reactor.

A Shunt Compensator is modeled under a VoltageLevel in a Substation.  One Terminal is modeled under the Shunt Compensator as a connection point to the circuit.  Figure below shows a Shunt Compensator modeled in the IMM model hierarchy with parent/child associations labeled.    For more information on modeling SCADA values, refer to the SCADA section of this document.

Figure 18 - Shunt Compensator

## Attributes

The attributes for a Shunt Compensator are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Switching Priority | Switching priority number. | Integer |  | 12345 |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Automatic Voltage Regulation Delay | Time delay in seconds required for the device to be connected or disconnected by automatic voltage regulation (AVR). | Seconds | None |  |
| Automatic Voltage Regulation Enabled | T = Automatic voltage regulation enabled. | Boolean |  |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Impedance | The positive sequence impedance of the capacitor. | Impeadance | None |  |
| Latitude | Latiitude coordinates. | Float | None |  |
| Load Based Regulation Enabled | T = Load based voltage regulation enabled. | Boolean |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Maximum Sections | For a capacitor bank, the maximum number of sections that may be switched in. | Counter | None |  |
| Maximum kV | The maximum voltage at which the capacitor bank should operate. | Voltage | None |  |
| Minimum kV | The minimum voltage at which the capacitor bank should operate. | Voltage | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| Nominal MVAr | Nominal MVAr output of the capacitor bank at the nominal kV. This number should be positive. | Reactive Power | None |  |
| Nominal kV | The nominal voltage at which the nominal MVAr was measured. This should normally be within 10% of the voltage at which the capacitor is connected to the network. | Voltage | None |  |
| Normal Sections | For a capacitor bank, the normal number of sections switched in. This number should correspond to the Nominal MVAr. | Counter | None |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode | None |  |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| Remove | The equipment is removed from the network. | Boolean | False |  |
| Remove Enable | The equipment can be removed from the network. | Boolean | False |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Switch On Count | The switch on count since the capacitor count was last reset or initialized. | Counter | None |  |
| Switch On Date | The date and time when the capacitor bank was last switched on. | Absolute Date/Time | None |  |
| Voltage Sensitivity | Voltage sensitivity required for the device to regulate the bus voltage, in per unit voltage/MVAr. | PU kV per MVAr | None |  |
| Y Per Section | For a capacitor bank, the admittance of each switchable section. Calculated using the MVAr per section and corrected for network voltage. | Admittance | None |  |
| mVAr Per Section | For a capacitor bank, the size in MVAr of each switchable section at the Nominal kV. | Reactive Power | None |  |

## Linkage

The required links for a Shunt Compensator are defined in Table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operated By (Operatorship) | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Owned By (Ownership) | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Series Compensators

## Modeling Approach

In the ERCOT CIM model a SeriesCompensator is defined as a series capacitor, reactor, or AC transmission line without charging susceptance.

Although Series Compensators are contained within a Substation in the ERCOT model, they are not modeled under a Substation in the ERCOT model.  Series compensators are modeled in the container named ERCOT-Series Compensator under ERCOT Texas Network, where they are grouped by voltage level.

Figure below shows a Series Compensator in the IMM model hierarchy.  Series Compensators must be modeled under a line and have two Terminals that serve as connection points to the circuit.  Analog SCADA values that provide limits and ratings for the Series Compensator are modeled under the Terminals.  These SCADA values can be modeled using multiple configurations.  More information on modeling SCADA values can be found in the SCADA section of this document.

Seriescompensator cannot go between different voltage levels and should be contained within one substation.

Figure 19 - Series Compensator

## Attributes

The attributes for a Series Compensator are shown in the table below

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Emergency Max Shadow Price | States the Emergency Max Shadow price for a SeriesCompensator. | DoubleFloat | 99999 |  |
| Latitude | Latiitude coordinates. | Float | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Max Shadow Price | States the Max Shadow price | DoubleFloat | 99999 |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode | None |  |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| Reactance | Positive sequence reactance | Float | None |  |
| Remove | The equipment is removed from the network. | Boolean | False |  |
| Remove Enable | The equipment can be removed from the network. | Boolean | False |  |
| Resistance | Positive sequence resistance | Float | None |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |

## Linkage

The required links for a Series Compensator are defined in Table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Lines

## Modeling Approach

This section describes the modeling of the Line container class as well as the ACLineSegment (transmission lines that connect two Substations) and SeriesCompensators (transmission lines that are fully contained within a substation) classes.

The Line class is modeled underneath a Geographical and Sub Geographical Region.  The Geographical Region in which the line will be created differs depending on what type of sub-classes the line will contain.  If the line is to contain an ACLineSegment, then the line must be in a Sub Geographical Region (named after the base voltage of the line) which is underneath the “ERCOT – AC Lines”.  Likewise, if the line will contain a SeriesCompensator, it must be created underneath both the “ERCOT – Series Compensators” geographical region and the sub geographical region corresponding to the line’s base voltage.

Figure 20 - Location of Lines containing ACLineSegments

Figure 21 - Location of Lines containing SeriesCompensators

## Attributes

The attributes for a Line are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| TEID | Transmission Element ID | Integer | Auto-populated |  |
| 15 minute rating Max Shadow Price | 15 minute rating Max Shadow price | DoubleFloat |  |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Emergency Max Shadow Price | Emergency Max Shadow price | DoubleFloat |  |  |
| Latitude | Latiitude coordinates. | Float | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Max Shadow Price | Max shadow price | DoubleFloat |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |

## Linkage

There are no required links.

# Modeling ACLineSegment

## Modeling Approach

The ACLineSegment class represents an AC transmission line that connects two different Substations.  An ACLineSegment cannot be contained within a single Substation.  Additionally, an  ACLineSegment must be underneath a Line instance and must have two Terminals.

ACLinesegment cannot go between different voltage levels.

Figure 22 - ACLineSegment

## Attributes

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| 15 minute rating Max Shadow Price | 15 minute rating Max Shadow price | Double Float |  |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| b0ch | Zero sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. | Double Float |  |  |
| bch | Positive sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. | Double Float |  |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool |  |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool |  |  |
| Emergency Max Shadow Price | Emergency Max Shadow price | Double Float |  |  |
| g0ch | Zero sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | Double Float |  |  |
| gch | Positive sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | Double Float |  |  |
| Latitude | Latiitude coordinates. | Float | None |  |
| length | Segment length for calculating line section capabilities (long length units). | Float |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Max Shadow Price | Max shadow price | Double Float |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Long Int | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | String |  |  |
| PSS®E | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | String |  |  |
| r | Positive sequence series resistance of the entire line section. | Double Float |  |  |
| R0 | Zero sequence series resistance of the entire line section. | Double Float |  |  |
| Remove | The equipment is removed from the network. | Bool |  |  |
| Remove Enable | The equipment can be removed from the network in the EMS. | Bool |  |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool |  |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Bool |  |  |
| Transmission Element ID | Transmission Element ID | Integer | Auto-populated |  |
| x | Positive sequence series reactance of the entire line section. | Double Float |  |  |
| X0 | Zero sequence series reactance of the entire line section. | Double Float |  |  |

## Linkage

The required links for a ACLineSegment are defined in Table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| BaseVoltage | A link to a BaseVoltage is only necessary when there is no VoltageLevel container used. If a VoltageLevel container is used the disconnector will inherit a BaseVoltage from the VoltageLevel. | Network/Base Voltage |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Substation

## Modeling Approach

The ERCOT CIM model defines a Substation as collection of equipment for purposes other than generation or utilization, through which electric energy in bulk is passed for the purposes of switching or modifying its characteristics.

A Substation is modeled under a SubGeographicalRegion.  VoltageLevels, Transformers and Device types are modeled under the Substation along with generic equipment.  The Substation serves as a container for these instances.  Figure below shows a Substation modeled in the IMM model hierarchy with parent/child associations labeled.    For more information on modeling VoltageLevels, Device Types, and PowerTransformers please see relevant sections.

Figure 23 - Substation

## Attributes

The attributes for a Substation are shown in the table below.

| Attribute | Description | Data Type | Default value | Sample data |
| --- | --- | --- | --- | --- |
| Transmission Element ID | Transmission Element ID | Integer |  |  |
| abnormalForAlarm | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | Boolean | FALSE |  |
| abnormalForSCADA | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | Boolean | FALSE |  |
| alarmLocation | Alarm location, must match LOC.ID_LOC in the Alarm database. | String8 |  |  |
| audibleTone | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | Boolean | FALSE |  |
| forNetwork | This flag is used to indicate this substation is used by Network application. | Boolean | FALSE |  |
| forScada | This flag is used to indicate this substation is used by SCADA application. | Boolean | FALSE |  |
| inhibitAbnormalForAlarm | Permanently Inhibit the flag of abnormalForAlarm . | Boolean | FALSE |  |
| inhibitAbnormalForSCADA | Permanently Inhibit the flag of abnormalForSCADA. | Boolean | FALSE |  |
| inhibitAudibleTone | Permanently Inhibit the flag of audibleTone. | Boolean | FALSE |  |
| inhibitLoggingAndAlarmList | Permanently Inhibit the flag of loggingAndAlarmList. | Boolean | FALSE |  |
| inhibitUnackAlarmList | Permanently Inhibit the flag of unacknowledgedAlarmList. | Boolean | FALSE |  |
| initiallyInhibit | A flag indicating that when the system first comes online, alarm indications for this SCADA entiry will initially be inhibited. | Boolean | FALSE |  |
| loggingAndAlarmList | A flag indicating that SCADA will issue neither an alarm nor an event. Therefore, entries will appear in the neither the alarm list nor the event logs. | Boolean | FALSE |  |
| overrideDefaultInhibitDef | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | Boolean | FALSE |  |
| unacknowledgedAlarmList | A flag ndicating that SCADA will issue an event to the event log, but will not issue unacknowledged alarm indications to the alarm list. | Boolean | FALSE |  |
| Alias Name | Free text name of the object or instance. | String100 |  |  |
| Latitude | Latiitude coordinates. | Float |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has seve | String30 |  |  |
| Longitude | Longitude coordinates. | Float |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String100 |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String500 |  |  |

## Linkage

Below are the required links for a Substation.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operated By (Operatorship) |  | Network/Companies |
| Own Percent (Ownership) |  | Network/Companies |

# Modeling Bay

## Modeling Approach

The ERCOT CIM model defines a Bay as a collection of Breakers and Disconnectors within a given VoltageLevel.  A Bay is modeled under a VoltageLevel. Only Breakers and Disconnectors can be modeled under a Bay. All the Breakers and Disconnectors defined under a Bay should also populate the Switch.voltageLevel association to indicate the VoltageLevel to which these devices belong to.

Figure 24 - Bay

## Attributes

The attributes for a Bay are shown in the table below.

| Attribute | Description | Data Type | Default value | Sample data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String |  |  |
| bay Energy Measurement Flag | Indicates the presence/absence of kWh/kvarh measurements. | Boolean | False |  |
| bay Power Measurement Flag | Indicates the presence/absence of MW/MVAr measurements. | Boolean | False |  |
| Breaker Configuration | Breaker configuration. | Breakerconfiguration |  |  |
| Busbar Configuration | Busbar configuration. | BusbarConfiguration |  |  |
| Description | Description of the object or instance. | String |  |  |
| Latitude | Latiitude coordinates. | Integer |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Longitude | Longitude coordinates. | Integer |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Transmission Element ID | Transmission Element ID. | Integer |  |  |

## Linkage

The required links for a Bay are defined below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling SCADA

## Modeling Approach for SCADA

This section describes the approach for modeling SCADA in the ERCOT CIM model. SCADA stands for Supervisory Control and Data Acquisition. It refers to the centralized systems which monitor and control entire sites, or complexes of systems spread over large areas. The control actions are performed automatically by the remote terminal units or by programming logic controllers.

In the ERCOT CIM model Analog and Discrete measurements are created under equipment’s Terminal. A Terminal association ascertains the ConnectivityNode in the network model that closely represents location of the physical measuring device in the field. In addition to ConnectivityNode, it is useful to know equipment in the network model, this measurement data is being supplied for. In case of most measurements this equipment is usually the parent of identified terminal.

Knowledge of the medium being utilized to transfer the measured data to ERCOT is equally essential. Most of the measurements in the CIM model use ICCP, SCADA RTUs or Calculation as the media for data transfer. The CIM model identifies the transfer medium for a measurement as its MeasurementValueSource. The subtle differences in modeling Analog and Discrete measurements from each of these MeasurementValueSources are outlined in this section.

The CIM classes, MeasurementLocation, MeasurementGroup, Analog, Discrete, AnalogValue and DiscreteValue are mainly utilized for defining the SCADA measurement components in the network model. Figure below shows the modeling of MVAR telemetry for a load as modeled in the IMM hierarchy. As can be seen in figure, an Analog named MVAR is modeled under the Load’s Terminal. An AnalogValue MVAR_SValue is modeled under the MVAR Analog. Both the Analog and AnalogValue instances are together used to define various SCADA specific features of the MVAR measurement. A MeasurementLocation is visible be modeled under the load, indicating the presence of measurements at the load. A MeasurementGroup, MGRP is modeled under the MeasurementLocation. The following sections describe the modeling of each of these classes in detail.

Figure 25 - IMM hierarchical view for SCADA measurement.

### Modeling Approach for MeasurementLocation

A MeasurementLocation is used to identify equipment in the network model which is being monitored using Analog and Discrete measurements. This monitored equipment can be of type Breaker, Busbarsection, Synchronousmachine, Transfomerwinding etc.

In the figure above a MeasurementLocation is created under the load at which the MVAR flow measurements are being monitored. A MeasurementLocation must have the exact same name as that of its parent device. In the ERCOT CIM model, a MeasurementLocation also holds the SCADA device-type for its parent device. With the exception of Lines and PowerTransformers, any equipment in the ERCOT network model must have only one child MeasurementLocation of a specific device-type. In case of Lines/PowerTransformers a maximum of two MeasurementLocation children may be present, one each of each end/winding of the Line/Transformer.

#### Linkage

The required links for a MeasurementLocation are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| HasTypeofDeviceType | Identifies the device type at which the measurement is being defined | Other Orphans/DeviceTypeName |
| HasAPermissionArea | Identifies the permission area | List_Information/Permission Areas/ERCOT |

### Modeling Approach for a MeasurementGroup

The ERCOT data dictionary defines a MeasurementGroup as a group of related Analog or Discrete measurements. In the ERCOT CIM model, MeasurementGroups are created under MeasurementLocations. Analog and Discrete measurements that are sourced from SCADA RTU’s and/or ICCP are collected together by associations to MeasurementGroup. MeasurementGroups that are under the same parent MeasurementLocation must have unique names, no longer than 4 characters. An example of a MeasurementGroup MGRP as visible in the IMM hierarchy view is shown in the below figure. Also the AnalogValues, MVAR_SValue and MW_SValue that are sourced from ICCP, both reference the MGRP.

Figure 26 - IMM hierarchical view of a load with multiple SCADA measurements.

#### Attributes

The attributes for a MeasurementGroup are shown in the table below.

| Attribute | Description | Data Type | DefaultValue | Sample Data |
| --- | --- | --- | --- | --- |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |
| buffer Period | Number of seconds to wait for a cluster of exceptions to be reported. | Short Integer | None | 3 |
| Description | Description of the object or instance. | String | None | XYZ |
| grace Period | Number of seconds to wait before declaring an expected scan "late". | Short Integer | None | 5 |
| integrity Period | Number of seconds between integrity scans. | Short Integer | None | 3 |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 323 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| scan Period | Number of seconds between scans. | Short Integer | None | 4 |

### Modeling Approach for a Calculation

A Calculation is a type of MeasurementValueSource for Analog and Discrete measurements in the network model. Calculations are usually defined when a physical quantity desired to be monitored at a particular equipment isn’t directly measured but can be computed using one or more direct/derived measurements.

In the ERCOT CIM model, a Calculation is modeled under a MeasurementLocation using one or many MeasurementArguments and/or ConstantArguments.  An example of a Calculation CALC is visible in the hierarchy view in the figure. Note that, all Calculations under the same parent MeasurementLocation should have unique names, no longer than 4 characters as well.

Figure 27 - IMM hierarchical view of a calculation definition.

#### Attributes

The attributes for a Calculation are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 232 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Type | Type | String | None | XYZ |

#### Linkage

The required links for a Calculation are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| CalculationTriggeredByCalculationTriggerTimer | Identifies Timer to be used to trigger re-computations when the inputs change. | List_Information/Calculation Trigger Timers |
| CalculationUsesFunction | Identifies the function used to do the Calculation | List_Information/Functions |

### Modeling Approach for MeasurementArgument

When creating Calculations in the ERCOT CIM model, input/output parameters that involve Analog and Discrete measurements are defined using instances of type MeasurementArgument. Each MeasurementArgument must be associated to a single SCADA AnalogValue and/or SCADA DiscreteValue in the model. Note that the output parameter of a Calculation should always be MeasurementArgument whereas not all input parameters of a Calculation need be of type MeasurementArgument.

As mentioned in earlier sections, MeasurementArguments are created under a Calculation. The Calculation CALC shown in the hierarchical view in figure has two MeasurementArguments, namely CBMW and LDMW as its input/output parameters.

#### Attributes

The attributes for a MeasurementArgument are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| referenceflag | True when the Measurement is an input and False when the Measurement is an output. | Boolean | False | False |
| triggerFlag | True if a change in the value of the associated MeasurementValue triggers a recalculation of the output | Boolean | False | False |
| Zonal Attribute | Temporary attribute to support dual SCADA feeds. | Boolean | False | False |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |
| Description | Description of the object or instance. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 343 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Reference Name | If this is a Reference, name for the reference. | String | None | XYZ |

#### Linkage

The required links for a MeasurementArgument are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| AssignedTo(FunctionArgument) | Identifies to which function argument of the function it belongs to. | List_Information/Functions/ |
| MappedTo(MeasurementValue) | Identifies a MeasurementValue that is acting as an input/output feed to/for this MeasurementArgument. |  |

### Modeling Approach for ConstantArgument

In addition to MeasurementArguments, the ERCOT data dictionary allows scalar inputs parameters to be defined for a Calculation using instances of type ConstantArguments. Similar to MeasurementArgument modeling, ConstantArguments are modeled under a Calculation as well. ConstantArguments can only serve as input parameters of a Calculation. The IMM hierarchical view for the Calculation CALC in figure shows one such CalculationArgument, namely 1NEG as its input.

#### Attributes

The attributes for a ConstantArgument are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| referenceflag | True when the Measurement is an input and False when the Measurement is an output. | Boolean | False | False |
| Zonal Attribute | Temporary attribute to support dual SCADA feeds. | Boolean | False | False |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |
| LocalName | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 232 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Reference Name | If this is a Reference, name for the reference. | String | None | XYZ |

#### Linkage

The required links for a ConstantArgument are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| AssignedTo(FunctionArgument) | Identifies to which function argument of the function it belongs to. | List_Information/Function/ FuctionArgument |
| MappedTo(ConstantValue) | Identifies a ConstantValue that is acting as an input/output feed to/for this ConstantArgument. |  |

### Modeling Function and FunctionArguments

In the ERCOT CIM model Functions are utilized to define commonly use mathematical computations pertaining to SCADA measurements. Functions get referenced when defining Calculations in the model. Some of the function definitions available for re-use in the ERCOT CIM model include absolute value (ABS), addition (ADD3), average (AVG1), bestOf (BEST), division (DIV), multiplication (MULT) and MVA-computation (MVA1). A list of all available Functions in the model can be viewed in the IMM hierarchy at the path List_Information/Functions.

The CIM model uses FunctionArguments to define the characteristic features of the input and output parameters of a function.  The attributes ReadFlag and WriteFlag for a FunctionArgument are of special importance. As the names suggests ReadFlag and WriteFlag help define the I/O nature of the parameter, i.e. the parameter will be considered as an input to the function when it’s ReadFlag = True and WriteFlag = False. Similarly the variant will be considered as an output to the Function when it’s ReadFlag = True and WriteFlag = False. In the CIM model FunctionArguments get referenced when defining MeasurementArguments and/or ConstantArguments for a Calculation.

Figure 28 - IMM hierarchical view of a Function definition in the ERCOT model.

An example of the function ADD is visible in the figure. This function has three FunctionArguments under it namely, ARG1, ARG2 and ARG3. When defining Calculations in the model the total number of input/output parameters (MeasurementArguments and/or ConstantArguments) is limited by the total number of FunctionArguments defined in the referenced Function. Thus if a calculation is to be modeled by referencing the Function ADD, it must have 3 input/output parameters (MeasurementArguments and/or ConstantArguments) modeled as its children.

### Modeling Approach for Analog and Discrete Measurement

The ERCOT data dictionary defines Analog and/or Discrete measurement as any measured, calculated or non-measured quantity. Any piece of equipment in the model can have measurements, e.g. a substation may have temperature measurements and door open indications, a transformer may have oil temperature and tank pressure measurements, a bay may contain a number of power flow measurements and a breaker may contain a switch status measurement.

As mentioned earlier, in the ERCOT model Analog and Discrete measurements are created under a terminal. The choice of a measurement is dependent on the nature of the physical quantity being measured. For example, MW/MVAR/MVA measurements will be identified as Analog measurement in the ERCOT model, whereas Status-like binary-logic based measurements will be classified as Discrete measurements in the ERCOT model.

#### Attributes

The attributes for Analog and Discrete measurements are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data | Analog | Discrete |
| --- | --- | --- | --- | --- | --- | --- |
| ForNetwork | In the case of SCADA measurement this boolean needs to be set to False. | Boolean | False | False | X |  |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False | X | X |
| Transmission Element ID | Transmission Element ID. | Long Integer | Auto Populated | 343 | X | X |
| Alias Name | Free text name of the object or instance. | String | None | XYZ | X | X |
| Description | Description of the object or instance. | String | None | XYZ | X | X |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ | X | X |
| Maximum Value | Normal value range maximum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | Float | None | 23 | X | X |
| Minimum Value | Normal value range minimum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | Float | None | 34 | X | X |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | String | 234 | X | X |
| Normal Value | Normal measurement value, e.g., used for percentage calculations. | Float | None | 34 | X | X |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ | X | X |
| Positive Flow In | If true then this measurement is a MW, MVAR or AMPS with the convention that a positive value measured at the Terminal means power is flowing into the related PowerSystemResource. | Boolean | False | False | X |  |

#### Linkage

The required links for Analog and Discrete measurements are defined in the table below

| Link Name | Description | Path Name | Analog | Discrete |
| --- | --- | --- | --- | --- |
| MeasurementUsesAMeasurementType | Specify the type of measurement ex. threephasepower, threephasereactivepower, threephaseactivepower, linecurrent, etc. | List_Information/MeasurementType | X | X |
| MeasurementUsesAUnit | Dimension of the telemetered value. Ex. MVA, MW, MVAr, A, etc. | List_Information/Units | X | X |
| MeasurementMemberOfPowerSystemResource | The device identified in this association is exactly same as the parent device of the associated terminal. | Network/ERCOTTexasNetwork/ERCOTSubstations/WeatherZone/Substation/VoltageLevel/Device | X | X |
| MeasurementOwnedByOwnership | The operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies | X | X |
| MeasurementOwnedByOperatorship | The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies | X | X |

### Modeling Approach for SCADA AnalogValue and DiscreteValue

The ERCOT data dictionary utilizes AnalogValues and/or DiscreteValues to define current state for the Analog and/or Discrete measurement. A state value is an instance of a measurement from a specific source. Analog and/or Discrete measurements can be associated with many state values, each representing a different source for the measurement.

In the ERCOT CIM model AnalogValues and/or DiscreteValues are used to define inputs for the EMS SCADA database or the ICCP database by variations in the linkages of AnalogValue and/or DiscreteValue. For simplicity the prior type of AnalogValue and/or DiscreteValue is referred as SCADA measurementvalue and the later is referred as ICCP measurementvalue this section onwards. The current section will describe the modeling subtleties of SCADA measurementvalues whereas the ICCP measurementvalues will be covered in the following sections.

All Analog and/or Discrete measurements irrespective of their MeasurementValueSource should have a SCADA MeasurementValue of appropriate type created under it. The hierarchical view in the figure shows the AnalogValue MVAR_SValue created under the Analog MVAR.

#### Attributes

The attributes for a SCADA AnalogValues and DiscreteValues are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data | Analog | Discrete |
| --- | --- | --- | --- | --- | --- | --- |
| Abnormal Alarm Delay Time | The number of seconds for the alarm to remain on the persistence alarm list before toning/alarming because it remained in the violated state. | Long Integer | None | 23 | X | X |
| Abnormal For Alarm | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | Boolean | False | False | X | X |
| Abnormal For SCADA | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | Boolean | False | False | X | X |
| Audible Tone | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | Boolean | False | False | X | X |
| Auto Acknowledge | When set to true, this flag specifies that alarms will be automatically acknowledged on return to normal. This will only occur if the Alarm Return to Violations flag is not set on the Limit Names table. | Boolean | False | False | X | X |
| Auto Ack and Delete Alarms | Automatically acknowledge and delete alarms if the Analog is manually entered or successfully controlled by the operator to a normal state. | Boolean | False | False | X | X |
| Block via Primary Site | Block Value and Quality update via Primary Site: Do not allow update from the primary site. | Boolean | False | False | X | X |
| Block via Secondary Site | Block Value and Quality update via Secondary Site: Do not allow update from the secondary site. | Boolean | False | False | X | X |
| byPass | When set to true, this flag specifies allowing bypass entry of Suspect values if telemetered from a remote site or SCADA Front End. | Boolean | False | False | X | X |
| Control Demand Scan | True = Issues a demand scan request to the RTU at a configurable number of seconds after any successful control requests are issued. This feature is primarily used by measurements with a slow scan rate to provide more timely feedback on the success or failure of the control operation. | Boolean | False | False | X | X |
| Initially Inhibit | A flag indicating that when the system first comes online, alarm indications for this SCADA entry will initially be inhibited. | Boolean | False | False | X | X |
| Inhibit Abnormal For Alarm | Permanently Inhibit the flag of abnormalForAlarm. | Boolean | False | False | X | X |
| Inhibit Abnormal For SCADA | Permanently Inhibit the flag of abnormalForSCADA. | Boolean | False | False | X | X |
| Inhibit Audible Tone | Permanently Inhibit the flag of audibleTone. | Boolean | False | False | X | X |
| Inhibit Logging and Alarm List | Permanently Inhibit the flag of loggingAndAlarmList | Boolean | False | False | X | X |
| Inhibit Unacknowledged Alarm List | Permanently Inhibit the flag of unacknowledgedAlarmList. | Boolean | False | False | X | X |
| Logging and Alarm List | Permanently Inhibit the flag of loggingAndAlarmList. | Boolean | False | False | X | X |
| Not In Service | flag indicating not in service. | Boolean | False | False | X | X |
| Override Default Inhibit Definition | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | Boolean | False | False | X | X |
| Record Historical Data | When set to true, this flag specifies that state changes on the Analog are recorded in the historical data review file. | Boolean | False | False | X | X |
| Return to Normal Alarm Delay Time | The number of seconds for the alarm to remain on the persistence alarm list before toning/alarming because it remained in the normal state. | Boolean | False | False | X | X |
| Time Delay | The number of seconds after the control request is successfully issued before sending a demand scan request to the associated RTU. | Boolean | False | False | X | X |
| Unacknowledged Alarm List | Permanently Inhibit the flag of unacknowledgedAlarmList. | Boolean | False | False | X | X |
| XEnable Auto SE Replacement | TRUE = Allow automatic State Estimator replacement. Automatically substitute the display value with a good quality state estimated value if the quality of the telemetered Analog becomes SUSPECT. | Boolean | False | False | X |  |
| Invert Analog Via Secondary Site | TRUE = Negate the Analog value when received from the secondary site. | Boolean | False | False | X |  |
| Invert Sign | When set to true, this flag specifies that the Analog value, as received by SCADA, is inverted before using in other applications. | Boolean | False | False | X |  |
| Negative Uni-Polar Clamping | True = positive values will be forced (clamped) to zero before updating into the database. | Boolean | False | False | X |  |
| Peak Data | When set to true, this flag specifies that the Peak Data Processing task will sample this Analog. | Boolean | False | False | X |  |
| Positive Uni-Polar Clamping | TRUE = negative values will be forced (clamped) to zero before updating into the database. | Boolean | False | False | X |  |
| SE Deadband | Display values of good quality which are different than a good quality state-estimated value by more than this amount are considered anomalous, and automatically substituted with the state-estimated value, if the global Automatic State-Estimator Replacement function is enabled. | Boolean | False | False | X |  |
| Zero Clamping Deadband | If value is greater than zero, then any value between zero and the entered value will be forced (clamped) to zero for update into the database. | Boolean | False | False | X |  |
| Invert Status | True = The status point value, as received by SCADA, is inverted before using in other applications. | Boolean | False | False |  | X |
| Invert Extended Status via ISD | True = The extended status bit (XIS) will be inverted when received from the primary site. | Boolean | False | False |  | X |
| Invert Extended Status Via Sec Site | True = The extended status bit (XIS) will be inverted when received from the secondary site. | Boolean | False | False |  | X |
| Invert Status Bit Received Via ISD | True = The status bit (SIS) will be inverted when received from the primary site. | Boolean | False | False |  | X |
| Invert Status Bit Received Via Sec Site | True = The status bit (SIS) will be inverted when received from the secondary site. | Boolean | False | False |  | X |
| Momentary Change Detection | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Boolean | False | False |  | X |
| No ISD Download | True = Even though the Point is associated with a remote site, the Point will not be included in the Intersite Data download request for status values to the remote site. The remote site is only used for determining which site to send Supervisory Controls to. | Boolean | False | False |  | X |
| No Warning if Hanging | Don't issue warning message if a lone Topology Node is defined, which is not defined on any other record within the Substation. | Boolean | False | False |  | X |
| status Bit Live Indication | T = S bit true indicates LIVE, false indicates DEAD; F = S bit true indicates DEAD, false indicates LIVE. | Boolean | False | False |  | X |
| Tap Changer Timeout | The timeout between steps of a multiple raise/lower supervisory control sequence for a tap changer. | Boolean | False | False |  | X |
| Three State | True = A three-state point is modeled. | Boolean | False | False |  | X |
| Alias Name | Free text name of the object or instance. | String | None | XYZ | X | X |
| Allow SELECT Step | TRUE = a separate SELECT action is allowed (but not required) prior to the supervisory control action. | Boolean | False | False | X | X |
| Component Status | True when value represents status of communication path component. | Boolean | False | False | X | X |
| Description | Description of the object or instance. | String | None | XYZ | X | X |
| from Calculation | When set to true, this flag specifies the source of the data is from Calculation, set to false otherwise. | Boolean | False | False | X | X |
| From External Program | When set to true, this flag specifies the source of the data is an external program, set to false otherwise. | Boolean | False | False | X | X |
| from Manual Entry | When set to true, this flag specifies the source of the data is from Manual Entry, set to false otherwise. | Boolean | False | False | X | X |
| from Remote | When set to true, this flag specifies the source of the data is ICCP, set to false otherwise. | Boolean | False | False | X | X |
| HABC Name | Connection ID of value using HABConnect. | String | None | False | X | X |
| ISD Name | Dollar-separacted SCADA Composite ID. | String | None | False | X | X |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ | X | X |
| Mapped In OAG | T = This data-point is also represented in the OAG model as a data item (designated member of a data packet). | Boolean | False | False | X | X |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | XYZ | X | X |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ | X | X |
| Require EXECUTE Step | True = a supervisory control action is not initiated when a control action is received, and must wait for an additional EXECUTE action. | Boolean | False | False | X | X |
| Require SELECT Step | TRUE = a separate SELECT action is required before a supervisory control action. | Boolean | False | False | X | X |
| Sensor Accuracy | The limit, expressed as a percentage of the sensor maximum, that errors will not exceed when the sensor is used under reference conditions. | Double Float | None | 45 | X | X |
| Tabular Display Priority | Priority of tabular display. | Long Integer | 0 | 3 | X | X |
| Time Stamp | The time when the value was last updated. | Date Time | None | 3/4/2009 | X | X |
| Value | Value of measurement. | Float | None | 4 | X | X |
| VMD Scope | True when value has VMD scope. | Boolean | False | False | X | X |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False | X | X |
| Control MMI Sequence | true = override any default settings. | Boolean | False | False | X |  |
| From State Estimator | When set to true, this flag specifies the source of the data is state estimator; otherwise it is usually set to False. | Boolean | False | False | X |  |
| Historical Recording Deadband | Threshold (percentage currently recorded Analog data) above which additional data points should not be retained. | Double Float | 0 | 45.6 | X |  |
| Negate Value Received from ISD | When set to true, this flag specifies that the polarity of the Analog value received via ISD will be switched. | Boolean | False | False | X |  |
| Skip Limit Checking | When set to true, this flag specifies disable reasonability limit checking for this Analog. | Boolean | False | False | X |  |
| Zero Clamping Deadband | If value is greater than zero, then any value between zero and the entered value will be forced (clamped) to zero for update into the database. | Float | None | 4.5 | X |  |
| Allow Control from Foreign Sites | True = Another site may issue a control on this point. | Boolean | False | False |  | X |
| Allow Multiple Raise or Lower | True = Multiple Tap Raise and Lower commands may be issued consecutively without re-selecting the... | Boolean | False | False |  | X |
| Feedback Analog | True = The Analog Name which is configured to provide feedback of the associated Analog value for control completion checks of Raise/Lower supervisory controls. The chosen Analog must be modeled under the same Device as the controlling Point record. This field is optional. | String | None | XYZ |  | X |
| Log for Control Issued | True = Controls issued on this point will be logged in the system activity log. | Boolean | False | False |  | X |

#### Linkage

The required links for SCADA AnalogValues and DiscreteValues are defined in the table below.

| Link Name | Description | Path Name | Analog | Discrete |
| --- | --- | --- | --- | --- |
| BelongTo(Site) | Identifies a SCADA Site that is used to transfer data measured by this measurement. W.r.t. to Nodal model, sites, QSE1-QSE3 and TSP1-TSP3are usually used with certain exceptions. | List_Information/Site | X | X |
| HasSecondary(Site) | Identifies a backup SCADA Site that may be used to transfer data measured by this measurement. W.r.t. to Nodal model, sites, QSE4-QSE7 and TSP4-TSP7 are usually used with certain exceptions. | List_Information/Site | X | X |
| CalculatedBy(Calculation) | Identifies the Calculation to which this measurement belongs. |  | X | X |
| GroupedBy(MeasurementGroup) | Identifies the measurement group to which this measurement belongs. | Points to the Measurement Group created under a MeasurementLocation | X | X |
| BelongTo (Analog Alarm Category) | Identifies whether an Analog Value belongs to Analog Alarm Category | List_Information/Analog Alarm Categories | X |  |
| HasNameof(AnalogName) | The name of the Analog value | List_Information/Analog Names | X |  |
| HasA(Accuracy Class) | Identifies if the Analog value has an accuracy class | List_Information/Accuracy Classes | X |  |
| BelongTo (Discrete Alarm Category) | Identifies whether a Discrete Value belongs to Discrete Alarm Category | List_Information/Discrete Alarm Categories |  | X |
| HasNameof(DiscreteName) | The name of the Discrete value | List_Information/Discrete Names |  | X |
| Has(ConversionTable) | Identifies whether a Discrete value has a Conversion Table | List_Information/Conversion Tables |  | X |
| HasTypeof(DiscreteType) | Identifies whether a Discrete Value has type of Discrete type. | List_Information/Discrete Type |  | X |

### Modeling Approach for Auxiliary SCADA Lists

This subsection briefly describes the various auxiliary SCADA lists in the ERCOT CIM model that are utilized when creating SCADA Analog and/or Discrete measurementvalues.

- Sites: The Sites table is used to define valid SCADA sites, including the local site. Each Point, Analog, and Count Record in the model must be associated with a SCADA Site record in this table. Only data retrieved via intersite data will be associated with any site other than the local site name. In the ERCOT model, DE is the designated local site. 	The various other sites currently defined and used in the ERCOT model are, QSE1, QSE2, QSE3, QSE4, QSE5, QSE6, QSE7, SI, TSP1, TSP2, TSP3, TSP4, TSP5, TSP6, TSP7, etc..

- Analog Alarm Category: This reference table is used to define Analog alarm category information for the SCADA subsystem. The Analog alarm categories currently defined and used in the ERCOT model are: AL and BB.

- Discrete Alarm Category: This reference table is used to model SCADA Discrete Alarm Category information. The Discrete alarm categories currently defined and used in the ERCOT model are, AL, BB, AL, AV, B1, B2, B3, B4, and SS.

- Analog Name: This reference table is used to define various types of Analog measurements that can be defined in the ERCOT CIM model. Some of the Analog Names currently defined and used in the ERCOT model are, AMP, MW, MVA, MVAR, HZ etc.

- Discrete Name: This reference table is used to define various types of Discrete measurements that can be defined in the ERCOT CIM model. Some of the Discrete Names currently defined and used in the ERCOT model are, ST, AVR, RBST, etc.

- Permission Areas: This reference table is used to define valid areas of responsibility for SCADA measurements. The Permission areas currently defined and used in the ERCOT CIM model are, AL, COMMS, EAST, ECAR, ERCOT, GEN, NORT, SOUT, and SYSTEM.

- Conversion Tables: This reference table is used to specify a method of data conversion to be utilized for measurements. The only conversion table used in the ERCOT model is the OAG (Open Access Gateway).

- Accuracy Class: This reference table holds accuracy information for measurement, generation and load schedules. The accuracy classes that are currently defined and used in the ERCOT CIM model are, DCLN, KCL, KV, LD, LDHR, LDHW, LDLR, LDLW, LDMR, LDMW, etc..

- Analog Limit Names: This reference table is used to define valid Limit names and parameters to be used when defining Limit. The Analog Limit names currently defined and used in the ERCOT model are: 15MN, DA15, DAEM, DANR, DM15, DMEM, DMNR, EMGY, etc..

- Discrete Type: This reference table is used to define parameters for switching devices, such as breakers or disconnects, in the SCADA topology model. The various Discrete Types defined currently defined and used in the ERCOT model are, CA_M, COO, HU_T, IN_T, MNB, MOB, MOO, N_A, N_T, O_C, O_C1, etc.

- DeviceTypeName: This reference table is used to define the SCADA device type names  The various Discrete Types defined currently defined and used in the ERCOT model are, BKR, BS, BUS, CAP, CB, LD, GEN etc.. More DeviceTypeNames can be found by navigating to .other Orphans/DeviceTypeName

# Modeling ICCP

## Modeling Approach for ICCP

This section describes the approach for modeling ICCP (Inter Control Center Protocol). It is used to provide data exchange between control centers, utilities, power pools, regional control centers and Non-Utility Generators. The data that is sent can be periodic system data, block data transfer, information messages, device control requests etc. Figure below shows the modeling of MVAR telemetry that is sourced from ICCP for a load as modeled in the IMM hierarchy.

Figure 29 - IMM hierarchical view of ICCP-sourced measurements in the ERCOT model.

As mentioned earlier the ERCOT CIM model allows multiple AnalogValues and/or DiscreteValues to be associated with the same Analog and/or Discrete measurement parent. This feature is exploited when modeling Analog and/or Discrete measurements that are sourced from ICCP in the ERCOT model. In practice the ERCOT CIM model allows a maximum of three AnalogValue and/or DisceteValues to reside under the same Analog and/or Discrete parent. As mentioned in the earlier section on SCADA one amongst these three AnalogValues and/or DiscreteValues is the SCADA measurementvalue that holds information necessary to define the instance in the EMS SCADA database and the other two may be utilized to provide information relevant to the ICCP source. An Analog and/or Discrete measurement may contain two ICCP measurementvalues in the scenarios when the telemetered ICCP value is desired to be visible in both ERCOT TSP and ERCOT QSE ICCP database. The modeling of ICCP will be described in the sections to follow.

## Modeling Approach for ICCP AnalogValue and DiscreteValue

The ERCOT CIM model utilizes AnalogValue and DiscreteValues to model ICCP related data. The current section will identify the modeling subtleties of ICCP measurementvalues. As mentioned earlier the ICCP AnalogValue and/or DiscereteValue is created under an Analog and/or Discrete measurement in the IMM hierarchy. In the figure below the AnalogValue, ICCP_Value is the ICCP AnalogValue that holds information relevant to the ICCP source of the MVAR Analog measurement. It is imperative for a SCADA AnalogValue/DiscreteValue to be defined under the same Analog parent utilizing the modeling approach described in the previous sections.

### Attributes

The attributes for ICCP AnalogValues and DiscreteValues are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data | Analog | Discrete |
| --- | --- | --- | --- | --- | --- | --- |
| Remote Site Normally Calculated. | Remote site normally calculated. True for ICCP, false otherwise. | Boolean | False | False | X | X |
| Remote Site Normally Estimated | Remote site normally estimated. True for ICCP, false otherwise. | Boolean | False | False | X | X |
| Remote Site Normally Manually Entered | Remote site normally manually entered. True for ICCP, false otherwise. | Boolean | False | False | X | X |
| Remote Site Normally Telemetered | Remote site normally telemetered. True for ICCP, false otherwise. | Boolean | False | False | X | X |
| ICCP Data Set Period | ICCP data set period used for the measurement. | Long Integer | None | 3 | X | X |

### Linkage

The required links for ICCP AnalogValues and DiscreteValues are defined in the table below.

| Link Name | Description | Path Name | Analog | Discrete |
| --- | --- | --- | --- | --- |
| MeasurementValue Source | MeasurementValueSource describes the alternative sources updating a MeasurementValue. | Network/Companies / MeasurementValueSource | X | X |

## Modeling Approach for MeasurementValueQuality

MeasurementValueQuality codes are flags which are utilized to know the quality of the data that is received or sent by or to ERCOT. There are various quality codes that are used by ERCOT and the MarketParticipant to communicate about the quality of data. In the ERCOT model a MeasurementValueQuality must be modeled under the ICCP AnalogValue or  DiscreteValue. The following figure shows this hierarchical association between AnalogValue/DisceretValue and a MeasurementValueQuality the MeasurementValueQuality, ICCP_Quality modeled under the ICCP AnalogValue ICCP_Value.

### Attributes

The attributes for ICCP MeasurementValueQuality are shown in the table below

| Attribute | Description | Data Type | Default Value | Sample Data | Analog | Discrete |
| --- | --- | --- | --- | --- | --- | --- |
| hasCOV | Whether or not ICCP item has Change of Value modifier. | Boolean | False | False | X | X |
| hasquality | Whether or not ICCP item has Quality modifier. | Boolean | False | False | X | X |
| hasTimeStamp | Whether or not ICCP item has Timestamp modifier. | Boolean | False | False | X | X |
| ZonalAttribute | Temporary attribute to support dual SCADA feeds. | Boolean | False | False | X | X |
| Alias Name | Free text name of the object or instance. | String | None | XYZ | X | X |
| Bad Reference | Measurement value may be incorrect due to a reference being out of calibration. | Boolean | False | False | X | X |
| Description | Description of the object or instance. | String | None | XYZ | X | X |
| Estimator Replaced | Value has been replaced by State Estimator. estimatorReplaced is not an IEC61850 quality bit but has been put in this class for convenience. | Boolean | False | False | X | X |
| Failure | This identifier indicates that a supervision function has detected an internal or external failure, e.g. communication failure. | Boolean | False | False | X | X |
| LocalName | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ | X | X |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | XYZ | X | X |
| Old Data | Measurement value is old and possibly invalid, as it has not been successfully updated during a specified time interval. | Boolean | False | False | X | X |
| Operator Blocked | Measurement value is blocked and hence unavailable for transmission. | Boolean | False | False | X | X |
| Oscillatory | To prevent some overload of the communication it is sensible to detect and suppress oscillating (fast changing) binary inputs. If a signal changes in a defined time (tosc) twice in the same direction (from 0 to 1 or from 1 to 0) then oscillation is detected and the detail quality identifier 'oscillatory' is set. If it is detected a configured numbers of transient changes could be passed by. In this time the validity status 'questionable' is set. If after this defined numbers of changes the signal is still in the oscillating state the value shall be set either to the opposite state of the previous stable value or to a defined default value. In this case the validity status 'questionable' is reset and 'invalid' is set as long as the signal is oscillating. If it is configured such that no transient changes should be passed by then the validity status 'invalid' is set immediately in addition to the detail quality identifier 'oscillatory' (used for status information only). | Boolean | False | False | X | X |
| Out of Range | Measurement value is beyond a predefined range of value. | Boolean | False | False | X | X |
| Over Flow | Measurement value is beyond the capability of being represented properly. For example, a counter value overflows from maximum count back to a value of zero. | Boolean | False | False | X | X |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ | X | X |
| Source | Source gives information related to the origin of a value. The value may be acquired from the process, defaulted or substituted. | Enumeration | PROCESS | PROCESS | X | X |
| Suspect | A correlation function has detected that the value is not consitent with other values. Typically set by a network State Estimator. | Boolean | False | False | X | X |
| Test | Measurement value is transmitted for test purposes. | Boolean | False | False | X | X |
| Validity | Validity may be good, questionable or invalid. Refer to the Validity enumeration for more details. | Enumeration | GOOD | GOOD | X | X |

### Linkage

The required links for ICCP MeasurementValueQuality are defined in the table below.

| Link Name | Description | Path Name | Analog | Discrete |
| --- | --- | --- | --- | --- |
| MeasurementValueQualityMemberOfMeasurementValue | A MeasurementValue has a MeasurementValueQuality associated with it. |  | X | X |

# Modeling Ratings

### Modeling Approach for Ratings

In the network model static ratings are required to be defined for different equipment types (eg. lines, transformers, etc.). In addition to defining operational thresholds for devices, these ratings help define the reasonable boundary conditions for analogs measurements telemetered on the devices as well.

The ERCOT CIM model utilizes instances of type AnalogLimitSets and AnalogLimits to model both, operational static limits of a device and SCADA limits of individual analog measurements. In the model both the Rating AnalogLimitSets and SCADA AnalogLimitSets are defined under an Analog. The attribute forNetwork on the parent Analog measurement is used to distinguish analogs containing Rating AnalogLimitSets (forNetwork = True) from analogs containing SCADA AnalogLimitsSets (forNetwork = False). The following sections describe the other subtle differences in modeling Rating AnalogLimitsSets and SCADA AnalogLimitSets.

### Modeling Approach for SCADA AnalogLimitSet

SCADA AnalogLimitSets (AnalogLimitSet.forNetwork = False) define a group of Limits that are help set the bounds of SCADA Analog telemetry. In the current ERCOT model SCADA AnalogLimitSets are modeled for Transfomers and Lines only. Figure below shows the modeling of SCADA AnalogLimitSets for a line as modeled in the IMM hierarchy. In the figure below the SCADA AnalogLimitSet, ALS is modeled under the Analog measurement named, MVA. Note that every Analog can contain only one SCADA AnalogLimitSet definition.

Figure 30 - IMM hierarchical view of SCADA limits in the ERCOT model.

#### Attributes

The attributes for AnalogLimitSet are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| ForNetwork | In the case of SCADA limits this boolean should be set to False. | Boolean | False | False |
| IsPercentageLimits | Tells if the limit values are in percentage of normalValue or the specified Unit for Measurements and Controls. | Boolean | False | False |
| ZonalAttribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |
| Description | Description of the object or instance. | String | None | XYZ |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 123 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Type | This value should be set to Limits when ForNetwork is False. | Enumerator | None | limits |

#### Linkage

The required links for AnalogLimitSet are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Belongs To (ModelingAuthoritySet) | An IdentifiedObject belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. |  |
| Has A (Season) | Defines season associated to the rating. |  |

### Modeling Approach for SCADA AnalogLimit

The ERCOT data dictionary utilizes the AnalogLimits to specify the limit values for the Analog measurement.  AnalogLimits are modeled under the AnalogLimitSet. The attribute limittype is utilized to classify the type of the AnalogLimit being modeled. The commonly utilized types are fifteen minute rating, two hour rating, normal rating and conductor rating. In the ERCOT CIM model every AnalogLimitSet can have a maximum of four distinctly typed AnalogLimits as its children. In the figure below, four AnalogLimits, namely 15MN, CONDUCTOR, EMGY and NRML are modeled as under of the AnalogLimitSet, ALS.

#### Attributes

The attributes for AnalogLimit are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| LowerThreshhold | The value below which the Analog is considered in violation of the limit. When the Upper Threshold is null, only the Lower Threshold is checked for violation. | Float | None | -24 |
| UpperThreshhold | The value above which the Analog is considered in violation of the limit. When the low limit is null, only the high limit is checked for violation. This value must be greater than the Lower Threshold. | Float | None | 24 |
| Deadband | Amount, expressed as a percentage of the range between upper and lower threshold, used in the limit comparison to eliminate extraneous alarms generated when an Analog value oscillates around a limit. When either threshold is null, the percentage is that of the non-null limit. | Double Float | None | 5 |
| LimitType | Type of limit. | Enumeration | None | Normal Rating |
| ForbiddenRegion | T = The Analog is in violation if it is smaller than the Upper Threshold and larger than the Lower Threshold. | Boolean | False | False |
| IgnoreLimitChecking | T = The limit should be ignored when checking the Analog for limit violations. | Boolean | False | False |
| UsePercentage | T = The value displayed in the deadband field (below) is the percentage deadband. Otherwise, the value displayed is the numeric deadband. | Boolean | False | False |
| Value | The value to supervise against. Should be Null for SCADA AnalogLimit. | Double Float | None | Null |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 123 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |

#### Linkage

The required links for AnalogLimit are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| AnalogLimitBelongstoLimitAlarmCategory | Describes the type of alarm to be raised when the limit is violated. This association should be populated for SCADA AnalogLimits. | List_Information/LimitAlarmCategory |
| AnalogLimitHasNameofAnalogLimitName | Describes the type of AnalogLimit. This association should be populated for SCADA AnalogLimits. | List_Information/AnalogLimitNames |

### Modeling Approach for Ratings AnalogLimitSet

Ratings AnalogLimitSets (AnalogLimitSet.forNetwork = True) define the static ratings of a device in the model. In the current ERCOT model Rating AnalogLimitSets are modeled for Transfomers and Lines only. When modeling Rating AnalogLimitSets, modeling flexibility is available to model different sets of ratings when direction of current flow through the device changes. This flexibility can be executed by utilizing the positiveFlowIn attribute on the parent Analog.

The figure below shows the modeling of Rating AnalogLimitSets for a line as modeled in the IMM hierarchy. In the figure the AnalogLimitSet Pos_Rating_ALS contains operational ratings of the line when current is flowing into the ERCOT grid whereas the AanlogLimitSet Neg_Rating_ALS contains operational ratings of the line when current is flowing out of the ERCOT grid. Note that every rating Analog (Analog.forNetwork = True) can contain only one rating AnalogLimitSet definition and no SCADA or ICCP AnalogValue children.

Figure 31 - IMM hierarchical view of static ratings of a device in the ERCOT model.

#### Attributes

The attributes for AnalogLimitSet are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| ForNetwork | In the case of SCADA limits this boolean should be set to False. | Boolean | False | False |
| IsPercentageLimits | Tells if the limit values are in percentage of normalValue or the specified Unit for Measurements and Controls. | Boolean | False | False |
| ZonalAttribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |
| Description | Description of the object or instance. | String | None | XYZ |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 123 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Type | This value should be set to Limits when ForNetwork is False. | Enumerator | None | rating |

#### Linkage

The required links for AnalogLimitSet are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Belongs To (ModelingAuthoritySet) | An IdentifiedObject belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. |  |
| Has A (Season) | Defines season associated to the rating. |  |

### Modeling Approach for Ratings AnalogLimit

The ERCOT data dictionary utilizes the AnalogLimits to specify the limit values for the Analog measurement.  AnalogLimits are modeled under the AnalogLimitSet. The attribute limittype is utilized to classify the type of the AnalogLimit being modeled. The commonly utilized types are fifteen minute rating, two hour rating, normal rating and conductor rating. In the ERCOT CIM model every AnalogLimitSet can have a maximum of four distinctly typed AnalogLimits as its children. In the figure, four AnalogLimits, namely 15MN, CONDUCTOR, EMGY and NRML are modeled as under of the AnalogLimitSet, ALS.

#### Attributes

The attributes for AnalogLimit are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| Value | The value to supervise against. Should be Null for SCADA AnalogLimit. | Double Float | None | Null |
| Deadband | Amount, expressed as a percentage of the range between upper and lower threshold, used in the limit comparison to eliminate extraneous alarms generated when an Analog value oscillates around a limit. When either threshold is null, the percentage is that of the non-null limit. | Double Float | None | 5 |
| LimitType | Type of limit. | Enumeration | None | Normal Rating |
| LowerThreshhold | The value below which the Analog is considered in violation of the limit. When the Upper Threshold is null, only the Lower Threshold is checked for violation. | Float | None | -24 |
| UpperThreshhold | The value above which the Analog is considered in violation of the limit. When the low limit is null, only the high limit is checked for violation. This value must be greater than the Lower Threshold. | Float | None | 24 |
| ForbiddenRegion | T = The Analog is in violation if it is smaller than the Upper Threshold and larger than the Lower Threshold. | Boolean | False | False |
| IgnoreLimitChecking | T = The limit should be ignored when checking the Analog for limit violations. | Boolean | False | False |
| UsePercentage | T = The value displayed in the deadband field (below) is the percentage deadband. Otherwise, the value displayed is the numeric deadband. | Boolean | False | False |
| Zonal Attribute | Temp Attribute to support dual SCADA feeds. | Boolean | False | False |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 123 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |

#### Linkage

The required links for AnalogLimit are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| AnalogLimitBelongstoLimitAlarmCategory | Describes the type of alarm to be raised when the limit is violated. This association should be not populated for ratings AnalogLimits. | List_Information/LimitAlarmCategory |
| AnalogLimitHasNameofAnalogLimitName | Describes the type of AnalogLimit. This association should not be populated for ratings AnalogLimits. | List_Information/AnalogLimitNames |

# Modeling Transformers

## Modeling Approach

A Transformer is defined as an energy transformation device that transforms alternating current or voltage at one level to alternating current or voltage at another level depending on the application of the device. The two most common usages of Power Transformers are as a voltage Step-Up Transformer from generation level to transmission level and as a Step-Down Transformer from transmission level to load end users.

Transformers are modeled under a Substation in the ERCOT Model. The three types of transformers currently modeled are Two-winding, Three-winding and phase shifting transformers. Three-winding transformers are modeled as three two-winding transformers with a common tie at 1Kv and are associated to a TransformerKluge. A Power Transformer is required to have a PowerTransformer class, 2 TransformerWinding being the Primary and Secondary, Terminal for each end and a unique TapChanger for a TransformerWinding specifying if it is a Load Tap Changer or a Fixed Tap.

The following subsections shows the hierarchical association on modeling PowerTransformer, TransformerWinding,TapChanger and TransformerKluge.

## Modeling approach for Powertransformer

PowerTransformer is modeled under Substation as a child instance. Transformer Type should be defined in this class depending on its operational use. The transformer types are voltageControl(regulates voltage), phaseControl(phase shifters), voltageAndPhaseControl and fix.

Figure below shows the parent/child hierarchy of a PowerTransformer in IMM.

Figure 32 - Hierarchy for PowerTransformer

### Attributes

The attributes for a PowerTransformer are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| 15 minute rating Max Shadow Price | States the 15 minute rating Max Shadow price for a Transformer. | DoubleFloat | 99999 |  |
| Alias Name | Free text name of the object or instance | String | None |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | TRUE |  |
| Emergency Max Shadow Price | States the Emergency Max Shadow price for a Transformer | DoubleFloat | 99999 |  |
| Latitude | Latiitude coordinates. | DoubleFloat | None |  |
| Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | String | None |  |
| Magnetizing Saturation Flux | Core magnetizing saturation curve knee flux level. | PerCent | None |  |
| Magnetizing Saturation Voltage | The reference voltage at which the magnetizing saturation measurements were made. | Voltage | None |  |
| Magnetizing Susceptance Saturation | Core shunt magnetizing susceptance in the saturation region, in per cent. | PerCent | None |  |
| Max Shadow Price | States the Max Shadow price for a Power Transformer. | DoubleFloat | 99999 |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Phases | Describes the phases carried by a power transformer. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode | None |  |
| RUC Monitored | he Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | TRUE |  |
| Transformer Cooling Type | Type of transformer cooling. | EnumTransformerCoolingType | FALSE |  |
| Transformer Type | Transformer Type. | EnumTransformerType | None | voltageControl, phaseControl, fix |
| Transmission Element ID | Transmission Element ID. | Integer | None |  |
| Voltage Sensitivity | SENSITIVITY OF VOLTAGE TO THE TRANSFORMER tap ratio. | PerCent | None |  |

### Linkage

The required links for a PowerTransformer are defined in table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operated By (Operatorship) | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Own Percent (Ownership) | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

## Modeling approach for Transformerwinding

TransformerWinding is modeled under PowerTransformer as a child instance. This is where the Impedance, Transformer Winding Ratings, Connection Type (Wye or Delta) and Winding Type (Primary and Secondary) are defined.

Figure below shows the parent/child hierarchy of a TransformerWinding in IMM.

Figure 33 - Hierarchy for TransformerWinding

### Attributes

The attributes for a TransformerWinding are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance | String | None |  |
| Connection Type | The type of connection of the winding (e.g. Delta, Wye, zigzag). | EnumWindingConnection | 1 |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | TRUE |  |
| Emergency Rating | The MVA that the winding can carry under emergency conditions. | ApparentPower | 99999 |  |
| Grounded | Set if the winding is grounded. | Boolean | TRUE |  |
| Insulation kV | Basic insulation level voltage rating. | Voltage | None |  |
| Latitude | Latiitude coordinates. | DoubleFloat | None |  |
| Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None |  |
| Normal Rating | The normal rating, in MVA, for the winding. | ApparentPower | 99999 |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Phases | Describes the phases carried by a power transformer. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode | None |  |
| RUC Monitored | he Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | TRUE |  |
| Rated KV | The rated voltage (phase-to-ground) of the winding, usually the same as the neutral voltage. | Voltage | None |  |
| Remove | The equipment is removed from the network. | Boolean | FALSE |  |
| Remove Enable | The equipment can be removed from the network. | Boolean | FALSE |  |
| Short Term Rating | MVA that the winding can carry for a short period of time. | ApparentPower | 99999 |  |
| Transmission Element ID | Transmission Element ID. | Integer | None |  |
| Winding Type | The type of winding, i.e., Primary, Secondary, Tertiary, Quaternary. | EnumWindingType | None |  |
| b | Magnetizing branch susceptance (B mag). | Susceptance | None |  |
| bmag Sat | Shunt magnetizing susceptance in saturation region. | Susceptance | None |  |
| g | Magnetizing branch conductance (G mag). | Conductance | None |  |
| gmag Sat | Shunt magnetizing conductance in saturation region. | Conductance | None |  |
| knee Sat | Magnetization curve saturation knee flux level (pu volts/pu hz) | Float | None |  |
| r | Positive sequence series resistance of the winding. | Resistance | None |  |
| r0 | Zero sequence series resistance of the winding. | Resistance | None |  |
| rground | Ground resistance path through connected grounding transformer. | Resistance | 0 |  |
| x | Positive sequence series reactance of the winding. | Reactance | None |  |
| x ground | Ground reactance path through connected grounding transformer. | Reactance | None |  |
| x0 | Zero sequence series reactance of the winding. | Reactance | None |  |

### Linkage

The required links for a TransformerWinding are defined in table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operated By (Operatorship) | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Own Percent (Ownership) | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

## Modeling TapChanger

TapChanger is modeled under TransformerWinding as a child instance. Tap Changers can be a Load Tap Changer or a Fixed tap(LTC Control Mode is set to “off”). If the Transformer is a Phase Shifting Transformer, a PhaseShifterImpedanceCurve should be associated with the TapChanger. All the properties of a TapChanger such as Step Size, Step Voltage Increment, Step Phase Increment, etc. are defined in this class.

Figure below shows the parent/child hierarchy of a TapChanger in IMM.

Figure 34 - Hierarchy for TapChanger

### Attributes

The attributes for a TapChanger are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| AVR Enabled | T =Automatic Voltage Regulation is enabled | Boolean | FALSE |  |
| AWR Enabled | T = automatic MW control is enabled | Boolean | FALSE |  |
| Alias Name | Free text name of the object or instance | String | None |  |
| Coupled To Transformer | T = indicates that the phase shifter is coupled to a transformer winding | Boolean | FALSE |  |
| Flow Sensitivity | The sensitivity of the regulated MW flow to angle changes, in MW per degree | Float | None |  |
| High Step | Highest possible tap step position, advance from neutral | TapStep | 0 |  |
| Initial Delay | For an LTC, the delay for initial tap changer operation (first step change). | Seconds | 10 |  |
| LTC Control Mode | For an LTC, the tap changer control mode, e.g.: Off, Local, Volt, MVAr | EnumTransformerControlMode | None | volt |
| Latitude | Latitude coordinates. | DoubleFloat | None |  |
| Load-Based Regulation Enabled | T = Load-Based Voltage Regulation is enabled | Boolean | FALSE |  |
| Figure below shows the parent/child hierarchy of a Power transformer in IMM. Figure below shows the parent/child hierarchy of a TransformerWinding in IMM. Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | String | None |  |
| Low Step | Lowest possible tap step position, retard from neutral | TapStep | 0 |  |
| Maximum kV | The maximum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | Voltage | None |  |
| Minimum kV | The minimum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | Voltage | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None |  |
| Neutral Angle | The CIM currently has no way of defining the angle associated with the neutral position of a TapChanger belonging to a phase shifter. Thus a neutralAngle attribute (measured in degrees) has been added to the TapChanger class. This attribute only appears in XML when the parent PowerTransformer is a phase shifter, i.e., when PowerTransformer.transformerType = "phaseControl" or "voltageAndPhaseControl". | AngleDegrees | None |  |
| Neutral KV | Voltage at which the winding operates at the neutral tap setting. | Voltage | None |  |
| Neutral Step | The neutral tap step position for this winding. | TapStep | 0 |  |
| Normal Step | The tap step position used in 'normal' network operation for this winding. For a 'Fixed' tap changer indicates the current physical tap setting. | TapStep | 0 |  |
| PAR Maximum MW | PAR maximum MW value (MW). | ActivePower | None |  |
| PAR Minimum MW | PAR minimum MW value (MW). | ActivePower | None |  |
| PAR Optimization | PAR optimization flag. | Boolean | FALSE |  |
| PAR Ramp Rate | PAR optimiation ramp rate (MW per minute). | ActivePower | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Step Phase Shift Increment | Phase shift, in degrees, per step position. A positive value indicates a positive phase shift from the winding where the tap is located to the other winding (for a two-winding transformer), or to the &quot;T&quot; point (for a three-winding transformer). | AngleDegrees | None |  |
| Step Voltage Increment | Tap step increment, in per cent of nominal voltage, per step position. | PerCent | None |  |
| Subsequent Delay | For an LTC, the delay for subsequent tap changer operation (second and later step changes). | Seconds | 5 |  |
| Transmission Element ID | Transmission Element ID. | Integer | None |  |

### Linkage

The required links for a TapChanger are entered in BOLD in table below. The path name shows where the links can be found in the model.  Definitions for all of the links can be found by clicking on the help button at the bottom of the links screen.

The required Links for a TapChanger varies depending on the operational use of the Transformer. Important points to consider are as follows:

- If the Transformer is a Phase Shifting Transformer, a Phase Shifter Impedance Curve should be associated through the “Has A (PhaseShifterImpedanceCurve)” linkage.

- If the Transformer is equipped with a Tap Ratio Curve, a Tap Ratio Curve should be associated through the “Has A (TapRatioCurve)” linkage.

- If the Transformer’s are operated in a Parallel configuration. A Master and a Follower should be identified amongst the Transformer’s in Parallel. Hence if the Transformer is a Follower, the “Has A Master (TapChanger)” should be associated indicating the Master Transformer.

- “Regulated By (LoadBasedRegulationCurve)” may be filled if the TapChanger is the LTC side.

- “Regulates (Measurement)” maybe filled if the TapChanger is the LTC side depending if Voltage or MW Flow Regulation is desired.

- “Regulates (Terminal)” should be filled if the TapChanger is the LTC side with the linkage shown in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Has A (PhaseShifterImpedanceCurve) |  | Curves/Phase Shifter Impedance Curves |
| Has A (TapRatioCurve) |  | Curves/Tap Ratio Curve |
| Has A Master (TapChanger) |  | Network/ERCOT Texas Network/ERCOT Substations/Sub Geographical Region/Substation/PowerTransformer/TransformerWinding/TapChanger |
| Regulated By (LoadBasedRegulationCurve) |  | Schedules/Regulation Schedule |
| Regulates (Measurement) | An LTC may regulate a specific measurement from the network, typically voltage. A phase shifter would typically be used to regulate a real power (MW) flow measurement. An LTC with significant phase shift characteristics could be used to regulate MW flow instead of voltage. |  |
| Regulates (Terminal) |  | Network/ERCOT Texas Network/ERCOT Substations/Sub Geographical Region/Substation/PowerTransformer/TransformerWinding/Terminal |
| RegulationSchedule | An LTC may have a regulation schedule. | Schedules/Regulation Schedules/Schedule |
| Operated By (Operatorship) | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Own Percent (Ownership) | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

## modeling approach for Transformerkluge

This class is used for Three Winding Transformers. In ERCOT CIM Model, Three winding transformers are modeled as a three 2-winding transformers with a common tie at 1KV. TransformerKluge is modeled under sysOrphan as a child instance. The 2-winding transformers that comprises the Three Winding Transformer are linked together in this class through the “Has A (PowerTransformer)”  links tab.

Figure below shows the parent/child hierarchy of a TransformerKluge in IMM.

Figure 35 - Hierarchy for TransformerKluge

### Attributes

The attributes for a TransformerKluge are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance | String | None |  |
| Description | Description of the object or instance. | Boolean | FALSE |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None |  |
| PSS/E 3 Winding ID | Attribute will be used to store the three winding transformer ID and Mark which transformers are to be grouped as three winding Transformers. | String2 | None |  |
| PSS/E 3 Winding Name | Attribute will be used to store the three winding transformer name. | String12 | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

The required links for a TransformerKluge are defined in table below

| Link Name | Description | Path Name |
| --- | --- | --- |
| Has A (PowerTransformer) | Indicates the Power Transformers associated to a Three Winding Transformer | Network/ERCOT Texas Network/ERCOT Substations/Sub Geographical Region/Substation/PowerTransformer |

# Modeling Load

## Modeling Approach

In the ERCOT CIM model, Loads are any classes that inherit from the class: EnergyConsumer. EnergyConsumer is an abstract class and should not be used for real loads.

CustomerLoad inherits from ConformLoad and is used in the ERCOT model. StationSupply also inherits from EnergyConsumer and is used in the ERCOT model. Loads of type StationSupply and CustomerLoad should be modeled under a VoltageLevel in a Substation.

## Modeling Approach for CustomerLoad

Conforming loads can be modeled as an instance of the CustomerLoad class. The instance needs to be contained in an equipmentContainer of the class VoltageLevel. The VoltageLevel needs to be contained in a Substation.

The CustomerLoad class is used to model the location in which power is being removed from the transmission grid.  Each CustomerLoad class represents a single transformer in the field.  The amount of power consumed by the CustomerLoad is dictated by an associated hourly schedule.

Each CustomerLoad instance should be associated with one instance of SettlementNOIELoadZone, or one instance of DCTie, or its parent Substation should be associated with one instance of SettlementLoadZone.

If a Load is assigned to a NOIE load zone, then its electrical bus can ONLY have loads that are assigned to the same NOIE load zone, i.e. cannot have other loads at the same electrical bus assigned to different load zone

In other words, all loads that connect to the same EB must belong to the same load zone. All those loads must either be associated to the same NOIE load zone, or none of them has this association.

CustomerLoad and Load instances cannot have association to PrivateAreaNetwork of type ERCOTPANTYPE.PrivateUseNetwork or SelfServe or BLT_Normally_out.

### Attributes

The attributes for a CustomerLoad are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Conforming Load Flag | Flag is set to YES if the load is conforming, i.e., tracks the area load to which the energy consumer belongs. | Boolean | True |  |
| Customer Count | Number of individual customers represented by this Demand. | Counter |  | 123 |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Description | Description of the object or instance. | String |  |  |
| Fixed Reactive Power | Reactive component of the load that is a fixed quantity, MVAr. | ReactivePower |  |  |
| Fixed Reactive Power Percent | Fixed MVAr as per cent of load area fixed MVAr. | Percent |  |  |
| Fixed Real Power | Real component of the load that is a fixed quantity, MW. | ActivePower |  |  |
| Fixed Real Power Percent | Fixed MW as per cent of load area fixed MW. | Percent |  | 45.1856 |
| height | height | Integer |  |  |
| label height | label height | Integer |  |  |
| label width | label width | Integer |  |  |
| label x co-ordinate | label x co-ordinate | Integer |  |  |
| label y co-ordinate | label y co-ordinate | Integer |  |  |
| Latitude | Latiitude coordinates. | Float |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Longitude | Longitude coordinates. | Float |  |  |
| Maximum MVAR | Maximum Reactive POWER LOAD. | Float |  | 80 |
| Maximum MW | Maximum REAL POWER LOAD. | Float |  | 80 |
| Minimum MVAR | MINIMUM Reative POWER LOAD. | Float |  | -80 |
| Minimum MW | MINIMUM REAL POWER LOAD. | Float |  | 0 |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  | 470542 |
| Nominal Reactive Power | Nominal value for reactive power, MVAr. | ReativePower |  | 5 |
| Nominal Reactive Power Percent | Nominal MVAr as per cent of load group nominal MVAr. | Percent |  |  |
| Nominal Real Power | Nominal value for real power, MW. Nominal real power is adjusted according to the load profile selected for the consumer. It equates to one per unit in the load profile. | ActivePower |  | 95 |
| Nominal Real Power Percent | Nominal MW as per cent of load group nominal MW. | Percent |  |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode |  |  |
| Power Factor | Power factor for nominal portion of load. Defined as MW/MVA. | PowerFactor |  | 0.999991 |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | String |  | 1 |
| Reactive Power Frequency Exponent | Exponent of per unit frequency effecting reactive power | Exponent |  |  |
| Reactive Power Voltage Exponent | Exponent of per unit voltage effecting reactive power. | Exponent |  |  |
| Real Power Frequency Exponent | Exponent of per unit frequency effecting real power. | Exponent |  |  |
| Real Power Voltage Exponent | Exponent of per unit voltage effecting real power. | Exponent |  |  |
| Remove | The equipment is removed from the network. | Boolean | False |  |
| Remove Enable | The equipment can be removed from the network. | Boolean | False |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Transmission Element ID | Transmission Element ID. | Integer |  |  |
| width | width | Integer |  |  |
| x co-ordinate | x co-ordinate | Integer |  |  |
| y co-ordinate | y co-ordinate | Integer |  |  |

### Linkage

The required links for a CustomerLoad are shown in the table below.

| Link Name | Description | Path |
| --- | --- | --- |
| Assigned To (ConformLoadGroup) | Consumers may be assigned to a load area. | Schedules/Load Area Schedules/ERCOT/SubLoadArea |
| Operated By (Operatorship) | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Own Percent (Ownership) | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

## Modeling Approach for StationSupply

Loads that are not customer load can be modeled as an instance of the StationSupply class. A StationSupply load may be either conforming or non-conforming. The instance needs to be contained in an equipmentContainer of the class VoltageLevel. The VoltageLevel needs to be contained in a Substation.

The StationSupply class is used to model the power necessary to support the generation of power (i.e. feed water pumps, condenser pumps, etc.).  The amount of power consumed by the station supply will be dependent on the output of an associated generator.

### Attributes

The required attributes for a StationSupply are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Conforming Load Flag | Flag is set to YES if the load is conforming, i.e., tracks the area load to which the energy consumer belongs. | Boolean | True |  |
| Customer Count | Number of individual customers represented by this Demand. | Counter |  | 123 |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| DAM Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Description | Description of the object or instance. | String |  |  |
| Fixed Reactive Power | Reactive component of the load that is a fixed quantity, MVAr. | ReactivePower |  |  |
| Fixed Reactive Power Percent | Fixed MVAr as per cent of load area fixed MVAr. | Percent |  |  |
| Fixed Real Power | Real component of the load that is a fixed quantity, MW. | ActivePower |  |  |
| Fixed Real Power Percent | Fixed MW as per cent of load area fixed MW. | Percent |  | 45.1856 |
| height | height | Integer |  |  |
| label height | label height | Integer |  |  |
| label width | label width | Integer |  |  |
| label x co-ordinate | label x co-ordinate | Integer |  |  |
| label y co-ordinate | label y co-ordinate | Integer |  |  |
| Latitude | Latiitude coordinates. | Float |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Longitude | Longitude coordinates. | Float |  |  |
| Maximum MVAR | Maximum Reactive POWER LOAD. | Float |  | 80 |
| Maximum MW | Maximum REAL POWER LOAD. | Float |  | 80 |
| Minimum MVAR | MINIMUM Reative POWER LOAD. | Float |  | -80 |
| Minimum MW | MINIMUM REAL POWER LOAD. | Float |  | 0 |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  | 470542 |
| Nominal Reactive Power | Nominal value for reactive power, MVAr. | ReativePower |  | 5 |
| Nominal Reactive Power Percent | Nominal MVAr as per cent of load group nominal MVAr. | Percent |  |  |
| Nominal Real Power | Nominal value for real power, MW. Nominal real power is adjusted according to the load profile selected for the consumer. It equates to one per unit in the load profile. | ActivePower |  | 95 |
| Nominal Real Power Percent | Nominal MW as per cent of load group nominal MW. | Percent |  |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode |  |  |
| Power Factor | Power factor for nominal portion of load. Defined as MW/MVA. | PowerFactor |  | 0.999991 |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | String |  | 1 |
| Reactive Power Frequency Exponent | Exponent of per unit frequency effecting reactive power | Exponent |  |  |
| Reactive Power Voltage Exponent | Exponent of per unit voltage effecting reactive power. | Exponent |  |  |
| Real Power Frequency Exponent | Exponent of per unit frequency effecting real power. | Exponent |  |  |
| Real Power Voltage Exponent | Exponent of per unit voltage effecting real power. | Exponent |  |  |
| Remove | The equipment is removed from the network. | Boolean | False |  |
| Remove Enable | The equipment can be removed from the network. | Boolean | False |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  |
| Step | Schedule is step function. | Boolean | False |  |
| Transmission Element ID | Transmission Element ID. | Integer |  |  |
| width | width | Integer |  |  |
| x co-ordinate | x co-ordinate | Integer |  |  |
| y co-ordinate | y co-ordinate | Integer |  |  |

### Linkage

The required associations for a StationsSupply are shown in the table below.

| Link Name | Description | Path |
| --- | --- | --- |
| Operated By (Operatorship) | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Own Percent (Ownership) | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

## Modeling Approach for ConformLoadGroup

All the ConformingLoads should be assigned to ConformLoadGroup. These are the Loads that follows a daily and seasonal load variation pattern. ConformLoadGroup should be created under a LoadArea/SubLoadArea under ‘Schedules/Load Area Schedules’.

### Attributes

The required attributes for a ConformLoadGroup are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Description | Description of the object or instance. | String |  |  |
| Forecast Enabled | Forecast enabled. | Boolean | False |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |

### Linkage

There are no required associations for a ConformLoadGroup.

## Modeling Approach for ConformLoadSchedule

A curve of load versus time (X-axis) showing the active power values (Y1-axis) and reactive power (Y2-axis) for each unit of the period covered. This curve represents a typical pattern of load over the time period for a given day type and season.

ConformLoadSchedule should be created under a LoadArea/SubLoadArea/ConformLoadGroup under ‘Schedules/Load Area Schedules’.

### Attributes

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String |  |
| Description | Description of the object or instance. | String |  |
| End Time | End Time. | Time | 01:00:00AM |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Start Time | Start Time. | Time | 12:00:00AM |
| Time Step | Time Step | Seconds |  |
| Value 1 Unit | Value 1 Unit. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | String | MW |
| Value 2 Unit | Value 2 Unit. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | String | MVAR |

### Linkage

There are no required links for ConformLoadSchedule.

# Modeling Curves

This section will cover modeling of Curves which include LoadBseRegulationCurve, MVArCapabilityCurve, PhaseShifterImpedanceCurve, RampRateCurves, StationSupplyWRCurve, and TransformerImpedanceCurve.

## Modeling Approach

The ERCOT CIM data dictionary defines a Curve as relationship between an independent variable (X-axis) and one or two dependent   variables (Y1-axis and Y2-axis), which can also serve as schedules. There are six types of curves which are LoadBseRegulationCurve, MVArCapabilityCurve, PhaseShifterImpedanceCurve, RampRateCurves, StationSupplyWRCurve, and TransformerImpedanceCurves. Figure below shows a RampRateCurve as modeled in IMM, with parent/child associations labeled, the screenshot should look similar for the other five types of curves with the exception of the Parent instance of the curve.

The number of CurveData associated with the MVArCapabilityCurves and RampRateCurve should not exceed 10.

All x_axisdata data points in a MVArCapabilityCurve should be unique. Only one y1_axisdata point in a MVArCapabilityCurve can be 0. Only one y2_axisdata point in a MVArCapabilityCurve can be 0.

Number of CurveScheduleData under PhaseShifterImpedanceCurve and TransformerImpedanceCurve are the same as Number of TapChanger step within PowerTransformer where the curve is asscociated to.

Figure 36 - Modeled RampRateCurves with parent/child associations labeled.

## Attributes Curves

The attributes for a Curve are shown in the Table 1 below. There is an additional four columns representing each type of GeneratingUnit by which it will specified if an attribute is used within that type. The labels of these columns are LoadBseRegulationCurve as LBRC, MVArCapabilityCurve as MVArCC, PhaseShifterImpedanceCurve as PSIC, RampRateCurves as RRC, StationSupplyWRCurve as SSWRC, and TransformerImpedanceCurve as TIC.

| Attribute | Description | Data Type | Default Value | Sample Data | LBRC | MVarCC | PSIC | RRC | SSWRC | TIC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| curveStyle | The style or shape of the curve. | EnumCurveStyle | None |  | X | X | X | X | X | X |
| xUnit | The X-axis units of measure. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | String20 | None |  | X | X | X | X | X | X |
| y1Unit | The Y1-axis units of measure. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | String20 | None |  | X | X | X | X | X | X |
| rampRateCurveId | Ramp Rate Curve ID. | String5 | None |  |  |  |  | X |  |  |
| y2Unit | The Y2-axis units of measure. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | String20 | None |  | X | X | X | X | X | X |
| coolantTemperature | The machine's coolant temperature in degrees Celsius (e.g., ambient air or stator circulating water). | Temperature | None |  |  | X |  |  |  |  |
| hydrogenPressure | The hydrogen coolant pressure. | Pressure | None |  |  | X |  |  |  |  |
| Emergency | Denote the type of ramp rate. | Boolean | None |  |  |  |  | X |  |  |

In table below, it specifies what are the curveStyle, xUnit, y1Unit, and y2Unit of each type of curve.

Curve Style and Unit Table

| Curve Name | Curve Style | X Unit | Y1 Unit | Y2 Unit |
| --- | --- | --- | --- | --- |
| LoadBseRegulationCurve | straightLineYValues | MW | KV | KV |
| MVArCapabilityCurve | straightLineYValues | MW | MVAr | MVAr |
| PhaseShifterImpedanceCurve | straightLineYValues | Degrees | Ratio | None |
| RampRateCurves | straightLineYValues | MW | MW/Min | MW/Min |
| StationSupplyWRCurve | straightLineYValues | MW | MW | MVAr |
| TransformerImpedanceCurve | straightLineYValues | Impedance | Tap | None |

## Linkage Curves

The required links for all Curves types are defined in Table below.

Linkage Table for Curves

| Link Name | Description | Path Name | LBRC | MVarCC | PSIC | RRC | SSWRC | TIC |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SynchronousMachine |  |  |  | X |  |  |  |  |
| Configuration |  |  |  |  |  | X |  |  |
| Member Of (EnergyConsumerResource) |  |  |  |  |  | X |  |  |
| Member Of (GeneratingUnit) |  |  |  |  |  | X |  |  |
| StationSupply |  |  |  |  |  |  | X |  |

# Modeling CurveData

## Modeling Approach

CureveData instances can be created both by ERCOT and Market Participants. Curve Data contains data point values for defining a curve or schedule. CurveData should be created as a child of one of allowed instances of Curve namely TransformerImpedanceCurve, StationSupplyWRCurve or PhaseShifterImpedanceCurve.

Figure 37 - CurveData

## Attributes

The following table shows all the attributes that are available for a CurveData.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance | String | None |  |
| Local Name | The localName is a human readable name of the object | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |
| X Axis Data | The data value of the X-axis variable, depending on the X-axis units |  | Double Float | 15 |
| Y1 Axis Data | The data value of the first Y-axis variable, depending on the Y-axis units |  | Double Float | 1 |
| Y2 Axis Data | The data value of the second Y-axis variable (if present), depending on the Y-axis unit. |  | Double Float | 1 |

## Linkage

There are no required links to the CurveData.

# Modeling RegularTimePoint

## Modeling Approach

Instances of RegularTimePoint can be created both by Market Participants and ERCOT. RegularTimePoint represents Time Points for a schedule where the time between the points is constant.

Figure 38 - RegularTimePoint

## Attributes

The following table shows all the attributes that are available for a RegularTimePoint.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| RT Name | Equivalent of IdentifiedObject.name. | String | None | SUN_0 |
| Sequence Number | Sequence Number. | Number | None | 1 |
| Value 1 | Value 1. | Float | None | 9.99 |
| Value 2 | Value 2. | Float | None | 0.1 |

## Linkage

There are no required links to the RegularTimePoint.

# Modeling Terminal

## Modeling Approach

Terminal’s can be created by TDSP’s. Terminal is an electrical connection point to a piece of conducting equipment. Terminals are connected at physical connection points called 'connectivity nodes'. A terminal should always be connected to conducting Equipment.

Terminals connected an Equipment can not be connected to the same connectivitynode.

Terminal associated to an equipment should have unique names.

Figure 39 - Terminal

## Attributes

The following table shows all the attributes that are available for a Terminal.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Description | Description of the object or instance. | String |  |  |
| Edge Val | edgeVal is a concatenation of all edge coordinates. | String |  |  |
| From X offset | From X offset | Number |  |  |
| From X perm | From X perm | Number |  |  |
| From Y offset | From Y offset | Number |  |  |
| From Y perm | From Y perm | Number |  |  |
| Height | height | Number |  |  |
| label height | label height | Number |  |  |
| label width | label width | Number |  |  |
| label x co-ordinate | label x co-ordinate | Number |  |  |
| label y co-ordinate | label y co-ordinate | Number |  |  |
| Local Name | The localName is a human readable name of the object. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| Near | Flag indicating whether the terminal is a near terminal of a branch. | Boolean |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| PSS/E Bus Name | Store the PSS¿E bus name that will be associated with the grouping of Connectivity Nodes in Option 2. | String |  |  |
| PSS/E Bus Number | Attribute will be used to store the PSS¿E bus number that will be associated with the grouping of Connectivity Nodes in Option 2. | Number |  |  |
| To X offset | To X offset | Number |  |  |
| To X perm | To X perm | Number |  |  |
| To Y offset | To Y offset | Number |  |  |
| To Y perm | To Y perm | Number |  |  |
| width | width | Number |  |  |
| x co-ordinate | x co-ordinate | Number |  |  |
| y co-ordinate | y co-ordinate | Number |  |  |

## Linkage

There are no required links to a Terminal.

# Modeling ConnectivityNode

## Modeling Approach

Connectivity nodes are points where terminals of conducting equipment are connected together with zero impedance. A ConnectivityNode is created under a ConnectivityNodeGroup in IMM. ConnectivityNodeGroup’s are created under a VoltageLevel.

Connectivity nodes must be associated to atleast 2 terminals.

The ConnectivityNodes in a ConnectivityNodeGroup must be in the same substation i.e. ConnectivityNodes in a given ConnectivityNodeGroup cannot span multiple Stations.

Figure 40 - ConnectivityNode

## Attributes

The following table shows all the attributes that are available for a ConnectivityNode.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Description | Description of the object or instance. | String |  |  |
| height | height | Integer |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| PSS/E Bus Name | Store the PSS¿E bus name that will be associated with the most favored Connectivity Node in Connectivity Node to Bus Processing Option 1. | String |  |  |
| PSS/E Bus Number | The PSS/E bus number associated with this point in the network. This attribute should only be used to model ficticious PSS/E busbars that are not associated with physical busbar sections. | Integer |  |  |
| Slack Bus Priority | Swing Bus Definition. | Integer |  |  |
| Transmission Element ID | Transmission Element ID. | String |  |  |
| width | width | Integer |  |  |
| x co-ordinate | x co-ordinate | Integer |  |  |
| y co-ordinate | y co-ordinate | Integer |  |  |

## Linkage

The required links for a ConnectivityNode are defined below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| EquipmentContainer | ConnectivityNodeMemberOfEquipmentContainer |  |

# Modeling ElectricalBus

## Modeling Approach

This section describes the approach for modeling an ElectricalBus. ElectricalBuses are modeled by the Market Participants.

ElectricalBus needs to be always contained in an instance of the class ConnectivityNode, which in turn is contained in an instance of the class ConnectivityNodeGroup. As per modeling approach for a HUBBus an electrical bus can become a part of the HUBBus definition by being contained under a ConnectivityNodeGroup which is associated to a HUBBus.

Every ElectricalBus should be within a LoadZone or a NOIELoadZone. All the loads connected to ElectricalBus should be in the same LoadZone or NOIELoadZone. If an ElectricalBus is connected to a DCTie Psuedo Load, then it cannot be connected to other loads.

The name of the electrical bus class is somewhat misleading.  It should be noted that instances of this class do not represent actual buswork in the field (see: BusbarSection).  Rather, the Electrical Bus class represents a settlement point.

Definition

An abstract Market construct used to denote connectivity nodes of interest.  LMP prices will be determined at these nodes.  Electrical buses are maintained by both TDSPs and ERCOT.

There are specific rules for where electrical buses must be located in the model.  An electrical bus must be associated with a connectivity node when:

- A load is attached to the node.

- A unit is attached to the node.

- Three or more switches are attached to the node and the node has a voltage reading.

- A resource node is associated with the node.

- An EPS meter is associated with the node.

Additionally, hub buses (as defined in the protocols) are required to contain at least one electrical bus.  If none of the above criteria is met for the nodes contained within a hub bus, an electrical bus must be added to the model and associated to one of the associated nodes.

Electrical buses are created and maintained by both TDSPs and ERCOT.  TDSPs will be responsible for maintaining electrical buses relating to their connectivity nodes (i.e. for loads, >3 switches, and hub buses).  ERCOT will maintain, on behalf of the resource entity, the electrical buses related to resource nodes and EPS meters.

In general, TDPSs will be responsible for electrical buses contained within their substations.  However, since EPS meters and resource nodes can be located in a TDSP’s substation, their will be certain cases where ERCOT will be responsible for electrical buses contained within a TDSP’s substation.

Example #1:  A TDSP is creating a NOMCR to reflect the future addition of a load transformer.  In addition to adding the load and associated switches, the TDSP must create an electrical bus and associate it to the same connectivity node in which the load is attached.

Example #2:  An RE informs ERCOT of a future EPS meter configuration change.  ERCOT will create a NOMCR changing the associated connectivity node of the EPS meter.  Additionally, ERCOT will move the EPS meter-related electrical bus to the new connectivity node.

Figure 41 - ElectricalBus

## Attributes

Following are the attributes for ElectricalBus.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. |  |  |
| Description | Description of the object or instance. |  |  |
| Display LMP | Display LMP? | Boolean | True |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |

## Linkages

| AssociationName | Class | Description |
| --- | --- | --- |
| ElectricalBus.ConnectivityNode | ConnectivityNode | ElectricalBusMemberOfConnectivityNode is a Required Linkage. ElectricalBus needs to be always contained in an instance of the class ConnectivityNode. |

# Modeling ConnectivityNodeGroup

## Modeling Approach

The ERCOT CIM model defines a connectivity node group as a grouping of connectivity nodes.  The Transmission operation (TO)’s planners will need to identify the PSS/E Bus name and PSS/E Bus number for each connectivity node group.  The PSS/E Bus name and PSS/E bus Number must be unique within the IMM.  These values cannot be duplicated. See figure  below as an example.

## Attributes

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Description | Description of the object or instance | String | None |  |
| Latitude | Latitude coordinates | Float | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| PSSEBusName | The bus name which is used by planners to idendify the bus Stores the PSS™E bus name that will be associated with the grouping of Connectivity Nodes in Option 2. | String12 | None |  |
| PSSEBusNumber | The bus number which is used by planners to idendify the bus Attribute will be used to store the PSS™E bus number that will be associated with the grouping of Connectivity Nodes in Option 2. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| TEID | Transmission Element ID | Integer | Auto-populated |  |

## Linkage

The required links for a Connectivity Node Group are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |
| PlanningArea | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number areas. | Network/Companies |
| Planning Zone | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number zones. | Network/Companies |

# Modeling Operatorship

## Modeling Approach

In the ERCOT CIM model an operator is assigned to each piece of equipment.  The operator of the equipment is given the right to edit the equipment and add instances under the equipment.  An operator must be created under a company and used as a link to equipment.

Figure 42 - Operatorship

## Attributes

The attributes for Operatorship are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Description | Description of the object or instance | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| Operate Percent | Operator share percentage | Float | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

## Linkage

None

# Modeling OwnershareRating

## Modeling Approach

OwnerShareRating can be utilized on Power Equipments that can be co-rated by different companies defined as an owner of the equipments. In ERCOT CIM Model, only transmission lines have the functionality to be dynamically rated and co-rated so only transmission lines will have OwnerShareRating class. OwnerShareRating is modeled under ACLineSegment or TransformerWinding as a child instance. As mentioned above, since only transmission lines have this capability in the ERCOT Model, only the lines will have an OwnerShareRating instance.

When defining an OwnerShareRating, the “Owned By (Dynamic Element)” , “Rated by (Ownership)” , “Reference (WeatherStation)” , and if possible “Reference (WeatherStationAlt)” should be properly linked according to their Path Name(see Linkage OwnerShareRating below).

Figure below shows the parent/child hierarchy of a OwnerShareRating in IMM.

Figure 43 - Hierarchy for OwnerShareRating

## Attributes

The attributes for a OwnerShareRating are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. |  |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

## Linkage

The required links for a OwnerShareRating are defined in table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Owned By (DynamicElement) | The Equipment name that is to be rated. | .other Orphans/DynamicElement/Line |
| Rated By (Ownership) | Registered Owner of the Equipment | Network/Companies/Company/Ownership |
| Reference (WeatherStation) | Weather Station the Equipment is assigned to. | .other Orphans/WeatherStation/Weather Stations |
| Reference (WeatherStationAlt) | Alternate Weather Station that the owner intends to assign to the Equipment. | .other Orphans/WeatherStation/Weather Stations |

# Classes Only Modeled By ERCOT

Modeling guidelines for the classes described beyond this point are classes that will only be allowed to be submitted by ERCOT. These classes will appear in models posted by ERCOT.

# Modeling BaseVoltage

## Modeling Approach

BaseVoltage’s are created by ERCOT. These are a collection of Base Voltages which are used to verify that the BusbarSection, BaseVoltage and other voltage attributes in the CIM are given a value existing in the collection.

Figure 44 - BaseVoltage

## Attributes

The following table shows all the attributes that are available for a BaseVoltage.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance | String | None |  |
| Local Name | The localName is a human readable name of the object | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |
| Nominal Voltage | The PowerSystemResource's base voltage |  |  | 69kv |

## Linkage

There are no required linkages to the BaseVoltage.

# Modeling Company

## Modeling Approach

Instances of this class are created by ERCOT based on the Registration Information. A Company is a legal entity that owns and operates power system resources and is a party to interchange and transmission contracts.

Figure 45 - Company

## Attributes

The following table shows all the attributes that are available for a Company.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None | RECONEX_L |
| Company Type | The type of company, e.g.: pool, municipal, private. | String | None | LSE |
| Cooperative | Cooperative boolean. | Boolean | None | False |
| Description | Description of the object or instance. | String |  |  |
| DUNS | DUNS Number | String |  | 802745240 |
| Local Name | The localName is a human readable name of the object. | String |  | RECNXL |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  | 6544 |
| Municipality | Municipality boolean. | Boolean |  | False |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |
| Primary Phone | Primary Phone number for contact. |  |  |  |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number owners. | Number |  |  |
| QSE ID | A 14 character QSE ID used for ERCOT LFC. | String |  |  |
| QSE OPA ID | A 6 character QSE OPA ID for the QSE operating in the QSE Simulator. |  |  |  |
| Secondary Phone | Secondary Phone number for contact. |  |  |  |
| Transmission Element ID | Transmission Element ID. | Number |  | 1331 |

## Linkage

There are no required linkages to the Company.

# Modeling SubgeographicalRegion

## Modeling Approach

SubgeographicalRegion’s can be created only by ERCOT. It is a subset of a geographical region of a power system network model.

Figure 46 - SubGeographicalRegion

## Attributes

The following table shows all the attributes that are available for a SubGeographical Region.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Description | Description of the object or instance. | String |  |  |
| is WeatherZone | Indicates whether a SubGeographicalRegion is a Weather Zone. | Boolean | False |  |
| Local Name | The localName is a human readable name of the object. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. |  |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number Alternate Areas and Zones. |  |  |  |

## Linkage

There are no required links to the SubgeographicalRegion.

# Modeling Geographical Region

## Modeling Approach

Geograpraphical Regions are created by ERCOT. A geographical region represents a region of a power system network model.

Figure 47 - GeographicalRegion

## Attributes

The following table shows all the attributes that are available for a Geographical Region.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance | String | None |  |
| Local Name | The localName is a human readable name of the object | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs | String | None |  |

## Linkage

There are no required links to the Geographical Region

# Modeling Market Objects

Market Objects include classes of the type:

- SettlementHUB

- AggregateHUB

- HUBBus

- PricingVector

- ResourceNode

- EPSMeter

- SettlementLoadZone

- SettlementNOIELoadZone

## Modeling Approach for SettlementHUB

This section describes the approach for modeling a SettlementHUB. SettlementHUB’s are modeled by ERCOT. A SettlementHUB is a designated Settlement Point for an ERCOT HUB.The SettlementHUB should only be contained within an instance of class sysOrphan, named “ERCOT_Settlement_Hubs”. There are four SettlementHUBs currently defined in ERCOT Model

- HB_HOUSTON

- HB_NORTH

- HB_SOUTH

- HB_WEST

Figure 48 - SettlementHub

### Attributes

The following table shows all the attributes that are available for a Settlement Hub. There are no required attributes for a SettlementHub.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance | String | None |  |
| Local Name | The localName is a human readable name of the object | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs | String | None |  |

### Linkage

The following is a required linkage.

| AssociationName | Class | Description |
| --- | --- | --- |
| Domain.MemberOfSysOrphan | SysOrphan | SettlementHUB needs to be contained only within the instance of class sysorphan. |

## Modeling Approach for AggregateHUB

This section describes the approach for modeling an AggregateHUB. AggregateHUB’s are modeled by ERCOT. There are two AggregateHubs “HB_HUBAVG” and “HB_BUSAVG”  defined in the ERCOT model based on the HUB Calculation Methods.

### HB_HUBAVG

The HB_HUBAVG for both Day-Ahead and Real-Time is the simple average of four prices from the applicable time period: the North 345 kV Hub price, the South 345 kV Hub price, the Houston 345 kV Hub price, and the West 345 kV Hub price.

Like SettlementHUB’s, this AggregateHUB should only be contained within an instance of class sysorphan  named “ERCOT_Settlement_Hubs”.

#### Attributes

Following are the attributes.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| AggregateHub.hubCalculationMethod | HubCalculationMethod should be set to ERCOT_HUBS | Enumeration | None. |

#### Linkage

Below are the required linkages to AggregateHub.

| AssociationName | Class | Description |
| --- | --- | --- |
| Domain.MemberOfSysOrphan | SysOrphan | AggregateHUB should only be contained within an instance of the class sysOrphan. |
| AggregateHub.SettlementHUB | SettlementHUB | “AggregateHub.SettlementHUB” is a Required Linkage. In this particular case all the SettlementHubs that are defined under “ERCOT_Settlement_Hubs” must be associated to “ERCOT_HUB_AVG”. |

### HB_BUSAVG

The HB_BUSAVG is the simple average of the Hub Bus prices for each hour of the Settlement Interval of the DAM in the Day-Ahead and is the simple average of the time weighted Hub Bus prices for each 15-minute Settlement Interval in Real-Time, for each Hub Bus included in this Hub.

Like SettlementHUB’s, this AggregateHUB should only be contained within an instance of class  sysorphan  named “ERCOT_Settlement_Hubs”.

#### Attributes

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| AggregateHub.hubCalculationMethod | HubCalculationMethod should be set to ALL_ERCOT_345KV_HUBBUSES | Enumeration | None. |

#### Linkage

| AssociationName | Class | Description |
| --- | --- | --- |
| Domain.MemberOfSysOrphan | SysOrphan | AggregateHUB should only be contained within an instance of the class sysOrphan. |
| AggregateHub.SettlementHUB | SettlementHUB | “AggregateHub.SettlementHUB” is a Required Linkage. In this particular case all the SettlementHubs that are defined under “ERCOT_Settlement_Hubs” must be associated to “ERCOT_345KV_HUBBUSES_AVG”. |

## Modeling Approach for HUBBus

This section describes the approach for modeling a HUBBus. HUBBus’ are modeled by ERCOT. A HUBBus by definition is an energized Electrical Bus or group of energized Electrical Buses defined as a single element in the Hub definition.

HUBBus needs to be contained within an instance of the class SettlementHUB.

Figure 49 - HubBus

#### Attributes

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| None |  |  |  |

#### Linkages

| AssociationName | Class | Description |
| --- | --- | --- |
| HUBBus.SettlementHub | SettlementHUB | “HUBBus.SettlementHub” is a Required Linkage. HUBBus needs to be contained in an instance of the class SettlementHUB |
| ConnectivityNodeGroup.HasAHUBBus | ConnectivityNode | “ConnectivityNodeGroup.HasAHUBBus” is a Required Linkage. HUBBus must be associated to a ConnectivityNodeGroup that has at least one ElectricalBus under it. If a HUBBus is associated to more than one ConnectivityNodeGroups then all the associated ConnectivityNodeGroups must belong to the same station. |

## Modeling Approach for PricingVector

This section describes the approach for modeling a PricingVector. PricingVector’s are modeled by ERCOT. PricingVector is the location where the metered price is calculated. PricingVector needs to be always contained with in an instance of the class ElectricalBus.

PricingVector’s name should be unique with in the model. PricingVector’s can not be connected to BusbarSection or EndCap.

Figure 50 - PricingVector

### Attributes

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| teid | Transmission Element ID | Integer | Autopopulated |

### Linkages

| AssociationName | Class | Description |
| --- | --- | --- |
| PricingVector.ElectricalBus | ElectricalBus | PricingVectorMemberOfElectricalBus is a Required Linkage. PricingVector needs to be always contained in an instance of the class ElectricalBus. |
| PricingVector.Terminal | Terminal | PricingVectorHasATerminal is a Required Linkage. PricingVector must be associated to a terminal where the price is calculated. |

## Modeling Approach for EPSMeter

This section describes the approach for modeling a EPSMeter. EPSMeters are modeled by ERCOT. EPSMeter is a meter polled directly by ERCOT for use in the financial settlement of the market. EPSMeter needs to be contained only with in the instance of class  sysorphan  with EPS_Meter as its name.

### Attributes

Following are the attributes for EPSMeters.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| AcceptedStatus | EPS meter location has been accepted by settlements. | Boolean | false |
| RID | Resource number for EPS meter Identifier | String | Autopopulated |
| teid | Transmission Element ID | Integer | Autopopulated |

### Linkages

| AssociationName | Class | Description |
| --- | --- | --- |
| Domain.MemberOfSysOrphan | SysOrphan | DomainMemberOfsysOrphan is a Required Linkage. This implies that an EPSMeter needs to be contained only in the instance of class sysorphan. |
| PricingVector.EPSMeter_HasA | PricingVector | PricingVector should be associated to a EPSMeter. |

## Modeling Approach for ResourceNode

This section describes the approach for modeling a ResourceNode. ResourceNode’s are modeled by ERCOT. ResourceNode is either a logical construct that creates a virtual pricing point required to model a Combined-Cycle Configuration or an Electrical Bus defined in the Network Operations Model, at which a Settlement Point Price is calculated and used in Settlement.  ResourceNode needs to be always contained within an instance of the class ElectricalBus.

ResourceNode’s should not be associated to a LoadResource or a ControllableLoadResource. ResourceNode’s that are associated to a PrivateUseNetwork, should not be connected to a Physical GeneratingUnit. Every GeneratingUnit should be associated to ResourceNode unless the GeneratingUnit is part of a DCTie or Non-Modeled-Generation or Block Load Transfer or Retired or Mothballed.

Figure 51 - ResourceNode

### Attributes

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| None |  |  |  |

### Linkages

| AssociationName | Class | Description |
| --- | --- | --- |
| ResourceNode.ElectricalBus | ElectricalBus | ResourceNode needs to be always contained in an instance of the class ElectricalBus. |

## Modeling Approach for SettlementLoadZone

The ERCOT CIM model defines a SettlementLoadZone as Settlement Point for ERCOT Load Zones. ERCOT will designate Settlement Load Zones to specific zones allowing for additional subdivision of the network to facilitate analyses and documentation.

SettlementLoadZone needs to be contained only with in the instance of class  sysorphan  with “ERCOT Settlement Zones” as its name.

The settlement load zones will be pre-populated and maintained by ERCOT in the IMM. This data may change with future settlement load zones additions.

The each Settlement load zone name and PSS/E ID must be unique within the IMM.  These values cannot be duplicated. See figure below as an example.

### Attributes

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

| AssociationName | Class | Description |
| --- | --- | --- |
| Substation.SettlementLoadZone | Substation | SettlementLoadZoneContainsSubstation is a Required Linkage. All the Substations with Loads must be associated to at least one SettlementLoadZone |

## Modeling Approach for SettlementNOIELoadZone

The ERCOT CIM model defines a SettlementNoieLoadZone as Settlement Point for ERCOT NOIE Load Zones.

ERCOT will designate Settlement Noie Load Zones to specific zones allowing for additional subdivision of the network to facilitate analyses and documentation.

The Settlement Load Zones will be pre-populated and maintained by ERCOT in the IMM. This data may change with future settlement load zones additions.

The each Settlement load zone name and PSS/E ID must be unique within the IMM.  These values cannot be duplicated. See figure below as an example.

SettlementNOIELoadZone needs to be contained only with in the instance of class  sysorphan  with “NOIE_Load_Zones” as its name.

### Attributes

| Attribute | Description | Data Type | Default Value |
| --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |

### Linkages

There are no required links.

# Modeling Generation

This section will cover modeling of GeneratingUnits, CombinedCyclePlants, ControllableLoadResources and LoadResources.

## Modeling Generating Unit

GeneratingUnit is modeled  using a ResourceController, GeneratingUnit, and SynchronousMachine. Figure 52 below shows a Generating Unit as modeled in IMM, with parent/child associations labeled. In this figure a Resource Controller named GEN_RC is modeled under a Substation. A Generating Unit, GEN is located under the Resource Controller, GEN_RC. Within the same substation, under Voltage Level, 13.8  a Synchronous Machine  is modeled.

Figure 52 – Modeled Generating Unit with parent/child associations labeled.

### Modeling Approach for Resource Controller

The ERCOT CIM  data dictionary defines a ResourceController as a plant controller. A ResourceController is modeled under a Substation.  Figure below shows a Resource Controller in IMM, with parent/child associations labeled. Every GeneratingUnit in the network model must be contained within a ResourceController. Only in case of CombinedCyclePlants, multiple GeneratingUnits may be present within the same ResourceController.

Figure 53 – Modeled Resource Controller with parent/child association.

#### Attributes

The attributes for a ResourceController are shown in the table below.

Attribute Table for Resource Controllers

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| TEID | Transmission Element ID | Integer | Auto-populated |  |
| externalJointUnit |  | Boolean | False |  |
| frequencyBias |  | Float | None |  |
| gross |  | Boolean | False |  |
| jointUnit |  | Boolean | False |  |
| physical |  | Boolean | False |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Latitude | Latiitude coordinates. | Float | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |

#### Linkage

The required links for a ResourceController are defined in defined in the table.

Linkage Table for Resource Controllers

| Link Name | Description | Path Name |
| --- | --- | --- |
| Substation | The Substation link is used in order to identify the location of the device | Network/ERCOT Substations/Weather_Zone |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

### Modeling Approach for Generating Unit

The ERCOT CIM model defines a GeneratingUnit as a single or set of SynchronousMachines for converting mechanical power into alternating-current power. A GeneratingUnit is modeled under a ResourceController. An emergency and a normal rampratecurve must be modeled under every market participating GeneratingUnit. Modeling of curves in is covered in detail in Section ___.

In the ERCOT CIM model a GeneratingUnit can be of four different types: HydroGeneratingUnit, NuclearGeneratingUnit, ThermalGeneratingUnit, and WindGeneratingUnit. Below figure below shows a GeneratingUnit in IMM, with parent/child associations labeled.

Figure 54 – Modeled Generating Unit with parent/child association.

#### Attributes

The attributes for all four types of GeneratingUnit are shown in the table below.  There is an additional four columns representing each type of GeneratingUnit by which it will specified if an attribute is used within that type. The labels of these columns are H for HydroGeneratingUnits, N for NuclearGeneratingUnits, T for ThermalGeneratingUnits and W for WindGeneratingUnits. Required attributes are listed at the top of the table in bold text.  Most of the Boolean values will have default values upon creation.  These values are listed in the table along with sample data for the field.

Attribute Table for Generating Units

| Attribute | Description | Data Type | Default Value | Sample Data | H | N | T | W |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TEID | Transmission Element ID | Integer | Auto-populated |  | X | X | X | X |
| coldStartTime | coldStartTime | Float | False |  | X | X | X | X |
| commercialOperationsDate | Commericial operations date. | Date | None |  | X | X | X | X |
| controlPulseHigh | Pulse high limit which is the largest control pulse that the unit can respond to. | Seconds | 0.5 |  | X | X | X | X |
| controlPulseLow | Pulse low limit which is the smallest control pulse that the unit can respond to. | Seconds | 0.5 |  | X | X | X | X |
| controlResponseRate | MW change for a control pulse of one second in the most responsive loading level of the unit. | PowerROCPerSec | 2 |  | X | X | X | X |
| efficiency | The efficiency of the unit in converting mechanical energy, from the prime mover, into electrical energy. | PU | 1 |  | X | X | X | X |
| freqBias | Unit Regulating Frequency Bias as MW per 0.1 Hz. | Float | None |  | X | X | X | X |
| freqDevDeadband | Frequency deviation deadband for Feed-Forward correction. | Float | None |  | X | X | X | X |
| genOperatingMode | Operating mode for secondary control, e.g.: Off, Manual, Fixed, LFC, AGC, EDC, RPN, MRN, or REG. | EnumGeneratorOperatingMode | 0 |  | X | X | X | X |
| governorMPL | Governor motor position limit. | PU | 1 |  | X | X | X | X |
| governorSCD | Governor Speed Changer Droop. | PerCent | 5 |  | X | X | X | X |
| highReasonabilityLimit | High reasonability limit. | ActivePower | None |  | X | X | X | X |
| hotintTime | Hot-to-intermediate time (Seasonal). | Float | None |  | X | X | X | X |
| hotStartTime | Hot start time. | Float | None |  | X | X | X | X |
| intColdTime | Intermediate-to-cold time (Seasonal). | Float | None |  | X | X | X | X |
| lowReasonabilityLimit | Low reasonability limit. | ActivePower | None |  | X | X | X | X |
| lowReasonabilityRampRateLimit | Low reasonability ramp rate limit. | ActivePower | None |  | X | X | X | X |
| maxDailyStarts | Maximum daily starts (seasonal parameter). | Float | None |  | X | X | X | X |
| maximumOperatingMW | This is the maximum operating MW limit the dispatcher can enter for this unit. | ActivePower | None |  | X | X | X | X |
| maxONTime | Maximum On-Line time. | Float | None |  | X | X | X | X |
| maxWeeklyEnergy | Maximum weekly energy (seasonal parameter). | Float | None |  | X | X | X | X |
| maxWeeklyStarts | Maximum weekly starts (seasonal parameter). | Float | None |  | X | X | X | X |
| minimumOperatingMW | This is the minimum operating MW limit the dispatcher can enter for this unit. | ActivePower | 0 |  | X | X | X | X |
| minOFFTime | Minimum Off-Line time. | Float | None |  | X | X | X | X |
| minONTime | Minimum On-Line time. | Float | None |  | X | X | X | X |
| modelDetail | Detail level of the generator model data. | Classification | 3 |  | X | X | X | X |
| penaltyFactor | The unit's penalty factor as calculated by the Network Sensitivity function. | PenaltyFactor | 1 |  | X | X | X | X |
| PrimaryFuelType | Primary fuel type. | EnumERCOTFuelType | None |  | X | X | X | X |
| qualificationStatus | Qualification status. | Boolean | FALSE |  | X | X | X | X |
| seasonalMaxSustainableRating | Seasonal maximum sustainable rating. | ActivePower | None |  | X | X | X | X |
| seasonalMinEmergencyRating | Seasonal minimum emergency rating. | ActivePower | None |  | X | X | X | X |
| seasonalMinSustainableRating | Seasonal minimum sustainable rating. | ActivePower | None |  | X | X | X | X |
| SecondaryFuelType | Secondary fuel type. | EnumERCOTFuelType | None |  | X | X | X | X |
| stepChange | Unit allowable step change which specifies the maximum stored energy in the boiler. | ActivePower | 5 |  | X | X | X | X |
| Alias Name | Free text name of the object or instance. | String | None |  | X | X | X | X |
| allocSpinResMW | The planned unused capacity (spinning reserve) which can be used to support emergency load. | ActivePower | None |  | X | X | X | X |
| autoCntrlMarginMW | The planned unused capacity which can be used to support automatic control overruns, in MW. | ActivePower | None |  | X | X | X | X |
| baseMW | For dispatchable units, this value represents the economic MW basepoint, for units that are not dispatchable, this value represents the fixed generation value. The value must be between the operating low and high limits. | ActivePower | None |  | X | X | X | X |
| blackStart | Determines if a unit is qualified to black start. | Bool | FALSE |  | X | X | X | X |
| blockLoadTransfer | Block load transfer. | Boolean | FALSE |  | X | X | X | X |
| controlDeadband | Unit control error deadband. When a unit's desired MW change is less than this deadband, then no control pulses will be sent to the unit. | ActivePower | None |  | X | X | X | X |
| DAM_Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  | X | X | X | X |
| DAM_Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  | X | X | X | X |
| description | Description of the object or instance. | String1000 | None |  | X | X | X | X |
| dispReserveFlag | Display Reserve Flag | Boolean | FALSE |  | X | X | X | X |
| energyMinMW | Energy Minimum MW. | HeatPerHour | None |  | X | X | X | X |
| fastStartFlag | Fast Start Flag. | Boolean | FALSE |  | X | X | X | X |
| frequencyDeadBandHz | Allowable deviation of the unit frequency. | Float | None |  | X | X | X | X |
| fuelPriority | Fuel Priority. | Priority | None |  | X | X | X | X |
| genControlMode | Select the unit control mode as Setpoint (S) or Pulse (P). | EnumGeneratorControlMode | None |  | X | X | X | X |
| genControlSource | The source of controls for a generating unit, i.e., Unavailable, Off-AGC, On-AGC, Plant Control. | EnumGeneratorControlSource | None |  | X | X | X | X |
| highControlLimit | High limit for secondary (AGC) control. | ActivePower | None |  | X | X | X | X |
| highReasonabilityRampRateLimit | High reasonability ramp rate limit. | ActivePower | None |  | X | X | X | X |
| initialMW | Default generation for use when the operating type is fixed. An entry is required because the unit may later be placed in a fixed operating type mode even though that may not be the initial selection. | ActivePower | None |  | X | X | X | X |
| intStartTime | Intermediate start time. | Float | None |  | X | X | X | X |
| Latitude | Latiitude coordinates. | Float | None |  | X | X | X | X |
| localName | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  | X | X | X | X |
| Longitude | Longitude coordinates. | Float | None |  | X | X | X | X |
| longPF | Additional information is not available. | ParticipationFactor | None |  | X | X | X | X |
| lowControlLimit | Low limit for secondary (AGC) control. | ActivePower | None |  | X | X | X | X |
| lowerRampRate | Lower Ramp Rate. | PowerROCPerMin | None |  | X | X | X | X |
| maxCapacityLimit | Maximum possible capacity. | Integer | None |  | X | X | X | X |
| maxDownRampRate | Default maximum ramp rate in down direction. | Float | None |  | X | X | X | X |
| maximumAllowableSpinngReserve | Maximum allowable spinning reserve. Spinning reserve will never be considered greater than this value regardless of the current operating point. | ActivePower | None |  | X | X | X | X |
| maximumCurrentCapacity | (MW) Default current max capacity. Operator Enterable. | Float | None |  | X | X | X | X |
| maximumCurrentCapacityRef | (MW) Reference value for Advisory ECO maximum. Entered in modeling. | Float | None |  | X | X | X | X |
| maximumEconomicMW | Maximum high economic MW limit that should not exceed the maximum operating MW limit. | ActivePower | None |  | X | X | X | X |
| maximumEconomicMWRef | Maximum economic dispatch reference value. | Float | None |  | X | X | X | X |
| maxResponseReserveLimit | Maximum responsive reserve limit MW. | Float | None |  | X | X | X | X |
| maxSpinReserveContribution | Maximum Spinning Reserve Contribution. | Float | None |  | X | X | X | X |
| maxUpRampRate | Default maximum ramp rate in up direction. | Float | None |  | X | X | X | X |
| minCapacityLimit | The Lowest continuous economical capacity limit. | Integer | None |  | X | X | X | X |
| minimumEconomicMW | Low economic MW limit that must be greater than or equal to the minimum operating MW limit. | ActivePower | 0 |  | X | X | X | X |
| minimumOffTime | Minimum time interval between unit shutdown and startup. | Seconds | None |  | X | X | X | X |
| minResponseReserveLimit | Minimum responsive reserve limit MW. | Float | None |  | X | X | X | X |
| mRID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String100 |  |  | X | X | X | X |
| normalPF | Economic participation factor based on the slope of the unit incremental cost curve at the current operating point of the unit. | ParticipationFactor | 1 |  | X | X | X | X |
| onlineThresholdDeadbandPercent | Unit online threshold deadband percentage. | Float | None |  | X | X | X | X |
| OUSPriority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  | X | X | X | X |
| pathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String500 | None |  | X | X | X | X |
| psseid | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String2 | None |  | X | X | X | X |
| raiseRampRate | Raise Ramp Rate | PowerROCPerMin | None |  | X | X | X | X |
| ratedGrossMaxMW | The unit's gross rated maximum capacity (Book Value). | ActivePower | None |  | X | X | X | X |
| ratedGrossMinMW | The gross rated minimum generation level which the unit can safely operate at while delivering power to the transmission grid. | ActivePower | None |  | X | X | X | X |
| ratedNetMaxMW | The net rated maximum capacity determined by subtracting the auxiliary power used to operate the internal plant machinery from the rated gross maximum capacity. | ActivePower | None |  | X | X | X | X |
| reliabilityMustRun | TRUE - Unit is qualified to reliability must run. | Boolean | FALSE |  | X | X | X | X |
| reserveDiscountFactor | Reserve Discount Factor. | Float | None |  | X | X | X | X |
| resourceCategory | Type of resource. | String50 | None |  | X | X | X | X |
| RUC_Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  | X | X | X | X |
| RUC_Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | TRUE |  | X | X | X | X |
| shortPF | Short Participation Factor | ParticipationFactor | None |  | X | X | X | X |
| spinningReserveMax | Max spinning reserve from this unit. Usuallly derived from response rate. Applicable only to non-peakers. | Float | None |  | X | X | X | X |
| spinReserveRamp | Spin Reserve Ramp | PowerROCPerMin | None |  | X | X | X | X |
| startupTime | Time it takes to get the unit on-line, from the time that the prime mover mechanical power is applied. | Seconds | None |  | X | X | X | X |
| synCondenserCapable | Flag indicating whether the Resource is Synchronous Condenser capable. | Boolean | FALSE |  | X | X | X | X |
| tieLinePF | Unit frequency and tie-line regulation participation factor. | ParticipationFactor | 1 |  | X | X | X | X |
| wfrmcr | wfrmcr. | Boolean | FALSE |  | X | X | X | X |
| hydroUnitWaterCost | The equivalent cost of water that drives the hydro turbine, expressed as (dollars/cubic meter). | Float | None |  | X |  |  |  |
| boilerEfficiency | (%) Boiler efficiency factor. The heat rate curve will be divided by this factor to account for a dirty boiler or any other cause for loos of efficiency of the heat cycle. | Float | None |  |  |  | X |  |
| boilerColdStartEnergy | Boiler cold start engergy (MBTU). | Float | None |  |  |  | X |  |
| oMCost | Operating and maintenance cost for the thermal unit. | CostPerHeatUnit | None |  |  |  | X |  |
| turbineColdStartEnergy | Turbine cold start energy MBTU (used by UC only). | Float | None |  |  |  | X |  |

#### Linkage

The required links for all GeneratingUnit types are defined in the table below.

Linkage Table for Generating Units

| Link Name | Description | Path Name |
| --- | --- | --- |
| DCTie | Should be populated only when the unit is part of a DC Tie. | Netowrk/DCTies |
| GenerationType |  | List_Information/GenerationType |
| PrivateAreaNetwork | Should be populated only when the unit is part of a PUN or if the unit is retired, mothballed or blockloadtransfer. | Network/PrivateAreaNetworks |
| ProtectedSwitch | ?? | ?? |
| ResourceNode | All market participating gen units should have this populated | Network/ERCOT Texas Network/ERCOT Substations/Weather_Zone/Substation/Voltage_Level/ConnectivityNodeGrou/ConnectivityNode/ElectricalBus/ |
| SubLoadArea | All units should be part of a subloadarea | Schedules/Load Area Schedules |

### Modeling Approach for Synchronous Machine

The ERCOT CIM data dictionary  defines a SynchronousMachine as an electromechanical device that operates synchronously with the network. It is a single machine operating either as a generator or synchronous condenser or pump. In the ERCOT CIM model a SynchronousMachine is modeled under a Voltage Level.   Every SynchronousMachine may have a MVArCapabilityCurve defined as a child under the SynchronousMachine. Modeling of MVar Capability is described in  Section ____ of this document. A single terminal must be modeled under a SynchronousMachine. One or many SCADA measurement/s may be modeled under the terminal. Figure 55 – Modeled Synchronous Machine with parent/child association. below shows a SynchronousMachine in IMM model hierarchy, with parent/child associations labeled.

Figure 55 – Modeled Synchronous Machine with parent/child association.

#### Attributes

The attributes for a SynchronousMachine are shown in the table below.

Attribute Table for Synchronous Machine

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| TEID | Transmission Element ID | Integer | Auto-populated |  |
| inertia | The energy stored in the rotor when operating at rated speed. This value is used in the accelerating power reference frame for operator training simulator solutions. | Inertia | 5 |  |
| xSubtrans | Subtransient reactance, also known as X''. | Reactance | None |  |
| xTrans | Transient reactance, also known as X''. | Resitance | False |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| avrEnabled |  |  |  |  |
| aVRToManualLag | Time delay, in seconds, required when switching from AVR to manual for a lagging MVAr violation. | Seconds | None |  |
| aVRToManualLead | Time delay, in seconds, required when switching from Automatic Voltage Regulation to Manual for a leading MVAr violation. | Seconds | None |  |
| baseMVAr | Default base MVAr value. This value represents the initial MVAr that can be used by any application function. | ReactivePower | None |  |
| condenserMW | Condensor MW | ActivePower | None |  |
| coolantCondition | Temperature or pressure of coolant medium. | Float | None |  |
| coolantType | Method of cooling the machine, e.g., air, hydrogen gas, water. | EnumCoolantType | None |  |
| DAM_Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  |
| DAM_Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  |
| damping | Damping torque coefficient, a proportionality constant that, when multiplied by the angular velocity of the rotor poles with respect to the magnetic field (frequency), results in the damping torque. | Damping | None |  |
| description | Description of the object or instance. | String1000 | None |  |
| Latitude | Latiitude coordinates. | Float | None |  |
| loadBasedRegulationEnabled | T = Load based voltage regulation enabled. | Boolean | False |  |
| localName | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| manualToAVR | Time delay, in seconds, required when switching from Manual to Automatic Voltage Regulation. This value is used in the accelerating power reference frame for powerflow solutions. | Seconds | None |  |
| maximumKV | Maximum kV limit for the unit. | Voltage | None |  |
| maximumMVAr | Maximum MVAr limit. This is the maximum (nameplate) limit for the unit. | ReactivePower | None |  |
| minimumKV | Minimum kV limit for the unit. | Voltage | None |  |
| minimumMVAr | Minimum MVAr limit for the unit. | ReactivePower | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| operatingMode | Current mode of operation, i.e., generator or condenser. | EnumSynchronousMachineOperatingMode | None |  |
| OUSPriority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  |
| pathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String500 | None |  |
| phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | PhaseCode | None |  |
| psseid | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String2 | None |  |
| r | Positive sequence resistance of the synchronous machine. | Resistance | None |  |
| r0 | Zero sequence resistance of the synchronous machine. | Resistance | None |  |
| ratedMVA | Nameplate MVA rating for the unit. | ApparentPower | None |  |
| Reduce | Attribute will be used to mark generators on low voltage systems that should be reduced and attached directly to the Transmission Level. | Boolean | FALSE |  |
| referencePriority | Priority of unit for reference bus selection. 0 = don t care (default) 1 = highest priority. 2 is less than 1 and so on. | Integer | None |  |
| remove | The equipment is removed from the network. | Boolean | FALSE |  |
| removeEnable | The equipment can be removed from the network. | Boolean | FALSE |  |
| RUC_Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | None |  |
| RUC_Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | None |  |
| type | Modes that this synchronous machine can operate in, i.e., as a generator, condenser, or both. | EnumSynchronousMachineType | None |  |
| varManual | Manually entered MVAR overrides capability curve. | Boolean | False |  |
| x | Positive sequence reactance of the synchronous machine. | Reactance | 0.12 |  |
| x0 | Zero sequence reactance of the synchronous machine. | Reactance | 0.05 |  |
| xDirectSubtrans | Direct-axis subtransient reactance, also known as X'd. | Reactance | None |  |
| xDirectSync | Direct-axis synchronous reactance. The quotient of a sustained value of that AC component of armature voltage that is produced by the total direct-axis flux due to direct-axis armature current and the value of the AC component of this current, the machine running at rated speed. (Xd) | Reactance | None |  |
| xDirectTrans | Direct-axis transient reactance, also known as X'd. | Reactance | None |  |
| xQuadSubtrans | Quadrature-axis subtransient reactance, also known as X'q. | Reactance | None |  |
| xQuadSync | Quadrature-axis synchronous reactance (Xq) , the ratio of the component of reactive armature voltage, due to the quadrature-axis component of armature current, to this component of current, under steady state conditions and at rated frequency. | Reactance | None |  |
| xQuadTrans | Quadrature-axis transient reactance, also known as X'q. | Reactance | None |  |

#### Linkage

The required links for a SynchronousMachine are defined in the tableError: Reference source not found below.

Linkage Table for Synchronous Machines

| Link Name | Description | Path Name |
| --- | --- | --- |
| BaseVoltage | A link to a BaseVoltage is only necessary when there is no VoltageLevel container used. If a VoltageLevel container is used the disconnector will inherit a BaseVoltage from the VoltageLevel. | Network/Base Voltage |
| MemberOf_GeneratingUnit | A synchronous machine may operate as a generator and such becomes a member of a generating unit | Network/Weather_Zone/Substation/Resource_Controller |
| AccuracyClass |  |  |
| LoadBasedRegulationCurve |  |  |
| Terminal |  |  |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |
| InitiallyUsesMVArCapabilityCurve | This link defines the default MVArCapabilityCurve for use by a SynchronousMachine. The instance of the MVArCapabilityCurve should be created by the user. | Network/Weather_Zone/Substation/Voltage_Level/Synchronous_Machine |

## Modeling Combined Cycle PLant

This section concentrates on the modeling of combined cycle plants in the ERCOT CIM model, Instances of type CombinedCyclePlant, LogicalConfiguration, Configuration, TransState and ConfigurationMember are utilized when modeling a CombinedCyclePlant. Figure 56 –Combined Cycle with parent/child associations labeled. below shows a complete CombinedCyclePlant as modeled in IMM hierarchy, with parent/child associations labeled. As can be seen in figure a CombinedCyclePlant named __SUB_CC is modeled under the ResourceController, RC. All GeneratingUnits that are part of __SUB_CC are modeled within the ResourceController RC as well. The following sections will describe the modeling of each of these classes in detail.

Figure 56 –Combined Cycle with parent/child associations labeled.

### Modeling Approach for Combined Cycle Plant

The ERCOT CIM data dictionary defines a CombinedCyclePlant as a set of combustion turbines and steam turbines where the exhaust heat from the combustion turbines is recovered to make steam for the steam turbines, resulting in greater overall plant efficiency.  Figure 57 – Modeled Combined Cycle Plant with parent/child association labeled. above shows a Combined Cycle Plant modeled in IMM, with parent/child associations labeled. Notice the presence of a Pseudoterminal under the CombinedCyclePlant, SUB_CC. This psuedoterminal does not connect to into the network topology and is solely utilized for the purpose of readily displaying SCADA/ICCP telemetry being provided for the CombinedCycplePlant. Modeling of Pseudoterminals is described in detail in that section.

Figure 57 – Modeled Combined Cycle Plant with parent/child association labeled.

#### Attributes

The attributes for a CombinedCyclePlant are shown in the table below.

Attribute Table for Combined Cycle Plants

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| TEID | Transmission Element ID | Integer | Auto-populated |  |
| commercialOperationsDate | Date commercial operations started. | Date | None |  |
| LogicalResourceNodeName | Logical resource node name. | String12 | None |  |
| blockLoadTransfer | Block load transfer. | Boolean | FALSE |  |
| combCyclePlantRating | The combined cycle plant's output rating, in MW | ActivePower | None |  |
| GstTpspiMax | GstTpspiMax | Float | None |  |
| GstTpspiMin | GstTpspiMin | Float | None |  |
| GtMax | GtMax | Float | None |  |
| GtMin | GtMin | Float | None |  |
| Latitude | Latiitude coordinates. | Float | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |
| qualificationStatus | Qualification status. | Boolean | FALSE |  |
| resourceCategory | Type of resource. | String50 | None |  |
| wfrmcr | wfrmcr. | Boolean | FALSE |  |

#### Linkage

The required links for a CombinedCyclePlant are defined in the table.

Linkage Table for Combined Cycle Plants

| Link Name | Description | Path Name |
| --- | --- | --- |
| Resource Controller | The Resource Controller link is used in order to associate a Combined Cycle Plant with its respective Resource Controller | Network/ERCOT Substations/Weather_Zone/Substation |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

### Modeling Approach for Logical Configuration

The ERCOT CIM model  utilizes an LogicalConfiguration as a  collection of all configurations  in a combined cycle plant that operate with the same number of primary combustion turbines and primary steam turbines. As mentioned earlier one or many LogicalConfiguration/s can be present within a CombinedCyclePlant. - Figure 58 below shows one such  CombinedCyclePlant  as modeled in IMM hierarchy with 2/3 logicalConfigurations, with parent/child associations labeled.

Figure 58 – Modeled Logical Configuration with parent/child association.

#### Attributes

The attributes for a LogicalConfiguration are shown in the table below.  Required attributes are listed at the top of the table in bold text.  Most of the Boolean values will have default values upon creation.  These values are listed in the table along with sample data for the field.

Attribute Table for Logical Configurations

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |

#### Linkage

The required links for a LogicalConfiguration are defined in the Error: Reference source not found below.  The path name shows where the links can be found in the model.  Definitions for all of the links can be found by clicking on the help button at the bottom of the links screen.

Linkage Table for Logical Configurations

| Link Name | Description | Path Name |
| --- | --- | --- |
| Combined Cycle Plant | The Combined Cycle Plant link is used in order to associate Logical Configuration a with its respective Combined Cycle Plant | Network/ERCOT Substations/Weather_Zone/Substation/Resource_Controller |

### Modeling Approach for Configuration

The ERCOT CIM model utilizes instances of type   Configuration to define the constituents and operational characteristics of the various combinations of combustion turbines and steam turbines a CombinedCyclePlant can operate with.  IN the ERCOT model as mentioned in the earlier sections, a configuration can be created under a LogicalConfigurtion only. Every  configuration must contain two (emergency & normal) RampRateCurves, and one/many ConfigurationMembers. Modeling of RampRateCurves is covered in detail in Section ___. Within a single CombinedCyclePlant, every configuration must be able to startup., shut down or transition to/from other configuration in the same CCP. Figure 59 below shows a Combined Cycle Plant modeled in IMM, with parent/child associations labeled.

Figure 59 -- Modeled Configuration with parent/child associations labeled.

#### Attributes

The attributes for a Configuration are shown in the below.

Attribute Table for Configurations

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| highReasonabilityLimit | High reasonability limit. | ActivePower | None |  |
| highReasonabilityRampRateLimit | High reasonability ramp rate limit. | ActivePower | None |  |
| hotintTime | Hot-to-intermediate time (Seasonal). | Float | None |  |
| hotStartTime | Hot start time. | Float | None |  |
| intColdTime | Intermediate-to-cold time (Seasonal). | Float | None |  |
| intStartTime | Intermediate start time. | Float | None |  |
| lowReasonabilityLimit | Low reasonability limit. | ActivePower | None |  |
| lowReasonabilityRampRateLimit | Low reasonability ramp rate limit. | ActivePower | None |  |
| maxDailyStarts | Maximum daily starts (seasonal parameter). | Float | None |  |
| maxONTime | Maximum On-Line time. | Float | None |  |
| maxWeeklyEnergy | Maximum weekly energy (seasonal parameter). | Float | None |  |
| maxWeeklyStarts | Maximum weekly starts (seasonal parameter). | Float | None |  |
| minOFFTime | Minimum Off-Line time. | Float | None |  |
| minONTime | Minimum On-Line time. | Float | None |  |
| primaryConfiguration | Primary configuration? | Boolean | FALSE |  |
| qualificationStatus | Qualification status. | Boolean | FALSE |  |
| seasonalMaxEmergencyRating | Seasonal maximum emergency rating. | ActivePower | None |  |
| seasonalMaxSustainableRating | Seasonal maximum sustainable rating. | ActivePower | None |  |
| seasonalMinEmergencyRating | Seasonal minimum emergency rating. | ActivePower | None |  |
| seasonalMinSustainableRating | Seasonal minimum sustainable rating. | ActivePower | None |  |
| coldStartTime | Cold Start Time | Float | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globaly unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |
| ShutdownFlag | Determines whether a Combined Cycle Plant can be shut-down in this Logical Configuration | Boolean | False |  |
| StartupFlag | Determines Whether a Combined Cycle Plant can be started in this Logical Configuration | Boolean | Flase |  |

#### Linkage

The required links for a Configuration are defined in the table below

Linkage Table for Configurations

| Link Name | Description | Path Name |
| --- | --- | --- |
| Logical Configuration | The Combined Cycle Plant link is used in order to associate Configuration a with its respective Logical Configuration | Network/ERCOT Substations/Weather_Zone/Substation/Resource_Controller/Combined_Cycle_Plant/ |

### Modeling Approach for Trans State

The ERCOT CIM data dictionary  uses  instances of type TransState to define the available transitions  between the various configurations of a  Combine Cycle Configurations. One/many TransStates may be defined for every configuration within a CombinedCyclePlant. Every transstate is defined as an uptransition when the total number of primary members in the To-configuration are greater tha or equal to the same in the from configuration. Figure 60 below shows a Trans State modeled in IMM, with parent/child associations labeled.

Figure 60 -- Modeled Trans State with parent/child associations labeled.

#### Attributes

The attributes for a TransState are shown in the table below.

Attribute Table for Trans State

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |
| upTransition | Up Transition | Boolean | False |  |

#### Linkage

The required links for a TransState are defined in the table below.

Linkage Table for Trans States

| Link Name | Description | Path Name |
| --- | --- | --- |
| ToConfig_Configuration | The next Configuration that this configuration can traverse into. | Network/ERCOT Substations/Weather_Zone/Substation/Resource_Controller/Combined_Cycle_Plant/Logic_Configyration |
| FromConfig_Configuration | The current Configuration in which this Trans State is under. |  |

### Modeling Approach for Configuration Member

The ERCOT CIM  data dictionary utilizes instances of type  ConfigurationMember to identify the ThermalGeneratingUnits that are a member of CCP Configuration instance along with their operational nature (Steam/Gas Turbine) and primary/alternate status of the associated resource. in the ERCOT CIM model, one/many configurationmembers can be defined within a configuration. Figure 61 below shows a ConfigurationMember modeled in IMM, with parent/child associations labeled.

Figure 61 -- Modeled Configuration Member with parent/child associations labeled.

#### Attributes

The attributes for a ConfigurationMember are shown in the table below.

Attribute Table for Configuration Members

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| primary | Determines if this is the primary unit in the Configuration that it falls under. | Boolean | FALSE |  |
| steam | Determines if this is a steam generating unit. | Boolean | FALSE |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |

#### Linkage

The required links for a ConfigurationMember are defined in the table below.

Linkage Table for Configuration Member

| Link Name | Description | Path Name |
| --- | --- | --- |
| ThermalGeneratingUnit | The link determines which Unit is the Configuration Member. | Network/ERCOT Substations/Weather_Zone/Substation/Resource_Controller/Thermal_Generating_unit |
| Configuration | The link determines under which Confifguration this Configuration Member falls into. | Network/ERCOT Substations/Weather_Zone/Substation/Resource_Controller/Combined_Cycle_Plant |

# Modeling Controllable Load Resources and Load resources

## Modeling Approach

The ERCOT CIM model defines a LoadResource as a load that is capable of providing Ancillary Service to the ERCOT System. A ControllableLoadResource is a LoadResource capable of controllably reducing or increasing consumption under dispatch control (similar to AGC) and that immediately responds proportionally to frequency changes (similar to generator governor action).  Figure 62 and Figure 63 below show a Controllable Load Resource and Load resource respectively in IMM, with parent/child associations labeled.

Figure 62 – Modeled Controllable Load Resource with parent/child associations labeled.

Figure 63 – Modeled Load Resource with parent/child associations labeled.

## Attributes

The attributes for both ControllableLoadResources and LoadResources are shown in the table below.

Attribute Table for Controllable Load Resources and Load Resources

| Attribute | Description | Data Type | Default Value | Sample Data | CLR | LR |
| --- | --- | --- | --- | --- | --- | --- |
| TEID | Transmission Element ID | Integer | Auto-populated |  | X | X |
| maxDeploymentTime | Maximum deployment time. | Float | None |  | X |  |
| maxWeeklyEnergy | Maximum weekly energy. | Float | None |  | X | X |
| minNoticeTime | Minimum notice time (seconds). | Float | None |  | X | X |
| rampRateSlopeDownLimit | Reasonability Limit for Down Ramp Rate. | Float | None |  | X |  |
| rampRateSlopeUpLimit | Reasonability Limit for UP Ramp Rate. | Float | None |  | X |  |
| Alias Name | Free text name of the object or instance. | String | None |  | X | X |
| blockLoadTransfer | Determines if the device is a block load transfer. | Boolean | False |  | X | X |
| commercialOperationsDate | Date commercial operations started. | Date | None |  | X | X |
| DAM_Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  | X | X |
| DAM_Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | FALSE |  | X | X |
| height |  |  |  |  | X | X |
| idth |  |  |  |  | X | X |
| label_height |  |  |  |  | X | X |
| label_width |  |  |  |  | X | X |
| label_xval |  |  |  |  | X | X |
| label_yval |  |  |  |  | X | X |
| Latitude | Latiitude coordinates. | Float | None |  | X | X |
| loadFreqBias | Regulating Frequency Bias as MW per 0.1 Hz. | Float | None |  | X | X |
| loadFreqDevDeadband | Frequency deviation deadband for Feed-Forward correction (in Hz). | Float | None |  | X | X |
| loadId | A 14 character load ID used in ERCOT LFC. | String14 | None |  | X | X |
| loadSubStationId | ID of load's substation. | String18 | None |  | X | X |
| localName | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  | X | X |
| Longitude | Longitude coordinates. | Float | None |  | X | X |
| maxDailyDeployment | Maximum daily deployments. | Float | None |  | X | X |
| maxInterruptionTime | Maximum interruption time. | Float | None |  | X | X |
| MaxPowerConsumption | Maximum power consumption for resource. | Float | None |  | X | X |
| maxWeeklyDeployment | Maximum weekly deployments. | Float | None |  | X | X |
| minInterruptionTime | Minimum interruption time. | Float | None |  | X | X |
| MinPowerConsumption | Minimum power consumption for resource. | Float | None |  | X | X |
| minRestorationTime | Minimum restoration time. | Float | None |  | X | X |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  | X | X |
| OUSPriority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Integer | None |  | X | X |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  | X | X |
| psseid | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String2 | None |  | X | X |
| qualificationStatus | Qualification status. | Boolean | False |  | X | X |
| RelayType | Type of relay. | EnumRelayType | None |  | X | X |
| resourceCategory | Type of resource. | String50 | None |  | X | X |
| RUC_Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | False |  | X | X |
| RUC_Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean | True |  | X | X |
| wfrmcr | wfrmcr. | Boolean | FALSE |  | X | X |

Table 1

## Linkage

The required links for both ControllableLoadResources and LoadResources are defined in table below.

Linkage Table for Controllable Load Resources and Load Resources

| Link Name | Description | Path Name | CLR | LR |
| --- | --- | --- | --- | --- |
| HasA_EnergyConsumer |  |  | X | X |
| HostControlArea |  |  |  | X |

# Modeling Owner Share Limits

### Modeling Approach

Owner Share Limits are used for GeneratingUnits, ControllableLoadResource or LoadResource. OwnerShareLimit (OSL) is mainly used for modeling Jointly Owned Units (Split Generation Units). A OwnerShareLimit is created for each Owner. If there are 3 owners for a unit then 3 OwnerShareLimits are created for that unit. Each OSL is associated to an Ownership record which points to each of the owners.

At least one Ownersharelimit instance should be associated with every LoadResource, ControllableLoadResource, ThermalGeneratingUnit, HydroGeneratingUnit, WindGeneratingUnit, and NuclearGeneratingUnit.

### Attributes

The attributes for an OwnerShareLimit are shown in the table below.

Attribute Table for Owner Share Limits

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| TEID | Transmission Element ID | Integer | Auto-populated |  |
| highReasonabilityLimit | highReasonabilityLimit split based on the ownership percentage. | ActivePower | None |  |
| lowReasonabilityLimit | lowReasonabilityLimit split based on the ownership percentage. | ActivePower | None |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Latitude | Latiitude coordinates. | Float | None |  |
| localName | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Longitude | Longitude coordinates. | Float | None |  |
| maxWeeklyEnergy | Maximum weekly energy (seasonal parameter) split based on the ownership percentage. | Float | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |

### Linkage

The required links for a OwnerShareLimits are defined in the table below.

Linkage Table for Owner Share Limits

| Link Name | Description | Path Name |
| --- | --- | --- |
| GeneratingUnit | Determines which Generating Unit this owner share limit represents. | Network/ERCOT Substations/Weather_Zone/Substation |
| EnergyConsumerResource | Determines which Controllable Load Resource or Load Resource this owner share limit represents | Network/ERCOT Substations/Weather_Zone/Substation/Voltage_Level/Customer_Load |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Flowgate Group

## Modeling Approach

In the ERCOT CIM model a FlowgateGroup is a grouping of flowgate elements.  Flowgate groups are modeled under the path Network/Flowgate in the model hierarchy.  Figure below shows a flowgate group in the model.

Figure 64 - FlowgateGroup

## Attributes

The attributes for a FlowgateGroup are shown in the table below

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| infB | Impact Normalization Factor for Base Case | Float | None |  |
| infC | Impact Normalization Factor for Contingency | Float | None |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Default Limit | Default Limit | DoubleFloat | None |  |
| Description | Description of the object or instance | String | None |  |
| Eligible | Eligible | Boolean |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Max Shadow Price | States the Max Shadow price | DoubleFloat | 99999 |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Rating | Flowgate Group Rating | Float | None |  |
| Thermal Limit | Thermal limit | Boolean | False |  |
| TEID | Transmission Element ID | Integer | Auto-populated |  |

## Linkage

The required links for a series FlowgateGroup are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Monitored Group |  | List_Information/Monitored Groups |

# Modeling Flowgate Element

## Modeling Approach

In the ERCOT CIM model a FlowgateElement is a market based element defining a region for energy production.  FlowgateElements are modeled under a flowgate group in the model hierarchy.  Figure below shows a flowgate element in the model.

Figure 65 - FlowgateElement

## Attributes

The attributes for a flowgate element are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Biddable | Biddable | Boolean | False |  |
| endDate | End Date | Date | None |  |
| monitored | Monitored | Boolean | False |  |
| rating | Rating | DoubleFloat | None |  |
| startDate | Start Date | Date | None |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Description | Description of the object or instance | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Max Shadow Price | States the Max Shadow price | DoubleFloat | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Positive Flow In | Determines metered direction of EPS meter | Boolean | True |  |
| Principle Element | Principle Element | Boolean | False |  |

## Linkage

None

# Modeling Ownership

## Modeling Approach

In the ERCOT CIM model an owner is assigned to each piece of equipment.  The owner of the equipment is given the right to edit the equipment, add instances under the equipment, and add other owners or operators for the equipment.  It is possible to have multiple owners for a single piece of equipment.  An owner must be created under a company and used as a link to a piece of equipment.

Figure 66 - Ownership

## Attributes

The attributes for ownership are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Own Percent | Owner share percentage | Float | None |  |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |
| Penalty Factor | Determines metered direction of EPS meter | Float | None |  |

## Linkage

None

# Modeling DC Ties

DC Tie is defined as a non-synchronous transmission interconnection between ERCOT and non-ERCOT electric power systems. A DC Tie includes a DC Tie Load -- A Load used to represent the withdrawal of power from the ERCOT System to a DC Tie and a DC Tie Resource-- A Resource used to represent the injection of power into the ERCOT System from a DC Tie.

## Modeling Approach

This section describes the approach for modeling a DCTie. This is one of the instances that is modeled by ERCOT.

A DCTie needs to be contained only in the instance of class sysorphan (ERCOT Texas Network)

An example of a DC Tie DC_E  is visible in the hierarchy view in the figure below.

The attribute DC Tie Zone name for DC tie should always match the name field

Figure 67 - DcTie

## Attributes

The attributes for a DC Tie are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| DC Tie Zone name for DC tie | DC Tie Zone name for DC tie. | String |  |
| Alias Name | Free text name of the object or instance. |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |

## Linkage

The required links for a DC Tie are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| IdentifiedObjectBelongsToModelingAuthoritySet | An IdentifiedObject belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. |  |
| TieCorridorPartOfDCTie | A Tie Corridor should be a Part of the DC tie to identify the lines that are part of the DC tie. This is a required association |  |

GeneratingUnitPartOfDCTie is a required reverse association. The Pseudo Generating Unit created for the DC Tie must be associated a  DCTie.

EnergyConsumerPartOfDCTie is a required reverse association. The Pseudo Load created for the DC Tie must be associated a  DCTie.

# Modeling Contingencies

Contingencies are modeled to study the “What-if” situations. They are defined on Lines, PowerTransformers and generating units which are likely to affect the system reliability incase of a forced outage. Network Security Analysis application is used to gauge its impact before they occur and alert the operators to any potential overloads or serious voltage violations.

The initial load of base contingencies will be responsibility of ERCOT. These contingencies make up a set of base contingencies. Changes to the list of base contingencies will be submitted by Market Participants using SAMRs. ERCOT will approve or reject the SAMRs and notify the Market Participant. The approved changes are added by ERCOT Staff to the Network Operations Model via NOMCRs. The Information Model Manager (IMM) provides basic validation of the equipment names/ID’s as the contingency is defined.

## Modeling Approach for contingency

In ERCOT CIM model, Contingency is defined as “An event threatening system reliability, consisting of one or more Contingency Elements”.

The location of contingencies in the Network model is shown in the figure below. A new Contingency can be added under the object called “Contingencies” by right mouse clicking on it and selecting ‘New’. Note that duplicate names are not allowed in the model while creating an instance. Complete the required attributes and links for the instance created. The attributes and links for Contingencies are described in the following sections.

Figure 68 - Hierarchy of Contingencies

### Attributes

The following table shows the attributes and their descriptions for Contingencies.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Device Name | Device Name. | String100 |  | Contingency name |
| Device Type | Device Type. | String100 |  | Station_A XFMR 138/69 |
| Action Type | Action Type. | String100 |  |  |
| Active Mode | Contingency active mode. | Enumeration |  | Default |
| Alias Name | Free text name of the object or instance. | String |  | _CB |
| Enable Cascading | TRUE if Cascading contigency analysis needs to performed, default is FALSE. | Boolean |  | FALSE |
| Enable Redefinition | T=enable F=disable dynamic redefinition. | Boolean | FALSE | FALSE |
| Enable SPS | T=enable F=disable SPS functions. | Boolean | FALSE | FALSE |
| End Date | Final Date this Contingency is in use. | Absolute Date Time | 1/1/2100 | 1/1/2100 |
| Generation Loss | The amount (in MW) of generation you expect the contingency to lose. | Float |  | 9999 |
| Generator Participation Factor | Short/Long. | Enumeration |  | normal |
| Load Loss | The amount (in MW) of load you expect the contingency to lose. | Float |  | 9999 |
| Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  | Station_A 138/69 transformer XFMR1 |
| Max Shadow Price | States the Max Shadow price for a Contingency. | Double Float | 99999 | 99999 |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  | 1785236 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Probability Of Occurrence | A number between 0 and 1. Contingencies with a probability less than 0.5 are considered 'low probability' contingencies. | Float |  | 1 |
| Process Type | Contingency process type. | Enumeration |  | Use Wide |
| Refractor | Set to TRUE to force a partial refactorization method when updating the matrices for the contingency solution. The default is FALSE, in this case the software will automatically determine whether a factor update or partial refactorization is more efficient for the contingency being processed, and use the most efficient method. | Boolean |  | FALSE |
| Response Time | The time frame of response in seconds for the components associated with this contingency. | Long Integer |  | 1 |
| RunFlag | Run Flag. | Boolean | TRUE | TRUE |
| Start Date | Starting Date this Contingency is expected to be in use. | Date Time | 1/1/2001 | 1/1/2001 |

Table: Attributes for contingencies

### Linkage

The following table shows the links for Contingencies.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| IdentifiedObjectBelongsToModelingAuthoritySet | An Identified Object belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. |  |

Contingency Links

## Modeling Approach for Contingency Element

The ERCOT CIM model defines a ContingencyElement as an element of a system event to be studied by contingency analysis, representing a change in status of a single piece of equipment.

Contingency element is modeled under the object type ‘Contingency’ as a child instance. Duplicate names are not allowed for contingency elements. The location of the contingency elements in the model tree is shown below.

Figure 69 - Hierarchy for Contingency Elements

### Attributes

The following table shows the attributes and their descriptions for ContingencyElement.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String |  |  |
| CB Fault | Indicates TRUE if this CB is included in post contingency and related to CB fault due to the dynamic redefinition logic. | Boolean |  | TRUE |
| Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  | 1785236 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Status | The status of contingency element, i.e. Open/Close for Switch, Removed or not for other conducting equipment. Status = TRUE for an OPEN Switch or Removed conducting equipment. | Boolean | TRUE | TRUE |

Contingency Element Attributes

### Linkage

The following table shows the links for Contingency Element.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| IdentifiedObjectBelongsToModelingAuthoritySet | An Identified Object belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. |  |
| ContingencyElementHasAEquipment | The equipment to be studied | Network/ERCOT Texas Network |

Contingency Element Links

## Modeling approach for Contingency Groups

ContingencyGroup is used for activation of groups of contingencies. Contingencies can belong to multiple groups.

The following figure shows the location of the ContingencyGroups in the network model tree. A new contingency group can be created under the object called “Contingency Groups” by right mouse clicking on it and selecting ‘New’.

Figure 70 - Hierarchy for Contingency Groups

### Attributes

The following table shows the attributes and their descriptions for Contingency Groups.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Maintain Sub Systems | This field sets whether the subsystems for the contingencies in this CTGGroup are maintained even though the group is inactive. When Maintain Subsystems set ON, and Study is set OFF, CA maintains the contingency local subsystems for base case changes. If Maintain Subsystems is set OFF and Study is set OFF, the subsystems are deleted. | Boolean | TRUE | TRUE |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  | 1785236 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Study | T=activate the contigencies in the group. | Boolean | TRUE | TRUE |

Table: Contingency Group Attributes

### Linkage

The following table shows the links for contingency groups.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| IdentifiedObjectBelongsToModelingAuthoritySet | An Identified Object belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. |  |

Contingency Group Links

## Modeling approach for Contingency Group Members

ContingencyGroupMembers are used to create many to many relationship between Contingency and Contingency Group. These are the contingencies that are studied as a group.

The following figure shows the location of the Contingency Group Member in the network model tree. A new contingency group member can be created under the object called “Contingency Groups” by right mouse clicking on it and selecting ‘New’.

Figure 71 - Hierarchy for Contingency Group Member

### Attributes

The following table shows the attributes and their descriptions for Contingency Group Members.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String |  |  |
| Local Name | The local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, Voltage Level, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  | 1785236 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |  |
| Study | T=activate the contigencies in the group. | Boolean | TRUE | TRUE |

Contingency Group Member Attributes

### Linkage

The following table shows the links for ContingencyGroups.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| ContingencyGroupMemberHasAContingency | Conteingency which is a member of this group | Contingencies_and_RASs /Contingencies |
| IdentifiedObjectBelongsToModelingAuthoritySet | An Identified Object belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. |  |

Contingency Group Member Links

# Modeling Remedial Action Schemes (RAS)

## Modeling Approach

Remedial Action Schemes encompass Remedial Action Plans (RAP), Special Protection Schemes (SPS), Remedial Action Plans Conditional (RAPC), and Mitigation Plans.  All RASs are in response to a specific Contingency.

Special Protection Schemes are automatic, relay controlled actions taken to relieve an overload condition on one or more transmission elements.  RAPs are manual corrective actions agreed upon between ERCOT and Market Participants to be taken to relieve an overload condition on one or more transmission elements. RAPCs are different from RAPs in that the corrective actions only relieve the overload under a specific system condition.  For example, if Line A is out of service AND contingency X occurs, and then the RAPC is put into affect.  If Line A is in-service AND contingency X occurs, then the RAPC is not followed.  Mitigation Plans are similar to RAPs, except that Mitigation Plans can involve shedding of load.

## Modeling Approach RAS

Changes to the base Remedial Action Schemes will be submitted by Market Participants through PTC using a SAMR. ERCOT will approve or reject the SAMRs and notify the Market Participant.  The SAMR types for RAS include RAP, SPS, RAPC, and Mitigation Plans.  The approved changes are added by ERCOT Staff to the Network Operations Model using the NOMCR process. The Information Model Manager (IMM) provides a basic level of validation.

Figure below shows the IMM hierarchy for an example RASs.  An RAS has a Stage, the state of a remedial action scheme, and a Trigger Condition, which is the set of gates that would logically trigger the RAS.

Figure 72 - RAS

Under the Stage is a Stage Trigger, or condition that is triggered within a stage.  Under the Stage Trigger is the Private Protective Actions, which are specific to a RAS trigger condition.  Under the Private Protective Actions, the individual Private Actions are housed and can include any of the actions listed in the table below.

| Protective Action | Description |
| --- | --- |
| ProtActACLineSegment | Protective action to put an ACLineSegment in-service/out-of-service. |
| ProtActAnalog | Base class for protective actions that are non-switching. |
| ProtActEnergyConsumer | RAS protective action associated with a load instance. |
| ProtActSeriesCompensator | Protective action to put a series compensator in-service/out-of-service. |
| ProtActStationReduction | Protective action to reduce station generation. |
| ProtActSwitch | Protective action to move a switch. |
| ProtActSynchronousMachine | Protective action to change output of a synchronous machine. |
| ProtActTransformerWinding | Protective action to put a TransformerWinding in-service/out-of-service. |
| ProtectiveAction | Base class for a protective action for RAS. |
| ProtectiveActionShared | Protective actions that can be shared among triggers. |

The collection of RAS logical Gates are housed under the Trigger Condition.  Each Gate can have various Pin inputs listed in the table below.

| PinType | Description |
| --- | --- |
| GateInputPin | Input pin for a special protection scheme gate. |
| PinBranchGroup | Branch flow summation input pin for RAS. |
| PinFlow | Network solution flow input pin for RAS. |
| PinGate | Input pin that maps to a Gate for RAS. |
| PinSwitch | Input pin that maps to network solution switch status for RAS. |
| PinTriggerCondition | Input pin that maps to a TriggerCondition for RAS. |
| PinVoltage | Input pin that maps to a network voltage for RAS. |

### Attributes

Class Attributes and Linkage tables have been combined wherever possible and when the classes are close in proximity to each other within the Network Model hierarchy.  The table below lists the attributes for Remedial Action Schemes.  The default values populated will be used unless changed by user. The required attributes are shown bolded.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Active | User specified active | Boolean | False |  |
| isRAP | This is a remedial action plan (RAP) | Boolean | False |  |
| isRAS | This is a remedial action scheme (RAS) | Boolean | False |  |
| AliasName | Free text name of the object or instance. | String | None | RAS_12 |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | RAS_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

The following table shows the required links for Remedial Action Schemes.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Belongs To (Contingency) | Links to specific Contingency. | Contengencies_and_RASs/ Contengencies/Cont_Name |

## Modeling Approach RAS-Stage, Stage Trigger, Private Protective Actions

A Remedial Action Schemes’ Stage, Trigger Condition, or set of gates that would logically trigger the RAS, and Private Protective Actions, which are specific to a Trigger Condition share the same attributes.  Their attributes table has been combined but their Linkage tables remain separate.

### Attributes

The table below lists the attributes for RAS-Stage, Stage Trigger, and Private Protective Actions.  The default values populated will be used unless changed by user. The required attributes are shown bolded.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| AliasName | Free text name of the object or instance. | String | None | STAGE_12 |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | STAGE_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage for RAS-Stage

The following table shows the required links for a Stage.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| BelongsTo (ModelAuthoritySet) | An Identified Object belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. |  |

### Linkage for RAS-Stage Trigger

The following table shows the required links for Stage Trigger.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| TriggeredBy | Trigger Condition | Contingencies_and_RASs/RemedialActionSchemes/RAS_1/TRIG |

### Linkage for RAS- Private Protective Actions

The following table shows the required links for Private Protective Actions.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| BelongsTo (ModelAuthoritySet) | An Identified Object belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. |  |

## Modeling Approach RAS-Protective Action ACLine Segment, Series   Compensator, Switch, and Transformer Winding

Four types of Private Protective Actions do not directly include SCADA measurements include those for ACLine Segments, Series Compensators, Switches, and Transformer Windings and share the same attributes.  Both their Attributes and Linkage tables are combined.  For a description of these classes, see section  Modeling Approach RAS above.

### Attributes

The table below lists the attributes for Protective Action ACLine Segment, Series   Compensator, Switch, and Transformer Winding.  The default values populated will be used unless changed by user. The required attributes are shown bolded.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| inService | Element put in service | Boolean | False |  |
| enableArming |  | Boolean | False |  |
| AliasName | Free text name of the object or instance. | String | None | PPA_12 |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

The following table shows the required links for Protective Action ACLine Segment, Series   Compensator, Switch, and Transformer Winding.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| References (Transmission Device), where Transmission Device is either a Switch, ACLine Segment, ect… | References device that performs Protective Action. | Network/ERCOT Texas Network/ERCOT Substations/WZ_NORTH_CENTRAL/Sub/138/SWITCH_123 |

## Modeling Approach RAS-Protective Action Analog, Energy Consumer, Station Reduction, and Synchronous Machine

Four types of Private Protective Actions could include SCADA measurements include those for Analogs, Energy Consumers, Station Reductions, and Synchronous Machines and share the same attributes.  Both their Attributes and Linkage tables are combined.  For a description of these classes, see section Modeling Approach RAS above.

### Attributes

The table below lists the attributes for Protective Action Analog, Energy Consumer, Station Reduction, and Synchronous Machine.  The default values populated will be used unless changed by user. The required attributes are shown bolded.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Action Value | If no SCADA value, then is the value to reduce by | Float | None |  |
| Action Value from SCADA | True, the action value is obtained from SCADA otherwise from actionValue attribute | Boolean | False |  |
| Is Reduced To | If true, action is a 'reduce to' otherwise it is a 'reduce by'. | Boolean | False |  |
| inService | Element put in service | Boolean | False |  |
| enableArming |  | Boolean | False |  |
| AliasName | Free text name of the object or instance. | String | None | PPA_12 |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

The following table shows the required links for Protective Action ACLine Segment, Series   Compensator, Switch, and Transformer Winding.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| References (Element), where Element is either AnalogValue,EnergyConsumer, Substation, or SynchronousMachine | References element that performs Protective Action. | Network/ERCOT Texas Network/ERCOT Substations/WZ_NORTH_CENTRAL/Sub |

## Modeling Approach RAS-Protective Action and Protective Action Shared

The Protective Action class is the base class for the Remedial Action Scheme.  Protective Action Shared can be shared among triggers.  These classes’ Attributes tables are combined.

### Attributes

The table below lists the attributes for Protective Action.  The default values populated will be used unless changed by user. The required attributes are shown bolded.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| enableArming |  | Boolean | False |  |
| AliasName | Free text name of the object or instance. | String | None | PPA_12 |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage for RAS- Protective Action

The following table shows the required links for Protective Action.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Armed By(DiscreteValue) | Discrete Value |  |

### Linkage for RAS- Protective Action Shared

The following table shows the required links for Protective Action Shared.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Armed By(DiscreteValue) | Discrete Value |  |
| Has (SharedProtectiveActions) |  |  |

## Modeling Approach RAS- Trigger Condition

A Trigger Condition is the set of gates that would logically trigger the RAS.  The Gate class is mentioned in the following section.

### Attributes

The table below lists the attributes for a Trigger Condition.  The default values populated will be used unless changed by user. The required attributes are shown bolded.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

The following table shows the required links for a Trigger Condition.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Has Resulting (Gate) | Gate | Contingencies_and_RASs/RemedialActionSchemes/RAS/TRG/GT |

## Modeling Approach RAS- Gate

The Gate class is a Special Protection Scheme gate which evaluates to Boolean.  The types of inputs available to the gate class are mentioned in the section that follows.

### Attributes

The table below lists the attributes for a Gate.  The default values populated will be used unless changed by user. The required attributes are shown bolded.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| thresholdValue | Threshold value for gate type of (GE,GT,LE,LT,NE,EQ) with single gate input | Float |  |  |
| Change Threshold | Use change limit for voltages. | Boolean | False |  |
| Emergency Threshold | Use the branch emergency limit as threshold. | Boolean | False |  |
| gatetype | Gate Type. | Enum GateType |  |  |
| level | Level of the gate. | Integer | 0 |  |
| limitPercentage | Percentage of the limit. 90% should enter 90. | Float |  |  |
| Loadshed Threshold | Use the branch loadshed limit as threshold. | Boolean | False |  |
| lowerThreshold | Use lower limit (for FlowSummation and voltage). | Boolean | False |  |
| normalThreshold | Use the branch normal limit as threshold. | Boolean | False |  |
| upperThreshold | Use upper limit (for FlowSummation and voltage). | Boolean | False |  |
| useLimit Threshold | Use the branch limit as threashold value, otherwise use Gate::thresholdValue. | Boolean | False |  |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

The following table shows the required links for a Gate.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Belong To(ModelAuthoritySet) | An IdentifiedObject belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. |  |

## Modeling Approach RAS- Gate Input Pin, Pin Branch Group, Pin Branch Group, Pin Gate, Pin Switch, Pin Trigger Condition, and Pin Voltage

Each Gate can have various Pin inputs including Gate Input Pin, Pin Branch Group, Pin Branch Group, Pin Gate, Pin Switch, Pin Trigger Condition, and Pin Voltage.  Their Attributes tables are combined, but their Linkage tables are listed separately.  Pin Flow is discussed in the following section.  For a description of these classes, see section 22.1.1 Modeling Approach RAS above.

### Attributes

The table below lists the attributes for Gate Input Pin, Pin Branch Group, Pin Branch Group, Pin Gate, Pin Switch, Pin Trigger Condition, and Pin Voltage.  The default values populated will be used unless changed by user. The required attributes are shown bolded.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Flow MVA | If true the input is a MVA. | Boolean | False |  |
| Flow MVAR | If true the input is a MVAR. | Boolean | False |  |
| Flow MW | If true, the input is a MW. | Boolean | False |  |
| Negate | If true, input is negated first and then input to the gate. Only applicable to logical gates. | Boolean | False |  |
| Use Absolute Value | Use absolute value of input (only applies to analog inputs). | Boolean | False |  |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage for RAS- Gate Input Pin

The following table shows the required links for Gate Input Pin.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| BelongsTo (ModelAuthoritySet) | An IdentifiedObject belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. | Contengencies_and_RASs/ |

### Links for RAS- Pin Branch Group

The following table shows the required links for Pin Branch Group.  The path name shows where the links can be found in the model.  Definitions for all of the links can be found by clicking on the help button at the bottom of the links screen.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| BelongsTo(BranchGroup) | Branch Group | Network/BranchGroup/N_TO_W |

### Links for RAS- Pin Gate

The following table shows the required links for Pin Gate.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Has A (Gate) | Gate | Contingencies_and_RASs/RemedialActionSchemes/_a/TC1/Gate |

### Linkage for RAS- Pin Switch

The following table shows the required links for Pin Switch.  The path name shows where the links can be found in the model.  Definitions for all of the links can be found by clicking on the help button at the bottom of the links screen.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Has A (Switch) | Switch | Network/ERCOT Texas Network/ERCOT Substations/WZ_COAST/SUB/138/DCS1 |

### Linkage for RAS- Pin Trigger Condition

The following table shows the required links for Pin Trigger Condition.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Has A (Trigger Condition) | Trigger Condition | Contingencies_and_RASs/RemedialActionSchemes/RAS/TrigCon |

### Linkage for RAS- Pin Voltage

The following table shows the required links for Pin Voltage.  The path name shows where the links can be found in the model.  Definitions for all of the links can be found by clicking on the help button at the bottom of the links screen.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Has A (ConnectivityNode) | Connectivity Node | Network/ERCOT Texas Network/ERCOT Substations/WZ_COAST/SUB/138/CN |

## Modeling Approach for RAS-Pin Flow

Each Gate can have various Pin inputs including Pin Flow.  The other Pin classes, Gate Input Pin, Pin Branch Group, Pin Branch Group, Pin Gate, Pin Switch, Pin Trigger Condition, and Pin Voltage, are discussed in the section above.  For a description of these classes, see section 22.1.1 Modeling Approach RAS above.

### Attributes

The table below lists the attributes for Pin Flow.  The default values populated will be used unless changed by user. The required attributes are shown bolded.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Either End | True if doing status input on a branch and want to check if either end is out. | Boolean | False |  |
| Flow MVA | If true the input is a MVA. | Boolean | False |  |
| Flow MVAR | If true the input is a MVAR. | Boolean | False |  |
| Flow MW | If true, the input is a MW. | Boolean | False |  |
| Input Is Flow | If true, the input is a flow, otherwise it is branch status. | Boolean | False |  |
| Into Bus | Flow into the bus is positive. | Boolean | False |  |
| Negate | If true, input is negated first and then input to the gate. Only applicable to logical gates. | Boolean | False |  |
| Out Of Bus | Flow out of the bus is positive. | Boolean | False |  |
| Use Absolute Value | Use absolute value of input (only applies to analog inputs). | Boolean | False |  |
| LocalName | The Local Name is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | PPA_ab |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Float | None | 123456 |
| PathName | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

The following table shows the required links for Pin Flow.

| Linkage Name | Description | Path Name |
| --- | --- | --- |
| Has A (Terminal) | Terminal | Network/ERCOT Texas Network/ERCOT Substations/WZ_COAST/SUB/138/Device/Terminal |

# Modeling PrivateAreaNetworks

## Modeling Approach

In the ERCOT CIM model instance of type PrivateAreaNetwork are utilized for identifying individual GeneratingUnits that are Retired, Mothballed or Non-MarketParticipating (Non-Modeled Generation), pseudo Generation/Loads that are modeled to represent BlockLoadTransfers, loads that are part of a Self Serving Entity and to identify Load and/or GeneratingUnits that form a Private Use network. This modeling distinction is defined by the enumerated attribute networkType (labeled as “Type of Private Use Network” in IMM).

Figure below shows a PrivateAreaNetwork named _PrivteAreaNetwrk_A   in the IMM hierarchical view. Also visible are the various types of Private Use Networks that can be defined.

Figure 73 - IMM hierarchical view of a PrivateAreaNetwork as modeled in the ERCOT model.

## Attributes

The attributes for PrivateAreaNetwork are shown in the table below.

| Attribute | Description | Data Type | Default | Sample Data |
| --- | --- | --- | --- | --- |
| Type of Private Use Network | Describes the Type of Private Use Network | Enumeration | None | Retired Generation |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None | XYZ |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String | None | 123 |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None | XYZ |
| Alias Name | Free text name of the object or instance. | String | None | XYZ |

## Linkage

The required links for PrivateAreaNetworks are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| Belongs To (ModelingAuthoritySet) | An IdentifiedObject belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. |  |

# Modeling Branch Group

## Modeling Approach

BranchGroup is defined as Directed Sum of terminal Flows. These groups are defined by operations for monitoring secure MW flows between different transfer areas.

This section describes the approach for modeling a BranchGroup. This is one of the instances that is modeled by ERCOT.A BranchGroup needs to be contained only in the instance of class sysorphan (BranchGroup)

An example of a BranchGroup N_TO_H is visible in the hierarchy view in the figure.

Figure 74 - BranchGroup

## Attributes

The attributes for a BranchGroup are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| Description | Description of the object or instance | String |  |
| Monitor Active Power | Monitor active power. ( True or False) | Boolean | True |
| Monitor Reactive Power | Monitor Reactive power. ( True or False) | Boolean | False |
| Alias Name | Free text name of the object or instance. | String |  |
| Eligible | Eligible Flag | Boolean | False |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Max Shadow Price | States the Max Shadow price for a BranchGroup. | Double Float | 99999 |
| Maximum Active Power | Maximum Active Power | Double Float | 0 |
| Maximum MVAR | Maximum MVAR | Double Float |  |
| Maximum MW | Maximum MW | Double Float | 0 |
| Maximum Reactive Power | Maximum Reactive Power | Double Float | 0 |
| Minimum Active Power | Minimum Active Power | Double Float | 0 |
| Minimum MVAR | Minimum MVAR | Double Float |  |
| Minimum MW | Minimum MW | Double Float | 0 |
| Minimum Reactive Power | Minimum Reactive Power | Double Float | 0 |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Transmission Element ID | Transmission Element ID | Integer |  |

## Linkage

The required links for a BranchGroup are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| IdentifiedObjectBelongsToModelingAuthoritySet | An IdentifiedObject belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. |  |
| MonitoredMemberOfMonitoredGroup | Branch Group Member of MonitoredGroup | List_Information/Monitored Groups/ISO |
| BranchGroupReferencesTerminal | BranchGroupReferencesTerminal |  |
| BranchGroupReferencesInverseTerminal | BranchGroupReferencesInverseTerminal |  |

# Modeling Branch Group Terminal

## Modeling Approach

BranchGroupTerminal is defined as Directed terminal flow to add into BranchGroup. This is one of the instances that is modeled by ERCOT.A BranchGroupTerminal needs to be contained only in the instance of class BranchGroup.

An example of a BranchGroupTerminal 2967 is visible in the hierarchy view in the below figure.

Figure 75 - BranchGroupTerminal

## Attributes

The attributes for a BranchGroupTerminal are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| Description | Description of the object or instance | String |  |
| Alias Name | Free text name of the object or instance. | String |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Positive Flow In | Positive Flow In | Boolean |  |

## Linkage

The required links for a BranchGroupTerminal are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| IdentifiedObjectBelongsToModelingAuthoritySet | An IdentifiedObject belongs to a Modeling Authority Set for purposes of defining a group of data maintained by the same Modeling Authority. |  |
| BranchGroupTerminalReferencesTerminal | BranchGroupTerminalReferencesTerminal | Network/ERCOT Texas Network/ERCOT-AC Lines/138/2967/1/2967_B |

# Modeling Endcap

## Modeling Approach

EndCap is defined as a cap to terminate the line or device

An example of an ENDCAP_8010 is visible in the hierarchy view in the figure.

Figure 76 - EndCap

## Attributes

The attributes for an EndCap are shown in the table below.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| Description | Description of the object or instance | String |  |
| Alias Name | Free text name of the object or instance. | String |  |
| DAM Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean |  |
| DAM secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured | Boolean |  |
| Latitude | Latiitude coordinates | Float |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Longitude | Longitude coordinates | Float |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| OUS Priority | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | Long Int |  |
| PSSE ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Phases | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | String |  |
| RUC Monitored | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | Boolean |  |
| RUC Secured | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured | Boolean |  |
| Remove | The equipment is removed from the network | Boolean |  |
| Remove Enable | The equipment can be removed from the network in the EMS | Boolean |  |
| Transmission Element ID | Transmission Element ID | Integer |  |

## Linkage

The Required links for an EndCap are defined in the table below.

| Link Name | Description | Path Name |
| --- | --- | --- |
| BaseVoltage | A link to a BaseVoltage is only necessary when there is no VoltageLevel container used. If a VoltageLevel container is used the disconnector will inherit a BaseVoltage from the VoltageLevel. | Network/Base Voltage |
| Operatorship | The Operatorship link is used for permission rights. The Operator of equipment has the right to edit the equipment. An operator can only be assigned by the creator or owner of the equipment. | Network/Companies |
| Ownership | The Ownership link is used for permission rights. The owner of equipment has editing and administrative rights. An owner can only be assigned by the creator of the equipment. | Network/Companies |

# Modeling Tiecorridor

## Modeling Approach

TieCorridor is defined under a SubLoadArea and is linked to a TieLine

An example of a TieCorridor 10_A is visible in the hierarchy view in the figure.

Figure 77 - TieCorridor

## Attributes

The attributes for a TieCorridor are shown in the table below.  Required attributes are listed at the top of the table in bold text.

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| Description | Description of the object or instance | String |  |
| Alias Name | Free text name of the object or instance. | String |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Maximum MW Inflow Alarm Limit | Maximum MW Inflow Alarm Limit | Float |  |
| Maximum MW Outflow Alarm Limit | Maximum MW Outflow Alarm Limit | Float |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Tie ID | Tie ID | Integer |  |
| Tie is Internal | Tie is Internal ? | Boolean |  |
| Transmission Element ID | Transmission Element ID | Integer |  |

## Linkage

The Required links for a TieCorridor are defined in the table below.  The path name shows where the links can be found in the model.  Definitions for all of the links can be found by clicking on the help button at the bottom of the links screen.

| Link Name | Description | Path Name |
| --- | --- | --- |
| TieCorridorConnectsFromHostControlArea | To side of the Tie Corridor | Network/HostControlArea/ERCOT |
| TieCorridorConnectsToSubLoadArea | SubLoad Area the Tie corridor connects to | Schedules/Load Area Schedules/ERCOT/WXZNRTHC |
| TieCorridorConnectsToaHostControlArea | From Side of the Tie Corridor | Network/HostControlArea/ERCOT |

# Modeling PermissionArea

## Modeling Approach

PermissionArea is modeled under sysOrphan “Permission Areas” as a child instance. PermissionArea is used to define valid areas of responsibility for SCADA measurements. The Permission Areas currently defined and used in the ERCOT CIM model are, AL, COMMS, EAST, ECAR, ERCOT, GEN, NORT, SOUT, and SYSTEM.

Figure below shows the parent/child hierarchy of a PermissionArea in IMM.

Figure 78 - Hierarchy for PermissionArea

## Attributes

The attributes for a PermissionArea are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. |  |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

## Linkage

None.

# Modeling Approach for DayType

## Modeling Approach

Group of similar days, e.g., Mon/Tue/Wed, Thu/Fri, Sat/Sun, Holiday1, Holiday2.

Figure 79 - DayType

## Attributes

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String |  |
| Description | Description of the object or instance. | String |  |
| End Time | Time daytype ends | Time |  |
| Fri Flag | Indicates whether Friday is included in this Day Type. | Boolean |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Mon Flag | Indicates whether Monday is included in this Day Type. | Boolean |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Sat Flag | Indicates whether Saturday is included in this Day Type. | Boolean |  |
| Start Time | Time daytype starts |  |  |
| Sun Flag | Indicates whether Sunday is included in this Day Type. | Boolean |  |
| Thurs Flag | Indicates whether Thursday is included in this Day Type. | Boolean |  |
| Tues Flag | Indicates whether Tuesday is included in this Day Type. | Boolean |  |
| Wed Flag | Indicates whether Wednesday is included in this Day Type. | Boolean |  |

## Linkage

There are no required links.

# Modeling Approach for LoadType

## Modeling Approach

Container for shared attributes for loads of the same type.

Figure 80 - LoadType

## Attributes

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. |  |  |
| Description | Description of the object or instance. |  |  |
| exp P Frequency | Load watts are proportional to (V**WVEXP)*(F**WFEXP). |  |  |
| exp P Voltage | Exp P Voltage. |  |  |
| exp Q Frequency | Load vars are proportional to (V**RVEXP)*(F**RFEXP). |  |  |
| exp Q Voltage | Exp Q Voltage. |  |  |
| Initial Time | The initial time on the cooling characteristic in seconds. |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. |  |  |
| Maximum Scaling | The maximum value that the load could be scaled by upon its reconection. |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |

## Linkage

There are no required links.

# Modeling Approach for SubLoadArea

The class is the second level in a hierarchical structure for grouping of loads for the purpose of load flow load scaling.

Figure 81 - SubLoadArea

## Attributes

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. |  |  |
| Description | Description of the object or instance. |  |  |
| Forecast Enabled | Forecast enabled. |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |

## Linkage

There are no required links.

# Modeling Approach for Season

## Modeling Approach

A specified time period of the year, e.g., Spring, Summer, Fall, Winter.  Season Types may be defined with starting and ending month and day.  All defined season types must make up one year.

Figure 82 - Season

## Attributes

| Attribute | Description | Data Type | Default |
| --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String |  |
| Description | Description of the object or instance. | String |  |
| End Date | Date season ends. | Time |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | String |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String |  |
| Season Name | Name of the Season. | String | Winter |
| Start Date | Date season starts. | Time |  |

## Linkage

There are no required links.

# Modeling PseudoTerminal

## Modeling Approach

The pseudo terminal is defined to provide UI support. The psuedoterminal does not connect to into the network topology and is solely utilized for the purpose of readily displaying SCADA/ICCP telemetry being provided for the equipment.

PsuedoTerminal shoud not be Associated to a connectivityNode.

Psuedoterminal should not be associated to a RegulatingconductingEquipment.

Figure 83 - PseudoTerminal

## Attributes

The attributes for a PseudoTerminal are shown in the table below.

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. |  |  |  |
| Description | Description of the object or instance. |  |  |  |
| Edge Val | edgeVal is a concatenation of all edge coordinates. |  |  |  |
| From X offset | From X offset |  |  |  |
| From X perm | From X perm |  |  |  |
| From Y offset | From Y offset |  |  |  |
| From Y perm | From Y perm |  |  |  |
| height | height |  |  |  |
| label height | label height |  |  |  |
| label width | label width |  |  |  |
| label x co-ordinate | label x co-ordinate |  |  |  |
| label y co-ordinate | label y co-ordinate |  |  |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. |  |  |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. |  |  |  |
| Near | Flag indicating whether the terminal is a near terminal of a branch. |  |  |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. |  |  |  |
| PSS/E Bus Name | Store the PSS¿E bus name that will be associated with the grouping of Connectivity Nodes in Option 2. |  |  |  |
| PSS/E Bus Number | Attribute will be used to store the PSS¿E bus number that will be associated with the grouping of Connectivity Nodes in Option 2. |  |  |  |
| To X offset | To X offset |  |  |  |
| To X perm | To X perm |  |  |  |
| To Y offset | To Y offset |  |  |  |
| To Y perm | To Y perm |  |  |  |
| width | width |  |  |  |
| x co-ordinate | x co-ordinate |  |  |  |
| y co-ordinate | y co-ordinate |  |  |  |

## Linkage

There are no required links for a PseudoTerminal.

# Modeling Planning Objects

## Modeling Approach for Planning Area

The ERCOT CIM model defines a planning area as planning areas.

Planning areas are commonly used to designate sections of the network which represent control areas between which there are scheduled flows.  Planning areas will be pre-populated and maintained by ERCOT in the IMM. This data may change with future planning area additions.

The each planning area name and PSS/E ID must be unique within the IMM.  These values cannot be duplicated. See figure below as an example.

Figure 84 - PlanningArea

### Attributes

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

There are no required links for Planning Area.

## Modeling Approach for Planning Zones

The ERCOT CIM model defines planning zones as planning zones.

Planners designate buses to specific zones allowing for additional subdivision of the network to facilitate analyses and documentation.

The Planning zones will be pre-populated and maintained by ERCOT in the IMM. This data may change with future planning zones additions.

Each planning zone name and PSS/E ID must be unique within the IMM.  These values cannot be duplicated. See figure below as an example.

Figure 85 - PlanningZone

### Attributes

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

There are no required links for PlanningZones.

## Modeling Approach for SubcontrolArea

The ERCOT CIM model defines a SubcontrolArea as an area defined for the purpose of tracking interchange with surrounding areas via tie points; may or may not serve as a control area. Right now, the Load area schedules are the same field as subcontrol area. The subcontrol area is a future area for data.

The subcontrol areas will be pre-populated and maintained by ERCOT in the IMM. This data may change with future subcontrol areas additions.

The each Subcontrol area name and PSS/E ID must be unique within the IMM.  These values cannot be duplicated. See figure below as an example.

Figure 86 - SubcontrolArea

### Attributes

| Attribute | Description | Data Type | Default Value | Sample Data |
| --- | --- | --- | --- | --- |
| Alias Name | Free text name of the object or instance. | String | None |  |
| Local Name | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | String | None |  |
| Model Resource ID | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | Integer | Auto-populated |  |
| PSS®E ID | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers | String | None |  |
| Path Name | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | String | None |  |

### Linkage

There are no required links to SubcontrolArea.

# Appendix A - Validation Rules – Required Fields

This appendix lists all of the validation rules for attributes that must be defined for a specific class. It also lists any validation for attributes that must be within a specific value range.

| ClassName | Attributes | Required | Range |
| --- | --- | --- | --- |
| AccumulatorLimit | value | x | >=0 |
| AccumulatorValue | cstatus | x |  |
| ACLineSegment | r | x | >= -500 and <= 500 |
| ACLineSegment | x | x | >= -1000 and <= 1000 |
| ACLineSegment | teid | x | >=0 and <= 999999999 |
| Address | City | x |  |
| Address | PostalCode | x |  |
| Address | State | x |  |
| Address | Street1 | x |  |
| AggregateHub | hubCalculationMethod | x |  |
| AirCompressor | teid | x | >=0 and <= 999999999 |
| AlternateLimit | highLimit | x |  |
| AlternateLimit | lowLimit | x |  |
| Analog | teid | x | >=0 and <= 999999999 |
| AnalogValue | cstatus | x |  |
| AreaReserveSpec | lowerRegMarginReqt | x | >= 0 |
| AreaReserveSpec | opReserveReqt | x | >= 0 |
| AreaReserveSpec | primaryReserveReqt | x | >= 0 |
| AreaReserveSpec | raiseRegMarginReqt | x | >= 0 |
| AreaReserveSpec | spinningReserveReqt | x | >= 0 |
| BasePower | basePower | x |  |
| BaseVoltage | nominalVoltage | x | >=0 and <= 1100 |
| BasicIntervalSchedule | startTime | x |  |
| BasicIntervalSchedule | value1Unit | x |  |
| BasicIntervalSchedule | value2Unit | x |  |
| Bay | teid | x | >=0 and <= 999999999 |
| BranchGroup | maximumActivePower | x |  |
| BranchGroup | maximumReactivePower | x |  |
| BranchGroup | minimumReactivePower | x |  |
| BranchGroup | monitorActivePower | x |  |
| BranchGroup | teid | x | >=0 and <= 999999999 |
| BranchGroupTerminal | positiveFlowIn | x |  |
| Breaker | InTransitTime | x |  |
| Breaker | teid | x | >=0 and <= 999999999 |
| BusbarSection | teid | x | >=0 and <= 999999999 |
| BWRSteamSupply | teid | x | >=0 and <= 999999999 |
| CAESPlant | teid | x | >=0 and <= 999999999 |
| CogenerationPlant | teid | x | >=0 and <= 999999999 |
| CombinedCyclePlant | LogicalResourceNodeName | x |  |
| CombinedCyclePlant | teid | x | >=0 and <= 999999999 |
| CombinedCyclePlant | aliasName | x |  |
| CombustionTurbine | teid | x | >=0 and <= 999999999 |
| CommunicationLink | teid | x | >=0 and <= 999999999 |
| Company | companyType | x |  |
| Company | DUNS | x |  |
| Company | PrimaryPhone | x |  |
| Company | teid | x | >=0 and <= 999999999 |
| Company | aliasName | x |  |
| CompositeSwitch | teid | x | >=0 and <= 999999999 |
| ConductingEquipment | teid | x | >=0 and <= 999999999 |
| Conductor | teid | x | >=0 and <= 999999999 |
| Configuration | highReasonabilityLimit | x | >= lowReasonabilityLimit |
| Configuration | highReasonabilityRamp RateLimit | x | >= lowReasonabilityRampRateLimit |
| Configuration | hotintTime | x |  |
| Configuration | hotStartTime | x | <= intStartTime |
| Configuration | intColdTime | x |  |
| Configuration | intStartTime | x | <= coldStartTime |
| Configuration | lowReasonabilityLimit | x | >= 0 |
| Configuration | lowReasonabilityRampRateLimit | x |  |
| Configuration | maxDailyStarts | x |  |
| Configuration | maxONTime | x |  |
| Configuration | maxWeeklyEnergy | x |  |
| Configuration | maxWeeklyStarts | x | >= maxDailyStarts |
| Configuration | minOFFTime | x |  |
| Configuration | minONTime | x | <= maxONTime |
| Configuration | primaryConfiguration | x |  |
| Configuration | qualificationStatus | x |  |
| Configuration | seasonalMaxEmergencyRating | x | >= seasonalMinEmergencyRating |
| Configuration | seasonalMaxSustainableRating | x | >= seasonalMinSustainableRating |
| Configuration | seasonalMinEmergencyRating | x |  |
| Configuration | seasonalMinSustainableRating | x |  |
| ConformLoad | conformingLoadFlag | x |  |
| ConformLoad | pfixedPct | x |  |
| ConformLoad | pnomPct | x |  |
| ConformLoad | powerFactor | x |  |
| ConformLoad | qfixed | x |  |
| ConformLoad | qnomPct | x |  |
| ConformLoad | teid | x | >=0 and <= 999999999 |
| ConformLoadSchedule | startTime | x |  |
| ConformLoadSchedule | value1Unit | x |  |
| ConformLoadSchedule | value2Unit | x |  |
| ConformLoadSchedule | aliasName | x |  |
| ConnectivityNode | teid | x | >=0 and <= 999999999 |
| ConnectivityNodeGroup | PSSEBusNumber | x | can not be between 9400-9999 and 94000-99999 |
| ConnectivityNodeGroup | teid | x | >=0 and <= 999999999 |
| Connector | teid | x | >=0 and <= 999999999 |
| Contact | EmailAddress | x |  |
| Contact | FirstName | x |  |
| Contact | LastName | x |  |
| Contact | PrimaryPhone | x |  |
| Contact | City | x |  |
| Contact | PostalCode | x |  |
| Contact | State | x |  |
| Contact | Street1 | x |  |
| Contingency | DeviceName | x |  |
| Contingency | DeviceType | x |  |
| ControlHouseEquipment | teid | x | >=0 and <= 999999999 |
| ControllableLoadResource | maxDeploymentTime | x |  |
| ControllableLoadResource | maxWeeklyEnergy | x |  |
| ControllableLoadResource | minNoticeTime | x |  |
| ControllableLoadResource | rampRateSlopeDownLimit | x |  |
| ControllableLoadResource | rampRateSlopeUpLimit | x |  |
| ControllableLoadResource | maxDailyDeployment | x |  |
| ControllableLoadResource | maxInterruptionTime | x | >= minInterruptionTime |
| ControllableLoadResource | maxWeeklyDeployment | x | >= maxDailyDeployment |
| ControllableLoadResource | minInterruptionTime | x |  |
| ControllableLoadResource | minRestorationTime | x |  |
| ControllableLoadResource | teid | x | >=0 and <= 999999999 |
| ControllableLoadResource | aliasName | x |  |
| CurrentRelay | teid | x | >=0 and <= 999999999 |
| Curve | curveStyle | x |  |
| Curve | xUnit | x |  |
| Curve | y1Unit | x |  |
| Curve | y2Unit | x |  |
| CurveData | xvalue | x |  |
| CurveData | y1value | x |  |
| CurveData | y2value | x |  |
| CustomerLoad | conformingLoadFlag | x |  |
| CustomerLoad | pfixedPct | x |  |
| CustomerLoad | pnomPct | x |  |
| CustomerLoad | qfixed | x |  |
| CustomerLoad | qnomPct | x |  |
| CustomerLoad | teid | x | >=0 and <= 999999999 |
| DayType | FriFlag | x |  |
| DayType | MonFlag | x |  |
| DayType | SatFlag | x |  |
| DayType | SunFlag | x |  |
| DayType | ThursFlag | x |  |
| DayType | TuesFlag | x |  |
| DayType | WedFlag | x |  |
| DCLineSegment | r | x |  |
| DCLineSegment | teid | x | >=0 and <= 999999999 |
| DCTie | DCTieLZName | x |  |
| Disconnector | initiallyOpen | x |  |
| Disconnector | normalOpen | x |  |
| Disconnector | teid | x | >=0 and <= 999999999 |
| Discrete | teid | x | >=0 and <= 999999999 |
| DiscreteValue | cstatus | x |  |
| DrumBoiler | teid | x | >=0 and <= 999999999 |
| EndCap | teid | x | >=0 and <= 999999999 |
| EnergyConsumer | conformingLoadFlag | x |  |
| EnergyConsumer | pfixedPct | x |  |
| EnergyConsumer | pnomPct | x |  |
| EnergyConsumer | qfixed | x |  |
| EnergyConsumer | qnomPct | x |  |
| EnergyConsumer | teid | x | >=0 and <= 999999999 |
| EnergyConsumer AltConnection | percentTransfer | x |  |
| EnergyConsumerResource | maxDailyDeployment | x |  |
| EnergyConsumerResource | maxInterruptionTime | x | <= minInterruptionTime |
| EnergyConsumerResource | maxWeeklyDeployment | x | >= maxDailyDeployment |
| EnergyConsumerResource | minInterruptionTime | x |  |
| EnergyConsumerResource | minRestorationTime | x |  |
| EnergyConsumerResource | teid | x | >=0 and <= 999999999 |
| EPSMeter | AcceptedStatus | x |  |
| EPSMeter | RID | x |  |
| EPSMeter | teid | x | >=0 and <= 999999999 |
| Equipment | teid | x | >=0 and <= 999999999 |
| EquipmentContainer | teid | x | >=0 and <= 999999999 |
| EquivalentSource | teid | x | >=0 and <= 999999999 |
| ERCOTVersion | ContactEmail | x |  |
| ERCOTVersion | ContactPhoneNumber | x |  |
| ERCOTVersion | date | x |  |
| ERCOTVersion | ModelAdmin | x |  |
| ERCOTVersion | version | x |  |
| Feeder | teid | x | >=0 and <= 999999999 |
| FlowgateElement | biddable | x |  |
| FlowgateElement | endDate | x |  |
| FlowgateElement | monitored | x |  |
| FlowgateElement | rating | x |  |
| FlowgateElement | startDate | x |  |
| FlowgateGroup | infB | x |  |
| FlowgateGroup | infC | x |  |
| FlowgateGroup | teid | x | >=0 and <= 999999999 |
| FossilSteamSupply | teid | x | >=0 and <= 999999999 |
| FrequencyConverter | teid | x | >=0 and <= 999999999 |
| FrequencyRelay | teid | x | >=0 and <= 999999999 |
| Fuse | initiallyOpen | x |  |
| Fuse | normalOpen | x |  |
| Fuse | teid | x | >=0 and <= 999999999 |
| Gate | thresholdValue | x |  |
| GeneratingUnit | coldStartTime | x |  |
| GeneratingUnit | controlPulseHigh | x |  |
| GeneratingUnit | controlPulseLow | x |  |
| GeneratingUnit | controlResponseRate | x |  |
| GeneratingUnit | efficiency | x | >= 0.001 and <= 2 |
| GeneratingUnit | freqBias | x |  |
| GeneratingUnit | freqDevDeadband | x |  |
| GeneratingUnit | governorMPL | x |  |
| GeneratingUnit | governorSCD | x |  |
| GeneratingUnit | highReasonabilityLimit | x | >= lowReasonabilityLimit |
| GeneratingUnit | highReasonabilityRamp RateLimit | x | >= lowReasonabilityRampRateLimit |
| GeneratingUnit | hotintTime | x |  |
| GeneratingUnit | hotStartTime | x | <= intStartTime |
| GeneratingUnit | intColdTime | x |  |
| GeneratingUnit | intStartTime | x | <= coldStartTime |
| GeneratingUnit | lowReasonabilityLimit | x | >= 0 |
| GeneratingUnit | lowReasonabilityRamp RateLimit | x |  |
| GeneratingUnit | maxDailyStarts | x |  |
| GeneratingUnit | maximumOperatingMW | x | equal to highReasonabilityLimit |
| GeneratingUnit | maxONTime | x |  |
| GeneratingUnit | maxWeeklyEnergy | x |  |
| GeneratingUnit | maxWeeklyStarts | x | >= maxDailyStarts |
| GeneratingUnit | minimumOperatingMW | x | equal to lowReasonabilityLimit |
| GeneratingUnit | minOFFTime | x |  |
| GeneratingUnit | minONTime | x | <= maxONTime |
| GeneratingUnit | modelDetail | x |  |
| GeneratingUnit | penaltyFactor | x |  |
| GeneratingUnit | seasonalMaxSustainableRating | x | >= seasonalMinSustainableRating |
| GeneratingUnit | seasonalMinEmergencyRating | x |  |
| GeneratingUnit | seasonalMinSustainableRating | x |  |
| GeneratingUnit | stepChange | x |  |
| GeneratingUnit | teid | x | >=0 and <= 999999999 |
| GenericEquipment | teid | x | >=0 and <= 999999999 |
| GenericUnderfrequency Relay | relayDelayTime | x |  |
| GenericUnderfrequency Relay | teid | x | >=0 and <= 999999999 |
| Ground | teid | x | >=0 and <= 999999999 |
| GroundDisconnector | initiallyOpen | x |  |
| GroundDisconnector | normalOpen | x |  |
| GroundDisconnector | teid | x | >=0 and <= 999999999 |
| HeatExchanger | teid | x | >=0 and <= 999999999 |
| HeatRecoveryBoiler | teid | x | >=0 and <= 999999999 |
| HostControlArea | areaControlMode | x |  |
| HostControlArea | forGeneration | x |  |
| HostControlArea | forNetwork | x |  |
| HostControlArea | teid | x | >=0 and <= 999999999 |
| HydroGeneratingUnit | coldStartTime | x |  |
| HydroGeneratingUnit | controlPulseHigh | x |  |
| HydroGeneratingUnit | controlPulseLow | x |  |
| HydroGeneratingUnit | controlResponseRate | x |  |
| HydroGeneratingUnit | efficiency | x | >= 0.001 and <= 1.2 |
| HydroGeneratingUnit | freqBias | x |  |
| HydroGeneratingUnit | freqDevDeadband | x |  |
| HydroGeneratingUnit | governorMPL | x |  |
| HydroGeneratingUnit | governorSCD | x |  |
| HydroGeneratingUnit | highReasonabilityLimit | x | >= lowReasonabilityLimit |
| HydroGeneratingUnit | highReasonabilityRampRateLimit | x | >= lowReasonabilityRampRateLimit |
| HydroGeneratingUnit | hotintTime | x |  |
| HydroGeneratingUnit | hotStartTime | x | <= intStartTime |
| HydroGeneratingUnit | intColdTime | x |  |
| HydroGeneratingUnit | intStartTime | x | <= coldStartTime |
| HydroGeneratingUnit | lowReasonabilityLimit | x | >= 0 |
| HydroGeneratingUnit | lowReasonabilityRampRateLimit | x |  |
| HydroGeneratingUnit | maxDailyStarts | x |  |
| HydroGeneratingUnit | maximumOperatingMW | x | equal to highReasonabilityLimit |
| HydroGeneratingUnit | maxONTime | x |  |
| HydroGeneratingUnit | maxWeeklyEnergy | x |  |
| HydroGeneratingUnit | maxWeeklyStarts | x | >= maxDailyStarts |
| HydroGeneratingUnit | minimumOperatingMW | x | >=0 and <= 999 and equal to lowReasonabilityLimit |
| HydroGeneratingUnit | minOFFTime | x |  |
| HydroGeneratingUnit | minONTime | x | <= maxONTime |
| HydroGeneratingUnit | modelDetail | x |  |
| HydroGeneratingUnit | penaltyFactor | x |  |
| HydroGeneratingUnit | seasonalMaxSustainableRating | x | >= seasonalMinSustainableRating |
| HydroGeneratingUnit | seasonalMinEmergencyRating | x |  |
| HydroGeneratingUnit | seasonalMinSustainableRating | x |  |
| HydroGeneratingUnit | stepChange | x |  |
| HydroGeneratingUnit | teid | x | >=0 and <= 999999999 |
| HydroPowerPlant | teid | x | >=0 and <= 999999999 |
| HydroPump | teid | x | >=0 and <= 999999999 |
| HydroTurbine | teid | x | >=0 and <= 999999999 |
| InductionMotorLoad | conformingLoadFlag | x |  |
| InductionMotorLoad | pfixedPct | x |  |
| InductionMotorLoad | pnomPct | x |  |
| InductionMotorLoad | qfixed | x |  |
| InductionMotorLoad | qnomPct | x |  |
| InductionMotorLoad | teid | x | >=0 and <= 999999999 |
| IrregularIntervalSchedule | startTime | x |  |
| IrregularIntervalSchedule | value1Unit | x |  |
| IrregularIntervalSchedule | value2Unit | x |  |
| IrregularTimePoint | time | x |  |
| IrregularTimePoint | value1 | x |  |
| IrregularTimePoint | value2 | x |  |
| Jumper | initiallyOpen | x |  |
| Jumper | normalOpen | x |  |
| Jumper | teid | x | >=0 and <= 999999999 |
| Junction | teid | x | >=0 and <= 999999999 |
| LevelVsVolumeCurve | curveStyle | x |  |
| LevelVsVolumeCurve | xUnit | x |  |
| LevelVsVolumeCurve | y1Unit | x |  |
| LevelVsVolumeCurve | y2Unit | x |  |
| Line | teid | x | >=0 and <= 999999999 |
| Load | conformingLoadFlag | x |  |
| Load | pfixedPct | x |  |
| Load | pnomPct | x |  |
| Load | qfixedPct | x |  |
| Load | qnomPct | x |  |
| Load | teid | x | >=0 and <= 999999999 |
| LoadBasedRegulation Curve | curveStyle | x |  |
| LoadBasedRegulation Curve | xUnit | x |  |
| LoadBasedRegulation Curve | y1Unit | x |  |
| LoadBasedRegulation Curve | y2Unit | x |  |
| LoadBasedRegulation Curve | aliasName | x |  |
| LoadBreakSwitch | initiallyOpen | x |  |
| LoadBreakSwitch | normalOpen | x |  |
| LoadBreakSwitch | teid | x | >=0 and <= 999999999 |
| LoadDemandModel | startTime | x |  |
| LoadDemandModel | value1Unit | x |  |
| LoadDemandModel | value2Unit | x |  |
| LoadResource | maxWeeklyEnergy | x |  |
| LoadResource | minNoticeTime | x |  |
| LoadResource | maxDailyDeployment | x |  |
| LoadResource | maxInterruptionTime | x | >= minInterruptionTime |
| LoadResource | maxWeeklyDeployment | x | >= maxDailyDeployment |
| LoadResource | minInterruptionTime | x |  |
| LoadResource | teid | x | >=0 and <= 999999999 |
| LoadResource | aliasName | x |  |
| MeasurementArgument | referenceName | x | Required if ReferenceFlag = True |
| MeasurementValue | cstatus | x |  |
| MeasurementValueQuality | hasCOV | x |  |
| MeasurementValueQuality | hasQuality | x |  |
| MeasurementValueQuality | hasTimestamp | x |  |
| MeasurementValueSource | biverAus | x |  |
| MeasurementValueSource | biverTay | x |  |
| MeasurementValueSource | BufferTime | x |  |
| MeasurementValueSource | defaultDataSetPeriod | x |  |
| MeasurementValueSource | GraceTime | x |  |
| MeasurementValueSource | iccpDomainAus | x |  |
| MeasurementValueSource | iccpDomainTay | x |  |
| MeasurementValueSource | IntegrityPeriod | x |  |
| MeasurementValueSource | lnkapp | x |  |
| MeasurementValueSource | MaxDisPerDataset | x |  |
| MeasurementValueSource | maxScanRate | x |  |
| MeasurementValueSource | protocolVersion | x |  |
| MeasurementValueSource | remoteIdAus | x |  |
| MeasurementValueSource | remoteIdTay | x |  |
| MeasurementValueSource | savecaseType | x |  |
| MeasurementValueSource | trsfr | x |  |
| ModelVersion | date | x |  |
| ModelVersion | information | x |  |
| ModelVersion | version | x |  |
| MVArCapabilityCurve | curveStyle | x |  |
| MVArCapabilityCurve | xUnit | x |  |
| MVArCapabilityCurve | y1Unit | x |  |
| MVArCapabilityCurve | y2Unit | x |  |
| MVArCapabilityCurve | aliasName | x |  |
| NonConformLoad | conformingLoadFlag | x |  |
| NonConformLoad | pfixedPct | x |  |
| NonConformLoad | pnomPct | x |  |
| NonConformLoad | qfixedPct | x |  |
| NonConformLoad | qnomPct | x |  |
| NonConformLoad | teid | x | >=0 and <= 999999999 |
| NuclearGeneratingUnit | coldStartTime | x |  |
| NuclearGeneratingUnit | controlPulseHigh | x |  |
| NuclearGeneratingUnit | controlPulseLow | x |  |
| NuclearGeneratingUnit | controlResponseRate | x |  |
| NuclearGeneratingUnit | efficiency | x | >= 0.001 and <= 1.2 |
| NuclearGeneratingUnit | freqBias | x |  |
| NuclearGeneratingUnit | freqDevDeadband | x |  |
| NuclearGeneratingUnit | governorMPL | x |  |
| NuclearGeneratingUnit | governorSCD | x |  |
| NuclearGeneratingUnit | highReasonabilityLimit | x | >= lowReasonabilityLimit |
| NuclearGeneratingUnit | highReasonabilityRampRateLimit | x | >= lowReasonabilityRampRateLimit |
| NuclearGeneratingUnit | hotintTime | x |  |
| NuclearGeneratingUnit | hotStartTime | x | <= intStartTime |
| NuclearGeneratingUnit | intColdTime | x |  |
| NuclearGeneratingUnit | intStartTime | x | <= coldStartTime |
| NuclearGeneratingUnit | lowReasonabilityLimit | x | >= 0 |
| NuclearGeneratingUnit | lowReasonabilityRampRateLimit | x |  |
| NuclearGeneratingUnit | maxDailyStarts | x |  |
| NuclearGeneratingUnit | maximumOperatingMW | x | equal to highReasonabilityLimit |
| NuclearGeneratingUnit | maxONTime | x |  |
| NuclearGeneratingUnit | maxWeeklyEnergy | x |  |
| NuclearGeneratingUnit | maxWeeklyStarts | x | >= maxDailyStarts |
| NuclearGeneratingUnit | minimumOperatingMW | x | equal to lowReasonabilityLimit |
| NuclearGeneratingUnit | minOFFTime | x |  |
| NuclearGeneratingUnit | minONTime | x | <= maxONTime |
| NuclearGeneratingUnit | modelDetail | x |  |
| NuclearGeneratingUnit | penaltyFactor | x |  |
| NuclearGeneratingUnit | seasonalMaxSustainableRating | x | >= seasonalMinSustainableRating |
| NuclearGeneratingUnit | seasonalMinEmergencyRating | x |  |
| NuclearGeneratingUnit | seasonalMinSustainableRating | x |  |
| NuclearGeneratingUnit | stepChange | x |  |
| NuclearGeneratingUnit | teid | x | >=0 and <= 999999999 |
| OwnerShareLimits | highReasonabilityLimit | x | >= lowReasonabilityLimit |
| OwnerShareLimits | lowReasonabilityLimit | x |  |
| OwnerShareLimits | maxWeeklyEnergy | x |  |
| OwnerShareLimits | teid | x | >=0 and <= 999999999 |
| OwnerShareLimits | aliasName | x |  |
| OwnerShareRating | teid | x | >=0 and <= 999999999 |
| Ownership | ownPercent | x | >= 0 and <= 100 |
| Ownership | teid | x | >=0 and <= 999999999 |
| PenstockLossCurve | curveStyle | x |  |
| PenstockLossCurve | xUnit | x |  |
| PenstockLossCurve | y1Unit | x |  |
| PenstockLossCurve | y2Unit | x |  |
| PhaseShifterImpedance Curve | curveStyle | x |  |
| PhaseShifterImpedance Curve | xUnit | x |  |
| PhaseShifterImpedance Curve | y1Unit | x |  |
| PhaseShifterImpedance Curve | y2Unit | x |  |
| PhaseShifterImpedance Curve | aliasName | x |  |
| PhysicalTiePoint | teid | x | >=0 and <= 999999999 |
| PlanningBay | teid | x | >=0 and <= 999999999 |
| Plant | teid | x | >=0 and <= 999999999 |
| PowerCutZone | teid | x | >=0 and <= 999999999 |
| PowerSystemResource | teid | x | >=0 and <= 999999999 |
| PowerTransformer | bmagSat | x |  |
| PowerTransformer | transformerType | x |  |
| PowerTransformer | voltageSensitivity | x |  |
| PowerTransformer | teid | x | >=0 and <= 999999999 |
| PricingVector | teid | x | >=0 and <= 999999999 |
| PrimeMover | teid | x | >=0 and <= 999999999 |
| ProtectedSwitch | initiallyOpen | x |  |
| ProtectedSwitch | normalOpen | x |  |
| ProtectedSwitch | teid | x | >=0 and <= 999999999 |
| ProtectionEquipment | teid | x | >=0 and <= 999999999 |
| PseudoCompany | teid | x | >=0 and <= 999999999 |
| PWRSteamSupply | teid | x | >=0 and <= 999999999 |
| RampRateCurve | Emergency | x |  |
| RampRateCurve | curveStyle | x |  |
| RampRateCurve | xUnit | x |  |
| RampRateCurve | y1Unit | x |  |
| RampRateCurve | y2Unit | x |  |
| RampRateCurve | aliasName | x |  |
| Rating | ratingType | x |  |
| Rating | TempPoint | x |  |
| Rating | forNetwork | x |  |
| RectifierInverter | teid | x | >=0 and <= 999999999 |
| RegularIntervalSchedule | startTime | x |  |
| RegularIntervalSchedule | value1Unit | x |  |
| RegularIntervalSchedule | value2Unit | x |  |
| RegulatingCondEq | teid | x | >=0 and <= 999999999 |
| RegulationSchedule | startTime | x |  |
| RegulationSchedule | value1Unit | x |  |
| RegulationSchedule | value2Unit | x |  |
| RemedialActionScheme | active | x |  |
| RemedialActionScheme | isRAP | x |  |
| RemedialActionScheme | isRAS | x |  |
| RemoteUnit | teid | x | >=0 and <= 999999999 |
| Reservoir | teid | x | >=0 and <= 999999999 |
| ResourceController | externalJointUnit | x |  |
| ResourceController | frequencyBias | x |  |
| ResourceController | gross | x |  |
| ResourceController | jointUnit | x |  |
| ResourceController | physical | x |  |
| ResourceController | teid | x | >=0 and <= 999999999 |
| SeasonDayTypeSchedule | startTime | x |  |
| SeasonDayTypeSchedule | value1Unit | x |  |
| SeasonDayTypeSchedule | value2Unit | x |  |
| SeriesCompensator | r | x |  |
| SeriesCompensator | x | x |  |
| SeriesCompensator | teid | x | >=0 and <= 999999999 |
| ShuntCompensator | aVRDelay | x |  |
| ShuntCompensator | maximumkV | x |  |
| ShuntCompensator | minimumkV | x |  |
| ShuntCompensator | nominalkV | x |  |
| ShuntCompensator | nominalMVAr | x |  |
| ShuntCompensator | switchingPriority | x |  |
| ShuntCompensator | voltSensitivity | x |  |
| ShuntCompensator | avrEnabled | x |  |
| ShuntCompensator | teid | x | >=0 and <= 999999999 |
| StaticVarCompensator | b | x |  |
| StaticVarCompensator | capacitiveRating | x | > 0 |
| StaticVarCompensator | fixedMVAr | x | < 0 |
| StaticVarCompensator | highVoltageChangeThreshold | x |  |
| StaticVarCompensator | inductiveRating | x | < 0 |
| StaticVarCompensator | lowVoltageChangeThreshold | x |  |
| StaticVarCompensator | maximumkV | x |  |
| StaticVarCompensator | minimumkV | x |  |
| StaticVarCompensator | steadyStateMVARMax | x | postContingencyMVARMax >steadyStateMVARMax > steadyStateMVARMin > postContingencyMVARMin |
| StaticVarCompensator | steadyStateMVARMin | x | postContingencyMVARMax >steadyStateMVARMax > steadyStateMVARMin > postContingencyMVARMin |
| StaticVarCompensator | teid | x | >=0 and <= 999999999 |
| StationSupply | conformingLoadFlag | x |  |
| StationSupply | pfixedPct | x |  |
| StationSupply | pnomPct | x |  |
| StationSupply | qfixed | x |  |
| StationSupply | qnomPct | x |  |
| StationSupply | teid | x | >=0 and <= 999999999 |
| StationSupplyWRCurve | aliasName | x |  |
| SteamSupply | teid | x | >=0 and <= 999999999 |
| SteamTurbine | teid | x | >=0 and <= 999999999 |
| SubControlArea | ControlAreaNumber | x |  |
| SubControlArea | teid | x | >=0 and <= 999999999 |
| Subcritical | teid | x | >=0 and <= 999999999 |
| SubGeographicalRegion | isWeatherZone | x |  |
| SubGeographicalRegion | aliasName | x | if isWeatherZone=true |
| Substation | forNetwork | x |  |
| Substation | forScada | x |  |
| Substation | teid | x | >=0 and <= 999999999 |
| Supercritical | teid | x | >=0 and <= 999999999 |
| Switch | teid | x | >=0 and <= 999999999 |
| SynchrocheckRelay | teid | x | >=0 and <= 999999999 |
| SynchronousMachine | baseMVAr | x |  |
| SynchronousMachine | inertia | x |  |
| SynchronousMachine | maximumKV | x | >=0 and <= 1100 |
| SynchronousMachine | maximumMVAr | x |  |
| SynchronousMachine | minimumKV | x | >=0 and <= 1100 |
| SynchronousMachine | minimumMVAr | x |  |
| SynchronousMachine | r | x |  |
| SynchronousMachine | ratedMVA | x | >= maximumMVAr |
| SynchronousMachine | x | x | >=0 and <= 500 |
| SynchronousMachine | xSubtrans | x |  |
| SynchronousMachine | xTrans | x |  |
| SynchronousMachine | teid | x | >=0 and <= 999999999 |
| TapChanger | avrEnabled | x |  |
| TapChanger | awrEnabled | x |  |
| TapChanger | highStep | x | >=0 and <= 99 |
| TapChanger | initialDelay | x |  |
| TapChanger | lowStep | x | >=0 and <= 99 |
| TapChanger | maximumkV | x |  |
| TapChanger | minimumkV | x |  |
| TapChanger | neutralAngle | x |  |
| TapChanger | neutralKV | x | >=0 and <= 1100 |
| TapChanger | neutralStep | x | >=0 and <= 99 |
| TapChanger | normalStep | x | >=-99 and <= 99 , >= lowStep and <= highStep |
| TapChanger | stepVoltageIncrement | x | >=0 and <= 100 |
| TapChanger | subsequentDelay | x |  |
| TapChanger | teid | x | >=0 and <= 999999999 |
| ThermalGeneratingUnit | coldStartTime | x |  |
| ThermalGeneratingUnit | controlPulseHigh | x |  |
| ThermalGeneratingUnit | controlPulseLow | x |  |
| ThermalGeneratingUnit | controlResponseRate | x |  |
| ThermalGeneratingUnit | efficiency | x | >= 0.001 and <= 1.2 |
| ThermalGeneratingUnit | freqBias | x |  |
| ThermalGeneratingUnit | freqDevDeadband | x |  |
| ThermalGeneratingUnit | governorMPL | x |  |
| ThermalGeneratingUnit | governorSCD | x |  |
| ThermalGeneratingUnit | highReasonabilityLimit | x | >= lowReasonabilityLimit |
| ThermalGeneratingUnit | highReasonabilityRampRateLimit | x | >= lowReasonabilityRampRateLimit |
| ThermalGeneratingUnit | hotintTime | x |  |
| ThermalGeneratingUnit | hotStartTime | x | <= intStartTime |
| ThermalGeneratingUnit | intColdTime | x |  |
| ThermalGeneratingUnit | intStartTime | x | <= coldStartTime |
| ThermalGeneratingUnit | lowReasonabilityLimit | x | >= 0 |
| ThermalGeneratingUnit | lowReasonabilityRampRateLimit | x |  |
| ThermalGeneratingUnit | maxDailyStarts | x |  |
| ThermalGeneratingUnit | maximumOperatingMW | x | equal to highReasonabilityLimit |
| ThermalGeneratingUnit | maxONTime | x |  |
| ThermalGeneratingUnit | maxWeeklyEnergy | x |  |
| ThermalGeneratingUnit | maxWeeklyStarts | x | >= maxDailyStarts |
| ThermalGeneratingUnit | minimumOperatingMW | x | >=0 and <= 999 and equal to lowReasonabilityLimit |
| ThermalGeneratingUnit | minOFFTime | x |  |
| ThermalGeneratingUnit | minONTime | x | <= maxONTime |
| ThermalGeneratingUnit | modelDetail | x |  |
| ThermalGeneratingUnit | penaltyFactor | x |  |
| ThermalGeneratingUnit | seasonalMaxSustainableRating | x | >= seasonalMinSustainableRating |
| ThermalGeneratingUnit | seasonalMinEmergencyRating | x |  |
| ThermalGeneratingUnit | seasonalMinSustainableRating | x |  |
| ThermalGeneratingUnit | stepChange | x |  |
| ThermalGeneratingUnit | teid | x | >=0 and <= 999999999 |
| TieCorridor | teid | x | >=0 and <= 999999999 |
| TieEnd | teid | x | >=0 and <= 999999999 |
| TieLine | teid | x | >=0 and <= 999999999 |
| TransformerWinding | b | x | >=-100 and <= 100 |
| TransformerWinding | connectionType | x |  |
| TransformerWinding | emergencyMVA | x | <= shortTermMVA |
| TransformerWinding | g | x | >=0 and <= 999 |
| TransformerWinding | grounded | x |  |
| TransformerWinding | r | x | >=-50 and <= 500 |
| TransformerWinding | r0 | x | >=-5000 and <= 5000 |
| TransformerWinding | ratedMVA | x |  |
| TransformerWinding | rground | x | >=0 and <= 10 |
| TransformerWinding | shortTermMVA | x |  |
| TransformerWinding | x | x | >= -1000 and <= 1000 |
| TransformerWinding | x0 | x | >= -10000 and <= 10000 |
| TransformerWinding | teid | x | >=0 and <= 999999999 |
| VoltageControlZone | teid | x | >=0 and <= 999999999 |
| VoltageLevel | teid | x | >=0 and <= 999999999 |
| VoltageRelay | teid | x | >=0 and <= 999999999 |
| WindGeneratingUnit | coldStartTime | x |  |
| WindGeneratingUnit | controlPulseHigh | x |  |
| WindGeneratingUnit | controlPulseLow | x |  |
| WindGeneratingUnit | controlResponseRate | x |  |
| WindGeneratingUnit | efficiency | x | >= 0.001 and <= 1.2 |
| WindGeneratingUnit | freqBias | x |  |
| WindGeneratingUnit | freqDevDeadband | x |  |
| WindGeneratingUnit | governorMPL | x |  |
| WindGeneratingUnit | governorSCD | x |  |
| WindGeneratingUnit | highReasonabilityLimit | x | >= lowReasonabilityLimit |
| WindGeneratingUnit | highReasonabilityRampRateLimit | x | >= lowReasonabilityRampRateLimit |
| WindGeneratingUnit | hotintTime | x |  |
| WindGeneratingUnit | hotStartTime | x | <= intStartTime |
| WindGeneratingUnit | intColdTime | x |  |
| WindGeneratingUnit | intStartTime | x | <= coldStartTime |
| WindGeneratingUnit | lowReasonabilityLimit | x | >= 0 |
| WindGeneratingUnit | lowReasonabilityRampRateLimit | x |  |
| WindGeneratingUnit | maxDailyStarts | x |  |
| WindGeneratingUnit | maximumOperatingMW | x | equal to highReasonabilityLimit |
| WindGeneratingUnit | maxONTime | x |  |
| WindGeneratingUnit | maxWeeklyEnergy | x |  |
| WindGeneratingUnit | maxWeeklyStarts | x | >= maxDailyStarts |
| WindGeneratingUnit | minimumOperatingMW | x | >=0 and <= 999 and equal to lowReasonabilityLimit |
| WindGeneratingUnit | minOFFTime | x |  |
| WindGeneratingUnit | minONTime | x | <= maxONTime |
| WindGeneratingUnit | modelDetail | x |  |
| WindGeneratingUnit | penaltyFactor | x |  |
| WindGeneratingUnit | seasonalMaxSustainableRating | x | >= seasonalMinSustainableRating |
| WindGeneratingUnit | seasonalMinEmergencyRating | x |  |
| WindGeneratingUnit | seasonalMinSustainableRating | x |  |
| WindGeneratingUnit | stepChange | x |  |
| WindGeneratingUnit | teid | x | >=0 and <= 999999999 |

# Appendix B - Validation Rules – Required associations

This appendix lists all of the validation rules for associations that must be defined for a specific class.

| ClassA | ClassB |
| --- | --- |
| Accumulator | MeasurementType |
| Accumulator | Operatorship |
| Accumulator | Ownership |
| Accumulator | Terminal |
| Accumulator | Unit |
| AccumulatorLimitSet | Accumulator |
| AccumulatorValue | MeasurementGroup |
| AccumulatorValue | MeasurementValueSource |
| AccumulatorValue | PermissionArea |
| AccumulatorValue | RemoteSource |
| ACLineSegment | BaseVoltage |
| ACLineSegment | Operatorship |
| ACLineSegment | Ownership |
| AggregateHub | SettlementHUB |
| AlternateLimit | AlternateLimitSet |
| Analog | Operatorship |
| Analog | Ownership |
| Analog | Unit |
| AnalogLimit | AnalogLimitSet |
| AnalogLimitSet | Analog |
| AngleDifference | MonitoredGroup |
| Bay | Operatorship |
| Bay | Ownership |
| BranchGroup | MonitoredGroup |
| Breaker | Operatorship |
| Breaker | Ownership |
| BusbarSection | BaseVoltage |
| BusbarSection | Operatorship |
| BusbarSection | Ownership |
| BWRSteamSupply | Operatorship |
| BWRSteamSupply | Ownership |
| CAESPlant | Operatorship |
| CAESPlant | Ownership |
| CogenerationPlant | Operatorship |
| CogenerationPlant | Ownership |
| CombinedCyclePlant | Operatorship |
| CombinedCyclePlant | Ownership |
| CombustionTurbine | Operatorship |
| CombustionTurbine | Ownership |
| ConformLoad | ConformLoadGroup |
| ConnectivityNode | EquipmentContainer |
| Connector | Operatorship |
| Connector | Ownership |
| ControllableLoadResource | Operatorship |
| ControllableLoadResource | Ownership |
| ControllableLoadResource | Operatorship |
| ControllableLoadResource | Ownership |
| CurrentRelay | Operatorship |
| CurrentRelay | Ownership |
| CurveData | Curve |
| CustomerLoad | ConformLoadGroup |
| CustomerLoad | Operatorship |
| CustomerLoad | Ownership |
| Disconnector | Operatorship |
| Disconnector | Ownership |
| Discrete | MeasurementType |
| Discrete | Operatorship |
| Discrete | Ownership |
| Discrete | Unit |
| EndCap | EquipmentContainer |
| EndCap | Operatorship |
| EndCap | Ownership |
| EnergyConsumerResource | Operatorship |
| EnergyConsumerResource | Ownership |
| EPSMeter | PricingVector |
| FlowgateGroup | MonitoredGroup |
| HydroGeneratingUnit | Operatorship |
| HydroGeneratingUnit | Ownership |
| InductionMotorLoad | Operatorship |
| InductionMotorLoad | Ownership |
| Junction | Operatorship |
| Load | ConformLoadGroup |
| Load | EquipmentContainer |
| Load | Operatorship |
| Load | Ownership |
| LoadResource | EnergyConsumer |
| LoadResource | Operatorship |
| Measurement | Unit |
| MeasurementLocation | PermissionArea |
| Monitored | MonitoredGroup |
| MonitoredRating | MonitoredGroup |
| MVArCapabilityCurve | SynchronousMachine |
| NuclearGeneratingUnit | Operatorship |
| NuclearGeneratingUnit | Ownership |
| OwnerShareLimits | Operatorship |
| OwnerShareLimits | Ownership |
| PowerTransformer | Operatorship |
| ResourceController | Operatorship |
| ResourceController | Ownership |
| SeriesCompensator | Operatorship |
| SeriesCompensator | Ownership |
| SettlementLoadZone | Substation |
| ShuntCompensator | Operatorship |
| ShuntCompensator | Ownership |
| StaticVarCompensator | Operatorship |
| StaticVarCompensator | Ownership |
| StationSupply | Operatorship |
| StationSupply | Ownership |
| StringMeasurement | Unit |
| StringMeasurementValue | PermissionArea |
| SubGeographicalRegion | GeographicalRegion |
| Substation | SubGeographicalRegion |
| Substation | Operatorship |
| Substation | Ownership |
| SynchronousMachine | Operatorship |
| SynchronousMachine | Ownership |
| TapChanger | Operatorship |
| TapChanger | Ownership |
| ThermalGeneratingUnit | CombinedCyclePlant |
| ThermalGeneratingUnit | Operatorship |
| ThermalGeneratingUnit | Ownership |
| TransformerWinding | Operatorship |
| TransformerWinding | Ownership |
| TransmissionPath | ServicePoint |
| TransmissionPath | ServicePoint |
| VLSBusBarMonitored | MonitoredGroup |
| VoltageLevel | Substation |
| VoltageLevel | Operatorship |
| VoltageLevel | Ownership |
| VoltageMonitored | MonitoredGroup |
| WindGeneratingUnit | Operatorship |
| WindGeneratingUnit | Ownership |

# Appendix C - Validation Rules – COMPLEX rules

This appendix lists all of the validation rules that are more complex than required fields and range checks. These include validation rules that are conditional based upon certain conditions, involve associations with other attributes, and those that describe specific data relationships. The validation rule is explained descriptively and not in a formal language.

| Rule No. | Validation Rule |
| --- | --- |
| R1 | The abstract classes GeneratingUnit, Switch, EnergyConsumer,EnergyCosumerResource should not be used. Only the classes representing the actual classes should be used. For ex: Only instances of ThermalGeneratingUnit, NuclearGeneratingUnit, HydroGeneratingUnit or WindGeneratingUnit should be created instead of the generic GeneratingUnit Class |
| R2 | Each PowerTransformer and its associated TransformerWindings and TapChangers must be contained within one substation. |
| R3 | A PowerTransformer must be contained by a Substation. A TransformerWinding must be contained by a PowerTransformer. A TapChanger must be contained by a TransformerWinding( Check for associations between transformer, winding and tap. |
| R4 | A Measurement must be associated with a PowerSystemResource to convey containment information for the Measurement. |
| R5 | Transmission line measurements should be associated with an ACLineSegment or SeriesCompensator not with a Line. Transmission line measurements must be associated with a terminal. |
| R6 | Transformer measurements should be associated with a PowerTransformer. Transformer Windings should not have measurements. |
| R7 | A Measurement can be associated with at most one Terminal. |
| R8 | Combined Cycle configuration names should be unique for each Combined Cycle Plant. |
| R9 | ConnectivityNodes may only be placed within ConnectivityNodeGroup. |
| R10 | SynchronousMachine's minimumMVAr and maximumMVAr attributes and the minimum/maximum MVAr value specified in the associated MVArCapabilityCurve data should match. |
| R11 | Terminals connected to the same piece of Equipment can not be connected to the same connectivitynode |
| R12 | Voltage Levels can't be empty. There should always be classes associated to voltage levels. |
| R13 | The normal and neutral tap of the transformer must be within low and high steps |
| R14 | If there are 2 identical transformers in parallel with one marked Master and the other as Follower , the tap changer of the follower should always point towards the master tapchanger and not to itself. |
| R15 | Connectivity nodes must be associated to atleast 2 terminals. |
| R16 | Terminal associated to a any given equipment should have unique names. |
| R17 | ACLinesegment cannot go between different voltage levels. |
| R18 | Seriescompensator cannot go between different voltage levels and should be contained within one substation |
| R19 | The regulated terminal of a shuntcompensator must be in the same substation as the shuntcompensator's terminal (RegulatingCondEq->Terminal) |
| R20 | A shuntcompensator's SwitchedBy switch's terminal must be connected to shuntcompensator's terminal through a connectivitynode. |
| R21 | Transformer and Line ratings should follow these rules. NormalRating<=twohourrating<=15minrating |
| R22 | Sum of Ownership.ownershippercent should total 100% for SplitGenerationUnits(SGR). An SGR will have 1 record in one of the GeneratingUnit classes and "n" number of OwnerShareLimits that are associated to that GeneratingUnit. Each OwnerShareLimit will point to a OwnerShip record. The sum of all these ownership.ownershippercent should be equal to 100. |
| R23 | DCTie Psuedo Load breaker default value must be "Closed". |
| R24 | BLT(BlockLoadTransfer) must only group loads and only zero or one psuedo GeneratingUnit per BLT. The breaker for this psuedo gen if modeleld must have a default value of OPEN. |
| R25 | HubBus must have atleast one electrical bus. |
| R26 | The ConnectivityNodes in a ConnectivityNodeGroup must be in the SAME STATION i.e. ConnectivityNodes in a given ConnectivityNodeGroup cannot span multiple Stations. |
| R27 | If a HubBus is associated to more than 1 ConnectivityNodeGroup then ALL the associated ConnectivityNodeGroups must belong to the same station. |
| R28 | SynchronousMachine's 'ratedMVA' attribute should be greater than or equal to the 'baseMW' attribute of the GeneratingUnit it is associated to. |
| R29 | Check the baseVoltage (if not null) of each conducting equipment connected to a connectivityNode to be the same. |
| R30 | Only AnalogLimit instances that are children of an AnalogLimitSet instance with the LimitSet.forNetwork = False/Null should have the LimitAlarmCategory and AnalogLimitName associations populated. OR If the parent AnalogLimitSet instance’s the LimitSet.forNetwork = True of if the AnalogLimit instance’s parent is a Rating instance, the two associations do not need to be populated. |
| R31 | The energy consumer that is part of the DCTie must have ONE and ONLY one controllable load resource mapped to it. This energyconsumer can NOT be associated to a "non-controllable load resource". It has to be associated only to "controllable load resource". |
| R32 | Only AnalogLimit instances that are children of an AnalogLimitSet instance with the LimitSet.forNetwork = False/Null should have the lower and upper thresholds |
| R33 | Substation names should not exceed 8 chars. |
| R34 | The target voltage setting specified by the regulation schedules must be within 80% to 120% of the rated kV |
| R35 | The number of CurveData associated with the MVArCapabilityCurves and RampRateCurve should not exceed 10 |
| R36 | Two RampRateCurves (one with Emergency = True) should be associated with a ControllableLoadResource, a Configuration and a ThermalGeneratingUnit / HydroGeneratingUnit / NuclearGeneratingUnit / WindGeneratingUnit which has no association to a DCTie and a PrivateAreaNetwork (NetworkType: Non Modeled Generation, Mothballed, Retired) or a CombinedCyclePlant. |
| R37 | The FromConfig and ToConfig of a TransState shouldn't be same |
| R38 | FromConfig and ToConfig of a TransState must belong to the same CombinedCyclePlant |
| R39 | A Contingency can’t contain duplicate ContingencyElements |
| R40 | The controllable load resource must be associated with exactly two RampRateCurves, one for normal condition and the other for emergency condition |
| R41 | There is no duplicated CC configuration, i.e. there should not be 2 CC configurations that contain the same CCU combination with exactly same status of Primary/Alternate flag |
| R42 | Each CC plant must have at least one CC configuration to startup/shutdown |
| R43 | If a ThermalGeneratingUnit is a unit in a CombinedCyclePlant, then it cannot be a SplitGenerationResource. |
| R44 | If any Measurement instance has more than one (MeasurementValue instance that is associted with MeasurementValueSource instance) then only one can have Company != ERCOT |
| R45 | Each CustomerLoad instance should be associated with One instance of SettlementNOIELoadZone, Or One instance of DCTie, Or Its parent Substation should be associated with one instance of SettlementLoadZone |
| R46 | For any instance of MeasurementArgument with ReferenceFlag = True, the Calculation link on the associated MeasurementValue instance should not be same as the parent Calculation instance of the MeasurementArgument instance. |
| R47 | MeasurementValue instances that are sourced from or output of a calculation should have its Primary Site as “DE”. |
| R48 | Every ElectricalBus should be in a LoadZone or a NOIE load zone |
| R49 | PsuedoTerminal shoud not be Associated to a connectivityNode |
| R50 | Psuedoterminal should not be associated to a RegulatingconductingEquipment |
| R51 | EnergyConsumerResource(LoadResource and ControllableLoadResource) should not have any association to ResourceNode |
| R52 | If PAN.networktype = retired or mothbolled, then there should be only one genunit associated to it. |
| R53 | x/r ratio for ACLineSegment should follow these rules. For 345kv x/r > 7, 138kv x/r> 1.5, 69kv x/r > 1 |
| R54 | A resourceNode that is associated to a PrivateUseNetwork(PUN), should not be associated to any Physical Generating Unit |
| R55 | Every GeneratingUnit(Thermal, Hydro, Nuclear, Wind) should have an association to a ResourceNode unless the GeneratingUnit is associated to a DCTie, NonModelledGeneration or BlockLoadType resource. |
| R56 | If a Load is assigned to a NOIE load zone, then its electrical bus can ONLY have loads that are assigned to the same NOIE load zone, i.e. cannot have other loads at the same electrical bus assigned to different load zone In other words, all loads that connect to the same EB must belong to the same load zone. All those loads must either be associated to the same NOIE load zone, or none of them has this association. |
| R57 | DCTIE ElectricalBus can only connect to DCTIE load. The ElectricalBus connecting to terminal of DCTIE pseudo load (DCTIE attribute of CUSTOMERLOAD instance) cannot have other loads connect to it |
| R58 | Each CombinedCyclePlant Configuration instance should have at least one association to a ConfigurationMember instance |
| R59 | PricingVector's should have a unique name |
| R60 | MeasurementGroup and Calculation instances associated to a Zonal MeasurementLocation should have unique names. Similarly MeasurementGroup and Calculation instances associated to a Nodal MeasurementLocation should have unique names |
| R61 | Measurementargument and ConstantArgument instances associated to a Calculation should have unique names |
| R62 | Zonal Measurements(Analog, Discrete) associated to a terminal should have unique names. |
| R63 | Nodal Measurements(Analog, Discrete) associated to a terminal should have unique names. |
| R64 | At least one Ownersharelimit instance should be associated with every LoadResource, ControllableLoadResource, ThermalGeneratingUnit, HydroGeneratingUnit, WindGeneratingUnit, NuclearGeneratingUnit, |
| R65 | Every zonal AnalogLimitSet should be associated with a zonal Analog - Every Nodal AnalogLimitSet should be associated with Nodal Analog. |
| R66 | Every Zonal AnalogValue with NO association to a AnalogName should be associated with a zonal MeasurementValueQuality and MeasurementValueSource. Every Nodal AnalogValue with no association to a AnalogName should be associated with a Nonal MeasurementValueQuality and MeasurementValueSource |
| R67 | Every zonal AnalogValue with association to a AnalogName should be associated with a zonal site and should be associated to atleast one zonal MeasurementGroup or one zonal Calculation - Every Nodal AnalogValue with association to a AnalogName should be associated with a zonal site and should be associated to atleast one Nodal MeasurementGroup or one Nodal Calculation |
| R68 | Every zonal DiscreteValue with association to a DiscreteName should be associated with a zonal site and should be associated to atleast one zonal MeasurementGroup or one zonal Calculation - Every Nodal discreteValue with association to a discreteName should be associated with a zonal site and should be associated to atleast one Nodal MeasurementGroup or one Nodal Calculation |
| R69 | Every zonal Analog should be associated with a zonal AnalogValue - Every Nodal Analog should be associated with a Nodal AnalogValue |
| R70 | Every zonal analoglimit associated with analoglimitname should be associated with a zonal analoglimitset. Every nodal analoglimit associated with analoglimitname should be associated with a nodal analoglimitset |
| R71 | Every zonal MeasurementArgument and ConstantArgument should be associated with a zonal Calculation - Every Nodal MeasurementArgument and ConstantArgument should be associated with a Nodal Calculation |
| R72 | Every zonal ConstantValue should be associated with a zonal ConstantArgument - Every Nodal ConstantValue should be associated with a Nodal ConstantArgument |
| R73 | Every configuration should either be able to StartUp or Shutdown or transition into another configuration, else it is invalid. |
| R74 | Attributes, HightReasonabilityLimit, LowReasonabilityLimit and MaxWeeklyenergy should be populated for any ownersharelimits associated with a LoadResource, a ControllableLoadResource, and a ThermalGeneratingUnit / HydroGeneratingUnit / NuclearGeneratingUnit / WindGeneratingUnit which has no association to a DCTie and a PrivateAreaNetwork (NetworkType: Non Modeled Generation Retired, Mothballed, BlockLoadTransfer). |
| R75 | Attributes (Operational Resource Parameters), MinOnlineTime, minOfflineTime, hotstartTime, IntStartTime, ColdStartTime, Maxweeklystarts, maxonlinetime, maxdailystarts, maxweeklystarts, hotinttime, intcoldtime, syscondensercapable should be populated for any Configuration and any ThermalGeneratingUnit / HydroGeneratingUnit / NuclearGeneratingUnit / WindGeneratingUnit which has no association to a CombinedCyclePlant, a DCTie and a PrivateAreaNetwork (NetworkType: Non Modeled Generation, Retired, Mothballed, BlockLoadTransfer) . |
| R76 | Attributes (Resource Parameters), HighReasonabilityLimit, LowReasonabilityLimit, HighReasonabilityRampRateLimit, LowReasonabilityRampRateLimit, MaxSustainableRating, MinSustainableRating, MaxEmergencyRating, MinEmergencyRating should be populated for any Configuration and any ThermalGeneratingUnit / HydroGeneratingUnit / NuclearGeneratingUnit / WindGeneratingUnit which has no association to a DCTie and a PrivateAreaNetwork (NetworkType: Non Modeled Generation, Retired, Mothballed, BlockLoadTransfer). |
| R77 | Each Configuration must have at least one PRIMARY CCU (defined as CONFIGURATIONMEMBER with PRIMARY flag = ‘TRUE’ ) |
| R78 | Each CombinedCyclePlant must have at least one configuration that can start up (i.e. STARTUPFLAG = ‘TRUE’) |
| R79 | Each CombinedCyclePlant must have at least one configuration that can shut down (i.e. SHUTDOWNFLAG = ‘TRUE’) |
| R80 | Each Configuration must satisfy at least one of the two conditions a) have at least one in-transstate (i.e. transstate with that configuration as TOCONFIG_CONFIGURATION) or b) its STARTUPFLAG is set to ‘True’ |
| R81 | Each Configuration must have at least one of the two conditions a) have at least one out-transstate (i.e. transstate with that configuration as FROMCONFIG_CONFIGURATION) or b) its SHUTDNFLAG is set to ‘True’ |
| R82 | All Configurations must have path to transit from start-up configuration AND transit to shut-down figuration in some way. This can be direct transstate or through other configurations. This is to prevent CC Plant being trapped ONLINE or OFFLINE |
| R83 | Validate the UpTransition Attribute on a TransState: If UpTransition = True, count of primary members in the FromConfiguration < count of primary members in the ToConfiguration and if UpTransition = False, count of primary members in the FromConfiguration > count of primary members in the ToConfiguration. |
| R84 | Every Zonal DiscreteValue with no association to a DiscreteName should be associated with a zonal MeasurementValueQuality and a zonal MeasurementValueSource. Every Nodal DiscreteValue with no association to a DiscreteName should be associated with a Nodal MeasurementValueQuality and a nodal MeasurementValueSource. |
| R85 | All x_axisdata data points in a MVArCapabilityCurve should be unique |
| R86 | Only one y1_axisdata point in a MVArCapabilityCurve can be 0. |
| R87 | Only one y2_axisdata point in a MVArCapabilityCurve can be 0. |
| R88 | For every ICCPQualityConversion instance, a. Only One of the following attributes ICalculated, IManual, IEstimated, ITelemetered should be true, and b. Only One of the following attributes IValid, INotValid, ISuspect, IHeld should be true, and c. Only One of the following attributes OValid, ONotValid, OSuspect, OHeld should be true, and d. Only One of the following attributes OCalculated, OManual, OEstimated, ITelemetered should be true. |
| R89 | There should be atleast one swing bus in the model. i.e. atleast one connectivity node with SlackBusPriority = True |
| R90 | There should be no Pricingvector associated to a BusbarSection or a Endcap. |
| R91 | For an EnergyConsumer (CustomerLoad or StationSupply), if conformingLoadFlag = True, then the EnergyConsumer should be associated to a ConformLoadGroup |
| R92 | When a MeasurementLocation has more than one children (MeasurementGroup or Calculation), (All zonal analogvalues and discretevalues associated to the child MeasurementGroup) and (All zonal Analogvalues and discretevalues associated with measurementargument having referencefalg = False within the child calculation) should be associated to the same terminal. All Nodal analogvalues and discretevalues associated to the child MeasurementGroup) and (All Nodal Analogvalues and discretevalues associated with measurementargument having referencefalg = False within the child calculation) should be associated to the same terminal. For example 1. MeasLoc1 -> MeasGrp1 -> AnalogValue1 ->Analog1 ->Terminal1 2. MeasLoc1 -> MeasGrp1 -> AnalogValue2 ->Analog2->Terminal1 3. MeasLoc1 -> Calc1 -> MeasArg1 (referenceflag = false) -> AnalogValue3 ->Analog3 ->Terminal1 4. MeasLoc1 -> Calc1 -> MeasArg1 (referenceflag = false) -> AnalogValue4 ->Analog4->Terminal1 |
| R93 | A TriggerCondition may have multiple Gates associated with it. One of them must be its resulting Gate, (i.e. the Gate determing the trigger condition). This resulting Gate must be of type: or/and/nand/nor |
| R94 | If a Gate is of the following types: gt/ge/ lt/le/eq/ne, then its input must be exactly One PinFlow or PinBranchGroup or PinVoltage. If input is PinFlow then PinFlow.InputIsFlow must be TRUE, |
| R95 | If a Gate is of the following types: or/and/nand/nor, then its input must be one or more PinGate or PinSwitch. or PinFlow. If input is PinFlow then PinFlow.InputIsFlow must be FALSE |
| R96 | If a Gate is of the following types: not, then its input must be exactly one PinGate or PinSwitch. |
| R97 | MRID and TEIDs in the entire model should be unique. |
| R98 | Any Company with CompanyType = QSE or ERCOT can Own and Operate Zero Or One Substation with ForNetwork = False and ForSCADA = True. |
| R99 | For any GeneratingUnit, LoadResource and ControllableLoadResource each QSE operator of the GeneratinUnit needs to Own a Substation with ForNetwork = False and ForSCADA = True. Ex. GU->OSL->Operatorship->Company->Ownership ->Substation (forNetwork = False and ForSCADA = True) |
| R100 | The owner of a GeneratingUnit , LoadResource and ControllableLoadResource should always be an RE or ERCOT. Operator should be a QSE or ERCOT. |
| R101 | For every generating unit that’s not associated to a combined cycle plant, maximumOperatingMW = HRL and minimumOperatingMW = LRL |
| R102 | All instances of the following classes should have a unique name, Contingencies ContingencyGroups RemedialActionSchemes SharedProtectiveActions VoltageLimitSets , ResourceNode, HubBus |
| R103 | The total number of CalculationArguments (MeasurementArgument and/or ConstantArgument) associated to a Calculation must be equal to or greater than the total number of FunctionArguments the associated Function |
| R104 | In a Calculation every associated CalculationArgument (MeasurementArgument and/or ConstantArgument) should be associated to a unique FunctionArgument in the function associated to the Calculation |
| R105 | The Name of a measurementlocation should be same as the name of the associated PowerSystemResource unless the PowerSystemResource is of the Type = CombinedCyclePlant. In case of a CombinedCyclePlant the name of the MeasurementLocation should be same as the aliasname of the associated combinedcycleplant. |
| R106 | All conformLoads should have conformingloadflag = True and all nonconformloads should have conformingloadflag = False |
| R107 | A BLT-load, DCTie-load and a PUN-load should be of the type NonConformLoad |
| R108 | Length Limitations 2 AclineSegment. 4 TapChanger ,ConnectivityNode,ContingencyGroup Configuration,MeasurementGroup,Calculation VoltageLimitSet,VoltageLevel,CurveData,PowerTransformer Gate,PinBranchGroup,PinFlow,PinGate,PinSwitch PinTriggerCondition,PinVoltgae,Stage,StageTrigger AnalogName,Analog,AnalogLimit,AnalogLimitName DiscreteName,Discrete,MeasurementArgument,ConstantArgument ConstantValue 6 Company.(IO.Localname) 8 Substation,LoadbasedRegulationCurve MVArCapabilityCurve,PhaseShifterImpedanceCurve RampRateCurve,StationSupplyWRCurve,RemedialActionScheme TriggerCondition,Function,Site 12 IccpQualityConversionSet,IccpQualityConversion 14 Breaker,Disconnector,TransformerWinding,CutomerLoad LoadResource,Line,ShuntCompensator,StaticVarCompensator ResourceController,Company.(IO.AliasName),TieLine TieCorridor,ThermalGeneratingUnit,HydroGeneratingUnit NuclearGeneratingUnit,WindGeneratingUnit,SynchronousMachine SubLoadArea,LogicalConfiguration,PrivateUseNetwork |
| R109 | Every PowerSystemResource can have only one MeasurementLocation of a Particular Devicetype, i.e. Given a condition Device1 ->MeasLoc1 (RDFID: ABCD) DeviceTypeName: LD, Device1 ->MeasLoc1 (RDFID: FGHD) DeviceTypeName: LD : Invalid Device1 ->MeasLoc1 (RDFID: ABCD) DeviceTypeName: LDRES : Valid. |
| R110 | Measurement Argument or Constant argument under a Calculation should not be mapped to same Measurement Value or Constant Value. |
| R111 | An electrical bus must be associated with a connectivity node when: * a load is attached to the node. * Three or more switches are attached to the node and the node has a voltage reading |
| R112 | The RID for EPSmeter must be unique |
| R113 | customerLoad and Load instances cannot have association to PrivateAreaNetwork of type ERCOTPANTYPE.PrivateUseNetwork or SelfServe or BLT_Normally_out |
| R114 | Number of CurveScheduleData under PhaseShifterImpedanceCurve and TransformerImpedanceCurve are the same as Number of TapChanger step within PowerTransformer where the curve is asscociated to |
| R115 | FlowgateElement must associate with terminal of line/transformer/series (not allow association to other type of equipment) |
| R116 | OwnerShareLimit.name should be unique for Split generation resource . |
| R117 | A HubBus associates with 1..n ConnectivityNodeGroups. If a HubBus is associated to more than 1 ConnectivityNodeGroups, then ALL the associated ConnectivityNodeGroups must belong to the same Substation |
| R118 | Each DCTIE must associate with ONE and ONLY ONE ThermalGeneratingUnit |
| R119 | If a breaker or disconnector is modeled under a Bay instead of a VoltageLevel, then the association between Breaker/Disconnector to VoltageLevel should be populated. |
| R120 | If the Transformer is a Phase Shifting Transformer, a Phase Shifter Impedance Curve should be associated through the “Has A (PhaseShifterImpedanceCurve)” linkage. |
| R121 | If the Transformer is equipped with a Tap Ratio Curve, a Tap Ratio Curve should be associated through the “Has A (TapRatioCurve)” linkage. |

# Appendix D – Classes Not Allowed

Classes that are marked as “Not Allowed” cannot have data instances within the ERCOT CIM XML data file. The importers would ignore this data, but references between a "NOT_ALLOWED" class and a "USED" class could produce an invalid model/solution, especially if topology related. A list of classes and their compatibility with ERCOT applications will be published, and the classes marked as “Not Allowed” must NOT be populated via NOMCRs or they will be rejected in the NMMS validation step.

In the future, data for some of the classes currently “Not Allowed” may be allowed, but only after the impact has been evaluated and  the changes tested by all affected ERCOT applications. Newly created classes could also be allowed after being tested by affected ERCOT applications.

| BASICINTERVALSCHEDULE | NOT_ALLOWED - ABSTRACT |
| --- | --- |
| COMPOSITESWITCH | NOT_ALLOWED - TOPOLOGY |
| CONDUCTINGEQUIPMENT | NOT_ALLOWED - ABSTRACT |
| CONDUCTOR | NOT_ALLOWED - ABSTRACT |
| CONFORMLOAD | NOT_ALLOWED - ABSTRACT |
| CONNECTOR | NOT_ALLOWED - TOPOLOGY |
| CURVE | NOT_ALLOWED - ABSTRACT |
| DCLINESEGMENT | NOT_ALLOWED - TOPOLOGY |
| ENERGYAREA | NOT_ALLOWED - ABSTRACT |
| ENERGYCONSUMER | NOT_ALLOWED - ABSTRACT |
| ENERGYCONSUMERRESOURCE | NOT_ALLOWED - ABSTRACT |
| EQUIPMENT | NOT_ALLOWED - ABSTRACT |
| EQUIPMENTCONTAINER | NOT_ALLOWED - ABSTRACT |
| EQUIVALENTSOURCE | NOT_ALLOWED - TOPOLOGY |
| FEEDER | NOT_ALLOWED - TOPOLOGY |
| FREQUENCYCONVERTER | NOT_ALLOWED - TOPOLOGY |
| FUSE | NOT_ALLOWED - TOPOLOGY |
| GATEINPUTPIN | NOT_ALLOWED - ABSTRACT |
| GENERATINGUNIT | NOT_ALLOWED - ABSTRACT |
| GROUND | NOT_ALLOWED - TOPOLOGY |
| GROUNDDISCONNECTOR | NOT_ALLOWED - TOPOLOGY |
| JUMPER | NOT_ALLOWED - TOPOLOGY |
| JUNCTION | NOT_ALLOWED - TOPOLOGY |
| LIMIT | NOT_ALLOWED - ABSTRACT |
| LIMITSET | NOT_ALLOWED - ABSTRACT |
| LOADBREAKSWITCH | NOT_ALLOWED - TOPOLOGY |
| LOADGROUP | NOT_ALLOWED - ABSTRACT |
| MEASUREMENT | NOT_ALLOWED - ABSTRACT |
| POWERSYSTEMRESOURCE | NOT_ALLOWED - ABSTRACT |
| PROTECTEDSWITCH | NOT_ALLOWED - ABSTRACT |
| RECTIFIERINVERTER | NOT_ALLOWED - TOPOLOGY |
| REGULARINTERVALSCHEDULE | NOT_ALLOWED - ABSTRACT |
| REGULATINGCONDEQ | NOT_ALLOWED - ABSTRACT |
| SWITCH | NOT_ALLOWED - ABSTRACT |