ERCOT Operating Guides

- Table of Contents

- June 1, 2009

1.	Introduction	1-3

1.1	Document Purpose	1-3

1.2	Document Relationship	1-5

1.3	Process for Operating Guide Revision	1-6

1.4	Market Overview	1-17

1.5	Conformance to NERC Policies, Procedures, and Reliability Standards	1-19

1.6	Operating Definitions	1-22

1.7	Entity Definitions and Roles	1-24

1.7.1 ERCOT Control Area Authority	1-24

1.7.2 Qualified Scheduling Entities	1-24

1.7.3 Transmission Operator (TO)	1-24

1.7.4 Resource Entity	1-25

1.7.5 Load Serving Entities (LSE)	1-26

1.8	Operational Training	1-27

1.8.1 Operator Training Objectives	1-27

1.8.2 System Operator Training Requirements	1-27

1.8.3 ERCOT Operations Training Seminar	1-27

1.8.4 ERCOT Black Start Training	1-28

1.8.5 ERCOT Severe Weather Drill	1-28

1.8.6 Criteria For The Selection Of Operators	1-28

1.8.7 Training Practices	1-28

1.9	Document Revisions	1-30

2.	System Operations	2-5

2.1	Operational Duties	2-5

2.2	System Monitoring and Control	2-7

2.2.1 Overview	2-7

2.2.2 Security Criteria	2-8

2.2.3 Automatic Generation Control Systems	2-9

2.2.4 Automatic Voltage Regulators and Power System Stabilizers	2-11

2.2.5 Turbine Speed Governors	2-11

2.2.6 Performance/Disturbance/Compliance Analysis	2-12

2.2.7 Time Error and Time Synchronization	2-12

2.3	Dispatch Duties	2-14

2.3.1 Control Area Operator Authority	2-14

2.3.2 Dispatch Instruction Procedures	2-15

2.4	Scheduling	2-18

2.4.1 Day Ahead Scheduling	2-18

2.4.2 Adjustment Period Scheduling Process	2-20

2.4.3 Direct Current Tie Interconnection Day Ahead Scheduling Process	2-22

2.4.4 Temporary Deviations from Scheduling Procedures	2-23

2.4.5 Real-Time Schedules	2-23

2.5	Ancillary Services	2-31

2.5.1 ERCOT Responsibilities	2-31

2.5.2 Responsive Reserve	2-36

2.5.3 Non-Spinning Reserve Service (NSRS)	2-39

2.5.4 Replacement Reserve Service (RPRS)	2-40

2.5.5 Balancing Energy Service	2-41

2.6	Changes in System Status	2-44

2.6.1 Changes in Resource Status	2-44

2.6.2 Changes in Transmission Facility Status	2-44

2.7	Outage Coordination	2-45

2.7.1 ERCOT Control Area Authority Responsibilities	2-45

2.7.2 Forced Outages	2-45

2.7.3 Scheduled Outages	2-46

2.8	Congestion Management	2-48

2.8.1 Overview of ERCOT Coordinated Congestion Management	2-48

2.9	Requirements for Under-Frequency Relaying	2-50

2.9.1 Automatic Firm Load Shedding	2-50

2.9.2 Generators	2-51

2.10	System Voltage Profile	2-52

2.10.1 Introduction	2-52

2.10.2 Maintaining Voltage Profile	2-52

2.10.3 Special Consideration for Nuclear Power Plants	2-53

2.10.4 Reactive Considerations for Gas and Steam Turbine Power Plants	2-54

2.11	External Control Area Inter-Ties	2-55

2.11.1 Control Area Operations	2-55

2.11.2 Operation of DC Ties	2-55

2.12	Document Control	2-56

3.	Operational Interfaces	3-4

3.1	System Control Interfaces with ERCOT	3-4

3.1.1 Introduction	3-4

3.1.2 Compliance with Dispatch Instructions	3-4

3.1.3 Qualified Scheduling Entities	3-6

3.1.4 Power Generation Companies	3-11

3.1.5 Transmission and/or Distribution Service Providers	3-25

3.1.6 Responsibility For Equipment Ratings	3-28

3.2	Scheduling Interfaces with ERCOT	3-29

3.2.1 Scheduling-Related Duties of Qualified Scheduling Entities	3-29

3.2.2 Scheduling Process	3-31

3.2.3 Procurement of Replacement Reserve Service Resources	3-33

3.2.4 Procurement of Additional Ancillary Services	3-33

3.2.5 Direct Current Tie Interconnection Day Ahead Scheduling Process	3-33

3.2.6 Dynamic Schedules	3-34

3.2.7 Approval of the Use of Responsibility Transfer (RspT) Schedules	3-35

3.3	Document Control	3-38

4.	Emergency Operation	4-4

4.1	Introduction	4-4

4.2	Emergency Notifications	4-5

4.2.1 Operating Condition Notice	4-5

4.2.2 Advisory	4-6

4.2.3 Watch	4-7

4.2.4 Emergency Notice	4-9

4.3	Operation To Maintain Transmission System Security	4-11

4.3.1 Remedial Action Plans	4-13

4.4	Block Load Transfers between ERCOT and Non-ERCOT Control Areas	4-14

4.4.1 Introduction and General Information	4-15

4.4.2 BLTs to ERCOT	4-15

4.4.3 BLTs from ERCOT	4-16

4.5	Energy Emergency Alert (EEA)	4-17

4.5.1 General	4-20

4.5.2 Operating Procedures	4-20

4.5.3 Implementation	4-21

4.6	Black Start	4-26

4.6.1 Principles	4-27

4.6.2 Strategies	4-27

4.6.3 Priorities	4-28

4.6.4 Responsibilities	4-28

4.6.5 Emergency Back Up Communication Facilities Criteria	4-30

4.7	Document Control	4-31

Attachment 4A:  Detailed Black Start Information	4-33

4A.1 CONSIDERATIONS FOR SYSTEM RESTORATION	4-33

4A.2 ERCOT COORDINATION	4-37

4A.3 Considerations For Black Start Testing	4-38

4A.4 Criteria for ERCOT and Transmission Operator Black Start Plans	4-38

5	Planning	5-3

5.1	Planning Criteria	5-3

5.1.1 Introduction	5-3

5.1.2 Load Forecasts	5-4

5.1.3 Resource Capability	5-4

5.1.4 Transmission Reliability Testing	5-4

5.1.5 Reports Of Testing	5-6

5.1.6 System Modeling Information	5-6

5.1.7 ERCOT Clarifications and Definitions of NERC Planning Standards

Contingency Types C and D	5-12

5.2	Document Control	5-14

6	Reports and Forms	6-3

6.1	Reports	6-3

6.1.1 Disturbance Report	6-3

6.1.2 Relay Misoperation Report	6-4

6.2	Forms	6-5

6.2.1 Turbine Governor Speed Regulation Tests	6-5

6.2.2 Seasonal Unit Net Real Power Capability Verification	6-18

6.2.3 Biennial Unit Reactive Limits (Lead and Lag) Verification	6-20

6.2.4 Seasonal Hydro Responsive Reserve Net Capability Verification	6-24

6.2.5 Annual LaaR Telemetry Test	6-25

6.2.6 Biennial Test for LaaRs Providing Responsive Reserve Service	6-26

6.3	Document Control	6-31

7	Disturbance Monitoring and System Protection	7-3

7.1	Disturbance Monitoring Requirements	7-3

7.1.1 Introduction	7-3

7.1.2 Fault Recording Equipment	7-3

7.1.3 Dynamic Disturbance Recording Equipment	7-6

7.1.4 Equipment Reporting Requirements	7-6

7.1.5 Review Process	7-6

7.2	System Protective Relaying	7-7

7.2.1 Introduction	7-7

7.2.2 Design and Operating Requirements for ERCOT System Facilities	7-7

7.2.3 Performance Analysis Requirements for ERCOT System Facilities	7-10

7.2.4 Maintenance and Testing Requirements for ERCOT System Facilities	7-12

7.2.5 Requirements and Recommendations for ERCOT System Facilities	7-12

7.3	Document Control	7-23

8	Operational Metering and Communication	8-3

8.1	Operational Metering	8-3

8.1.1 ERCOT Interface RTUs	8-4

8.1.2 ERCOT ICCP Interface	8-4

8.1.3 Validation of Real Time Signals with Settlement Metering for Resources	8-4

8.1.4 Data from ERCOT to QSE’s	8-5

8.1.5 Data From ERCOT to TDSP	8-5

8.1.6 Data from QSE/TDSP to ERCOT	8-5

8.1.7 TDSP/QSE Metering Restoration	8-8

8.1.8 QSE and TDSP Data Acquisition	8-8

8.2	Calibration and Testing	8-8

8.2.1 Responsibility	8-8

8.2.2 Notification	8-9

8.2.3 Test Equipment	8-9

8.2.4 Disputes	8-9

8.2.5 Calibration Testing	8-9

8.2.6 Exchange of Information	8-9

8.2.7 Documentation	8-9

8.2.8 Operator One-line Displays	8-11

8.2.9 Notification of Changes	8-11

8.3	Communications	8-12

8.3.1 ERCOT WAN	8-12

8.3.2 ERCOT Responsibilities	8-15

8.3.3 QSE and TDSP Responsibilities	8-15

8.3.4 TDSP and QSE Supplied Communications	8-17

8.3.5 Maintenance and Restoration	8-17

8.4	Document Control	8-19

Attachment 8A:  ERCOT Data Sets	8-21