## Slide 1: Critique of Proposal to Designate SAPS-Shrew as CRE
Shams Siddiqi, Ph.D.
Crescent Power, Inc.
(512) 263-0653
shams@crescentpower.net
June 4, 2009
Notes: <number>

## Slide 2: Considerations for CRE Selection
June 4, 2009
<number>
Is the Element sufficiently “parallel” (i.e. has similar shift factors for all zones) to the CSC?
Do too many Resources get the “wrong” price signal (i.e. cluster to the other zone and are Boundary Generation Resources) when resolving congestion on the CRE using zonal Balancing Energy Service (BES)?
Does resolving congestion on the CRE using zonal BES create sufficient inefficiencies that would negate the benefit of using market-based zonal solutions over optimized local solutions?
Does the amount of CRE overload relief justify the amount of zonal BES deployment needed to resolve the CRE overload?

## Slide 3: Protocols Test for Parallelism
June 4, 2009
<number>
Section 7.2.3 CRE test: Yz = a (Xz) + bz
Max bz was originally proposed at 0.05 in Nov 2001 (see PRR300), but Stakeholder wanted TAC to set this value (not to exceed 0.2) and that never happened
With CSC PTDFs of 0.4, the 0.05 cutoff implies that if SPD calculates a zonal BES deployment to be relieving CRE congestion by 10%, the maximum that deployment could actually be congesting the CRE is 15%
PRR300 was written when CSCs and CREs were all 345kV lines – so it didn’t matter much which was Y vs. X; but with 138kV CRE lines, the Y must be the CSC values and X the CRE values for bz values to have any meaning (Luminant, EON, and I naturally did this and got bz values around 0.2 for SAPS-Menard; whereas ERCOT did the opposite resulting in meaningless bz values from ERCOT)
With bz value of 0.21, SAPS-Menard exceeds any reasonable bz limit of around 0.05 by 400%

## Slide 4: Sample bz Test Results
June 4, 2009
<number>
<number>
0.21
0.17
0.21
Average: 0.14
DFW local lines
0.15
Average excluding outlier: 0.024
Current CREs
One outlier (local 138 kV): 0.068
Badly Fails bz Test
Fails bz Test
San Angelo to Menard
Current CREs

## Slide 5: Why bz Test Matters
June 4, 2009
<number>
SAPS-Menard as CRE to W-N CSC: a=4.78, bz=0.21, R2=0.44
Correlation Coefficient R2=1 (=Explained variation/Total variation, i.e. fraction of total variation that can be explained); R2 values of less than 0.81 represent lack of correlation
SAPS-Menard S-W deployment impact is 200% of N-W impact whereas CSC S-W impact is 90% of N-W impact
ERCOT will deploy more than twice as much BES in N if CRE than local if not CRE
Zonal methods lead to inefficient results
R2=0.44 also confirms the lack of correlation

## Slide 6: Zonal v. Local Solution for CRE
June 4, 2009
<number>
There are CREs where only a few resources can efficiently relieve congestion (due to high impact) on those CREs
Resolving congestion on those CREs using zonal BES where resources are dispatch using zonal average shift factors is likely to result in many more resources being inefficiently dispatched
This creates inefficiencies that may negate the benefits of using market-based zonal solutions over optimized local solutions
So the question is: What is the limit on the concentration of capacity able to resolve congestion on the candidate CRE above which inefficiencies of zonal dispatch outweigh the benefits of using market-based zonal solutions?

## Slide 7: Concentration Limit for CREs
June 4, 2009
<number>
Concentration Limit: Movable capacity of 200% of the element’s rating should not have average PTDF greater than twice the zonal average PTDF, both with respect to zonal average shift factor on the opposite terminal of the element
E.g. for a candidate CRE rated at 1000MW with CRE-related terminal zone average shift fact difference of 0.2, the most effective 2000MW on either side of the constraint should not have an impact greater than 0.4 since that capacity can resolve 800MW of overload on the element twice as effectively as zonal BES
[Hope to have estimates of the increased amount of wind curtailment and increased amount of BES Up if SAPS-Shrew becomes a CRE]

## Slide 8: Concentration Limit for CREs
June 4, 2009
<number>

## Slide 9: What are Implications of CRE?
June 4, 2009
<number>
Assume that SAPS-Shrew is parallel, creates no boundary generation, and doesn’t have a more efficient local solution (all of which are false):
What does it mean to have a CRE with inter-zonal PTDF of 0.029 when the CSC PTDF is 0.39?
To relieve 1MW overload on SAPS-Shrew requires 13MW of W-N CSC flow reduction
With a CSC Shadow Price Cap of $5,600/MW/hr, it means ERCOT will deploy BES to resolve post-345kV double contingency overload on SAPS-Shrew up to a cost of $72,800/hr for each 1MW of overload
The Shadow Price on SAPS-Shrew reflects the cost the system (Consumers) are paying for relieving each MW of overload
This aspect is particularly important for this constraint since it’s likely that this constraint will bind often

## Slide 10: PTDF Cutoff Value
June 4, 2009
<number>
In Nodal, the Shadow Price Cap for such constraints is proposed to be around $4000/MW/hr (reasonable cap)
Protecting a few MWs of load curtailment in anticipation of the very low probability event of 345kV double circuit outage at a cost of over $10,000/MW/hr makes no sense – that load would gladly get a fraction of that cost and forego the protection against the very low probability event
In managing the constraint locally, ERCOT can enforce the $4000/MW/hr cap in its local deployments; whereas, making it a CRE automatically results in a Shadow Price Cap of about $72,800/MW/hr for that constraint.
The PTDF cutoff somewhat tries to limit the Shadow Price – this cutoff should be at least 0.05 if not much higher (0.05 translates to $44,800/MW/hr cap – still too high)
PJM also uses a 0.05 PTDF cutoff for post-contingency binding elements (good criteria to use for local deployment as well)

## Slide 11: CRE Test Results for SAPS-Menard
June 4, 2009
<number>
Badly fails bz (Parallel) Test: bz=0.21 (cutoff 0.05), R2=0.44 (minimum 0.81- terrible fit)
Badly fails PTDF (Impact) Test: PTDF=0.029 (cutoff 0.05)
Badly fails Concentration Limit: Ratio=2.86 (limit 2.0)
Minimize Local Relief Costs: Issuing OOMC to Ferguson thereby reducing OOME Down to wind resources would minimize uplift costs

## Slide 12: Recommendation: Reject CRE
June 4, 2009
<number>
SAPS-Menard fails almost all CRE tests – if this is still made a CRE, then the CRE tests are meaningless and CRE selection becomes merely a political exercise (on what basis can we reject future CRE nominations by ERCOT?)
The system operated even with this line open – so there may be other solutions that need to be explored with the reconfigured system around this constraint
Recommendation: Reject CRE and let Market Participants and ERCOT try to resolve many of the issues outlined in this presentation
If, after further analysis and experience operating under the changed transmission system, ERCOT still determines that it would like this constraint to be a CRE, they are free to bring it back to TAC with better information and more operational history
Notes: <number>