## Slide 1: San Angelo Power Station - Menard
May 2009
ERCOT Analysis

## Slide 2: Changes to Power Flow Study to Examine Reconfiguration
Add an additional bus (#6489) at SAPS
Add zero impedance branches between the two original SAPS busses and the new SAPS bus
Re-terminate the line from Menard into the new SAPS bus #6489
Increase the ratings on the Menard to SAPS 138 kV line to 117 MVA
Add an additional bus (#6443) at Red Creek
Add a zero impedance branch between the original Red Creek bus and the new Red Creek bus
Re-terminate the line from Ballinger into the new Red Creek bus
Re-terminate the line from SAPS into the new Red Creek bus

## Slide 3: Overview of SAPs-Menard Reconfiguration

## Slide 4: Current SAPS one line

## Slide 5: SAPS change summary
Addition of breaker 10335 at SAPS, which will be normally closed
Open breakers 4590 and 6120 at SAPS to isolate the SAPS south bus from the north bus
Live Oaks, Menard, and Red Creek 138 kV lines connected to the SAPS south bus with the SAPS 138/69 kV auto
Twin Buttes, Concho, and College Hills West 138 kV lines connected to SAPS north bus
Open breaker 3615 to SAPS 138/69 kV auto under high load/wind conditions to isolate the 69 kV system and avoid contingency overloads

## Slide 6: Current Red Creek one line

## Slide 7: Red Creek change summary
Open breakers 5970, 6745, 5945 and 6720 at Red Creek to isolate Red Creek south bus from north bus
Ballinger and Ben Ficklen/SAPS 138 kV lines connected to the south bus
Both 345/138 kV autos, Nicole, North Angelo, and Concho 138 kV lines connected to north bus

## Slide 8: Current Menard one line

## Slide 9: Menard change summary
De-energize and remove 69 kV line section between Menard breaker 2900 and Yellow Jacket
Reconnect the Eden to Yellow Jacket 69 kV line into Yellow Jacket breakers 7355 and 5995 through moab 6237
Tap SAPS to Menard 138 kV line just west of Menard (Shrew) with a new 138 kV line section from Shrew to Yellow Jacket through moab 7197
Energize Yellow Jacket #2 138/69 kV auto by closing Yellow Jacket breakers 1475, 9210 and 9250

## Slide 10: SAPS Before and After
existing
new
Notes: Add breaker to supply SAPS-Menard line from SAPS 4A(South Bus) and add new tap at SHREW which connects Yellow Jacket and Eden. Note Phase shifter is not in service.
Note the line from BENF is not new but since the line now goes to the new SARC 4B buss it appears to be new in this drawing.
<number>

## Slide 11: Red Creek Before and After
existing
new
Notes: New buss SARC 4B separates BALG to SAPS from the 345 KV at SARC.
<number>

## Slide 12: The resulting configuration provides:
Isolation of the SAPS to Menard 138 kV line from the 345 kV system at Red Creek and Twin Buttes
Retention of the 138 kV sources at Ballinger (bypassing Red Creek) and Sonora to provide voltage support of Menard/Mason area
Addition of second 138/69 kV auto in the Menard area.

## Slide 13: General Info
The reconfigured San Angelo Power Station (SAPS) to Menard 138kV line returned to service on May 15, 2009.
Shrew Tap added between SAPS and Menard.
Following is ERCOT’s analysis for this line with the reconfiguration and evaluation as a CRE

## Slide 14: Operations Case Facts
58,000 load case was chosen to do the study.
Gen-Plan: July 14th 2008 for the HE 1600
No significant Basecase violations (Thermal & Voltage)
Wind Generation: 2300 MW

## Slide 15: W – N Transfer Limit
Loss of DCKT Long Creek – Sweet Water Cogen & Abilene Mulberry Creek 345 kV overloads SAPS – Shrew 138 kV line with a W – N transfer limit of 660 MW.
Opening the tie between SAPS 4A & SAPS 4B relieves the SAPS – Shrew line by 10 %.
W – N transfer limit can be increased to 720 MW by doing this switching action.
Alternative Switching: Opening Schkade – Twin Butte relieves the SAPS – Shrew line by 8 %
Notes: ERCOT has proposed the PCAP as an alternative in case the bus needs to be tied together temporarily
<number>

## Slide 16: Power Transfer Distribution Factors
From Bus Number | From Bus Name | To Bus Number | To Bus Name | % PTDF From | % PTDF To | Nom kV (Max)
3048 | SHREW | 6083 | SAPS 4D | -3.08 | 3.08 | 138
2711 | MENA | 3048 | SHREW | -2.79 | 2.79 | 138

## Slide 17
Bus Name | P Sensitivity
HHOLLOW2 | 0.040859
HHOLLOW4 | 0.040859
BLUF_CRK | 0.040859
BUFF_GAP | 0.040859
BUFF_GAP | 0.040859
HHOLLOW3 | 0.040859
BUFF_GAP | 0.040859
H_HOLLOW | 0.040859
PBSES | 0.040738
PBSES | 0.040738
PB2SES | 0.040738
PB2SES | 0.040738
Generator Shift Factors For SAPS – Shrew 138 kV
Bus Name | P Sensitivity
PB2SES | 0.040738
PB2SES | 0.040738
PB2SES | 0.040738
KUNITZ | 0.040686
DELAWARE | 0.040686
NWF | 0.040585
SWEC | 0.040203
OWF | 0.040019
OECCS | 0.039967
OECCS | 0.039967
OECCS | 0.039967

## Slide 18: Generator Shift Factors For SAPS – Shrew 138 kV (cont’d)
Bus Name | P Sensitivity
FLCNS | 0.039239
FLCNS | 0.039239
FLCNS | 0.039239
BULLCRK | 0.039121
BULLCRK | 0.039121
PC_SOUTH | 0.03906
ELB | 0.03906
PC_NORTH | 0.03906
MGSES | 0.038955
MGSES | 0.038955
MGSES | 0.038955
MGSES | 0.038955
Bus Name | P Sensitivity
OECCS | 0.039967
OECCS | 0.039967
OECCS | 0.039967
QALSW | 0.039941
QALSW | 0.039941
QALSW | 0.039941
QALSW | 0.039941
QALSW | 0.039941
QALSW | 0.039941
MCDLD | 0.03987
MCDLD | 0.03987

## Slide 19: Generator Shift Factors For SAPS – Shrew 138 kV (cont’d)
Bus Name | P Sensitivity
MGSES | 0.038955
MGSES | 0.038955
MGSES | 0.038955
MGSES | 0.038819
ENAS | 0.038787
STWF | 0.038759
TRENT | 0.038759
CSEC | 0.038636
BRAZ_WND | 0.038596
BRAZ_WND | 0.038596
RDCANYON | 0.038264
SWEETWND | 0.03717
Bus Name | P Sensitivity
SWEETWN2 | 0.03717
SWEETWN2 | 0.03717
SWEETWN4 | 0.03717
SWEETWN4 | 0.03717
SWEETWN4 | 0.03717
SWEETWN3 | 0.03717
MWEC | 0.036807
INDL | 0.036712
PYR | 0.036712
TKWSW1 | 0.036712
TKWSW | 0.036712

## Slide 20: Generator Shift Factors For SAPS – Shrew 138 kV (cont’d)
Bus Name | P Sensitivity
FERGUS | -0.05462
WIRTZ | -0.05124
WIRTZ | -0.05124
MARBFA | -0.04662
MARBFA | -0.04662
BUCHAN | -0.04358
BUCHAN | -0.04358
BUCHAN | -0.04358
Bus Name | P Sensitivity
SWCOG | 0.035783
SWCOG | 0.035783
SWCOG | 0.035783
SWCOG | 0.035783
WEC | 0.034912
LNCRK2 | 0.031079
LNCRK2 | 0.031079
LNCRK | 0.031079
INKSDA | -0.0615

## Slide 21: CRE Analysis – Protocol Section 7.2.3
Analyzing the reconfiguration for the SAPS to Menard line the CRE test results are as follows:
  Generation changing zones: 800.999988 Max b: .02992
  Criteria:
  Less than 1500MWs changed : Met by SAPS-Shrew
  Least Squares Fit < 0.2 : Met by SAPS-Shrew