## Instructions and notes
USER NOTES:
* Enter data in the "white" cells only. Grayed cells have formulas or are used for calculations
* This workbook is set-up to test for 25 CREs
* This workbook is set-up to handle 1,000 generators
* There should be no blank rows or columns in the data. i.e. do not fill in column J on the Base GSFs worksheet
then skip column K and begin entering data in column L. The data should be contiguous.
* If a user changes the column order for GSF output on the pw CUT AND PASTE worksheet, the cut & paste macro
may not copy the correct GSFs to the base GSFs worksheet.
Make sure that the bus mapping in range AL5:Anxxxx is correct for the bus numbers of the study case
otherwise you will get some #N/A in the vlookups and give data errors.
IF movable gens only are desired for the analysis
Step A: | Cust and paste the Generator Sensitivity data from Power World into the 'pw CUT and Paste' worksheet, cell B3 (see notes about column order)
Step B: | Make sure that the 'Movable Gens excluded list' in cells R5:U164 is a good list
Step C: | Click the big button in cells Q1:Q5
Step D: | Check the warnings and flags in cells R2:V2 and AB2:AF2 to make sure that the data is ok before transferring as directed in the steps below
Step 1: | Enter the Bus number, Bus name unit ID, area Name, and Generator MW value in columns A:E of the Base GSFs worksheet.
Step 2: | Enter GSFs for the CSCs and CREs in columns F:AH on the Base GSFs worksheet.
There are currently 4 CSCs that a CRE can be checked against.
Aside for Step 2:
There is a short macro that can be executed for the CREs that will make cutting and pasting from PowerWorld much quicker.
It can be executed from either the Base GSFs worksheet or the pw CUT AND PASTE worksheet.
Step 3: | Enter the CSC or CRE headings in row 2 of the Base GSFs worksheet. These heading titles are used to count the number
of CREs that will be computed.
Step 4: | Enter the CSCs that each CRE will be checked against in cells J1016:AH1016 on the CRE computation worksheet.
Step 5: | click on the "Compute least squares fit for eth CREs associated with the CSCs" button in cells H1040:I1045 on
the CRE computation worksheet.
Step 6: | The CRE output will be given in row 1043 on the CRE computation worksheet.
A red which indicates "failed CRE test" will mean that the CRE failed the test
A green which indicates "passed CRE test" will mean that the CRE passed the test for the given CSC

## Base GSFs
Shift Factors with 2406 Norwood 345 kV as reference bus | [6 empty] | Important Note: The complete shift factors need to be entered for all circuits, i.e. if it is a
double circuit line then either use an interface defined for both lines or double the GSF values
[5 empty] | CSC 1 | CSC 2 | CSC 3 | CSC4 | CSC 5 | CRE 1 | CRE 2 | CRE 3 | CRE 4 | CRE 5 | CRE 6 | CRE 7 | CRE 8 | CRE 9 | CRE 10 | CRE 11 | CRE 12 | CRE 13 | CRE 14 | CRE 15 | CRE 16 | CRE 17 | CRE 18 | CRE 19 | CRE 20 | CRE 21 | CRE 22 | CRE 23 | CRE 24 | CRE 25
Number | Name | ID | Area Name | Gen MW | CSC 1: 44645 Sngltn to 45500 THW, 44645 Sngltn to 44500 OBrien (CSC#1 N-H); CSC 2: 3409 LkCrk to 3414 Tmplsw, 3405 Trdnghse to 3412 Tmpl PecCrk (CSC#2 N-S); double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 6230 AbilMulCrk to 1435 LngCrk, 1420 Swtwtr to 1439 LngCrk (CSC#3 W-N); double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 3414 Tmplsw to 3409 LkCrk, 3412 Tmpl PecCrk to 3405 Trdnghse (CSC#4 S-N); double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 1435 LngCrk to 6230 AbilMulCrk, 1439 LngCrk to 1420 Swtwtr (CSC#5 N-W); double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: Gibbons Creek - Singleton #1 (967 - 44645); double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: Gibbons Creek - Singleton # 2 (967 - 44645); double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: Jewett - Singleton # 1 (3390 - 44645); double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: Jewett - Singleton # 2 (3391 - 44645); double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: Kuykendahl - King # 1 (45971 - 40900); double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: Kuykendahl - King # 2 (45972 - 40900); double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: Roans Prairie - Kuykendahl (40600 - 45972); double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: Tomball - Kuykendahl (46500 - 45971); double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: Singleton - Roans Prairie (44645 - 40600); double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: Singleton - Tomball (44645 - 46500)
238 | BOSQUESW505 | 1 | NORTH | 255 | CSC 1: -0.023279; CSC 2: 0.060896; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.013407; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.060896; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.013407; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.015042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.015042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.00762; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.027523; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.010367; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.018507; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.018507; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.010367; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.018507; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.02344
239 | BOSQUESW502 | 1 | NORTH | 149 | CSC 1: -0.023279; CSC 2: 0.060896; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.013407; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.060896; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.013407; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.015042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.015042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.00762; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.027523; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.010367; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.018507; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.018507; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.010367; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.018507; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.02344
244 | WHITNYDM01 | 1 | NORTH | 15 | CSC 1: -0.017932; CSC 2: -0.003746; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.014743; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003746; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.014743; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.010658; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.010658; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008215; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.020704; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.007993; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.014255; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.014255; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.007993; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.014255; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.018049
245 | WHITNYDM02 | 2 | NORTH | 15 | CSC 1: -0.017932; CSC 2: -0.003746; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.014743; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003746; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.014743; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.010658; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.010658; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008215; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.020704; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.007993; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.014255; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.014255; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.007993; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.014255; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.018049
247 | BOSQUESW501 | 2 | NORTH | 156 | CSC 1: -0.023279; CSC 2: 0.060896; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.013407; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.060896; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.013407; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.015042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.015042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.00762; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.027523; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.010367; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.018507; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.018507; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.010367; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.018507; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.02344
251 | BOSQUESW803 | 2 | NORTH | 150 | CSC 1: -0.021117; CSC 2: -0.002046; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.015483; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.002046; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.015483; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.013097; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.013097; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008943; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.024027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.009411; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.016788; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.016788; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.009411; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.016788; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.021258
253 | BOSQUESW804 | 2 | NORTH | 80 | CSC 1: -0.021117; CSC 2: -0.002046; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.015483; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.002046; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.015483; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.013097; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.013097; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008943; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.024027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.009411; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.016788; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.016788; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.009411; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.016788; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.021258
332 | RWMILLER01 | 1 | NORTH | 73 | CSC 1: -0.006814; CSC 2: -0.011535; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018279; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.011535; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018279; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.004302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.004302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.003807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.006643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.003075; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.003075; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.006825
333 | RWMILLER02 | 2 | NORTH | 119 | CSC 1: -0.006814; CSC 2: -0.011535; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018279; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.011535; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018279; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.004302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.004302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.003807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.006643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.003075; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.003075; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.006825
334 | RWMILLER03 | 3 | NORTH | 208 | CSC 1: -0.006814; CSC 2: -0.011535; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018279; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.011535; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018279; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.004302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.004302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.003807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.006643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.003075; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.003075; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.006825
335 | RWMILLER04 | 4 | NORTH | 102 | CSC 1: -0.006814; CSC 2: -0.011535; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018279; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.011535; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018279; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.004302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.004302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.003807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.006643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.003075; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.003075; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.006825
336 | RWMILLER05 | 5 | NORTH | 101 | CSC 1: -0.006814; CSC 2: -0.011535; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018279; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.011535; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018279; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.004302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.004302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.003807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.006643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.003075; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.003075; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.005415; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.006825
344 | MRSSHPRD | 1 | NORTH | 0 | CSC 1: -0.005972; CSC 2: -0.012455; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.013791; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.012455; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.013791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003764; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003764; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.003655; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.005502; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002714; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.004746; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.004746; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002714; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.004746; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.005966
345 | MRSSHPRD01 | 2 | NORTH | 0 | CSC 1: -0.005972; CSC 2: -0.012455; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.013791; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.012455; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.013791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003764; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003764; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.003655; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.005502; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002714; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.004746; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.004746; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002714; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.004746; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.005966
366 | JNSNCNTY802 | 1 | NORTH | 168 | CSC 1: -0.005616; CSC 2: 0.000237; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.009554; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.000237; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.009554; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002311; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00584; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002518; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.004464; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.004464; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002518; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.004464; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.005639
367 | JNSNCNTY802 | 2 | NORTH | 90 | CSC 1: -0.005616; CSC 2: 0.000237; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.009554; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.000237; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.009554; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002311; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00584; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002518; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.004464; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.004464; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002518; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.004464; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.005639
503 | NTHTEXAS01 | 1 | NORTH | 0 | CSC 1: -0.005008; CSC 2: -0.008563; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.006169; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.008563; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.006169; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002835; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.004779; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002265; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.00398; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.00398; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002265; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.00398; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.005013
504 | NTHTEXAS02 | 2 | NORTH | 14.4 | CSC 1: -0.005008; CSC 2: -0.008563; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.006169; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.008563; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.006169; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002835; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.004779; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002265; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.00398; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.00398; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002265; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.00398; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.005013
505 | NTHTEXAS03 | 3 | NORTH | 30.4 | CSC 1: -0.005008; CSC 2: -0.008563; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.006169; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.008563; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.006169; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002835; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.004779; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002265; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.00398; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.00398; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002265; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.00398; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.005013
580 | JCKCNTY801 | 1 | NORTH | 288 | CSC 1: -0.00372; CSC 2: -0.007295; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.000202; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.007295; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.000202; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002396; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002396; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002204; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.003397; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001689; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.002956; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.002956; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001689; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.002956; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.003718
581 | JCKCNTY802 | 2 | NORTH | 147 | CSC 1: -0.00372; CSC 2: -0.007295; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.000202; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.007295; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.000202; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002396; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002396; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002204; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.003397; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001689; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.002956; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.002956; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001689; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.002956; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.003718
582 | JCKCNTY803 | 3 | NORTH | 147 | CSC 1: -0.00372; CSC 2: -0.007295; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.000202; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.007295; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.000202; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002396; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002396; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002204; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.003397; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001689; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.002956; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.002956; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001689; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.002956; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.003718
728 | WOLFRIDGE801 | 1 | NORTH | 11.2 | CSC 1: -0.002276; CSC 2: -0.00679; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.002589; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.00679; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.002589; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00146; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00146; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.00154; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.001896; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001039; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.001809; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.001809; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001039; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.001809; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.00227
837 | NEWMAN_G5 | 1 | NORTH | 0 | CSC 1: 0.002149; CSC 2: -0.006627; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.000797; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006627; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.000797; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001496; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001496; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000417; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002608; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000961; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001708; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001708; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000961; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001708; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.00216
842 | OLINGER_G1 | 1 | NORTH | 55.4 | CSC 1: 0.002131; CSC 2: -0.006586; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.000912; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006586; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.000912; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000437; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002632; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000953; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000953; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.002143
843 | OLINGER_G2 | 1 | NORTH | 76.2 | CSC 1: 0.002131; CSC 2: -0.006586; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.000912; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006586; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.000912; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000437; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002632; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000953; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000953; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.002143
844 | OLINGER_G3 | 1 | NORTH | 103.9 | CSC 1: 0.002131; CSC 2: -0.006586; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.000912; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006586; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.000912; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000437; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002632; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000953; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000953; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.002143
845 | OLINGER_G4 | 1 | NORTH | 51.9 | CSC 1: 0.002131; CSC 2: -0.006586; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.000912; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006586; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.000912; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000437; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002632; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000953; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000953; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.002143
923 | SPENCER_G4 | 1 | NORTH | 48 | CSC 1: -0.0013; CSC 2: -0.005233; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.009639; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.005233; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.009639; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.000842; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.000842; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.00098; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.000963; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.000596; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.001033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.001033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.000596; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.001033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.001294
924 | SPENCER_G5 | 1 | NORTH | 52 | CSC 1: -0.0013; CSC 2: -0.005233; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.009639; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.005233; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.009639; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.000842; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.000842; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.00098; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.000963; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.000596; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.001033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.001033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.000596; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.001033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.001294
948 | STEAM1 | 1 | NORTH | 0 | CSC 1: 0.002274; CSC 2: -0.006819; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.000769; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006819; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.000769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001524; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001524; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000485; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.002285
949 | STEAM2 | 1 | NORTH | 26 | CSC 1: 0.002273; CSC 2: -0.006818; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.000769; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006818; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.000769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001524; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001524; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000485; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002832; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.002285
950 | STEAM3 | 1 | NORTH | 41 | CSC 1: 0.002273; CSC 2: -0.006818; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.000769; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006818; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.000769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001524; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001524; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000485; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002832; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.002285
1002 | PBCTAGE_1G | A | WEST | 64 | CSC 1: -0.013225; CSC 2: -0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009521; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011345; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.013147
1003 | PBCTBGE_2G | B | WEST | 65 | CSC 1: -0.013225; CSC 2: -0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009521; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011345; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.013147
1004 | PBCTCGE_3G | C | WEST | 62 | CSC 1: -0.013225; CSC 2: -0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009521; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011345; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.013147
1005 | PBCTDGE_4G | D | WEST | 65 | CSC 1: -0.013225; CSC 2: -0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009521; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011345; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.013147
1006 | PBCTEGE_5G | E | WEST | 65 | CSC 1: -0.013225; CSC 2: -0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009521; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011345; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.013147
1007 | PB5GEN_6G | 5 | WEST | 91.2 | CSC 1: -0.013225; CSC 2: -0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009521; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011345; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.013147
1008 | PB6GEN_7G | 6 | WEST | 515 | CSC 1: -0.013225; CSC 2: -0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.037103; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37879; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.008006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009521; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011345; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.006083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.010505; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.013147
1037 | MORGAN5G_5G | 5 | WEST | 137 | CSC 1: -0.011672; CSC 2: -0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008269; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01009; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011615
1039 | MRGNAG_1G | A | WEST | 69 | CSC 1: -0.011672; CSC 2: -0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008269; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01009; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011615
1040 | MRGNBG_2G | B | WEST | 70 | CSC 1: -0.011672; CSC 2: -0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008269; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01009; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011615
1041 | MRGNCG_3G | C | WEST | 69 | CSC 1: -0.011672; CSC 2: -0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008269; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01009; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011615
1042 | MRGNDG_4G | D | WEST | 68 | CSC 1: -0.011672; CSC 2: -0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008269; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01009; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011615
1043 | MRGNEG_5G | E | WEST | 0 | CSC 1: -0.011672; CSC 2: -0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008269; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01009; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011615
1044 | MRGNFG_6G | F | WEST | 0 | CSC 1: -0.011672; CSC 2: -0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.3791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.0071; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008269; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01009; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011615
1045 | CALENG1G_1G | 1 | WEST | 73.4 | CSC 1: -0.011867; CSC 2: -0.033043; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38629; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.033043; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38629; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007214; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007214; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008431; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01024; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005448; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009427; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009427; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005448; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009427; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011806
1046 | CALENG2G_2G | 2 | WEST | 73.4 | CSC 1: -0.011867; CSC 2: -0.033043; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38629; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.033043; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38629; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007214; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007214; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008431; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01024; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005448; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009427; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009427; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005448; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009427; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011806
1047 | CALENG3G_3G | 3 | WEST | 70.4 | CSC 1: -0.011867; CSC 2: -0.033043; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38629; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.033043; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38629; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007214; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007214; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008431; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01024; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005448; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009427; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009427; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005448; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009427; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011806
1058 | LONGSHORE_5 | 1 | WEST | 30 | CSC 1: -0.011723; CSC 2: -0.03261; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38724; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.03261; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38724; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00713; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00713; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010123; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005381; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005381; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011664
1058 | LONGSHORE_5 | 2 | WEST | 44 | CSC 1: -0.011723; CSC 2: -0.03261; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38724; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.03261; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38724; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00713; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00713; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010123; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005381; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005381; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011664
1061 | CIELOGEN_1G | 1 | WEST | 19.8 | CSC 1: -0.011608; CSC 2: -0.032298; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.36395; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032298; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.36395; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007062; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007062; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008213; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010043; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005325; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005325; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011552
1062 | CIELOGEN_2G | 1 | WEST | 12.2 | CSC 1: -0.011608; CSC 2: -0.032298; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.36395; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032298; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.36395; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007062; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007062; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008213; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010043; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005325; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005325; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011552
1068 | SCURRYCW_1G | 1 | WEST | 28.2 | CSC 1: -0.011627; CSC 2: -0.032357; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.36456; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032357; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.36456; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008229; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010058; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005334; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009237; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009237; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005334; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009237; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011571
1073 | SCURRYCW_2G | 2 | WEST | 24 | CSC 1: -0.011627; CSC 2: -0.032357; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.36456; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032357; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.36456; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008229; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010058; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005334; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009237; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009237; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005334; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009237; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011571
1326 | STANTONW_8 | 1 | WEST | 20.1 | CSC 1: -0.012529; CSC 2: -0.035096; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37833; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.035096; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.0076; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.0076; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008959; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010785; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005757; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009953; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009953; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005757; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009953; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012461
1327 | WILDHRSE_1G | 1 | WEST | 0 | CSC 1: -0.012171; CSC 2: -0.034078; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37418; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034078; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37418; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007391; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007391; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008667; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010499; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005588; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009669; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009669; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005588; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009669; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012109
1328 | OCOTILLO_1G | 1 | WEST | 11.6 | CSC 1: -0.012451; CSC 2: -0.034877; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37672; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034877; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37672; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007554; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007554; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008894; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010723; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.00572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009891; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009891; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.00572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009891; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012384
1333 | MCDDONAL_8 | 1 | WEST | 42.8 | CSC 1: -0.012325; CSC 2: -0.034505; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37667; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034505; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37667; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007481; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007481; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008792; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010621; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.00566; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.00566; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.01226
1343 | TRENTIPP_8 | 1 | WEST | 30 | CSC 1: -0.011742; CSC 2: -0.033015; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.35037; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.033015; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.35037; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00714; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00714; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008275; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010207; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005381; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009329; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009329; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005381; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009329; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011692
1349 | WESTXWIN_1G | 1 | WEST | 1.3 | CSC 1: -0.013476; CSC 2: -0.038651; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.36538; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.038651; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.36538; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00815; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00815; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009698; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011588; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.00619; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.010705; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.010705; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.00619; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.010705; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.013405
1350 | NWPWRG1_1G | 1 | WEST | 6.9 | CSC 1: -0.013476; CSC 2: -0.038651; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.36538; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.038651; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.36538; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00815; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00815; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009698; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011588; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.00619; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.010705; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.010705; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.00619; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.010705; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.013405
1354 | AEPWIND_8 | 1 | WEST | 20.2 | CSC 1: -0.011742; CSC 2: -0.033015; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.35037; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.033015; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.35037; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00714; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00714; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008275; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010207; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005381; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009329; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009329; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005381; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009329; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011692
1360 | GUNSIGHT_8 | 1 | WEST | 0 | CSC 1: -0.012148; CSC 2: -0.034012; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37305; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034012; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37305; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007377; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007377; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008648; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010481; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.00965; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.00965; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.00965; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012086
1416 | SWETWATR_1G | 1 | WEST | 0 | CSC 1: -0.010509; CSC 2: -0.028652; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.48409; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.028652; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.48409; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006422; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006422; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007361; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.009113; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004819; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004819; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010461
1417 | SWETWATR_2G | 2 | WEST | 0 | CSC 1: -0.010509; CSC 2: -0.028652; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.48409; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.028652; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.48409; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006422; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006422; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007361; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.009113; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004819; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004819; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010461
1418 | SWETWATR_3G | 3 | WEST | 0 | CSC 1: -0.010509; CSC 2: -0.028652; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.48409; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.028652; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.48409; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006422; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006422; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007361; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.009113; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004819; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004819; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010461
1419 | SWETWATR_4G | 4 | WEST | 0 | CSC 1: -0.010509; CSC 2: -0.028652; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.48409; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.028652; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.48409; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006422; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006422; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007361; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.009113; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004819; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004819; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010461
1432 | GRHAMSES_2G | 2 | NORTH | 366 | CSC 1: -0.006329; CSC 2: -0.01458; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.085492; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.01458; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.085492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003983; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003983; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.004102; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.005598; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002891; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.005028; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.005028; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002891; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.005028; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.006309
1433 | GRHAMSES_1G | 1 | NORTH | 242 | CSC 1: -0.00693; CSC 2: -0.016209; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.00425; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.016209; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.00425; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.004331; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.004331; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.004475; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.006213; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.00316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.005506; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.005506; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.00316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.005506; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.006913
1437 | MESQUITW_1G | 1 | NORTH | 40 | CSC 1: -0.008939; CSC 2: -0.023451; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.36731; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.023451; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.36731; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.005506; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.005506; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.006132; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.0078; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004093; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.007102; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.007102; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004093; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.007102; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.008903
1438 | MESQUITW_2G | 1 | NORTH | 23.6 | CSC 1: -0.008936; CSC 2: -0.023439; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.36687; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.023439; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.36687; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.005504; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.005504; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.006129; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.007797; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004092; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.007099; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.007099; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004092; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.007099; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.008899
1442 | COKFIELD_5 | 1 | NORTH | 16.5 | CSC 1: -0.00831; CSC 2: -0.021313; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.29934; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.021313; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.29934; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.005139; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.005139; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.005642; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.007269; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.003803; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.006602; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.006602; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.003803; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.006602; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.008278
1453 | WCPWRCO_1G | 1 | NORTH | 204 | CSC 1: -0.004383; CSC 2: -0.00846; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.029598; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.00846; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.029598; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002838; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002838; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002644; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00392; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001996; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.003483; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.003483; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001996; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.003483; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.004374
1454 | WCPWRCO_2G | 2 | NORTH | 204 | CSC 1: -0.004383; CSC 2: -0.00846; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.029598; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.00846; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.029598; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002838; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002838; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002644; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00392; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001996; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.003483; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.003483; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001996; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.003483; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.004374
1455 | WCPWRCO_3G | 3 | NORTH | 242 | CSC 1: -0.004383; CSC 2: -0.00846; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.029598; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.00846; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.029598; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002838; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002838; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002644; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00392; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001996; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.003483; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.003483; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001996; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.003483; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.004374
1479 | WFCOGEN_1G | 1 | NORTH | 16 | CSC 1: -0.006259; CSC 2: -0.014726; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.006258; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.014726; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.006258; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.004072; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.005543; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.004973; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.004973; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.004973; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.00624
1479 | WFCOGEN_1G | 2 | NORTH | 16 | CSC 1: -0.006259; CSC 2: -0.014726; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.006258; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.014726; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.006258; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.004072; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.005543; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.004973; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.004973; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.004973; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.00624
1482 | WFCOGEN_2G | 1 | NORTH | 16 | CSC 1: -0.006259; CSC 2: -0.014726; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.006258; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.014726; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.006258; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.004072; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.005543; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.004973; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.004973; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.004973; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.00624
1482 | WFCOGEN_2G | 2 | NORTH | 13.6 | CSC 1: -0.006259; CSC 2: -0.014726; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.006258; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.014726; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.006258; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.004072; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.005543; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.004973; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.004973; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.004973; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.00624
1600 | BARTNWND_1G | 1 | NORTH | 12 | CSC 1: -0.006115; CSC 2: -0.012726; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.003386; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.012726; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.003386; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003852; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003852; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.003739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00564; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002779; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.004859; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.004859; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002779; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.004859; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.006109
1643 | SLSTR1PP_1G | 1 | NORTH | 6 | CSC 1: -0.010641; CSC 2: -0.022654; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.068458; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.022654; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.068458; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006542; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006542; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.006331; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010656
1675 | PEC_1G | 1 | NORTH | 76.7 | CSC 1: 0.00182; CSC 2: -0.00635; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001592; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.00635; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001592; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001149; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001149; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002424; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000813; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001446; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001446; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000813; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001446; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.00183
1676 | PEC_2G | 2 | NORTH | 79.6 | CSC 1: 0.00182; CSC 2: -0.00635; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001592; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.00635; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001592; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001149; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001149; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002424; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000813; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001446; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001446; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000813; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001446; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.00183
1677 | PEC_3G | 3 | NORTH | 88.4 | CSC 1: 0.00182; CSC 2: -0.00635; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001592; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.00635; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001592; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001149; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001149; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002424; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000813; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001446; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001446; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000813; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001446; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.00183
1678 | LAMARPWR_1G | 1 | NORTH | 160 | CSC 1: 0.001753; CSC 2: -0.006206; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001665; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006206; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001665; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000353; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002319; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000783; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000783; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001763
1679 | LAMARPWR_2G | 2 | NORTH | 156 | CSC 1: 0.001753; CSC 2: -0.006206; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001665; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006206; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001665; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000353; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002319; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000783; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000783; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001763
1680 | LAMARPWR_3G | 3 | NORTH | 196 | CSC 1: 0.001753; CSC 2: -0.006206; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001665; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006206; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001665; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000353; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002319; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000783; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000783; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001763
1681 | LAMARPWR_4G | 4 | NORTH | 156 | CSC 1: 0.001753; CSC 2: -0.006206; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001665; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006206; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001665; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000353; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002319; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000783; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000783; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001763
1682 | LAMARPWR_5G | 5 | NORTH | 157 | CSC 1: 0.001753; CSC 2: -0.006206; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001665; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006206; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001665; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000353; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002319; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000783; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000783; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001763
1683 | LAMARPWR_6G | 6 | NORTH | 198 | CSC 1: 0.001753; CSC 2: -0.006206; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001665; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006206; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001665; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000353; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002319; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000783; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000783; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001763
1687 | VALLEY_1G | 1 | NORTH | 170 | CSC 1: 0.001436; CSC 2: -0.005979; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.002066; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.005979; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.002066; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00092; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00092; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.001961; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.00064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001141; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001141; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.00064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001141; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001445
1688 | VALLEY_2G | 2 | NORTH | 527 | CSC 1: 0.001436; CSC 2: -0.005979; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.002066; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.005979; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.002066; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00092; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00092; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.001961; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.00064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001141; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001141; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.00064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001141; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001445
1689 | VALLEY_3G | 3 | NORTH | 375 | CSC 1: 0.001655; CSC 2: -0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000317; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001665
1861 | EAGLEMNT_1G | MB | NORTH | 0 | CSC 1: -0.002676; CSC 2: -0.003062; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.007178; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003062; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.007178; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00182; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00182; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.001381; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.002459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001213; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.002127; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.002127; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001213; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.002127; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.002677
1862 | EAGLEMNT_2G | MB | NORTH | 0 | CSC 1: -0.002676; CSC 2: -0.003062; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.007178; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003062; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.007178; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00182; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00182; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.001381; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.002459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001213; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.002127; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.002127; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001213; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.002127; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.002677
1863 | EAGLEMNT_3G | MB | NORTH | 0 | CSC 1: -0.002676; CSC 2: -0.003062; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.007178; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003062; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.007178; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00182; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00182; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.001381; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.002459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001213; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.002127; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.002127; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001213; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.002127; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.002677
1877 | WLFHOLW_1G | 1 | NORTH | 217.3 | CSC 1: -0.004217; CSC 2: -0.002581; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.011339; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.002581; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.011339; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002908; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002908; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.001949; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.004025; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001904; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.003351; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.003351; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001904; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.003351; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.004223
1878 | WLFHOLW_2G | 2 | NORTH | 215.7 | CSC 1: -0.004217; CSC 2: -0.002581; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.011339; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.002581; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.011339; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002908; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002908; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.001949; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.004025; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001904; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.003351; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.003351; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001904; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.003351; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.004223
1879 | WLFHOLW_3G | 3 | NORTH | 272.4 | CSC 1: -0.004217; CSC 2: -0.002581; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.011339; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.002581; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.011339; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002908; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002908; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.001949; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.004025; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001904; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.003351; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.003351; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001904; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.003351; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.004223
1889 | DECRDOVA_1G | 1 | NORTH | 0 | CSC 1: -0.004024; CSC 2: -0.002052; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.004768; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.002052; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.004768; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002776; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002776; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.001833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.003869; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.003198; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.003198; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.003198; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.004031
1892 | DECRDOVA_2G | A | NORTH | 65 | CSC 1: -0.005013; CSC 2: -0.003287; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.009424; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003287; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.009424; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003347; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003347; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002357; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00497; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.003984; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.003984; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.003984; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.005026
1893 | DECRDOVA_3G | B | NORTH | 65 | CSC 1: -0.005013; CSC 2: -0.003287; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.009424; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003287; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.009424; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003347; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003347; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002357; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00497; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.003984; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.003984; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.003984; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.005026
1894 | DECRDOVA_4G | C | NORTH | 65 | CSC 1: -0.005013; CSC 2: -0.003287; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.009424; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003287; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.009424; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003347; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003347; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002357; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00497; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.003984; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.003984; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.003984; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.005026
1895 | DECRDOVA_5G | D | NORTH | 65 | CSC 1: -0.005013; CSC 2: -0.003287; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.009424; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003287; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.009424; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.003347; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.003347; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.002357; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00497; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.002257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.003984; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.003984; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.002257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.003984; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.005026
1937 | MDLTHELP_5G | 5 | NORTH | 224 | CSC 1: -0.003295; CSC 2: 0.010123; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.003702; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.010123; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.003702; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002759; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002759; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.000359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.003352; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.00262; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.00262; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.00262; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.003314
1938 | MDLTHELP_6G | 6 | NORTH | 226 | CSC 1: -0.003295; CSC 2: 0.010123; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.003702; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.010123; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.003702; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002759; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002759; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.000359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.003352; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.00262; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.00262; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.00262; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.003314
1941 | MDLTHELP_1G | 1 | NORTH | 216.4 | CSC 1: -0.002239; CSC 2: 0.011024; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.002531; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.011024; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.002531; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000161; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.002354; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.000996; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.00178; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.00178; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.000996; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.00178; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.002256
1942 | MDLTHELP_2G | 2 | NORTH | 216.1 | CSC 1: -0.002239; CSC 2: 0.011024; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.002531; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.011024; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.002531; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000161; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.002354; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.000996; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.00178; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.00178; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.000996; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.00178; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.002256
1943 | MDLTHELP_3G | 3 | NORTH | 212 | CSC 1: -0.003295; CSC 2: 0.010123; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.003702; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.010123; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.003702; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002759; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002759; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.000359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.003352; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.00262; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.00262; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.00262; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.003314
1944 | MDLTHELP_4G | 4 | NORTH | 211 | CSC 1: -0.003295; CSC 2: 0.010123; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.003702; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.010123; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.003702; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.002759; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.002759; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.000359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.003352; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.00262; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.00262; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.00262; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.003314
1947 | HANDLEY_3G | 3 | NORTH | 316 | CSC 1: -0.002233; CSC 2: 0.001182; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001863; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.001182; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001863; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.001633; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.001633; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.000807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.002172; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.001775; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.001775; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.001775; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.002238
1948 | HANDLEY_4G | 4 | NORTH | 435 | CSC 1: -0.002055; CSC 2: 0.000919; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001742; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.000919; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001742; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.0015; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.0015; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.000756; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.001992; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.000926; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.001633; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.001633; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.000926; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.001633; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.00206
1949 | HANDLEY_5G | 5 | NORTH | 435 | CSC 1: -0.002233; CSC 2: 0.001182; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001863; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.001182; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001863; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.001633; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.001633; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.000807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.002172; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.001006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.001775; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.001775; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.001006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.001775; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.002238
2371 | COLLIN_1G | MB | NORTH | 0 | CSC 1: 0.000723; CSC 2: -0.004938; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.003222; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.004938; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.003222; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.000481; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.000481; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.001107; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000319; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.000575; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.000575; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000319; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.000575; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.000731
2381 | NTHLK1_G | 1 | NORTH | 0 | CSC 1: 0.000535; CSC 2: -0.003496; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.002078; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003496; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.002078; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -5.2e-05; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.000733; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000236; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.000425; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.000425; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000236; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.000425; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.00054
2382 | NTHLK2_G | 2 | NORTH | 0 | CSC 1: 0.000535; CSC 2: -0.003496; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.002078; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003496; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.002078; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -5.2e-05; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.000733; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000236; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.000425; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.000425; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000236; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.000425; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.00054
2383 | NTHLK3_G | 3 | NORTH | 0 | CSC 1: 0.000535; CSC 2: -0.003496; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.002078; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003496; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.002078; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -5.2e-05; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.000733; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000236; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.000425; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.000425; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000236; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.000425; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.00054
2413 | MTCK6_G | 6 | NORTH | 0 | CSC 1: 0.001429; CSC 2: -0.003793; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.000538; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003793; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.000538; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001214; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001214; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.00064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001136; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001136; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.00064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001136; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001435
2414 | MTCK7_G | 7 | NORTH | 0 | CSC 1: 0.001429; CSC 2: -0.003793; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.000538; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003793; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.000538; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001214; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001214; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.00064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001136; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001136; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.00064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001136; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001435
2417 | MTCK8_G | 8 | NORTH | 444.8 | CSC 1: 0.001429; CSC 2: -0.003793; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.000538; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.003793; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.000538; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001214; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001214; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.001393; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.00064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001136; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001136; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.00064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001136; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001435
2451 | LKHB1_G | 1 | NORTH | 391 | CSC 1: 0.002587; CSC 2: -0.006879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.0001; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.0001; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001839; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001839; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000582; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002982; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001159; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.002057; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.002057; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001159; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.002057; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.002599
2452 | LKHB2_G | 2 | NORTH | 516 | CSC 1: 0.002587; CSC 2: -0.006879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.0001; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.0001; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001839; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001839; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000582; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002982; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001159; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.002057; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.002057; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001159; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.002057; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.002599
3107 | STRYKER_1G | 1 | NORTH | 182 | CSC 1: 0.007022; CSC 2: -0.015864; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.002655; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.015864; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.002655; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.003723; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.003723; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.011091; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.00315; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.005582; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.005582; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.00315; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.005582; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.007051
3108 | STRYKER_2G | 2 | NORTH | 484 | CSC 1: 0.007022; CSC 2: -0.015864; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.002655; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.015864; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.002655; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.003723; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.003723; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.001119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.011091; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.00315; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.005582; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.005582; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.00315; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.005582; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.007051
3126 | TRINIDAD_6G | 1 | NORTH | 224 | CSC 1: 0.00332; CSC 2: -0.012713; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.003742; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.012713; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.003742; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002239; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002239; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.001867; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.006676; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001495; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.002639; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.002639; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001495; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.002639; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.003328
3309 | ASPN_G | 1 | NORTH | 50 | CSC 1: 0.006956; CSC 2: -0.014983; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.002605; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.014983; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.002605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.002885; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.010324; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.00312; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.005529; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.005529; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.00312; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.005529; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.006985
3403 | THOUSE_1G | 1 | NORTH | 0 | CSC 1: -0.024519; CSC 2: 0.1142; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.011979; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.1142; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.011979; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.016371; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.016371; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.006247; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.029716; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.010915; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.019493; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.019493; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.010915; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.019493; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.024692
3404 | THOUSE_2G | 2 | NORTH | 807 | CSC 1: -0.024519; CSC 2: 0.1142; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.011979; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.1142; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.011979; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.016371; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.016371; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.006247; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.029716; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.010915; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.019493; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.019493; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.010915; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.019493; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.024692
3416 | LAKE_CRK1_G | 1 | NORTH | 0 | CSC 1: -0.025592; CSC 2: 0.00807; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.013069; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.00807; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.013069; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.015222; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.015222; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.010944; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.030324; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.01139; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.020346; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.020346; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.01139; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.020346; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.025774
3417 | LAKE_CRK2_G | 2 | NORTH | 0 | CSC 1: -0.025592; CSC 2: 0.00807; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.013069; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: -0.00807; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.013069; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.015222; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.015222; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.010944; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.030324; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.01139; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.020346; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.020346; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.01139; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.020346; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.025774
5026 | BRAUNIG_VHB1 | 1 | SOUTH | 215 | CSC 1: -0.13896; CSC 2: -0.41029; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.032165; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41029; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.032165; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081237; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081237; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11103; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.1131; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064851; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064851; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13732
5027 | BRAUNIG_VHB2 | 2 | SOUTH | 216 | CSC 1: -0.13896; CSC 2: -0.41029; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.032165; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41029; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.032165; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081237; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081237; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11103; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.1131; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064851; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064851; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13732
5028 | BRAUNIG_VHB3 | 3 | SOUTH | 407 | CSC 1: -0.13883; CSC 2: -0.41017; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.032364; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41017; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.032364; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081152; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081152; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11092; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11299; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.06481; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11023; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11023; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.06481; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11023; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13716
5264 | LEON_LCP3G3 | 3 | SOUTH | 0 | CSC 1: -0.13887; CSC 2: -0.40879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.033005; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.40879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.033005; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11299; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064849; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064849; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1372
5265 | LEON_LCP4G4 | 4 | SOUTH | 89 | CSC 1: -0.13887; CSC 2: -0.40879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.033005; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.40879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.033005; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11299; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064849; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064849; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1372
5266 | LEON_LCPCT1 | 1 | SOUTH | 44 | CSC 1: -0.13887; CSC 2: -0.40879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.033005; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.40879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.033005; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11299; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064849; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064849; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1372
5267 | LEON_LCPCT2 | 2 | SOUTH | 44 | CSC 1: -0.13887; CSC 2: -0.40879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.033005; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.40879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.033005; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11299; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064849; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064849; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1372
5268 | LEON_LCPCT3 | 3 | SOUTH | 43 | CSC 1: -0.13887; CSC 2: -0.40879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.033005; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.40879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.033005; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11299; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064849; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064849; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1372
5269 | LEON_LCPCT4 | 4 | SOUTH | 45 | CSC 1: -0.13887; CSC 2: -0.40879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.033005; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.40879; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.033005; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11299; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064849; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064849; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1372
5396 | CALAVER_OWS1 | 1 | SOUTH | 418 | CSC 1: -0.13884; CSC 2: -0.41056; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.032154; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41056; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.032154; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081161; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081161; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11093; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064793; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11024; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11024; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064793; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11024; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1372
5397 | CALAVER_OWS2 | 2 | SOUTH | 400 | CSC 1: -0.13884; CSC 2: -0.41056; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.032154; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41056; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.032154; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081161; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081161; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11093; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064793; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11024; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11024; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064793; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11024; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1372
5436 | TUTTL_WBT1G1 | 1 | SOUTH | 48.8 | CSC 1: -0.13887; CSC 2: -0.41162; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031611; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41162; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031611; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081171; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081171; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11095; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11307; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064811; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064811; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13723
5438 | TUTTL_WBT3G3 | 3 | SOUTH | 95 | CSC 1: -0.13887; CSC 2: -0.41162; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031611; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41162; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031611; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081171; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081171; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11095; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11307; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064811; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064811; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13723
5439 | TUTTL_WBT4G4 | 4 | SOUTH | 151 | CSC 1: -0.13887; CSC 2: -0.41162; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031611; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41162; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031611; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081171; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081171; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11095; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11307; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064811; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064811; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13723
5476 | BRA_AVR1_CT1 | 1 | SOUTH | 155 | CSC 1: -0.14009; CSC 2: -0.40945; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031456; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.40945; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031456; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081913; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081913; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11389; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.065492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11123; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11123; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.065492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11123; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13833
5477 | BRA_AVR1_ST | 1 | SOUTH | 174 | CSC 1: -0.14009; CSC 2: -0.40945; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031456; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.40945; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031456; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081913; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081913; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11389; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.065492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11123; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11123; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.065492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11123; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13833
5478 | BRA_AVR1_CT2 | 1 | SOUTH | 155 | CSC 1: -0.14009; CSC 2: -0.40945; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031456; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.40945; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031456; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081913; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081913; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11389; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.065492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11123; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11123; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.065492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11123; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13833
5503 | RAYBURNGEN3 | 1 | SOUTH | 17.6 | CSC 1: -0.16148; CSC 2: -0.3708; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029468; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.3708; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029468; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.095184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.095184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12951; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12855; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.076591; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12827; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12827; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.076591; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12827; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15868
5505 | RAYBURNGEN1 | 1 | SOUTH | 0 | CSC 1: -0.16148; CSC 2: -0.3708; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029468; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.3708; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029468; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.095184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.095184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12951; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12855; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.076591; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12827; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12827; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.076591; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12827; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15868
5506 | RAYBURNGEN2 | 1 | SOUTH | 0 | CSC 1: -0.16148; CSC 2: -0.3708; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029468; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.3708; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029468; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.095184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.095184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12951; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12855; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.076591; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12827; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12827; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.076591; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12827; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15868
5508 | RAYBURNCC9 | 1 | SOUTH | 47.7 | CSC 1: -0.16096; CSC 2: -0.37237; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029185; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37237; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029185; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.094859; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.094859; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12908; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12821; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.076276; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.076276; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15821
5509 | RAYBURNCC10 | 1 | SOUTH | 37.3 | CSC 1: -0.16096; CSC 2: -0.37237; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029185; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37237; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029185; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.094859; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.094859; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12908; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12821; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.076276; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.076276; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15821
5511 | RAYBURNCC7 | 1 | SOUTH | 47.5 | CSC 1: -0.16096; CSC 2: -0.37237; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029185; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37237; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029185; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.094859; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.094859; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12908; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12821; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.076276; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.076276; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15821
5512 | RAYBURNCC8 | 1 | SOUTH | 49.3 | CSC 1: -0.16096; CSC 2: -0.37237; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029185; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37237; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029185; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.094859; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.094859; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12908; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12821; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.076276; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.076276; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15821
5728 | FALCONHYDRO2 | 2 | SOUTH | 12 | CSC 1: -0.15365; CSC 2: -0.37379; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.036208; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37379; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.036208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.090265; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.090265; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12291; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.073216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.073216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15054
5729 | FALCONHYDRO3 | 3 | SOUTH | 11 | CSC 1: -0.15365; CSC 2: -0.37379; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.036208; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37379; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.036208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.090265; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.090265; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12291; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.073216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.073216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15054
5890 | PEARSALLGEN1 | 1 | SOUTH | 19.2 | CSC 1: -0.13908; CSC 2: -0.38521; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.045026; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38521; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.045026; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11114; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.065352; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.065352; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13706
5891 | PEARSALLGEN2 | 1 | SOUTH | 19.4 | CSC 1: -0.13908; CSC 2: -0.38521; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.045026; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38521; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.045026; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11114; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.065352; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.065352; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13706
5892 | PEARSALLGEN3 | 1 | SOUTH | 19.1 | CSC 1: -0.13908; CSC 2: -0.38521; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.045026; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38521; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.045026; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.081466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.081466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11114; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.065352; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.065352; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11042; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13706
5932 | SI_RAY9 | 9 | SOUTH | 32 | CSC 1: -0.15776; CSC 2: -0.37553; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031151; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37553; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031151; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092717; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092717; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12622; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075341; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075341; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15443
5933 | SI_RAY6 | 6 | SOUTH | 15.4 | CSC 1: -0.15776; CSC 2: -0.37553; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031151; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37553; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031151; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092717; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092717; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12622; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075341; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075341; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15443
5935 | SI_RAY10 | 10 | SOUTH | 47 | CSC 1: -0.15776; CSC 2: -0.37553; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031151; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37553; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031151; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092717; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092717; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12622; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075341; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075341; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15443
6016 | SWMESA | 1 | WEST | 18.8 | CSC 1: -0.018389; CSC 2: -0.05244; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.35834; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.05244; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.35834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.011017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.011017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.01367; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.015536; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.0085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.014606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.014606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.0085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.014606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.018245
6144 | MCADOO1A | 1 | WEST | 15 | CSC 1: -0.011004; CSC 2: -0.030395; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.3178; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.030395; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.3178; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006709; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006709; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.00772; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.009564; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005044; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008742; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008742; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005044; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008742; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010956
6407 | TURKTRAK1A | 1 | WEST | 33.9 | CSC 1: -0.014769; CSC 2: -0.04369; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.33003; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.04369; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.33003; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.008902; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.008902; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.010663; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.012734; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.006773; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.011733; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.011733; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.006773; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.011733; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.0147
6637 | SNYDERW1A | 1 | WEST | 12.6 | CSC 1: -0.01167; CSC 2: -0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.36732; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032502; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.36732; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007099; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007099; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008263; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010093; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005354; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005354; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011613
6948 | DENISNDM | 1 | NORTH | 40 | CSC 1: 0.001261; CSC 2: -0.005865; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.002285; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.005865; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.002285; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00081; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00081; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000148; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.001765; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000561; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001003; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001003; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000561; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001003; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.00127
6948 | DENISNDM | 2 | NORTH | 31 | CSC 1: 0.001261; CSC 2: -0.005865; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.002285; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.005865; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.002285; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00081; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00081; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000148; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.001765; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000561; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001003; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001003; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000561; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001003; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.00127
7000 | L_FERGUS1_1Y | 1 | SOUTH | 400 | CSC 1: -0.1048; CSC 2: -0.42603; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.04465; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42603; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.04465; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.060806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.060806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.082829; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.088575; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.04736; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.083289; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.083289; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.04736; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.083289; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.10493
7004 | L_SIMGID1_1Y | 1 | SOUTH | 132 | CSC 1: -0.11857; CSC 2: -0.45693; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.02712; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.45693; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.02712; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.069208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.069208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.09509; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.10021; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.051359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.094388; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.094388; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.051359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.094388; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.12075
7005 | L_SIMGID1_2Y | 2 | SOUTH | 133 | CSC 1: -0.11857; CSC 2: -0.45693; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.02712; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.45693; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.02712; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.069208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.069208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.09509; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.10021; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.051359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.094388; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.094388; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.051359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.094388; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.12075
7006 | L_SIMGID1_3Y | 3 | SOUTH | 324.9 | CSC 1: -0.11857; CSC 2: -0.45693; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.02712; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.45693; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.02712; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.069208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.069208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.09509; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.10021; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.051359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.094388; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.094388; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.051359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.094388; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.12075
7007 | L_LOSTPI1_1Y | 1 | SOUTH | 158.6 | CSC 1: -0.11776; CSC 2: -0.46888; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.02565; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46888; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.02565; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.068273; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.068273; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.094186; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.099583; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.052038; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.093635; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.093635; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.052038; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.093635; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11892
7008 | L_LOSTPI1_2Y | 2 | SOUTH | 157.7 | CSC 1: -0.11776; CSC 2: -0.46888; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.02565; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46888; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.02565; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.068273; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.068273; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.094186; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.099583; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.052038; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.093635; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.093635; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.052038; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.093635; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11892
7009 | L_LOSTPI1_3Y | 3 | SOUTH | 173.9 | CSC 1: -0.11776; CSC 2: -0.46888; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.02565; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46888; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.02565; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.068273; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.068273; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.094186; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.099583; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.052038; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.093635; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.093635; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.052038; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.093635; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11892
7014 | L_HAYSEN1_1Y | 1 | SOUTH | 223.9 | CSC 1: -0.13093; CSC 2: -0.43253; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.43253; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.076287; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.076287; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.10793; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.060202; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.060202; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13016
7015 | L_HAYSEN1_2Y | 2 | SOUTH | 225 | CSC 1: -0.13093; CSC 2: -0.43253; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.43253; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.076287; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.076287; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.10793; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.060202; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.060202; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13016
7016 | L_HAYSEN1_3Y | 3 | SOUTH | 224.6 | CSC 1: -0.13093; CSC 2: -0.43253; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.43253; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.076287; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.076287; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.10793; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.060202; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.060202; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13016
7017 | L_HAYSEN1_4Y | 4 | SOUTH | 226.7 | CSC 1: -0.13093; CSC 2: -0.43253; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.43253; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.076287; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.076287; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.10793; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.060202; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.060202; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13016
7020 | L_AUSTPL1_1Y | 1 | SOUTH | 0 | CSC 1: -0.11266; CSC 2: -0.46374; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.028531; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46374; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.028531; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.065179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.065179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.089625; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.095566; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.0503; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.089562; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.089562; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.0503; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.089562; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11333
7020 | L_AUSTPL1_1Y | 2 | SOUTH | 0 | CSC 1: -0.11266; CSC 2: -0.46374; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.028531; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46374; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.028531; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.065179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.065179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.089625; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.095566; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.0503; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.089562; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.089562; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.0503; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.089562; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11333
7022 | L_BUCHAN1_1Y | 1 | SOUTH | 0 | CSC 1: -0.097819; CSC 2: -0.42514; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.044745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42514; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.044745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.056703; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.056703; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.076869; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.083343; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.044074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.077747; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.077747; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.044074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.077747; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.098053
7023 | L_BUCHAN1_2Y | 2 | SOUTH | 0 | CSC 1: -0.097819; CSC 2: -0.42514; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.044745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42514; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.044745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.056703; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.056703; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.076869; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.083343; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.044074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.077747; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.077747; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.044074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.077747; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.098053
7024 | L_BUCHAN1_3Y | 3 | SOUTH | 0 | CSC 1: -0.097819; CSC 2: -0.42514; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.044745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42514; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.044745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.056703; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.056703; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.076869; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.083343; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.044074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.077747; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.077747; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.044074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.077747; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.098053
7026 | L_INKSDA1_1Y | 1 | SOUTH | 0 | CSC 1: -0.098332; CSC 2: -0.41652; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.050769; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41652; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.050769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.057038; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.057038; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.077384; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.083513; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.04439; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.07815; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.07815; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.04439; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.07815; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.098491
7028 | L_MARBFA1_1Y | 1 | SOUTH | 0 | CSC 1: -0.10665; CSC 2: -0.43505; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.040674; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.43505; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.040674; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.061835; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.061835; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.084423; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.090226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.048062; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.084767; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.084767; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.048062; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.084767; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1069
7029 | L_MARBFA1_2Y | 2 | SOUTH | 0 | CSC 1: -0.10665; CSC 2: -0.43505; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.040674; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.43505; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.040674; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.061835; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.061835; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.084423; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.090226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.048062; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.084767; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.084767; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.048062; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.084767; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1069
7031 | L_MARSFO1G1Y | 1 | SOUTH | 0 | CSC 1: -0.11048; CSC 2: -0.45371; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.03245; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.45371; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.03245; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.063964; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.063964; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.08772; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.093642; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.049514; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.087826; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.087826; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.049514; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.087826; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11098
7032 | L_MARSFO1G2Y | 2 | SOUTH | 0 | CSC 1: -0.11048; CSC 2: -0.45371; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.03245; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.45371; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.03245; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.063964; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.063964; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.08772; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.093642; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.049514; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.087826; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.087826; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.049514; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.087826; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11098
7033 | L_MARSFO1G3Y | 3 | SOUTH | 0 | CSC 1: -0.11048; CSC 2: -0.45371; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.03245; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.45371; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.03245; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.063964; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.063964; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.08772; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.093642; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.049514; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.087826; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.087826; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.049514; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.087826; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11098
7035 | L_WIRTZ_1G1Y | 1 | SOUTH | 0 | CSC 1: -0.10461; CSC 2: -0.42788; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.043662; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42788; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.043662; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.060686; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.060686; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.082668; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.088489; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.04724; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.083142; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.083142; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.04724; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.083142; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.10477
7036 | L_WIRTZ_1G2Y | 2 | SOUTH | 0 | CSC 1: -0.10461; CSC 2: -0.42788; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.043662; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42788; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.043662; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.060686; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.060686; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.082668; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.088489; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.04724; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.083142; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.083142; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.04724; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.083142; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.10477
7038 | L_DELAWA1_1Y | 1 | WEST | 3.5 | CSC 1: -0.013175; CSC 2: -0.036956; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37872; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.036956; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37872; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007977; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007977; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009481; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011305; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.00606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.010466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.010466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.00606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.010466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.013098
7038 | L_DELAWA1_1Y | 2 | WEST | 3 | CSC 1: -0.013175; CSC 2: -0.036956; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37872; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.036956; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37872; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007977; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007977; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009481; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011305; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.00606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.010466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.010466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.00606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.010466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.013098
7303 | L_WPPGS12_1Y | 1 | SOUTH | 50 | CSC 1: -0.12902; CSC 2: -0.43728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.026365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.43728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.026365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.076339; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.076339; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10462; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.10815; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.053557; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.053557; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13355
7303 | L_WPPGS12_1Y | 2 | SOUTH | 50 | CSC 1: -0.12902; CSC 2: -0.43728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.026365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.43728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.026365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.076339; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.076339; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10462; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.10815; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.053557; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.053557; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13355
7305 | L_WPPGS34_1Y | 3 | SOUTH | 50 | CSC 1: -0.12902; CSC 2: -0.43728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.026365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.43728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.026365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.076339; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.076339; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10462; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.10815; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.053557; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.053557; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13355
7305 | L_WPPGS34_1Y | 4 | SOUTH | 50 | CSC 1: -0.12902; CSC 2: -0.43728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.026365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.43728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.026365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.076339; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.076339; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10462; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.10815; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.053557; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.053557; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13355
7487 | L_CANYHY8_1Y | 1 | SOUTH | 0 | CSC 1: -0.12718; CSC 2: -0.43467; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030569; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.43467; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030569; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.074079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.074079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10152; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.1053; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.058122; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10104; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10104; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.058122; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10104; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.12676
7605 | L_MCQUEE9_1Y | 1 | SOUTH | 0 | CSC 1: -0.13406; CSC 2: -0.42373; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029937; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42373; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029937; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.078326; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.078326; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10721; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.06157; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1065; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1065; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.06157; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1065; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13336
7605 | L_MCQUEE9_1Y | 2 | SOUTH | 0 | CSC 1: -0.13406; CSC 2: -0.42373; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029937; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42373; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029937; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.078326; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.078326; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10721; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.06157; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1065; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1065; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.06157; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1065; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13336
7605 | L_MCQUEE9_1Y | 3 | SOUTH | 0 | CSC 1: -0.13406; CSC 2: -0.42373; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029937; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42373; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029937; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.078326; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.078326; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10721; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11006; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.06157; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1065; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1065; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.06157; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1065; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13336
7609 | L_SCHUMA8_1Y | 1 | SOUTH | 0 | CSC 1: -0.13511; CSC 2: -0.42125; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030422; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42125; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030422; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.078874; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.078874; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10794; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.062583; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1073; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1073; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.062583; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1073; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13392
7624 | L_LAKEWO9_1Y | 1 | SOUTH | 0 | CSC 1: -0.13605; CSC 2: -0.41977; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029501; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41977; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.079728; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.079728; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10905; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11161; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.061867; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10814; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10814; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.061867; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10814; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13593
7624 | L_LAKEWO9_1Y | 2 | SOUTH | 0 | CSC 1: -0.13605; CSC 2: -0.41977; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029501; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41977; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.079728; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.079728; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10905; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11161; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.061867; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10814; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10814; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.061867; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10814; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13593
7800 | L_GUADGE1_1Y | 1 | SOUTH | 147 | CSC 1: -0.13804; CSC 2: -0.41677; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030064; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41677; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11028; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11261; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.0643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.0643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1365
7801 | L_GUADGE1_2Y | 2 | SOUTH | 138 | CSC 1: -0.13804; CSC 2: -0.41677; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030064; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41677; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11028; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11261; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.0643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.0643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1365
7802 | L_GUADGE1_3Y | 3 | SOUTH | 146 | CSC 1: -0.13804; CSC 2: -0.41677; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030064; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41677; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11028; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11261; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.0643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.0643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1365
7803 | L_GUADGE1_4Y | 4 | SOUTH | 149 | CSC 1: -0.13804; CSC 2: -0.41677; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030064; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41677; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11028; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11261; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.0643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.0643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1365
7804 | L_GUADGE1_5Y | 5 | SOUTH | 182 | CSC 1: -0.13804; CSC 2: -0.41677; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030064; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41677; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11028; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11261; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.0643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.0643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1365
7805 | L_GUADGE1_6Y | 6 | SOUTH | 203 | CSC 1: -0.13804; CSC 2: -0.41677; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030064; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.41677; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030064; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11028; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11261; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.0643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.0643; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1096; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1365
7807 | L_BASTEN1_1Y | 1 | SOUTH | 152.5 | CSC 1: -0.11642; CSC 2: -0.46952; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.026377; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46952; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.026377; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.067325; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.067325; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.092878; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.098449; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.052078; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.092539; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.092539; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.052078; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.092539; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11701
7808 | L_BASTEN1_2Y | 1 | SOUTH | 149.5 | CSC 1: -0.11642; CSC 2: -0.46952; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.026377; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46952; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.026377; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.067325; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.067325; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.092878; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.098449; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.052078; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.092539; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.092539; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.052078; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.092539; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11701
7809 | L_BASTEN1_3Y | 1 | SOUTH | 232.6 | CSC 1: -0.11642; CSC 2: -0.46952; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.026377; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46952; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.026377; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.067325; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.067325; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.092878; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.098449; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.052078; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.092539; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.092539; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.052078; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.092539; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11701
7810 | L_RIONOG1G1Y | 1 | SOUTH | 148 | CSC 1: -0.13459; CSC 2: -0.42441; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029712; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42441; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029712; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.078526; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.078526; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10752; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.062312; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10688; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10688; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.062312; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10688; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13343
7811 | L_RIONOG1G2Y | 2 | SOUTH | 148 | CSC 1: -0.13459; CSC 2: -0.42441; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029712; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42441; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029712; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.078526; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.078526; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10752; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.062312; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10688; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10688; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.062312; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10688; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13343
7812 | L_RIONOG1G3Y | 3 | SOUTH | 154 | CSC 1: -0.13459; CSC 2: -0.42441; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029712; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42441; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029712; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.078526; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.078526; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10752; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.062312; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10688; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10688; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.062312; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10688; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13343
7813 | L_RIONOG1S1Y | 4 | SOUTH | 293 | CSC 1: -0.13459; CSC 2: -0.42441; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029712; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.42441; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029712; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.078526; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.078526; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10752; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.062312; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10688; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10688; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.062312; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10688; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13343
8032 | AMISTADHYD1 | 1 | SOUTH | 33 | CSC 1: -0.10379; CSC 2: -0.28577; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.13221; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.28577; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.13221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.06088; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.06088; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.082617; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.084083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.048778; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.082399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.082399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.048778; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.082399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.10227
8033 | AMISTADHYD2 | 2 | SOUTH | 25 | CSC 1: -0.10379; CSC 2: -0.28577; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.13221; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.28577; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.13221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.06088; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.06088; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.082617; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.084083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.048778; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.082399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.082399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.048778; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.082399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.10227
8048 | FALCONHYDRO1 | 1 | SOUTH | 12 | CSC 1: -0.15365; CSC 2: -0.37379; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.036208; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37379; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.036208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.090265; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.090265; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12291; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.073216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.073216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15054
8173 | VICEC51A | 5 | SOUTH | 144 | CSC 1: -0.15995; CSC 2: -0.37441; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029122; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37441; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029122; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.094252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.094252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12828; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12755; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12704; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12704; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12704; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15735
8174 | VICEC61A | 6 | SOUTH | 188 | CSC 1: -0.15995; CSC 2: -0.37441; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029122; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37441; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029122; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.094252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.094252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12828; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12755; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12704; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12704; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12704; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15735
8262 | ELPS | 1 | SOUTH | 6 | CSC 1: -0.11564; CSC 2: -0.31505; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.10506; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.31505; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.10506; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.067817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.067817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.092196; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.093504; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.054424; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.091806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.091806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.054424; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.091806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11389
8442 | NBEC7 | 1 | SOUTH | 0 | CSC 1: -0.15884; CSC 2: -0.37428; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030694; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37428; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.093377; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.093377; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12649; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075887; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075887; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15545
8459 | B_DAVIS0B | 7 | SOUTH | 0 | CSC 1: -0.15864; CSC 2: -0.37459; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030735; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37459; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.093257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.093257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12635; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1259; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1259; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1259; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15527
8460 | B_DAVIS0A | MB | SOUTH | 0 | CSC 1: -0.15864; CSC 2: -0.37459; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030735; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37459; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.093257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.093257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12635; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1259; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1259; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1259; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15527
8560 | CNOPGT1 | MB | SOUTH | 148.3 | CSC 1: -0.15882; CSC 2: -0.3743; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030698; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.3743; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030698; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.09337; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.09337; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12709; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12648; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.07588; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.07588; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15544
8561 | CNOPGT2 | 1 | SOUTH | 148.6 | CSC 1: -0.15882; CSC 2: -0.3743; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030698; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.3743; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030698; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.09337; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.09337; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12709; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12648; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.07588; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.07588; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15544
8562 | CNOPST1 | 2 | SOUTH | 153 | CSC 1: -0.15882; CSC 2: -0.3743; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030698; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.3743; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030698; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.09337; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.09337; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12709; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12648; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.07588; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.07588; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12605; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15544
8926 | LGE_GT10A | 3 | SOUTH | 158 | CSC 1: -0.15991; CSC 2: -0.3728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.3728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.094033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.094033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12798; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12723; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.076463; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.076463; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15645
8927 | LGE_GT20A | 1 | SOUTH | 153 | CSC 1: -0.15991; CSC 2: -0.3728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.3728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.094033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.094033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12798; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12723; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.076463; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.076463; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15645
8928 | LGE_STG0A | 2 | SOUTH | 100 | CSC 1: -0.15991; CSC 2: -0.3728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.3728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.094033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.094033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12798; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12723; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.076463; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.076463; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15645
8930 | ICPGN10A | 3 | SOUTH | 149 | CSC 1: -0.15991; CSC 2: -0.3728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.3728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.094033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.094033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12798; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12723; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.076463; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.076463; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15645
8931 | ICPGN20A | 1 | SOUTH | 150 | CSC 1: -0.15991; CSC 2: -0.3728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.3728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.094033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.094033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12798; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12723; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.076463; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.076463; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15645
8932 | ICPGN30A | 2 | SOUTH | 127 | CSC 1: -0.15991; CSC 2: -0.3728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030365; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.3728; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030365; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.094033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.094033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12798; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12723; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.076463; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.076463; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12691; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15645
8933 | FGNTS001 | 3 | SOUTH | 146.5 | CSC 1: -0.15696; CSC 2: -0.37521; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.03213; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37521; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.03213; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092239; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092239; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12558; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12515; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.074928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.074928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15367
8934 | FGNTS101 | 1 | SOUTH | 147.9 | CSC 1: -0.15696; CSC 2: -0.37521; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.03213; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37521; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.03213; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092239; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092239; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12558; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12515; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.074928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.074928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15367
8935 | FGNTS201 | 2 | SOUTH | 173 | CSC 1: -0.15696; CSC 2: -0.37521; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.03213; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37521; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.03213; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092239; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092239; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12558; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12515; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.074928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.074928; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12457; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15367
8936 | MVGN#1 | 3 | SOUTH | 216.6 | CSC 1: -0.15752; CSC 2: -0.37544; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031443; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37544; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031443; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12603; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12556; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15419
8937 | MVGN#2 | 1 | SOUTH | 216.7 | CSC 1: -0.15752; CSC 2: -0.37544; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031443; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37544; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031443; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12603; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12556; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15419
8938 | MVGN#3 | 2 | SOUTH | 250.9 | CSC 1: -0.15752; CSC 2: -0.37544; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031443; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37544; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031443; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12603; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12556; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15419
8981 | HECN1 | 3 | SOUTH | 144.8 | CSC 1: -0.15752; CSC 2: -0.37544; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031444; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37544; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031444; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092571; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092571; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12603; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12556; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15419
8982 | HECN2 | 1 | SOUTH | 144.1 | CSC 1: -0.15752; CSC 2: -0.37544; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031444; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37544; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031444; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092571; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092571; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12603; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12556; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15419
8983 | HECN3 | 2 | SOUTH | 171.9 | CSC 1: -0.15752; CSC 2: -0.37544; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031444; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37544; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031444; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092571; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092571; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12603; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12556; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15419
9000 | DECKR_G1 | 3 | SOUTH | 280 | CSC 1: -0.11254; CSC 2: -0.46587; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.028106; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46587; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.028106; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.065091; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.065091; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.08956; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.095548; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.05017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.089472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.089472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.05017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.089472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11328
9001 | DECKR_G2 | 1 | SOUTH | 400 | CSC 1: -0.11254; CSC 2: -0.46587; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.028106; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46587; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.028106; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.065091; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.065091; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.08956; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.095548; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.05017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.089472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.089472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.05017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.089472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11328
9002 | DECKR_G3 | 2 | SOUTH | 0 | CSC 1: -0.1117; CSC 2: -0.46853; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.027807; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46853; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.027807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.064577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.064577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.0889; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.095026; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.049662; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.088817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.088817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.049662; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.088817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11256
9003 | DECKR_G4 | 3 | SOUTH | 44 | CSC 1: -0.1117; CSC 2: -0.46853; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.027807; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46853; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.027807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.064577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.064577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.0889; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.095026; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.049662; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.088817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.088817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.049662; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.088817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11256
9004 | DECKR_G5 | 4 | SOUTH | 44 | CSC 1: -0.1117; CSC 2: -0.46853; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.027807; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46853; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.027807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.064577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.064577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.0889; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.095026; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.049662; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.088817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.088817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.049662; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.088817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11256
9005 | DECKR_G6 | 5 | SOUTH | 44 | CSC 1: -0.1117; CSC 2: -0.46853; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.027807; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46853; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.027807; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.064577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.064577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.0889; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.095026; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.049662; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.088817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.088817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.049662; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.088817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11256
9016 | SANDH_G1 | 6 | SOUTH | 45 | CSC 1: -0.11364; CSC 2: -0.46433; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.028121; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46433; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.028121; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.065761; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.065761; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.090476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.096307; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.050737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.050737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11432
9017 | SANDH_G2 | 1 | SOUTH | 45 | CSC 1: -0.11364; CSC 2: -0.46433; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.028121; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46433; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.028121; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.065761; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.065761; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.090476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.096307; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.050737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.050737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11432
9018 | SANDH_G3 | 2 | SOUTH | 45 | CSC 1: -0.11364; CSC 2: -0.46433; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.028121; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46433; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.028121; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.065761; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.065761; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.090476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.096307; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.050737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.050737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11432
9019 | SANDH_G4 | 3 | SOUTH | 0 | CSC 1: -0.11364; CSC 2: -0.46433; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.028121; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46433; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.028121; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.065761; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.065761; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.090476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.096307; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.050737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.050737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11432
9020 | SANDHG5A | 4 | SOUTH | 150 | CSC 1: -0.11364; CSC 2: -0.46433; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.028121; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46433; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.028121; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.065761; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.065761; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.090476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.096307; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.050737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.050737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11432
9021 | SANDHG5C | 5A | SOUTH | 140 | CSC 1: -0.11364; CSC 2: -0.46433; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.028121; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.46433; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.028121; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.065761; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.065761; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.090476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.096307; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.050737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.050737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.090344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.11432
11001 | NAV1CT | 5C | WEST | 70.4 | CSC 1: -0.012481; CSC 2: -0.034881; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38297; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034881; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38297; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008924; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012412
11009 | NAV2CT | 1 | WEST | 71.4 | CSC 1: -0.012481; CSC 2: -0.034881; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38297; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034881; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38297; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008924; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012412
11011 | NAV3ST | 1 | WEST | 92.8 | CSC 1: -0.012481; CSC 2: -0.034881; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38297; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034881; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38297; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008924; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012412
11012 | NAV4CT | 1 | WEST | 80 | CSC 1: -0.012481; CSC 2: -0.034881; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38297; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034881; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38297; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008924; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012412
11013 | NAV5CT | 1 | WEST | 80 | CSC 1: -0.012481; CSC 2: -0.034881; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38297; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034881; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38297; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008924; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012412
11014 | NAV6ST | 1 | WEST | 115 | CSC 1: -0.012481; CSC 2: -0.034881; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38297; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034881; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38297; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007572; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008924; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.01074; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009914; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012412
11020 | TIEHVSG_1G | 1 | WEST | 208.2 | CSC 1: -0.012489; CSC 2: -0.034906; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38292; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034906; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38292; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.00893; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010746; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012421
11021 | TIEHVCG_1G | 1 | WEST | 142.1 | CSC 1: -0.012489; CSC 2: -0.034906; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38292; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034906; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38292; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.00893; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010746; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012421
11022 | TIEHVCG_2G | 1 | WEST | 132.4 | CSC 1: -0.012489; CSC 2: -0.034906; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38292; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034906; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38292; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.00893; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010746; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012421
11023 | TIEHVCG_3G | 1 | WEST | 137.4 | CSC 1: -0.012489; CSC 2: -0.034906; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38292; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034906; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38292; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.00893; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010746; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012421
11024 | TIEHVCG_4G | 1 | WEST | 147 | CSC 1: -0.012489; CSC 2: -0.034906; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38292; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034906; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38292; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.00893; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010746; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012421
11025 | TIEHVSG_2G | 1 | WEST | 213.2 | CSC 1: -0.012489; CSC 2: -0.034906; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38292; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.034906; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38292; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007577; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.00893; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010746; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012421
11056 | ROSCOE_1G | 1 | WEST | 41.8 | CSC 1: -0.010844; CSC 2: -0.029734; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.32676; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.029734; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.32676; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006618; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006618; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007626; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.009391; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004974; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004974; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010793
11057 | CHAMPION_1G | 1 | WEST | 25.3 | CSC 1: -0.010844; CSC 2: -0.029734; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.32676; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.029734; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.32676; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006618; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006618; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007626; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.009391; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004974; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004974; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010793
11058 | PYRON_1G | 1 | WEST | 49.8 | CSC 1: -0.010844; CSC 2: -0.029734; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.32676; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.029734; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.32676; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006618; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006618; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007626; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.009391; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004974; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004974; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010793
11059 | INADALE_1G | 1 | WEST | 39.4 | CSC 1: -0.010844; CSC 2: -0.029734; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.32676; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.029734; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.32676; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006618; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006618; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007626; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.009391; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004974; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004974; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010793
11065 | ELBOWCK_1G | 1 | WEST | 23.4 | CSC 1: -0.011723; CSC 2: -0.03261; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.38724; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.03261; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.38724; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00713; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00713; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010123; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005381; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005381; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011664
11147 | NOTREES_1G | 1 | WEST | 29.8 | CSC 1: -0.01308; CSC 2: -0.036675; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37852; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.036675; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37852; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007921; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011228; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.006015; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.01039; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.01039; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.006015; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.01039; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.013004
11309 | BULLCREK_2G | 1 | WEST | 20.9 | CSC 1: -0.011929; CSC 2: -0.033275; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.3702; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.033275; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.3702; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00725; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00725; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008473; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010301; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011869
11310 | BULLCREK_1G | 1 | WEST | 15.1 | CSC 1: -0.011929; CSC 2: -0.033275; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.3702; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.033275; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.3702; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00725; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00725; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008473; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010301; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009476; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011869
11320 | COYOTE_1G | 1 | WEST | 22.5 | CSC 1: -0.011973; CSC 2: -0.033409; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37058; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.033409; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37058; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007276; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007276; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008509; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010337; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005496; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009512; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009512; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005496; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009512; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011913
11691 | KMICHICT1_G | 1 | NORTH | 144 | CSC 1: 0.001655; CSC 2: -0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000317; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001665
11692 | KMICHICT2_G | 1 | NORTH | 146 | CSC 1: 0.001655; CSC 2: -0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000317; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001665
11693 | KMICHIST3_G | 2 | NORTH | 312 | CSC 1: 0.001655; CSC 2: -0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000317; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001665
11694 | KMICHICT4_G | 3 | NORTH | 144 | CSC 1: 0.001655; CSC 2: -0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000317; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001665
11695 | KMICHICT5_G | 4 | NORTH | 148 | CSC 1: 0.001655; CSC 2: -0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000317; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001665
11696 | KMICHIST6_G | 5 | NORTH | 310 | CSC 1: 0.001655; CSC 2: -0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: -0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006072; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: 0.001786; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001063; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000317; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002194; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.001316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.001665
12322 | ENNSTRAC_1G | 6 | NORTH | 196 | CSC 1: 0.000504; CSC 2: -0.005281; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.003281; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.005281; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.003281; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.000778; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.000778; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.001147; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.000998; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000231; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.000401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.000401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000231; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.000401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.000502
12323 | ENNSTRAC_2G | 1 | NORTH | 116 | CSC 1: 0.000504; CSC 2: -0.005281; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.003281; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.005281; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.003281; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.000778; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.000778; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.001147; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.000998; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.000231; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.000401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.000401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.000231; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.000401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.000502
12411 | FPLEFR1A_G | 2 | NORTH | 161 | CSC 1: 0.003135; CSC 2: -0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000892; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.003817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.003149
12412 | FPLEFR1B_G | 1 | NORTH | 164 | CSC 1: 0.003135; CSC 2: -0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000892; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.003817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.003149
12413 | FPLEFR1C_G | 2 | NORTH | 164 | CSC 1: 0.003135; CSC 2: -0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000892; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.003817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.003149
12414 | FPLEFR1S_G | 3 | NORTH | 414 | CSC 1: 0.003135; CSC 2: -0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000892; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.003817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.003149
12421 | FPLEFR2A_G | 4 | NORTH | 162 | CSC 1: 0.003135; CSC 2: -0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000892; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.003817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.003149
12422 | FPLEFR2B_G | 1 | NORTH | 161 | CSC 1: 0.003135; CSC 2: -0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000892; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.003817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.003149
12423 | FPLEFR2C_G | 2 | NORTH | 163 | CSC 1: 0.003135; CSC 2: -0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000892; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.003817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.003149
12424 | FPLEFR2S_G | 3 | NORTH | 415 | CSC 1: 0.003135; CSC 2: -0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.008002; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -4.4e-05; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002033; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000892; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.003817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001404; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.002492; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.003149
12440 | PARKD_1SVC8 | 4 | NORTH | 0 | CSC 1: 0.002536; CSC 2: -0.006516; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.00013; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006516; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.00013; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001929; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001929; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000502; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001136; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.002016; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.002016; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001136; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.002016; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.002548
12449 | PARKD_2SVC8 | 1 | NORTH | 0 | CSC 1: 0.002536; CSC 2: -0.006516; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.00013; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.006516; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.00013; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.001929; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.001929; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.000502; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.002739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.001136; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.002016; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.002016; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.001136; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.002016; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.002548
13116 | TGATEWAY_1G | 1 | NORTH | 151 | CSC 1: 0.006526; CSC 2: -0.014026; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.002345; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.014026; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.002345; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002829; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002829; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.003181; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.009428; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.002927; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.005188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.005188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.002927; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.005188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.006554
13117 | TGATEWAY_2G | 1 | NORTH | 130 | CSC 1: 0.006526; CSC 2: -0.014026; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.002345; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.014026; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.002345; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002829; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002829; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.003181; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.009428; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.002927; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.005188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.005188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.002927; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.005188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.006554
13118 | TGATEWAY_3G | 2 | NORTH | 148 | CSC 1: 0.006526; CSC 2: -0.014026; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.002345; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.014026; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.002345; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002829; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002829; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.003181; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.009428; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.002927; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.005188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.005188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.002927; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.005188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.006554
13119 | TGATEWAY_4G | 3 | NORTH | 399 | CSC 1: 0.006526; CSC 2: -0.014026; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.002345; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.014026; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.002345; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002829; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002829; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.003181; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.009428; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.002927; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.005188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.005188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.002927; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.005188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.006554
13131 | CALFREST_1G | 4 | NORTH | 150.7 | CSC 1: 0.011428; CSC 2: -0.02111; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.005008; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.02111; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.005008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.01109; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.016608; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.005126; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.009084; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.009084; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.005126; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.009084; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.011475
13132 | CALFREST_2G | 1 | NORTH | 151 | CSC 1: 0.011428; CSC 2: -0.02111; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.005008; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.02111; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.005008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.01109; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.016608; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.005126; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.009084; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.009084; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.005126; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.009084; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.011475
13133 | CALFREST_3G | 2 | NORTH | 177.4 | CSC 1: 0.011428; CSC 2: -0.02111; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.005008; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.02111; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.005008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.002145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.002145; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.01109; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.016608; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.005126; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.009084; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.009084; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.005126; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.009084; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.011475
13134 | CALFREST_4G | 3 | NORTH | 151.5 | CSC 1: 0.011224; CSC 2: -0.0209; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.004908; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.0209; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.004908; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.010864; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.016392; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.005035; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.008922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.008922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.005035; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.008922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.01127
13135 | CALFREST_5G | 4 | NORTH | 152.3 | CSC 1: 0.011224; CSC 2: -0.0209; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.004908; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.0209; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.004908; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.010864; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.016392; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.005035; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.008922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.008922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.005035; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.008922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.01127
13136 | CALFREST_6G | 5 | NORTH | 177.5 | CSC 1: 0.011224; CSC 2: -0.0209; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.004908; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.0209; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.004908; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.00208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.00208; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: 0.010864; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: 0.016392; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.005035; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.008922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.008922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.005035; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.008922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.01127
32883 | BRYN_DNSBY3 | 6 | NORTH | 0 | CSC 1: 0.035069; CSC 2: -0.13142; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.011826; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.13142; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.011826; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.20421; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.20421; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.16894; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.14132; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.015726; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.027875; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.027875; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.015726; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.027875; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.035216
32884 | BRYN_DNSBY13 | 1 | NORTH | 46 | CSC 1: 0.035069; CSC 2: -0.13142; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.011826; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.13142; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.011826; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.20421; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.20421; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.16894; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.14132; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.015726; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.027875; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.027875; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.015726; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.027875; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.035216
32886 | BRYN_ATKINS3 | 1 | NORTH | 0 | CSC 1: 0.038428; CSC 2: -0.12543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.011732; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.12543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.011732; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.21781; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.21781; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1776; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.15045; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.017226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.017226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.038594
32887 | BRYN_ATKINS6 | MB | NORTH | 0 | CSC 1: 0.038428; CSC 2: -0.12543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.011732; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.12543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.011732; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.21781; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.21781; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1776; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.15045; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.017226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.017226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.038594
32888 | BRYN_ATKINS7 | MB | NORTH | 13.6 | CSC 1: 0.038428; CSC 2: -0.12543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.011732; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.12543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.011732; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.21781; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.21781; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1776; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.15045; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.017226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.017226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.038594
32890 | BRYN_ATKINS4 | 1 | NORTH | 0 | CSC 1: 0.038428; CSC 2: -0.12543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.011732; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.12543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.011732; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.21781; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.21781; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1776; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.15045; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.017226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.017226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.038594
32891 | BRYN_ATKINS5 | MB | NORTH | 0 | CSC 1: 0.038428; CSC 2: -0.12543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.011732; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.12543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.011732; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.21781; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.21781; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1776; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.15045; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.017226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.017226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.030545; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.038594
32892 | BRYN_DNSBY14 | MB | NORTH | 105 | CSC 1: 0.035069; CSC 2: -0.13142; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.011826; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.13142; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.011826; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: 0.20421; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: 0.20421; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.16894; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.14132; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.015726; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.027875; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.027875; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.015726; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: 0.027875; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.035216
36998 | RDCNYNG1 | 1 | WEST | 16.8 | CSC 1: -0.011496; CSC 2: -0.031944; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.35538; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.031944; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.35538; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006997; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006997; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008122; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.009954; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005273; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009132; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009132; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005273; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009132; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011441
38332 | TNWDWRDU2_8 | 1 | WEST | 20 | CSC 1: -0.018459; CSC 2: -0.052642; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.35811; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.052642; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.35811; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.011058; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.011058; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.013726; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.015592; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.008533; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.014661; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.014661; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.008533; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.014661; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.018314
38437 | TNSRBNMESA9 | 1 | WEST | 37.5 | CSC 1: -0.018507; CSC 2: -0.052784; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.35792; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.052784; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.35792; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.011086; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.011086; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.013765; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.015631; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.008556; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.014699; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.014699; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.008556; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.014699; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.018361
38611 | TNBPAMCG1_8 | 1 | HOUSTON | 153.2 | CSC 1: -0.21876; CSC 2: -0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17568; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22408
38612 | TNBPAMCG2_8 | 1 | HOUSTON | 153.5 | CSC 1: -0.21876; CSC 2: -0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17568; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22408
38613 | TNBPAMCG3_8 | 2 | HOUSTON | 152.3 | CSC 1: -0.21876; CSC 2: -0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17568; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22408
38614 | TNBPAMCG4_8 | 3 | HOUSTON | 96 | CSC 1: -0.21876; CSC 2: -0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17568; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22408
38615 | TNBPAMCG5_8 | 4 | HOUSTON | 244 | CSC 1: -0.21876; CSC 2: -0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17568; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22408
38711 | TNTXCTY1CG8 | 1 | HOUSTON | 100.3 | CSC 1: -0.21876; CSC 2: -0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17568; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22408
38712 | TNTXCTY2CG8 | 1 | HOUSTON | 92.9 | CSC 1: -0.21876; CSC 2: -0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17568; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22408
38713 | TNTXCTY3CG8 | 1 | HOUSTON | 102.7 | CSC 1: -0.21876; CSC 2: -0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17568; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22408
38714 | TNTXCTY4CG8 | 1 | HOUSTON | 103 | CSC 1: -0.21876; CSC 2: -0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.25273; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.019532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13769; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1858; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17568; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19402; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22408
39760 | TNSCLP1___8 | 1 | HOUSTON | 93.4 | CSC 1: -0.21372; CSC 2: -0.28082; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.021172; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.28082; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.021172; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.12804; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.12804; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.17304; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.16503; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.17206; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.17206; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.17206; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.20839
39770 | TNSCLP2___8 | 1 | HOUSTON | 91.6 | CSC 1: -0.21372; CSC 2: -0.28082; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.021172; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.28082; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.021172; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.12804; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.12804; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.17304; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.16503; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.17206; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.17206; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.17206; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.20839
39775 | TNSCLP4___8 | 1 | HOUSTON | 95.2 | CSC 1: -0.21372; CSC 2: -0.28082; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.021172; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.28082; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.021172; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.12804; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.12804; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.17304; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.16503; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.17206; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.17206; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.17206; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.20839
39790 | TNSCLP3___8 | 1 | HOUSTON | 87.6 | CSC 1: -0.21372; CSC 2: -0.28082; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.021172; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.28082; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.021172; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.12804; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.12804; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.17304; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.16503; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.17206; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.17206; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.17206; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.20839
48511 | LPE_GT1_8070 | 1 | HOUSTON | 42 | CSC 1: -0.21561; CSC 2: -0.23543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018558; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018558; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.1436; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.1436; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19363; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15616; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.21079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.21079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15616; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.21079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23663
48512 | LPE_GT2_8075 | 1 | HOUSTON | 42 | CSC 1: -0.21561; CSC 2: -0.23543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018558; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018558; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.1436; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.1436; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19363; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15616; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.21079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.21079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15616; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.21079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23663
48513 | LPE_GT3_8080 | 2 | HOUSTON | 39 | CSC 1: -0.21561; CSC 2: -0.23543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018558; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018558; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.1436; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.1436; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19363; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15616; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.21079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.21079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15616; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.21079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23663
48514 | LPE_GT4_8085 | 3 | HOUSTON | 39 | CSC 1: -0.21561; CSC 2: -0.23543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018558; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018558; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.1436; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.1436; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19363; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15616; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.21079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.21079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15616; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.21079; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23663
48521 | BVE_GT1_GT1 | 4 | HOUSTON | 167.7 | CSC 1: -0.22422; CSC 2: -0.27125; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.020534; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.27125; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.020534; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13138; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13138; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.17747; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.16873; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.11184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.17467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.17467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.11184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.17467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21007
48522 | BVE_GT2_5035 | 1 | HOUSTON | 166.4 | CSC 1: -0.22422; CSC 2: -0.27125; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.020534; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.27125; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.020534; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13138; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13138; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.17747; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.16873; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.11184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.17467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.17467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.11184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.17467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21007
48523 | BVE_ST1_GN1 | 2 | HOUSTON | 252.4 | CSC 1: -0.22422; CSC 2: -0.27125; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.020534; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.27125; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.020534; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13138; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13138; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.17747; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.16873; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.11184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.17467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.17467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.11184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.17467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21007
48531 | BYU_GT1_8075 | 3 | HOUSTON | 65 | CSC 1: -0.21654; CSC 2: -0.2427; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018966; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.2427; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018966; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14111; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14111; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17947; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.14626; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.14626; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.232
48532 | BYU_GT2_8055 | 1 | HOUSTON | 62 | CSC 1: -0.21654; CSC 2: -0.2427; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018966; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.2427; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018966; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14111; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14111; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17947; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.14626; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.14626; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.232
48533 | BYU_GT3_8060 | 2 | HOUSTON | 67 | CSC 1: -0.21654; CSC 2: -0.2427; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018966; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.2427; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018966; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14111; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14111; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17947; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.14626; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.14626; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.232
48534 | BYU_GT4_8065 | 3 | HOUSTON | 65 | CSC 1: -0.21654; CSC 2: -0.2427; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018966; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.2427; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018966; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14111; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14111; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17947; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.14626; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.14626; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20349; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.232
48581 | CBY_GN1_1 | 4 | HOUSTON | 595.2 | CSC 1: -0.21506; CSC 2: -0.22963; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018236; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.22963; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018236; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14558; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14558; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19625; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18439; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.16466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.21672; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.21672; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.16466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.21672; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.24001
48582 | CBY_GN2_2 | 1 | HOUSTON | 596.8 | CSC 1: -0.21534; CSC 2: -0.23174; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018353; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23174; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018353; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14486; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14486; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19529; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.1836; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.16176; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.21459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.21459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.16176; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.21459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23867
48583 | CBY_GT4_1 | 2 | HOUSTON | 172 | CSC 1: -0.21544; CSC 2: -0.22867; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018184; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.22867; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.1459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.1459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19668; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18475; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.16943; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.21851; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.21851; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.16943; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.21851; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23928
48584 | CBY_GT4_2 | 1 | HOUSTON | 172 | CSC 1: -0.21544; CSC 2: -0.22867; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018184; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.22867; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.1459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.1459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19668; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18475; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.16943; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.21851; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.21851; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.16943; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.21851; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23928
48585 | CBY_ST4_1 | 2 | HOUSTON | 172 | CSC 1: -0.21544; CSC 2: -0.22867; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018184; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.22867; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018184; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.1459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.1459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19668; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18475; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.16943; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.21851; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.21851; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.16943; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.21851; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23928
48591 | CHE_GT2_5030 | 3 | HOUSTON | 173 | CSC 1: -0.19975; CSC 2: -0.21543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.017445; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.21543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.017445; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.15043; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.15043; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.20266; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18974; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.20762; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.2429; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.2429; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.20762; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.2429; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.25061
48594 | CHE_GN4_8025 | 2 | HOUSTON | 142 | CSC 1: -0.21728; CSC 2: -0.23586; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018574; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23586; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14346; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14346; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19344; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18205; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.2088; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.2088; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.2088; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23633
48641 | DPEC_GT15040 | 4 | HOUSTON | 163.2 | CSC 1: -0.21652; CSC 2: -0.23913; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018772; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23913; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018772; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14233; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14233; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18081; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15567; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15567; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23265
48642 | DPEC_GT25025 | 1 | HOUSTON | 157.1 | CSC 1: -0.21652; CSC 2: -0.23913; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018772; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23913; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018772; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14233; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14233; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18081; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15567; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15567; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23265
48643 | DPEC_GT35010 | 2 | HOUSTON | 157.5 | CSC 1: -0.21652; CSC 2: -0.23913; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018772; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23913; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018772; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14233; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14233; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18081; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15567; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15567; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23265
48644 | DPEC_GT45070 | 3 | HOUSTON | 157 | CSC 1: -0.21652; CSC 2: -0.23913; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018772; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23913; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018772; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14233; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14233; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18081; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15567; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15567; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23265
48645 | DPEC_ST55065 | 4 | HOUSTON | 282 | CSC 1: -0.21652; CSC 2: -0.23913; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018772; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23913; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018772; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14233; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14233; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19195; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18081; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15567; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15567; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23265
48671 | FTR_GT1_5105 | 5 | NORTH | 154.2 | CSC 1: 0.037011; CSC 2: -0.12309; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.012408; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.12309; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.012408; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.18188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.18188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.24427; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.22445; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.007045; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.097288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.097288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.007045; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.90271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.03321
48672 | FTR_GT2_5110 | 1 | NORTH | 159 | CSC 1: 0.037011; CSC 2: -0.12309; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.012408; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.12309; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.012408; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.18188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.18188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.24427; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.22445; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.007045; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.097288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.097288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.007045; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.90271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.03321
48673 | FTR_GT3_5085 | 2 | NORTH | 158 | CSC 1: 0.037011; CSC 2: -0.12309; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.012408; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.12309; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.012408; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.18188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.18188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.24427; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.22445; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.007045; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.097288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.097288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.007045; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.90271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.03321
48674 | FTR_CN4_5095 | 3 | NORTH | 380 | CSC 1: 0.037011; CSC 2: -0.12309; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.012408; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.12309; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.012408; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.18188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.18188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.24427; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.22445; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: 0.007045; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: 0.097288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: 0.097288; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: 0.007045; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.90271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: 0.03321
48690 | GBY_GN5_5 | 4 | HOUSTON | 398 | CSC 1: -0.21065; CSC 2: -0.22692; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018078; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.22692; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018078; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14651; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14651; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19748; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18542; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.16158; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.21896; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.21896; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.16158; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.21896; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.2463
48691 | GBY_73741085 | 5 | HOUSTON | 37.6 | CSC 1: -0.23035; CSC 2: -0.24259; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018941; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.24259; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018941; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17952; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22818
48691 | GBY_73741085 | A | HOUSTON | 37.6 | CSC 1: -0.23035; CSC 2: -0.24259; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018941; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.24259; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018941; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17952; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22818
48692 | GBY_81821075 | B | HOUSTON | 37.6 | CSC 1: -0.23035; CSC 2: -0.24259; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018941; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.24259; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018941; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17952; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22818
48692 | GBY_81821075 | C | HOUSTON | 44 | CSC 1: -0.23035; CSC 2: -0.24259; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018941; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.24259; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018941; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17952; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22818
48693 | GBY_83841065 | D | HOUSTON | 45.6 | CSC 1: -0.23035; CSC 2: -0.24259; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018941; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.24259; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018941; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17952; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22818
48693 | GBY_83841065 | E | HOUSTON | 43.2 | CSC 1: -0.23035; CSC 2: -0.24259; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018941; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.24259; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018941; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19041; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17952; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.13008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.13008; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19373; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22818
48731 | CBE_GT1 | F | HOUSTON | 76 | CSC 1: -0.19435; CSC 2: -0.31415; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.023095; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.31415; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.023095; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.1166; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.1166; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.15791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.15241; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.087922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.087922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.19465
48732 | CBE_GT2 | 1 | HOUSTON | 76 | CSC 1: -0.19435; CSC 2: -0.31415; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.023095; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.31415; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.023095; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.1166; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.1166; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.15791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.15241; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.087922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.087922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.19465
48733 | CBE_ST12 | 1 | HOUSTON | 105 | CSC 1: -0.19435; CSC 2: -0.31415; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.023095; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.31415; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.023095; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.1166; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.1166; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.15791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.15241; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.087922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.087922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.19465
48734 | CBE_GT3 | 1 | HOUSTON | 76 | CSC 1: -0.19435; CSC 2: -0.31415; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.023095; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.31415; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.023095; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.1166; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.1166; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.15791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.15241; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.087922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.087922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.19465
48735 | CBE_GT4 | 1 | HOUSTON | 76 | CSC 1: -0.19435; CSC 2: -0.31415; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.023095; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.31415; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.023095; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.1166; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.1166; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.15791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.15241; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.087922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.087922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.19465
48736 | CBE_ST34 | 1 | HOUSTON | 105 | CSC 1: -0.19435; CSC 2: -0.31415; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.023095; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.31415; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.023095; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.1166; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.1166; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.15791; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.15241; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.087922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.087922; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.15454; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.19465
48740 | PSG_GN2_8050 | 1 | HOUSTON | 182 | CSC 1: -0.21579; CSC 2: -0.23801; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.0187; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23801; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.0187; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19246; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18124; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15229; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15229; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23519
48741 | PSG_GT2_8040 | 1 | HOUSTON | 158.6 | CSC 1: -0.21579; CSC 2: -0.23801; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.0187; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23801; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.0187; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19246; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18124; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15229; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15229; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23519
48742 | PSG_GT3_8060 | 1 | HOUSTON | 157 | CSC 1: -0.21579; CSC 2: -0.23801; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.0187; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23801; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.0187; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14272; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19246; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18124; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15229; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15229; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23519
48772 | PHR_GN2_2 | 1 | HOUSTON | 0 | CSC 1: -0.21745; CSC 2: -0.2476; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.019243; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.2476; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.019243; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13944; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13944; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.18812; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17762; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.14149; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.19902; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.19902; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.14149; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.19902; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22815
48811 | CVC_GT3_5045 | MB | HOUSTON | 156 | CSC 1: -0.19975; CSC 2: -0.21543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.017445; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.21543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.017445; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.15043; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.15043; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.20266; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18974; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.20762; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.2429; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.2429; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.20762; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.2429; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.25061
48812 | CVC_GT2_5020 | 3 | HOUSTON | 158 | CSC 1: -0.19975; CSC 2: -0.21543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.017445; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.21543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.017445; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.15043; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.15043; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.20266; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18974; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.20762; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.2429; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.2429; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.20762; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.2429; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.25061
48813 | CVC_GT1_5035 | 2 | HOUSTON | 160 | CSC 1: -0.19975; CSC 2: -0.21543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.017445; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.21543; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.017445; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.15043; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.15043; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.20266; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18974; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.20762; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.2429; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.2429; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.20762; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.2429; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.25061
48815 | CVC_GT4_8005 | 1 | HOUSTON | 165 | CSC 1: -0.21182; CSC 2: -0.22936; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018216; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.22936; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018216; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14567; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14567; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19637; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.1845; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15673; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.21574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.21574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15673; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.21574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.24465
48841 | SJS_GT1_GT1 | 4 | HOUSTON | 78 | CSC 1: -0.21591; CSC 2: -0.24013; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018821; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.24013; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018821; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14199; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14199; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1915; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18044; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.14891; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20593; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20593; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.14891; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20593; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23408
48842 | SJS_GT2_GT2 | 1 | HOUSTON | 81 | CSC 1: -0.21591; CSC 2: -0.24013; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018821; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.24013; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018821; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14199; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14199; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1915; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18044; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.14891; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20593; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20593; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.14891; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20593; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23408
48851 | SRB_GN1_1 | 2 | HOUSTON | 165 | CSC 1: -0.21584; CSC 2: -0.23813; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018709; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23813; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018709; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14267; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14267; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1924; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18119; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15186; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20794; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20794; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15186; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20794; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23516
48852 | SRB_GN2_2 | 1 | HOUSTON | 176 | CSC 1: -0.21586; CSC 2: -0.23818; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018711; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23818; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018711; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14266; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14266; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19238; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18117; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15178; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20788; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20788; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15178; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20788; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23513
48853 | SRB_GN3_3 | 2 | HOUSTON | 213 | CSC 1: -0.21576; CSC 2: -0.23794; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018698; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23794; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018698; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14274; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14274; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18126; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.1521; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20814; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20814; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.1521; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20814; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23533
48854 | SRB_GN4_4 | 3 | HOUSTON | 228 | CSC 1: -0.21577; CSC 2: -0.23794; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018698; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23794; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018698; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14274; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14274; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18126; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15222; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15222; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20817; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23528
48855 | SRB_GT211035 | 4 | HOUSTON | 0 | CSC 1: -0.21588; CSC 2: -0.23822; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018714; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23822; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018714; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14264; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14264; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19236; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15173; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15173; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23509
48855 | SRB_GT211035 | B1 | HOUSTON | 0 | CSC 1: -0.21588; CSC 2: -0.23822; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018714; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23822; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018714; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14264; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14264; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19236; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.15173; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.20784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.20784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.15173; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.20784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23509
48873 | THW_ST3_ST_3 | B2 | HOUSTON | 107 | CSC 1: -0.25817; CSC 2: -0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19423; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22508
48874 | THW_ST4_ST_4 | 3 | HOUSTON | 108 | CSC 1: -0.25817; CSC 2: -0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19423; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22508
48875 | THW_3132 | 4 | HOUSTON | 55 | CSC 1: -0.25817; CSC 2: -0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19423; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22508
48875 | THW_3132 | A | HOUSTON | 53 | CSC 1: -0.25817; CSC 2: -0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19423; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22508
48877 | THW_3334 | B | HOUSTON | 55 | CSC 1: -0.25817; CSC 2: -0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19423; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22508
48877 | THW_3334 | C | HOUSTON | 57 | CSC 1: -0.25817; CSC 2: -0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19423; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22508
48879 | THW_4142 | D | HOUSTON | 56 | CSC 1: -0.25817; CSC 2: -0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19423; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22508
48879 | THW_4142 | E | HOUSTON | 55 | CSC 1: -0.25817; CSC 2: -0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19423; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22508
48881 | THW_4344 | F | HOUSTON | 58 | CSC 1: -0.25817; CSC 2: -0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19423; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22508
48881 | THW_4344 | G | HOUSTON | 58 | CSC 1: -0.25817; CSC 2: -0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23414; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018467; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14405; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19423; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18271; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.10831; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.18179; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.22508
48883 | THW_GT1_GT_1 | H | HOUSTON | 0 | CSC 1: -0.24952; CSC 2: -0.23133; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.018314; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.23133; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.018314; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14501; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19549; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18376; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.11113; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.18737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.18737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.11113; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.18737; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.23239
48885 | THW_5152 | B2 | HOUSTON | 46.4 | CSC 1: -0.28523; CSC 2: -0.22483; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.017961; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.22483; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.017961; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14722; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14722; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19842; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18621; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.12401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.12401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21224
48885 | THW_5152 | A | HOUSTON | 47.2 | CSC 1: -0.28523; CSC 2: -0.22483; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.017961; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.22483; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.017961; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14722; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14722; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19842; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18621; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.12401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.12401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21224
48886 | THW_5354 | B | HOUSTON | 45.6 | CSC 1: -0.28523; CSC 2: -0.22483; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.017961; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.22483; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.017961; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14722; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14722; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19842; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18621; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.12401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.12401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21224
48886 | THW_5354 | C | HOUSTON | 46.4 | CSC 1: -0.28523; CSC 2: -0.22483; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.017961; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.22483; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.017961; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14722; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14722; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19842; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18621; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.12401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.12401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21224
48887 | THW_5556 | D | HOUSTON | 47.2 | CSC 1: -0.28523; CSC 2: -0.22483; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.017961; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.22483; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.017961; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14722; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14722; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19842; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18621; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.12401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.12401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21224
48887 | THW_5556 | E | HOUSTON | 45.6 | CSC 1: -0.28523; CSC 2: -0.22483; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.017961; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.22483; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.017961; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14722; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14722; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.19842; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18621; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.12401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.12401; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1816; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21224
48911 | TGF_GT1_8000 | F | HOUSTON | 69.2 | CSC 1: -0.19835; CSC 2: -0.30785; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.022898; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.30785; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.022898; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.11866; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.11866; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.16062; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.15466; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.094734; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.15841; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.15841; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.094734; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.15841; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.19585
48921 | WAP_GN1_1 | 1 | HOUSTON | 166 | CSC 1: -0.22396; CSC 2: -0.26482; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.02015; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.26482; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.02015; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.18039; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17117; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.11175; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.11175; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21643
48922 | WAP_GN2_2 | 1 | HOUSTON | 166 | CSC 1: -0.22396; CSC 2: -0.26482; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.02015; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.26482; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.02015; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.18039; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17117; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.11175; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.11175; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21643
48923 | WAP_GN3_3 | 2 | HOUSTON | 248 | CSC 1: -0.22396; CSC 2: -0.26482; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.02015; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.26482; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.02015; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.18039; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17117; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.11175; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.11175; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21643
48924 | WAP_GN4_4 | 3 | HOUSTON | 546 | CSC 1: -0.22396; CSC 2: -0.26482; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.02015; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.26482; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.02015; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.18039; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17117; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.11175; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.11175; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21643
48929 | WAPGT21_GT1 | 4 | HOUSTON | 0 | CSC 1: -0.22396; CSC 2: -0.26482; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.02015; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.26482; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.02015; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.13359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.13359; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.18039; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.17117; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.11175; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.11175; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.17834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.21643
48940 | WARVUE_GT1 | B1 | HOUSTON | 12 | CSC 1: -0.2148; CSC 2: -0.22973; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.01824; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.22973; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.01824; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.14555; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.14555; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.1962; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.18436; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.16143; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.21582; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.21582; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.16143; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.21582; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.24104
58909 | PEARSALLSCG1 | G1 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58909 | PEARSALLSCG1 | 1 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58909 | PEARSALLSCG1 | 2 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58909 | PEARSALLSCG1 | 3 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58909 | PEARSALLSCG1 | 4 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58909 | PEARSALLSCG1 | 5 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58919 | PEARSALLSCG2 | 6 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58919 | PEARSALLSCG2 | 1 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58919 | PEARSALLSCG2 | 2 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58919 | PEARSALLSCG2 | 3 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58919 | PEARSALLSCG2 | 4 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58919 | PEARSALLSCG2 | 5 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58929 | PEARSALLSCG3 | 6 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58929 | PEARSALLSCG3 | 1 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58929 | PEARSALLSCG3 | 2 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58929 | PEARSALLSCG3 | 3 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58929 | PEARSALLSCG3 | 4 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58929 | PEARSALLSCG3 | 5 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58949 | PEARSALLSCG4 | 6 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58949 | PEARSALLSCG4 | 1 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58949 | PEARSALLSCG4 | 2 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58949 | PEARSALLSCG4 | 3 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58949 | PEARSALLSCG4 | 4 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
58949 | PEARSALLSCG4 | 5 | HOUSTON | 0 | CSC 1: -0.1374; CSC 2: -0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38131; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.048745; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08048; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.10978; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11116; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.064551; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.10909; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.13542
60000 | DSKY2 | 6 | WEST | 19.1 | CSC 1: -0.020593; CSC 2: -0.059001; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.3495; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.059001; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.3495; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.012302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.012302; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.015439; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.017324; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.009531; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.016355; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.016355; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.009531; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.016355; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.02042
60003 | KING_NE1A | 1 | WEST | 20 | CSC 1: -0.018389; CSC 2: -0.05244; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.35834; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.05244; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.35834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.011017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.011017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.01367; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.015536; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.0085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.014606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.014606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.0085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.014606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.018245
60005 | KING_SE1A | 1 | WEST | 10 | CSC 1: -0.018389; CSC 2: -0.05244; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.35834; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.05244; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.35834; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.011017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.011017; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.01367; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.015536; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.0085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.014606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.014606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.0085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.014606; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.018245
60007 | KING_SW1A | 1 | WEST | 20 | CSC 1: -0.018074; CSC 2: -0.051519; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.35948; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.051519; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.35948; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.010833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.010833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.013416; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.015281; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.008353; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.014356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.014356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.008353; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.014356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.017934
60016 | WOODWRD11A | 1 | WEST | 20 | CSC 1: -0.018448; CSC 2: -0.052609; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.35815; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.052609; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.35815; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.011052; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.011052; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.013717; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.015583; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.008528; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.014653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.014653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.008528; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.014653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.018303
60017 | ORNNWP1 | 1 | WEST | 20 | CSC 1: -0.020179; CSC 2: -0.057701; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.35168; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.057701; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.35168; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.012061; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.012061; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.015109; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.016986; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.009339; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.016027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.016027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.009339; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.016027; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.020011
60018 | DSKY1 | 1 | WEST | 21 | CSC 1: -0.020744; CSC 2: -0.059359; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.34958; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.059359; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.34958; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.01239; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.01239; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.015563; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.017443; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.009603; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.016475; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.016475; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.009603; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.016475; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.020568
60019 | KING_NW1A | 1 | WEST | 20 | CSC 1: -0.018074; CSC 2: -0.051519; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.35948; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.051519; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.35948; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.010833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.010833; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.013416; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.015281; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.008353; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.014356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.014356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.008353; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.014356; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.017934
60057 | CALLAHAN1A | 1 | WEST | 22.8 | CSC 1: -0.0131; CSC 2: -0.038903; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.33739; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.038903; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.33739; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007926; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007926; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009316; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011387; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005995; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.010407; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.010407; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005995; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.010407; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.013049
60058 | BUFF_GAP1A | 1 | WEST | 24 | CSC 1: -0.011643; CSC 2: -0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010087; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011591
60060 | CIRELLO | 1 | WEST | 46.6 | CSC 1: -0.011643; CSC 2: -0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010087; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011591
60063 | BUFF_GAP1B | 1 | WEST | 34 | CSC 1: -0.011643; CSC 2: -0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010087; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011591
60066 | H_HOLLOW1A | 1 | WEST | 44.4 | CSC 1: -0.011643; CSC 2: -0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010087; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011591
60068 | HHOLLOW21A | 1 | WEST | 36.8 | CSC 1: -0.011643; CSC 2: -0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010087; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011591
60070 | HHOLLOW31A | 1 | WEST | 44.8 | CSC 1: -0.011643; CSC 2: -0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010087; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011591
60072 | HHOLLOW41A | 1 | WEST | 23 | CSC 1: -0.011643; CSC 2: -0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.032759; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.43205; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007085; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.008226; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.010087; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005336; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.009249; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.011591
60081 | WHRLWIND1A | 1 | WEST | 12 | CSC 1: -0.010289; CSC 2: -0.028071; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.27469; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.028071; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.27469; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.00629; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.00629; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007154; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.008974; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004712; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008174; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008174; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004712; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008174; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010246
60201 | RIO DRCS | 1 | WEST | 0 | CSC 1: -0.0183; CSC 2: -0.052169; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.35874; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.052169; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.35874; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.010965; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.010965; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.013598; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.015463; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.008459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.014535; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.014535; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.008459; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.014535; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.018156
60202 | FRNDDRCS | F | WEST | 0 | CSC 1: -0.029482; CSC 2: -0.084983; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.31752; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.084983; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.31752; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.017486; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.017486; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.022591; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.024521; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.013698; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.023413; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.023413; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.013698; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.023413; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.029189
71051 | L_BITTCR1_1N | F | WEST | 7.5 | CSC 1: -0.010892; CSC 2: -0.030004; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.43453; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.030004; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.43453; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006646; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006646; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007656; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00944; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004994; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004994; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010842
71054 | L_SWEETW1_1N | W1 | WEST | 21.5 | CSC 1: -0.010892; CSC 2: -0.030004; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.43453; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.030004; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.43453; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006646; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006646; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007656; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00944; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004994; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004994; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010842
71057 | L_SWEETW1_2N | W1 | WEST | 27 | CSC 1: -0.010892; CSC 2: -0.030004; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.43453; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.030004; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.43453; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006646; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006646; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007656; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00944; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004994; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004994; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010842
71059 | L_SWEETW1_3N | W1 | WEST | 23.8 | CSC 1: -0.010892; CSC 2: -0.030004; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.43453; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.030004; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.43453; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006646; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006646; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007656; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00944; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004994; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004994; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010842
71060 | L_SWEETW1_4N | W1 | WEST | 21 | CSC 1: -0.010892; CSC 2: -0.030004; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.43453; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.030004; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.43453; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006646; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006646; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007656; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00944; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004994; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004994; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010842
71061 | L_SWEETW1_5N | W1 | WEST | 16.1 | CSC 1: -0.010892; CSC 2: -0.030004; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.43453; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.030004; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.43453; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.006646; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.006646; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.007656; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.00944; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.004994; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.004994; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.008653; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.010842
76031 | L_GOATMO1_1N | W1 | WEST | 30 | CSC 1: -0.012772; CSC 2: -0.036407; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.37015; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.036407; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.37015; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007744; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007744; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009123; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011018; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.00586; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.010146; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.010146; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.00586; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.010146; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.01271
76091 | L_DIVIDE1_1N | W1 | WEST | 22.5 | CSC 1: -0.013016; CSC 2: -0.037266; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.36659; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.037266; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.36659; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007886; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007886; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011224; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005972; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.01034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.01034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005972; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.01034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012953
76095 | L_CAPRSI1_1N | W1 | WEST | 29.9 | CSC 1: -0.013016; CSC 2: -0.037266; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.36659; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.037266; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.36659; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007886; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007886; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011224; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005972; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.01034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.01034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005972; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.01034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012953
76096 | L_CAPRSI1_2N | W1 | WEST | 37.2 | CSC 1: -0.013016; CSC 2: -0.037266; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.36659; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.037266; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.36659; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007886; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007886; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011224; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005972; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.01034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.01034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005972; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.01034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012953
76097 | L_CAPRGE1_1N | W1 | WEST | 42.9 | CSC 1: -0.013016; CSC 2: -0.037266; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.36659; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.037266; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.36659; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.007886; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.007886; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.009313; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.011224; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.005972; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.01034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.01034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.005972; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.01034; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.012953
78189 | L_CUERHY9_1Y | W1 | SOUTH | 12 | CSC 1: -0.14251; CSC 2: -0.4071; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.029472; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.4071; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.029472; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.083748; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.083748; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11437; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11602; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.065188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11328; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11328; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.065188; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11328; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.14209
80003 | MILHWYS | F | SOUTH | 0 | CSC 1: -0.15776; CSC 2: -0.37553; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.031152; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37553; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.031152; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092717; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092717; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12622; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075341; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075341; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1252; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15443
80012 | LAR | F | SOUTH | 0 | CSC 1: -0.14582; CSC 2: -0.37044; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.045863; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37044; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.045863; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.08559; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.08559; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11658; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.069162; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.069162; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.14315
80080 | GWINDT11A | 1 | SOUTH | 28.2 | CSC 1: -0.15791; CSC 2: -0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12634; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15457
80080 | GWINDT11A | 2 | SOUTH | 0 | CSC 1: -0.15791; CSC 2: -0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12634; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15457
80080 | GWINDT11A | 3 | SOUTH | 0 | CSC 1: -0.15791; CSC 2: -0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12634; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15457
80080 | GWINDT11A | 4 | SOUTH | 3.8 | CSC 1: -0.15791; CSC 2: -0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12634; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15457
80081 | GWINDT21A | 1 | SOUTH | 28.2 | CSC 1: -0.15791; CSC 2: -0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12634; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15457
80081 | GWINDT21A | 2 | SOUTH | 7.2 | CSC 1: -0.15791; CSC 2: -0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12634; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15457
80081 | GWINDT21A | 3 | SOUTH | 8.6 | CSC 1: -0.15791; CSC 2: -0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12634; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15457
80081 | GWINDT21A | 4 | SOUTH | 4.4 | CSC 1: -0.15791; CSC 2: -0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12634; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15457
80180 | PNSCALT11A | 1 | SOUTH | 43.8 | CSC 1: -0.15791; CSC 2: -0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12634; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15457
80180 | PNSCALT11A | 2 | SOUTH | 10 | CSC 1: -0.15791; CSC 2: -0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12634; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15457
80181 | PNSCALT21A | 1 | SOUTH | 16.5 | CSC 1: -0.15791; CSC 2: -0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12634; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15457
80181 | PNSCALT21A | 2 | SOUTH | 10 | CSC 1: -0.15791; CSC 2: -0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37559; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030971; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.092806; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12634; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12585; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075419; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12532; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15457
80263 | B_DAVIS31A | 3 | HOUSTON | 0 | CSC 1: -0.15864; CSC 2: -0.37459; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030735; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37459; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.093257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.093257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12635; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1259; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1259; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1259; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15527
80264 | B_DAVIS41A | 4 | HOUSTON | 0 | CSC 1: -0.15864; CSC 2: -0.37459; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.030735; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37459; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.030735; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.093257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.093257; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12635; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.075784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1259; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1259; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.075784; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1259; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15527
80265 | LARECU40A | 4 | SOUTH | 100 | CSC 1: -0.14582; CSC 2: -0.37044; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.045866; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37044; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.045866; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.085589; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.085589; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11658; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.06916; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.06916; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.14314
80266 | LARECU50A | 5 | SOUTH | 100 | CSC 1: -0.14582; CSC 2: -0.37044; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.045866; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37044; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.045866; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.085589; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.085589; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.11658; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.11694; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.06916; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.06916; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11574; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.14314
88198 | BEEVILLE | F | SOUTH | 0 | CSC 1: -0.1525; CSC 2: -0.38377; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.032081; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.38377; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.032081; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.089583; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.089583; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12207; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12224; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.072148; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.12107; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.12107; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.072148; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.12107; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.1499
88253 | HAMILTON | F | SOUTH | 0 | CSC 1: -0.10379; CSC 2: -0.28577; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.13221; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.28577; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.13221; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.06088; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.06088; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.082617; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.084083; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.048778; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.082399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.082399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.048778; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.082399; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.10227
88299 | ZAPATA | F | SOUTH | 0 | CSC 1: -0.15049; CSC 2: -0.37244; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.040109; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37244; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.040109; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.088376; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.088376; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12035; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12038; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.071578; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.11944; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.11944; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.071578; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.11944; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.14755
88508 | FALFURRI | F | SOUTH | 0 | CSC 1: -0.15423; CSC 2: -0.37385; double circuit line then either use an interface defined for both lines or double the GSF values CSC 3: 0.035584; double circuit line then either use an interface defined for both lines or double the GSF values CSC4: 0.37385; double circuit line then either use an interface defined for both lines or double the GSF values CSC 5: -0.035584; double circuit line then either use an interface defined for both lines or double the GSF values CRE 1: -0.090615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 2: -0.090615; double circuit line then either use an interface defined for both lines or double the GSF values CRE 3: -0.12338; double circuit line then either use an interface defined for both lines or double the GSF values CRE 4: -0.12314; double circuit line then either use an interface defined for both lines or double the GSF values CRE 5: -0.073482; double circuit line then either use an interface defined for both lines or double the GSF values CRE 6: -0.1224; double circuit line then either use an interface defined for both lines or double the GSF values CRE 7: -0.1224; double circuit line then either use an interface defined for both lines or double the GSF values CRE 8: -0.073482; double circuit line then either use an interface defined for both lines or double the GSF values CRE 9: -0.1224; double circuit line then either use an interface defined for both lines or double the GSF values CRE 10: -0.15111
x | x | x | x | x | bar: CSC 1 to double circuit line then either use an interface defined for both lines or double the GSF values CRE 25

## N_H CRE Calculation
[5 empty] | N to H | N to S | W to N | S to N | N to W | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | [15 empty] | 10
Bus Number | Bus Name | ID | Area Name | Gen MW | CSC 1 weighted GSF #1 | CSC 2 weighted GSF #2 | CSC 3 weighted GSF #3 | CSC 4 weighted GSF #4 | CSC 5 weighted GSF #5 | Gibbons Creek - Singleton #1 (967 - 44645) | Gibbons Creek - Singleton # 2 (967 - 44645) | Jewett - Singleton # 1 (3390 - 44645) | Jewett - Singleton # 2 (3391 - 44645) | Kuykendahl - King # 1 (45971 - 40900) | Kuykendahl - King # 2 (45972 - 40900) | Roans Prairie - Kuykendahl (40600 - 45972) | Tomball - Kuykendahl (46500 - 45971) | Singleton - Roans Prairie (44645 - 40600) | Singleton - Tomball (44645 - 46500)
238 | BOSQUESW505 | 1 | NORTH | 255 | -5.9361 | 15.5285 | 3.4188 | -15.5285 | -3.4188 | -3.8357 | -3.8357 | -1.9431 | -7.0184 | -2.6436 | -4.7193 | -4.7193 | -2.6436 | -4.7193 | -5.9772
239 | BOSQUESW502 | 1 | NORTH | 149 | -3.4686 | 9.0735 | 1.9976 | -9.0735 | -1.9976 | -2.2413 | -2.2413 | -1.1354 | -4.1009 | -1.5447 | -2.7575 | -2.7575 | -1.5447 | -2.7575 | -3.4926
244 | WHITNYDM01 | 1 | NORTH | 15 | -0.26898 | -0.05619 | 0.22115 | 0.05619 | -0.22115 | -0.15987 | -0.15987 | -0.12323 | -0.31056 | -0.1199 | -0.21382 | -0.21382 | -0.1199 | -0.21382 | -0.27074
245 | WHITNYDM02 | 2 | NORTH | 15 | -0.26898 | -0.05619 | 0.22115 | 0.05619 | -0.22115 | -0.15987 | -0.15987 | -0.12323 | -0.31056 | -0.1199 | -0.21382 | -0.21382 | -0.1199 | -0.21382 | -0.27074
247 | BOSQUESW501 | 2 | NORTH | 156 | -3.6315 | 9.4998 | 2.0915 | -9.4998 | -2.0915 | -2.3466 | -2.3466 | -1.1887 | -4.2936 | -1.6173 | -2.8871 | -2.8871 | -1.6173 | -2.8871 | -3.6566
251 | BOSQUESW803 | 2 | NORTH | 150 | -3.1675 | -0.3069 | 2.3224 | 0.3069 | -2.3224 | -1.9646 | -1.9646 | -1.3415 | -3.604 | -1.4117 | -2.5182 | -2.5182 | -1.4117 | -2.5182 | -3.1887
253 | BOSQUESW804 | 2 | NORTH | 80 | -1.6894 | -0.16368 | 1.2386 | 0.16368 | -1.2386 | -1.0478 | -1.0478 | -0.71544 | -1.9222 | -0.75288 | -1.343 | -1.343 | -0.75288 | -1.343 | -1.7006
332 | RWMILLER01 | 1 | NORTH | 73 | -0.49742 | -0.84205 | 1.3344 | 0.84205 | -1.3344 | -0.31405 | -0.31405 | -0.27791 | -0.48494 | -0.22448 | -0.3953 | -0.3953 | -0.22448 | -0.3953 | -0.49822
333 | RWMILLER02 | 2 | NORTH | 119 | -0.81087 | -1.3727 | 2.1752 | 1.3727 | -2.1752 | -0.51194 | -0.51194 | -0.45303 | -0.79052 | -0.36593 | -0.64438 | -0.64438 | -0.36593 | -0.64438 | -0.81217
334 | RWMILLER03 | 3 | NORTH | 208 | -1.4173 | -2.3993 | 3.802 | 2.3993 | -3.802 | -0.89482 | -0.89482 | -0.79186 | -1.3817 | -0.6396 | -1.1263 | -1.1263 | -0.6396 | -1.1263 | -1.4196
335 | RWMILLER04 | 4 | NORTH | 102 | -0.69503 | -1.1766 | 1.8645 | 1.1766 | -1.8645 | -0.4388 | -0.4388 | -0.38831 | -0.67759 | -0.31365 | -0.55233 | -0.55233 | -0.31365 | -0.55233 | -0.69615
336 | RWMILLER05 | 5 | NORTH | 101 | -0.68821 | -1.165 | 1.8462 | 1.165 | -1.8462 | -0.4345 | -0.4345 | -0.38451 | -0.67094 | -0.31057 | -0.54692 | -0.54692 | -0.31057 | -0.54692 | -0.68932
344 | MRSSHPRD | 1 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345 | MRSSHPRD01 | 2 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
366 | JNSNCNTY802 | 1 | NORTH | 168 | -0.94349 | 0.039816 | 1.6051 | -0.039816 | -1.6051 | -0.63571 | -0.63571 | -0.38825 | -0.98112 | -0.42302 | -0.74995 | -0.74995 | -0.42302 | -0.74995 | -0.94735
367 | JNSNCNTY802 | 2 | NORTH | 90 | -0.50544 | 0.02133 | 0.85986 | -0.02133 | -0.85986 | -0.34056 | -0.34056 | -0.20799 | -0.5256 | -0.22662 | -0.40176 | -0.40176 | -0.22662 | -0.40176 | -0.50751
503 | NTHTEXAS01 | 1 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504 | NTHTEXAS02 | 2 | NORTH | 14.4 | -0.072115 | -0.12331 | 0.088834 | 0.12331 | -0.088834 | -0.045994 | -0.045994 | -0.040824 | -0.068818 | -0.032616 | -0.057312 | -0.057312 | -0.032616 | -0.057312 | -0.072187
505 | NTHTEXAS03 | 3 | NORTH | 30.4 | -0.15224 | -0.26032 | 0.18754 | 0.26032 | -0.18754 | -0.097098 | -0.097098 | -0.086184 | -0.14528 | -0.068856 | -0.12099 | -0.12099 | -0.068856 | -0.12099 | -0.1524
580 | JCKCNTY801 | 1 | NORTH | 288 | -1.0714 | -2.101 | 0.058176 | 2.101 | -0.058176 | -0.69005 | -0.69005 | -0.63475 | -0.97834 | -0.48643 | -0.85133 | -0.85133 | -0.48643 | -0.85133 | -1.0708
581 | JCKCNTY802 | 2 | NORTH | 147 | -0.54684 | -1.0724 | 0.029694 | 1.0724 | -0.029694 | -0.35221 | -0.35221 | -0.32399 | -0.49936 | -0.24828 | -0.43453 | -0.43453 | -0.24828 | -0.43453 | -0.54655
582 | JCKCNTY803 | 3 | NORTH | 147 | -0.54684 | -1.0724 | 0.029694 | 1.0724 | -0.029694 | -0.35221 | -0.35221 | -0.32399 | -0.49936 | -0.24828 | -0.43453 | -0.43453 | -0.24828 | -0.43453 | -0.54655
728 | WOLFRIDGE801 | 1 | NORTH | 11.2 | -0.025491 | -0.076048 | -0.028997 | 0.076048 | 0.028997 | -0.016352 | -0.016352 | -0.017248 | -0.021235 | -0.011637 | -0.020261 | -0.020261 | -0.011637 | -0.020261 | -0.025424
837 | NEWMAN_G5 | 1 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
842 | OLINGER_G1 | 1 | NORTH | 55.4 | 0.11806 | -0.36486 | -0.050525 | 0.36486 | 0.050525 | 0.08033 | 0.08033 | 0.02421 | 0.14581 | 0.052796 | 0.093848 | 0.093848 | 0.052796 | 0.093848 | 0.11872
843 | OLINGER_G2 | 1 | NORTH | 76.2 | 0.16238 | -0.50185 | -0.069494 | 0.50185 | 0.069494 | 0.11049 | 0.11049 | 0.033299 | 0.20056 | 0.072619 | 0.12908 | 0.12908 | 0.072619 | 0.12908 | 0.1633
844 | OLINGER_G3 | 1 | NORTH | 103.9 | 0.22141 | -0.68429 | -0.094757 | 0.68429 | 0.094757 | 0.15066 | 0.15066 | 0.045404 | 0.27346 | 0.099017 | 0.17601 | 0.17601 | 0.099017 | 0.17601 | 0.22266
845 | OLINGER_G4 | 1 | NORTH | 51.9 | 0.1106 | -0.34181 | -0.047333 | 0.34181 | 0.047333 | 0.075255 | 0.075255 | 0.02268 | 0.1366 | 0.049461 | 0.087919 | 0.087919 | 0.049461 | 0.087919 | 0.11122
923 | SPENCER_G4 | 1 | NORTH | 48 | -0.0624 | -0.25118 | -0.46267 | 0.25118 | 0.46267 | -0.040416 | -0.040416 | -0.04704 | -0.046224 | -0.028608 | -0.049584 | -0.049584 | -0.028608 | -0.049584 | -0.062112
924 | SPENCER_G5 | 1 | NORTH | 52 | -0.0676 | -0.27212 | -0.50123 | 0.27212 | 0.50123 | -0.043784 | -0.043784 | -0.05096 | -0.050076 | -0.030992 | -0.053716 | -0.053716 | -0.030992 | -0.053716 | -0.067288
948 | STEAM1 | 1 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
949 | STEAM2 | 1 | NORTH | 26 | 0.059098 | -0.17727 | -0.019994 | 0.17727 | 0.019994 | 0.039624 | 0.039624 | 0.01261 | 0.073632 | 0.026442 | 0.046982 | 0.046982 | 0.026442 | 0.046982 | 0.05941
950 | STEAM3 | 1 | NORTH | 41 | 0.093193 | -0.27954 | -0.031529 | 0.27954 | 0.031529 | 0.062484 | 0.062484 | 0.019885 | 0.11611 | 0.041697 | 0.074087 | 0.074087 | 0.041697 | 0.074087 | 0.093685
1002 | PBCTAGE_1G | A | WEST | 64 | -0.8464 | -2.3746 | 24.2426 | 2.3746 | -24.2426 | -0.51238 | -0.51238 | -0.60934 | -0.72608 | -0.38931 | -0.67232 | -0.67232 | -0.38931 | -0.67232 | -0.84141
1003 | PBCTBGE_2G | B | WEST | 65 | -0.85962 | -2.4117 | 24.6213 | 2.4117 | -24.6213 | -0.52039 | -0.52039 | -0.61886 | -0.73742 | -0.39539 | -0.68283 | -0.68283 | -0.39539 | -0.68283 | -0.85455
1004 | PBCTCGE_3G | C | WEST | 62 | -0.81995 | -2.3004 | 23.485 | 2.3004 | -23.485 | -0.49637 | -0.49637 | -0.5903 | -0.70339 | -0.37715 | -0.65131 | -0.65131 | -0.37715 | -0.65131 | -0.81511
1005 | PBCTDGE_4G | D | WEST | 65 | -0.85962 | -2.4117 | 24.6213 | 2.4117 | -24.6213 | -0.52039 | -0.52039 | -0.61886 | -0.73742 | -0.39539 | -0.68283 | -0.68283 | -0.39539 | -0.68283 | -0.85455
1006 | PBCTEGE_5G | E | WEST | 65 | -0.85962 | -2.4117 | 24.6213 | 2.4117 | -24.6213 | -0.52039 | -0.52039 | -0.61886 | -0.73742 | -0.39539 | -0.68283 | -0.68283 | -0.39539 | -0.68283 | -0.85455
1007 | PB5GEN_6G | 5 | WEST | 91.2 | -1.2061 | -3.3838 | 34.5456 | 3.3838 | -34.5456 | -0.73015 | -0.73015 | -0.86832 | -1.0347 | -0.55477 | -0.95806 | -0.95806 | -0.55477 | -0.95806 | -1.199
1008 | PB6GEN_7G | 6 | WEST | 515 | -6.8109 | -19.108 | 195.0769 | 19.108 | -195.0769 | -4.1231 | -4.1231 | -4.9033 | -5.8427 | -3.1327 | -5.4101 | -5.4101 | -3.1327 | -5.4101 | -6.7707
1037 | MORGAN5G_5G | 5 | WEST | 137 | -1.5991 | -4.4528 | 51.936 | 4.4528 | -51.936 | -0.9727 | -0.9727 | -1.1329 | -1.3823 | -0.73377 | -1.2703 | -1.2703 | -0.73377 | -1.2703 | -1.5913
1039 | MRGNAG_1G | A | WEST | 69 | -0.80537 | -2.2426 | 26.1576 | 2.2426 | -26.1576 | -0.4899 | -0.4899 | -0.57056 | -0.69621 | -0.36956 | -0.63977 | -0.63977 | -0.36956 | -0.63977 | -0.80144
1040 | MRGNBG_2G | B | WEST | 70 | -0.81704 | -2.2751 | 26.5367 | 2.2751 | -26.5367 | -0.497 | -0.497 | -0.57883 | -0.7063 | -0.37492 | -0.64904 | -0.64904 | -0.37492 | -0.64904 | -0.81305
1041 | MRGNCG_3G | C | WEST | 69 | -0.80537 | -2.2426 | 26.1576 | 2.2426 | -26.1576 | -0.4899 | -0.4899 | -0.57056 | -0.69621 | -0.36956 | -0.63977 | -0.63977 | -0.36956 | -0.63977 | -0.80144
1042 | MRGNDG_4G | D | WEST | 68 | -0.7937 | -2.2101 | 25.7785 | 2.2101 | -25.7785 | -0.4828 | -0.4828 | -0.56229 | -0.68612 | -0.36421 | -0.6305 | -0.6305 | -0.36421 | -0.6305 | -0.78982
1043 | MRGNEG_5G | E | WEST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1044 | MRGNFG_6G | F | WEST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1045 | CALENG1G_1G | 1 | WEST | 73.4 | -0.87104 | -2.4254 | 28.3538 | 2.4254 | -28.3538 | -0.52951 | -0.52951 | -0.61884 | -0.75162 | -0.39988 | -0.69194 | -0.69194 | -0.39988 | -0.69194 | -0.86656
1046 | CALENG2G_2G | 2 | WEST | 73.4 | -0.87104 | -2.4254 | 28.3538 | 2.4254 | -28.3538 | -0.52951 | -0.52951 | -0.61884 | -0.75162 | -0.39988 | -0.69194 | -0.69194 | -0.39988 | -0.69194 | -0.86656
1047 | CALENG3G_3G | 3 | WEST | 70.4 | -0.83544 | -2.3262 | 27.195 | 2.3262 | -27.195 | -0.50787 | -0.50787 | -0.59354 | -0.7209 | -0.38354 | -0.66366 | -0.66366 | -0.38354 | -0.66366 | -0.83114
1058 | LONGSHORE_5 | 1 | WEST | 30 | -0.35169 | -0.9783 | 11.6172 | 0.9783 | -11.6172 | -0.2139 | -0.2139 | -0.24948 | -0.30369 | -0.16143 | -0.27939 | -0.27939 | -0.16143 | -0.27939 | -0.34992
1058 | LONGSHORE_5 | 2 | WEST | 44 | -0.51581 | -1.4348 | 17.0385 | 1.4348 | -17.0385 | -0.31372 | -0.31372 | -0.3659 | -0.44541 | -0.23676 | -0.40977 | -0.40977 | -0.23676 | -0.40977 | -0.51322
1061 | CIELOGEN_1G | 1 | WEST | 19.8 | -0.22984 | -0.6395 | 7.2062 | 0.6395 | -7.2062 | -0.13983 | -0.13983 | -0.16262 | -0.19885 | -0.10544 | -0.18258 | -0.18258 | -0.10544 | -0.18258 | -0.22873
1062 | CIELOGEN_2G | 1 | WEST | 12.2 | -0.14162 | -0.39404 | 4.4402 | 0.39404 | -4.4402 | -0.086156 | -0.086156 | -0.1002 | -0.12252 | -0.064965 | -0.1125 | -0.1125 | -0.064965 | -0.1125 | -0.14093
1068 | SCURRYCW_1G | 1 | WEST | 28.2 | -0.32788 | -0.91247 | 10.2805 | 0.91247 | -10.2805 | -0.19949 | -0.19949 | -0.23206 | -0.28364 | -0.15042 | -0.26048 | -0.26048 | -0.15042 | -0.26048 | -0.3263
1073 | SCURRYCW_2G | 2 | WEST | 24 | -0.27905 | -0.77657 | 8.7493 | 0.77657 | -8.7493 | -0.16978 | -0.16978 | -0.1975 | -0.24139 | -0.12802 | -0.22169 | -0.22169 | -0.12802 | -0.22169 | -0.2777
1326 | STANTONW_8 | 1 | WEST | 20.1 | -0.25183 | -0.70543 | 7.6044 | 0.70543 | -7.6044 | -0.15276 | -0.15276 | -0.18008 | -0.21678 | -0.11572 | -0.20006 | -0.20006 | -0.11572 | -0.20006 | -0.25047
1327 | WILDHRSE_1G | 1 | WEST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1328 | OCOTILLO_1G | 1 | WEST | 11.6 | -0.14443 | -0.40457 | 4.3699 | 0.40457 | -4.3699 | -0.087626 | -0.087626 | -0.10317 | -0.12439 | -0.066352 | -0.11474 | -0.11474 | -0.066352 | -0.11474 | -0.14365
1333 | MCDDONAL_8 | 1 | WEST | 42.8 | -0.52751 | -1.4768 | 16.1215 | 1.4768 | -16.1215 | -0.32019 | -0.32019 | -0.3763 | -0.45458 | -0.24225 | -0.41905 | -0.41905 | -0.24225 | -0.41905 | -0.52473
1343 | TRENTIPP_8 | 1 | WEST | 30 | -0.35226 | -0.99045 | 10.5111 | 0.99045 | -10.5111 | -0.2142 | -0.2142 | -0.24825 | -0.30621 | -0.16143 | -0.27987 | -0.27987 | -0.16143 | -0.27987 | -0.35076
1349 | WESTXWIN_1G | 1 | WEST | 1.3 | -0.017519 | -0.050246 | 0.475 | 0.050246 | -0.475 | -0.010595 | -0.010595 | -0.012607 | -0.015064 | -0.008047 | -0.013917 | -0.013917 | -0.008047 | -0.013917 | -0.017427
1350 | NWPWRG1_1G | 1 | WEST | 6.9 | -0.092984 | -0.26669 | 2.5211 | 0.26669 | -2.5211 | -0.056235 | -0.056235 | -0.066916 | -0.079957 | -0.042711 | -0.073864 | -0.073864 | -0.042711 | -0.073864 | -0.092494
1354 | AEPWIND_8 | 1 | WEST | 20.2 | -0.23719 | -0.6669 | 7.0775 | 0.6669 | -7.0775 | -0.14423 | -0.14423 | -0.16715 | -0.20618 | -0.1087 | -0.18845 | -0.18845 | -0.1087 | -0.18845 | -0.23618
1360 | GUNSIGHT_8 | 1 | WEST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1416 | SWETWATR_1G | 1 | WEST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1417 | SWETWATR_2G | 2 | WEST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1418 | SWETWATR_3G | 3 | WEST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1419 | SWETWATR_4G | 4 | WEST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1432 | GRHAMSES_2G | 2 | NORTH | 366 | -2.3164 | -5.3363 | -31.2901 | 5.3363 | 31.2901 | -1.4578 | -1.4578 | -1.5013 | -2.0489 | -1.0581 | -1.8402 | -1.8402 | -1.0581 | -1.8402 | -2.3091
1433 | GRHAMSES_1G | 1 | NORTH | 242 | -1.6771 | -3.9226 | -1.0285 | 3.9226 | 1.0285 | -1.0481 | -1.0481 | -1.083 | -1.5035 | -0.76472 | -1.3325 | -1.3325 | -0.76472 | -1.3325 | -1.6729
1437 | MESQUITW_1G | 1 | NORTH | 40 | -0.35756 | -0.93804 | -14.6923 | 0.93804 | 14.6923 | -0.22024 | -0.22024 | -0.24528 | -0.312 | -0.16372 | -0.28408 | -0.28408 | -0.16372 | -0.28408 | -0.35612
1438 | MESQUITW_2G | 1 | NORTH | 23.6 | -0.21089 | -0.55316 | -8.6582 | 0.55316 | 8.6582 | -0.12989 | -0.12989 | -0.14464 | -0.18401 | -0.096571 | -0.16754 | -0.16754 | -0.096571 | -0.16754 | -0.21002
1442 | COKFIELD_5 | 1 | NORTH | 16.5 | -0.13711 | -0.35166 | -4.9392 | 0.35166 | 4.9392 | -0.084793 | -0.084793 | -0.093093 | -0.11994 | -0.062749 | -0.10893 | -0.10893 | -0.062749 | -0.10893 | -0.13659
1453 | WCPWRCO_1G | 1 | NORTH | 204 | -0.89413 | -1.7258 | -6.038 | 1.7258 | 6.038 | -0.57895 | -0.57895 | -0.53938 | -0.79968 | -0.40718 | -0.71053 | -0.71053 | -0.40718 | -0.71053 | -0.8923
1454 | WCPWRCO_2G | 2 | NORTH | 204 | -0.89413 | -1.7258 | -6.038 | 1.7258 | 6.038 | -0.57895 | -0.57895 | -0.53938 | -0.79968 | -0.40718 | -0.71053 | -0.71053 | -0.40718 | -0.71053 | -0.8923
1455 | WCPWRCO_3G | 3 | NORTH | 242 | -1.0607 | -2.0473 | -7.1627 | 2.0473 | 7.1627 | -0.6868 | -0.6868 | -0.63985 | -0.94864 | -0.48303 | -0.84289 | -0.84289 | -0.48303 | -0.84289 | -1.0585
1479 | WFCOGEN_1G | 1 | NORTH | 16 | -0.10014 | -0.23562 | 0.10013 | 0.23562 | -0.10013 | -0.062848 | -0.062848 | -0.065152 | -0.088688 | -0.045728 | -0.079568 | -0.079568 | -0.045728 | -0.079568 | -0.09984
1479 | WFCOGEN_1G | 2 | NORTH | 16 | -0.10014 | -0.23562 | 0.10013 | 0.23562 | -0.10013 | -0.062848 | -0.062848 | -0.065152 | -0.088688 | -0.045728 | -0.079568 | -0.079568 | -0.045728 | -0.079568 | -0.09984
1482 | WFCOGEN_2G | 1 | NORTH | 16 | -0.10014 | -0.23562 | 0.10013 | 0.23562 | -0.10013 | -0.062848 | -0.062848 | -0.065152 | -0.088688 | -0.045728 | -0.079568 | -0.079568 | -0.045728 | -0.079568 | -0.09984
1482 | WFCOGEN_2G | 2 | NORTH | 13.6 | -0.085122 | -0.20027 | 0.085109 | 0.20027 | -0.085109 | -0.053421 | -0.053421 | -0.055379 | -0.075385 | -0.038869 | -0.067633 | -0.067633 | -0.038869 | -0.067633 | -0.084864
1600 | BARTNWND_1G | 1 | NORTH | 12 | -0.07338 | -0.15271 | 0.040632 | 0.15271 | -0.040632 | -0.046224 | -0.046224 | -0.044868 | -0.06768 | -0.033348 | -0.058308 | -0.058308 | -0.033348 | -0.058308 | -0.073308
1643 | SLSTR1PP_1G | 1 | NORTH | 6 | -0.063846 | -0.13592 | 0.41075 | 0.13592 | -0.41075 | -0.039252 | -0.039252 | -0.037986 | -0.06204 | -0.028836 | -0.050742 | -0.050742 | -0.028836 | -0.050742 | -0.063936
1675 | PEC_1G | 1 | NORTH | 76.7 | 0.13959 | -0.48705 | -0.12211 | 0.48705 | 0.12211 | 0.088128 | 0.088128 | 0.028609 | 0.18592 | 0.062357 | 0.11091 | 0.11091 | 0.062357 | 0.11091 | 0.14036
1676 | PEC_2G | 2 | NORTH | 79.6 | 0.14487 | -0.50546 | -0.12672 | 0.50546 | 0.12672 | 0.09146 | 0.09146 | 0.029691 | 0.19295 | 0.064715 | 0.1151 | 0.1151 | 0.064715 | 0.1151 | 0.14567
1677 | PEC_3G | 3 | NORTH | 88.4 | 0.16089 | -0.56134 | -0.14073 | 0.56134 | 0.14073 | 0.10157 | 0.10157 | 0.032973 | 0.21428 | 0.071869 | 0.12783 | 0.12783 | 0.071869 | 0.12783 | 0.16177
1678 | LAMARPWR_1G | 1 | NORTH | 160 | 0.28048 | -0.99296 | -0.2664 | 0.99296 | 0.2664 | 0.17904 | 0.17904 | 0.05648 | 0.37104 | 0.12528 | 0.22288 | 0.22288 | 0.12528 | 0.22288 | 0.28208
1679 | LAMARPWR_2G | 2 | NORTH | 156 | 0.27347 | -0.96814 | -0.25974 | 0.96814 | 0.25974 | 0.17456 | 0.17456 | 0.055068 | 0.36176 | 0.12215 | 0.21731 | 0.21731 | 0.12215 | 0.21731 | 0.27503
1680 | LAMARPWR_3G | 3 | NORTH | 196 | 0.34359 | -1.2164 | -0.32634 | 1.2164 | 0.32634 | 0.21932 | 0.21932 | 0.069188 | 0.45452 | 0.15347 | 0.27303 | 0.27303 | 0.15347 | 0.27303 | 0.34555
1681 | LAMARPWR_4G | 4 | NORTH | 156 | 0.27347 | -0.96814 | -0.25974 | 0.96814 | 0.25974 | 0.17456 | 0.17456 | 0.055068 | 0.36176 | 0.12215 | 0.21731 | 0.21731 | 0.12215 | 0.21731 | 0.27503
1682 | LAMARPWR_5G | 5 | NORTH | 157 | 0.27522 | -0.97434 | -0.2614 | 0.97434 | 0.2614 | 0.17568 | 0.17568 | 0.055421 | 0.36408 | 0.12293 | 0.2187 | 0.2187 | 0.12293 | 0.2187 | 0.27679
1683 | LAMARPWR_6G | 6 | NORTH | 198 | 0.34709 | -1.2288 | -0.32967 | 1.2288 | 0.32967 | 0.22156 | 0.22156 | 0.069894 | 0.45916 | 0.15503 | 0.27581 | 0.27581 | 0.15503 | 0.27581 | 0.34907
1687 | VALLEY_1G | 1 | NORTH | 170 | 0.24412 | -1.0164 | -0.35122 | 1.0164 | 0.35122 | 0.1564 | 0.1564 | 0.03757 | 0.33337 | 0.1088 | 0.19397 | 0.19397 | 0.1088 | 0.19397 | 0.24565
1688 | VALLEY_2G | 2 | NORTH | 527 | 0.75677 | -3.1509 | -1.0888 | 3.1509 | 1.0888 | 0.48484 | 0.48484 | 0.11647 | 1.0334 | 0.33728 | 0.60131 | 0.60131 | 0.33728 | 0.60131 | 0.76152
1689 | VALLEY_3G | 3 | NORTH | 375 | 0.62062 | -2.277 | -0.66975 | 2.277 | 0.66975 | 0.39863 | 0.39863 | 0.11887 | 0.82275 | 0.27713 | 0.4935 | 0.4935 | 0.27713 | 0.4935 | 0.62438
1861 | EAGLEMNT_1G | MB | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1862 | EAGLEMNT_2G | MB | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1863 | EAGLEMNT_3G | MB | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1877 | WLFHOLW_1G | 1 | NORTH | 217.3 | -0.91635 | -0.56085 | 2.464 | 0.56085 | -2.464 | -0.63191 | -0.63191 | -0.42352 | -0.87463 | -0.41374 | -0.72817 | -0.72817 | -0.41374 | -0.72817 | -0.91766
1878 | WLFHOLW_2G | 2 | NORTH | 215.7 | -0.90961 | -0.55672 | 2.4458 | 0.55672 | -2.4458 | -0.62726 | -0.62726 | -0.4204 | -0.86819 | -0.41069 | -0.72281 | -0.72281 | -0.41069 | -0.72281 | -0.9109
1879 | WLFHOLW_3G | 3 | NORTH | 272.4 | -1.1487 | -0.70306 | 3.0887 | 0.70306 | -3.0887 | -0.79214 | -0.79214 | -0.53091 | -1.0964 | -0.51865 | -0.91281 | -0.91281 | -0.51865 | -0.91281 | -1.1503
1889 | DECRDOVA_1G | 1 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1892 | DECRDOVA_2G | A | NORTH | 65 | -0.32584 | -0.21366 | 0.61256 | 0.21366 | -0.61256 | -0.21755 | -0.21755 | -0.15321 | -0.32305 | -0.14671 | -0.25896 | -0.25896 | -0.14671 | -0.25896 | -0.32669
1893 | DECRDOVA_3G | B | NORTH | 65 | -0.32584 | -0.21366 | 0.61256 | 0.21366 | -0.61256 | -0.21755 | -0.21755 | -0.15321 | -0.32305 | -0.14671 | -0.25896 | -0.25896 | -0.14671 | -0.25896 | -0.32669
1894 | DECRDOVA_4G | C | NORTH | 65 | -0.32584 | -0.21366 | 0.61256 | 0.21366 | -0.61256 | -0.21755 | -0.21755 | -0.15321 | -0.32305 | -0.14671 | -0.25896 | -0.25896 | -0.14671 | -0.25896 | -0.32669
1895 | DECRDOVA_5G | D | NORTH | 65 | -0.32584 | -0.21366 | 0.61256 | 0.21366 | -0.61256 | -0.21755 | -0.21755 | -0.15321 | -0.32305 | -0.14671 | -0.25896 | -0.25896 | -0.14671 | -0.25896 | -0.32669
1937 | MDLTHELP_5G | 5 | NORTH | 224 | -0.73808 | 2.2676 | 0.82925 | -2.2676 | -0.82925 | -0.61802 | -0.61802 | -0.080416 | -0.75085 | -0.32973 | -0.58688 | -0.58688 | -0.32973 | -0.58688 | -0.74234
1938 | MDLTHELP_6G | 6 | NORTH | 226 | -0.74467 | 2.2878 | 0.83665 | -2.2878 | -0.83665 | -0.62353 | -0.62353 | -0.081134 | -0.75755 | -0.33267 | -0.59212 | -0.59212 | -0.33267 | -0.59212 | -0.74896
1941 | MDLTHELP_1G | 1 | NORTH | 216.4 | -0.48452 | 2.3856 | 0.54771 | -2.3856 | -0.54771 | -0.44167 | -0.44167 | 0.03484 | -0.50941 | -0.21553 | -0.38519 | -0.38519 | -0.21553 | -0.38519 | -0.4882
1942 | MDLTHELP_2G | 2 | NORTH | 216.1 | -0.48385 | 2.3823 | 0.54695 | -2.3823 | -0.54695 | -0.44106 | -0.44106 | 0.034792 | -0.5087 | -0.21524 | -0.38466 | -0.38466 | -0.21524 | -0.38466 | -0.48752
1943 | MDLTHELP_3G | 3 | NORTH | 212 | -0.69854 | 2.1461 | 0.78482 | -2.1461 | -0.78482 | -0.58491 | -0.58491 | -0.076108 | -0.71062 | -0.31206 | -0.55544 | -0.55544 | -0.31206 | -0.55544 | -0.70257
1944 | MDLTHELP_4G | 4 | NORTH | 211 | -0.69525 | 2.136 | 0.78112 | -2.136 | -0.78112 | -0.58215 | -0.58215 | -0.075749 | -0.70727 | -0.31059 | -0.55282 | -0.55282 | -0.31059 | -0.55282 | -0.69925
1947 | HANDLEY_3G | 3 | NORTH | 316 | -0.70563 | 0.37351 | -0.58871 | -0.37351 | 0.58871 | -0.51603 | -0.51603 | -0.25501 | -0.68635 | -0.3179 | -0.5609 | -0.5609 | -0.3179 | -0.5609 | -0.70721
1948 | HANDLEY_4G | 4 | NORTH | 435 | -0.89392 | 0.39976 | -0.75777 | -0.39976 | 0.75777 | -0.6525 | -0.6525 | -0.32886 | -0.86652 | -0.40281 | -0.71035 | -0.71035 | -0.40281 | -0.71035 | -0.8961
1949 | HANDLEY_5G | 5 | NORTH | 435 | -0.97135 | 0.51417 | -0.81041 | -0.51417 | 0.81041 | -0.71035 | -0.71035 | -0.35104 | -0.94482 | -0.43761 | -0.77212 | -0.77212 | -0.43761 | -0.77212 | -0.97353
2371 | COLLIN_1G | MB | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2381 | NTHLK1_G | 1 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2382 | NTHLK2_G | 2 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2383 | NTHLK3_G | 3 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2413 | MTCK6_G | 6 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2414 | MTCK7_G | 7 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2417 | MTCK8_G | 8 | NORTH | 444.8 | 0.63562 | -1.6871 | 0.2393 | 1.6871 | -0.2393 | 0.53999 | 0.53999 | 0.079619 | 0.61961 | 0.28467 | 0.50529 | 0.50529 | 0.28467 | 0.50529 | 0.63829
2451 | LKHB1_G | 1 | NORTH | 391 | 1.0115 | -2.6897 | -0.0391 | 2.6897 | 0.0391 | 0.71905 | 0.71905 | 0.22756 | 1.166 | 0.45317 | 0.80429 | 0.80429 | 0.45317 | 0.80429 | 1.0162
2452 | LKHB2_G | 2 | NORTH | 516 | 1.3349 | -3.5496 | -0.0516 | 3.5496 | 0.0516 | 0.94892 | 0.94892 | 0.30031 | 1.5387 | 0.59804 | 1.0614 | 1.0614 | 0.59804 | 1.0614 | 1.3411
3107 | STRYKER_1G | 1 | NORTH | 182 | 1.278 | -2.8872 | 0.48321 | 2.8872 | -0.48321 | 0.67759 | 0.67759 | 0.20366 | 2.0186 | 0.5733 | 1.0159 | 1.0159 | 0.5733 | 1.0159 | 1.2833
3108 | STRYKER_2G | 2 | NORTH | 484 | 3.3986 | -7.6782 | 1.285 | 7.6782 | -1.285 | 1.8019 | 1.8019 | 0.5416 | 5.368 | 1.5246 | 2.7017 | 2.7017 | 1.5246 | 2.7017 | 3.4127
3126 | TRINIDAD_6G | 1 | NORTH | 224 | 0.74368 | -2.8477 | 0.83821 | 2.8477 | -0.83821 | 0.50154 | 0.50154 | -0.41821 | 1.4954 | 0.33488 | 0.59114 | 0.59114 | 0.33488 | 0.59114 | 0.74547
3309 | ASPN_G | 1 | NORTH | 50 | 0.3478 | -0.74915 | 0.13025 | 0.74915 | -0.13025 | 0.1565 | 0.1565 | 0.14425 | 0.5162 | 0.156 | 0.27645 | 0.27645 | 0.156 | 0.27645 | 0.34925
3403 | THOUSE_1G | 1 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3404 | THOUSE_2G | 2 | NORTH | 807 | -19.7868 | 92.1618 | 9.6671 | -92.1618 | -9.6671 | -13.2114 | -13.2114 | -5.0413 | -23.9808 | -8.8084 | -15.7309 | -15.7309 | -8.8084 | -15.7309 | -19.9264
3416 | LAKE_CRK1_G | 1 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3417 | LAKE_CRK2_G | 2 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5026 | BRAUNIG_VHB1 | 1 | SOUTH | 215 | -29.876 | -88.2132 | 6.9155 | 88.2132 | -6.9155 | -17.466 | -17.466 | -23.8719 | -24.3169 | -13.943 | -23.7218 | -23.7218 | -13.943 | -23.7218 | -29.5229
5027 | BRAUNIG_VHB2 | 2 | SOUTH | 216 | -30.0149 | -88.6235 | 6.9476 | 88.6235 | -6.9476 | -17.5472 | -17.5472 | -23.9829 | -24.43 | -14.0078 | -23.8321 | -23.8321 | -14.0078 | -23.8321 | -29.6603
5028 | BRAUNIG_VHB3 | 3 | SOUTH | 407 | -56.5018 | -166.9396 | 13.1721 | 166.9396 | -13.1721 | -33.0289 | -33.0289 | -45.1428 | -45.9886 | -26.3777 | -44.862 | -44.862 | -26.3777 | -44.862 | -55.8253
5264 | LEON_LCP3G3 | 3 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5265 | LEON_LCP4G4 | 4 | SOUTH | 89 | -12.3599 | -36.3823 | 2.9374 | 36.3823 | -2.9374 | -7.2263 | -7.2263 | -9.8754 | -10.0566 | -5.7716 | -9.8137 | -9.8137 | -5.7716 | -9.8137 | -12.2109
5266 | LEON_LCPCT1 | 1 | SOUTH | 44 | -6.1105 | -17.9868 | 1.4522 | 17.9868 | -1.4522 | -3.5725 | -3.5725 | -4.8822 | -4.9718 | -2.8534 | -4.8517 | -4.8517 | -2.8534 | -4.8517 | -6.0368
5267 | LEON_LCPCT2 | 2 | SOUTH | 44 | -6.1105 | -17.9868 | 1.4522 | 17.9868 | -1.4522 | -3.5725 | -3.5725 | -4.8822 | -4.9718 | -2.8534 | -4.8517 | -4.8517 | -2.8534 | -4.8517 | -6.0368
5268 | LEON_LCPCT3 | 3 | SOUTH | 43 | -5.9716 | -17.578 | 1.4192 | 17.578 | -1.4192 | -3.4913 | -3.4913 | -4.7713 | -4.8588 | -2.7885 | -4.7414 | -4.7414 | -2.7885 | -4.7414 | -5.8996
5269 | LEON_LCPCT4 | 4 | SOUTH | 45 | -6.2494 | -18.3956 | 1.4852 | 18.3956 | -1.4852 | -3.6537 | -3.6537 | -4.9932 | -5.0848 | -2.9182 | -4.962 | -4.962 | -2.9182 | -4.962 | -6.174
5396 | CALAVER_OWS1 | 1 | SOUTH | 418 | -58.0343 | -171.612 | 13.4404 | 171.612 | -13.4404 | -33.9253 | -33.9253 | -46.3696 | -47.2419 | -27.0835 | -46.0795 | -46.0795 | -27.0835 | -46.0795 | -57.3483
5397 | CALAVER_OWS2 | 2 | SOUTH | 400 | -55.5352 | -164.222 | 12.8616 | 164.222 | -12.8616 | -32.4644 | -32.4644 | -44.3728 | -45.2076 | -25.9172 | -44.0952 | -44.0952 | -25.9172 | -44.0952 | -54.8788
5436 | TUTTL_WBT1G1 | 1 | SOUTH | 48.8 | -6.777 | -20.0871 | 1.5426 | 20.0871 | -1.5426 | -3.9611 | -3.9611 | -5.4146 | -5.5178 | -3.1628 | -5.3809 | -5.3809 | -3.1628 | -5.3809 | -6.6967
5438 | TUTTL_WBT3G3 | 3 | SOUTH | 95 | -13.1929 | -39.104 | 3.003 | 39.104 | -3.003 | -7.7112 | -7.7112 | -10.5407 | -10.7416 | -6.157 | -10.4752 | -10.4752 | -6.157 | -10.4752 | -13.0367
5439 | TUTTL_WBT4G4 | 4 | SOUTH | 151 | -20.9698 | -62.1548 | 4.7733 | 62.1548 | -4.7733 | -12.2568 | -12.2568 | -16.7542 | -17.0734 | -9.7865 | -16.65 | -16.65 | -9.7865 | -16.65 | -20.7214
5476 | BRA_AVR1_CT1 | 1 | SOUTH | 155 | -21.714 | -63.4649 | 4.8757 | 63.4649 | -4.8757 | -12.6965 | -12.6965 | -17.3502 | -17.6526 | -10.1513 | -17.2402 | -17.2402 | -10.1513 | -17.2402 | -21.4418
5477 | BRA_AVR1_ST | 1 | SOUTH | 174 | -24.3757 | -71.2445 | 5.4733 | 71.2445 | -5.4733 | -14.2529 | -14.2529 | -19.477 | -19.8165 | -11.3956 | -19.3535 | -19.3535 | -11.3956 | -19.3535 | -24.0701
5478 | BRA_AVR1_CT2 | 1 | SOUTH | 155 | -21.714 | -63.4649 | 4.8757 | 63.4649 | -4.8757 | -12.6965 | -12.6965 | -17.3502 | -17.6526 | -10.1513 | -17.2402 | -17.2402 | -10.1513 | -17.2402 | -21.4418
5503 | RAYBURNGEN3 | 1 | SOUTH | 17.6 | -2.842 | -6.5261 | 0.51864 | 6.5261 | -0.51864 | -1.6752 | -1.6752 | -2.2793 | -2.2624 | -1.348 | -2.2575 | -2.2575 | -1.348 | -2.2575 | -2.7928
5505 | RAYBURNGEN1 | 1 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5506 | RAYBURNGEN2 | 1 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5508 | RAYBURNCC9 | 1 | SOUTH | 47.7 | -7.6776 | -17.7621 | 1.3921 | 17.7621 | -1.3921 | -4.5248 | -4.5248 | -6.1572 | -6.1156 | -3.6384 | -6.0982 | -6.0982 | -3.6384 | -6.0982 | -7.5465
5509 | RAYBURNCC10 | 1 | SOUTH | 37.3 | -6.0037 | -13.8894 | 1.0886 | 13.8894 | -1.0886 | -3.5382 | -3.5382 | -4.8147 | -4.7822 | -2.8451 | -4.7686 | -4.7686 | -2.8451 | -4.7686 | -5.9011
5511 | RAYBURNCC7 | 1 | SOUTH | 47.5 | -7.6455 | -17.6876 | 1.3863 | 17.6876 | -1.3863 | -4.5058 | -4.5058 | -6.1313 | -6.09 | -3.6231 | -6.0726 | -6.0726 | -3.6231 | -6.0726 | -7.5148
5512 | RAYBURNCC8 | 1 | SOUTH | 49.3 | -7.9352 | -18.3579 | 1.4388 | 18.3579 | -1.4388 | -4.6765 | -4.6765 | -6.3637 | -6.3208 | -3.7604 | -6.3028 | -6.3028 | -3.7604 | -6.3028 | -7.7996
5728 | FALCONHYDRO2 | 2 | SOUTH | 12 | -1.8438 | -4.4855 | 0.4345 | 4.4855 | -0.4345 | -1.0832 | -1.0832 | -1.4749 | -1.4725 | -0.87859 | -1.4634 | -1.4634 | -0.87859 | -1.4634 | -1.8065
5729 | FALCONHYDRO3 | 3 | SOUTH | 11 | -1.6902 | -4.1117 | 0.39829 | 4.1117 | -0.39829 | -0.99291 | -0.99291 | -1.352 | -1.3498 | -0.80538 | -1.3414 | -1.3414 | -0.80538 | -1.3414 | -1.656
5890 | PEARSALLGEN1 | 1 | SOUTH | 19.2 | -2.6703 | -7.396 | 0.8645 | 7.396 | -0.8645 | -1.5641 | -1.5641 | -2.1339 | -2.1598 | -1.2548 | -2.12 | -2.12 | -1.2548 | -2.12 | -2.6316
5891 | PEARSALLGEN2 | 1 | SOUTH | 19.4 | -2.6982 | -7.4731 | 0.8735 | 7.4731 | -0.8735 | -1.5804 | -1.5804 | -2.1562 | -2.1822 | -1.2678 | -2.1421 | -2.1421 | -1.2678 | -2.1421 | -2.659
5892 | PEARSALLGEN3 | 1 | SOUTH | 19.1 | -2.6564 | -7.3575 | 0.86 | 7.3575 | -0.86 | -1.556 | -1.556 | -2.1228 | -2.1485 | -1.2482 | -2.109 | -2.109 | -1.2482 | -2.109 | -2.6179
5932 | SI_RAY9 | 9 | SOUTH | 32 | -5.0485 | -12.017 | 0.99683 | 12.017 | -0.99683 | -2.9669 | -2.9669 | -4.0392 | -4.0236 | -2.4109 | -4.0065 | -4.0065 | -2.4109 | -4.0065 | -4.9416
5933 | SI_RAY6 | 6 | SOUTH | 15.4 | -2.4296 | -5.7832 | 0.47973 | 5.7832 | -0.47973 | -1.4278 | -1.4278 | -1.9438 | -1.9363 | -1.1603 | -1.9281 | -1.9281 | -1.1603 | -1.9281 | -2.3782
5935 | SI_RAY10 | 10 | SOUTH | 47 | -7.415 | -17.65 | 1.4641 | 17.65 | -1.4641 | -4.3577 | -4.3577 | -5.9325 | -5.9096 | -3.541 | -5.8845 | -5.8845 | -3.541 | -5.8845 | -7.258
6016 | SWMESA | 1 | WEST | 18.8 | -0.34571 | -0.98587 | 6.7368 | 0.98587 | -6.7368 | -0.20712 | -0.20712 | -0.257 | -0.29208 | -0.1598 | -0.27459 | -0.27459 | -0.1598 | -0.27459 | -0.34301
6144 | MCADOO1A | 1 | WEST | 15 | -0.16506 | -0.45593 | 4.767 | 0.45593 | -4.767 | -0.10064 | -0.10064 | -0.1158 | -0.14346 | -0.07566 | -0.13113 | -0.13113 | -0.07566 | -0.13113 | -0.16434
6407 | TURKTRAK1A | 1 | WEST | 33.9 | -0.50067 | -1.4811 | 11.1881 | 1.4811 | -11.1881 | -0.30178 | -0.30178 | -0.36148 | -0.43168 | -0.2296 | -0.39775 | -0.39775 | -0.2296 | -0.39775 | -0.49833
6637 | SNYDERW1A | 1 | WEST | 12.6 | -0.14704 | -0.40953 | 4.6282 | 0.40953 | -4.6282 | -0.089447 | -0.089447 | -0.10411 | -0.12717 | -0.06746 | -0.11681 | -0.11681 | -0.06746 | -0.11681 | -0.14632
6948 | DENISNDM | 1 | NORTH | 40 | 0.05044 | -0.2346 | -0.0914 | 0.2346 | 0.0914 | 0.0324 | 0.0324 | 0.00592 | 0.0706 | 0.02244 | 0.04012 | 0.04012 | 0.02244 | 0.04012 | 0.0508
6948 | DENISNDM | 2 | NORTH | 31 | 0.039091 | -0.18182 | -0.070835 | 0.18182 | 0.070835 | 0.02511 | 0.02511 | 0.004588 | 0.054715 | 0.017391 | 0.031093 | 0.031093 | 0.017391 | 0.031093 | 0.03937
7000 | L_FERGUS1_1Y | 1 | SOUTH | 400 | -41.9204 | -170.4124 | 17.86 | 170.4124 | -17.86 | -24.3224 | -24.3224 | -33.1316 | -35.43 | -18.944 | -33.3156 | -33.3156 | -18.944 | -33.3156 | -41.9708
7004 | L_SIMGID1_1Y | 1 | SOUTH | 132 | -15.6515 | -60.3153 | 3.5798 | 60.3153 | -3.5798 | -9.1355 | -9.1355 | -12.5519 | -13.2275 | -6.7794 | -12.4592 | -12.4592 | -6.7794 | -12.4592 | -15.9394
7005 | L_SIMGID1_2Y | 2 | SOUTH | 133 | -15.7701 | -60.7722 | 3.607 | 60.7722 | -3.607 | -9.2047 | -9.2047 | -12.647 | -13.3277 | -6.8307 | -12.5536 | -12.5536 | -6.8307 | -12.5536 | -16.0601
7006 | L_SIMGID1_3Y | 3 | SOUTH | 324.9 | -38.524 | -148.4579 | 8.8113 | 148.4579 | -8.8113 | -22.4857 | -22.4857 | -30.8947 | -32.5576 | -16.6865 | -30.6667 | -30.6667 | -16.6865 | -30.6667 | -39.2326
7007 | L_LOSTPI1_1Y | 1 | SOUTH | 158.6 | -18.6767 | -74.3645 | 4.0681 | 74.3645 | -4.0681 | -10.8281 | -10.8281 | -14.9379 | -15.7939 | -8.2532 | -14.8505 | -14.8505 | -8.2532 | -14.8505 | -18.8609
7008 | L_LOSTPI1_2Y | 2 | SOUTH | 157.7 | -18.5708 | -73.9425 | 4.045 | 73.9425 | -4.045 | -10.7667 | -10.7667 | -14.8531 | -15.7042 | -8.2064 | -14.7662 | -14.7662 | -8.2064 | -14.7662 | -18.7538
7009 | L_LOSTPI1_3Y | 3 | SOUTH | 173.9 | -20.4785 | -81.5384 | 4.4605 | 81.5384 | -4.4605 | -11.8727 | -11.8727 | -16.3789 | -17.3175 | -9.0494 | -16.2831 | -16.2831 | -9.0494 | -16.2831 | -20.6804
7014 | L_HAYSEN1_1Y | 1 | SOUTH | 223.9 | -29.3141 | -96.8426 | 6.5748 | 96.8426 | -6.5748 | -17.0807 | -17.0807 | -23.4139 | -24.1646 | -13.4792 | -23.2836 | -23.2836 | -13.4792 | -23.2836 | -29.1419
7015 | L_HAYSEN1_2Y | 2 | SOUTH | 225 | -29.4581 | -97.3183 | 6.6071 | 97.3183 | -6.6071 | -17.1646 | -17.1646 | -23.5289 | -24.2833 | -13.5455 | -23.398 | -23.398 | -13.5455 | -23.398 | -29.2851
7016 | L_HAYSEN1_3Y | 3 | SOUTH | 224.6 | -29.4058 | -97.1453 | 6.5954 | 97.1453 | -6.5954 | -17.1341 | -17.1341 | -23.4871 | -24.2402 | -13.5214 | -23.3564 | -23.3564 | -13.5214 | -23.3564 | -29.233
7017 | L_HAYSEN1_4Y | 4 | SOUTH | 226.7 | -29.6807 | -98.0536 | 6.657 | 98.0536 | -6.657 | -17.2943 | -17.2943 | -23.7067 | -24.4668 | -13.6478 | -23.5748 | -23.5748 | -13.6478 | -23.5748 | -29.5064
7020 | L_AUSTPL1_1Y | 1 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7020 | L_AUSTPL1_1Y | 2 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7022 | L_BUCHAN1_1Y | 1 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7023 | L_BUCHAN1_2Y | 2 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7024 | L_BUCHAN1_3Y | 3 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7026 | L_INKSDA1_1Y | 1 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7028 | L_MARBFA1_1Y | 1 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7029 | L_MARBFA1_2Y | 2 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7031 | L_MARSFO1G1Y | 1 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7032 | L_MARSFO1G2Y | 2 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7033 | L_MARSFO1G3Y | 3 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7035 | L_WIRTZ_1G1Y | 1 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7036 | L_WIRTZ_1G2Y | 2 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7038 | L_DELAWA1_1Y | 1 | WEST | 3.5 | -0.046113 | -0.12935 | 1.3255 | 0.12935 | -1.3255 | -0.027919 | -0.027919 | -0.033183 | -0.039567 | -0.02121 | -0.036631 | -0.036631 | -0.02121 | -0.036631 | -0.045843
7038 | L_DELAWA1_1Y | 2 | WEST | 3 | -0.039525 | -0.11087 | 1.1362 | 0.11087 | -1.1362 | -0.023931 | -0.023931 | -0.028443 | -0.033915 | -0.01818 | -0.031398 | -0.031398 | -0.01818 | -0.031398 | -0.039294
7303 | L_WPPGS12_1Y | 1 | SOUTH | 50 | -6.4509 | -21.8639 | 1.3182 | 21.8639 | -1.3182 | -3.8169 | -3.8169 | -5.2312 | -5.4074 | -2.6778 | -5.1441 | -5.1441 | -2.6778 | -5.1441 | -6.6775
7303 | L_WPPGS12_1Y | 2 | SOUTH | 50 | -6.4509 | -21.8639 | 1.3182 | 21.8639 | -1.3182 | -3.8169 | -3.8169 | -5.2312 | -5.4074 | -2.6778 | -5.1441 | -5.1441 | -2.6778 | -5.1441 | -6.6775
7305 | L_WPPGS34_1Y | 3 | SOUTH | 50 | -6.4509 | -21.8639 | 1.3182 | 21.8639 | -1.3182 | -3.8169 | -3.8169 | -5.2312 | -5.4074 | -2.6778 | -5.1441 | -5.1441 | -2.6778 | -5.1441 | -6.6775
7305 | L_WPPGS34_1Y | 4 | SOUTH | 50 | -6.4509 | -21.8639 | 1.3182 | 21.8639 | -1.3182 | -3.8169 | -3.8169 | -5.2312 | -5.4074 | -2.6778 | -5.1441 | -5.1441 | -2.6778 | -5.1441 | -6.6775
7487 | L_CANYHY8_1Y | 1 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7605 | L_MCQUEE9_1Y | 1 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7605 | L_MCQUEE9_1Y | 2 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7605 | L_MCQUEE9_1Y | 3 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7609 | L_SCHUMA8_1Y | 1 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7624 | L_LAKEWO9_1Y | 1 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7624 | L_LAKEWO9_1Y | 2 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7800 | L_GUADGE1_1Y | 1 | SOUTH | 147 | -20.2917 | -61.2652 | 4.4194 | 61.2652 | -4.4194 | -11.8526 | -11.8526 | -16.2116 | -16.5531 | -9.4521 | -16.1119 | -16.1119 | -9.4521 | -16.1119 | -20.0662
7801 | L_GUADGE1_2Y | 2 | SOUTH | 138 | -19.0494 | -57.5143 | 4.1488 | 57.5143 | -4.1488 | -11.1269 | -11.1269 | -15.2191 | -15.5396 | -8.8734 | -15.1255 | -15.1255 | -8.8734 | -15.1255 | -18.8377
7802 | L_GUADGE1_3Y | 3 | SOUTH | 146 | -20.1537 | -60.8484 | 4.3893 | 60.8484 | -4.3893 | -11.772 | -11.772 | -16.1013 | -16.4405 | -9.3878 | -16.0023 | -16.0023 | -9.3878 | -16.0023 | -19.9297
7803 | L_GUADGE1_4Y | 4 | SOUTH | 149 | -20.5678 | -62.0987 | 4.4795 | 62.0987 | -4.4795 | -12.0139 | -12.0139 | -16.4322 | -16.7783 | -9.5807 | -16.3311 | -16.3311 | -9.5807 | -16.3311 | -20.3392
7804 | L_GUADGE1_5Y | 5 | SOUTH | 182 | -25.1231 | -75.8521 | 5.4716 | 75.8521 | -5.4716 | -14.6747 | -14.6747 | -20.0715 | -20.4943 | -11.7026 | -19.9481 | -19.9481 | -11.7026 | -19.9481 | -24.8439
7805 | L_GUADGE1_6Y | 6 | SOUTH | 203 | -28.0219 | -84.6043 | 6.103 | 84.6043 | -6.103 | -16.3679 | -16.3679 | -22.3874 | -22.859 | -13.0529 | -22.2498 | -22.2498 | -13.0529 | -22.2498 | -27.7105
7807 | L_BASTEN1_1Y | 1 | SOUTH | 152.5 | -17.7547 | -71.6023 | 4.0225 | 71.6023 | -4.0225 | -10.2671 | -10.2671 | -14.1639 | -15.0135 | -7.9419 | -14.1122 | -14.1122 | -7.9419 | -14.1122 | -17.8445
7808 | L_BASTEN1_2Y | 1 | SOUTH | 149.5 | -17.4054 | -70.1937 | 3.9434 | 70.1937 | -3.9434 | -10.0651 | -10.0651 | -13.8853 | -14.7181 | -7.7857 | -13.8346 | -13.8346 | -7.7857 | -13.8346 | -17.4934
7809 | L_BASTEN1_3Y | 1 | SOUTH | 232.6 | -27.0802 | -109.211 | 6.1353 | 109.211 | -6.1353 | -15.6598 | -15.6598 | -21.6034 | -22.8992 | -12.1133 | -21.5246 | -21.5246 | -12.1133 | -21.5246 | -27.2172
7810 | L_RIONOG1G1Y | 1 | SOUTH | 148 | -19.9198 | -62.8124 | 4.3974 | 62.8124 | -4.3974 | -11.6218 | -11.6218 | -15.9125 | -16.3302 | -9.2222 | -15.819 | -15.819 | -9.2222 | -15.819 | -19.7478
7811 | L_RIONOG1G2Y | 2 | SOUTH | 148 | -19.9198 | -62.8124 | 4.3974 | 62.8124 | -4.3974 | -11.6218 | -11.6218 | -15.9125 | -16.3302 | -9.2222 | -15.819 | -15.819 | -9.2222 | -15.819 | -19.7478
7812 | L_RIONOG1G3Y | 3 | SOUTH | 154 | -20.7273 | -65.3588 | 4.5756 | 65.3588 | -4.5756 | -12.093 | -12.093 | -16.5576 | -16.9922 | -9.596 | -16.4603 | -16.4603 | -9.596 | -16.4603 | -20.5484
7813 | L_RIONOG1S1Y | 4 | SOUTH | 293 | -39.4357 | -124.3515 | 8.7056 | 124.3515 | -8.7056 | -23.0081 | -23.0081 | -31.5025 | -32.3293 | -18.2574 | -31.3173 | -31.3173 | -18.2574 | -31.3173 | -39.0953
8032 | AMISTADHYD1 | 1 | SOUTH | 33 | -3.425 | -9.4304 | 4.3628 | 9.4304 | -4.3628 | -2.009 | -2.009 | -2.7264 | -2.7747 | -1.6097 | -2.7192 | -2.7192 | -1.6097 | -2.7192 | -3.375
8033 | AMISTADHYD2 | 2 | SOUTH | 25 | -2.5947 | -7.1443 | 3.3052 | 7.1443 | -3.3052 | -1.522 | -1.522 | -2.0654 | -2.1021 | -1.2194 | -2.06 | -2.06 | -1.2194 | -2.06 | -2.5568
8048 | FALCONHYDRO1 | 1 | SOUTH | 12 | -1.8438 | -4.4855 | 0.4345 | 4.4855 | -0.4345 | -1.0832 | -1.0832 | -1.4749 | -1.4725 | -0.87859 | -1.4634 | -1.4634 | -0.87859 | -1.4634 | -1.8065
8173 | VICEC51A | 5 | SOUTH | 144 | -23.0321 | -53.9158 | 4.1936 | 53.9158 | -4.1936 | -13.5723 | -13.5723 | -18.4722 | -18.3672 | -10.8871 | -18.293 | -18.293 | -10.8871 | -18.293 | -22.6588
8174 | VICEC61A | 6 | SOUTH | 188 | -30.0697 | -70.39 | 5.4749 | 70.39 | -5.4749 | -17.7194 | -17.7194 | -24.1165 | -23.9794 | -14.2137 | -23.8826 | -23.8826 | -14.2137 | -23.8826 | -29.5824
8262 | ELPS | 1 | SOUTH | 6 | -0.69385 | -1.8903 | 0.63035 | 1.8903 | -0.63035 | -0.4069 | -0.4069 | -0.55318 | -0.56102 | -0.32654 | -0.55084 | -0.55084 | -0.32654 | -0.55084 | -0.68333
8442 | NBEC7 | 1 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS0B | 7 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8460 | B_DAVIS0A | MB | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8560 | CNOPGT1 | MB | SOUTH | 148.3 | -23.5537 | -55.5081 | 4.5525 | 55.5081 | -4.5525 | -13.8468 | -13.8468 | -18.8479 | -18.757 | -11.253 | -18.6928 | -18.6928 | -11.253 | -18.6928 | -23.0519
8561 | CNOPGT2 | 1 | SOUTH | 148.6 | -23.6014 | -55.6204 | 4.5617 | 55.6204 | -4.5617 | -13.8748 | -13.8748 | -18.886 | -18.7949 | -11.2758 | -18.7306 | -18.7306 | -11.2758 | -18.7306 | -23.0985
8562 | CNOPST1 | 2 | SOUTH | 153 | -24.3002 | -57.2673 | 4.6968 | 57.2673 | -4.6968 | -14.2856 | -14.2856 | -19.4452 | -19.3514 | -11.6096 | -19.2852 | -19.2852 | -11.6096 | -19.2852 | -23.7825
8926 | LGE_GT10A | 3 | SOUTH | 158 | -25.2659 | -58.9019 | 4.7977 | 58.9019 | -4.7977 | -14.8572 | -14.8572 | -20.2201 | -20.102 | -12.0812 | -20.0515 | -20.0515 | -12.0812 | -20.0515 | -24.7193
8927 | LGE_GT20A | 1 | SOUTH | 153 | -24.4664 | -57.0379 | 4.6458 | 57.0379 | -4.6458 | -14.387 | -14.387 | -19.5802 | -19.4659 | -11.6988 | -19.4169 | -19.4169 | -11.6988 | -19.4169 | -23.937
8928 | LGE_STG0A | 2 | SOUTH | 100 | -15.9911 | -37.2797 | 3.0365 | 37.2797 | -3.0365 | -9.4033 | -9.4033 | -12.7975 | -12.7228 | -7.6463 | -12.6908 | -12.6908 | -7.6463 | -12.6908 | -15.6451
8930 | ICPGN10A | 3 | SOUTH | 149 | -23.8267 | -55.5468 | 4.5244 | 55.5468 | -4.5244 | -14.0109 | -14.0109 | -19.0683 | -18.957 | -11.393 | -18.9093 | -18.9093 | -11.393 | -18.9093 | -23.3112
8931 | ICPGN20A | 1 | SOUTH | 150 | -23.9867 | -55.9196 | 4.5548 | 55.9196 | -4.5548 | -14.105 | -14.105 | -19.1962 | -19.0842 | -11.4695 | -19.0362 | -19.0362 | -11.4695 | -19.0362 | -23.4676
8932 | ICPGN30A | 2 | SOUTH | 127 | -20.3087 | -47.3452 | 3.8564 | 47.3452 | -3.8564 | -11.9422 | -11.9422 | -16.2528 | -16.158 | -9.7108 | -16.1173 | -16.1173 | -9.7108 | -16.1173 | -19.8693
8933 | FGNTS001 | 3 | SOUTH | 146.5 | -22.9952 | -54.9675 | 4.707 | 54.9675 | -4.707 | -13.513 | -13.513 | -18.397 | -18.334 | -10.977 | -18.2494 | -18.2494 | -10.977 | -18.2494 | -22.5125
8934 | FGNTS101 | 1 | SOUTH | 147.9 | -23.215 | -55.4928 | 4.752 | 55.4928 | -4.752 | -13.6421 | -13.6421 | -18.5728 | -18.5092 | -11.0819 | -18.4238 | -18.4238 | -11.0819 | -18.4238 | -22.7276
8935 | FGNTS201 | 2 | SOUTH | 173 | -27.1548 | -64.9105 | 5.5585 | 64.9105 | -5.5585 | -15.9573 | -15.9573 | -21.7248 | -21.6504 | -12.9625 | -21.5504 | -21.5504 | -12.9625 | -21.5504 | -26.5847
8936 | MVGN#1 | 3 | SOUTH | 216.6 | -34.119 | -81.3214 | 6.8106 | 81.3214 | -6.8106 | -20.0511 | -20.0511 | -27.2974 | -27.1956 | -16.2918 | -27.0772 | -27.0772 | -16.2918 | -27.0772 | -33.3986
8937 | MVGN#2 | 1 | SOUTH | 216.7 | -34.1348 | -81.3589 | 6.8137 | 81.3589 | -6.8137 | -20.0604 | -20.0604 | -27.3101 | -27.2082 | -16.2993 | -27.0897 | -27.0897 | -16.2993 | -27.0897 | -33.4141
8938 | MVGN#3 | 2 | SOUTH | 250.9 | -39.522 | -94.1992 | 7.889 | 94.1992 | -7.889 | -23.2263 | -23.2263 | -31.6202 | -31.5023 | -18.8717 | -31.365 | -31.365 | -18.8717 | -31.365 | -38.6875
8981 | HECN1 | 3 | SOUTH | 144.8 | -22.809 | -54.3643 | 4.5531 | 54.3643 | -4.5531 | -13.4043 | -13.4043 | -18.2486 | -18.1805 | -10.8913 | -18.1014 | -18.1014 | -10.8913 | -18.1014 | -22.3273
8982 | HECN2 | 1 | SOUTH | 144.1 | -22.6988 | -54.1015 | 4.5311 | 54.1015 | -4.5311 | -13.3395 | -13.3395 | -18.1603 | -18.0926 | -10.8386 | -18.0139 | -18.0139 | -10.8386 | -18.0139 | -22.2194
8983 | HECN3 | 2 | SOUTH | 171.9 | -27.0779 | -64.5388 | 5.4052 | 64.5388 | -5.4052 | -15.913 | -15.913 | -21.6639 | -21.5831 | -12.9296 | -21.4892 | -21.4892 | -12.9296 | -21.4892 | -26.5059
9000 | DECKR_G1 | 3 | SOUTH | 280 | -31.5106 | -130.443 | 7.8697 | 130.443 | -7.8697 | -18.2255 | -18.2255 | -25.0768 | -26.7534 | -14.0476 | -25.0522 | -25.0522 | -14.0476 | -25.0522 | -31.7184
9001 | DECKR_G2 | 1 | SOUTH | 400 | -45.0152 | -186.3472 | 11.2424 | 186.3472 | -11.2424 | -26.0364 | -26.0364 | -35.824 | -38.2192 | -20.068 | -35.7888 | -35.7888 | -20.068 | -35.7888 | -45.312
9002 | DECKR_G3 | 2 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9003 | DECKR_G4 | 3 | SOUTH | 44 | -4.9149 | -20.6155 | 1.2235 | 20.6155 | -1.2235 | -2.8414 | -2.8414 | -3.9116 | -4.1811 | -2.1851 | -3.9079 | -3.9079 | -2.1851 | -3.9079 | -4.9527
9004 | DECKR_G5 | 4 | SOUTH | 44 | -4.9149 | -20.6155 | 1.2235 | 20.6155 | -1.2235 | -2.8414 | -2.8414 | -3.9116 | -4.1811 | -2.1851 | -3.9079 | -3.9079 | -2.1851 | -3.9079 | -4.9527
9005 | DECKR_G6 | 5 | SOUTH | 44 | -4.9149 | -20.6155 | 1.2235 | 20.6155 | -1.2235 | -2.8414 | -2.8414 | -3.9116 | -4.1811 | -2.1851 | -3.9079 | -3.9079 | -2.1851 | -3.9079 | -4.9527
9016 | SANDH_G1 | 6 | SOUTH | 45 | -5.1139 | -20.895 | 1.2654 | 20.895 | -1.2654 | -2.9592 | -2.9592 | -4.0714 | -4.3338 | -2.2832 | -4.0655 | -4.0655 | -2.2832 | -4.0655 | -5.1444
9017 | SANDH_G2 | 1 | SOUTH | 45 | -5.1139 | -20.895 | 1.2654 | 20.895 | -1.2654 | -2.9592 | -2.9592 | -4.0714 | -4.3338 | -2.2832 | -4.0655 | -4.0655 | -2.2832 | -4.0655 | -5.1444
9018 | SANDH_G3 | 2 | SOUTH | 45 | -5.1139 | -20.895 | 1.2654 | 20.895 | -1.2654 | -2.9592 | -2.9592 | -4.0714 | -4.3338 | -2.2832 | -4.0655 | -4.0655 | -2.2832 | -4.0655 | -5.1444
9019 | SANDH_G4 | 3 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9020 | SANDHG5A | 4 | SOUTH | 150 | -17.0463 | -69.6501 | 4.2181 | 69.6501 | -4.2181 | -9.8642 | -9.8642 | -13.5714 | -14.446 | -7.6105 | -13.5516 | -13.5516 | -7.6105 | -13.5516 | -17.148
9021 | SANDHG5C | 5A | SOUTH | 140 | -15.9099 | -65.0068 | 3.9369 | 65.0068 | -3.9369 | -9.2065 | -9.2065 | -12.6666 | -13.483 | -7.1032 | -12.6482 | -12.6482 | -7.1032 | -12.6482 | -16.0048
11001 | NAV1CT | 5C | WEST | 70.4 | -0.87866 | -2.4556 | 26.9612 | 2.4556 | -26.9612 | -0.53307 | -0.53307 | -0.62825 | -0.7561 | -0.40374 | -0.69795 | -0.69795 | -0.40374 | -0.69795 | -0.8738
11009 | NAV2CT | 1 | WEST | 71.4 | -0.89114 | -2.4905 | 27.3441 | 2.4905 | -27.3441 | -0.54064 | -0.54064 | -0.63717 | -0.76684 | -0.40948 | -0.70786 | -0.70786 | -0.40948 | -0.70786 | -0.88622
11011 | NAV3ST | 1 | WEST | 92.8 | -1.1582 | -3.237 | 35.5397 | 3.237 | -35.5397 | -0.70268 | -0.70268 | -0.82815 | -0.99667 | -0.53221 | -0.92002 | -0.92002 | -0.53221 | -0.92002 | -1.1518
11012 | NAV4CT | 1 | WEST | 80 | -0.99848 | -2.7905 | 30.6377 | 2.7905 | -30.6377 | -0.60576 | -0.60576 | -0.71392 | -0.8592 | -0.4588 | -0.79312 | -0.79312 | -0.4588 | -0.79312 | -0.99296
11013 | NAV5CT | 1 | WEST | 80 | -0.99848 | -2.7905 | 30.6377 | 2.7905 | -30.6377 | -0.60576 | -0.60576 | -0.71392 | -0.8592 | -0.4588 | -0.79312 | -0.79312 | -0.4588 | -0.79312 | -0.99296
11014 | NAV6ST | 1 | WEST | 115 | -1.4353 | -4.0113 | 44.0417 | 4.0113 | -44.0417 | -0.87078 | -0.87078 | -1.0263 | -1.2351 | -0.65953 | -1.1401 | -1.1401 | -0.65953 | -1.1401 | -1.4274
11020 | TIEHVSG_1G | 1 | WEST | 208.2 | -2.6002 | -7.2674 | 79.7248 | 7.2674 | -79.7248 | -1.5775 | -1.5775 | -1.8592 | -2.2373 | -1.1949 | -2.0656 | -2.0656 | -1.1949 | -2.0656 | -2.5861
11021 | TIEHVCG_1G | 1 | WEST | 142.1 | -1.7747 | -4.9601 | 54.4135 | 4.9601 | -54.4135 | -1.0767 | -1.0767 | -1.269 | -1.527 | -0.81551 | -1.4098 | -1.4098 | -0.81551 | -1.4098 | -1.765
11022 | TIEHVCG_2G | 1 | WEST | 132.4 | -1.6535 | -4.6216 | 50.6991 | 4.6216 | -50.6991 | -1.0032 | -1.0032 | -1.1823 | -1.4228 | -0.75984 | -1.3135 | -1.3135 | -0.75984 | -1.3135 | -1.6445
11023 | TIEHVCG_3G | 1 | WEST | 137.4 | -1.716 | -4.7961 | 52.6138 | 4.7961 | -52.6138 | -1.0411 | -1.0411 | -1.227 | -1.4765 | -0.78854 | -1.3631 | -1.3631 | -0.78854 | -1.3631 | -1.7066
11024 | TIEHVCG_4G | 1 | WEST | 147 | -1.8359 | -5.1312 | 56.2898 | 5.1312 | -56.2898 | -1.1138 | -1.1138 | -1.3127 | -1.5797 | -0.84363 | -1.4584 | -1.4584 | -0.84363 | -1.4584 | -1.8259
11025 | TIEHVSG_2G | 1 | WEST | 213.2 | -2.6627 | -7.442 | 81.6394 | 7.442 | -81.6394 | -1.6154 | -1.6154 | -1.9039 | -2.291 | -1.2236 | -2.1152 | -2.1152 | -1.2236 | -2.1152 | -2.6482
11056 | ROSCOE_1G | 1 | WEST | 41.8 | -0.45328 | -1.2429 | 13.6584 | 1.2429 | -13.6584 | -0.27663 | -0.27663 | -0.31877 | -0.39254 | -0.20791 | -0.36011 | -0.36011 | -0.20791 | -0.36011 | -0.45115
11057 | CHAMPION_1G | 1 | WEST | 25.3 | -0.27435 | -0.75227 | 8.2669 | 0.75227 | -8.2669 | -0.16744 | -0.16744 | -0.19294 | -0.23759 | -0.12584 | -0.21796 | -0.21796 | -0.12584 | -0.21796 | -0.27306
11058 | PYRON_1G | 1 | WEST | 49.8 | -0.54003 | -1.4808 | 16.2724 | 1.4808 | -16.2724 | -0.32958 | -0.32958 | -0.37977 | -0.46767 | -0.24771 | -0.42903 | -0.42903 | -0.24771 | -0.42903 | -0.53749
11059 | INADALE_1G | 1 | WEST | 39.4 | -0.42725 | -1.1715 | 12.8741 | 1.1715 | -12.8741 | -0.26075 | -0.26075 | -0.30046 | -0.37001 | -0.19598 | -0.33943 | -0.33943 | -0.19598 | -0.33943 | -0.42524
11065 | ELBOWCK_1G | 1 | WEST | 23.4 | -0.27432 | -0.76307 | 9.0614 | 0.76307 | -9.0614 | -0.16684 | -0.16684 | -0.19459 | -0.23688 | -0.12592 | -0.21792 | -0.21792 | -0.12592 | -0.21792 | -0.27294
11147 | NOTREES_1G | 1 | WEST | 29.8 | -0.38978 | -1.0929 | 11.2799 | 1.0929 | -11.2799 | -0.23605 | -0.23605 | -0.28024 | -0.33459 | -0.17925 | -0.30962 | -0.30962 | -0.17925 | -0.30962 | -0.38752
11309 | BULLCREK_2G | 1 | WEST | 20.9 | -0.24932 | -0.69545 | 7.7372 | 0.69545 | -7.7372 | -0.15152 | -0.15152 | -0.17709 | -0.21529 | -0.11445 | -0.19805 | -0.19805 | -0.11445 | -0.19805 | -0.24806
11310 | BULLCREK_1G | 1 | WEST | 15.1 | -0.18013 | -0.50245 | 5.59 | 0.50245 | -5.59 | -0.10948 | -0.10948 | -0.12794 | -0.15555 | -0.082688 | -0.14309 | -0.14309 | -0.082688 | -0.14309 | -0.17922
11320 | COYOTE_1G | 1 | WEST | 22.5 | -0.26939 | -0.7517 | 8.3381 | 0.7517 | -8.3381 | -0.16371 | -0.16371 | -0.19145 | -0.23258 | -0.12366 | -0.21402 | -0.21402 | -0.12366 | -0.21402 | -0.26804
11691 | KMICHICT1_G | 1 | NORTH | 144 | 0.23832 | -0.87437 | -0.25718 | 0.87437 | 0.25718 | 0.15307 | 0.15307 | 0.045648 | 0.31594 | 0.10642 | 0.1895 | 0.1895 | 0.10642 | 0.1895 | 0.23976
11692 | KMICHICT2_G | 1 | NORTH | 146 | 0.24163 | -0.88651 | -0.26076 | 0.88651 | 0.26076 | 0.1552 | 0.1552 | 0.046282 | 0.32032 | 0.10789 | 0.19214 | 0.19214 | 0.10789 | 0.19214 | 0.24309
11693 | KMICHIST3_G | 2 | NORTH | 312 | 0.51636 | -1.8945 | -0.55723 | 1.8945 | 0.55723 | 0.33166 | 0.33166 | 0.098904 | 0.68453 | 0.23057 | 0.41059 | 0.41059 | 0.23057 | 0.41059 | 0.51948
11694 | KMICHICT4_G | 3 | NORTH | 144 | 0.23832 | -0.87437 | -0.25718 | 0.87437 | 0.25718 | 0.15307 | 0.15307 | 0.045648 | 0.31594 | 0.10642 | 0.1895 | 0.1895 | 0.10642 | 0.1895 | 0.23976
11695 | KMICHICT5_G | 4 | NORTH | 148 | 0.24494 | -0.89866 | -0.26433 | 0.89866 | 0.26433 | 0.15732 | 0.15732 | 0.046916 | 0.32471 | 0.10937 | 0.19477 | 0.19477 | 0.10937 | 0.19477 | 0.24642
11696 | KMICHIST6_G | 5 | NORTH | 310 | 0.51305 | -1.8823 | -0.55366 | 1.8823 | 0.55366 | 0.32953 | 0.32953 | 0.09827 | 0.68014 | 0.22909 | 0.40796 | 0.40796 | 0.22909 | 0.40796 | 0.51615
12322 | ENNSTRAC_1G | 6 | NORTH | 196 | 0.098784 | -1.0351 | 0.64308 | 1.0351 | -0.64308 | 0.15249 | 0.15249 | -0.22481 | 0.19561 | 0.045276 | 0.078596 | 0.078596 | 0.045276 | 0.078596 | 0.098392
12323 | ENNSTRAC_2G | 1 | NORTH | 116 | 0.058464 | -0.6126 | 0.3806 | 0.6126 | -0.3806 | 0.090248 | 0.090248 | -0.13305 | 0.11577 | 0.026796 | 0.046516 | 0.046516 | 0.026796 | 0.046516 | 0.058232
12411 | FPLEFR1A_G | 2 | NORTH | 161 | 0.50474 | -1.2883 | 0.007084 | 1.2883 | -0.007084 | 0.32731 | 0.32731 | 0.14361 | 0.61454 | 0.22604 | 0.40121 | 0.40121 | 0.22604 | 0.40121 | 0.50699
12412 | FPLEFR1B_G | 1 | NORTH | 164 | 0.51414 | -1.3123 | 0.007216 | 1.3123 | -0.007216 | 0.33341 | 0.33341 | 0.14629 | 0.62599 | 0.23026 | 0.40869 | 0.40869 | 0.23026 | 0.40869 | 0.51644
12413 | FPLEFR1C_G | 2 | NORTH | 164 | 0.51414 | -1.3123 | 0.007216 | 1.3123 | -0.007216 | 0.33341 | 0.33341 | 0.14629 | 0.62599 | 0.23026 | 0.40869 | 0.40869 | 0.23026 | 0.40869 | 0.51644
12414 | FPLEFR1S_G | 3 | NORTH | 414 | 1.2979 | -3.3128 | 0.018216 | 3.3128 | -0.018216 | 0.84166 | 0.84166 | 0.36929 | 1.5802 | 0.58126 | 1.0317 | 1.0317 | 0.58126 | 1.0317 | 1.3037
12421 | FPLEFR2A_G | 4 | NORTH | 162 | 0.50787 | -1.2963 | 0.007128 | 1.2963 | -0.007128 | 0.32935 | 0.32935 | 0.1445 | 0.61835 | 0.22745 | 0.4037 | 0.4037 | 0.22745 | 0.4037 | 0.51014
12422 | FPLEFR2B_G | 1 | NORTH | 161 | 0.50474 | -1.2883 | 0.007084 | 1.2883 | -0.007084 | 0.32731 | 0.32731 | 0.14361 | 0.61454 | 0.22604 | 0.40121 | 0.40121 | 0.22604 | 0.40121 | 0.50699
12423 | FPLEFR2C_G | 2 | NORTH | 163 | 0.51101 | -1.3043 | 0.007172 | 1.3043 | -0.007172 | 0.33138 | 0.33138 | 0.1454 | 0.62217 | 0.22885 | 0.4062 | 0.4062 | 0.22885 | 0.4062 | 0.51329
12424 | FPLEFR2S_G | 3 | NORTH | 415 | 1.301 | -3.3208 | 0.01826 | 3.3208 | -0.01826 | 0.84369 | 0.84369 | 0.37018 | 1.5841 | 0.58266 | 1.0342 | 1.0342 | 0.58266 | 1.0342 | 1.3068
12440 | PARKD_1SVC8 | 4 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2SVC8 | 1 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY_1G | 1 | NORTH | 151 | 0.98543 | -2.1179 | 0.35409 | 2.1179 | -0.35409 | 0.42718 | 0.42718 | 0.48033 | 1.4236 | 0.44198 | 0.78339 | 0.78339 | 0.44198 | 0.78339 | 0.98965
13117 | TGATEWAY_2G | 1 | NORTH | 130 | 0.84838 | -1.8234 | 0.30485 | 1.8234 | -0.30485 | 0.36777 | 0.36777 | 0.41353 | 1.2256 | 0.38051 | 0.67444 | 0.67444 | 0.38051 | 0.67444 | 0.85202
13118 | TGATEWAY_3G | 2 | NORTH | 148 | 0.96585 | -2.0758 | 0.34706 | 2.0758 | -0.34706 | 0.41869 | 0.41869 | 0.47079 | 1.3953 | 0.4332 | 0.76782 | 0.76782 | 0.4332 | 0.76782 | 0.96999
13119 | TGATEWAY_4G | 3 | NORTH | 399 | 2.6039 | -5.5964 | 0.93566 | 5.5964 | -0.93566 | 1.1288 | 1.1288 | 1.2692 | 3.7618 | 1.1679 | 2.07 | 2.07 | 1.1679 | 2.07 | 2.615
13131 | CALFREST_1G | 4 | NORTH | 150.7 | 1.7222 | -3.1813 | 0.75471 | 3.1813 | -0.75471 | 0.32325 | 0.32325 | 1.6713 | 2.5028 | 0.77249 | 1.369 | 1.369 | 0.77249 | 1.369 | 1.7293
13132 | CALFREST_2G | 1 | NORTH | 151 | 1.7256 | -3.1876 | 0.75621 | 3.1876 | -0.75621 | 0.32389 | 0.32389 | 1.6746 | 2.5078 | 0.77403 | 1.3717 | 1.3717 | 0.77403 | 1.3717 | 1.7327
13133 | CALFREST_3G | 2 | NORTH | 177.4 | 2.0273 | -3.7449 | 0.88842 | 3.7449 | -0.88842 | 0.38052 | 0.38052 | 1.9674 | 2.9463 | 0.90935 | 1.6115 | 1.6115 | 0.90935 | 1.6115 | 2.0357
13134 | CALFREST_4G | 3 | NORTH | 151.5 | 1.7004 | -3.1663 | 0.74356 | 3.1663 | -0.74356 | 0.31512 | 0.31512 | 1.6459 | 2.4834 | 0.7628 | 1.3517 | 1.3517 | 0.7628 | 1.3517 | 1.7074
13135 | CALFREST_5G | 4 | NORTH | 152.3 | 1.7094 | -3.1831 | 0.74749 | 3.1831 | -0.74749 | 0.31678 | 0.31678 | 1.6546 | 2.4965 | 0.76683 | 1.3588 | 1.3588 | 0.76683 | 1.3588 | 1.7164
13136 | CALFREST_6G | 5 | NORTH | 177.5 | 1.9923 | -3.7098 | 0.87117 | 3.7098 | -0.87117 | 0.3692 | 0.3692 | 1.9284 | 2.9096 | 0.89371 | 1.5837 | 1.5837 | 0.89371 | 1.5837 | 2.0004
32883 | BRYN_DNSBY3 | 6 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32884 | BRYN_DNSBY13 | 1 | NORTH | 46 | 1.6132 | -6.0456 | 0.544 | 6.0456 | -0.544 | 9.3937 | 9.3937 | -7.7714 | -6.5006 | 0.7234 | 1.2822 | 1.2822 | 0.7234 | 1.2822 | 1.6199
32886 | BRYN_ATKINS3 | 1 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32887 | BRYN_ATKINS6 | MB | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32888 | BRYN_ATKINS7 | MB | NORTH | 13.6 | 0.52262 | -1.7058 | 0.15956 | 1.7058 | -0.15956 | 2.9622 | 2.9622 | -2.4153 | -2.0461 | 0.23427 | 0.41541 | 0.41541 | 0.23427 | 0.41541 | 0.52488
32890 | BRYN_ATKINS4 | 1 | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32891 | BRYN_ATKINS5 | MB | NORTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32892 | BRYN_DNSBY14 | MB | NORTH | 105 | 3.6822 | -13.7996 | 1.2417 | 13.7996 | -1.2417 | 21.442 | 21.442 | -17.739 | -14.8384 | 1.6512 | 2.9269 | 2.9269 | 1.6512 | 2.9269 | 3.6977
36998 | RDCNYNG1 | 1 | WEST | 16.8 | -0.19313 | -0.53666 | 5.9704 | 0.53666 | -5.9704 | -0.11755 | -0.11755 | -0.13645 | -0.16723 | -0.088586 | -0.15342 | -0.15342 | -0.088586 | -0.15342 | -0.19221
38332 | TNWDWRDU2_8 | 1 | WEST | 20 | -0.36918 | -1.0528 | 7.1622 | 1.0528 | -7.1622 | -0.22116 | -0.22116 | -0.27452 | -0.31184 | -0.17066 | -0.29322 | -0.29322 | -0.17066 | -0.29322 | -0.36628
38437 | TNSRBNMESA9 | 1 | WEST | 37.5 | -0.69401 | -1.9794 | 13.4219 | 1.9794 | -13.4219 | -0.41573 | -0.41573 | -0.51619 | -0.58616 | -0.32085 | -0.55121 | -0.55121 | -0.32085 | -0.55121 | -0.68854
38611 | TNBPAMCG1_8 | 1 | HOUSTON | 153.2 | -33.5142 | -38.7178 | 2.9923 | 38.7178 | -2.9923 | -21.0933 | -21.0933 | -28.4652 | -26.9146 | -20.8127 | -29.7236 | -29.7236 | -20.8127 | -29.7236 | -34.3287
38612 | TNBPAMCG2_8 | 1 | HOUSTON | 153.5 | -33.5798 | -38.7936 | 2.9982 | 38.7936 | -2.9982 | -21.1346 | -21.1346 | -28.5209 | -26.9673 | -20.8534 | -29.7818 | -29.7818 | -20.8534 | -29.7818 | -34.396
38613 | TNBPAMCG3_8 | 2 | HOUSTON | 152.3 | -33.3173 | -38.4903 | 2.9747 | 38.4903 | -2.9747 | -20.9694 | -20.9694 | -28.2979 | -26.7565 | -20.6904 | -29.5489 | -29.5489 | -20.6904 | -29.5489 | -34.1271
38614 | TNBPAMCG4_8 | 3 | HOUSTON | 96 | -21.0011 | -24.2618 | 1.8751 | 24.2618 | -1.8751 | -13.2178 | -13.2178 | -17.8372 | -16.8656 | -13.0419 | -18.6257 | -18.6257 | -13.0419 | -18.6257 | -21.5115
38615 | TNBPAMCG5_8 | 4 | HOUSTON | 244 | -53.3777 | -61.6654 | 4.7658 | 61.6654 | -4.7658 | -33.5951 | -33.5951 | -45.3362 | -42.8667 | -33.1481 | -47.3404 | -47.3404 | -33.1481 | -47.3404 | -54.675
38711 | TNTXCTY1CG8 | 1 | HOUSTON | 100.3 | -21.9417 | -25.3485 | 1.9591 | 25.3485 | -1.9591 | -13.8098 | -13.8098 | -18.6361 | -17.621 | -13.6261 | -19.46 | -19.46 | -13.6261 | -19.46 | -22.475
38712 | TNTXCTY2CG8 | 1 | HOUSTON | 92.9 | -20.3229 | -23.4783 | 1.8145 | 23.4783 | -1.8145 | -12.7909 | -12.7909 | -17.2612 | -16.321 | -12.6207 | -18.0243 | -18.0243 | -12.6207 | -18.0243 | -20.8168
38713 | TNTXCTY3CG8 | 1 | HOUSTON | 102.7 | -22.4668 | -25.9551 | 2.0059 | 25.9551 | -2.0059 | -14.1402 | -14.1402 | -19.0821 | -18.0426 | -13.9521 | -19.9256 | -19.9256 | -13.9521 | -19.9256 | -23.0128
38714 | TNTXCTY4CG8 | 1 | HOUSTON | 103 | -22.5324 | -26.0309 | 2.0118 | 26.0309 | -2.0118 | -14.1816 | -14.1816 | -19.1378 | -18.0953 | -13.9929 | -19.9839 | -19.9839 | -13.9929 | -19.9839 | -23.08
39760 | TNSCLP1___8 | 1 | HOUSTON | 93.4 | -19.9612 | -26.2283 | 1.9775 | 26.2283 | -1.9775 | -11.959 | -11.959 | -16.1623 | -15.4143 | -10.1181 | -16.0699 | -16.0699 | -10.1181 | -16.0699 | -19.4635
39770 | TNSCLP2___8 | 1 | HOUSTON | 91.6 | -19.5765 | -25.7228 | 1.9394 | 25.7228 | -1.9394 | -11.7286 | -11.7286 | -15.8508 | -15.1172 | -9.9231 | -15.7602 | -15.7602 | -9.9231 | -15.7602 | -19.0884
39775 | TNSCLP4___8 | 1 | HOUSTON | 95.2 | -20.3459 | -26.7338 | 2.0156 | 26.7338 | -2.0156 | -12.1895 | -12.1895 | -16.4738 | -15.7113 | -10.3131 | -16.3796 | -16.3796 | -10.3131 | -16.3796 | -19.8386
39790 | TNSCLP3___8 | 1 | HOUSTON | 87.6 | -18.7216 | -24.5996 | 1.8547 | 24.5996 | -1.8547 | -11.2164 | -11.2164 | -15.1587 | -14.4571 | -9.4898 | -15.072 | -15.072 | -9.4898 | -15.072 | -18.2549
48511 | LPE_GT1_8070 | 1 | HOUSTON | 42 | -9.0556 | -9.888 | 0.77944 | 9.888 | -0.77944 | -6.0311 | -6.0311 | -8.1323 | -7.6528 | -6.5589 | -8.8533 | -8.8533 | -6.5589 | -8.8533 | -9.9383
48512 | LPE_GT2_8075 | 1 | HOUSTON | 42 | -9.0556 | -9.888 | 0.77944 | 9.888 | -0.77944 | -6.0311 | -6.0311 | -8.1323 | -7.6528 | -6.5589 | -8.8533 | -8.8533 | -6.5589 | -8.8533 | -9.9383
48513 | LPE_GT3_8080 | 2 | HOUSTON | 39 | -8.4088 | -9.1817 | 0.72376 | 9.1817 | -0.72376 | -5.6003 | -5.6003 | -7.5514 | -7.1062 | -6.0904 | -8.221 | -8.221 | -6.0904 | -8.221 | -9.2285
48514 | LPE_GT4_8085 | 3 | HOUSTON | 39 | -8.4088 | -9.1817 | 0.72376 | 9.1817 | -0.72376 | -5.6003 | -5.6003 | -7.5514 | -7.1062 | -6.0904 | -8.221 | -8.221 | -6.0904 | -8.221 | -9.2285
48521 | BVE_GT1_GT1 | 4 | HOUSTON | 167.7 | -37.601 | -45.4881 | 3.4436 | 45.4881 | -3.4436 | -22.0328 | -22.0328 | -29.7612 | -28.296 | -18.7562 | -29.2925 | -29.2925 | -18.7562 | -29.2925 | -35.2294
48522 | BVE_GT2_5035 | 1 | HOUSTON | 166.4 | -37.3095 | -45.1355 | 3.4169 | 45.1355 | -3.4169 | -21.862 | -21.862 | -29.5305 | -28.0767 | -18.6108 | -29.0654 | -29.0654 | -18.6108 | -29.0654 | -34.9563
48523 | BVE_ST1_GN1 | 2 | HOUSTON | 252.4 | -56.5921 | -68.4627 | 5.1828 | 68.4627 | -5.1828 | -33.1608 | -33.1608 | -44.7927 | -42.5875 | -28.2294 | -44.0872 | -44.0872 | -28.2294 | -44.0872 | -53.0227
48531 | BYU_GT1_8075 | 3 | HOUSTON | 65 | -14.0754 | -15.7754 | 1.2328 | 15.7754 | -1.2328 | -9.1724 | -9.1724 | -12.3721 | -11.6654 | -9.5067 | -13.2266 | -13.2266 | -9.5067 | -13.2266 | -15.0803
48532 | BYU_GT2_8055 | 1 | HOUSTON | 62 | -13.4257 | -15.0473 | 1.1759 | 15.0473 | -1.1759 | -8.7491 | -8.7491 | -11.8011 | -11.127 | -9.0679 | -12.6161 | -12.6161 | -9.0679 | -12.6161 | -14.3843
48533 | BYU_GT3_8060 | 2 | HOUSTON | 67 | -14.5084 | -16.2608 | 1.2707 | 16.2608 | -1.2707 | -9.4546 | -9.4546 | -12.7528 | -12.0243 | -9.7992 | -13.6336 | -13.6336 | -9.7992 | -13.6336 | -15.5443
48534 | BYU_GT4_8065 | 3 | HOUSTON | 65 | -14.0754 | -15.7754 | 1.2328 | 15.7754 | -1.2328 | -9.1724 | -9.1724 | -12.3721 | -11.6654 | -9.5067 | -13.2266 | -13.2266 | -9.5067 | -13.2266 | -15.0803
48581 | CBY_GN1_1 | 4 | HOUSTON | 595.2 | -128.0031 | -136.6758 | 10.8541 | 136.6758 | -10.8541 | -86.6474 | -86.6474 | -116.805 | -109.7507 | -98.0044 | -128.9923 | -128.9923 | -98.0044 | -128.9923 | -142.8545
48582 | CBY_GN2_2 | 1 | HOUSTON | 596.8 | -128.5167 | -138.3006 | 10.9531 | 138.3006 | -10.9531 | -86.4513 | -86.4513 | -116.5509 | -109.5719 | -96.5414 | -128.0691 | -128.0691 | -96.5414 | -128.0691 | -142.4389
48583 | CBY_GT4_1 | 2 | HOUSTON | 172 | -37.0564 | -39.3316 | 3.1276 | 39.3316 | -3.1276 | -25.0953 | -25.0953 | -33.8283 | -31.7773 | -29.1413 | -37.5841 | -37.5841 | -29.1413 | -37.5841 | -41.156
48584 | CBY_GT4_2 | 1 | HOUSTON | 172 | -37.0564 | -39.3316 | 3.1276 | 39.3316 | -3.1276 | -25.0953 | -25.0953 | -33.8283 | -31.7773 | -29.1413 | -37.5841 | -37.5841 | -29.1413 | -37.5841 | -41.156
48585 | CBY_ST4_1 | 2 | HOUSTON | 172 | -37.0564 | -39.3316 | 3.1276 | 39.3316 | -3.1276 | -25.0953 | -25.0953 | -33.8283 | -31.7773 | -29.1413 | -37.5841 | -37.5841 | -29.1413 | -37.5841 | -41.156
48591 | CHE_GT2_5030 | 3 | HOUSTON | 173 | -34.5561 | -37.2692 | 3.018 | 37.2692 | -3.018 | -26.0235 | -26.0235 | -35.0598 | -32.8255 | -35.919 | -42.0212 | -42.0212 | -35.919 | -42.0212 | -43.3552
48594 | CHE_GN4_8025 | 2 | HOUSTON | 142 | -30.8532 | -33.4916 | 2.6375 | 33.4916 | -2.6375 | -20.3709 | -20.3709 | -27.4685 | -25.8517 | -21.6213 | -29.6502 | -29.6502 | -21.6213 | -29.6502 | -33.5584
48641 | DPEC_GT15040 | 4 | HOUSTON | 163.2 | -35.3362 | -39.0257 | 3.0636 | 39.0257 | -3.0636 | -23.2283 | -23.2283 | -31.3261 | -29.508 | -25.4052 | -33.9853 | -33.9853 | -25.4052 | -33.9853 | -37.969
48642 | DPEC_GT25025 | 1 | HOUSTON | 157.1 | -34.0154 | -37.567 | 2.9491 | 37.567 | -2.9491 | -22.36 | -22.36 | -30.1552 | -28.4051 | -24.4556 | -32.715 | -32.715 | -24.4556 | -32.715 | -36.5498
48643 | DPEC_GT35010 | 2 | HOUSTON | 157.5 | -34.1021 | -37.6627 | 2.9566 | 37.6627 | -2.9566 | -22.417 | -22.417 | -30.232 | -28.4774 | -24.5179 | -32.7983 | -32.7983 | -24.5179 | -32.7983 | -36.6428
48644 | DPEC_GT45070 | 3 | HOUSTON | 157 | -33.9938 | -37.5431 | 2.9472 | 37.5431 | -2.9472 | -22.3458 | -22.3458 | -30.136 | -28.387 | -24.44 | -32.6942 | -32.6942 | -24.44 | -32.6942 | -36.5265
48645 | DPEC_ST55065 | 4 | HOUSTON | 282 | -61.0589 | -67.4341 | 5.2937 | 67.4341 | -5.2937 | -40.1371 | -40.1371 | -54.1296 | -50.9881 | -43.8987 | -58.7245 | -58.7245 | -43.8987 | -58.7245 | -65.6081
48671 | FTR_GT1_5105 | 5 | NORTH | 154.2 | 5.7071 | -18.9799 | 1.9133 | 18.9799 | -1.9133 | -28.0465 | -28.0465 | -37.6667 | -34.6102 | 1.0863 | 15.0018 | 15.0018 | 1.0863 | -139.1982 | 5.121
48672 | FTR_GT2_5110 | 1 | NORTH | 159 | 5.8847 | -19.5707 | 1.9729 | 19.5707 | -1.9729 | -28.9196 | -28.9196 | -38.8392 | -35.6876 | 1.1202 | 15.4688 | 15.4688 | 1.1202 | -143.5312 | 5.2804
48673 | FTR_GT3_5085 | 2 | NORTH | 158 | 5.8477 | -19.4476 | 1.9605 | 19.4476 | -1.9605 | -28.7377 | -28.7377 | -38.595 | -35.4631 | 1.1131 | 15.3715 | 15.3715 | 1.1131 | -142.6285 | 5.2472
48674 | FTR_CN4_5095 | 3 | NORTH | 380 | 14.0642 | -46.7727 | 4.715 | 46.7727 | -4.715 | -69.1159 | -69.1159 | -92.8234 | -85.291 | 2.6771 | 36.9694 | 36.9694 | 2.6771 | -343.0306 | 12.6198
48690 | GBY_GN5_5 | 4 | HOUSTON | 398 | -83.8379 | -90.3126 | 7.195 | 90.3126 | -7.195 | -58.3102 | -58.3102 | -78.5954 | -73.7972 | -64.3104 | -87.1473 | -87.1473 | -64.3104 | -87.1473 | -98.0278
48691 | GBY_73741085 | 5 | HOUSTON | 37.6 | -8.661 | -9.1213 | 0.71218 | 9.1213 | -0.71218 | -5.3078 | -5.3078 | -7.1593 | -6.7501 | -4.891 | -7.2842 | -7.2842 | -4.891 | -7.2842 | -8.5797
48691 | GBY_73741085 | A | HOUSTON | 37.6 | -8.661 | -9.1213 | 0.71218 | 9.1213 | -0.71218 | -5.3078 | -5.3078 | -7.1593 | -6.7501 | -4.891 | -7.2842 | -7.2842 | -4.891 | -7.2842 | -8.5797
48692 | GBY_81821075 | B | HOUSTON | 37.6 | -8.661 | -9.1213 | 0.71218 | 9.1213 | -0.71218 | -5.3078 | -5.3078 | -7.1593 | -6.7501 | -4.891 | -7.2842 | -7.2842 | -4.891 | -7.2842 | -8.5797
48692 | GBY_81821075 | C | HOUSTON | 44 | -10.1353 | -10.6738 | 0.8334 | 10.6738 | -0.8334 | -6.2112 | -6.2112 | -8.3779 | -7.8991 | -5.7235 | -8.5241 | -8.5241 | -5.7235 | -8.5241 | -10.0401
48693 | GBY_83841065 | D | HOUSTON | 45.6 | -10.5038 | -11.062 | 0.86371 | 11.062 | -0.86371 | -6.4371 | -6.4371 | -8.6826 | -8.1863 | -5.9316 | -8.834 | -8.834 | -5.9316 | -8.834 | -10.4052
48693 | GBY_83841065 | E | HOUSTON | 43.2 | -9.951 | -10.4798 | 0.81825 | 10.4798 | -0.81825 | -6.0983 | -6.0983 | -8.2256 | -7.7554 | -5.6195 | -8.3691 | -8.3691 | -5.6195 | -8.3691 | -9.8575
48731 | CBE_GT1 | F | HOUSTON | 76 | -14.7703 | -23.8756 | 1.7552 | 23.8756 | -1.7552 | -8.8619 | -8.8619 | -12.0012 | -11.5831 | -6.6821 | -11.7447 | -11.7447 | -6.6821 | -11.7447 | -14.793
48732 | CBE_GT2 | 1 | HOUSTON | 76 | -14.7703 | -23.8756 | 1.7552 | 23.8756 | -1.7552 | -8.8619 | -8.8619 | -12.0012 | -11.5831 | -6.6821 | -11.7447 | -11.7447 | -6.6821 | -11.7447 | -14.793
48733 | CBE_ST12 | 1 | HOUSTON | 105 | -20.4063 | -32.9861 | 2.425 | 32.9861 | -2.425 | -12.2434 | -12.2434 | -16.5807 | -16.0029 | -9.2318 | -16.2263 | -16.2263 | -9.2318 | -16.2263 | -20.4377
48734 | CBE_GT3 | 1 | HOUSTON | 76 | -14.7703 | -23.8756 | 1.7552 | 23.8756 | -1.7552 | -8.8619 | -8.8619 | -12.0012 | -11.5831 | -6.6821 | -11.7447 | -11.7447 | -6.6821 | -11.7447 | -14.793
48735 | CBE_GT4 | 1 | HOUSTON | 76 | -14.7703 | -23.8756 | 1.7552 | 23.8756 | -1.7552 | -8.8619 | -8.8619 | -12.0012 | -11.5831 | -6.6821 | -11.7447 | -11.7447 | -6.6821 | -11.7447 | -14.793
48736 | CBE_ST34 | 1 | HOUSTON | 105 | -20.4063 | -32.9861 | 2.425 | 32.9861 | -2.425 | -12.2434 | -12.2434 | -16.5807 | -16.0029 | -9.2318 | -16.2263 | -16.2263 | -9.2318 | -16.2263 | -20.4377
48740 | PSG_GN2_8050 | 1 | HOUSTON | 182 | -39.2736 | -43.3171 | 3.4034 | 43.3171 | -3.4034 | -25.9747 | -25.9747 | -35.0283 | -32.9853 | -27.7171 | -37.8842 | -37.8842 | -27.7171 | -37.8842 | -42.8053
48741 | PSG_GT2_8040 | 1 | HOUSTON | 158.6 | -34.2241 | -37.7478 | 2.9658 | 37.7478 | -2.9658 | -22.6351 | -22.6351 | -30.5246 | -28.7443 | -24.1535 | -33.0134 | -33.0134 | -24.1535 | -33.0134 | -37.3018
48742 | PSG_GT3_8060 | 1 | HOUSTON | 157 | -33.8789 | -37.3669 | 2.9359 | 37.3669 | -2.9359 | -22.4067 | -22.4067 | -30.2167 | -28.4544 | -23.9098 | -32.6803 | -32.6803 | -23.9098 | -32.6803 | -36.9255
48772 | PHR_GN2_2 | 1 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48811 | CVC_GT3_5045 | MB | HOUSTON | 156 | -31.1604 | -33.6069 | 2.7214 | 33.6069 | -2.7214 | -23.4663 | -23.4663 | -31.6146 | -29.5999 | -32.3893 | -37.8919 | -37.8919 | -32.3893 | -37.8919 | -39.0948
48812 | CVC_GT2_5020 | 3 | HOUSTON | 158 | -31.5599 | -34.0378 | 2.7563 | 34.0378 | -2.7563 | -23.7672 | -23.7672 | -32.02 | -29.9794 | -32.8046 | -38.3777 | -38.3777 | -32.8046 | -38.3777 | -39.5961
48813 | CVC_GT1_5035 | 2 | HOUSTON | 160 | -31.9594 | -34.4686 | 2.7912 | 34.4686 | -2.7912 | -24.068 | -24.068 | -32.4253 | -30.3589 | -33.2198 | -38.8635 | -38.8635 | -33.2198 | -38.8635 | -40.0973
48815 | CVC_GT4_8005 | 1 | HOUSTON | 165 | -34.9506 | -37.8447 | 3.0056 | 37.8447 | -3.0056 | -24.0359 | -24.0359 | -32.401 | -30.4422 | -25.8603 | -35.5971 | -35.5971 | -25.8603 | -35.5971 | -40.3671
48841 | SJS_GT1_GT1 | 4 | HOUSTON | 78 | -16.8408 | -18.7298 | 1.468 | 18.7298 | -1.468 | -11.0755 | -11.0755 | -14.9372 | -14.0742 | -11.6151 | -16.0629 | -16.0629 | -11.6151 | -16.0629 | -18.2586
48842 | SJS_GT2_GT2 | 1 | HOUSTON | 81 | -17.4885 | -19.4502 | 1.5245 | 19.4502 | -1.5245 | -11.5014 | -11.5014 | -15.5117 | -14.6155 | -12.0618 | -16.6807 | -16.6807 | -12.0618 | -16.6807 | -18.9608
48851 | SRB_GN1_1 | 2 | HOUSTON | 165 | -35.6136 | -39.2919 | 3.087 | 39.2919 | -3.087 | -23.5412 | -23.5412 | -31.7468 | -29.8964 | -25.0571 | -34.3098 | -34.3098 | -25.0571 | -34.3098 | -38.8021
48852 | SRB_GN2_2 | 1 | HOUSTON | 176 | -37.9912 | -41.9202 | 3.2931 | 41.9202 | -3.2931 | -25.1076 | -25.1076 | -33.8592 | -31.8861 | -26.714 | -36.5869 | -36.5869 | -26.714 | -36.5869 | -41.3824
48853 | SRB_GN3_3 | 2 | HOUSTON | 213 | -45.9569 | -50.6816 | 3.9827 | 50.6816 | -3.9827 | -30.4034 | -30.4034 | -41.0006 | -38.6086 | -32.3964 | -44.3345 | -44.3345 | -32.3964 | -44.3345 | -50.1249
48854 | SRB_GN4_4 | 3 | HOUSTON | 228 | -49.1965 | -54.2505 | 4.2631 | 54.2505 | -4.2631 | -32.5447 | -32.5447 | -43.8882 | -41.3277 | -34.7059 | -47.4639 | -47.4639 | -34.7059 | -47.4639 | -53.645
48855 | SRB_GT211035 | 4 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48855 | SRB_GT211035 | B1 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48873 | THW_ST3_ST_3 | B2 | HOUSTON | 107 | -27.6242 | -25.0524 | 1.976 | 25.0524 | -1.976 | -15.4136 | -15.4136 | -20.7823 | -19.5501 | -11.5887 | -19.4514 | -19.4514 | -11.5887 | -19.4514 | -24.0839
48874 | THW_ST4_ST_4 | 3 | HOUSTON | 108 | -27.8824 | -25.2866 | 1.9944 | 25.2866 | -1.9944 | -15.5576 | -15.5576 | -20.9765 | -19.7328 | -11.697 | -19.6332 | -19.6332 | -11.697 | -19.6332 | -24.309
48875 | THW_3132 | 4 | HOUSTON | 55 | -14.1994 | -12.8774 | 1.0157 | 12.8774 | -1.0157 | -7.9229 | -7.9229 | -10.6825 | -10.0491 | -5.9568 | -9.9984 | -9.9984 | -5.9568 | -9.9984 | -12.3796
48875 | THW_3132 | A | HOUSTON | 53 | -13.683 | -12.4092 | 0.97875 | 12.4092 | -0.97875 | -7.6348 | -7.6348 | -10.294 | -9.6837 | -5.7402 | -9.6348 | -9.6348 | -5.7402 | -9.6348 | -11.9294
48877 | THW_3334 | B | HOUSTON | 55 | -14.1994 | -12.8774 | 1.0157 | 12.8774 | -1.0157 | -7.9229 | -7.9229 | -10.6825 | -10.0491 | -5.9568 | -9.9984 | -9.9984 | -5.9568 | -9.9984 | -12.3796
48877 | THW_3334 | C | HOUSTON | 57 | -14.7157 | -13.3457 | 1.0526 | 13.3457 | -1.0526 | -8.211 | -8.211 | -11.0709 | -10.4145 | -6.1734 | -10.362 | -10.362 | -6.1734 | -10.362 | -12.8297
48879 | THW_4142 | D | HOUSTON | 56 | -14.4575 | -13.1116 | 1.0342 | 13.1116 | -1.0342 | -8.0669 | -8.0669 | -10.8767 | -10.2318 | -6.0651 | -10.1802 | -10.1802 | -6.0651 | -10.1802 | -12.6046
48879 | THW_4142 | E | HOUSTON | 55 | -14.1994 | -12.8774 | 1.0157 | 12.8774 | -1.0157 | -7.9229 | -7.9229 | -10.6825 | -10.0491 | -5.9568 | -9.9984 | -9.9984 | -5.9568 | -9.9984 | -12.3796
48881 | THW_4344 | F | HOUSTON | 58 | -14.9739 | -13.5798 | 1.0711 | 13.5798 | -1.0711 | -8.355 | -8.355 | -11.2652 | -10.5972 | -6.2817 | -10.5438 | -10.5438 | -6.2817 | -10.5438 | -13.0548
48881 | THW_4344 | G | HOUSTON | 58 | -14.9739 | -13.5798 | 1.0711 | 13.5798 | -1.0711 | -8.355 | -8.355 | -11.2652 | -10.5972 | -6.2817 | -10.5438 | -10.5438 | -6.2817 | -10.5438 | -13.0548
48883 | THW_GT1_GT_1 | H | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48885 | THW_5152 | B2 | HOUSTON | 46.4 | -13.2348 | -10.4319 | 0.83339 | 10.4319 | -0.83339 | -6.8311 | -6.8311 | -9.2067 | -8.6401 | -5.7542 | -8.4262 | -8.4262 | -5.7542 | -8.4262 | -9.848
48885 | THW_5152 | A | HOUSTON | 47.2 | -13.463 | -10.6118 | 0.84776 | 10.6118 | -0.84776 | -6.9489 | -6.9489 | -9.3655 | -8.7891 | -5.8534 | -8.5715 | -8.5715 | -5.8534 | -8.5715 | -10.0178
48886 | THW_5354 | B | HOUSTON | 45.6 | -13.0066 | -10.2521 | 0.81902 | 10.2521 | -0.81902 | -6.7133 | -6.7133 | -9.048 | -8.4911 | -5.6549 | -8.2809 | -8.2809 | -5.6549 | -8.2809 | -9.6782
48886 | THW_5354 | C | HOUSTON | 46.4 | -13.2348 | -10.4319 | 0.83339 | 10.4319 | -0.83339 | -6.8311 | -6.8311 | -9.2067 | -8.6401 | -5.7542 | -8.4262 | -8.4262 | -5.7542 | -8.4262 | -9.848
48887 | THW_5556 | D | HOUSTON | 47.2 | -13.463 | -10.6118 | 0.84776 | 10.6118 | -0.84776 | -6.9489 | -6.9489 | -9.3655 | -8.7891 | -5.8534 | -8.5715 | -8.5715 | -5.8534 | -8.5715 | -10.0178
48887 | THW_5556 | E | HOUSTON | 45.6 | -13.0066 | -10.2521 | 0.81902 | 10.2521 | -0.81902 | -6.7133 | -6.7133 | -9.048 | -8.4911 | -5.6549 | -8.2809 | -8.2809 | -5.6549 | -8.2809 | -9.6782
48911 | TGF_GT1_8000 | F | HOUSTON | 69.2 | -13.7256 | -21.3032 | 1.5845 | 21.3032 | -1.5845 | -8.2111 | -8.2111 | -11.1152 | -10.7027 | -6.5556 | -10.9618 | -10.9618 | -6.5556 | -10.9618 | -13.5528
48921 | WAP_GN1_1 | 1 | HOUSTON | 166 | -37.1777 | -43.9608 | 3.3449 | 43.9608 | -3.3449 | -22.1758 | -22.1758 | -29.9442 | -28.4137 | -18.5512 | -29.6046 | -29.6046 | -18.5512 | -29.6046 | -35.9272
48922 | WAP_GN2_2 | 1 | HOUSTON | 166 | -37.1777 | -43.9608 | 3.3449 | 43.9608 | -3.3449 | -22.1758 | -22.1758 | -29.9442 | -28.4137 | -18.5512 | -29.6046 | -29.6046 | -18.5512 | -29.6046 | -35.9272
48923 | WAP_GN3_3 | 2 | HOUSTON | 248 | -55.5426 | -65.6764 | 4.9972 | 65.6764 | -4.9972 | -33.1301 | -33.1301 | -44.736 | -42.4494 | -27.715 | -44.2286 | -44.2286 | -27.715 | -44.2286 | -53.6744
48924 | WAP_GN4_4 | 3 | HOUSTON | 546 | -122.2833 | -144.5939 | 11.0019 | 144.5939 | -11.0019 | -72.9396 | -72.9396 | -98.4913 | -93.4572 | -61.0177 | -97.3742 | -97.3742 | -61.0177 | -97.3742 | -118.1702
48929 | WAPGT21_GT1 | 4 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48940 | WARVUE_GT1 | B1 | HOUSTON | 12 | -2.5776 | -2.7567 | 0.21888 | 2.7567 | -0.21888 | -1.7465 | -1.7465 | -2.3544 | -2.2123 | -1.9371 | -2.5898 | -2.5898 | -1.9371 | -2.5898 | -2.8924
58909 | PEARSALLSCG1 | G1 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58909 | PEARSALLSCG1 | 1 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58909 | PEARSALLSCG1 | 2 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58909 | PEARSALLSCG1 | 3 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58909 | PEARSALLSCG1 | 4 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58909 | PEARSALLSCG1 | 5 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58919 | PEARSALLSCG2 | 6 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58919 | PEARSALLSCG2 | 1 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58919 | PEARSALLSCG2 | 2 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58919 | PEARSALLSCG2 | 3 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58919 | PEARSALLSCG2 | 4 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58919 | PEARSALLSCG2 | 5 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58929 | PEARSALLSCG3 | 6 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58929 | PEARSALLSCG3 | 1 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58929 | PEARSALLSCG3 | 2 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58929 | PEARSALLSCG3 | 3 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58929 | PEARSALLSCG3 | 4 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58929 | PEARSALLSCG3 | 5 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58949 | PEARSALLSCG4 | 6 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58949 | PEARSALLSCG4 | 1 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58949 | PEARSALLSCG4 | 2 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58949 | PEARSALLSCG4 | 3 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58949 | PEARSALLSCG4 | 4 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58949 | PEARSALLSCG4 | 5 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60000 | DSKY2 | 6 | WEST | 19.1 | -0.39333 | -1.1269 | 6.6754 | 1.1269 | -6.6754 | -0.23497 | -0.23497 | -0.29488 | -0.33089 | -0.18204 | -0.31238 | -0.31238 | -0.18204 | -0.31238 | -0.39002
60003 | KING_NE1A | 1 | WEST | 20 | -0.36778 | -1.0488 | 7.1668 | 1.0488 | -7.1668 | -0.22034 | -0.22034 | -0.2734 | -0.31072 | -0.17 | -0.29212 | -0.29212 | -0.17 | -0.29212 | -0.3649
60005 | KING_SE1A | 1 | WEST | 10 | -0.18389 | -0.5244 | 3.5834 | 0.5244 | -3.5834 | -0.11017 | -0.11017 | -0.1367 | -0.15536 | -0.085 | -0.14606 | -0.14606 | -0.085 | -0.14606 | -0.18245
60007 | KING_SW1A | 1 | WEST | 20 | -0.36148 | -1.0304 | 7.1896 | 1.0304 | -7.1896 | -0.21666 | -0.21666 | -0.26832 | -0.30562 | -0.16706 | -0.28712 | -0.28712 | -0.16706 | -0.28712 | -0.35868
60016 | WOODWRD11A | 1 | WEST | 20 | -0.36896 | -1.0522 | 7.163 | 1.0522 | -7.163 | -0.22104 | -0.22104 | -0.27434 | -0.31166 | -0.17056 | -0.29306 | -0.29306 | -0.17056 | -0.29306 | -0.36606
60017 | ORNNWP1 | 1 | WEST | 20 | -0.40358 | -1.154 | 7.0336 | 1.154 | -7.0336 | -0.24122 | -0.24122 | -0.30218 | -0.33972 | -0.18678 | -0.32054 | -0.32054 | -0.18678 | -0.32054 | -0.40022
60018 | DSKY1 | 1 | WEST | 21 | -0.43562 | -1.2465 | 7.3411 | 1.2465 | -7.3411 | -0.26019 | -0.26019 | -0.32682 | -0.3663 | -0.20166 | -0.34597 | -0.34597 | -0.20166 | -0.34597 | -0.43193
60019 | KING_NW1A | 1 | WEST | 20 | -0.36148 | -1.0304 | 7.1896 | 1.0304 | -7.1896 | -0.21666 | -0.21666 | -0.26832 | -0.30562 | -0.16706 | -0.28712 | -0.28712 | -0.16706 | -0.28712 | -0.35868
60057 | CALLAHAN1A | 1 | WEST | 22.8 | -0.29868 | -0.88699 | 7.6925 | 0.88699 | -7.6925 | -0.18071 | -0.18071 | -0.2124 | -0.25962 | -0.13669 | -0.23728 | -0.23728 | -0.13669 | -0.23728 | -0.29752
60058 | BUFF_GAP1A | 1 | WEST | 24 | -0.27943 | -0.78622 | 10.3693 | 0.78622 | -10.3693 | -0.17004 | -0.17004 | -0.19742 | -0.24209 | -0.12806 | -0.22198 | -0.22198 | -0.12806 | -0.22198 | -0.27818
60060 | CIRELLO | 1 | WEST | 46.6 | -0.54256 | -1.5266 | 20.1337 | 1.5266 | -20.1337 | -0.33016 | -0.33016 | -0.38333 | -0.47005 | -0.24866 | -0.431 | -0.431 | -0.24866 | -0.431 | -0.54014
60063 | BUFF_GAP1B | 1 | WEST | 34 | -0.39586 | -1.1138 | 14.6898 | 1.1138 | -14.6898 | -0.24089 | -0.24089 | -0.27968 | -0.34296 | -0.18142 | -0.31447 | -0.31447 | -0.18142 | -0.31447 | -0.39409
60066 | H_HOLLOW1A | 1 | WEST | 44.4 | -0.51695 | -1.4545 | 19.1832 | 1.4545 | -19.1832 | -0.31457 | -0.31457 | -0.36523 | -0.44786 | -0.23692 | -0.41066 | -0.41066 | -0.23692 | -0.41066 | -0.51464
60068 | HHOLLOW21A | 1 | WEST | 36.8 | -0.42846 | -1.2055 | 15.8996 | 1.2055 | -15.8996 | -0.26073 | -0.26073 | -0.30272 | -0.3712 | -0.19636 | -0.34036 | -0.34036 | -0.19636 | -0.34036 | -0.42655
60070 | HHOLLOW31A | 1 | WEST | 44.8 | -0.52161 | -1.4676 | 19.356 | 1.4676 | -19.356 | -0.31741 | -0.31741 | -0.36852 | -0.4519 | -0.23905 | -0.41436 | -0.41436 | -0.23905 | -0.41436 | -0.51928
60072 | HHOLLOW41A | 1 | WEST | 23 | -0.26779 | -0.75346 | 9.9372 | 0.75346 | -9.9372 | -0.16295 | -0.16295 | -0.1892 | -0.232 | -0.12273 | -0.21273 | -0.21273 | -0.12273 | -0.21273 | -0.26659
60081 | WHRLWIND1A | 1 | WEST | 12 | -0.12347 | -0.33685 | 3.2962 | 0.33685 | -3.2962 | -0.07548 | -0.07548 | -0.085848 | -0.10769 | -0.056544 | -0.098088 | -0.098088 | -0.056544 | -0.098088 | -0.12295
60201 | RIO DRCS | 1 | WEST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRNDDRCS | F | WEST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71051 | L_BITTCR1_1N | F | WEST | 7.5 | -0.08169 | -0.22503 | 3.259 | 0.22503 | -3.259 | -0.049845 | -0.049845 | -0.05742 | -0.0708 | -0.037455 | -0.064897 | -0.064897 | -0.037455 | -0.064897 | -0.081315
71054 | L_SWEETW1_1N | W1 | WEST | 21.5 | -0.23418 | -0.64509 | 9.3425 | 0.64509 | -9.3425 | -0.14289 | -0.14289 | -0.1646 | -0.20296 | -0.10737 | -0.18604 | -0.18604 | -0.10737 | -0.18604 | -0.2331
71057 | L_SWEETW1_2N | W1 | WEST | 27 | -0.29408 | -0.81011 | 11.7324 | 0.81011 | -11.7324 | -0.17944 | -0.17944 | -0.20671 | -0.25488 | -0.13484 | -0.23363 | -0.23363 | -0.13484 | -0.23363 | -0.29273
71059 | L_SWEETW1_3N | W1 | WEST | 23.8 | -0.25923 | -0.7141 | 10.3419 | 0.7141 | -10.3419 | -0.15817 | -0.15817 | -0.18221 | -0.22467 | -0.11886 | -0.20594 | -0.20594 | -0.11886 | -0.20594 | -0.25804
71060 | L_SWEETW1_4N | W1 | WEST | 21 | -0.22873 | -0.63008 | 9.1252 | 0.63008 | -9.1252 | -0.13957 | -0.13957 | -0.16078 | -0.19824 | -0.10487 | -0.18171 | -0.18171 | -0.10487 | -0.18171 | -0.22768
71061 | L_SWEETW1_5N | W1 | WEST | 16.1 | -0.17536 | -0.48306 | 6.996 | 0.48306 | -6.996 | -0.107 | -0.107 | -0.12326 | -0.15198 | -0.080403 | -0.13931 | -0.13931 | -0.080403 | -0.13931 | -0.17456
76031 | L_GOATMO1_1N | W1 | WEST | 30 | -0.38316 | -1.0922 | 11.1044 | 1.0922 | -11.1044 | -0.23232 | -0.23232 | -0.27369 | -0.33054 | -0.1758 | -0.30438 | -0.30438 | -0.1758 | -0.30438 | -0.3813
76091 | L_DIVIDE1_1N | W1 | WEST | 22.5 | -0.29286 | -0.83849 | 8.2484 | 0.83849 | -8.2484 | -0.17744 | -0.17744 | -0.20954 | -0.25254 | -0.13437 | -0.23265 | -0.23265 | -0.13437 | -0.23265 | -0.29144
76095 | L_CAPRSI1_1N | W1 | WEST | 29.9 | -0.38918 | -1.1143 | 10.9612 | 1.1143 | -10.9612 | -0.23579 | -0.23579 | -0.27846 | -0.3356 | -0.17856 | -0.30917 | -0.30917 | -0.17856 | -0.30917 | -0.38729
76096 | L_CAPRSI1_2N | W1 | WEST | 37.2 | -0.4842 | -1.3863 | 13.6373 | 1.3863 | -13.6373 | -0.29336 | -0.29336 | -0.34644 | -0.41753 | -0.22216 | -0.38465 | -0.38465 | -0.22216 | -0.38465 | -0.48185
76097 | L_CAPRGE1_1N | W1 | WEST | 42.9 | -0.55839 | -1.5987 | 15.7269 | 1.5987 | -15.7269 | -0.33831 | -0.33831 | -0.39953 | -0.48151 | -0.2562 | -0.44359 | -0.44359 | -0.2562 | -0.44359 | -0.55568
78189 | L_CUERHY9_1Y | W1 | SOUTH | 12 | -1.7102 | -4.8852 | 0.35366 | 4.8852 | -0.35366 | -1.005 | -1.005 | -1.3724 | -1.3922 | -0.78226 | -1.3593 | -1.3593 | -0.78226 | -1.3593 | -1.7051
80003 | MILHWYS | F | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80080 | GWINDT11A | 1 | SOUTH | 28.2 | -4.4532 | -10.5916 | 0.87338 | 10.5916 | -0.87338 | -2.6171 | -2.6171 | -3.5629 | -3.5488 | -2.1268 | -3.5341 | -3.5341 | -2.1268 | -3.5341 | -4.3588
80080 | GWINDT11A | 2 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80080 | GWINDT11A | 3 | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80080 | GWINDT11A | 4 | SOUTH | 3.8 | -0.60007 | -1.4272 | 0.11769 | 1.4272 | -0.11769 | -0.35266 | -0.35266 | -0.48011 | -0.47821 | -0.28659 | -0.47622 | -0.47622 | -0.28659 | -0.47622 | -0.58735
80081 | GWINDT21A | 1 | SOUTH | 28.2 | -4.4532 | -10.5916 | 0.87338 | 10.5916 | -0.87338 | -2.6171 | -2.6171 | -3.5629 | -3.5488 | -2.1268 | -3.5341 | -3.5341 | -2.1268 | -3.5341 | -4.3588
80081 | GWINDT21A | 2 | SOUTH | 7.2 | -1.137 | -2.7042 | 0.22299 | 2.7042 | -0.22299 | -0.6682 | -0.6682 | -0.90968 | -0.90608 | -0.54302 | -0.90231 | -0.90231 | -0.54302 | -0.90231 | -1.1129
80081 | GWINDT21A | 3 | SOUTH | 8.6 | -1.3581 | -3.2301 | 0.26635 | 3.2301 | -0.26635 | -0.79813 | -0.79813 | -1.0866 | -1.0823 | -0.6486 | -1.0778 | -1.0778 | -0.6486 | -1.0778 | -1.3293
80081 | GWINDT21A | 4 | SOUTH | 4.4 | -0.69482 | -1.6526 | 0.13627 | 1.6526 | -0.13627 | -0.40835 | -0.40835 | -0.55591 | -0.55372 | -0.33184 | -0.55141 | -0.55141 | -0.33184 | -0.55141 | -0.68009
80180 | PNSCALT11A | 1 | SOUTH | 43.8 | -6.9166 | -16.4508 | 1.3565 | 16.4508 | -1.3565 | -4.0649 | -4.0649 | -5.5339 | -5.512 | -3.3034 | -5.4891 | -5.4891 | -3.3034 | -5.4891 | -6.77
80180 | PNSCALT11A | 2 | SOUTH | 10 | -1.5791 | -3.7559 | 0.30971 | 3.7559 | -0.30971 | -0.92806 | -0.92806 | -1.2634 | -1.2585 | -0.75419 | -1.2532 | -1.2532 | -0.75419 | -1.2532 | -1.5457
80181 | PNSCALT21A | 1 | SOUTH | 16.5 | -2.6056 | -6.1972 | 0.51102 | 6.1972 | -0.51102 | -1.5313 | -1.5313 | -2.0847 | -2.0764 | -1.2444 | -2.0678 | -2.0678 | -1.2444 | -2.0678 | -2.5503
80181 | PNSCALT21A | 2 | SOUTH | 10 | -1.5791 | -3.7559 | 0.30971 | 3.7559 | -0.30971 | -0.92806 | -0.92806 | -1.2634 | -1.2585 | -0.75419 | -1.2532 | -1.2532 | -0.75419 | -1.2532 | -1.5457
80263 | B_DAVIS31A | 3 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80264 | B_DAVIS41A | 4 | HOUSTON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80265 | LARECU40A | 4 | SOUTH | 100 | -14.5816 | -37.0439 | 4.5866 | 37.0439 | -4.5866 | -8.5589 | -8.5589 | -11.658 | -11.6943 | -6.916 | -11.5741 | -11.5741 | -6.916 | -11.5741 | -14.3144
80266 | LARECU50A | 5 | SOUTH | 100 | -14.5816 | -37.0439 | 4.5866 | 37.0439 | -4.5866 | -8.5589 | -8.5589 | -11.658 | -11.6943 | -6.916 | -11.5741 | -11.5741 | -6.916 | -11.5741 | -14.3144
88198 | BEEVILLE | F | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
x | x | x | x | x | x | x | x | x | x | [10 empty] | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | bar: 1 to 10
[5 empty] | CSC 1 | CSC 2 | CSC 3 | CSC 4 | CSC 5 | CRE 1 | CRE 2 | CRE 3 | CRE 4 | CRE 5 | CRE 6 | CRE 7 | CRE 8 | CRE 9 | CRE 10 | CRE 11 | CRE 12 | CRE 13 | CRE 14 | CRE 15 | CRE 16 | CRE 17 | CRE 18 | CRE 19 | CRE 20 | CRE 21 | CRE 22 | CRE 23 | CRE 24 | CRE 25
|  |  |  | North | 9.7874 | -112.7254 | -15.9554 | 112.7254 | 15.9554 | -146.453 | -146.453 | -243.3831 | -233.1196 | -3.7307 | 65.5506 | 65.5506 | -3.7307 | -785.6494 | 6.4518 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| GSF sums |  |  | South | -1759.2733 | -5311.3475 | 400.0372 | 5311.3475 | -400.0372 | -1028.5784 | -1028.5784 | -1406.128 | -1436.1136 | -816.3287 | -1397.2527 | -1397.2527 | -816.3287 | -1397.2527 | -1742.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | West | -56.9235 | -159.5698 | 1704.0277 | 159.5698 | -1704.0277 | -34.5131 | -34.5131 | -40.7606 | -48.9648 | -26.1591 | -45.2178 | -45.2178 | -26.1591 | -45.2178 | -56.6099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Houston | -2393.9809 | -2682.9967 | 208.8357 | 2682.9967 | -208.8357 | -1524.3306 | -1524.3306 | -2056.422 | -1940.8516 | -1538.1914 | -2166.5652 | -2166.5652 | -1538.1914 | -2166.5652 | -2485.3871 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Avg weighted GSF |  |  |  | North | 0.0005076 | -0.0058462 | -0.00082749 | 0.0058462 | 0.00082749 | -0.0075954 | -0.0075954 | -0.012622 | -0.01209 | -0.00019348 | 0.0033996 | 0.0033996 | -0.00019348 | -0.040746 | 0.00033461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weighted by Generation only |  |  |  | South | -0.13729 | -0.41449 | 0.031218 | 0.41449 | -0.031218 | -0.080269 | -0.080269 | -0.10973 | -0.11207 | -0.063705 | -0.10904 | -0.10904 | -0.063705 | -0.10904 | -0.13601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | West | -0.012691 | -0.035575 | 0.37991 | 0.035575 | -0.37991 | -0.0076945 | -0.0076945 | -0.0090874 | -0.010916 | -0.0058321 | -0.010081 | -0.010081 | -0.0058321 | -0.010081 | -0.012621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Houston | -0.21972 | -0.24624 | 0.019167 | 0.24624 | -0.019167 | -0.1399 | -0.1399 | -0.18874 | -0.17813 | -0.14117 | -0.19884 | -0.19884 | -0.14117 | -0.19884 | -0.22811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
North gen | 19281.7 |  |  | CSC 1 | CSC 1: N to H; CSC 5: CSC # --->; CRE 1: 1; CRE 2: 1; CRE 3: 1; CRE 4: 1; CRE 5: 1; CRE 6: 1; CRE 7: 1; CRE 8: 1; CRE 9: 1; CRE 10: 1
South gen | 12814.2 |  |  | CSC 2 | N to S |  |  |  |  | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value | A value
West gen | 4485.4 |  |  | CSC 3 | W to N |  |  |  |  | 2.3546 | 2.3546 | 1.7357 | 1.8149 | 3.0961 | 2.2014 | 2.2014 | 3.0961 | 2.0972 | 1.9149 | 1.6998 | 1.6998 | 1.6998 | 1.6998 | 1.6998 | 1.6998 | 1.6998 | 1.6998 | 1.6998 | 1.6998 | 1.6998 | 1.6998 | 1.6998 | 1.6998 | 1.6998
Houston gen | 10895.8 |  |  | CSC 4 | CSC 1: S to N
Total gen | 47477.1 |  |  | CSC 5 | N to W |  |  |  |  | CRE 1 | CRE 2 | CRE 3 | CRE 4 | CRE 5 | CRE 6 | CRE 7 | CRE 8 | CRE 9 | CRE 10 | CRE 11 | CRE 12 | CRE 13 | CRE 14 | CRE 15 | CRE 16 | CRE 17 | CRE 18 | CRE 19 | CRE 20 | CRE 21 | CRE 22 | CRE 23 | CRE 24 | CRE 25
[10 empty] | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2 | Diff ^2
check | 47477.1 | [8 empty] | 0.00033826 | 0.00033826 | 0.00050252 | 0.000504 | 1.2247e-06 | 4.8671e-05 | 4.8671e-05 | 1.2247e-06 | 0.0073888 | 1.773e-08 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[10 empty] | 0.002674 | 0.002674 | 0.0028276 | 0.00437 | 0.0035939 | 0.010558 | 0.010558 | 0.0035939 | 0.0083507 | 0.015169 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[10 empty] | 2.9451e-05 | 2.9451e-05 | 9.5016e-06 | 5.0712e-05 | 2.8795e-05 | 9.0289e-05 | 9.0289e-05 | 2.8795e-05 | 7.1417e-05 | 0.00013173 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[10 empty] | 0.012033 | 0.012033 | 0.011638 | 0.010726 | 0.047252 | 0.047535 | 0.047535 | 0.047252 | 0.038924 | 0.047129 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[10 empty] | Sum diff ^2 | Sum diff ^3 | Sum diff ^4 | Sum diff ^5 | Sum diff ^6 | Sum diff ^7 | Sum diff ^8 | Sum diff ^9 | Sum diff ^10 | Sum diff ^11 | Sum diff ^12 | Sum diff ^13 | Sum diff ^14 | Sum diff ^15 | Sum diff ^16 | Sum diff ^17 | Sum diff ^18 | Sum diff ^19 | Sum diff ^20 | Sum diff ^21 | Sum diff ^22 | Sum diff ^23 | Sum diff ^24 | Sum diff ^25 | Sum diff ^26
[10 empty] | 0.015075 | 0.015075 | 0.014977 | 0.015651 | 0.050876 | 0.058232 | 0.058232 | 0.050876 | 0.054735 | 0.06243 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[10 empty] | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint | Constraint
[10 empty] | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
[10 empty] | CSC1:CRE 1 | CSC1:CRE 2 | CSC1:CRE 3 | CSC1:CRE 4 | CSC1:CRE 5 | CSC1:CRE 6 | CSC1:CRE 7 | CSC1:CRE 8 | CSC1:CRE 9 | CSC1:CRE 10 | CSC:CRE 11 | CSC:CRE 12 | CSC:CRE 13 | CSC:CRE 14 | CSC:CRE 15 | CSC:CRE 16 | CSC:CRE 17 | CSC:CRE 18 | CSC:CRE 19 | CSC:CRE 20 | CSC:CRE 21 | CSC:CRE 22 | CSC:CRE 23 | CSC:CRE 24 | CSC:CRE 25
[10 empty] | 0.018392 | 0.018392 | 0.022417 | 0.02245 | 0.0011066 | -0.0069764 | -0.0069764 | 0.0011066 | 0.085958 | -0.00013315 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[8 empty] | Bi values |  | 0.051711 | 0.051711 | 0.053175 | 0.066106 | 0.059949 | 0.10275 | 0.10275 | 0.059949 | 0.091382 | 0.12316 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[10 empty] | 0.0054269 | 0.0054269 | 0.0030825 | 0.0071213 | 0.0053661 | 0.009502 | 0.009502 | 0.0053661 | 0.0084509 | 0.011478 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[10 empty] | 0.1097 | 0.1097 | 0.10788 | 0.10357 | 0.21738 | 0.21803 | 0.21803 | 0.21738 | 0.19729 | 0.21709 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[10 empty] | CRE 1 for CSC1 | CRE 2 for CSC1 | CRE 3 for CSC1 | CRE 4 for CSC1 | CRE 5 for CSC1 | CRE 6 for CSC1 | CRE 7 for CSC1 | CRE 8 for CSC1 | CRE 9 for CSC1 | CRE 10 for CSC1 | CRE for CSC | CRE for CSC | CRE for CSC | CRE for CSC | CRE for CSC | CRE for CSC | CRE for CSC | CRE for CSC | CRE for CSC | CRE for CSC | CRE for CSC | CRE for CSC | CRE for CSC | CRE for CSC | CRE for CSC
[20 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[9 empty] | Test | [10 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[9 empty] | for | [10 empty] | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[9 empty] | Goodness |  |  |  |  | problem | problem | problem | problem |  | problem | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE!
[10 empty] | Passes CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test | Failed CRE Test | Failed CRE Test | Failed CRE Test | Failed CRE Test | Passes CRE Test | Failed CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test | Passes CRE Test
[8 empty] | CRE criteria set point |  | CRE 1: 0.2
Note on K1016: enter CSC to be judged against
Run CRE Test for All CREs

## pw CUT AND PASTE
649 | POWER WORLD CUT AND PASTE AREA (column headings should match the col headings in green) PASTE into B3 | [12 empty] | 160 | [5 empty] | 160 | note: ----> | Bus mapping OK | [8 empty] | 0 | Get final bus mapping from ERCOT after the BOARD
| Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt |  |  |  | note: ------------------------> | All non-movable gens have been found and match |  |  |  |  | note: ----> | The incorrect number of moveable gens have been copied | [9 empty] | approves a final scenario
| Generator Sensitivities | [14 empty] | Movable Gens excluded list is below (R5:U164) | [5 empty] | 463 | <-- should be | 489 | [7 empty] | 2009 Bus Mapping
cnt | Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt |  | PW Unique | is PW gen excluded |  | BUS_NAM | BUS_NUM | UNIT_ID | Unique | Yes |  | cnt | Number of Bus | Name of Bus | ID | Area Name of Gen | Gen MW | P Sensitivity of Bus |  | 09 Zone |  | Number | Name | Scenario 3i CM Zone
1 | 238 | BOSQUESW505 | 1 | BEPC_TSP | YES | -0.023279 | 255 | 0 | 255 | 0 | 1.02 |  | 2381 | n |  | AES1 | 48500 | 1 | 485001 | y |  | 1 | 238 | BOSQUESW | 1 | NORTH | 244.8 | 0.005238 |  | NORTH | 0 | 1 | ROANSPRA | NORTH
2 | 239 | BOSQUESW502 | 1 | BEPC_TSP | YES | -0.023279 | 149 | 0 | 149 | 0 | 1.02 |  | 2391 | n |  | AIRCO G | 80227 | 1 | 802271 | y |  | 2 | 239 | BOSQUESW | 1 | NORTH | 119.8 | 0.005238 |  | NORTH | 0 | 2 | KEITHSW | NORTH
3 | 244 | WHITNYDM01 | 1 | BEPC_TSP | YES | -0.017932 | 15 | 0 | 15 | 0 | 1.035 |  | 2441 | n |  | ALCOA G | 80226 | 1 | 802261 | y |  | 3 | 244 | WHITNYDM | 1 | NORTH | 14.4 | 0.003973 |  | NORTH | 0 | 4 | IOLA | NORTH
4 | 245 | WHITNYDM02 | 2 | BEPC_TSP | YES | -0.017932 | 15 | 0 | 15 | 0 | 1.035 |  | 2452 | n |  | AMCHMCGN | 38690 | 3 | 386903 | y |  | 4 | 245 | WHITNYDM | 2 | NORTH | 14.4 | 0.003973 |  | NORTH | 0 | 9 | BEDIAS | NORTH
5 | 247 | BOSQUESW501 | 2 | BEPC_TSP | YES | -0.023279 | 156 | 0 | 156 | 0 | 1.02 |  | 2472 | n |  | AMO1 | 48510 | 1 | 485101 | y |  | 5 | 247 | BOSQUESW | 2 | NORTH | 119.8 | 0.005238 |  | NORTH | 0 | 13 | KEITH | NORTH
6 | 251 | BOSQUESW803 | 2 | BEPC_TSP | YES | -0.021117 | 150 | 0 | 150 | 0 | 1.032 |  | 2512 | n |  | AMOLCGN1 | 38580 | 1 | 385801 | y |  | 6 | 251 | BOSQUESW | 2 | NORTH | 147.8 | 0.004701 |  | NORTH | 0 | 17 | CARLOSSW | NORTH
7 | 253 | BOSQUESW804 | 2 | BEPC_TSP | YES | -0.021117 | 80 | 0 | 80 | 0 | 1.032 |  | 2532 | n |  | AMOLCGN2 | 38590 | 2 | 385902 | y |  | 7 | 253 | BOSQUESW | 2 | NORTH | 79.7 | 0.004701 |  | NORTH | 0 | 21 | CARLOS | NORTH
8 | 332 | RWMILLER01 | 1 | BEPC_TSP | YES | -0.006814 | 73 | 18.5 | 73 | 0 | 1.04 |  | 3321 | n |  | AMOLCGN3 | 38600 | 5 | 386005 | y |  | 8 | 332 | RWMILLER | 1 | NORTH | 0 | 0.001208 |  | NORTH | 0 | 25 | NORTHZUL | NORTH
9 | 333 | RWMILLER02 | 2 | BEPC_TSP | YES | -0.006814 | 119 | 37 | 119 | 0 | 1.04 |  | 3332 | n |  | BASF1 | 48520 | 1 | 485201 | y |  | 9 | 333 | RWMILLER | 2 | NORTH | 0 | 0.001208 |  | NORTH | 0 | 29 | BOONEVIL | NORTH
10 | 334 | RWMILLER03 | 3 | BEPC_TSP | YES | -0.006814 | 208 | 65 | 208 | 0 | 1.04 |  | 3343 | n |  | BASF1 | 48520 | 2 | 485202 | y |  | 10 | 334 | RWMILLER | 3 | NORTH | 159.7 | 0.001208 |  | NORTH | 0 | 31 | HEARNECI | NORTH
11 | 335 | RWMILLER04 | 4 | BEPC_TSP | YES | -0.006814 | 102 | 0 | 102 | 0 | 1.04 |  | 3354 | n |  | BAT #1 | 8388 | MB | 8388MB | y |  | 11 | 335 | RWMILLER | 4 | NORTH | 0 | 0.001208 |  | NORTH | 0 | 32 | ROBERTSO | NORTH
12 | 336 | RWMILLER05 | 5 | BEPC_TSP | YES | -0.006814 | 101 | 0 | 101 | 0 | 1.04 |  | 3365 | n |  | BAT #2 | 8393 | MB | 8393MB | y |  | 12 | 336 | RWMILLER | 5 | NORTH | 79.9 | 0.001208 |  | NORTH | 0 | 33 | WATSONCH | NORTH
13 | 344 | MRSSHPRD | 1 | BEPC_TSP | YES | -0.005972 | 0 | 0 | 12 |  | 1.03 |  | 3441 | n |  | BBRN 1 G | 3381 | 1 | 33811 | y |  | 13 | 344 | MRSSHPRD | 1 | NORTH | 11.5 | 0.000865 |  | NORTH | 0 | 34 | CALVERTM | NORTH
14 | 345 | MRSSHPRD01 | 2 | BEPC_TSP | YES | -0.005972 | 0 | 0 | 12 |  | 1.03 |  | 3452 | n |  | BBRN 2 G | 3382 | 2 | 33822 | y |  | 14 | 345 | MRSSHPRD | 2 | NORTH | 11.5 | 0.000865 |  | NORTH | 0 | 35 | HEARNE8 | NORTH
15 | 366 | JNSNCNTY802 | 1 | BEPC_TSP | YES | -0.005616 | 168 | 20 | 168 | 0 | 1.02 |  | 3661 | n |  | BRYN_TAM | 32798 | 1 | 327981 | y |  | 15 | 366 | JNSNCNTY | 1 | NORTH | 129 | 0.001226 |  | NORTH | 0 | 36 | HEARNE9 | NORTH
16 | 367 | JNSNCNTY802 | 2 | BEPC_TSP | YES | -0.005616 | 90 | 20 | 90 | 0 | 1.02 |  | 3672 | n |  | BSP 1 | 1320 | 1 | 13201 | y |  | 16 | 367 | JNSNCNTY | 2 | NORTH | 69.1 | 0.001226 |  | NORTH | 0 | 37 | RIDGE | NORTH
17 | 503 | NTHTEXAS01 | 1 | BEPC_TSP | YES | -0.005008 | 0 | 5 | 18 |  | 1.015 |  | 5031 | n |  | BTE GT1 | 48595 | 1 | 485951 | y |  | 17 | 503 | NTHTEXAS | 1 | NORTH | 0 | 0.00084 |  | NORTH | 0 | 38 | SUTTON | NORTH
18 | 504 | NTHTEXAS02 | 2 | BEPC_TSP | YES | -0.005008 | 14.4 | 5 | 18 |  | 1.015 |  | 5042 | n |  | BTE GT2 | 48596 | 2 | 485962 | y |  | 18 | 504 | NTHTEXAS | 2 | NORTH | 0 | 0.00084 |  | NORTH | 0 | 40 | JEWETT | NORTH
19 | 505 | NTHTEXAS03 | 3 | BEPC_TSP | YES | -0.005008 | 30.4 | 15 | 38 |  | 1.015 |  | 5053 | n |  | BTE GT3 | 48597 | 3 | 485973 | y |  | 19 | 505 | NTHTEXAS | 3 | NORTH | 0 | 0.00084 |  | NORTH | 0 | 43 | HILTPLKS | NORTH
20 | 580 | JCKCNTY801 | 1 | BEPC_TSP | YES | -0.00372 | 288 | 0 | 288 | 0 | 1.022 |  | 5801 | n |  | BTE ST1 | 48598 | 4 | 485984 | y |  | 20 | 580 | JCKCNTY8 | 1 | NORTH | 288.9 | 0.000561 |  | NORTH | 0 | 45 | OLETHA | NORTH
21 | 581 | JCKCNTY802 | 2 | BEPC_TSP | YES | -0.00372 | 147 | 0 | 147 | 0 | 1.022 |  | 5812 | n |  | CALGT1 | 48551 | 1 | 485511 | y |  | 21 | 581 | JCKCNTY8 | 2 | NORTH | 154.5 | 0.000561 |  | NORTH | 0 | 46 | FARRAR | NORTH
22 | 582 | JCKCNTY803 | 3 | BEPC_TSP | YES | -0.00372 | 147 | 0 | 147 | 0 | 1.022 |  | 5823 | n |  | CALST1 | 48552 | 2 | 485522 | y |  | 22 | 582 | JCKCNTY8 | 3 | NORTH | 154.5 | 0.000561 |  | NORTH | 0 | 47 | HILTOPLK | NORTH
23 | 728 | WOLFRIDGE801 | 1 | BEPC_TSP | YES | -0.002276 | 11.2 | 0 | 112.5 | 0 | 0.99 |  | 7281 | n |  | CAP1 | 48561 | 1 | 485611 | y |  | 23 | 728 | WOLFRIDG | 1 | NORTH | 16.2 | 0.000308 |  | NORTH | 0 | 48 | HILTOPLK | NORTH
24 | 837 | NEWMAN_G5 | 1 | GRLNDTSP | YES | 0.002149 | 0 | 15 | 40 |  | 1.01 |  | 8371 | n |  | CAP2 | 48562 | 2 | 485622 | y |  | 24 | 837 | NEWMAN_G | 1 | NORTH | 0 | -0.000444 |  | NORTH |  | 53 | ELLIOTT | NORTH
25 | 842 | OLINGER_G1 | 1 | GRLNDTSP | YES | 0.002131 | 55.4 | 20 | 79 | 0 | 1.03 |  | 8421 | n |  | CAP3 | 48563 | 3 | 485633 | y |  | 25 | 842 | OLINGER_ | 1 | NORTH | 0 | -0.000442 |  | NORTH |  | 57 | FRANKLIN | NORTH
26 | 843 | OLINGER_G2 | 1 | GRLNDTSP | YES | 0.002131 | 76.2 | 25 | 110 | 0 | 1.03 |  | 8431 | n |  | CAP4 | 48564 | 4 | 485644 | y |  | 26 | 843 | OLINGER_ | 1 | NORTH | 0 | -0.000442 |  | NORTH |  | 61 | BRANCHVI | NORTH
27 | 844 | OLINGER_G3 | 1 | GRLNDTSP | YES | 0.002131 | 103.9 | 45 | 150 | 0 | 1.03 |  | 8441 | n |  | CAP5 | 48565 | 5 | 485655 | y |  | 27 | 844 | OLINGER_ | 1 | NORTH | 87 | -0.000442 |  | NORTH |  | 64 | MILANO | SOUTH
28 | 845 | OLINGER_G4 | 1 | GRLNDTSP | YES | 0.002131 | 51.9 | 0 | 76 | 0 | 1.03 |  | 8451 | n |  | CEC GT1 | 48593 | 1 | 485931 | y |  | 28 | 845 | OLINGER_ | 1 | NORTH | 0 | -0.000442 |  | NORTH |  | 65 | SILVERCI | NORTH
29 | 923 | SPENCER_G4 | 1 | GRLNDTSP | YES | -0.0013 | 48 | 20 | 61 | 0 | 1.03 |  | 9231 | n |  | CEL-B #1 | 8517 | 1 | 85171 | y |  | 29 | 923 | SPENCER_ | 1 | NORTH | 0 | 0.000149 |  | NORTH | 0 | 69 | BARCLAY | SOUTH
30 | 924 | SPENCER_G5 | 1 | GRLNDTSP | YES | -0.0013 | 52 | 20 | 66 | 0 | 1.03 |  | 9241 | n |  | CHAMPN G | 3348 | MB | 3348MB | y |  | 30 | 924 | SPENCER_ | 1 | NORTH | 0 | 0.000149 |  | NORTH | 0 | 73 | CALVERTS | NORTH
31 | 948 | STEAM1 | 1 | GRNVLTSP | YES | 0.002274 | 0 | 12 | 20 |  | 1.02 |  | 9481 | n |  | CIDINDUS | 86104 | EQ | 86104EQ | y |  | 31 | 948 | STEAM1 | 1 | NORTH | 0 | -0.000468 |  | NORTH |  | 75 | PETTIBON | SOUTH
32 | 949 | STEAM2 | 1 | GRNVLTSP | YES | 0.002273 | 26 | 8 | 26 | 0 | 0.99 |  | 9491 | n |  | CIDINDUS | 86105 | EQ | 86105EQ | y |  | 32 | 949 | STEAM2 | 1 | NORTH | 22.1 | -0.000468 |  | NORTH |  | 77 | CALVERT | NORTH
33 | 950 | STEAM3 | 1 | GRNVLTSP | YES | 0.002273 | 41 | 13 | 42 | 0 | 1.02 |  | 9501 | n |  | CLO #1 | 8161 | 1 | 81611 | y |  | 33 | 950 | STEAM3 | 1 | NORTH | 0 | -0.000468 |  | NORTH |  | 81 | PLESNTGR | NORTH
34 | 990 | GIBN_CREK_G1 | 1 | TMPA_TSP | YES | 0.051229 | 463 | 200 | 463 | 0 | 1.0275 |  | 9901 | y |  | CMPK 1 G | 1898 | 1 | 18981 | y |  | 34 | 1002 | PBCTAGE_ | A | WEST | 0 | 0.001407 |  | WEST | 0 | 85 | KOSSESWC | NORTH
35 | 1002 | PBCTAGE_1G | A | ONCOR ED | YES | -0.013225 | 64 | 64 | 66 | 0 | 1.036 |  | 1002A | n |  | CMPK 2 G | 1899 | 2 | 18992 | y |  | 35 | 1003 | PBCTBGE_ | B | WEST | 0 | 0.001407 |  | WEST | 0 | 86 | BEARGRAS | NORTH
36 | 1003 | PBCTBGE_2G | B | ONCOR ED | YES | -0.013225 | 65 | 65 | 66 | 0 | 1.036 |  | 1003B | n |  | COSW#1 | 8456 | 1 | 84561 | y |  | 36 | 1004 | PBCTCGE_ | C | WEST | 0 | 0.001407 |  | WEST | 0 | 89 | KOSSE | NORTH
37 | 1004 | PBCTCGE_3G | C | ONCOR ED | YES | -0.013225 | 62 | 62 | 67 | 0 | 1.036 |  | 1004C | n |  | COSW#2 | 8457 | 2 | 84572 | y |  | 37 | 1005 | PBCTDGE_ | D | WEST | 0 | 0.001407 |  | WEST | 0 | 91 | PERRY8 | NORTH
38 | 1005 | PBCTDGE_4G | D | ONCOR ED | YES | -0.013225 | 65 | 65 | 68 | 0 | 1.036 |  | 1005D | n |  | CSDR11 | 80140 | 11 | 8014011 | y |  | 38 | 1006 | PBCTEGE_ | E | WEST | 0 | 0.001407 |  | WEST | 0 | 92 | PERRY9 | NORTH
39 | 1006 | PBCTEGE_5G | E | ONCOR ED | YES | -0.013225 | 65 | 65 | 67 | 0 | 1.036 |  | 1006E | n |  | CSDR56 | 80139 | 5 | 801395 | y |  | 39 | 1007 | PB5GEN_6 | 5 | WEST | 0 | 0.001407 |  | WEST | 0 | 93 | PETTEWAY | NORTH
40 | 1007 | PB5GEN_6G | 5 | ONCOR ED | YES | -0.013225 | 91.2 | 40 | 114 | 0 | 1.036 |  | 10075 | n |  | CSDR56 | 80139 | 6 | 801396 | y |  | 40 | 1008 | PB6GEN_7 | 6 | WEST | 414.4 | 0.001407 |  | WEST | 0 | 95 | HALLSBUR | NORTH
41 | 1008 | PB6GEN_7G | 6 | ONCOR ED | YES | -0.013225 | 515 | 130 | 515 | 0 | 1.036 |  | 10086 | n |  | CSDR7 | 80138 | 7 | 801387 | y |  | 41 | 1037 | MORGAN5G | 5 | WEST | 0 | 0.00128 |  | WEST | 0 | 99 | BENHUR | NORTH
42 | 1037 | MORGAN5G_5G | 5 | ONCOR ED | YES | -0.011672 | 137 | 40 | 137 | 0 | 1.029 |  | 10375 | n |  | CSDR89 | 80137 | 8 | 801378 | y |  | 42 | 1039 | MRGNAG_1 | A | WEST | 69 | 0.00128 |  | WEST | 0 | 103 | GROESBEC | NORTH
43 | 1039 | MRGNAG_1G | A | ONCOR ED | YES | -0.011672 | 69 | 69 | 69 | 0 | 1.029 |  | 1039A | n |  | CSDR89 | 80137 | 9 | 801379 | y |  | 43 | 1040 | MRGNBG_2 | B | WEST | 70 | 0.00128 |  | WEST | 0 | 104 | BUTLER | NORTH
44 | 1040 | MRGNBG_2G | B | ONCOR ED | YES | -0.011672 | 70 | 70 | 71 | 0 | 1.029 |  | 1040B | n |  | CUF-138 | 86107 | EQ | 86107EQ | y |  | 44 | 1041 | MRGNCG_3 | C | WEST | 69 | 0.00128 |  | WEST | 0 | 107 | PRAIRIEH | NORTH
45 | 1041 | MRGNCG_3G | C | ONCOR ED | YES | -0.011672 | 69 | 69 | 70 | 0 | 1.029 |  | 1041C | n |  | CUF-230 | 86106 | EQ | 86106EQ | y |  | 45 | 1042 | MRGNDG_4 | D | WEST | 69 | 0.00128 |  | WEST | 0 | 110 | BUCKHOLT | NORTH
46 | 1042 | MRGNDG_4G | D | ONCOR ED | YES | -0.011672 | 68 | 68 | 68 | 0 | 1.029 |  | 1042D | n |  | DIB_GT3_ | 48614 | 4 | 486144 | y |  | 46 | 1043 | MRGNEG_5 | E | WEST | 68 | 0.00128 |  | WEST | 0 | 114 | BARTLETT | SOUTH
47 | 1043 | MRGNEG_5G | MB | ONCOR ED | YES | -0.011672 | 0 | 68 | 70 |  | 1.029 |  | 1043MB | n |  | DIB1 | 48611 | 1 | 486111 | y |  | 47 | 1044 | MRGNFG_6 | F | WEST | 66 | 0.00128 |  | WEST | 0 | 115 | DINGDONG | SOUTH
48 | 1044 | MRGNFG_6G | MB | ONCOR ED | YES | -0.011672 | 0 | 66 | 66 |  | 1.029 |  | 1044MB | n |  | DIB2 | 48612 | 2 | 486122 | y |  | 48 | 1045 | CALENG1G | 1 | WEST | 0 | 0.001289 |  | WEST | 0 | 116 | SALTY | SOUTH
49 | 1045 | CALENG1G_1G | 1 | ONCOR ED | YES | -0.011867 | 73.4 | 27 | 73.4 | 0 | 1.014 |  | 10451 | n |  | DIB3 | 48613 | 3 | 486133 | y |  | 49 | 1046 | CALENG2G | 2 | WEST | 0 | 0.001289 |  | WEST | 0 | 117 | CEDARVAL | SOUTH
50 | 1046 | CALENG2G_2G | 2 | ONCOR ED | YES | -0.011867 | 73.4 | 27 | 73.4 | 0 | 1.014 |  | 10462 | n |  | DOW17000 | 49851 | 37 | 4985137 | y |  | 50 | 1047 | CALENG3G | 3 | WEST | 53.6 | 0.001289 |  | WEST | 0 | 118 | BARTLETT | SOUTH
51 | 1047 | CALENG3G_3G | 3 | ONCOR ED | YES | -0.011867 | 70.4 | 27 | 70.4 | 0 | 1.014 |  | 10473 | n |  | DOW38100 | 49858 | 31 | 4985831 | y |  | 51 | 1058 | LONGSHOR | 1 | WEST | 30 | 0.001277 |  | WEST | 0 | 120 | TALBRTRI | SOUTH
52 | 1058 | LONGSHORE_5 | 1 | ONCOR ED | YES | -0.011723 | 30 | 0 | 150 |  | 1.01 |  | 10581 | n |  | DOW38200 | 49859 | 33 | 4985933 | y |  | 52 | 1058 | LONGSHOR | 2 | WEST | 44 | 0.001277 |  | WEST | 0 | 122 | SCHWERTN | SOUTH
53 | 1058 | LONGSHORE_5 | 2 | ONCOR ED | YES | -0.011723 | 44 | 0 | 220 |  | 1.01 |  | 10582 | n |  | DOW38300 | 49860 | 32 | 4986032 | y |  | 53 | 1058 | LONGSHOR | 3 | WEST | 23.4 | 0.001277 |  | WEST | 0 | 123 | JARREL | SOUTH
54 | 1061 | CIELOGEN_1G | 1 | ONCOR ED | YES | -0.011608 | 19.8 | 0 | 99 |  | 1 |  | 10611 | n |  | DOW39100 | 49862 | 36 | 4986236 | y |  | 54 | 1061 | CIELOGEN | 1 | WEST | 19.8 | 0.001283 |  | WEST | 0 | 125 | STLHOSHO | SOUTH
55 | 1062 | CIELOGEN_2G | 1 | ONCOR ED | YES | -0.011608 | 12.2 | 0 | 61 |  | 1 |  | 10621 | n |  | DOW39200 | 49863 | 35 | 4986335 | y |  | 55 | 1062 | CIELOGEN | 1 | WEST | 12.2 | 0.001283 |  | WEST | 0 | 126 | POAGE | SOUTH
56 | 1068 | SCURRYCW_1G | 1 | ONCOR ED | YES | -0.011627 | 28.2 | 1.3 | 141 | 0 | 1.0217 |  | 10681 | n |  | DOW41000 | 49865 | 41 | 4986541 | y |  | 56 | 1068 | SCURRYCW | 1 | WEST | 28.2 | 0.001283 |  | WEST | 0 | 127 | THRNDALN | SOUTH
57 | 1069 | KINDERMG_1G | 1 | ONCOR ED | YES | -0.011608 | 25 | 5 | 25 | 0 | 1.017 |  | 10691 | y |  | DOW42000 | 49866 | 42 | 4986642 | y |  | 57 | 1073 | SCURRYCW | 2 | WEST | 24 | 0.001283 |  | WEST | 0 | 130 | SEATON8 | SOUTH
58 | 1070 | KINDERMG_2G | 1 | ONCOR ED | YES | -0.011608 | 45.7 | 12 | 45.7 | 0 | 1.017 |  | 10701 | y |  | DOW49000 | 49869 | 45 | 4986945 | y |  | 58 | 1326 | STANTONW | 1 | WEST | 20.1 | 0.001347 |  | WEST | 0 | 131 | SEATON9 | SOUTH
59 | 1071 | KINDERMG_3G | 1 | ONCOR ED | YES | -0.011608 | 45.7 | 12 | 45.7 | 0 | 1.017 |  | 10711 | y |  | DOW61000 | 49870 | 61 | 4987061 | y |  | 59 | 1327 | WILDHRSE | 1 | WEST | 0 | 0.001318 |  | WEST | 0 | 132 | BELLCNTY | SOUTH
60 | 1073 | SCURRYCW_2G | 2 | ONCOR ED | YES | -0.011627 | 24 | 0 | 120 | 0 | 1.0217 |  | 10732 | n |  | DOW62000 | 49871 | 62 | 4987162 | y |  | 60 | 1328 | OCOTILLO | 1 | WEST | 11.6 | 0.001349 |  | WEST | 0 | 133 | BELLCNTY | SOUTH
61 | 1320 | BSP 1 | 1 | ONCOR ED | YES | -0.012605 | 25.5 | 2.9 | 25.8 | 0 | 1 |  | 13201 | y |  | DOW63000 | 49872 | 63 | 4987263 | y |  | 61 | 1333 | MCDDONAL | 1 | WEST | 42.8 | 0.001339 |  | WEST | 0 | 136 | TRIMMIER | SOUTH
62 | 1326 | STANTONW_8 | 1 | ONCOR ED | YES | -0.012529 | 20.1 | 0 | 100.5 |  | 1.01 |  | 13261 | n |  | DOW64000 | 49873 | 64 | 4987364 | y |  | 62 | 1343 | TRENTIPP | 1 | WEST | 30 | 0.001345 |  | WEST | 0 | 137 | MOODY | SOUTH
63 | 1327 | WILDHRSE_1G | 1 | ONCOR ED | YES | -0.012171 | 0 | 0 | 120 |  | 1 |  | 13271 | n |  | DOW65000 | 49876 | 65 | 4987665 | y |  | 63 | 1349 | WESTXWIN | 1 | WEST | 1.3 | 0.001415 |  | WEST | 0 | 139 | LAKEBELT | SOUTH
64 | 1328 | OCOTILLO_1G | 1 | ONCOR ED | YES | -0.012451 | 11.6 | 0 | 58 |  | 1.01 |  | 13281 | n |  | DOW66000 | 49877 | 66 | 4987766 | y |  | 64 | 1350 | NWPWRG1_ | 1 | WEST | 6.9 | 0.001415 |  | WEST | 0 | 141 | MOFFAT | SOUTH
65 | 1333 | MCDDONAL_8 | 1 | ONCOR ED | YES | -0.012325 | 42.8 | 0 | 214.2 |  | 1.01 |  | 13331 | n |  | DOW67000 | 49878 | 67 | 4987867 | y |  | 65 | 1354 | AEPWIND_ | 1 | WEST | 20.2 | 0.001345 |  | WEST | 0 | 142 | TUGTSVIL | NORTH
66 | 1343 | TRENTIPP_8 | 1 | ONCOR ED | YES | -0.011742 | 30 | 0 | 150 |  | 1.014 |  | 13431 | n |  | DOW81000 | 49882 | 81 | 4988281 | y |  | 66 | 1360 | GUNSIGHT | 1 | WEST | 24 | 0.001317 |  | WEST | 0 | 145 | LEONJUNC | NORTH
67 | 1349 | WESTXWIN_1G | 1 | ONCOR ED | YES | -0.013476 | 1.3 | 0 | 6.6 |  | 1.014 |  | 13491 | n |  | DOW82000 | 49884 | 82 | 4988482 | y |  | 67 | 1416 | SWETWATR | 1 | WEST | 26.4 | 0.001171 |  | WEST | 0 | 146 | SPRINGVA | NORTH
68 | 1350 | NWPWRG1_1G | 1 | ONCOR ED | YES | -0.013476 | 6.9 | 1 | 34.3 |  | 1.014 |  | 13501 | n |  | DOW83000 | 49885 | 83 | 4988583 | y |  | 68 | 1417 | SWETWATR | 2 | WEST | 60 | 0.001171 |  | WEST | 0 | 147 | LORENA | NORTH
69 | 1354 | AEPWIND_8 | 1 | ONCOR ED | YES | -0.011742 | 20.2 | 0 | 101 |  | 1 |  | 13541 | n |  | DOW84000 | 49886 | 84 | 4988684 | y |  | 69 | 1418 | SWETWATR | 3 | WEST | 57.2 | 0.001171 |  | WEST | 0 | 149 | SANTAFES | NORTH
70 | 1360 | GUNSIGHT_8 | 1 | ONCOR ED | YES | -0.012148 | 0 | 0 | 120 |  | 1.01 |  | 13601 | n |  | DUP1V#1 | 8066 | 1 | 80661 | y |  | 70 | 1419 | SWETWATR | 4 | WEST | 50.4 | 0.001171 |  | WEST | 0 | 153 | SANTAFE | NORTH
71 | 1416 | SWETWATR_1G | MB | ONCOR ED | YES | -0.010509 | 0 | 18 | 30 |  | 1.026 |  | 1416MB | n |  | EP1 | 48651 | 1 | 486511 | y |  | 71 | 1432 | GRHAMSES | 2 | NORTH | 0 | 0.000798 |  | NORTH | 0 | 157 | GATESVIL | NORTH
72 | 1417 | SWETWATR_2G | MB | ONCOR ED | YES | -0.010509 | 0 | 36 | 72 |  | 1.026 |  | 1417MB | n |  | EP1 | 48651 | 2 | 486512 | y |  | 72 | 1433 | GRHAMSES | 1 | NORTH | 0 | 0.000917 |  | NORTH | 0 | 158 | PANCAKE | NORTH
73 | 1418 | SWETWATR_3G | MB | ONCOR ED | YES | -0.010509 | 0 | 36 | 68 |  | 1.026 |  | 1418MB | n |  | EXN 15GT | 49803 | 1 | 498031 | y |  | 73 | 1437 | MESQUITW | 1 | NORTH | 57.6 | 0.001035 |  | NORTH | 0 | 160 | MOSHEIM | NORTH
74 | 1419 | SWETWATR_4G | MB | ONCOR ED | YES | -0.010509 | 0 | 36 | 61 |  | 1.026 |  | 1419MB | n |  | EXN 16GT | 49804 | 2 | 498042 | y |  | 74 | 1438 | MESQUITW | 1 | NORTH | 34 | 0.001034 |  | NORTH | 0 | 161 | MCGREGOR | NORTH
75 | 1432 | GRHAMSES_2G | 2 | ONCOR ED | YES | -0.006329 | 366 | 90 | 366 |  | 1.014 |  | 14322 | n |  | EXN 17GT | 49805 | 3 | 498053 | y |  | 75 | 1442 | COKFIELD | 1 | NORTH | 23.8 | 0.000978 |  | NORTH | 0 | 164 | PATTON | NORTH
76 | 1433 | GRHAMSES_1G | 1 | ONCOR ED | YES | -0.00693 | 242 | 60 | 242 | 0 | 1.038 |  | 14331 | n |  | EXN GT | 49837 | 4 | 498374 | y |  | 76 | 1453 | WCPWRCO_ | 1 | NORTH | 202.5 | 0.000602 |  | NORTH | 0 | 165 | WINDSORS | NORTH
77 | 1437 | MESQUITW_1G | 1 | ONCOR ED | YES | -0.008939 | 40 | 0 | 400 | 0 | 1.023 |  | 14371 | n |  | EXN_14GT | 49838 | 14 | 4983814 | y |  | 77 | 1454 | WCPWRCO_ | 2 | NORTH | 203.5 | 0.000602 |  | NORTH | 0 | 169 | WINDSOR | NORTH
78 | 1438 | MESQUITW_2G | 1 | ONCOR ED | YES | -0.008936 | 23.6 | 0 | 236 |  | 1.017 |  | 14381 | n |  | EXN938GT | 49826 | 5 | 498265 | y |  | 78 | 1455 | WCPWRCO_ | 3 | NORTH | 232.3 | 0.000602 |  | NORTH | 0 | 170 | COTTONBE | NORTH
79 | 1442 | COKFIELD_5 | 1 | ONCOR ED | YES | -0.00831 | 16.5 | 0 | 165 |  | 1.029 |  | 14421 | n |  | EXN941GT | 49828 | 10 | 4982810 | y |  | 79 | 1479 | WFCOGEN_ | 2 | NORTH | 0 | 0.000793 |  | NORTH | 0 | 173 | CRAWFORD | NORTH
80 | 1453 | WCPWRCO_1G | 1 | ONCOR ED | YES | -0.004383 | 204 | 50 | 204 | 0 | 1.02 |  | 14531 | n |  | EXN942GT | 49829 | 11 | 4982911 | y |  | 80 | 1479 | WFCOGEN_ | 1 | NORTH | 0 | 0.000793 |  | NORTH | 0 | 175 | CHINASPR | NORTH
81 | 1454 | WCPWRCO_2G | 2 | ONCOR ED | YES | -0.004383 | 204 | 50 | 204 | 0 | 1.02 |  | 14542 | n |  | EXN943GT | 49830 | 12 | 4983012 | y |  | 81 | 1482 | WFCOGEN_ | 1 | NORTH | 0 | 0.000793 |  | NORTH | 0 | 177 | BOSQUE | NORTH
82 | 1455 | WCPWRCO_3G | 3 | ONCOR ED | YES | -0.004383 | 242 | 50 | 242 | 0 | 1.02 |  | 14553 | n |  | EXN944GT | 49831 | 13 | 4983113 | y |  | 82 | 1482 | WFCOGEN_ | 2 | NORTH | 0 | 0.000793 |  | NORTH | 0 | 181 | CAYOTE | NORTH
83 | 1479 | WFCOGEN_1G | 1 | ONCOR ED | YES | -0.006259 | 16 | 12 | 20 | 0 | 1 |  | 14791 | n |  | EXN945GT | 49832 | 9 | 498329 | y |  | 83 | 1600 | BARTNWND | 1 | NORTH | 17.3 | 0.000906 |  | NORTH | 0 | 185 | MIDWAY | NORTH
84 | 1479 | WFCOGEN_1G | 2 | ONCOR ED | YES | -0.006259 | 16 | 12 | 20 | 0 | 1 |  | 14792 | n |  | FOR #1 | 8134 | 1 | 81341 | y |  | 84 | 1643 | SLSTR1PP | 1 | NORTH | 8.6 | 0.001841 |  | NORTH | 0 | 186 | NAVAROMI | NORTH
85 | 1482 | WFCOGEN_2G | 1 | ONCOR ED | YES | -0.006259 | 16 | 12 | 20 | 0 | 1 |  | 14821 | n |  | FOR #10 | 80053 | 10 | 8005310 | y |  | 85 | 1675 | PEC_1G | 1 | NORTH | 62.2 | -0.000386 |  | NORTH |  | 190 | DAWSON | NORTH
86 | 1482 | WFCOGEN_2G | 2 | ONCOR ED | YES | -0.006259 | 13.6 | 12 | 17 | 0 | 1 |  | 14822 | n |  | FOR #2 | 8138 | 2 | 81382 | y |  | 86 | 1676 | PEC_2G | 2 | NORTH | 64.5 | -0.000386 |  | NORTH |  | 192 | TELICO | NORTH
87 | 1600 | BARTNWND_1G | 1 | ONCOR ED | YES | -0.006115 | 12 | 0 | 120 | 0 | 1.022 |  | 16001 | n |  | FOR #3 | 8153 | 3 | 81533 | y |  | 87 | 1677 | PEC_3G | 3 | NORTH | 74.5 | -0.000386 |  | NORTH |  | 193 | BARRY | NORTH
88 | 1643 | SLSTR1PP_1G | 1 | ONCOR ED | YES | -0.010641 | 6 | 0 | 60 | 0 | 1.022 |  | 16431 | n |  | FOR #4 | 8154 | 4 | 81544 | y |  | 88 | 1678 | LAMARPWR | 1 | NORTH | 165.1 | -0.000374 |  | NORTH |  | 194 | PURDON | NORTH
89 | 1675 | PEC_1G | 1 | ONCOR ED | YES | 0.00182 | 76.7 | 35 | 76.7 | 0 | 1.022 |  | 16751 | n |  | FOR #5 | 8155 | 5 | 81555 | y |  | 89 | 1679 | LAMARPWR | 2 | NORTH | 162.2 | -0.000374 |  | NORTH |  | 195 | FREESTON | NORTH
90 | 1676 | PEC_2G | 2 | ONCOR ED | YES | 0.00182 | 79.6 | 35 | 79.6 | 0 | 1.022 |  | 16762 | n |  | FOR #6 | 8156 | 6 | 81566 | y |  | 90 | 1680 | LAMARPWR | 3 | NORTH | 190 | -0.000374 |  | NORTH |  | 196 | FAIRFIEL | NORTH
91 | 1677 | PEC_3G | 3 | ONCOR ED | YES | 0.00182 | 88.4 | 35 | 88.4 | 0 | 1.022 |  | 16773 | n |  | FOR #7 | 8157 | 7 | 81577 | y |  | 91 | 1681 | LAMARPWR | 4 | NORTH | 164.1 | -0.000374 |  | NORTH |  | 197 | OAKGROVE | NORTH
92 | 1678 | LAMARPWR_1G | 1 | ONCOR ED | YES | 0.001753 | 160 | 67.7 | 160 | 0 | 1.038 |  | 16781 | n |  | FOR #8 | 80051 | 8 | 800518 | y |  | 92 | 1682 | LAMARPWR | 5 | NORTH | 164.1 | -0.000374 |  | NORTH |  | 198 | EMMETT | NORTH
93 | 1679 | LAMARPWR_2G | 2 | ONCOR ED | YES | 0.001753 | 156 | 67.7 | 156 | 0 | 1.038 |  | 16792 | n |  | FOR #9 | 80052 | 9 | 800529 | y |  | 93 | 1683 | LAMARPWR | 6 | NORTH | 190 | -0.000374 |  | NORTH |  | 200 | CHATFIEL | NORTH
94 | 1680 | LAMARPWR_3G | 3 | ONCOR ED | YES | 0.001753 | 196 | 129.1 | 196 | 0 | 1.038 |  | 16803 | n |  | FPP G1 | 7010 | 1 | 70101 | y |  | 94 | 1687 | VALLEY_1 | 1 | NORTH | 0 | -0.000317 |  | NORTH |  | 202 | SARDIS9 | NORTH
95 | 1681 | LAMARPWR_4G | 4 | ONCOR ED | YES | 0.001753 | 156 | 67.7 | 156 | 0 | 1.038 |  | 16814 | n |  | FPP G2 | 7011 | 2 | 70112 | y |  | 95 | 1688 | VALLEY_2 | 2 | NORTH | 0 | -0.000317 |  | NORTH |  | 203 | SARDIS8 | NORTH
96 | 1682 | LAMARPWR_5G | 5 | ONCOR ED | YES | 0.001753 | 157 | 67.7 | 157 | 0 | 1.038 |  | 16825 | n |  | FPP G3 | 7012 | 3 | 70123 | y |  | 96 | 1689 | VALLEY_3 | 3 | NORTH | 0 | -0.000356 |  | NORTH |  | 204 | BETHEL | NORTH
97 | 1683 | LAMARPWR_6G | 6 | ONCOR ED | YES | 0.001753 | 198 | 129.1 | 198 | 0 | 1.038 |  | 16836 | n |  | GIBCRK | 990 | 1 | 9901 | y |  | 97 | 1695 | MOSES_5 | EQ | NORTH | 384.2 | -0.000405 |  | NORTH |  | 205 | HIGHWY22 | NORTH
98 | 1687 | VALLEY_1G | 1 | ONCOR ED | YES | 0.001436 | 170 | 15 | 170 | 0 | 1.029 |  | 16871 | n |  | JKS1 | 5401 | 1 | 54011 | y |  | 98 | 1861 | EAGLEMNT | MB | NORTH | 0 | 0.000423 |  | NORTH | 0 | 206 | POWELLMP | NORTH
99 | 1688 | VALLEY_2G | 2 | ONCOR ED | YES | 0.001436 | 527 | 90 | 527 | 0 | 1.029 |  | 16882 | n |  | JOS #1 | 8139 | MB | 8139MB | y |  | 99 | 1862 | EAGLEMNT | MB | NORTH | 0 | 0.000423 |  | NORTH | 0 | 207 | SIMSBORO | NORTH
100 | 1689 | VALLEY_3G | 3 | ONCOR ED | YES | 0.001655 | 375 | 25 | 375 |  | 1.003 |  | 16893 | n |  | JTD1 | 5111 | 1 | 51111 | y |  | 100 | 1863 | EAGLEMNT | MB | NORTH | 0 | 0.000423 |  | NORTH | 0 | 208 | EUREKA | NORTH
101 | 1701 | MOSES_1G | 1 | ONCOR ED | YES | 0.001927 | 558 | 175 | 558 | 0 | 1.023 |  | 17011 | y |  | JTD2 | 5112 | 2 | 51122 | y |  | 101 | 1877 | WLFHOLW_ | 1 | NORTH | 223.6 | 0.000726 |  | NORTH | 0 | 210 | REAGORSP | NORTH
102 | 1702 | MOSES_2G | 2 | ONCOR ED | YES | 0.001927 | 579 | 175 | 579 | 0 | 1.023 |  | 17022 | y |  | KINDERMG | 1069 | 1 | 10691 | y |  | 102 | 1878 | WLFHOLW_ | 2 | NORTH | 222.7 | 0.000726 |  | NORTH | 0 | 211 | GOODLOE | NORTH
103 | 1703 | MOSES_3G | 3 | ONCOR ED | YES | 0.001927 | 808 | 463 | 808 | 0 | 1.023 |  | 17033 | y |  | KINDERMG | 1070 | 1 | 10701 | y |  | 103 | 1879 | WLFHOLW_ | 3 | NORTH | 243.8 | 0.000726 |  | NORTH | 0 | 212 | WINKLER | NORTH
104 | 1861 | EAGLEMNT_1G | MB | ONCOR ED | YES | -0.002676 | 0 | 30 | 112 |  | 1.022 |  | 1861MB | n |  | KINDERMG | 1071 | 1 | 10711 | y |  | 104 | 1889 | DECRDOVA | 1 | NORTH | 620.4 | 0.000703 |  | NORTH | 0 | 213 | HANEY | NORTH
105 | 1862 | EAGLEMNT_2G | MB | ONCOR ED | YES | -0.002676 | 0 | 40 | 100 |  | 1.022 |  | 1862MB | n |  | KOCHREF2 | 8461 | 1 | 84611 | y |  | 105 | 1892 | DECRDOVA | A | NORTH | 0 | 0.000939 |  | NORTH | 0 | 214 | ROCKETTS | NORTH
106 | 1863 | EAGLEMNT_3G | MB | ONCOR ED | YES | -0.002676 | 0 | 50 | 378 |  | 1.022 |  | 1863MB | n |  | LAR #1 | 8285 | MB | 8285MB | y |  | 106 | 1893 | DECRDOVA | B | NORTH | 0 | 0.000939 |  | NORTH | 0 | 215 | INDIA | NORTH
107 | 1877 | WLFHOLW_1G | 1 | ONCOR ED | YES | -0.004217 | 217.3 | 89.2 | 217.3 | 0 | 1.032 |  | 18771 | n |  | LAR #2 | 8287 | MB | 8287MB | y |  | 107 | 1894 | DECRDOVA | C | NORTH | 0 | 0.000939 |  | NORTH | 0 | 216 | ENNIS | NORTH
108 | 1878 | WLFHOLW_2G | 2 | ONCOR ED | YES | -0.004217 | 215.7 | 105 | 215.7 | 0 | 1.032 |  | 18782 | n |  | LAR #3 | 8288 | MB | 8288MB | y |  | 108 | 1895 | DECRDOVA | D | NORTH | 0 | 0.000939 |  | NORTH | 0 | 217 | GLNHEIGH | NORTH
109 | 1879 | WLFHOLW_3G | 3 | ONCOR ED | YES | -0.004217 | 272.4 | 89.2 | 272.4 | 0 | 1.032 |  | 18793 | n |  | LIM1 | 48721 | 1 | 487211 | y |  | 109 | 1937 | MDLTHELP | 5 | NORTH | 224.6 | 0.000703 |  | NORTH | 0 | 218 | ROCKETT | NORTH
110 | 1889 | DECRDOVA_1G | MB | ONCOR ED | YES | -0.004024 | 0 | 255 | 806 |  | 1.02 |  | 1889MB | n |  | LIM2 | 48722 | 2 | 487222 | y |  | 110 | 1938 | MDLTHELP | 6 | NORTH | 226.5 | 0.000703 |  | NORTH | 0 | 220 | CEDARHIL | NORTH
111 | 1892 | DECRDOVA_2G | A | ONCOR ED | YES | -0.005013 | 65 | 65 | 70 | 0 | 1.025 |  | 1892A | n |  | MNSN1 | 48730 | 1 | 487301 | y |  | 111 | 1941 | MDLTHELP | 1 | NORTH | 226.5 | 0.000517 |  | NORTH | 0 | 221 | TRUMBULL | NORTH
112 | 1893 | DECRDOVA_3G | B | ONCOR ED | YES | -0.005013 | 65 | 65 | 69 | 0 | 1.025 |  | 1893B | n |  | MOSES1 G | 1701 | 1 | 17011 | y |  | 112 | 1942 | MDLTHELP | 2 | NORTH | 216.9 | 0.000517 |  | NORTH | 0 | 222 | TRUMBULL | NORTH
113 | 1894 | DECRDOVA_4G | C | ONCOR ED | YES | -0.005013 | 65 | 65 | 69 | 0 | 1.025 |  | 1894C | n |  | MOSES2 G | 1702 | 2 | 17022 | y |  | 113 | 1943 | MDLTHELP | 3 | NORTH | 212.1 | 0.000703 |  | NORTH | 0 | 223 | SAINTPAU | NORTH
114 | 1895 | DECRDOVA_5G | D | ONCOR ED | YES | -0.005013 | 65 | 65 | 68 | 0 | 1.025 |  | 1895D | n |  | MOSES3 G | 1703 | 3 | 17033 | y |  | 114 | 1944 | MDLTHELP | 4 | NORTH | 223.6 | 0.000703 |  | NORTH | 0 | 224 | ITASCA | NORTH
115 | 1898 | COMCHEPK_1G | 1 | ONCOR ED | YES | -0.004493 | 1217 | 1150 | 1217 | 0 | 1.032 |  | 18981 | y |  | MTNLK 1G | 3097 | 1 | 30971 | y |  | 115 | 1945 | HANDLEY_ | MB | NORTH | 0 | 0.000394 |  | NORTH | 0 | 225 | FORRESTO | NORTH
116 | 1899 | COMCHEPK_2G | 2 | ONCOR ED | YES | -0.004493 | 1159 | 1128 | 1159 | 0 | 1.032 |  | 18992 | y |  | MTNLK 2G | 3098 | 2 | 30982 | y |  | 116 | 1946 | HANDLEY_ | MB | NORTH | 0 | 0.000394 |  | NORTH | 0 | 228 | PEORIA | NORTH
117 | 1937 | MDLTHELP_5G | 5 | ONCOR ED | YES | -0.003295 | 224 | 74 | 224 | 0 | 1 |  | 19375 | n |  | MTNLK 3G | 3099 | 3 | 30993 | y |  | 117 | 1947 | HANDLEY_ | 3 | NORTH | 0 | 0.000407 |  | NORTH | 0 | 230 | DWUSSWW | NORTH
118 | 1938 | MDLTHELP_6G | 6 | ONCOR ED | YES | -0.003295 | 226 | 74 | 226 | 0 | 1 |  | 19386 | n |  | NBY #5 | 8437 | MB | 8437MB | y |  | 118 | 1948 | HANDLEY_ | 4 | NORTH | 0 | 0.000374 |  | NORTH | 0 | 232 | LAMPOSTS | NORTH
119 | 1941 | MDLTHELP_1G | 1 | ONCOR ED | YES | -0.002239 | 216.4 | 74 | 216.4 | 0 | 1 |  | 19411 | n |  | NBY #6 | 8438 | MB | 8438MB | y |  | 119 | 1949 | HANDLEY_ | 5 | NORTH | 0 | 0.000407 |  | NORTH | 0 | 234 | CHATT | NORTH
120 | 1942 | MDLTHELP_2G | 2 | ONCOR ED | YES | -0.002239 | 216.1 | 74 | 216.1 | 0 | 1 |  | 19422 | n |  | NBY #7 | 8442 | MB | 8442MB | y |  | 120 | 2371 | COLLIN_1 | MB | NORTH | 0 | -0.000185 |  | NORTH |  | 236 | LAMPOST | NORTH
121 | 1943 | MDLTHELP_3G | 3 | ONCOR ED | YES | -0.003295 | 212 | 74 | 212 | 0 | 1 |  | 19433 | n |  | NORTHDC7 | 6096 | EQ | 6096EQ | y |  | 121 | 2381 | NTHLK1_G | 1 | NORTH | 0 | -0.000133 |  | NORTH |  | 237 | BLANTON | NORTH
122 | 1944 | MDLTHELP_4G | 4 | ONCOR ED | YES | -0.003295 | 211 | 74 | 211 | 0 | 1 |  | 19444 | n |  | OKLAUN1G | 6752 | 1 | 67521 | y |  | 122 | 2382 | NTHLK2_G | 2 | NORTH | 0 | -0.000133 |  | NORTH |  | 238 | BOSQUESW | NORTH
123 | 1947 | HANDLEY_3G | 3 | ONCOR ED | YES | -0.002233 | 316 | 100 | 395 | 0 | 1.022 |  | 19473 | n |  | PET1 | 48761 | 1 | 487611 | y |  | 123 | 2383 | NTHLK3_G | 3 | NORTH | 0 | -0.000133 |  | NORTH |  | 239 | BOSQUESW | NORTH
124 | 1948 | HANDLEY_4G | 4 | ONCOR ED | YES | -0.002055 | 435 | 150 | 435 | 0 | 1.022 |  | 19484 | n |  | PWR1 | 48791 | 1 | 487911 | y |  | 124 | 2413 | MTCK6_G | 6 | NORTH | 0 | -0.000286 |  | NORTH |  | 240 | WHITNEY5 | NORTH
125 | 1949 | HANDLEY_5G | 5 | ONCOR ED | YES | -0.002233 | 435 | 150 | 435 | 0 | 1.022 |  | 19495 | n |  | PWR2 | 48792 | 2 | 487922 | y |  | 125 | 2414 | MTCK7_G | 7 | NORTH | 0 | -0.000286 |  | NORTH |  | 241 | WHITNEY8 | NORTH
126 | 2371 | COLLIN_1G | MB | ONCOR ED | YES | 0.000723 | 0 | 40 | 138 |  | 1.022 |  | 2371MB | n |  | PWR3 | 48793 | 3 | 487933 | y |  | 126 | 2417 | MTCK8_G | 8 | NORTH | 0 | -0.000286 |  | NORTH |  | 242 | WHITNEYD | NORTH
127 | 2381 | NTHLK1_G | MB | ONCOR ED | YES | 0.000535 | 0 | 35 | 156 |  | 1.022 |  | 2381MB | n |  | PWR4 | 48794 | 4 | 487944 | y |  | 127 | 2418 | MTCK2_G | 2 | NORTH | 0 | -0.000172 |  | NORTH |  | 243 | WHITNEYS | NORTH
128 | 2382 | NTHLK2_G | MB | ONCOR ED | YES | 0.000535 | 0 | 35 | 181 |  | 1.022 |  | 2382MB | n |  | PWR5 | 48795 | 5 | 487955 | y |  | 128 | 2419 | MTCK3_G | MB | NORTH | 0 | -0.000172 |  | NORTH |  | 244 | WHITNYDM | NORTH
129 | 2383 | NTHLK3_G | MB | ONCOR ED | YES | 0.000535 | 0 | 50 | 329 |  | 1.022 |  | 2383MB | n |  | PWR6 | 48796 | 1 | 487961 | y |  | 129 | 2451 | LKHB1_G | 1 | NORTH | 0 | -0.000523 |  | NORTH |  | 245 | WHITNYDM | NORTH
130 | 2413 | MTCK6_G | 6 | ONCOR ED | YES | 0.001429 | 0 | 30 | 118 |  | 1.022 |  | 24136 | n |  | PWR8 | 48797 | 6 | 487976 | y |  | 130 | 2452 | LKHB2_G | 2 | NORTH | 0 | -0.000523 |  | NORTH |  | 246 | BOSQUESW | NORTH
131 | 2414 | MTCK7_G | 7 | ONCOR ED | YES | 0.001429 | 0 | 30 | 115 |  | 1.022 |  | 24147 | n |  | REYSHR G | 80223 | 1 | 802231 | y |  | 131 | 3107 | STRYKER_ | 1 | NORTH | 0 | -0.001362 |  | NORTH |  | 247 | BOSQUESW | NORTH
132 | 2417 | MTCK8_G | 8 | ONCOR ED | YES | 0.001429 | 444.8 | 60 | 556 | 0 | 1.022 |  | 24178 | n |  | S&LCGN1 | 39190 | 1 | 391901 | y |  | 132 | 3108 | STRYKER_ | 2 | NORTH | 0 | -0.001362 |  | NORTH |  | 249 | ROGERSHL | NORTH
133 | 2451 | LKHB1_G | 1 | ONCOR ED | YES | 0.002587 | 391 | 80 | 391 | 0 | 1.022 |  | 24511 | n |  | SAND 4 G | 3432 | 4 | 34324 | y |  | 133 | 3126 | TRINIDAD | 1 | NORTH | 0 | -0.000575 |  | NORTH |  | 250 | FRTGATES | NORTH
134 | 2452 | LKHB2_G | 2 | ONCOR ED | YES | 0.002587 | 516 | 80 | 516 | 0 | 1.022 |  | 24522 | n |  | SANDOW_5 | 13432 | 5 | 134325 | y |  | 134 | 3403 | THOUSE_1 | 1 | NORTH | 439.2 | 0.005547 |  | NORTH | 0 | 251 | BOSQUESW | NORTH
135 | 3097 | MARTLAKE_1G | 1 | ONCOR ED | YES | 0.006102 | 790 | 500 | 790 | 0 | 1.017 |  | 30971 | y |  | SANMIGUE | 5903 | 1 | 59031 | y |  | 135 | 3404 | THOUSE_2 | 2 | NORTH | 622.7 | 0.005547 |  | NORTH | 0 | 252 | BOSQUESW | NORTH
136 | 3098 | MARTLAKE_2G | 2 | ONCOR ED | YES | 0.006102 | 795 | 461 | 795 | 0 | 1.017 |  | 30982 | y |  | SHELL_ | 48820 | 1 | 488201 | y |  | 136 | 3416 | LAKE_CRK | 1 | NORTH | 0 | 0.00582 |  | NORTH | 0 | 253 | BOSQUESW | NORTH
137 | 3099 | MARTLAKE_3G | 3 | ONCOR ED | YES | 0.006102 | 804 | 500 | 804 | 0 | 1.017 |  | 30993 | y |  | SHELL_ | 48821 | 2 | 488212 | y |  | 137 | 3417 | LAKE_CRK | 2 | NORTH | 0 | 0.00582 |  | NORTH | 0 | 254 | FORTGATE | NORTH
138 | 3107 | STRYKER_1G | 1 | ONCOR ED | YES | 0.007022 | 182 | 45 | 182 | 0 | 1.029 |  | 31071 | n |  | SHL_CPS | 48822 | 1 | 488221 | y |  | 138 | 5026 | BRAUNIG_ | 1 | SOUTH | 0 | 0.015771 |  | SOUTH | 0 | 258 | HAMILTON | NORTH
139 | 3108 | STRYKER_2G | 2 | ONCOR ED | YES | 0.007022 | 484 | 75 | 484 | 0 | 1.029 |  | 31082 | n |  | SHL_CPS | 48822 | 2 | 488222 | y |  | 139 | 5027 | BRAUNIG_ | 2 | SOUTH | 0 | 0.015771 |  | SOUTH | 0 | 260 | KEMPNER | SOUTH
140 | 3126 | TRINIDAD_6G | 1 | ONCOR ED | YES | 0.00332 | 224 | 46 | 224 | 0 | 1 |  | 31261 | n |  | SHLDNST1 | 48814 | 1 | 488141 | y |  | 140 | 5028 | BRAUNIG_ | 3 | SOUTH | 0 | 0.015618 |  | SOUTH | 0 | 262 | INDIANGA | NORTH
141 | 3309 | ASPN_G | 1 | ONCOR ED | YES | 0.006956 | 50 | 0 | 50 |  | 1 |  | 33091 | n |  | SI RAY5 | 5934 | 5 | 59345 | y |  | 141 | 5264 | LEON_LCP | 3 | SOUTH | 0 | 0.015561 |  | SOUTH | 0 | 265 | ENERGYSW | NORTH
142 | 3348 | CHAMPION_1G | MB | ONCOR ED | YES | 0.006911 | 0 | 42 | 42 |  | 1 |  | 3348MB | y |  | SOL1 | 48845 | 1 | 488451 | y |  | 142 | 5265 | LEON_LCP | 4 | SOUTH | 0 | 0.015561 |  | SOUTH | 0 | 269 | ENERGY | NORTH
143 | 3381 | BBRN_1G | 1 | ONCOR ED | YES | 0.012396 | 618 | 225 | 618 | 0 | 1.03 |  | 33811 | y |  | STARCO#1 | 8511 | 1 | 85111 | y |  | 143 | 5266 | LEON_LCP | 1 | SOUTH | 39.2 | 0.015561 |  | SOUTH | 0 | 270 | MORTONVA | NORTH
144 | 3382 | BBRN_2G | 2 | ONCOR ED | YES | 0.012396 | 589 | 225 | 589 | 0 | 1.03 |  | 33822 | y |  | STP1 | 5911 | 1 | 59111 | y |  | 144 | 5267 | LEON_LCP | 2 | SOUTH | 39.2 | 0.015561 |  | SOUTH | 0 | 273 | GUSTINE | NORTH
145 | 3403 | THOUSE_1G | MB | ONCOR ED | YES | -0.024519 | 0 | 200 | 563 |  | 1.012 |  | 3403MB | n |  | STP2 | 5912 | 2 | 59122 | y |  | 145 | 5268 | LEON_LCP | 3 | SOUTH | 38.3 | 0.015561 |  | SOUTH | 0 | 274 | GORMAN | NORTH
146 | 3404 | THOUSE_2G | 2 | ONCOR ED | YES | -0.024519 | 807 | 250 | 807 |  | 1.012 |  | 34042 | n |  | TNPONE#1 | 39960 | 1 | 399601 | y |  | 146 | 5269 | LEON_LCP | 4 | SOUTH | 39.2 | 0.015561 |  | SOUTH | 0 | 275 | LEONPLNT | NORTH
147 | 3416 | LAKE_CRK1_G | MB | ONCOR ED | YES | -0.025592 | 0 | 33 | 75 |  | 1.029 |  | 3416MB | n |  | TNPONE#2 | 39970 | 1 | 399701 | y |  | 147 | 5396 | CALAVER_ | 1 | SOUTH | 89.3 | 0.015755 |  | SOUTH | 0 | 276 | HGHWY101 | NORTH
148 | 3417 | LAKE_CRK2_G | MB | ONCOR ED | YES | -0.025592 | 0 | 40 | 222 |  | 1.029 |  | 3417MB | n |  | UCAR #1 | 8148 | 2 | 81482 | y |  | 148 | 5397 | CALAVER_ | 2 | SOUTH | 0 | 0.015755 |  | SOUTH | 0 | 277 | HASSE | NORTH
149 | 3432 | SANDOW_4G | 4 | ONCOR ED | YES | -0.086218 | 580 | 225 | 580 |  | 1.029 |  | 34324 | y |  | UCAR #2 | 8147 | 10 | 814710 | y |  | 149 | 5436 | TUTTL_WB | 1 | SOUTH | 0 | 0.015725 |  | SOUTH | 0 | 279 | OLDEN | NORTH
150 | 5026 | BRAUNIG_VHB1 | 1 | CPS_TSP | YES | -0.13896 | 215 | 40 | 215 | 0 | 1.0192 |  | 50261 | n |  | UCCCGNGG | 39480 | 1 | 394801 | y |  | 150 | 5438 | TUTTL_WB | 3 | SOUTH | 92.3 | 0.015725 |  | SOUTH | 0 | 281 | DOWNING | NORTH
151 | 5027 | BRAUNIG_VHB2 | 2 | CPS_TSP | YES | -0.13896 | 216 | 40 | 216 | 0 | 1.0192 |  | 50272 | n |  | UCCCGNSG | 39470 | 1 | 394701 | y |  | 151 | 5439 | TUTTL_WB | 4 | SOUTH | 0 | 0.015725 |  | SOUTH | 0 | 282 | EOLIANRD | NORTH
152 | 5028 | BRAUNIG_VHB3 | 3 | CPS_TSP | YES | -0.13883 | 407 | 60 | 407 | 0 | 1.0138 |  | 50283 | n |  | VAL #1 | 8506 | 1 | 85061 | y |  | 152 | 5476 | BRA_AVR1 | 1 | SOUTH | 152 | 0.015287 |  | SOUTH | 0 | 283 | ZEPHYR | NORTH
153 | 5111 | CALAVER_JTD1 | 1 | CPS_TSP | YES | -0.13885 | 430 | 80 | 430 | 0 | 1.0138 |  | 51111 | y |  | VAL #2 | 8507 | 2 | 85072 | y |  | 153 | 5477 | BRA_AVR1 | 1 | SOUTH | 166 | 0.015287 |  | SOUTH | 0 | 284 | EARLY | NORTH
154 | 5112 | CALAVER_JTD2 | 2 | CPS_TSP | YES | -0.13885 | 430 | 80 | 430 | 0 | 1.0138 |  | 51122 | y |  | VISTRONG | 80224 | 1 | 802241 | y |  | 154 | 5478 | BRA_AVR1 | 1 | SOUTH | 152 | 0.015287 |  | SOUTH | 0 | 285 | RISINGST | NORTH
155 | 5264 | LEON_LCP3G3 | 3 | CPS_TSP | YES | -0.13887 | 0 | 20 | 58 |  | 1.0197 |  | 52643 | n |  | VISTRONG | 80225 | 2 | 802252 | y |  | 155 | 5503 | RAYBURNG | 1 | SOUTH | 0 | 0.012278 |  | SOUTH | 0 | 289 | NIMROD | NORTH
156 | 5265 | LEON_LCP4G4 | 4 | CPS_TSP | YES | -0.13887 | 89 | 25 | 89 | 0 | 1.0197 |  | 52654 | n |  | WAP5 | 48925 | 5 | 489255 | y |  | 156 | 5505 | RAYBURNG | 1 | SOUTH | 0 | 0.012278 |  | SOUTH | 0 | 290 | SHILOH | NORTH
157 | 5266 | LEON_LCPCT1 | 1 | CPS_TSP | YES | -0.13887 | 44 | 24 | 44 | 0 | 1.0197 |  | 52661 | n |  | WAP6 | 48926 | 6 | 489266 | y |  | 157 | 5506 | RAYBURNG | 1 | SOUTH | 0 | 0.012278 |  | SOUTH | 0 | 291 | DELEON | NORTH
158 | 5267 | LEON_LCPCT2 | 2 | CPS_TSP | YES | -0.13887 | 44 | 24 | 44 | 0 | 1.0197 |  | 52672 | n |  | WAP7 | 48927 | 7 | 489277 | y |  | 158 | 5508 | RAYBURNC | 1 | SOUTH | 24.6 | 0.012553 |  | SOUTH | 0 | 292 | HOLDER8 | NORTH
159 | 5268 | LEON_LCPCT3 | 3 | CPS_TSP | YES | -0.13887 | 43 | 24 | 43 | 0 | 1.0197 |  | 52683 | n |  | WAP8 | 48928 | 8 | 489288 | y |  | 159 | 5509 | RAYBURNC | 1 | SOUTH | 19.6 | 0.012553 |  | SOUTH | 0 | 293 | HOLDER9 | NORTH
160 | 5269 | LEON_LCPCT4 | 4 | CPS_TSP | YES | -0.13887 | 45 | 24 | 45 | 0 | 1.0197 |  | 52694 | n |  | WELSHDC1 | 5920 | EQ | 5920EQ | y |  | 160 | 5511 | RAYBURNC | 1 | SOUTH | 24.8 | 0.012553 |  | SOUTH | 0 | 294 | MOUNTARY | NORTH
161 | 5396 | CALAVER_OWS1 | 1 | CPS_TSP | YES | -0.13884 | 418 | 80 | 418 | 0 | 1.0192 |  | 53961 | n | [7 empty] | 161 | 5512 | RAYBURNC | 1 | SOUTH | 25.7 | 0.012553 |  | SOUTH | 0 | 295 | STEPHENV | NORTH
162 | 5397 | CALAVER_OWS2 | 2 | CPS_TSP | YES | -0.13884 | 400 | 80 | 400 | 0 | 1.0192 |  | 53972 | n | [7 empty] | 162 | 5728 | FALCONHY | 2 | SOUTH | 12 | 0.009694 |  | SOUTH | 0 | 296 | STPHNVLT | NORTH
163 | 5401 | CALAVER_JKS1 | 1 | CPS_TSP | YES | -0.14093 | 562 | 100 | 562 | 0 | 1.026 |  | 54011 | y | [7 empty] | 163 | 5729 | FALCONHY | 3 | SOUTH | 11 | 0.009694 |  | SOUTH | 0 | 297 | CARLTONS | NORTH
164 | 5436 | TUTTL_WBT1G1 | 1 | CPS_TSP | YES | -0.13887 | 48.8 | 20 | 61 | 0 | 1.012 |  | 54361 | n | [7 empty] | 164 | 5890 | PEARSALL | 1 | SOUTH | 0 | 0.013457 |  | SOUTH | 0 | 298 | CARLTON | NORTH
165 | 5438 | TUTTL_WBT3G3 | 3 | CPS_TSP | YES | -0.13887 | 95 | 25 | 95 | 0 | 1.012 |  | 54383 | n | [7 empty] | 165 | 5891 | PEARSALL | 1 | SOUTH | 0 | 0.013457 |  | SOUTH | 0 | 299 | STEPHNVI | NORTH
166 | 5439 | TUTTL_WBT4G4 | 4 | CPS_TSP | YES | -0.13887 | 151 | 40 | 151 | 0 | 1.012 |  | 54394 | n | [7 empty] | 166 | 5892 | PEARSALL | 1 | SOUTH | 0 | 0.013457 |  | SOUTH | 0 | 300 | JOHNSVIL | NORTH
167 | 5476 | BRA_AVR1_CT1 | 1 | CPS_TSP | YES | -0.14009 | 155 | 90 | 155 | 0 | 1.025 |  | 54761 | n | [7 empty] | 167 | 5932 | SI_RAY9 | 9 | SOUTH | 0 | 0.009126 |  | SOUTH | 0 | 301 | LINGLEVI | NORTH
168 | 5477 | BRA_AVR1_ST | 1 | CPS_TSP | YES | -0.14009 | 174 | 138 | 174 | 0 | 1.025 |  | 54771 | n | [7 empty] | 168 | 5933 | SI_RAY6 | 6 | SOUTH | 0 | 0.009126 |  | SOUTH | 0 | 302 | SELDEN | NORTH
169 | 5478 | BRA_AVR1_CT2 | 1 | CPS_TSP | YES | -0.14009 | 155 | 90 | 155 | 0 | 1.025 |  | 54781 | n | [7 empty] | 169 | 5935 | SI_RAY10 | 10 | SOUTH | 43 | 0.009126 |  | SOUTH | 0 | 303 | NORFORK | NORTH
170 | 5503 | RAYBURNGEN3 | 1 | STEC_TSP | YES | -0.16148 | 17.6 | 6 | 22 | 0 | 1.0224 |  | 55031 | n | [7 empty] | 170 | 6016 | SWMESA | 1 | WEST | 18.8 | 0.001885 |  | WEST | 0 | 304 | WRIGHT | NORTH
171 | 5505 | RAYBURNGEN1 | 1 | STEC_TSP | YES | -0.16148 | 0 | 1 | 11 |  | 1.0223 |  | 55051 | n | [7 empty] | 171 | 6100 | OKLA7A | EQ | WEST | 200.3 | 0.000937 |  | WEST | 0 | 305 | BLUFFDAL | NORTH
172 | 5506 | RAYBURNGEN2 | 1 | STEC_TSP | YES | -0.16148 | 0 | 1 | 11 |  | 1.0223 |  | 55061 | n | [7 empty] | 172 | 6144 | MCADOO1A | 1 | WEST | 22.5 | 0.001257 |  | WEST | 0 | 306 | BUNKER | NORTH
173 | 5508 | RAYBURNCC9 | 1 | STEC_TSP | YES | -0.16096 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 |  | 55081 | n | [7 empty] | 173 | 6407 | TURKTRAK | 1 | WEST | 33.9 | 0.001538 |  | WEST | 0 | 307 | GRANBURY | NORTH
174 | 5509 | RAYBURNCC10 | 1 | STEC_TSP | YES | -0.16096 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 |  | 55091 | n | [7 empty] | 174 | 6637 | SNYDERW1 | 1 | WEST | 12.6 | 0.001286 |  | WEST | 0 | 308 | BUNKER01 | NORTH
175 | 5511 | RAYBURNCC7 | 1 | STEC_TSP | YES | -0.16096 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 |  | 55111 | n | [7 empty] | 175 | 6948 | DENISNDM | 2 | NORTH | 25.8 | -0.000286 |  | NORTH |  | 309 | TOLARTAP | NORTH
176 | 5512 | RAYBURNCC8 | 1 | STEC_TSP | YES | -0.16096 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 |  | 55121 | n | [7 empty] | 176 | 6948 | DENISNDM | 1 | NORTH | 31 | -0.000286 |  | NORTH |  | 310 | IVAN | NORTH
177 | 5728 | FALCONHYDRO2 | 2 | STEC_TSP | YES | -0.15365 | 12 | 0 | 12 | 0 | 1.0234 |  | 57282 | n | [7 empty] | 177 | 7000 | L_FERGUS | 1 | SOUTH | 424.4 | 0.020878 |  | SOUTH | 0 | 311 | HILLCITY | NORTH
178 | 5729 | FALCONHYDRO3 | 3 | STEC_TSP | YES | -0.15365 | 11 | 0 | 11 | 0 | 1.0234 |  | 57293 | n | [7 empty] | 178 | 7004 | L_SIMGID | 1 | SOUTH | 140 | 0.034451 |  | SOUTH | 0 | 315 | GLENROSE | NORTH
179 | 5890 | PEARSALLGEN1 | 1 | STEC_TSP | YES | -0.13908 | 19.2 | 6 | 24 | 0 | 1.0226 |  | 58901 | n | [7 empty] | 179 | 7005 | L_SIMGID | 2 | SOUTH | 135 | 0.034451 |  | SOUTH | 0 | 319 | MERIDIAN | NORTH
180 | 5891 | PEARSALLGEN2 | 1 | STEC_TSP | YES | -0.13908 | 19.4 | 6 | 24.3 | 0 | 1.0226 |  | 58911 | n | [7 empty] | 180 | 7006 | L_SIMGID | 3 | SOUTH | 338 | 0.034451 |  | SOUTH | 0 | 322 | LIPAN | NORTH
181 | 5892 | PEARSALLGEN3 | 1 | STEC_TSP | YES | -0.13908 | 19.1 | 6 | 23.9 | 0 | 1.0226 |  | 58921 | n | [7 empty] | 181 | 7007 | L_LOSTPI | 1 | SOUTH | 171 | 0.028713 |  | SOUTH | 0 | 323 | CRANFILS | NORTH
182 | 5903 | SANMIGUELGEN | 1 | STEC_TSP | YES | -0.14527 | 396.3 | 180 | 396.3 | 0 | 1.0336 |  | 59031 | y | [7 empty] | 182 | 7008 | L_LOSTPI | 2 | SOUTH | 167 | 0.028713 |  | SOUTH | 0 | 327 | POWELL | NORTH
183 | 5911 | STP_GN1___1 | 1 | STP | YES | -0.19638 | 1333 | 1249 | 1333 | 0 | 1.0406 |  | 59111 | y | [7 empty] | 183 | 7009 | L_LOSTPI | 3 | SOUTH | 188 | 0.028713 |  | SOUTH | 0 | 331 | RWMILLER | NORTH
184 | 5912 | STP_GN2___2 | 2 | STP | YES | -0.19638 | 1332 | 1249 | 1332 | 0 | 1.0406 |  | 59122 | y | [7 empty] | 184 | 7014 | L_HAYSEN | 1 | SOUTH | 230 | 0.020019 |  | SOUTH | 0 | 332 | RWMILLER | NORTH
185 | 5920 | WELSHDC1 | EQ | DCEAST | YES | 0 | 400.3 | -600 | 600 | 0 | 1.025 |  | 5920EQ | y | [7 empty] | 185 | 7015 | L_HAYSEN | 2 | SOUTH | 234 | 0.020019 |  | SOUTH | 0 | 333 | RWMILLER | NORTH
186 | 5932 | SI_RAY9 | 9 | BPUB TSP | YES | -0.15776 | 32 | 32 | 38 | 0 | 1.035 |  | 59329 | n | [7 empty] | 186 | 7016 | L_HAYSEN | 3 | SOUTH | 226 | 0.020019 |  | SOUTH | 0 | 334 | RWMILLER | NORTH
187 | 5933 | SI_RAY6 | 6 | BPUB TSP | YES | -0.15776 | 15.4 | 10 | 19.3 | 0 | 1.035 |  | 59336 | n | [7 empty] | 187 | 7017 | L_HAYSEN | 4 | SOUTH | 228 | 0.020019 |  | SOUTH | 0 | 335 | RWMILLER | NORTH
188 | 5934 | SI_RAY5 | 5 | BPUB TSP | YES | 0 | 0 | 10 | 15 |  | 1.035 |  | 59345 | y | [7 empty] | 188 | 7020 | L_AUSTPL | 2 | SOUTH | 7.6 | 0.024941 |  | SOUTH | 0 | 336 | RWMILLER | NORTH
189 | 5935 | SI_RAY10 | 10 | BPUB TSP | YES | -0.15776 | 47 | 10 | 47 | 0 | 1.03 |  | 593510 | n | [7 empty] | 189 | 7020 | L_AUSTPL | 1 | SOUTH | 7.6 | 0.024941 |  | SOUTH | 0 | 343 | MRSSHPRD | NORTH
190 | 6016 | SWMESA | 1 | AEP_TNC | YES | -0.018389 | 18.8 | 0 | 75 |  | 1.03 |  | 60161 | n | [7 empty] | 190 | 7022 | L_BUCHAN | 1 | SOUTH | 15.2 | 0.020137 |  | SOUTH | 0 | 344 | MRSSHPRD | NORTH
191 | 6096 | NORTHDC7 | EQ | NORTH_DC | YES | 0 | 50 | -220 | 220 | 0 | 1.035 |  | 6096EQ | y | [7 empty] | 191 | 7023 | L_BUCHAN | 2 | SOUTH | 0 | 0.020137 |  | SOUTH | 0 | 345 | MRSSHPRD | NORTH
192 | 6144 | MCADOO1A | 1 | AEP_TNC | YES | -0.011004 | 15 | 0 | 150 | 0 | 1.025 |  | 61441 | n | [7 empty] | 192 | 7024 | L_BUCHAN | 3 | SOUTH | 12 | 0.020137 |  | SOUTH | 0 | 350 | ABBYBEND | NORTH
193 | 6407 | TURKTRAK1A | 1 | AEP_TNC | YES | -0.014769 | 33.9 | 0 | 169.5 | 0 | 1.025 |  | 64071 | n | [7 empty] | 193 | 7026 | L_INKSDA | 1 | SOUTH | 10.9 | 0.020124 |  | SOUTH | 0 | 352 | PROTROYA | NORTH
194 | 6637 | SNYDERW1A | 1 | AEP_TNC | YES | -0.01167 | 12.6 | 0 | 63 | 0 | 1.025 |  | 66371 | n | [7 empty] | 194 | 7028 | L_MARBFA | 1 | SOUTH | 0 | 0.021768 |  | SOUTH | 0 | 356 | SPUNKY8 | NORTH
195 | 6752 | OKLA0A | 1 | AEP_TNC | YES | -0.007829 | 649.7 | 175 | 649.7 | 0 | 1.035 |  | 67521 | y | [7 empty] | 195 | 7029 | L_MARBFA | 2 | SOUTH | 14.2 | 0.021768 |  | SOUTH | 0 | 357 | SPUNKY9 | NORTH
196 | 6948 | DENISNDM | 1 | RYBRNTSP | YES | 0.001261 | 40 | 5 | 40 |  | 1.015 |  | 69481 | n | [7 empty] | 196 | 7031 | L_MARSFO | 1 | SOUTH | 23.9 | 0.023598 |  | SOUTH | 0 | 363 | HOOD8 | NORTH
197 | 6948 | DENISNDM | 2 | RYBRNTSP | YES | 0.001261 | 31 | 5 | 40 |  | 1.015 |  | 69482 | n | [7 empty] | 197 | 7032 | L_MARSFO | 2 | SOUTH | 17.4 | 0.023598 |  | SOUTH | 0 | 364 | HOOD | NORTH
198 | 7000 | L_FERGUS1_1Y | 1 | LCRA TSC | YES | -0.1048 | 400 | 65 | 423.3 | 0 | 1.015 |  | 70001 | n | [7 empty] | 198 | 7033 | L_MARSFO | 3 | SOUTH | 23.9 | 0.023598 |  | SOUTH | 0 | 366 | JNSNCNTY | NORTH
199 | 7004 | L_SIMGID1_1Y | 1 | LCRA TSC | YES | -0.11857 | 132 | 40 | 132 | 0 | 1.02 |  | 70041 | n | [7 empty] | 199 | 7035 | L_WIRTZ_ | 1 | SOUTH | 0 | 0.020982 |  | SOUTH | 0 | 367 | JNSNCNTY | NORTH
200 | 7005 | L_SIMGID1_2Y | 2 | LCRA TSC | YES | -0.11857 | 133 | 32 | 139 | 0 | 1.02 |  | 70052 | n | [7 empty] | 200 | 7036 | L_WIRTZ_ | 2 | SOUTH | 19.6 | 0.020982 |  | SOUTH | 0 | 370 | JNSNCNTY | NORTH
201 | 7006 | L_SIMGID1_3Y | 3 | LCRA TSC | YES | -0.11857 | 324.9 | 60 | 329 | 0 | 1.02 |  | 70063 | n | [7 empty] | 201 | 7038 | L_DELAWA | 1 | WEST | 7 | 0.001403 |  | WEST | 0 | 373 | ACTON | NORTH
202 | 7007 | L_LOSTPI1_1Y | 1 | LCRA TSC | YES | -0.11776 | 158.6 | 110 | 158 | 0 | 1 |  | 70071 | n | [7 empty] | 202 | 7038 | L_DELAWA | 2 | WEST | 6 | 0.001403 |  | WEST | 0 | 377 | FALLCREE | NORTH
203 | 7008 | L_LOSTPI1_2Y | 2 | LCRA TSC | YES | -0.11776 | 157.7 | 107 | 160 | 0 | 1 |  | 70082 | n | [7 empty] | 203 | 7487 | L_CANYHY | 1 | SOUTH | 0 | 0.021346 |  | SOUTH | 0 | 380 | FRIENDSH | NORTH
204 | 7009 | L_LOSTPI1_3Y | 3 | LCRA TSC | YES | -0.11776 | 173.9 | 72 | 175 | 0 | 1 |  | 70093 | n | [7 empty] | 204 | 7605 | L_MCQUEE | 2 | SOUTH | 0 | 0.020734 |  | SOUTH | 0 | 384 | GEORGESC | NORTH
205 | 7010 | L_FPPYD11_1Y | 1 | LCRA TSC | YES | -0.13105 | 547.4 | 200 | 606 | 0 | 1.02 |  | 70101 | y | [7 empty] | 205 | 7605 | L_MCQUEE | 1 | SOUTH | 0 | 0.020734 |  | SOUTH | 0 | 385 | LITTLEHO | NORTH
206 | 7011 | L_FPPYD11_2Y | 2 | LCRA TSC | YES | -0.13105 | 552.2 | 200 | 598 | 0 | 1.02 |  | 70112 | y | [7 empty] | 206 | 7605 | L_MCQUEE | 3 | SOUTH | 0 | 0.020734 |  | SOUTH | 0 | 387 | NEWHOPE | NORTH
207 | 7012 | L_FPPYD21_3Y | 3 | LCRA TSC | YES | -0.13117 | 427.5 | 200 | 436 | 0 | 1.02 |  | 70123 | y | [7 empty] | 207 | 7609 | L_SCHUMA | 1 | SOUTH | 0 | 0.017891 |  | SOUTH | 0 | 391 | BONO | NORTH
208 | 7014 | L_HAYSEN1_1Y | 1 | LCRA TSC | YES | -0.13093 | 223.9 | 74 | 223.9 | 0 | 1.008 |  | 70141 | n | [7 empty] | 208 | 7624 | L_LAKEWO | 2 | SOUTH | 0 | 0.024647 |  | SOUTH | 0 | 393 | CONCORD | NORTH
209 | 7015 | L_HAYSEN1_2Y | 2 | LCRA TSC | YES | -0.13093 | 225 | 74 | 225 | 0 | 1.008 |  | 70152 | n | [7 empty] | 209 | 7624 | L_LAKEWO | 1 | SOUTH | 0 | 0.024647 |  | SOUTH | 0 | 394 | CONCORD | NORTH
210 | 7016 | L_HAYSEN1_3Y | 3 | LCRA TSC | YES | -0.13093 | 224.6 | 74 | 224.6 | 0 | 1.008 |  | 70163 | n | [7 empty] | 210 | 7800 | L_GUADGE | 1 | SOUTH | 159 | 0.016098 |  | SOUTH | 0 | 395 | DOMINO | NORTH
211 | 7017 | L_HAYSEN1_4Y | 4 | LCRA TSC | YES | -0.13093 | 226.7 | 74 | 226.7 | 0 | 1.008 |  | 70174 | n | [7 empty] | 211 | 7801 | L_GUADGE | 2 | SOUTH | 152 | 0.016098 |  | SOUTH | 0 | 398 | JOSHUA | NORTH
212 | 7020 | L_AUSTPL1_1Y | 1 | LCRA TSC | YES | -0.11266 | 0 | 0 | 8 |  | 1 |  | 70201 | n | [7 empty] | 212 | 7802 | L_GUADGE | 3 | SOUTH | 147 | 0.016098 |  | SOUTH | 0 | 399 | CROWLEY | NORTH
213 | 7020 | L_AUSTPL1_1Y | 2 | LCRA TSC | YES | -0.11266 | 0 | 0 | 8 |  | 1 |  | 70202 | n | [7 empty] | 213 | 7803 | L_GUADGE | 4 | SOUTH | 153 | 0.016098 |  | SOUTH | 0 | 404 | JESSICA | NORTH
214 | 7022 | L_BUCHAN1_1Y | 1 | LCRA TSC | YES | -0.097819 | 0 | 0 | 18 |  | 1 |  | 70221 | n | [7 empty] | 214 | 7804 | L_GUADGE | 5 | SOUTH | 188 | 0.016098 |  | SOUTH | 0 | 405 | EGAN | NORTH
215 | 7023 | L_BUCHAN1_2Y | 2 | LCRA TSC | YES | -0.097819 | 0 | 0 | 18 |  | 1 |  | 70232 | n | [7 empty] | 215 | 7805 | L_GUADGE | 6 | SOUTH | 207 | 0.016098 |  | SOUTH | 0 | 412 | BURLESON | NORTH
216 | 7024 | L_BUCHAN1_3Y | 3 | LCRA TSC | YES | -0.097819 | 0 | 0 | 15 |  | 1 |  | 70243 | n | [7 empty] | 216 | 7807 | L_BASTEN | 1 | SOUTH | 157.1 | 0.025166 |  | SOUTH | 0 | 415 | KEENE | NORTH
217 | 7026 | L_INKSDA1_1Y | 1 | LCRA TSC | YES | -0.098332 | 0 | 0 | 13.7 |  | 1 |  | 70261 | n | [7 empty] | 217 | 7808 | L_BASTEN | 1 | SOUTH | 153.7 | 0.025166 |  | SOUTH | 0 | 419 | LILLIAN8 | NORTH
218 | 7028 | L_MARBFA1_1Y | 1 | LCRA TSC | YES | -0.10665 | 0 | 0 | 18 |  | 1 |  | 70281 | n | [7 empty] | 218 | 7809 | L_BASTEN | 1 | SOUTH | 230.2 | 0.025166 |  | SOUTH | 0 | 420 | LILLIAN9 | NORTH
219 | 7029 | L_MARBFA1_2Y | 2 | LCRA TSC | YES | -0.10665 | 0 | 0 | 18 |  | 1 |  | 70292 | n | [7 empty] | 219 | 7810 | L_RIONOG | 1 | SOUTH | 151 | 0.018027 |  | SOUTH | 0 | 428 | VALLYBRN | NORTH
220 | 7031 | L_MARSFO1G1Y | 1 | LCRA TSC | YES | -0.11048 | 0 | 0 | 36 |  | 1 |  | 70311 | n | [7 empty] | 220 | 7811 | L_RIONOG | 2 | SOUTH | 160 | 0.018027 |  | SOUTH | 0 | 429 | RETTA | NORTH
221 | 7032 | L_MARSFO1G2Y | 2 | LCRA TSC | YES | -0.11048 | 0 | 0 | 35 |  | 1 |  | 70322 | n | [7 empty] | 221 | 7812 | L_RIONOG | 3 | SOUTH | 163 | 0.018027 |  | SOUTH | 0 | 430 | TIMBERGR | NORTH
222 | 7033 | L_MARSFO1G3Y | 3 | LCRA TSC | YES | -0.11048 | 0 | 0 | 36 |  | 1 |  | 70333 | n | [7 empty] | 222 | 7813 | L_RIONOG | 4 | SOUTH | 301 | 0.018027 |  | SOUTH | 0 | 432 | CONLEY | NORTH
223 | 7035 | L_WIRTZ_1G1Y | 1 | LCRA TSC | YES | -0.10461 | 0 | 0 | 29 |  | 1 |  | 70351 | n | [7 empty] | 223 | 8032 | AMISTADH | 1 | SOUTH | 33 | 0.009684 |  | SOUTH | 0 | 433 | WILDCAT | NORTH
224 | 7036 | L_WIRTZ_1G2Y | 2 | LCRA TSC | YES | -0.10461 | 0 | 0 | 29.7 |  | 1 |  | 70362 | n | [7 empty] | 224 | 8033 | AMISTADH | 2 | SOUTH | 25 | 0.009684 |  | SOUTH | 0 | 435 | LKALVARA | NORTH
225 | 7038 | L_DELAWA1_1Y | 1 | LCRA TSC | YES | -0.013175 | 3.5 | 0 | 35 | 0 | 1 |  | 70381 | n | [7 empty] | 225 | 8048 | FALCONHY | 1 | SOUTH | 12 | 0.009694 |  | SOUTH | 0 | 436 | GRANDVIE | NORTH
226 | 7038 | L_DELAWA1_1Y | 2 | LCRA TSC | YES | -0.013175 | 3 | 0 | 30 | 0 | 1 |  | 70382 | n | [7 empty] | 226 | 8173 | VICEC51A | 5 | SOUTH | 125.4 | 0.013509 |  | SOUTH | 0 | 440 | GRIFFITH | NORTH
227 | 7303 | L_WPPGS12_1Y | 1 | LCRA TSC | YES | -0.12902 | 50 | 0 | 50 | 0 | 1.025 |  | 73031 | n | [7 empty] | 227 | 8174 | VICEC61A | 6 | SOUTH | 163.7 | 0.013509 |  | SOUTH | 0 | 441 | VENUS | NORTH
228 | 7303 | L_WPPGS12_1Y | 2 | LCRA TSC | YES | -0.12902 | 50 | 0 | 50 | 0 | 1.025 |  | 73032 | n | [7 empty] | 228 | 8189 | CUECPL2A | 1 | SOUTH | 12 | 0.024263 |  | SOUTH | 0 | 443 | SANDFLAT | NORTH
229 | 7305 | L_WPPGS34_1Y | 3 | LCRA TSC | YES | -0.12902 | 50 | 0 | 50 | 0 | 1.025 |  | 73053 | n | [7 empty] | 229 | 8262 | ELPS | 1 | SOUTH | 6 | 0.010534 |  | SOUTH | 0 | 444 | COVINGTO | NORTH
230 | 7305 | L_WPPGS34_1Y | 4 | LCRA TSC | YES | -0.12902 | 50 | 0 | 50 | 0 | 1.025 |  | 73054 | n | [7 empty] | 230 | 8459 | B_DAVIS0 | MB | SOUTH | 0 | 0.009041 |  | SOUTH | 0 | 447 | SANDFLAT | NORTH
231 | 7487 | L_CANYHY8_1Y | 1 | LCRA TSC | YES | -0.12718 | 0 | 0 | 6 |  | 1 |  | 74871 | n | [7 empty] | 231 | 8460 | B_DAVIS0 | MB | SOUTH | 0 | 0.009041 |  | SOUTH | 0 | 451 | NASAUBAY | NORTH
232 | 7605 | L_MCQUEE9_1Y | 1 | LCRA TSC | YES | -0.13406 | 0 | 0 | 2.4 |  | 1.025 |  | 76051 | n | [7 empty] | 232 | 8560 | CNOPGT1 | 1 | SOUTH | 158.9 | 0.009004 |  | SOUTH | 0 | 455 | NASSAUBA | NORTH
233 | 7605 | L_MCQUEE9_1Y | 2 | LCRA TSC | YES | -0.13406 | 0 | 0 | 2.4 |  | 1.025 |  | 76052 | n | [7 empty] | 233 | 8561 | CNOPGT2 | 2 | SOUTH | 161.2 | 0.009004 |  | SOUTH | 0 | 466 | WAPLES9 | NORTH
234 | 7605 | L_MCQUEE9_1Y | 3 | LCRA TSC | YES | -0.13406 | 0 | 0 | 2.8 |  | 1.025 |  | 76053 | n | [7 empty] | 234 | 8562 | CNOPST1 | 3 | SOUTH | 162 | 0.009004 |  | SOUTH | 0 | 467 | WAPLES8 | NORTH
235 | 7609 | L_SCHUMA8_1Y | 1 | LCRA TSC | YES | -0.13511 | 0 | 0 | 4 |  | 1 |  | 76091 | n | [7 empty] | 235 | 8926 | LGE_GT10 | 1 | SOUTH | 158 | 0.008747 |  | SOUTH | 0 | 470 | FAIRVIEW | NORTH
236 | 7624 | L_LAKEWO9_1Y | 1 | LCRA TSC | YES | -0.13605 | 0 | 0 | 2.4 |  | 1 |  | 76241 | n | [7 empty] | 236 | 8927 | LGE_GT20 | 2 | SOUTH | 151.5 | 0.008747 |  | SOUTH | 0 | 471 | LAKEWOOD | NORTH
237 | 7624 | L_LAKEWO9_1Y | 2 | LCRA TSC | YES | -0.13605 | 0 | 0 | 2.4 |  | 1 |  | 76242 | n | [7 empty] | 237 | 8928 | LGE_STG0 | 3 | SOUTH | 88 | 0.008747 |  | SOUTH | 0 | 473 | THORPSPR | NORTH
238 | 7800 | L_GUADGE1_1Y | 1 | LCRA TSC | YES | -0.13804 | 147 | 30 | 147 | 0 | 1.02 |  | 78001 | n | [7 empty] | 238 | 8930 | ICPGN10A | 1 | SOUTH | 158 | 0.008747 |  | SOUTH | 0 | 475 | STOCKTNB | NORTH
239 | 7801 | L_GUADGE1_2Y | 2 | LCRA TSC | YES | -0.13804 | 138 | 30 | 138 | 0 | 1.02 |  | 78012 | n | [7 empty] | 239 | 8931 | ICPGN20A | 2 | SOUTH | 136.7 | 0.008747 |  | SOUTH | 0 | 477 | FOX8 | NORTH
240 | 7802 | L_GUADGE1_3Y | 3 | LCRA TSC | YES | -0.13804 | 146 | 30 | 146 | 0 | 1.02 |  | 78023 | n | [7 empty] | 240 | 8932 | ICPGN30A | 3 | SOUTH | 137.6 | 0.008747 |  | SOUTH | 0 | 478 | FOX9 | NORTH
241 | 7803 | L_GUADGE1_4Y | 4 | LCRA TSC | YES | -0.13804 | 149 | 30 | 149 | 0 | 1.02 |  | 78034 | n | [7 empty] | 241 | 8933 | FGNTS001 | 1 | SOUTH | 128.9 | 0.009247 |  | SOUTH | 0 | 484 | SODASPRN | NORTH
242 | 7804 | L_GUADGE1_5Y | 5 | LCRA TSC | YES | -0.13804 | 182 | 30 | 182 | 0 | 1.02 |  | 78045 | n | [7 empty] | 242 | 8934 | FGNTS101 | 2 | SOUTH | 130.6 | 0.009247 |  | SOUTH | 0 | 487 | BROCK | NORTH
243 | 7805 | L_GUADGE1_6Y | 6 | LCRA TSC | YES | -0.13804 | 203 | 30 | 203 | 0 | 1.02 |  | 78056 | n | [7 empty] | 243 | 8935 | FGNTS201 | 3 | SOUTH | 148.9 | 0.009247 |  | SOUTH | 0 | 489 | STHBROCK | NORTH
244 | 7807 | L_BASTEN1_1Y | 1 | LCRA TSC | YES | -0.11642 | 152.5 | 83.5 | 152.5 | 0 | 1.004 |  | 78071 | n | [7 empty] | 244 | 8936 | MVGN#1 | 1 | SOUTH | 232 | 0.009173 |  | SOUTH | 0 | 491 | SOUTHBRO | NORTH
245 | 7808 | L_BASTEN1_2Y | 1 | LCRA TSC | YES | -0.11642 | 149.5 | 83.5 | 149.5 | 0 | 1.004 |  | 78081 | n | [7 empty] | 245 | 8937 | MVGN#2 | 2 | SOUTH | 236 | 0.009173 |  | SOUTH | 0 | 494 | TINTOP | NORTH
246 | 7809 | L_BASTEN1_3Y | 1 | LCRA TSC | YES | -0.11642 | 232.6 | 42 | 232.6 | 0 | 1.004 |  | 78091 | n | [7 empty] | 246 | 8938 | MVGN#3 | 3 | SOUTH | 246 | 0.009173 |  | SOUTH | 0 | 495 | RAILROAD | NORTH
247 | 7810 | L_RIONOG1G1Y | 1 | LCRA TSC | YES | -0.13459 | 148 | 0 | 148 | 0 | 1.02 |  | 78101 | n | [7 empty] | 247 | 8981 | HECN1 | 1 | SOUTH | 152 | 0.009173 |  | SOUTH | 0 | 498 | LIVEOAK | NORTH
248 | 7811 | L_RIONOG1G2Y | 2 | LCRA TSC | YES | -0.13459 | 148 | 0 | 148 | 0 | 1.02 |  | 78112 | n | [7 empty] | 248 | 8982 | HECN2 | 2 | SOUTH | 151 | 0.009173 |  | SOUTH | 0 | 501 | HILLTOP8 | NORTH
249 | 7812 | L_RIONOG1G3Y | 3 | LCRA TSC | YES | -0.13459 | 154 | 0 | 154 | 0 | 1.02 |  | 78123 | n | [7 empty] | 249 | 8983 | HECN3 | 3 | SOUTH | 179 | 0.009173 |  | SOUTH | 0 | 502 | NTHTEXAS | NORTH
250 | 7813 | L_RIONOG1S1Y | 4 | LCRA TSC | YES | -0.13459 | 293 | 0 | 293 | 0 | 1.02 |  | 78134 | n | [7 empty] | 250 | 9000 | DECKR_G1 | 1 | SOUTH | 315.7 | 0.02531 |  | SOUTH | 0 | 503 | NTHTEXAS | NORTH
251 | 8032 | AMISTADHYD1 | 1 | STEC_TSP | YES | -0.10379 | 33 | 13 | 33 | 0 | 1.03 |  | 80321 | n | [7 empty] | 251 | 9001 | DECKR_G2 | 2 | SOUTH | 408.2 | 0.02531 |  | SOUTH | 0 | 504 | NTHTEXAS | NORTH
252 | 8033 | AMISTADHYD2 | 2 | STEC_TSP | YES | -0.10379 | 25 | 13 | 25 | 0 | 1.03 |  | 80332 | n | [7 empty] | 252 | 9002 | DECKR_G3 | 3 | SOUTH | 0 | 0.025809 |  | SOUTH | 0 | 505 | NTHTEXAS | NORTH
253 | 8048 | FALCONHYDRO1 | 1 | STEC_TSP | YES | -0.15365 | 12 | 0 | 12 | 0 | 1.0234 |  | 80481 | n | [7 empty] | 253 | 9003 | DECKR_G4 | 4 | SOUTH | 50 | 0.025809 |  | SOUTH | 0 | 506 | HILLTOP9 | NORTH
254 | 8066 | DUP1V#1 | 1 | AEP_TCC | YES | -0.161 | 52.3 | 0 | 73 | 0 | 1.01 |  | 80661 | y | [7 empty] | 254 | 9004 | DECKR_G5 | 5 | SOUTH | 49 | 0.025809 |  | SOUTH | 0 | 509 | WTHFRDLK | NORTH
255 | 8134 | FOR #1 | 1 | AEP_TCC | YES | -0.16728 | 54.1 | 45 | 79 | 0 | 1 |  | 81341 | y | [7 empty] | 255 | 9005 | DECKR_G6 | 6 | SOUTH | 47 | 0.025809 |  | SOUTH | 0 | 511 | AGNESSWT | NORTH
256 | 8138 | FOR #2 | 2 | AEP_TCC | YES | -0.16728 | 63.1 | 45 | 81 | 0 | 1 |  | 81382 | y | [7 empty] | 256 | 9016 | SANDH_G1 | 1 | SOUTH | 48 | 0.025157 |  | SOUTH | 0 | 512 | NRTHWTHF | NORTH
257 | 8139 | JOS #1 | MB | AEP_TCC | YES | 0 | 0 | 45 | 255 |  | 1.02 |  | 8139MB | y | [7 empty] | 257 | 9017 | SANDH_G2 | 2 | SOUTH | 47 | 0.025157 |  | SOUTH | 0 | 514 | DUBLTRAN | NORTH
258 | 8147 | UCAR #2 | 10 | AEP_TCC | YES | -0.16378 | 18.2 | 0 | 28 |  | 1 |  | 814710 | y | [7 empty] | 258 | 9018 | SANDH_G3 | 3 | SOUTH | 43 | 0.025157 |  | SOUTH | 0 | 515 | SHADYGRO | NORTH
259 | 8148 | UCAR #1 | 2 | AEP_TCC | YES | -0.16378 | 6.1 | 0 | 7 | 0 | 1.009 |  | 81482 | y | [7 empty] | 259 | 9019 | SANDH_G4 | 4 | SOUTH | 0 | 0.025157 |  | SOUTH | 0 | 518 | ADVANCE | NORTH
260 | 8153 | FOR #3 | 3 | AEP_TCC | YES | -0.16728 | 63.1 | 45 | 79.9 | 0 | 1 |  | 81533 | y | [7 empty] | 260 | 9020 | SANDHG5A | 5A | SOUTH | 154 | 0.025157 |  | SOUTH | 0 | 519 | WHITT | NORTH
261 | 8154 | FOR #4 | 4 | AEP_TCC | YES | -0.16728 | 63.1 | 60 | 80 | 0 | 1 |  | 81544 | y | [7 empty] | 261 | 9021 | SANDHG5C | 5C | SOUTH | 152 | 0.025157 |  | SOUTH | 0 | 520 | ALEDOTAP | NORTH
262 | 8155 | FOR #5 | 5 | AEP_TCC | YES | -0.16728 | 63.1 | 60 | 78.4 | 0 | 1 |  | 81555 | y | [7 empty] | 262 | 11001 | NAV1CT | 1 | WEST | 80 | 0.001342 |  | WEST | 0 | 522 | HUDSONOA | NORTH
263 | 8156 | FOR #6 | 6 | AEP_TCC | YES | -0.16728 | 24.9 | 5 | 25 | 0 | 1 |  | 81566 | y | [7 empty] | 263 | 11009 | NAV2CT | 1 | WEST | 80 | 0.001342 |  | WEST | 0 | 526 | DICEY | NORTH
264 | 8157 | FOR #7 | 7 | AEP_TCC | YES | -0.16728 | 28.8 | 5 | 46 | 0 | 1 |  | 81577 | y | [7 empty] | 264 | 11011 | NAV3ST | 1 | WEST | 115 | 0.001342 |  | WEST | 0 | 527 | ALEDO | NORTH
265 | 8161 | COLETO0A | 1 | AEP_TCC | YES | -0.15506 | 633 | 200 | 633 | 0 | 1.03 |  | 81611 | y | [7 empty] | 265 | 11012 | NAV4CT | 1 | WEST | 80 | 0.001342 |  | WEST | 0 | 530 | SPRINGTO | NORTH
266 | 8173 | VICEC51A | 5 | AEP_TCC | YES | -0.15995 | 144 | 18 | 144 | 0 | 1.025 |  | 81735 | n | [7 empty] | 266 | 11013 | NAV5CT | 1 | WEST | 80 | 0.001342 |  | WEST | 0 | 531 | FLATROCK | NORTH
267 | 8174 | VICEC61A | 6 | AEP_TCC | YES | -0.15995 | 188 | 42 | 188 | 0 | 1.025 |  | 81746 | n | [7 empty] | 267 | 11014 | NAV6ST | 1 | WEST | 115 | 0.001342 |  | WEST | 0 | 532 | AGNES | NORTH
268 | 8262 | ELPS | 1 | AEP_TCC | YES | -0.11564 | 6 | 6 | 6 | 0 | 1.15 |  | 82621 | n | [7 empty] | 268 | 11020 | TIEHVSG_ | 1 | WEST | 212 | 0.001342 |  | WEST | 0 | 533 | FALTROCK | NORTH
269 | 8285 | LAR #1 | MB | AEP_TCC | YES | 0 | 0 | 9 | 32 |  | 1.0497 |  | 8285MB | y | [7 empty] | 269 | 11021 | TIEHVCG_ | 1 | WEST | 150 | 0.001342 |  | WEST | 0 | 534 | WETHFORD | NORTH
270 | 8287 | LAR #2 | MB | AEP_TCC | YES | 0 | 0 | 9 | 32 |  | 1.04 |  | 8287MB | y | [7 empty] | 270 | 11022 | TIEHVCG_ | 1 | WEST | 139 | 0.001342 |  | WEST | 0 | 537 | CNTERPOI | NORTH
271 | 8288 | LAR #3 | MB | AEP_TCC | YES | 0 | 0 | 25 | 105 |  | 1.04 |  | 8288MB | y | [7 empty] | 271 | 11023 | TIEHVCG_ | 1 | WEST | 137 | 0.001342 |  | WEST | 0 | 541 | RENO | NORTH
272 | 8388 | BATES0A | MB | AEP_TCC | YES | 0 | 0 | 21 | 71 |  | 1.033 |  | 8388MB | y | [7 empty] | 272 | 11024 | TIEHVCG_ | 1 | WEST | 154 | 0.001342 |  | WEST | 0 | 545 | BRIAR | NORTH
273 | 8393 | BATES0B | MB | AEP_TCC | YES | 0 | 0 | 25 | 110 |  | 1.03 |  | 8393MB | y | [7 empty] | 273 | 11025 | TIEHVSG_ | 1 | WEST | 213 | 0.001342 |  | WEST | 0 | 548 | BOYD | NORTH
274 | 8437 | NUECES_B0C | MB | AEP_TCC | YES | 0 | 0 | 7 | 30 |  | 1.03 |  | 8437MB | y | [7 empty] | 274 | 11056 | ROSCOE_1 | 1 | WEST | 41.8 | 0.001199 |  | WEST | 0 | 555 | GRAPEVIN | NORTH
275 | 8438 | NUECES_B0B | MB | AEP_TCC | YES | 0 | 0 | 26 | 169 |  | 1.03 |  | 8438MB | y | [7 empty] | 275 | 11057 | CHAMPION | 1 | WEST | 25.3 | 0.001199 |  | WEST | 0 | 556 | IBM | NORTH
276 | 8442 | NBEC7 | 7 | AEP_TCC | YES | -0.15884 | 0 | 81 | 367 |  | 1.0298 |  | 84427 | n | [7 empty] | 276 | 11058 | PYRON_1G | 1 | WEST | 49.8 | 0.001199 |  | WEST | 0 | 559 | HERITAGE | NORTH
277 | 8442 | NBEC7 | MB | AEP_TCC | YES | -0.15884 | 0 | 81 | 367 |  | 1.0298 |  | 8442MB | y | [7 empty] | 277 | 11059 | INADALE_ | 1 | WEST | 39.4 | 0.001199 |  | WEST | 0 | 562 | JOPLIN | NORTH
278 | 8456 | COSW#1 | 1 | AEP_TCC | YES | -0.15876 | 20 | 0 | 20 | 0 | 1.027 |  | 84561 | y | [7 empty] | 278 | 11147 | NOTREES_ | 1 | WEST | 29.8 | 0.001395 |  | WEST | 0 | 565 | KELLER | NORTH
279 | 8457 | COSW#2 | 2 | AEP_TCC | YES | -0.15876 | 14 | 0 | 14 | 0 | 1.027 |  | 84572 | y | [7 empty] | 279 | 11309 | BULLCREK | 1 | WEST | 20.9 | 0.001304 |  | WEST | 0 | 566 | CHERRYGR | NORTH
280 | 8459 | B_DAVIS0B | MB | AEP_TCC | YES | -0.15864 | 0 | 50 | 339 |  | 1.03 |  | 8459MB | n | [7 empty] | 280 | 11310 | BULLCREK | 1 | WEST | 15.1 | 0.001304 |  | WEST | 0 | 567 | WIZARDWE | NORTH
281 | 8460 | B_DAVIS0A | MB | AEP_TCC | YES | -0.15864 | 0 | 50 | 340 |  | 1.03 |  | 8460MB | n | [7 empty] | 281 | 11320 | COYOTE_1 | 1 | WEST | 0 | 0.001308 |  | WEST | 0 | 568 | PEDENROA | NORTH
282 | 8461 | KOCH_UP0A | 1 | AEP_TCC | YES | -0.1584 | 38 | 0 | 38 | 0 | 1.012 |  | 84611 | y | [7 empty] | 282 | 11691 | KMICHICT | 1 | NORTH | 140.1 | -0.000356 |  | NORTH |  | 570 | WISECNTY | NORTH
283 | 8506 | VAL #1 | 1 | AEP_TCC | YES | -0.15852 | 20.9 | 0 | 25 | 0 | 1.0055 |  | 85061 | y | [7 empty] | 283 | 11692 | KMICHICT | 2 | NORTH | 143 | -0.000356 |  | NORTH |  | 572 | AURORA | NORTH
284 | 8507 | VAL #2 | 2 | AEP_TCC | YES | -0.15852 | 20.9 | 0 | 25 | 0 | 1.0055 |  | 85072 | y | [7 empty] | 284 | 11693 | KMICHIST | 3 | NORTH | 301.4 | -0.000356 |  | NORTH |  | 573 | NEWARK | NORTH
285 | 8511 | OXY_CC0A | 1 | AEP_TCC | YES | -0.15845 | 30.3 | 0 | 38 | 0 | 1.027 |  | 85111 | y | [7 empty] | 285 | 11694 | KMICHICT | 4 | NORTH | 138.2 | -0.000356 |  | NORTH |  | 576 | RHOME | NORTH
286 | 8517 | CELANEBI0A | 1 | AEP_TCC | YES | -0.15798 | 29 | 0 | 29 | 0 | 1.02 |  | 85171 | y | [7 empty] | 286 | 11695 | KMICHICT | 5 | NORTH | 142.1 | -0.000356 |  | NORTH |  | 578 | ALLISON | NORTH
287 | 8560 | CNOPGT1 | 1 | AEP_TCC | YES | -0.15882 | 148.3 | 0 | 148.3 | 0 | 1.03 |  | 85601 | n | [7 empty] | 287 | 11696 | KMICHIST | 6 | NORTH | 299.5 | -0.000356 |  | NORTH |  | 579 | JCKCNTY8 | NORTH
288 | 8561 | CNOPGT2 | 2 | AEP_TCC | YES | -0.15882 | 148.6 | 0 | 148.6 | 0 | 1.03 |  | 85612 | n | [7 empty] | 288 | 12322 | ENNSTRAC | 1 | NORTH | 193.9 | -4.5e-05 |  | NORTH |  | 580 | JCKCNTY8 | NORTH
289 | 8562 | CNOPST1 | 3 | AEP_TCC | YES | -0.15882 | 153 | 0 | 153 | 0 | 1.03 |  | 85623 | n | [7 empty] | 289 | 12323 | ENNSTRAC | 2 | NORTH | 111.3 | -4.5e-05 |  | NORTH |  | 581 | JCKCNTY8 | NORTH
290 | 8926 | LGE_GT10A | 1 | AEP_TCC | YES | -0.15991 | 158 | 0 | 158 | 0 | 1.03 |  | 89261 | n | [7 empty] | 290 | 12411 | FPLEFR1A | 1 | NORTH | 161.3 | -0.000631 |  | NORTH |  | 582 | JCKCNTY8 | NORTH
291 | 8927 | LGE_GT20A | 2 | AEP_TCC | YES | -0.15991 | 153 | 0 | 153 | 0 | 1.03 |  | 89272 | n | [7 empty] | 291 | 12412 | FPLEFR1B | 2 | NORTH | 156.5 | -0.000631 |  | NORTH |  | 583 | DECATUR | NORTH
292 | 8928 | LGE_STG0A | 3 | AEP_TCC | YES | -0.15991 | 100 | 0 | 100 | 0 | 1.03 |  | 89283 | n | [7 empty] | 292 | 12413 | FPLEFR1C | 3 | NORTH | 148.8 | -0.000631 |  | NORTH |  | 584 | WOODIE | NORTH
293 | 8930 | ICPGN10A | 1 | AEP_TCC | YES | -0.15991 | 149 | 0 | 149 | 0 | 1.03 |  | 89301 | n | [7 empty] | 293 | 12414 | FPLEFR1S | 4 | NORTH | 398.3 | -0.000631 |  | NORTH |  | 585 | CHISOLM | NORTH
294 | 8931 | ICPGN20A | 2 | AEP_TCC | YES | -0.15991 | 150 | 0 | 150 | 0 | 1.03 |  | 89312 | n | [7 empty] | 294 | 12421 | FPLEFR2A | 1 | NORTH | 159.6 | -0.000631 |  | NORTH |  | 587 | GREENWOO | NORTH
295 | 8932 | ICPGN30A | 3 | AEP_TCC | YES | -0.15991 | 127 | 0 | 127 | 0 | 1.03 |  | 89323 | n | [7 empty] | 295 | 12422 | FPLEFR2B | 2 | NORTH | 155.9 | -0.000631 |  | NORTH |  | 588 | WILLOW | NORTH
296 | 8933 | FGNTS001 | 1 | AEP_TCC | YES | -0.15696 | 146.5 | 0 | 146.5 | 0 | 1.03 |  | 89331 | n | [7 empty] | 296 | 12423 | FPLEFR2C | 3 | NORTH | 156 | -0.000631 |  | NORTH |  | 590 | PERCHHIL | NORTH
297 | 8934 | FGNTS101 | 2 | AEP_TCC | YES | -0.15696 | 147.9 | 0 | 147.9 | 0 | 1.03 |  | 89342 | n | [7 empty] | 297 | 12424 | FPLEFR2S | 4 | NORTH | 394.8 | -0.000631 |  | NORTH |  | 595 | KEETER | NORTH
298 | 8935 | FGNTS201 | 3 | AEP_TCC | YES | -0.15696 | 173 | 0 | 173 | 0 | 1.03 |  | 89353 | n | [7 empty] | 298 | 13116 | TGATEWAY | 1 | NORTH | 152.6 | -0.00127 |  | NORTH |  | 596 | COTTONDA | NORTH
299 | 8936 | MVGN#1 | 1 | AEP_TCC | YES | -0.15752 | 216.6 | 0 | 216.6 | 0 | 1.0304 |  | 89361 | n | [7 empty] | 299 | 13117 | TGATEWAY | 2 | NORTH | 150.7 | -0.00127 |  | NORTH |  | 598 | ELNA | NORTH
300 | 8937 | MVGN#2 | 2 | AEP_TCC | YES | -0.15752 | 216.7 | 0 | 216.7 | 0 | 1.0304 |  | 89372 | n | [7 empty] | 300 | 13118 | TGATEWAY | 3 | NORTH | 149.7 | -0.00127 |  | NORTH |  | 600 | BRIDGEPO | NORTH
301 | 8938 | MVGN#3 | 3 | AEP_TCC | YES | -0.15752 | 250.9 | 0 | 250.9 | 0 | 1.0304 |  | 89383 | n | [7 empty] | 301 | 13119 | TGATEWAY | 4 | NORTH | 371.5 | -0.00127 |  | NORTH |  | 601 | EBRIDGPO | NORTH
302 | 8981 | HECN1 | 1 | AEP_TCC | YES | -0.15752 | 144.8 | 0 | 144.8 | 0 | 1.0304 |  | 89811 | n | [7 empty] | 302 | 13131 | CALFREST | 1 | NORTH | 153.1 | -0.002211 |  | NORTH |  | 608 | CRAFTON | NORTH
303 | 8982 | HECN2 | 2 | AEP_TCC | YES | -0.15752 | 144.1 | 0 | 144.1 | 0 | 1.0304 |  | 89822 | n | [7 empty] | 303 | 13132 | CALFREST | 2 | NORTH | 153.3 | -0.002211 |  | NORTH |  | 616 | CARTER | NORTH
304 | 8983 | HECN3 | 3 | AEP_TCC | YES | -0.15752 | 171.9 | 0 | 171.9 | 0 | 1.0304 |  | 89833 | n | [7 empty] | 304 | 13133 | CALFREST | 3 | NORTH | 167 | -0.002211 |  | NORTH |  | 618 | LONESTAR | NORTH
305 | 9000 | DECKR_G1 | 1 | AEN TSP | YES | -0.11254 | 280 | 50 | 321 | 0 | 1.015 |  | 90001 | n | [7 empty] | 305 | 13134 | CALFREST | 4 | NORTH | 156.7 | -0.00217 |  | NORTH |  | 620 | BOWIE8 | NORTH
306 | 9001 | DECKR_G2 | 2 | AEN TSP | YES | -0.11254 | 400 | 50 | 426 | 0 | 1.015 |  | 90012 | n | [7 empty] | 306 | 13135 | CALFREST | 5 | NORTH | 156.9 | -0.00217 |  | NORTH |  | 621 | BOWIE9 | NORTH
307 | 9002 | DECKR_G3 | 3 | AEN TSP | YES | -0.1117 | 0 | 24 | 42 |  | 1.015 |  | 90023 | n | [7 empty] | 307 | 13136 | CALFREST | 6 | NORTH | 169.6 | -0.00217 |  | NORTH |  | 628 | SPRNGCRE | NORTH
308 | 9003 | DECKR_G4 | 4 | AEN TSP | YES | -0.1117 | 44 | 24 | 44 | 0 | 1.015 |  | 90034 | n | [7 empty] | 308 | 32883 | BRYN_DNS | 1 | NORTH | 0 | -0.009033 |  | NORTH |  | 629 | ROMANJUA | NORTH
309 | 9004 | DECKR_G5 | 5 | AEN TSP | YES | -0.1117 | 44 | 24 | 44 | 0 | 1.015 |  | 90045 | n | [7 empty] | 309 | 32884 | BRYN_DNS | 1 | NORTH | 0 | -0.009033 |  | NORTH |  | 631 | NEWPORT | NORTH
310 | 9005 | DECKR_G6 | 6 | AEN TSP | YES | -0.1117 | 44 | 24 | 47 | 0 | 1.015 |  | 90056 | n | [7 empty] | 310 | 32886 | BRYN_ATK | MB | NORTH | 0 | -0.009615 |  | NORTH |  | 632 | JOHNSONS | NORTH
311 | 9016 | SANDH_G1 | 1 | AEN TSP | YES | -0.11364 | 45 | 2 | 49 | 0 | 1.0175 |  | 90161 | n | [7 empty] | 311 | 32887 | BRYN_ATK | MB | NORTH | 0 | -0.009615 |  | NORTH |  | 633 | MONTAGUE | NORTH
312 | 9017 | SANDH_G2 | 2 | AEN TSP | YES | -0.11364 | 45 | 2 | 46 | 0 | 1.0175 |  | 90172 | n | [7 empty] | 312 | 32888 | BRYN_ATK | 1 | NORTH | 0 | -0.009615 |  | NORTH |  | 634 | AUDUBONS | NORTH
313 | 9018 | SANDH_G3 | 3 | AEN TSP | YES | -0.11364 | 45 | 2 | 46 | 0 | 1.0175 |  | 90183 | n | [7 empty] | 313 | 32890 | BRYN_ATK | MB | NORTH | 0 | -0.009615 |  | NORTH |  | 635 | AUDUBON | NORTH
314 | 9019 | SANDH_G4 | 4 | AEN TSP | YES | -0.11364 | 0 | 2 | 47 |  | 1.0175 |  | 90194 | n | [7 empty] | 314 | 32891 | BRYN_ATK | MB | NORTH | 0 | -0.009615 |  | NORTH |  | 636 | JOHNSON | NORTH
315 | 9020 | SANDHG5A | 5A | AEN TSP | YES | -0.11364 | 150 | 84 | 155 | 0 | 1.0175 |  | 90205A | n | [7 empty] | 315 | 32892 | BRYN_DNS | 1 | NORTH | 0 | -0.009033 |  | NORTH |  | 640 | ROANOKE | NORTH
316 | 9021 | SANDHG5C | 5C | AEN TSP | YES | -0.11364 | 140 | 0 | 148 | 0 | 1.0175 |  | 90215C | n | [7 empty] | 316 | 36998 | RDCNYNG1 | 1 | WEST | 16.8 | 0.001278 |  | WEST | 0 | 645 | LEWISVLS | NORTH
317 | 11001 | NAV1CT | 1 | ONCOR ED | YES | -0.012481 | 70.4 | 18 | 70.4 | 0 | 1.029 |  | 110011 | n | [7 empty] | 317 | 38332 | TNWDWRDU | 1 | WEST | 20 | 0.001869 |  | WEST | 0 | 646 | LEWISVLS | NORTH
318 | 11009 | NAV2CT | 1 | ONCOR ED | YES | -0.012481 | 71.4 | 18 | 71.4 | 0 | 1.029 |  | 110091 | n | [7 empty] | 318 | 38437 | TNSRBNME | 1 | WEST | 37.5 | 0.001871 |  | WEST | 0 | 648 | COPPELL | NORTH
319 | 11011 | NAV3ST | 1 | ONCOR ED | YES | -0.012481 | 92.8 | 40 | 92.8 | 0 | 1.029 |  | 110111 | n | [7 empty] | 319 | 38611 | TNBPAMCG | 1 | HOUSTON | 145.6 | -0.027374 |  | HOUSTON |  | 649 | PNTHRCRE | NORTH
320 | 11012 | NAV4CT | 1 | ONCOR ED | YES | -0.012481 | 80 | 18 | 80 | 0 | 1.029 |  | 110121 | n | [7 empty] | 320 | 38612 | TNBPAMCG | 2 | HOUSTON | 135.1 | -0.027374 |  | HOUSTON |  | 651 | LEBANON | NORTH
321 | 11013 | NAV5CT | 1 | ONCOR ED | YES | -0.012481 | 80 | 18 | 80 | 0 | 1.029 |  | 110131 | n | [7 empty] | 321 | 38613 | TNBPAMCG | 3 | HOUSTON | 144.5 | -0.027374 |  | HOUSTON |  | 652 | AUBREY | NORTH
322 | 11014 | NAV6ST | 1 | ONCOR ED | YES | -0.012481 | 115 | 40 | 115 | 0 | 1.029 |  | 110141 | n | [7 empty] | 322 | 38614 | TNBPAMCG | 4 | HOUSTON | 82.6 | -0.027374 |  | HOUSTON |  | 653 | CUSTER2 | NORTH
323 | 11020 | TIEHVSG_1G | 1 | ONCOR ED | YES | -0.012489 | 208.2 | 63 | 208.2 | 0 | 1.012 |  | 110201 | n | [7 empty] | 323 | 38615 | TNBPAMCG | 1 | HOUSTON | 209.9 | -0.027374 |  | HOUSTON |  | 655 | CUSTER | NORTH
324 | 11021 | TIEHVCG_1G | 1 | ONCOR ED | YES | -0.012489 | 142.1 | 103 | 142.1 | 0 | 1.012 |  | 110211 | n | [7 empty] | 324 | 38711 | TNTXCTY1 | 1 | HOUSTON | 103.2 | -0.027374 |  | HOUSTON |  | 656 | MOUND | NORTH
325 | 11022 | TIEHVCG_2G | 1 | ONCOR ED | YES | -0.012489 | 132.4 | 103 | 132.4 | 0 | 1.012 |  | 110221 | n | [7 empty] | 325 | 38712 | TNTXCTY2 | 1 | HOUSTON | 88.6 | -0.027374 |  | HOUSTON |  | 657 | KIMBALRO | NORTH
326 | 11023 | TIEHVCG_3G | 1 | ONCOR ED | YES | -0.012489 | 137.4 | 103 | 137.4 | 0 | 1.012 |  | 110231 | n | [7 empty] | 326 | 38713 | TNTXCTY3 | 1 | HOUSTON | 90.9 | -0.027374 |  | HOUSTON |  | 658 | MCKAMY | NORTH
327 | 11024 | TIEHVCG_4G | 1 | ONCOR ED | YES | -0.012489 | 147 | 103 | 147 | 0 | 1.012 |  | 110241 | n | [7 empty] | 327 | 38714 | TNTXCTY4 | 1 | HOUSTON | 88.6 | -0.027374 |  | HOUSTON |  | 659 | BRIDGES | NORTH
328 | 11025 | TIEHVSG_2G | 1 | ONCOR ED | YES | -0.012489 | 213.2 | 63 | 213.2 | 0 | 1.012 |  | 110251 | n | [7 empty] | 328 | 39760 | TNSCLP1_ | 1 | HOUSTON | 95 | -0.01787 |  | HOUSTON |  | 660 | LEWISVIL | NORTH
329 | 11056 | ROSCOE_1G | 1 | ONCOR ED | YES | -0.010844 | 41.8 | 0 | 209 |  | 1 |  | 110561 | n | [7 empty] | 329 | 39770 | TNSCLP2_ | 1 | HOUSTON | 105.4 | -0.01787 |  | HOUSTON |  | 661 | CROSTIMB | NORTH
330 | 11057 | CHAMPION_1G | 1 | ONCOR ED | YES | -0.010844 | 25.3 | 0 | 126.5 |  | 1 |  | 110571 | n | [7 empty] | 330 | 39775 | TNSCLP4_ | 1 | HOUSTON | 101.5 | -0.01787 |  | HOUSTON |  | 662 | NAVO | NORTH
331 | 11058 | PYRON_1G | 1 | ONCOR ED | YES | -0.010844 | 49.8 | 0 | 249 |  | 1 |  | 110581 | n | [7 empty] | 331 | 39790 | TNSCLP3_ | 1 | HOUSTON | 98.9 | -0.01787 |  | HOUSTON |  | 663 | HEBRON | NORTH
332 | 11059 | INADALE_1G | 1 | ONCOR ED | YES | -0.010844 | 39.4 | 0 | 197 |  | 1 |  | 110591 | n | [7 empty] | 332 | 48511 | LPE_GT1_ | 1 | HOUSTON | 36.1 | -0.02906 |  | HOUSTON |  | 664 | HIGHLAND | NORTH
333 | 11065 | ELBOWCK_1G | 1 | ONCOR ED | YES | -0.011723 | 23.4 | 0 | 121.9 | 0 | 1 |  | 110651 | n | [7 empty] | 333 | 48512 | LPE_GT2_ | 2 | HOUSTON | 36.1 | -0.02906 |  | HOUSTON |  | 668 | CANYON | NORTH
334 | 11147 | NOTREES_1G | 1 | ONCOR ED | YES | -0.01308 | 29.8 | 0 | 149 | 0 | 1.017 |  | 111471 | n | [7 empty] | 334 | 48513 | LPE_GT3_ | 3 | HOUSTON | 35.3 | -0.02906 |  | HOUSTON |  | 670 | KRUM | NORTH
335 | 11309 | BULLCREK_2G | 1 | ONCOR ED | YES | -0.011929 | 20.9 | 0 | 180 |  | 1 |  | 113091 | n | [7 empty] | 335 | 48514 | LPE_GT4_ | 4 | HOUSTON | 35.3 | -0.02906 |  | HOUSTON |  | 671 | LAKEDALL | NORTH
336 | 11310 | BULLCREK_1G | 1 | ONCOR ED | YES | -0.011929 | 15.1 | 0 | 180 |  | 1 |  | 113101 | n | [7 empty] | 336 | 48521 | BVE_GT1_ | 1 | HOUSTON | 175.8 | -0.027165 |  | HOUSTON |  | 672 | RECTORRO | NORTH
337 | 11320 | COYOTE_1G | 1 | ONCOR ED | YES | -0.011973 | 22.5 | 0 | 225 |  | 1 |  | 113201 | n | [7 empty] | 337 | 48522 | BVE_GT2_ | 2 | HOUSTON | 169.5 | -0.027165 |  | HOUSTON |  | 673 | KRUMSW | NORTH
338 | 11691 | KMICHICT1_G | 1 | ONCOR ED | YES | 0.001655 | 144 | 80 | 144 | 0 | 1.026 |  | 116911 | n | [7 empty] | 338 | 48523 | BVE_ST1_ | 3 | HOUSTON | 262.9 | -0.027165 |  | HOUSTON |  | 675 | ROCKHILL | NORTH
339 | 11692 | KMICHICT2_G | 2 | ONCOR ED | YES | 0.001655 | 146 | 80 | 146 | 0 | 1.026 |  | 116922 | n | [7 empty] | 339 | 48531 | BYU_GT1_ | 1 | HOUSTON | 56.8 | -0.028418 |  | HOUSTON |  | 679 | MCPHERSO | NORTH
340 | 11693 | KMICHIST3_G | 3 | ONCOR ED | YES | 0.001655 | 312 | 60 | 312 | 0 | 1.026 |  | 116933 | n | [7 empty] | 340 | 48532 | BYU_GT2_ | 2 | HOUSTON | 55.9 | -0.028418 |  | HOUSTON |  | 680 | NRTHSANG | NORTH
341 | 11694 | KMICHICT4_G | 4 | ONCOR ED | YES | 0.001655 | 144 | 80 | 144 | 0 | 1.026 |  | 116944 | n | [7 empty] | 341 | 48533 | BYU_GT3_ | 3 | HOUSTON | 69 | -0.028418 |  | HOUSTON |  | 681 | FRISCO | NORTH
342 | 11695 | KMICHICT5_G | 5 | ONCOR ED | YES | 0.001655 | 148 | 80 | 148 | 0 | 1.026 |  | 116955 | n | [7 empty] | 342 | 48534 | BYU_GT4_ | 4 | HOUSTON | 56.8 | -0.028418 |  | HOUSTON |  | 684 | SPRING | NORTH
343 | 11696 | KMICHIST6_G | 6 | ONCOR ED | YES | 0.001655 | 310 | 60 | 310 | 0 | 1.026 |  | 116966 | n | [7 empty] | 343 | 48581 | CBY_GN1_ | 1 | HOUSTON | 0 | -0.029301 |  | HOUSTON |  | 691 | VALLEYVI | NORTH
344 | 12322 | ENNSTRAC_1G | 1 | ONCOR ED | YES | 0.000504 | 196 | 130 | 196 | 0 | 1.036 |  | 123221 | n | [7 empty] | 344 | 48582 | CBY_GN2_ | 2 | HOUSTON | 0 | -0.029185 |  | HOUSTON |  | 695 | MUENSTER | NORTH
345 | 12323 | ENNSTRAC_2G | 2 | ONCOR ED | YES | 0.000504 | 116 | 100 | 116 | 0 | 1.036 |  | 123232 | n | [7 empty] | 345 | 48591 | CHE_GT2_ | 2 | HOUSTON | 176 | -0.0301 |  | HOUSTON |  | 698 | SALEM | NORTH
346 | 12411 | FPLEFR1A_G | 1 | ONCOR ED | YES | 0.003135 | 161 | 72 | 161 | 0 | 1 |  | 124111 | n | [7 empty] | 346 | 48594 | CHE_GN4_ | 4 | HOUSTON | 123.9 | -0.029658 |  | HOUSTON |  | 704 | MTNSPRNG | NORTH
347 | 12412 | FPLEFR1B_G | 2 | ONCOR ED | YES | 0.003135 | 164 | 72 | 164 | 0 | 1 |  | 124122 | n | [7 empty] | 347 | 48641 | DPEC_GT1 | 1 | HOUSTON | 148.9 | -0.028325 |  | HOUSTON |  | 705 | HAWKINS9 | NORTH
348 | 12413 | FPLEFR1C_G | 3 | ONCOR ED | YES | 0.003135 | 164 | 72 | 164 | 0 | 1 |  | 124133 | n | [7 empty] | 348 | 48642 | DPEC_GT2 | 2 | HOUSTON | 145.8 | -0.028325 |  | HOUSTON |  | 706 | WOODBINE | NORTH
349 | 12414 | FPLEFR1S_G | 4 | ONCOR ED | YES | 0.003135 | 414 | 191 | 414 | 0 | 1 |  | 124144 | n | [7 empty] | 349 | 48643 | DPEC_GT3 | 3 | HOUSTON | 150.8 | -0.028325 |  | HOUSTON |  | 707 | HAWKINS8 | NORTH
350 | 12421 | FPLEFR2A_G | 1 | ONCOR ED | YES | 0.003135 | 162 | 72 | 162 | 0 | 1 |  | 124211 | n | [7 empty] | 350 | 48644 | DPEC_GT4 | 4 | HOUSTON | 149 | -0.028325 |  | HOUSTON |  | 708 | KIOWA | NORTH
351 | 12422 | FPLEFR2B_G | 2 | ONCOR ED | YES | 0.003135 | 161 | 72 | 161 | 0 | 1 |  | 124222 | n | [7 empty] | 351 | 48645 | DPEC_ST5 | 5 | HOUSTON | 242.6 | -0.028325 |  | HOUSTON |  | 709 | CALLISBU | NORTH
352 | 12423 | FPLEFR2C_G | 3 | ONCOR ED | YES | 0.003135 | 163 | 72 | 163 | 0 | 1 |  | 124233 | n | [7 empty] | 352 | 48671 | FTR_GT1_ | 1 | NORTH | 137.3 | -0.030159 |  | NORTH |  | 718 | WHTSBRSW | NORTH
353 | 12424 | FPLEFR2S_G | 4 | ONCOR ED | YES | 0.003135 | 415 | 191 | 415 | 0 | 1 |  | 124244 | n | [7 empty] | 353 | 48672 | FTR_GT2_ | 2 | NORTH | 152.6 | -0.030159 |  | NORTH |  | 722 | JORDAN | NORTH
354 | 12440 | PARKD_1SVC8 | 1 | ONCOR ED | YES | 0.002536 | 0 | 0 | 0 | 0 | 1.007 |  | 124401 | n | [7 empty] | 354 | 48673 | FTR_GT3_ | 3 | NORTH | 147.8 | -0.030159 |  | NORTH |  | 724 | SMS SW | WEST
355 | 12449 | PARKD_2SVC8 | 1 | ONCOR ED | YES | 0.002536 | 0 | 0 | 0 | 0 | 1.007 |  | 124491 | n | [7 empty] | 355 | 48674 | FTR_CN4_ | 4 | NORTH | 371.8 | -0.030159 |  | NORTH |  | 725 | SIVLSBND | NORTH
356 | 13116 | TGATEWAY_1G | 1 | ONCOR ED | YES | 0.006526 | 151 | 30 | 151 | 0 | 1.0232 |  | 131161 | n | [7 empty] | 356 | 48690 | GBY_GN5_ | 5 | HOUSTON | 0 | -0.029897 |  | HOUSTON |  | 726 | GAINESVI | NORTH
357 | 13117 | TGATEWAY_2G | 2 | ONCOR ED | YES | 0.006526 | 130 | 30 | 130 | 0 | 1.0232 |  | 131172 | n | [7 empty] | 357 | 48691 | GBY_7374 | A | HOUSTON | 0 | -0.030103 |  | HOUSTON |  | 727 | SIVELSBE | NORTH
358 | 13118 | TGATEWAY_3G | 3 | ONCOR ED | YES | 0.006526 | 148 | 30 | 148 | 0 | 1.0232 |  | 131183 | n | [7 empty] | 358 | 48691 | GBY_7374 | B | HOUSTON | 0 | -0.030103 |  | HOUSTON |  | 728 | WOLFRIDG | NORTH
359 | 13119 | TGATEWAY_4G | 4 | ONCOR ED | YES | 0.006526 | 399 | 65 | 399 | 0 | 1.0232 |  | 131194 | n | [7 empty] | 359 | 48692 | GBY_8182 | C | HOUSTON | 0 | -0.030103 |  | HOUSTON |  | 729 | SCURRYSW | WEST
360 | 13131 | CALFREST_1G | 1 | ONCOR ED | YES | 0.011428 | 150.7 | 40 | 150.7 | 0 | 1.031 |  | 131311 | n | [7 empty] | 360 | 48692 | GBY_8182 | D | HOUSTON | 0 | -0.030103 |  | HOUSTON |  | 730 | WOLFRIDG | NORTH
361 | 13132 | CALFREST_2G | 2 | ONCOR ED | YES | 0.011428 | 151 | 57 | 151 | 0 | 1.031 |  | 131322 | n | [7 empty] | 361 | 48693 | GBY_8384 | E | HOUSTON | 0 | -0.030103 |  | HOUSTON |  | 731 | HENRY | WEST
362 | 13133 | CALFREST_3G | 3 | ONCOR ED | YES | 0.011428 | 177.4 | 40 | 177.4 | 0 | 1.031 |  | 131333 | n | [7 empty] | 362 | 48693 | GBY_8384 | F | HOUSTON | 0 | -0.030103 |  | HOUSTON |  | 732 | BRYSON | NORTH
363 | 13134 | CALFREST_4G | 4 | ONCOR ED | YES | 0.011224 | 151.5 | 40 | 151.5 | 0 | 1.031 |  | 131344 | n | [7 empty] | 363 | 48731 | CBE_GT1 | 1 | HOUSTON | 76 | 0.033996 |  | HOUSTON | 0 | 733 | PADUCAH | WEST
364 | 13135 | CALFREST_5G | 5 | ONCOR ED | YES | 0.011224 | 152.3 | 57 | 152.3 | 0 | 1.031 |  | 131355 | n | [7 empty] | 364 | 48732 | CBE_GT2 | 1 | HOUSTON | 76 | 0.033996 |  | HOUSTON | 0 | 734 | MCADAMS | WEST
365 | 13136 | CALFREST_6G | 6 | ONCOR ED | YES | 0.011224 | 177.5 | 40 | 177.5 | 0 | 1.031 |  | 131366 | n | [7 empty] | 365 | 48733 | CBE_ST12 | 1 | HOUSTON | 105 | 0.033996 |  | HOUSTON | 0 | 735 | REDRIVER | NORTH
366 | 13432 | SANDOW_5G | 5 | ONCOR ED | YES | -0.072656 | 581 | 225 | 581 |  | 1.029 |  | 134325 | y | [7 empty] | 366 | 48734 | CBE_GT3 | 1 | HOUSTON | 76 | 0.033996 |  | HOUSTON | 0 | 736 | LIBERTY | WEST
367 | 32798 | BRYN_TAMUGEN | 1 | BRYN_TSP | YES | 0.040156 | 32 | 0 | 32 |  | 1.02 |  | 327981 | y | [7 empty] | 367 | 48735 | CBE_GT4 | 1 | HOUSTON | 76 | 0.033996 |  | HOUSTON | 0 | 737 | SMS | WEST
368 | 32883 | BRYN_DNSBY3 | 1 | BRYN_TSP | YES | 0.035069 | 0 | 2 | 48 |  | 1.015 |  | 328831 | n | [7 empty] | 368 | 48736 | CBE_ST34 | 1 | HOUSTON | 105 | 0.033996 |  | HOUSTON | 0 | 738 | SINCLAIR | NORTH
369 | 32884 | BRYN_DNSBY13 | 1 | BRYN_TSP | YES | 0.035069 | 46 | 2 | 46 | 0 | 1.015 |  | 328841 | n | [7 empty] | 369 | 48740 | PSG_GN2_ | 1 | HOUSTON | 180 | -0.028999 |  | HOUSTON |  | 739 | CHILDRES | WEST
370 | 32886 | BRYN_ATKINS3 | MB | BRYN_TSP | YES | 0.038428 | 0 | 5 | 12 |  | 1 |  | 32886MB | n | [7 empty] | 370 | 48741 | PSG_GT2_ | 1 | HOUSTON | 170 | -0.028999 |  | HOUSTON |  | 741 | DYEMOUND | NORTH
371 | 32887 | BRYN_ATKINS6 | MB | BRYN_TSP | YES | 0.038428 | 0 | 12 | 51 |  | 1.028 |  | 32887MB | n | [7 empty] | 371 | 48742 | PSG_GT3_ | 1 | HOUSTON | 170.3 | -0.028999 |  | HOUSTON |  | 742 | SINCLAIR | NORTH
372 | 32888 | BRYN_ATKINS7 | 1 | BRYN_TSP | YES | 0.038428 | 13.6 | 4 | 17 |  | 1.028 |  | 328881 | n | [7 empty] | 372 | 48772 | PHR_GN2_ | MB | HOUSTON | 0 | -0.027873 |  | HOUSTON |  | 743 | SALTCREE | WEST
373 | 32890 | BRYN_ATKINS4 | MB | BRYN_TSP | YES | 0.038428 | 0 | 5 | 22 |  | 1.031 |  | 32890MB | n | [7 empty] | 373 | 48811 | CVC_GT3_ | 3 | HOUSTON | 179 | -0.0301 |  | HOUSTON |  | 744 | WALNUTBE | NORTH
374 | 32891 | BRYN_ATKINS5 | MB | BRYN_TSP | YES | 0.038428 | 0 | 5 | 25 |  | 1.031 |  | 32891MB | n | [7 empty] | 374 | 48812 | CVC_GT2_ | 2 | HOUSTON | 177 | -0.0301 |  | HOUSTON |  | 745 | KING | WEST
375 | 32892 | BRYN_DNSBY14 | 1 | BRYN_TSP | YES | 0.035069 | 105 | 25 | 105 | 0 | 1.035 |  | 328921 | n | [7 empty] | 375 | 48813 | CVC_GT1_ | 1 | HOUSTON | 180 | -0.0301 |  | HOUSTON |  | 746 | STJO | NORTH
376 | 36998 | RDCNYNG1 | 1 | BEPC_TSP | YES | -0.011496 | 16.8 | 0 | 84 |  | 1.01 |  | 369981 | n | [7 empty] | 376 | 48815 | CVC_GT4_ | 4 | HOUSTON | 147.1 | -0.029648 |  | HOUSTON |  | 747 | KALGARY | WEST
377 | 38332 | TNWDWRDU2_8 | 1 | TNMP_TSP | YES | -0.018459 | 20 | 0 | 80 | 0 | 1.0232 |  | 383321 | n | [7 empty] | 377 | 48841 | SJS_GT1_ | 1 | HOUSTON | 0 | -0.028665 |  | HOUSTON |  | 748 | JAYTON | WEST
378 | 38437 | TNSRBNMESA9 | 1 | TNMP_TSP | YES | -0.018507 | 37.5 | 0 | 150 | 0 | 1.02 |  | 384371 | n | [7 empty] | 378 | 48842 | SJS_GT2_ | 2 | HOUSTON | 0 | -0.028665 |  | HOUSTON |  | 749 | GLENN | WEST
379 | 38580 | TNBP_CGN1_8 | 1 | TNMP_TSP | YES | -0.21876 | 70.8 | 0 | 70.8 | 0 | 1.005 |  | 385801 | y | [7 empty] | 379 | 48851 | SRB_GN1_ | 1 | HOUSTON | 0 | -0.028901 |  | HOUSTON |  | 750 | STJO | NORTH
380 | 38590 | TNBP_CGN2_8 | 2 | TNMP_TSP | YES | -0.21876 | 66.7 | 0 | 66.7 | 0 | 1.005 |  | 385902 | y | [7 empty] | 380 | 48852 | SRB_GN2_ | 2 | HOUSTON | 0 | -0.028898 |  | HOUSTON |  | 751 | ESPUELA | WEST
381 | 38600 | TNBP_CGN3_8 | 5 | TNMP_TSP | YES | -0.21876 | 53 | 0 | 53 | 0 | 1.005 |  | 386005 | y | [7 empty] | 381 | 48853 | SRB_GN3_ | 3 | HOUSTON | 0 | -0.028892 |  | HOUSTON |  | 752 | CLAIRMON | WEST
382 | 38611 | TNBPAMCG1_8 | 1 | TNMP_TSP | YES | -0.21876 | 153.2 | 0 | 153.2 | 0 | 1.005 |  | 386111 | n | [7 empty] | 382 | 48854 | SRB_GN4_ | 4 | HOUSTON | 0 | -0.028931 |  | HOUSTON |  | 753 | BISSETT | WEST
383 | 38612 | TNBPAMCG2_8 | 2 | TNMP_TSP | YES | -0.21876 | 153.5 | 0 | 153.5 | 0 | 1.005 |  | 386122 | n | [7 empty] | 383 | 48855 | SRB_GT21 | B1 | HOUSTON | 0 | -0.028899 |  | HOUSTON |  | 754 | CAPSCORN | NORTH
384 | 38613 | TNBPAMCG3_8 | 3 | TNMP_TSP | YES | -0.21876 | 152.3 | 0 | 152.3 | 0 | 1.005 |  | 386133 | n | [7 empty] | 384 | 48855 | SRB_GT21 | B2 | HOUSTON | 0 | -0.028899 |  | HOUSTON |  | 755 | ASPERMON | WEST
385 | 38614 | TNBPAMCG4_8 | 4 | TNMP_TSP | YES | -0.21876 | 96 | 0 | 96 |  | 1.005 |  | 386144 | n | [7 empty] | 385 | 48873 | THW_ST3_ | 3 | HOUSTON | 109 | -0.030854 |  | HOUSTON |  | 756 | NOCONA | NORTH
386 | 38615 | TNBPAMCG5_8 | 1 | TNMP_TSP | YES | -0.21876 | 244 | 0 | 244 | 0 | 1.005 |  | 386151 | n | [7 empty] | 386 | 48874 | THW_ST4_ | 4 | HOUSTON | 0 | -0.030854 |  | HOUSTON |  | 757 | BUSHKNOB | WEST
387 | 38690 | TNBP_CGN4_8 | 3 | TNMP_TSP | YES | -0.21876 | 40 | 0 | 40 |  | 1.005 |  | 386903 | y | [7 empty] | 387 | 48875 | THW_3132 | A | HOUSTON | 58 | -0.030854 |  | HOUSTON |  | 758 | ALCORN | NORTH
388 | 38711 | TNTXCTY1CG8 | 1 | TNMP_TSP | YES | -0.21876 | 100.3 | 59 | 100.3 | 0 | 1 |  | 387111 | n | [7 empty] | 388 | 48875 | THW_3132 | B | HOUSTON | 57 | -0.030854 |  | HOUSTON |  | 759 | MORAN | WEST
389 | 38712 | TNTXCTY2CG8 | 1 | TNMP_TSP | YES | -0.21876 | 92.9 | 59 | 92.9 | 0 | 1 |  | 387121 | n | [7 empty] | 389 | 48877 | THW_3334 | C | HOUSTON | 57 | -0.030854 |  | HOUSTON |  | 760 | ALBANY | WEST
390 | 38713 | TNTXCTY3CG8 | 1 | TNMP_TSP | YES | -0.21876 | 102.7 | 59 | 102.7 | 0 | 1 |  | 387131 | n | [7 empty] | 390 | 48877 | THW_3334 | D | HOUSTON | 59 | -0.030854 |  | HOUSTON |  | 761 | TRUSCOTT | WEST
391 | 38714 | TNTXCTY4CG8 | 1 | TNMP_TSP | YES | -0.21876 | 103 | 59 | 103 | 0 | 1 |  | 387141 | n | [7 empty] | 391 | 48879 | THW_4142 | F | HOUSTON | 0 | -0.030854 |  | HOUSTON |  | 762 | HARDYSW | NORTH
392 | 39190 | TNSLCGN1__8 | 1 | TNMP_TSP | YES | 0 | 0 | 10 | 30 |  | 1.03 |  | 391901 | y | [7 empty] | 392 | 48879 | THW_4142 | E | HOUSTON | 0 | -0.030854 |  | HOUSTON |  | 763 | ROCHESTE | WEST
393 | 39470 | TNDOWCGNSG8 | 1 | TNMP_TSP | YES | -0.21876 | 32 | 10 | 32 | 0 | 0.985 |  | 394701 | y | [7 empty] | 393 | 48881 | THW_4344 | H | HOUSTON | 0 | -0.030854 |  | HOUSTON |  | 764 | MUNDAY | WEST
394 | 39480 | TNDOWCGNGG8 | 1 | TNMP_TSP | YES | -0.21876 | 30 | 10 | 30 | 0 | 0.985 |  | 394801 | y | [7 empty] | 394 | 48881 | THW_4344 | G | HOUSTON | 0 | -0.030854 |  | HOUSTON |  | 765 | KNOX | WEST
395 | 39760 | TNSCLP1___8 | 1 | TNMP_TSP | YES | -0.21372 | 93.4 | 20 | 116.8 | 0 | 1.04 |  | 397601 | n | [7 empty] | 395 | 48883 | THW_GT1_ | B2 | HOUSTON | 0 | -0.03036 |  | HOUSTON |  | 766 | HARDY | NORTH
396 | 39770 | TNSCLP2___8 | 1 | TNMP_TSP | YES | -0.21372 | 91.6 | 20 | 114.5 | 0 | 1.04 |  | 397701 | n | [7 empty] | 396 | 48885 | THW_5152 | B | HOUSTON | 0 | -0.03003 |  | HOUSTON |  | 767 | HENRIETA | NORTH
397 | 39775 | TNSCLP4___8 | 1 | TNMP_TSP | YES | -0.21372 | 95.2 | 20 | 119 | 0 | 1.04 |  | 397751 | n | [7 empty] | 397 | 48885 | THW_5152 | A | HOUSTON | 0 | -0.03003 |  | HOUSTON |  | 768 | JOY | NORTH
398 | 39790 | TNSCLP3___8 | 1 | TNMP_TSP | YES | -0.21372 | 87.6 | 20 | 109.5 | 0 | 1.027 |  | 397901 | n | [7 empty] | 398 | 48886 | THW_5354 | C | HOUSTON | 0 | -0.03003 |  | HOUSTON |  | 769 | POSTOAKS | NORTH
399 | 39960 | TNTNPONE_18 | 1 | TNMP_TSP | YES | 0.031819 | 152.3 | 30 | 152.3 |  | 1.04 |  | 399601 | y | [7 empty] | 399 | 48886 | THW_5354 | D | HOUSTON | 0 | -0.03003 |  | HOUSTON |  | 770 | ARROWHEA | NORTH
400 | 39970 | TNTNPONE_28 | 1 | TNMP_TSP | YES | 0.031819 | 153 | 30 | 153 |  | 1.04 |  | 399701 | y | [7 empty] | 400 | 48887 | THW_5556 | E | HOUSTON | 0 | -0.03003 |  | HOUSTON |  | 771 | POSTOAK | NORTH
401 | 48500 | APD_GT1_8005 | 1 | CNP_TSP | YES | -0.21777 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 |  | 485001 | y | [7 empty] | 401 | 48887 | THW_5556 | F | HOUSTON | 0 | -0.03003 |  | HOUSTON |  | 772 | SHANNON | NORTH
402 | 48510 | AK_GT1__8040 | 1 | CNP_TSP | YES | -0.21733 | 33.4 | 8.1 | 34 |  | 1.0254 |  | 485101 | y | [7 empty] | 402 | 48911 | TGF_GT1_ | 1 | HOUSTON | 59.5 | 0.011062 |  | HOUSTON | 0 | 773 | SCOTLAND | NORTH
403 | 48511 | LPE_GT1_8070 | 1 | CNP_TSP | YES | -0.21561 | 42 | 0 | 42 | 0 | 1.0362 |  | 485111 | n | [7 empty] | 403 | 48921 | WAP_GN1_ | 1 | HOUSTON | 0 | -0.028481 |  | HOUSTON |  | 774 | KATZP | WEST
404 | 48512 | LPE_GT2_8075 | 2 | CNP_TSP | YES | -0.21561 | 42 | 0 | 42 | 0 | 1.0362 |  | 485122 | n | [7 empty] | 404 | 48922 | WAP_GN2_ | 2 | HOUSTON | 0 | -0.028481 |  | HOUSTON |  | 775 | LANHAM | NORTH
405 | 48513 | LPE_GT3_8080 | 3 | CNP_TSP | YES | -0.21561 | 39 | 0 | 39 | 0 | 1.0362 |  | 485133 | n | [7 empty] | 405 | 48923 | WAP_GN3_ | 3 | HOUSTON | 226.3 | -0.028481 |  | HOUSTON |  | 776 | BRIDWELL | NORTH
406 | 48514 | LPE_GT4_8085 | 4 | CNP_TSP | YES | -0.21561 | 39 | 0 | 39 | 0 | 1.0362 |  | 485144 | n | [7 empty] | 406 | 48924 | WAP_GN4_ | 4 | HOUSTON | 481 | -0.028481 |  | HOUSTON |  | 777 | GOREE | WEST
407 | 48520 | BSF_GT1_8070 | 1 | CNP_TSP | YES | -0.21166 | 72 | 0 | 72 | 0 | 1.0326 |  | 485201 | y | [7 empty] | 407 | 48929 | WAPGT21_ | B1 | HOUSTON | 0 | -0.028481 |  | HOUSTON |  | 778 | GILLESPI | WEST
408 | 48520 | BSF_GT1_8070 | 2 | CNP_TSP | YES | -0.21166 | 10 | 0 | 10 | 0 | 1.0326 |  | 485202 | y | [7 empty] | 408 | 60000 | DSKY2 | 1 | WEST | 19.1 | 0.001944 |  | WEST | 0 | 779 | SEYMOUR | NORTH
409 | 48521 | BVE_GT1_GT1 | 1 | CNP_TSP | YES | -0.22422 | 167.7 | 0 | 167.7 |  | 1.035 |  | 485211 | n | [7 empty] | 409 | 60003 | KING_NE1 | 1 | WEST | 20 | 0.001885 |  | WEST | 0 | 780 | ELBERT | NORTH
410 | 48522 | BVE_GT2_5035 | 2 | CNP_TSP | YES | -0.22422 | 166.4 | 0 | 166.4 |  | 1.035 |  | 485222 | n | [7 empty] | 410 | 60005 | KING_SE1 | 1 | WEST | 10 | 0.001885 |  | WEST | 0 | 781 | ELBERTSW | NORTH
411 | 48523 | BVE_ST1_GN1 | 3 | CNP_TSP | YES | -0.22422 | 252.4 | 0 | 252.4 |  | 1.035 |  | 485233 | n | [7 empty] | 411 | 60007 | KING_SW1 | 1 | WEST | 20 | 0.001829 |  | WEST | 0 | 782 | LAKEKEMP | NORTH
412 | 48531 | BYU_GT1_8075 | 1 | CNP_TSP | YES | -0.21654 | 65 | 0 | 65 |  | 1.0362 |  | 485311 | n | [7 empty] | 412 | 60016 | WOODWRD1 | 1 | WEST | 20 | 0.001868 |  | WEST | 0 | 783 | LAKEKEMP | NORTH
413 | 48532 | BYU_GT2_8055 | 2 | CNP_TSP | YES | -0.21654 | 62 | 0 | 62 |  | 1.0362 |  | 485322 | n | [7 empty] | 413 | 60017 | ORNNWP1 | 1 | WEST | 20 | 0.001977 |  | WEST | 0 | 784 | WESTOVER | NORTH
414 | 48533 | BYU_GT3_8060 | 3 | CNP_TSP | YES | -0.21654 | 67 | 0 | 67 |  | 1.0362 |  | 485333 | n | [7 empty] | 414 | 60018 | DSKY1 | 1 | WEST | 21 | 0.002012 |  | WEST | 0 | 785 | ORAN | NORTH
415 | 48534 | BYU_GT4_8065 | 4 | CNP_TSP | YES | -0.21654 | 65 | 0 | 65 |  | 1.0362 |  | 485344 | n | [7 empty] | 415 | 60019 | KING_NW1 | 1 | WEST | 20 | 0.001829 |  | WEST | 0 | 786 | BOMARTON | WEST
416 | 48551 | CAL_GT1_8045 | 1 | CNP_TSP | YES | -0.2158 | 149 | 0 | 149 | 0 | 1.0326 |  | 485511 | y | [7 empty] | 416 | 60057 | CALLAHAN | 1 | WEST | 22.8 | 0.001527 |  | WEST | 0 | 787 | OLNEY8 | NORTH
417 | 48552 | CAL_ST1_8000 | 2 | CNP_TSP | YES | -0.2158 | 65.1 | 0 | 65.1 | 0 | 1.0326 |  | 485522 | y | [7 empty] | 417 | 60058 | BUFF_GAP | 1 | WEST | 24 | 0.001275 |  | WEST | 0 | 788 | OLNEY9 | NORTH
418 | 48561 | CTL_GT2_8130 | 1 | CNP_TSP | YES | -0.21708 | 73.5 | 30.3 | 91.9 |  | 1.029 |  | 485611 | y | [7 empty] | 418 | 60060 | CIRELLO | 1 | WEST | 46.6 | 0.001275 |  | WEST | 0 | 789 | SEYMORMP | NORTH
419 | 48562 | CTL_GT3_8135 | 2 | CNP_TSP | YES | -0.21708 | 70.1 | 30.3 | 87.6 |  | 1.029 |  | 485622 | y | [7 empty] | 419 | 60063 | BUFF_GAP | 1 | WEST | 34 | 0.001275 |  | WEST | 0 | 790 | BENJAMIN | WEST
420 | 48563 | CTL_GT4_8140 | 3 | CNP_TSP | YES | -0.21708 | 69.6 | 30.3 | 87 |  | 1.029 |  | 485633 | y | [7 empty] | 420 | 60066 | H_HOLLOW | 1 | WEST | 44.4 | 0.001275 |  | WEST | 0 | 791 | JEAN | NORTH
421 | 48564 | CTL_GN1_8145 | 4 | CNP_TSP | YES | -0.21708 | 43.6 | 12.9 | 54.5 |  | 1.029 |  | 485644 | y | [7 empty] | 421 | 60068 | HHOLLOW2 | 1 | WEST | 36.8 | 0.001275 |  | WEST | 0 | 792 | MURRAY | NORTH
422 | 48565 | CTL_GN2_8155 | 5 | CNP_TSP | YES | -0.21708 | 9.8 | 3.4 | 12.2 |  | 1.029 |  | 485655 | y | [7 empty] | 422 | 60070 | HHOLLOW3 | 1 | WEST | 44.8 | 0.001275 |  | WEST | 0 | 794 | JACKSBOR | NORTH
423 | 48581 | CBY_GN1_1 | 1 | CNP_TSP | YES | -0.21506 | 595.2 | 108 | 744 | 0 | 1.0435 |  | 485811 | n | [7 empty] | 423 | 60072 | HHOLLOW4 | 1 | WEST | 23 | 0.001275 |  | WEST | 0 | 795 | STHBENDS | NORTH
424 | 48582 | CBY_GN2_2 | 2 | CNP_TSP | YES | -0.21534 | 596.8 | 110 | 746 | 0 | 1.0435 |  | 485822 | n | [7 empty] | 424 | 60081 | WHRLWIND | 1 | WEST | 12 | 0.001208 |  | WEST | 0 | 796 | SOUTHBEN | NORTH
425 | 48583 | CBY_GT4_1 | 1 | CNP_TSP | YES | -0.21544 | 172 | 0 | 172 | 0 | 1.0261 |  | 485831 | n | [7 empty] | 425 | 60201 | RIO DRCS | F | WEST | 0 | 0.001858 |  | WEST | 0 | 797 | MARKLEY | NORTH
426 | 48584 | CBY_GT4_2 | 2 | CNP_TSP | YES | -0.21544 | 172 | 0 | 172 | 0 | 1.0261 |  | 485842 | n | [7 empty] | 426 | 60202 | FRNDDRCS | F | WEST | 0 | 0.002714 |  | WEST | 0 | 800 | APOLLO_9 | NORTH
427 | 48585 | CBY_ST4_1 | 3 | CNP_TSP | YES | -0.21544 | 172 | 0 | 172 | 0 | 1.0261 |  | 485853 | n | [7 empty] | 427 | 71051 | L_BITTCR | W1 | WEST | 7.5 | 0.001208 |  | WEST | 0 | 801 | KRAFTTAP | NORTH
428 | 48591 | CHE_GT2_5030 | 2 | CNP_TSP | YES | -0.19975 | 173 | 50 | 173 | 0 | 1.029 |  | 485912 | n | [7 empty] | 428 | 71054 | L_SWEETW | W1 | WEST | 21.5 | 0.001208 |  | WEST | 0 | 802 | APOLLO | NORTH
429 | 48593 | CHE_GT1_8015 | 1 | CNP_TSP | YES | -0.21728 | 173 | 50 | 173 | 0 | 1.0362 |  | 485931 | y | [7 empty] | 429 | 71057 | L_SWEETW | W1 | WEST | 27 | 0.001208 |  | WEST | 0 | 803 | COLLEGE9 | NORTH
430 | 48594 | CHE_GN4_8025 | 4 | CNP_TSP | YES | -0.21728 | 142 | 60 | 142 | 0 | 1.0362 |  | 485944 | n | [7 empty] | 430 | 71059 | L_SWEETW | W1 | WEST | 23.8 | 0.001208 |  | WEST | 0 | 804 | RAYTHEON | NORTH
431 | 48595 | BTE_GT2_8075 | 1 | CNP_TSP | YES | -0.21351 | 162.8 | 130 | 162.8 | 0 | 1.0261 |  | 485951 | y | [7 empty] | 431 | 71060 | L_SWEETW | W1 | WEST | 21 | 0.001208 |  | WEST | 0 | 805 | FAIRDALE | NORTH
432 | 48596 | BTE_GT3_8045 | 2 | CNP_TSP | YES | -0.21351 | 161.4 | 130 | 161.4 | 0 | 1.0261 |  | 485962 | y | [7 empty] | 432 | 71061 | L_SWEETW | W1 | WEST | 16.1 | 0.001208 |  | WEST | 0 | 806 | JUPITER | NORTH
433 | 48597 | BTE_GT4_8055 | 3 | CNP_TSP | YES | -0.21351 | 158.9 | 130 | 158.9 | 0 | 1.0261 |  | 485973 | y | [7 empty] | 433 | 76031 | L_GASCCR | W1 | WEST | 30 | 0.001359 |  | WEST | 0 | 807 | PRAXAIR | NORTH
434 | 48598 | BTE_ST1_8070 | 4 | CNP_TSP | YES | -0.21351 | 269.2 | 60 | 269.2 | 0 | 1.0261 |  | 485984 | y | [7 empty] | 434 | 76091 | L_DIVIDE | W1 | WEST | 22.5 | 0.001379 |  | WEST | 0 | 808 | PLASTIPA | NORTH
435 | 48611 | DIB_GT1_8080 | 1 | CNP_TSP | YES | -0.21577 | 64 | 0 | 64 |  | 1.0326 |  | 486111 | y | [7 empty] | 435 | 76095 | L_CAPRSI | W1 | WEST | 29.9 | 0.001379 |  | WEST | 0 | 809 | OAKLAND | NORTH
436 | 48612 | DIB_GT2_8075 | 2 | CNP_TSP | YES | -0.21577 | 63.2 | 0 | 63.2 |  | 1.0326 |  | 486122 | y | [7 empty] | 436 | 76096 | L_CAPRSI | W1 | WEST | 37.2 | 0.001379 |  | WEST | 0 | 810 | CENTRVIL | NORTH
437 | 48613 | DIB_ST1_8085 | 3 | CNP_TSP | YES | -0.21577 | 67.9 | 30 | 82.6 |  | 1.0326 |  | 486133 | y | [7 empty] | 437 | 76097 | L_CAPRGE | W1 | WEST | 42.9 | 0.001379 |  | WEST | 0 | 812 | SWINDELL | NORTH
438 | 48614 | DIB_GT3_8090 | 4 | CNP_TSP | YES | -0.21577 | 73.6 | 15 | 73.6 |  | 1.0326 |  | 486144 | y | [7 empty] | 438 | 80003 | MILHWYS | F | SOUTH | 0 | 0.009126 |  | SOUTH | 0 | 813 | WYNNJOYC | NORTH
439 | 48641 | DPEC_GT15040 | 1 | CNP_TSP | YES | -0.21652 | 163.2 | 98 | 163.2 | 0 | 1.0319 |  | 486411 | n | [7 empty] | 439 | 80012 | LAR | F | SOUTH | 0 | 0.010751 |  | SOUTH | 0 | 814 | NEWMAN9 | NORTH
440 | 48642 | DPEC_GT25025 | 2 | CNP_TSP | YES | -0.21652 | 157.1 | 98 | 157.1 | 0 | 1.0319 |  | 486422 | n | [7 empty] | 440 | 80080 | GWINDT11 | 2 | SOUTH | 0 | 0.009098 |  | SOUTH | 0 | 815 | LAWLERT | NORTH
441 | 48643 | DPEC_GT35010 | 3 | CNP_TSP | YES | -0.21652 | 157.5 | 98 | 157.5 | 0 | 1.0319 |  | 486433 | n | [7 empty] | 441 | 80080 | GWINDT11 | 4 | SOUTH | 8.5 | 0.009098 |  | SOUTH | 0 | 816 | OLINGER_ | NORTH
442 | 48644 | DPEC_GT45070 | 4 | CNP_TSP | YES | -0.21652 | 157 | 98 | 157 | 0 | 1.0319 |  | 486444 | n | [7 empty] | 442 | 80080 | GWINDT11 | 3 | SOUTH | 16.9 | 0.009098 |  | SOUTH | 0 | 817 | ROSEHILL | NORTH
443 | 48645 | DPEC_ST55065 | 5 | CNP_TSP | YES | -0.21652 | 282 | 0 | 282 | 0 | 1.0319 |  | 486455 | n | [7 empty] | 443 | 80080 | GWINDT11 | 1 | SOUTH | 41.9 | 0.009098 |  | SOUTH | 0 | 818 | OLINGER | NORTH
444 | 48651 | EP_1_2 | 1 | CNP_TSP | YES | -0.21456 | 4 | 0 | 5 | 0 | 1.0362 |  | 486511 | y | [7 empty] | 444 | 80081 | GWINDT21 | 3 | SOUTH | 19.1 | 0.009098 |  | SOUTH | 0 | 819 | LYONS | NORTH
445 | 48651 | EP_1_2 | 2 | CNP_TSP | YES | -0.21456 | 17.7 | 10 | 21 | 0 | 1.0362 |  | 486512 | y | [7 empty] | 445 | 80081 | GWINDT21 | 4 | SOUTH | 9.8 | 0.009098 |  | SOUTH | 0 | 820 | LAWLER | NORTH
446 | 48671 | FTR_GT1_5105 | 1 | CNP_TSP | YES | 0.037011 | 154.2 | 0 | 154.2 | 0 | 1.0319 |  | 486711 | n | [7 empty] | 446 | 80081 | GWINDT21 | 1 | SOUTH | 41.9 | 0.009098 |  | SOUTH | 0 | 821 | FIREWHEE | NORTH
447 | 48672 | FTR_GT2_5110 | 2 | CNP_TSP | YES | 0.037011 | 159 | 0 | 159 | 0 | 1.0319 |  | 486722 | n | [7 empty] | 447 | 80081 | GWINDT21 | 2 | SOUTH | 16 | 0.009098 |  | SOUTH | 0 | 822 | PRAXAIRT | NORTH
448 | 48673 | FTR_GT3_5085 | 3 | CNP_TSP | YES | 0.037011 | 158 | 0 | 158 | 0 | 1.0319 |  | 486733 | n | [7 empty] | 448 | 80180 | PNSCALT1 | 1 | SOUTH | 65 | 0.009098 |  | SOUTH | 0 | 823 | WALNUT | NORTH
449 | 48674 | FTR_CN4_5095 | 4 | CNP_TSP | YES | 0.037011 | 380 | 0 | 380 | 0 | 1.0319 |  | 486744 | n | [7 empty] | 449 | 80180 | PNSCALT1 | 2 | SOUTH | 22.3 | 0.009098 |  | SOUTH | 0 | 825 | NAAMAN | NORTH
450 | 48690 | GBY_GN5_5 | 5 | CNP_TSP | YES | -0.21065 | 398 | 81 | 398 |  | 1.029 |  | 486905 | n | [7 empty] | 450 | 80181 | PNSCALT2 | 1 | SOUTH | 24.5 | 0.009098 |  | SOUTH | 0 | 826 | CASTLE_D | NORTH
451 | 48691 | GBY_73741085 | A | CNP_TSP | YES | -0.23035 | 37.6 | 20 | 47 | 0 | 1.0362 |  | 48691A | n | [7 empty] | 451 | 80181 | PNSCALT2 | 2 | SOUTH | 22.3 | 0.009098 |  | SOUTH | 0 | 827 | BRAND | NORTH
452 | 48691 | GBY_73741085 | B | CNP_TSP | YES | -0.23035 | 37.6 | 20 | 47 | 0 | 1.0362 |  | 48691B | n | [7 empty] | 452 | 80265 | LARECU40 | 4 | SOUTH | 87.1 | 0.010752 |  | SOUTH | 0 | 829 | COLLEGE8 | NORTH
453 | 48692 | GBY_81821075 | C | CNP_TSP | YES | -0.23035 | 37.6 | 20 | 47 | 0 | 1.0362 |  | 48692C | n | [7 empty] | 453 | 80266 | LARECU50 | 5 | SOUTH | 87.1 | 0.010752 |  | SOUTH | 0 | 830 | SHILOH | NORTH
454 | 48692 | GBY_81821075 | D | CNP_TSP | YES | -0.23035 | 44 | 20 | 55 | 0 | 1.0362 |  | 48692D | n | [7 empty] | 454 | 88198 | BEEVILLE | F | SOUTH | 0 | 0.012415 |  | SOUTH | 0 | 831 | OATES | NORTH
455 | 48693 | GBY_83841065 | E | CNP_TSP | YES | -0.23035 | 45.6 | 20 | 57 | 0 | 1.0362 |  | 48693E | n | [7 empty] | 455 | 88253 | HAMILTON | F | SOUTH | 0 | 0.009684 |  | SOUTH | 0 | 832 | MCCREE9 | NORTH
456 | 48693 | GBY_83841065 | F | CNP_TSP | YES | -0.23035 | 43.2 | 20 | 54 | 0 | 1.0362 |  | 48693F | n | [7 empty] | 456 | 88299 | ZAPATA | F | SOUTH | 0 | 0.010121 |  | SOUTH | 0 | 834 | MCCREE8 | NORTH
457 | 48721 | LEG_1___1 | 1 | CNP_TSP | YES | 0.024248 | 827 | 357 | 827 | 0 | 1.0348 |  | 487211 | y | [7 empty] | 457 | 88508 | FALFURRI | F | SOUTH | 0 | 0.009585 |  | SOUTH | 0 | 836 | KRAFT | NORTH
458 | 48722 | LEG_2___2 | 2 | CNP_TSP | YES | 0.024248 | 819 | 357 | 819 | 0 | 1.0348 |  | 487222 | y | [7 empty] | 458 | 80265 | LARECU40A | 4 | SOUTH | 80 | 0.045218 |  | SOUTH | 0 | 837 | NEWMAN_G | NORTH
459 | 48730 | MNS_GT | 1 | CNP_TSP | YES | -0.21698 | 43 | 0 | 46.1 |  | 1.0254 |  | 487301 | y | [7 empty] | 459 | 80266 | LARECU50A | 5 | SOUTH | 80 | 0.045218 |  | SOUTH | 0 | 842 | OLINGER_ | NORTH
460 | 48731 | CBE_GT1 | 1 | CNP_TSP | YES | -0.19435 | 76 | 0 | 76 | 0 | 1.029 |  | 487311 | n | [7 empty] | 460 | 88198 | BEEVILLE | F | SOUTH | 0 | 0.031171 |  | SOUTH | 0 | 843 | OLINGER_ | NORTH
461 | 48732 | CBE_GT2 | 1 | CNP_TSP | YES | -0.19435 | 76 | 0 | 76 | 0 | 1.029 |  | 487321 | n | [7 empty] | 461 | 88253 | HAMILTON | F | SOUTH | 0 | 0.13188 |  | SOUTH | 0 | 844 | OLINGER_ | NORTH
462 | 48733 | CBE_ST12 | 1 | CNP_TSP | YES | -0.19435 | 105 | 0 | 105 | 0 | 1.029 |  | 487331 | n | [7 empty] | 462 | 88299 | ZAPATA | F | SOUTH | 0 | 0.039663 |  | SOUTH | 0 | 845 | OLINGER_ | NORTH
463 | 48734 | CBE_GT3 | 1 | CNP_TSP | YES | -0.19435 | 76 | 0 | 76 | 0 | 1.029 |  | 487341 | n | [7 empty] | 463 | 88508 | FALFURRI | F | SOUTH | 0 | 0.033621 |  | SOUTH | 0 | 848 | MARQUIS | NORTH
464 | 48735 | CBE_GT4 | 1 | CNP_TSP | YES | -0.19435 | 76 | 0 | 76 | 0 | 1.029 |  | 487351 | n | [15 empty] | #N/A |  | 849 | NEWMAN8 | NORTH
465 | 48736 | CBE_ST34 | 1 | CNP_TSP | YES | -0.19435 | 105 | 0 | 105 | 0 | 1.029 |  | 487361 | n | [15 empty] | #N/A |  | 850 | CRIST | NORTH
466 | 48740 | PSG_GN2_8050 | 1 | CNP_TSP | YES | -0.21579 | 182 | 60 | 182 |  | 1.0326 |  | 487401 | n | [15 empty] | #N/A |  | 852 | MARQUIS9 | NORTH
467 | 48741 | PSG_GT2_8040 | 1 | CNP_TSP | YES | -0.21579 | 158.6 | 50 | 158.6 |  | 1.0326 |  | 487411 | n | [15 empty] | #N/A |  | 853 | GPLTEMP | NORTH
468 | 48742 | PSG_GT3_8060 | 1 | CNP_TSP | YES | -0.21579 | 157 | 50 | 157 |  | 1.0326 |  | 487421 | n | [15 empty] | #N/A |  | 855 | ELMGROVE | NORTH
469 | 48761 | PR_GT1__9040 | 1 | CNP_TSP | YES | -0.21632 | 26 | 0 | 35 |  | 1 |  | 487611 | y | [15 empty] | #N/A |  | 901 | WOODROW6 | NORTH
470 | 48772 | PHR_GN2_2 | MB | CNP_TSP | YES | -0.21745 | 0 | 72 | 459 |  | 1.0362 |  | 48772MB | n | [15 empty] | #N/A |  | 902 | POLES315 | NORTH
471 | 48791 | PSA_GT1_8160 | 1 | CNP_TSP | YES | -0.21207 | 52 | 20.8 | 65 | 0 | 1.0362 |  | 487911 | y | [15 empty] | #N/A |  | 903 | POLE_SP1 | NORTH
472 | 48792 | PSA_GT2_8155 | 2 | CNP_TSP | YES | -0.21207 | 52.8 | 20.3 | 66 | 0 | 1.0362 |  | 487922 | y | [15 empty] | #N/A |  | 904 | POLESPL2 | NORTH
473 | 48793 | PSA_GT3_8150 | 3 | CNP_TSP | YES | -0.21207 | 56 | 20.3 | 70 | 0 | 1.0362 |  | 487933 | y | [15 empty] | #N/A |  | 908 | SPNCR_SW | NORTH
474 | 48794 | PSA_GT4_8145 | 4 | CNP_TSP | YES | -0.21207 | 52.8 | 20.3 | 66 | 0 | 1.0362 |  | 487944 | y | [15 empty] | #N/A |  | 909 | KINGSROW | NORTH
475 | 48795 | PSA_GT5_8140 | 5 | CNP_TSP | YES | -0.21207 | 51.2 | 20.3 | 64 | 0 | 1.0362 |  | 487955 | y | [15 empty] | #N/A |  | 910 | HICKORY6 | NORTH
476 | 48796 | PSA_GN1_8165 | 1 | CNP_TSP | YES | -0.21207 | 83.2 | 43.1 | 104 | 0 | 1.0362 |  | 487961 | y | [15 empty] | #N/A |  | 911 | DENARCO1 | NORTH
477 | 48797 | PSA_GT6_8135 | 6 | CNP_TSP | YES | -0.21207 | 47.2 | 34.5 | 59 | 0 | 1.0362 |  | 487976 | y | [15 empty] | #N/A |  | 912 | N_DENT69 | NORTH
478 | 48811 | CVC_GT3_5045 | 3 | CNP_TSP | YES | -0.19975 | 156 | 91.8 | 156 | 0 | 1.029 |  | 488113 | n | [15 empty] | #N/A |  | 913 | INDSTRL1 | NORTH
479 | 48812 | CVC_GT2_5020 | 2 | CNP_TSP | YES | -0.19975 | 158 | 91.8 | 158 | 0 | 1.029 |  | 488122 | n | [15 empty] | #N/A |  | 914 | LOCUST69 | NORTH
480 | 48813 | CVC_GT1_5035 | 1 | CNP_TSP | YES | -0.19975 | 160 | 91.8 | 160 | 0 | 1.029 |  | 488131 | n | [15 empty] | #N/A |  | 915 | NLAKES69 | NORTH
481 | 48814 | CVC_ST5_5040 | 1 | CNP_TSP | YES | -0.19975 | 162 | 91.8 | 162 | 0 | 1.029 |  | 488141 | y | [15 empty] | #N/A |  | 916 | JMCRSTL1 | NORTH
482 | 48815 | CVC_GT4_8005 | 4 | CNP_TSP | YES | -0.21182 | 165 | 91.8 | 165 |  | 1.0362 |  | 488154 | n | [15 empty] | #N/A |  | 917 | POCKRUS1 | NORTH
483 | 48820 | SHELLG1_3015 | 1 | CNP_TSP | YES | -0.21573 | 71 | 34.5 | 71 |  | 1.029 |  | 488201 | y | [15 empty] | #N/A |  | 918 | TEASLEY1 | NORTH
484 | 48821 | SHELLG2 | 2 | CNP_TSP | YES | -0.21573 | 72 | 34.5 | 72 |  | 1.029 |  | 488212 | y | [15 empty] | #N/A |  | 920 | SPNCRGEN | NORTH
485 | 48822 | SHELLG3_3020 | 1 | CNP_TSP | YES | -0.21573 | 39 | 0 | 39 |  | 1.029 |  | 488221 | y | [15 empty] | #N/A |  | 923 | SPENCER_ | NORTH
486 | 48822 | SHELLG3_3020 | 2 | CNP_TSP | YES | -0.21573 | 30 | 0 | 30 |  | 1.029 |  | 488222 | y | [15 empty] | #N/A |  | 924 | SPENCER_ | NORTH
487 | 48841 | SJS_GT1_GT1 | 1 | CNP_TSP | YES | -0.21591 | 78 | 49 | 78 | 0 | 1.0362 |  | 488411 | n | [15 empty] | #N/A |  | 930 | RDWELLS1 | NORTH
488 | 48842 | SJS_GT2_GT2 | 2 | CNP_TSP | YES | -0.21591 | 81 | 49 | 81 | 0 | 1.0362 |  | 488422 | n | [15 empty] | #N/A |  | 932 | RDWELLS6 | NORTH
489 | 48845 | SOL_GT1 | 1 | CNP_TSP | YES | -0.21577 | 16.2 | 15.4 | 16.2 |  | 1.0326 |  | 488451 | y | [15 empty] | #N/A |  | 936 | DIESEL_D | NORTH
490 | 48851 | SRB_GN1_1 | 1 | CNP_TSP | YES | -0.21584 | 165 | 26 | 165 | 0 | 1.0217 |  | 488511 | n | [15 empty] | #N/A |  | 937 | STEAM_D | NORTH
491 | 48852 | SRB_GN2_2 | 2 | CNP_TSP | YES | -0.21586 | 176 | 26 | 176 | 0 | 1.0217 |  | 488522 | n | [15 empty] | #N/A |  | 938 | LTV_D | NORTH
492 | 48853 | SRB_GN3_3 | 3 | CNP_TSP | YES | -0.21576 | 213 | 35 | 213 | 0 | 1.029 |  | 488533 | n | [15 empty] | #N/A |  | 939 | TERREL_D | NORTH
493 | 48854 | SRB_GN4_4 | 4 | CNP_TSP | YES | -0.21577 | 228 | 35 | 228 |  | 1.029 |  | 488544 | n | [15 empty] | #N/A |  | 940 | IND_PK_D | NORTH
494 | 48855 | SRB_GT211035 | B1 | CNP_TSP | YES | -0.21588 | 0 | 0 | 18 |  | 1.014 |  | 48855B1 | n | [15 empty] | #N/A |  | 945 | MAMIE_D | NORTH
495 | 48855 | SRB_GT211035 | B2 | CNP_TSP | YES | -0.21588 | 0 | 0 | 12 |  | 1.014 |  | 48855B2 | n | [15 empty] | #N/A |  | 946 | DENT_RD_ | NORTH
496 | 48873 | THW_ST3_ST_3 | 3 | CNP_TSP | YES | -0.25817 | 107 | 19 | 107 | 0 | 1.0435 |  | 488733 | n | [15 empty] | #N/A |  | 947 | ONEAL_D | NORTH
497 | 48874 | THW_ST4_ST_4 | 4 | CNP_TSP | YES | -0.25817 | 108 | 19 | 108 | 0 | 1.0435 |  | 488744 | n | [15 empty] | #N/A |  | 948 | STEAM1 | NORTH
498 | 48875 | THW_3132 | A | CNP_TSP | YES | -0.25817 | 55 | 5 | 55 | 0 | 1.0435 |  | 48875A | n | [15 empty] | #N/A |  | 949 | STEAM2 | NORTH
499 | 48875 | THW_3132 | B | CNP_TSP | YES | -0.25817 | 53 | 5 | 53 | 0 | 1.0435 |  | 48875B | n | [15 empty] | #N/A |  | 950 | STEAM3 | NORTH
500 | 48877 | THW_3334 | C | CNP_TSP | YES | -0.25817 | 55 | 5 | 55 | 0 | 1.0435 |  | 48877C | n | [15 empty] | #N/A |  | 952 | DIESELA | NORTH
501 | 48877 | THW_3334 | D | CNP_TSP | YES | -0.25817 | 57 | 5 | 57 | 0 | 1.0435 |  | 48877D | n | [15 empty] | #N/A |  | 956 | DN_STEAM | NORTH
502 | 48879 | THW_4142 | E | CNP_TSP | YES | -0.25817 | 56 | 5 | 56 | 0 | 1.0435 |  | 48879E | n | [15 empty] | #N/A |  | 957 | GREENV_I | NORTH
503 | 48879 | THW_4142 | F | CNP_TSP | YES | -0.25817 | 55 | 5 | 55 | 0 | 1.0435 |  | 48879F | n | [15 empty] | #N/A |  | 958 | GREENV_I | NORTH
504 | 48881 | THW_4344 | G | CNP_TSP | YES | -0.25817 | 58 | 5 | 58 | 0 | 1.0435 |  | 48881G | n | [15 empty] | #N/A |  | 959 | N_DENT_T | NORTH
505 | 48881 | THW_4344 | H | CNP_TSP | YES | -0.25817 | 58 | 5 | 58 | 0 | 1.0435 |  | 48881H | n | [15 empty] | #N/A |  | 960 | SHELBY1 | NORTH
506 | 48883 | THW_GT1_GT_1 | B2 | CNP_TSP | YES | -0.24952 | 0 | 0 | 12 |  | 1.043 |  | 48883B2 | n | [15 empty] | #N/A |  | 961 | SHELBY2 | NORTH
507 | 48885 | THW_5152 | A | CNP_TSP | YES | -0.28523 | 46.4 | 5 | 58 |  | 1.029 |  | 48885A | n | [15 empty] | #N/A |  | 962 | BRYAN_E_ | NORTH
508 | 48885 | THW_5152 | B | CNP_TSP | YES | -0.28523 | 47.2 | 5 | 59 |  | 1.029 |  | 48885B | n | [15 empty] | #N/A |  | 963 | SHELBY3 | NORTH
509 | 48886 | THW_5354 | C | CNP_TSP | YES | -0.28523 | 45.6 | 5 | 57 |  | 1.029 |  | 48886C | n | [15 empty] | #N/A |  | 964 | GIBN_CRE | NORTH
510 | 48886 | THW_5354 | D | CNP_TSP | YES | -0.28523 | 46.4 | 5 | 58 |  | 1.029 |  | 48886D | n | [15 empty] | #N/A |  | 965 | GIBN_CRE | NORTH
511 | 48887 | THW_5556 | E | CNP_TSP | YES | -0.28523 | 47.2 | 5 | 59 |  | 1.029 |  | 48887E | n | [15 empty] | #N/A |  | 966 | GIBN_CRE | NORTH
512 | 48887 | THW_5556 | F | CNP_TSP | YES | -0.28523 | 45.6 | 5 | 57 |  | 1.029 |  | 48887F | n | [15 empty] | #N/A |  | 967 | GIBN_CRE | NORTH
513 | 48911 | TGF_GT1_8000 | 1 | CNP_TSP | YES | -0.19835 | 69.2 | 0 | 69.2 | 0 | 1.0326 |  | 489111 | n | [15 empty] | #N/A |  | 968 | BENDAVIS | NORTH
514 | 48921 | WAP_GN1_1 | 1 | CNP_TSP | YES | -0.22396 | 166 | 37 | 166 | 0 | 1.0362 |  | 489211 | n | [15 empty] | #N/A |  | 969 | GIBN_CRE | NORTH
515 | 48922 | WAP_GN2_2 | 2 | CNP_TSP | YES | -0.22396 | 166 | 37 | 166 | 0 | 1.0362 |  | 489222 | n | [15 empty] | #N/A |  | 970 | BENDAVIS | NORTH
516 | 48923 | WAP_GN3_3 | 3 | CNP_TSP | YES | -0.22396 | 248 | 93 | 248 | 0 | 1.0362 |  | 489233 | n | [15 empty] | #N/A |  | 971 | PRUITT_8 | NORTH
517 | 48924 | WAP_GN4_4 | 4 | CNP_TSP | YES | -0.22396 | 546 | 217 | 546 | 0 | 1.0362 |  | 489244 | n | [15 empty] | #N/A |  | 972 | W_DENT_T | NORTH
518 | 48925 | WAP_GN5_5 | 5 | CNP_TSP | YES | -0.22396 | 624.7 | 278 | 654 | 0 | 0.985 |  | 489255 | y | [15 empty] | #N/A |  | 973 | MCCREE_5 | NORTH
519 | 48926 | WAP_GN6_6 | 6 | CNP_TSP | YES | -0.22412 | 651 | 280 | 651 |  | 1.035 |  | 489266 | y | [15 empty] | #N/A |  | 974 | MCCREE1_ | NORTH
520 | 48927 | WAP_GN7_7 | 7 | CNP_TSP | YES | -0.22412 | 564 | 277 | 564 |  | 1.035 |  | 489277 | y | [15 empty] | #N/A |  | 975 | JKCREEK1 | NORTH
521 | 48928 | WAP_GN8_8 | 8 | CNP_TSP | YES | -0.22412 | 603 | 275 | 603 |  | 1.035 |  | 489288 | y | [15 empty] | #N/A |  | 976 | SHELBSTR | NORTH
522 | 48929 | WAPGT21_GT1 | B1 | CNP_TSP | YES | -0.22396 | 0 | 0 | 13 |  | 1.05 |  | 48929B1 | n | [15 empty] | #N/A |  | 977 | GREENV_I | NORTH
523 | 48940 | WARVUE_GT1 | G1 | CNP_TSP | YES | -0.2148 | 12 | 0 | 12 |  | 1.0435 |  | 48940G1 | n | [15 empty] | #N/A |  | 978 | JKCREEK3 | NORTH
524 | 49803 | EXN_15GT | 1 | CNP_TSP | YES | -0.21497 | 33 | 8.3 | 34 |  | 1.0326 |  | 498031 | y | [15 empty] | #N/A |  | 979 | GREENV_I | NORTH
525 | 49804 | EXN_16GT | 2 | CNP_TSP | YES | -0.21497 | 32 | 8.3 | 34.7 |  | 1.0326 |  | 498042 | y | [15 empty] | #N/A |  | 980 | GIBN_STR | NORTH
526 | 49805 | EXN_17GT | 3 | CNP_TSP | YES | -0.21497 | 31 | 8.3 | 32.7 |  | 1.0326 |  | 498053 | y | [15 empty] | #N/A |  | 981 | SPNCRINT | NORTH
527 | 49826 | EXN938GT | 5 | CNP_TSP | YES | -0.21497 | 43 | 9.2 | 45.9 |  | 1.0326 |  | 498265 | y | [15 empty] | #N/A |  | 982 | DN_STEAM | NORTH
528 | 49828 | EXN941GT | 10 | CNP_TSP | YES | -0.21497 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 |  | 4982810 | y | [15 empty] | #N/A |  | 983 | ARCO_T_8 | NORTH
529 | 49829 | EXN942GT | 11 | CNP_TSP | YES | -0.21497 | 20 | 5.4 | 20.4 | 0 | 1.0326 |  | 4982911 | y | [15 empty] | #N/A |  | 984 | W_DENT_T | NORTH
530 | 49830 | EXN943GT | 12 | CNP_TSP | YES | -0.21497 | 19 | 5.4 | 19.9 | 0 | 1.0326 |  | 4983012 | y | [15 empty] | #N/A |  | 985 | N_DENT_8 | NORTH
531 | 49831 | EXN944GT | 13 | CNP_TSP | YES | -0.21497 | 33 | 5.4 | 35 | 0 | 1.0326 |  | 4983113 | y | [15 empty] | #N/A |  | 986 | W_DENT_8 | NORTH
532 | 49832 | EXN945GT | 9 | CNP_TSP | YES | -0.21497 | 18.5 | 9.2 | 18.5 |  | 1.0326 |  | 498329 | y | [15 empty] | #N/A |  | 987 | GIBN_STR | NORTH
533 | 49837 | EXN_GT | 4 | CNP_TSP | YES | -0.21497 | 81 | 21.3 | 85.4 |  | 1.0326 |  | 498374 | y | [15 empty] | #N/A |  | 988 | W_DENT_5 | NORTH
534 | 49838 | EXN_14GT | 14 | CNP_TSP | YES | -0.21497 | 140 | 0 | 148 |  | 1.0326 |  | 4983814 | y | [15 empty] | #N/A |  | 989 | GIBN_STR | NORTH
535 | 49851 | DOW17000 | 37 | CNP_TSP | YES | -0.20934 | 39 | 0 | 62 | 0 | 1 |  | 4985137 | y | [15 empty] | #N/A |  | 990 | GIBN_CRE | NORTH
536 | 49858 | DOW38100 | 31 | CNP_TSP | YES | -0.20934 | 45 | 0 | 71.4 |  | 1 |  | 4985831 | y | [15 empty] | #N/A |  | 991 | BOWIE_T_ | NORTH
537 | 49859 | DOW38200 | 33 | CNP_TSP | YES | -0.20934 | 28 | 0 | 45 | 0 | 1 |  | 4985933 | y | [15 empty] | #N/A |  | 992 | BRIDGE_P | NORTH
538 | 49860 | DOW38300 | 32 | CNP_TSP | YES | -0.20934 | 63 | 0 | 101 |  | 1 |  | 4986032 | y | [15 empty] | #N/A |  | 993 | BENDAVIS | NORTH
539 | 49862 | DOW39100 | 36 | CNP_TSP | YES | -0.20934 | 54 | 0 | 86 | 0 | 1 |  | 4986236 | y | [15 empty] | #N/A |  | 994 | BENDAVIS | NORTH
540 | 49863 | DOW39200 | 35 | CNP_TSP | YES | -0.20934 | 55 | 0 | 88 | 0 | 1 |  | 4986335 | y | [15 empty] | #N/A |  | 995 | BENDASTR | NORTH
541 | 49865 | DOW41000 | 41 | CNP_TSP | YES | -0.20934 | 31 | 0 | 50 |  | 1 |  | 4986541 | y | [15 empty] | #N/A |  | 996 | BENDASTR | NORTH
542 | 49866 | DOW42000 | 42 | CNP_TSP | YES | -0.20934 | 11 | 0 | 18 |  | 1 |  | 4986642 | y | [15 empty] | #N/A |  | 997 | MCCRESTR | NORTH
543 | 49869 | DOW49000 | 45 | CNP_TSP | YES | -0.20934 | 59 | 0 | 94 |  | 1 |  | 4986945 | y | [15 empty] | #N/A |  | 998 | JKCRESTR | NORTH
544 | 49870 | DOW61000 | 61 | CNP_TSP | YES | -0.20934 | 44 | 0 | 70 | 0 | 1 |  | 4987061 | y | [15 empty] | #N/A |  | 999 | GREENSTR | NORTH
545 | 49871 | DOW62000 | 62 | CNP_TSP | YES | -0.20934 | 40 | 0 | 63 | 0 | 1 |  | 4987162 | y | [15 empty] | #N/A |  | 1000 | GREENSTR | NORTH
546 | 49872 | DOW63000 | 63 | CNP_TSP | YES | -0.20934 | 45 | 0 | 72 | 0 | 1 |  | 4987263 | y | [15 empty] | #N/A |  | 1001 | DN_STSTR | NORTH
547 | 49873 | DOW64000 | 64 | CNP_TSP | YES | -0.20934 | 41 | 0 | 64.8 | 0 | 1 |  | 4987364 | y | [15 empty] | #N/A |  | 1002 | PBCTAGE_ | WEST
548 | 49876 | DOW65000 | 65 | CNP_TSP | YES | -0.20934 | 63 | 0 | 101 | 0 | 1 |  | 4987665 | y | [15 empty] | #N/A |  | 1003 | PBCTBGE_ | WEST
549 | 49877 | DOW66000 | 66 | CNP_TSP | YES | -0.20934 | 61 | 0 | 97 | 0 | 1 |  | 4987766 | y | [15 empty] | #N/A |  | 1004 | PBCTCGE_ | WEST
550 | 49878 | DOW67000 | 67 | CNP_TSP | YES | -0.20934 | 65 | 0 | 103 | 0 | 1 |  | 4987867 | y | [15 empty] | #N/A |  | 1005 | PBCTDGE_ | WEST
551 | 49882 | DOW81000 | 81 | CNP_TSP | YES | -0.20934 | 47 | 0 | 76 | 0 | 1 |  | 4988281 | y | [15 empty] | #N/A |  | 1006 | PBCTEGE_ | WEST
552 | 49884 | DOW82000 | 82 | CNP_TSP | YES | -0.20934 | 51 | 0 | 80 | 0 | 1 |  | 4988482 | y | [15 empty] | #N/A |  | 1007 | PB5GEN_6 | WEST
553 | 49885 | DOW83000 | 83 | CNP_TSP | YES | -0.20934 | 51 | 0 | 80 | 0 | 1 |  | 4988583 | y | [15 empty] | #N/A |  | 1008 | PB6GEN_7 | WEST
554 | 49886 | DOW84000 | 84 | CNP_TSP | YES | -0.20934 | 107 | 0 | 171 | 0 | 0.98 |  | 4988684 | y | [15 empty] | #N/A |  | 1009 | N_DENSTR | WEST
555 | 58909 | PEARSALLSCG1 | 1 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589091 | n | [15 empty] | #N/A |  | 1010 | PERMIANB | WEST
556 | 58909 | PEARSALLSCG1 | 2 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589092 | n | [15 empty] | #N/A |  | 1011 | W_DENSTR | WEST
557 | 58909 | PEARSALLSCG1 | 3 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589093 | n | [15 empty] | #N/A |  | 1012 | W_DENSTR | WEST
558 | 58909 | PEARSALLSCG1 | 4 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589094 | n | [15 empty] | #N/A |  | 1015 | PERMIANB | WEST
559 | 58909 | PEARSALLSCG1 | 5 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589095 | n | [15 empty] | #N/A |  | 1018 | MOSS_5 | WEST
560 | 58909 | PEARSALLSCG1 | 6 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589096 | n | [15 empty] | #N/A |  | 1019 | MOSS_8 | WEST
561 | 58919 | PEARSALLSCG2 | 1 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589191 | n | [15 empty] | #N/A |  | 1020 | ECTORTIE | WEST
562 | 58919 | PEARSALLSCG2 | 2 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589192 | n | [15 empty] | #N/A |  | 1021 | MIDLET_5 | WEST
563 | 58919 | PEARSALLSCG2 | 3 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589193 | n | [15 empty] | #N/A |  | 1022 | MIDLNDE_ | WEST
564 | 58919 | PEARSALLSCG2 | 4 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589194 | n | [15 empty] | #N/A |  | 1023 | MIDLNDE_ | WEST
565 | 58919 | PEARSALLSCG2 | 5 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589195 | n | [15 empty] | #N/A |  | 1024 | FSCOGEN_ | WEST
566 | 58919 | PEARSALLSCG2 | 6 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589196 | n | [15 empty] | #N/A |  | 1025 | FSCOGEN_ | WEST
567 | 58929 | PEARSALLSCG3 | 1 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589291 | n | [15 empty] | #N/A |  | 1026 | ECTORTIE | WEST
568 | 58929 | PEARSALLSCG3 | 2 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589292 | n | [15 empty] | #N/A |  | 1027 | ODESEHV_ | WEST
569 | 58929 | PEARSALLSCG3 | 3 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589293 | n | [15 empty] | #N/A |  | 1028 | ODESEHV_ | WEST
570 | 58929 | PEARSALLSCG3 | 4 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589294 | n | [15 empty] | #N/A |  | 1030 | MRGNCRK_ | WEST
571 | 58929 | PEARSALLSCG3 | 5 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589295 | n | [15 empty] | #N/A |  | 1031 | MRGN6G_6 | WEST
572 | 58929 | PEARSALLSCG3 | 6 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589296 | n | [15 empty] | #N/A |  | 1032 | MRGNCRK_ | WEST
573 | 58949 | PEARSALLSCG4 | 1 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589491 | n | [15 empty] | #N/A |  | 1033 | MRGNCRK_ | WEST
574 | 58949 | PEARSALLSCG4 | 2 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589492 | n | [15 empty] | #N/A |  | 1034 | MCTMODEL | WEST
575 | 58949 | PEARSALLSCG4 | 3 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589493 | n | [15 empty] | #N/A |  | 1037 | MORGAN5G | WEST
576 | 58949 | PEARSALLSCG4 | 4 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589494 | n | [15 empty] | #N/A |  | 1039 | MRGNAG_1 | WEST
577 | 58949 | PEARSALLSCG4 | 5 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589495 | n | [15 empty] | #N/A |  | 1040 | MRGNBG_2 | WEST
578 | 58949 | PEARSALLSCG4 | 6 | STEC_TSP | YES | -0.1374 | 0 | 0 | 8.4 |  | 1.027 |  | 589496 | n | [15 empty] | #N/A |  | 1041 | MRGNCG_3 | WEST
579 | 60000 | DSKY2 | 1 | AEP_TNC | YES | -0.020593 | 19.1 | 0 | 76.5 |  | 1.039 |  | 600001 | n | [15 empty] | #N/A |  | 1042 | MRGNDG_4 | WEST
580 | 60003 | KING_NE1A | 1 | AEP_TNC | YES | -0.018389 | 20 | 0 | 80 |  | 1.03 |  | 600031 | n | [15 empty] | #N/A |  | 1043 | MRGNEG_5 | WEST
581 | 60005 | KING_SE1A | 1 | AEP_TNC | YES | -0.018389 | 10 | 0 | 40 |  | 1.035 |  | 600051 | n | [15 empty] | #N/A |  | 1044 | MRGNFG_6 | WEST
582 | 60007 | KING_SW1A | 1 | AEP_TNC | YES | -0.018074 | 20 | 0 | 80 |  | 1.03 |  | 600071 | n | [15 empty] | #N/A |  | 1045 | CALENG1G | WEST
583 | 60016 | WOODWRD11A | 1 | AEP_TNC | YES | -0.018448 | 20 | 0 | 80 |  | 1.033 |  | 600161 | n | [15 empty] | #N/A |  | 1046 | CALENG2G | WEST
584 | 60017 | ORNNWP1 | 1 | AEP_TNC | YES | -0.020179 | 20 | 0 | 80 |  | 1.027 |  | 600171 | n | [15 empty] | #N/A |  | 1047 | CALENG3G | WEST
585 | 60018 | DSKY1 | 1 | AEP_TNC | YES | -0.020744 | 21 | 0 | 84 | 0 | 1.023 |  | 600181 | n | [15 empty] | #N/A |  | 1048 | TONKAWA_ | WEST
586 | 60019 | KING_NW1A | 1 | AEP_TNC | YES | -0.018074 | 20 | 0 | 80 |  | 1.03 |  | 600191 | n | [15 empty] | #N/A |  | 1049 | ROSCOE_5 | WEST
587 | 60057 | CALLAHAN1A | 1 | AEP_TNC | YES | -0.0131 | 22.8 | 0 | 114 | 0 | 1.04 |  | 600571 | n | [15 empty] | #N/A |  | 1051 | HUNTSMAN | WEST
588 | 60058 | BUFF_GAP1A | 1 | AEP_TNC | YES | -0.011643 | 24 | 0 | 120 |  | 1 |  | 600581 | n | [15 empty] | #N/A |  | 1052 | REXALL_8 | WEST
589 | 60060 | CIRELLO | 1 | AEP_TNC | YES | -0.011643 | 46.6 | 0 | 233 | 0 | 1 |  | 600601 | n | [15 empty] | #N/A |  | 1053 | GENRUBR_ | WEST
590 | 60063 | BUFF_GAP1B | 1 | AEP_TNC | YES | -0.011643 | 34 | 0 | 170.2 | 0 | 1.02 |  | 600631 | n | [15 empty] | #N/A |  | 1054 | OLFNNSHL | WEST
591 | 60066 | H_HOLLOW1A | 1 | AEP_TNC | YES | -0.011643 | 44.4 | 0 | 222 | 0 | 1.005 |  | 600661 | n | [15 empty] | #N/A |  | 1055 | NYLONTAP | WEST
592 | 60068 | HHOLLOW21A | 1 | AEP_TNC | YES | -0.011643 | 36.8 | 0 | 184 | 0 | 1.025 |  | 600681 | n | [15 empty] | #N/A |  | 1056 | NYLON_8 | WEST
593 | 60070 | HHOLLOW31A | 1 | AEP_TNC | YES | -0.011643 | 44.8 | 0 | 224 | 0 | 1.025 |  | 600701 | n | [15 empty] | #N/A |  | 1057 | CHAMPION | WEST
594 | 60072 | HHOLLOW41A | 1 | AEP_TNC | YES | -0.011643 | 23 | 0 | 115 | 0 | 1.025 |  | 600721 | n | [15 empty] | #N/A |  | 1058 | LONGSHOR | WEST
595 | 60081 | WHRLWIND1A | 1 | AEP_TNC | YES | -0.010289 | 12 | 0 | 60 | 0 | 1.03 |  | 600811 | n | [15 empty] | #N/A |  | 1059 | MIDESSA_ | WEST
596 | 60201 | RIO DRCS | F | AEP_TNC | YES | -0.0183 | 0 | 0 | 0 | 0 | 1.025 |  | 60201F | n | [15 empty] | #N/A |  | 1060 | PYRON_5 | WEST
597 | 60202 | FRNDDRCS | F | AEP_TNC | YES | -0.029482 | 0 | 0 | 0 | 0 | 0.9985 |  | 60202F | n | [15 empty] | #N/A |  | 1061 | CIELOGEN | WEST
598 | 71051 | L_BITTCR1_1N | W1 | LCRA TSC | YES | -0.010892 | 7.5 | 0 | 37.5 |  | 1.02 |  | 71051W1 | n | [15 empty] | #N/A |  | 1062 | CIELOGEN | WEST
599 | 71054 | L_SWEETW1_1N | W1 | LCRA TSC | YES | -0.010892 | 21.5 | 0 | 107.5 |  | 1.02 |  | 71054W1 | n | [15 empty] | #N/A |  | 1063 | CIELOWIN | WEST
600 | 71057 | L_SWEETW1_2N | W1 | LCRA TSC | YES | -0.010892 | 27 | 0 | 135 |  | 1.02 |  | 71057W1 | n | [15 empty] | #N/A |  | 1064 | SUN_8 | WEST
601 | 71059 | L_SWEETW1_3N | W1 | LCRA TSC | YES | -0.010892 | 23.8 | 0 | 119 | 0 | 1.02 |  | 71059W1 | n | [15 empty] | #N/A |  | 1065 | KINDERML | WEST
602 | 71060 | L_SWEETW1_4N | W1 | LCRA TSC | YES | -0.010892 | 21 | 0 | 105 | 0 | 1.02 |  | 71060W1 | n | [15 empty] | #N/A |  | 1066 | KINDERML | WEST
603 | 71061 | L_SWEETW1_5N | W1 | LCRA TSC | YES | -0.010892 | 16.1 | 0 | 80.5 | 0 | 1.02 |  | 71061W1 | n | [15 empty] | #N/A |  | 1067 | GOLDENSW | WEST
604 | 76031 | L_GOATMO1_1N | W1 | AEP_TCC | YES | -0.012772 | 30 | 0 | 150 | 0 | 1.02 |  | 76031W1 | n | [15 empty] | #N/A |  | 1068 | SCURRYCW | WEST
605 | 76091 | L_DIVIDE1_1N | W1 | AEP_TNC | YES | -0.013016 | 22.5 | 0 | 112.5 |  | 1.02 |  | 76091W1 | n | [15 empty] | #N/A |  | 1069 | KINDERMG | WEST
606 | 76095 | L_CAPRSI1_1N | W1 | AEP_TNC | YES | -0.013016 | 29.9 | 0 | 149.5 | 0 | 1.02 |  | 76095W1 | n | [15 empty] | #N/A |  | 1070 | KINDERMG | WEST
607 | 76096 | L_CAPRSI1_2N | W1 | AEP_TNC | YES | -0.013016 | 37.2 | 0 | 186 | 0 | 1.02 |  | 76096W1 | n | [15 empty] | #N/A |  | 1071 | KINDERMG | WEST
608 | 76097 | L_CAPRGE1_1N | W1 | AEP_TNC | YES | -0.013016 | 42.9 | 0 | 214.5 | 0 | 1.02 |  | 76097W1 | n | [15 empty] | #N/A |  | 1072 | INADALE_ | WEST
609 | 78189 | L_CUERHY9_1Y | 1 | LCRA TSC | YES | -0.14251 | 12 | 0 | 12 | 0 | 1.02 |  | 781891 | n | [15 empty] | #N/A |  | 1073 | SCURRYCW | WEST
610 | 80003 | MILHWYS | F | AEP_TCC | YES | -0.15776 | 0 | 0 | 0 | 0 | 1.0168 |  | 80003F | n | [15 empty] | #N/A |  | 1074 | WINKSS_8 | WEST
611 | 80012 | LAR | F | AEP_TCC | YES | -0.14582 | 0 | 0 | 0 | 0 | 1.04 |  | 80012F | n | [15 empty] | #N/A |  | 1075 | WINKSS_9 | WEST
612 | 80051 | FOR #8 | 8 | AEP_TCC | YES | -0.16728 | 28 | 28 | 28 |  | 1 |  | 800518 | y | [15 empty] | #N/A |  | 1087 | WRDGLFTA | WEST
613 | 80052 | FOR #9 | 9 | AEP_TCC | YES | -0.16728 | 29.7 | 5 | 43.6 | 0 | 1 |  | 800529 | y | [15 empty] | #N/A |  | 1088 | WICKETT_ | WEST
614 | 80053 | FOR #10 | 10 | AEP_TCC | YES | -0.16728 | 68.4 | 45 | 75 | 0 | 1 |  | 8005310 | y | [15 empty] | #N/A |  | 1089 | WICKETAP | WEST
615 | 80080 | GWINDT11A | 1 | AEP_TCC | YES | -0.15791 | 28.2 | 0 | 94 | 0 | 1.025 |  | 800801 | n | [15 empty] | #N/A |  | 1091 | WARDGULF | WEST
616 | 80080 | GWINDT11A | 2 | AEP_TCC | YES | -0.15791 | 0 | 0 | 41 | 0 | 1.025 |  | 800802 | n | [15 empty] | #N/A |  | 1092 | LOVING_8 | WEST
617 | 80080 | GWINDT11A | 3 | AEP_TCC | YES | -0.15791 | 0 | 0 | 38 | 0 | 1.025 |  | 800803 | n | [15 empty] | #N/A |  | 1093 | ELMAR_8 | WEST
618 | 80080 | GWINDT11A | 4 | AEP_TCC | YES | -0.15791 | 3.8 | 0 | 19 | 0 | 1.025 |  | 800804 | n | [15 empty] | #N/A |  | 1094 | MASON_8 | WEST
619 | 80081 | GWINDT21A | 1 | AEP_TCC | YES | -0.15791 | 28.2 | 0 | 94 | 0 | 1.025 |  | 800811 | n | [15 empty] | #N/A |  | 1095 | SCRWBEAN | WEST
620 | 80081 | GWINDT21A | 2 | AEP_TCC | YES | -0.15791 | 7.2 | 0 | 36 | 0 | 1.025 |  | 800812 | n | [15 empty] | #N/A |  | 1096 | BLACKRVR | WEST
621 | 80081 | GWINDT21A | 3 | AEP_TCC | YES | -0.15791 | 8.6 | 0 | 43 | 0 | 1.025 |  | 800813 | n | [15 empty] | #N/A |  | 1097 | TWPPMTR_ | WEST
622 | 80081 | GWINDT21A | 4 | AEP_TCC | YES | -0.15791 | 4.4 | 0 | 22 | 0 | 1.025 |  | 800814 | n | [15 empty] | #N/A |  | 1098 | KWINDRO_ | WEST
623 | 80137 | CSDR89 | 8 | AEP_TCC | YES | -0.16378 | 33.9 | 0 | 39 | 0 | 1.003 |  | 801378 | y | [15 empty] | #N/A |  | 1099 | SWPORTAP | WEST
624 | 80137 | CSDR89 | 9 | AEP_TCC | YES | -0.16378 | 15 | 0 | 15 | 0 | 1.003 |  | 801379 | y | [15 empty] | #N/A |  | 1100 | SWPORTLA | WEST
625 | 80138 | CSDR7 | 7 | AEP_TCC | YES | -0.16378 | 6.1 | 0 | 7 | 0 | 1.014 |  | 801387 | y | [15 empty] | #N/A |  | 1101 | EDWARDS_ | WEST
626 | 80139 | CSDR56 | 5 | AEP_TCC | YES | -0.16378 | 15 | 0 | 15 |  | 1.0033 |  | 801395 | y | [15 empty] | #N/A |  | 1102 | JUDKINS_ | WEST
627 | 80139 | CSDR56 | 6 | AEP_TCC | YES | -0.16378 | 0 | 0 | 39 |  | 1.0033 |  | 801396 | y | [15 empty] | #N/A |  | 1103 | SANDHLTA | WEST
628 | 80140 | CSDR11 | 11 | AEP_TCC | YES | -0.16378 | 33.9 | 0 | 39 | 0 | 1.03 |  | 8014011 | y | [15 empty] | #N/A |  | 1104 | SANDHILL | WEST
629 | 80180 | PNSCALT11A | 1 | AEP_TCC | YES | -0.15791 | 43.8 | 0 | 148 | 0 | 1.025 |  | 801801 | n | [15 empty] | #N/A |  | 1105 | MONAHTAP | WEST
630 | 80180 | PNSCALT11A | 2 | AEP_TCC | YES | -0.15791 | 10 | 0 | 50 | 0 | 1.025 |  | 801802 | n | [15 empty] | #N/A |  | 1106 | MONAHN1_ | WEST
631 | 80181 | PNSCALT21A | 1 | AEP_TCC | YES | -0.15791 | 16.5 | 0 | 55 | 0 | 1.025 |  | 801811 | n | [15 empty] | #N/A |  | 1107 | MONAHTAP | WEST
632 | 80181 | PNSCALT21A | 2 | AEP_TCC | YES | -0.15791 | 10 | 0 | 50 | 0 | 1.025 |  | 801812 | n | [15 empty] | #N/A |  | 1108 | MONAHN2_ | WEST
633 | 80223 | REYSHR G | 1 | AEP_TCC | YES | -0.15991 | 12 | 0 | 12 | 0 | 1.032 |  | 802231 | y | [15 empty] | #N/A |  | 1109 | CULBESON | WEST
634 | 80224 | VISTRONG1 | 1 | AEP_TCC | YES | -0.16279 | 13.1 | 0 | 15 | 0 | 1.01 |  | 802241 | y | [15 empty] | #N/A |  | 1111 | BIG3ODTA | WEST
635 | 80225 | VISTRONG2 | 2 | AEP_TCC | YES | -0.16279 | 20.2 | 0 | 23 | 0 | 1.01 |  | 802252 | y | [15 empty] | #N/A |  | 1112 | BIG3OD_8 | WEST
636 | 80226 | ALCOA G | 1 | AEP_TCC | YES | -0.16648 | 32.3 | 5 | 48 | 0 | 1.015 |  | 802261 | y | [15 empty] | #N/A |  | 1113 | ODESASW_ | WEST
637 | 80227 | AIRCO G | 1 | AEP_TCC | YES | -0.16343 | 7.2 | 0 | 8 | 0 | 1.0104 |  | 802271 | y | [15 empty] | #N/A |  | 1116 | WINDWOOD | WEST
638 | 80263 | B_DAVIS31A | 3 | AEP_TCC | YES | -0.15864 | 0 | 0 | 180 |  | 1.0366 |  | 802633 | n | [15 empty] | #N/A |  | 1117 | MIDLANDW | WEST
639 | 80264 | B_DAVIS41A | 4 | AEP_TCC | YES | -0.15864 | 0 | 0 | 180 |  | 1.0366 |  | 802644 | n | [15 empty] | #N/A |  | 1118 | CRMWD8TA | WEST
640 | 80265 | LARECU40A | 4 | AEP_TCC | YES | -0.14582 | 100 | 0 | 100 |  | 1.039 |  | 802654 | n | [15 empty] | #N/A |  | 1119 | CRMWD8_8 | WEST
641 | 80266 | LARECU50A | 5 | AEP_TCC | YES | -0.14582 | 100 | 0 | 100 |  | 1.039 |  | 802665 | n | [15 empty] | #N/A |  | 1120 | MIDLAIRP | WEST
642 | 86104 | CID-138 | EQ | AEP_TCC | YES | -0.14582 | 0 | 0 | 0 | 0 | 1.01 |  | 86104EQ | y | [15 empty] | #N/A |  | 1121 | GLENHAVN | WEST
643 | 86105 | CID-230 | EQ | AEP_TCC | YES | -0.14582 | 15.7 | -500 | 500 | 0 | 1.01 |  | 86105EQ | y | [15 empty] | #N/A |  | 1122 | ODESSANO | WEST
644 | 86106 | CUF-230 | EQ | AEP_TCC | YES | -0.14582 | 0 | -500 | 500 | 0 | 1.01 |  | 86106EQ | y | [15 empty] | #N/A |  | 1123 | ODESSANO | WEST
645 | 86107 | CUF-138 | EQ | AEP_TCC | YES | -0.14582 | 0 | 0 | 0 | 0 | 1.01 |  | 86107EQ | y | [15 empty] | #N/A |  | 1126 | ODESSA2_ | WEST
646 | 88198 | BEEVILLE | F | AEP_TCC | YES | -0.1525 | 0 | 0 | 0 | 0 | 1.02 |  | 88198F | n | [15 empty] | #N/A |  | 1127 | ODESSA1_ | WEST
647 | 88253 | HAMILTON | F | AEP_TCC | YES | -0.10379 | 0 | 0 | 0 | 0 | 1.04 |  | 88253F | n | [15 empty] | #N/A |  | 1128 | LIQDAIR_ | WEST
648 | 88299 | ZAPATA | F | AEP_TCC | YES | -0.15049 | 0 | 0 | 0 | 0 | 1.02 |  | 88299F | n | [15 empty] | #N/A |  | 1129 | WESTOVER | WEST
649 | 88508 | FALFURRI | F | AEP_TCC | YES | -0.15423 | 0 | 0 | 0 | 0 | 1 |  | 88508F | n | [15 empty] | #N/A |  | 1130 | AMOSFOST | WEST
[30 empty] | #N/A |  | 1132 | MIDLDWNT | WEST
[30 empty] | #N/A |  | 1137 | TEXINSTA | WEST
[30 empty] | #N/A |  | 1138 | TEXASINS | WEST
[30 empty] | #N/A |  | 1141 | HOLTSS_8 | WEST
[30 empty] | #N/A |  | 1142 | HOLTSS_9 | WEST
[30 empty] | #N/A |  | 1143 | AMOCNCTA | WEST
[30 empty] | #N/A |  | 1144 | AMNCOWD_ | WEST
[30 empty] | #N/A |  | 1145 | AMGLDSMI | WEST
[30 empty] | #N/A |  | 1146 | NOTREES1 | WEST
[30 empty] | #N/A |  | 1147 | CHEYENTA | WEST
[30 empty] | #N/A |  | 1148 | CHEYENNE | WEST
[30 empty] | #N/A |  | 1149 | DOLRHIDE | WEST
[30 empty] | #N/A |  | 1150 | AMOCO3BA | WEST
[30 empty] | #N/A |  | 1152 | UNOCALDH | WEST
[30 empty] | #N/A |  | 1155 | ANDREWTA | WEST
[30 empty] | #N/A |  | 1156 | ANDREWS_ | WEST
[30 empty] | #N/A |  | 1158 | SLMSALE_ | WEST
[30 empty] | #N/A |  | 1159 | NOANDREW | WEST
[30 empty] | #N/A |  | 1160 | NOANDREW | WEST
[30 empty] | #N/A |  | 1161 | UNPKRBK_ | WEST
[30 empty] | #N/A |  | 1163 | LAMESA_8 | WEST
[30 empty] | #N/A |  | 1164 | LAMESA_9 | WEST
[30 empty] | #N/A |  | 1165 | EXMEANTA | WEST
[30 empty] | #N/A |  | 1166 | EXNMEANS | WEST
[30 empty] | #N/A |  | 1167 | MUSTANG_ | WEST
[30 empty] | #N/A |  | 1168 | PAULDTAP | WEST
[30 empty] | #N/A |  | 1169 | PAULDAVS | WEST
[30 empty] | #N/A |  | 1176 | GRANDVEW | WEST
[30 empty] | #N/A |  | 1177 | TEXMABEE | WEST
[30 empty] | #N/A |  | 1178 | ADOBEMEW | WEST
[30 empty] | #N/A |  | 1179 | TEXMATAP | WEST
[30 empty] | #N/A |  | 1180 | ECTRHILL | WEST
[30 empty] | #N/A |  | 1182 | MOCKNBRD | WEST
[30 empty] | #N/A |  | 1184 | GODDARD_ | WEST
[30 empty] | #N/A |  | 1198 | CRANE_9 | WEST
[30 empty] | #N/A |  | 1199 | ARCOCTAP | WEST
[30 empty] | #N/A |  | 1201 | ARCOCRN_ | WEST
[30 empty] | #N/A |  | 1202 | WARDSS_9 | WEST
[30 empty] | #N/A |  | 1203 | BARNSLEY | WEST
[30 empty] | #N/A |  | 1204 | EXNJCTAP | WEST
[30 empty] | #N/A |  | 1205 | EXONJUAN | WEST
[30 empty] | #N/A |  | 1206 | CRNATLTA | WEST
[30 empty] | #N/A |  | 1207 | CRANATLC | WEST
[30 empty] | #N/A |  | 1210 | MIDKIFF_ | WEST
[30 empty] | #N/A |  | 1211 | MIDKIFF_ | WEST
[30 empty] | #N/A |  | 1212 | UPTON_8 | WEST
[30 empty] | #N/A |  | 1213 | PEMBRKTA | WEST
[30 empty] | #N/A |  | 1214 | CRANEAST | WEST
[30 empty] | #N/A |  | 1215 | PEMBROOK | WEST
[30 empty] | #N/A |  | 1216 | REAGNSHE | WEST
[30 empty] | #N/A |  | 1217 | GLASCOCK | WEST
[30 empty] | #N/A |  | 1218 | GARDCITY | WEST
[30 empty] | #N/A |  | 1221 | TEXHARVY | WEST
[30 empty] | #N/A |  | 1222 | PECKTAP_ | WEST
[30 empty] | #N/A |  | 1223 | PECK_9 | WEST
[30 empty] | #N/A |  | 1226 | MDGULFTA | WEST
[30 empty] | #N/A |  | 1227 | MIDLGULF | WEST
[30 empty] | #N/A |  | 1228 | MIDBASIN | WEST
[30 empty] | #N/A |  | 1229 | STANTON_ | WEST
[30 empty] | #N/A |  | 1232 | CRANEHUM | WEST
[30 empty] | #N/A |  | 1233 | GETTY_9 | WEST
[30 empty] | #N/A |  | 1234 | PGASUSTA | WEST
[30 empty] | #N/A |  | 1235 | PEGASUS_ | WEST
[30 empty] | #N/A |  | 1236 | SPEGSTAP | WEST
[30 empty] | #N/A |  | 1237 | SOPGASUS | WEST
[30 empty] | #N/A |  | 1238 | ROYALTY_ | WEST
[30 empty] | #N/A |  | 1239 | COYANOSA | WEST
[30 empty] | #N/A |  | 1240 | WFCAMPTA | WEST
[30 empty] | #N/A |  | 1241 | WOLFCAMP | WEST
[30 empty] | #N/A |  | 1242 | NNATURAL | WEST
[30 empty] | #N/A |  | 1245 | WINKBAWT | WEST
[30 empty] | #N/A |  | 1246 | WINKBASN | WEST
[30 empty] | #N/A |  | 1249 | KEYSTONE | WEST
[30 empty] | #N/A |  | 1252 | VEST_9 | WEST
[30 empty] | #N/A |  | 1253 | MIDWAY_9 | WEST
[30 empty] | #N/A |  | 1254 | ODBASSS_ | WEST
[30 empty] | #N/A |  | 1255 | ODESBASN | WEST
[30 empty] | #N/A |  | 1256 | GOLDSMTH | WEST
[30 empty] | #N/A |  | 1257 | ECTRSHEL | WEST
[30 empty] | #N/A |  | 1259 | NTCOWDEN | WEST
[30 empty] | #N/A |  | 1262 | EMMATAP_ | WEST
[30 empty] | #N/A |  | 1263 | EMMA_9 | WEST
[30 empty] | #N/A |  | 1264 | SANADTAP | WEST
[30 empty] | #N/A |  | 1265 | SANANDRS | WEST
[30 empty] | #N/A |  | 1266 | MIDFARMS | WEST
[30 empty] | #N/A |  | 1267 | ANDREWS_ | WEST
[30 empty] | #N/A |  | 1270 | FRNKLCTY | WEST
[30 empty] | #N/A |  | 1273 | PHILANDS | WEST
[30 empty] | #N/A |  | 1274 | FULERTON | WEST
[30 empty] | #N/A |  | 1275 | EXXONFUL | WEST
[30 empty] | #N/A |  | 1277 | BAKKETAP | WEST
[30 empty] | #N/A |  | 1280 | BAKKE_9 | WEST
[30 empty] | #N/A |  | 1281 | AMMIDFTA | WEST
[30 empty] | #N/A |  | 1282 | AMOMIDFM | WEST
[30 empty] | #N/A |  | 1285 | MEANS_9 | WEST
[30 empty] | #N/A |  | 1292 | ECTRHARP | WEST
[30 empty] | #N/A |  | 1295 | WICKETT_ | WEST
[30 empty] | #N/A |  | 1296 | NORTHWRD | WEST
[30 empty] | #N/A |  | 1297 | WICKETAP | WEST
[30 empty] | #N/A |  | 1300 | EXSHARNR | WEST
[30 empty] | #N/A |  | 1301 | WILLOWVA | WEST
[30 empty] | #N/A |  | 1302 | MULESHOE | WEST
[30 empty] | #N/A |  | 1305 | SNYDER_8 | WEST
[30 empty] | #N/A |  | 1306 | SNYDER_9 | WEST
[30 empty] | #N/A |  | 1307 | KEYLYNTE | WEST
[30 empty] | #N/A |  | 1308 | GAILLYNT | WEST
[30 empty] | #N/A |  | 1309 | BLUFCKTA | WEST
[30 empty] | #N/A |  | 1310 | KNAPP_8 | WEST
[30 empty] | #N/A |  | 1311 | SACROC_8 | WEST
[30 empty] | #N/A |  | 1312 | SCURYCHV | WEST
[30 empty] | #N/A |  | 1313 | ENISCKTA | WEST
[30 empty] | #N/A |  | 1314 | ENNISCK_ | WEST
[30 empty] | #N/A |  | 1315 | BRAND_8 | WEST
[30 empty] | #N/A |  | 1317 | COAHOMAN | WEST
[30 empty] | #N/A |  | 1318 | CHINAGRV | WEST
[30 empty] | #N/A |  | 1319 | CHINAGRV | WEST
[30 empty] | #N/A |  | 1320 | BSP 1 | WEST
[30 empty] | #N/A |  | 1321 | CARBONSW | WEST
[30 empty] | #N/A |  | 1322 | BIGSPRIG | WEST
[30 empty] | #N/A |  | 1323 | BIGSPRIG | WEST
[30 empty] | #N/A |  | 1324 | BIGSPGWE | WEST
[30 empty] | #N/A |  | 1325 | AIRPARK_ | WEST
[30 empty] | #N/A |  | 1326 | STANTONW | WEST
[30 empty] | #N/A |  | 1327 | WILDHRSE | WEST
[30 empty] | #N/A |  | 1328 | OCOTILLO | WEST
[30 empty] | #N/A |  | 1329 | SPRABERY | WEST
[30 empty] | #N/A |  | 1330 | SPRABERY | WEST
[30 empty] | #N/A |  | 1331 | DRUMRIGT | WEST
[30 empty] | #N/A |  | 1332 | COSDEN_8 | WEST
[30 empty] | #N/A |  | 1333 | MCDDONAL | WEST
[30 empty] | #N/A |  | 1334 | CHNGOWNR | WEST
[30 empty] | #N/A |  | 1335 | FORSANTA | WEST
[30 empty] | #N/A |  | 1336 | FORSAN_8 | WEST
[30 empty] | #N/A |  | 1337 | CRMWDTAP | WEST
[30 empty] | #N/A |  | 1338 | CRMWDSVN | WEST
[30 empty] | #N/A |  | 1339 | ESKOTA_8 | WEST
[30 empty] | #N/A |  | 1340 | ESKOTA_9 | WEST
[30 empty] | #N/A |  | 1341 | SWTRDTAP | WEST
[30 empty] | #N/A |  | 1342 | SWEETWTD | WEST
[30 empty] | #N/A |  | 1343 | TRENTIPP | WEST
[30 empty] | #N/A |  | 1345 | COAHOMA_ | WEST
[30 empty] | #N/A |  | 1346 | IATHOWTA | WEST
[30 empty] | #N/A |  | 1347 | IATNHOW_ | WEST
[30 empty] | #N/A |  | 1348 | WSTBROOK | WEST
[30 empty] | #N/A |  | 1349 | WESTXWIN | WEST
[30 empty] | #N/A |  | 1350 | NWPWRG1_ | WEST
[30 empty] | #N/A |  | 1351 | BSPGGULF | WEST
[30 empty] | #N/A |  | 1352 | CHALK_9 | WEST
[30 empty] | #N/A |  | 1353 | NWPWRTAP | WEST
[30 empty] | #N/A |  | 1354 | AEPWIND_ | WEST
[30 empty] | #N/A |  | 1355 | ACKRLYVE | WEST
[30 empty] | #N/A |  | 1356 | ACKRLYVE | WEST
[30 empty] | #N/A |  | 1357 | BIGCRMWD | WEST
[30 empty] | #N/A |  | 1358 | KNOTT_9 | WEST
[30 empty] | #N/A |  | 1359 | ACKCHEV_ | WEST
[30 empty] | #N/A |  | 1360 | GUNSIGHT | WEST
[30 empty] | #N/A |  | 1362 | ACKERLY_ | WEST
[30 empty] | #N/A |  | 1363 | ACKRLNTC | WEST
[30 empty] | #N/A |  | 1364 | SPARNBRG | WEST
[30 empty] | #N/A |  | 1367 | IRA_9 | WEST
[30 empty] | #N/A |  | 1368 | SCURRY_9 | WEST
[30 empty] | #N/A |  | 1369 | LKTHOMAS | WEST
[30 empty] | #N/A |  | 1370 | SANTAFE_ | WEST
[30 empty] | #N/A |  | 1371 | MURRY_P8 | NORTH
[30 empty] | #N/A |  | 1373 | COLBASIN | WEST
[30 empty] | #N/A |  | 1374 | CHGRGULF | WEST
[30 empty] | #N/A |  | 1375 | AMOCO_9 | WEST
[30 empty] | #N/A |  | 1376 | AMOCOTAP | WEST
[30 empty] | #N/A |  | 1378 | COLOCITY | WEST
[30 empty] | #N/A |  | 1379 | LORAINE_ | WEST
[30 empty] | #N/A |  | 1380 | ROSCOE_9 | WEST
[30 empty] | #N/A |  | 1381 | SWEETWTR | WEST
[30 empty] | #N/A |  | 1382 | USGYPSTA | WEST
[30 empty] | #N/A |  | 1383 | USGYPTWO | WEST
[30 empty] | #N/A |  | 1384 | USGYPONE | WEST
[30 empty] | #N/A |  | 1385 | FLINTKOT | WEST
[30 empty] | #N/A |  | 1386 | FLINTST_ | WEST
[30 empty] | #N/A |  | 1387 | USGYPTAP | WEST
[30 empty] | #N/A |  | 1389 | WELCHTAP | WEST
[30 empty] | #N/A |  | 1390 | WELCH_9 | WEST
[30 empty] | #N/A |  | 1391 | DAWSON_9 | WEST
[30 empty] | #N/A |  | 1392 | OXYUSA_9 | WEST
[30 empty] | #N/A |  | 1394 | GTTYVTAP | WEST
[30 empty] | #N/A |  | 1395 | GETTYVLM | WEST
[30 empty] | #N/A |  | 1398 | RADIUMMT | WEST
[30 empty] | #N/A |  | 1400 | TXCOCOGD | WEST
[30 empty] | #N/A |  | 1401 | COGDELTA | WEST
[30 empty] | #N/A |  | 1402 | COGDELL_ | WEST
[30 empty] | #N/A |  | 1406 | OAKCREEK | WEST
[30 empty] | #N/A |  | 1407 | LONESTAR | WEST
[30 empty] | #N/A |  | 1409 | NOLANWTA | WEST
[30 empty] | #N/A |  | 1410 | ENSCRKSS | WEST
[30 empty] | #N/A |  | 1411 | ENSCRKSS | WEST
[30 empty] | #N/A |  | 1412 | PLAINVTA | WEST
[30 empty] | #N/A |  | 1416 | SWETWATR | WEST
[30 empty] | #N/A |  | 1417 | SWETWATR | WEST
[30 empty] | #N/A |  | 1418 | SWETWATR | WEST
[30 empty] | #N/A |  | 1419 | SWETWATR | WEST
[30 empty] | #N/A |  | 1420 | SWEETWTR | WEST
[30 empty] | #N/A |  | 1421 | WILLOWCK | NORTH
[30 empty] | #N/A |  | 1422 | BOWMAN_5 | NORTH
[30 empty] | #N/A |  | 1423 | BOWMAN_A | NORTH
[30 empty] | #N/A |  | 1424 | BOWMAN_B | NORTH
[30 empty] | #N/A |  | 1425 | FISHRDSS | NORTH
[30 empty] | #N/A |  | 1426 | FISHRDSS | NORTH
[30 empty] | #N/A |  | 1427 | FISHERRD | NORTH
[30 empty] | #N/A |  | 1429 | JACKSBRO | NORTH
[30 empty] | #N/A |  | 1430 | GRHAMSES | NORTH
[30 empty] | #N/A |  | 1431 | GRHAMSES | NORTH
[30 empty] | #N/A |  | 1432 | GRHAMSES | NORTH
[30 empty] | #N/A |  | 1433 | GRHAMSES | NORTH
[30 empty] | #N/A |  | 1434 | WCPWRCO_ | NORTH
[30 empty] | #N/A |  | 1435 | LONGCREK | NORTH
[30 empty] | #N/A |  | 1436 | PARKER_5 | NORTH
[30 empty] | #N/A |  | 1437 | MESQUITW | NORTH
[30 empty] | #N/A |  | 1438 | MESQUITW | NORTH
[30 empty] | #N/A |  | 1439 | LONCREK2 | NORTH
[30 empty] | #N/A |  | 1440 | COMCHESS | NORTH
[30 empty] | #N/A |  | 1441 | COMCHESS | NORTH
[30 empty] | #N/A |  | 1442 | COKFIELD | NORTH
[30 empty] | #N/A |  | 1446 | LKWICHIT | NORTH
[30 empty] | #N/A |  | 1447 | LKWICHIT | NORTH
[30 empty] | #N/A |  | 1448 | WCHTFLLS | NORTH
[30 empty] | #N/A |  | 1449 | WCHTFLLS | NORTH
[30 empty] | #N/A |  | 1450 | PLEASVAL | NORTH
[30 empty] | #N/A |  | 1451 | PLEASVAL | NORTH
[30 empty] | #N/A |  | 1452 | LANHAM_T | NORTH
[30 empty] | #N/A |  | 1453 | WCPWRCO_ | NORTH
[30 empty] | #N/A |  | 1454 | WCPWRCO_ | NORTH
[30 empty] | #N/A |  | 1455 | WCPWRCO_ | NORTH
[30 empty] | #N/A |  | 1464 | WFALLS_S | NORTH
[30 empty] | #N/A |  | 1467 | NORTHSTR | NORTH
[30 empty] | #N/A |  | 1468 | LKAROWHD | NORTH
[30 empty] | #N/A |  | 1469 | SUNSETSW | NORTH
[30 empty] | #N/A |  | 1470 | NEWPRT_P | NORTH
[30 empty] | #N/A |  | 1471 | CARTR_P8 | NORTH
[30 empty] | #N/A |  | 1472 | NAVYKSS1 | NORTH
[30 empty] | #N/A |  | 1473 | NAVYKSS1 | NORTH
[30 empty] | #N/A |  | 1474 | SCOTLD_P | NORTH
[30 empty] | #N/A |  | 1475 | WINDTHOR | NORTH
[30 empty] | #N/A |  | 1476 | MARKLY_8 | NORTH
[30 empty] | #N/A |  | 1477 | RICESW_8 | NORTH
[30 empty] | #N/A |  | 1478 | ARROWHD_ | NORTH
[30 empty] | #N/A |  | 1479 | WFCOGEN_ | NORTH
[30 empty] | #N/A |  | 1480 | RATHGBER | NORTH
[30 empty] | #N/A |  | 1482 | WFCOGEN_ | NORTH
[30 empty] | #N/A |  | 1483 | CITYVIEW | NORTH
[30 empty] | #N/A |  | 1484 | PPG_8 | NORTH
[30 empty] | #N/A |  | 1485 | CERAMIC_ | NORTH
[30 empty] | #N/A |  | 1486 | BOOMTOWN | NORTH
[30 empty] | #N/A |  | 1489 | SIKES_8 | NORTH
[30 empty] | #N/A |  | 1492 | RIVERBND | NORTH
[30 empty] | #N/A |  | 1493 | ARTHURST | NORTH
[30 empty] | #N/A |  | 1494 | WFSTHOSP | NORTH
[30 empty] | #N/A |  | 1496 | CERTEED2 | NORTH
[30 empty] | #N/A |  | 1497 | CERTEED1 | NORTH
[30 empty] | #N/A |  | 1498 | WFCOGEN_ | NORTH
[30 empty] | #N/A |  | 1499 | PARKWAY2 | NORTH
[30 empty] | #N/A |  | 1500 | PARKWAY1 | NORTH
[30 empty] | #N/A |  | 1503 | WFALLS_N | NORTH
[30 empty] | #N/A |  | 1504 | WFLSNBYP | NORTH
[30 empty] | #N/A |  | 1507 | SHPFIELD | NORTH
[30 empty] | #N/A |  | 1508 | WFLLSBSN | NORTH
[30 empty] | #N/A |  | 1509 | PETROLIA | NORTH
[30 empty] | #N/A |  | 1511 | WFBASIN_ | NORTH
[30 empty] | #N/A |  | 1512 | DIAMNDSH | NORTH
[30 empty] | #N/A |  | 1514 | SHPFIELD | NORTH
[30 empty] | #N/A |  | 1515 | SHPFIELD | NORTH
[30 empty] | #N/A |  | 1516 | IOWAPARK | NORTH
[30 empty] | #N/A |  | 1517 | BURKBURN | NORTH
[30 empty] | #N/A |  | 1518 | IOWAPARK | NORTH
[30 empty] | #N/A |  | 1519 | CRYOVAC_ | NORTH
[30 empty] | #N/A |  | 1520 | CRYOVAC_ | NORTH
[30 empty] | #N/A |  | 1522 | NAVYKPOO | NORTH
[30 empty] | #N/A |  | 1525 | ARCHCITY | NORTH
[30 empty] | #N/A |  | 1526 | BLACKWEL | NORTH
[30 empty] | #N/A |  | 1527 | HOLLIDAY | NORTH
[30 empty] | #N/A |  | 1530 | BAYLR_9 | NORTH
[30 empty] | #N/A |  | 1531 | SEYMRBAS | NORTH
[30 empty] | #N/A |  | 1532 | SEYMOUR_ | NORTH
[30 empty] | #N/A |  | 1533 | BOMARTON | WEST
[30 empty] | #N/A |  | 1536 | KMA_T9 | NORTH
[30 empty] | #N/A |  | 1537 | KMA_9 | NORTH
[30 empty] | #N/A |  | 1538 | ELECTRA_ | NORTH
[30 empty] | #N/A |  | 1541 | ROBNTECH | NORTH
[30 empty] | #N/A |  | 1543 | HENRITAW | NORTH
[30 empty] | #N/A |  | 1544 | HENRIETA | NORTH
[30 empty] | #N/A |  | 1545 | RINGMAG_ | NORTH
[30 empty] | #N/A |  | 1546 | RINGMAG_ | NORTH
[30 empty] | #N/A |  | 1547 | BELLEVUE | NORTH
[30 empty] | #N/A |  | 1548 | MONTAGUE | NORTH
[30 empty] | #N/A |  | 1549 | BOWIESVC | NORTH
[30 empty] | #N/A |  | 1550 | BOWIE1_9 | NORTH
[30 empty] | #N/A |  | 1552 | WZRDWLLS | NORTH
[30 empty] | #N/A |  | 1553 | CHCOWEST | NORTH
[30 empty] | #N/A |  | 1554 | CHCOCSER | NORTH
[30 empty] | #N/A |  | 1555 | JACKAMCO | NORTH
[30 empty] | #N/A |  | 1556 | JACKSBOR | NORTH
[30 empty] | #N/A |  | 1557 | JACKSINC | NORTH
[30 empty] | #N/A |  | 1558 | JACKSINC | NORTH
[30 empty] | #N/A |  | 1561 | ALVORD1_ | NORTH
[30 empty] | #N/A |  | 1562 | CHCOWEST | NORTH
[30 empty] | #N/A |  | 1563 | CHCOWEST | NORTH
[30 empty] | #N/A |  | 1564 | CHCOGHLL | NORTH
[30 empty] | #N/A |  | 1565 | BRDGPORT | NORTH
[30 empty] | #N/A |  | 1566 | DECATUR_ | NORTH
[30 empty] | #N/A |  | 1567 | DECATUR1 | NORTH
[30 empty] | #N/A |  | 1568 | ALLISON_ | NORTH
[30 empty] | #N/A |  | 1570 | RHOME_8 | NORTH
[30 empty] | #N/A |  | 1571 | ORAN1_8 | NORTH
[30 empty] | #N/A |  | 1572 | ORAN1_9 | NORTH
[30 empty] | #N/A |  | 1574 | PALOPNTO | NORTH
[30 empty] | #N/A |  | 1575 | MINWLLSW | NORTH
[30 empty] | #N/A |  | 1576 | PALOPNTO | NORTH
[30 empty] | #N/A |  | 1577 | MINWLLS2 | NORTH
[30 empty] | #N/A |  | 1579 | ALEDO1_9 | NORTH
[30 empty] | #N/A |  | 1580 | MINWLLS1 | NORTH
[30 empty] | #N/A |  | 1581 | GRAFORD_ | NORTH
[30 empty] | #N/A |  | 1583 | LIVEOAK1 | NORTH
[30 empty] | #N/A |  | 1584 | MINWLLSE | NORTH
[30 empty] | #N/A |  | 1585 | WTHFORDW | NORTH
[30 empty] | #N/A |  | 1586 | WTHFORD_ | NORTH
[30 empty] | #N/A |  | 1587 | WTHFORDE | NORTH
[30 empty] | #N/A |  | 1588 | LGNVISTA | NORTH
[30 empty] | #N/A |  | 1589 | WTHFORDW | NORTH
[30 empty] | #N/A |  | 1591 | SPRGTOWN | NORTH
[30 empty] | #N/A |  | 1592 | WTHFRDSS | NORTH
[30 empty] | #N/A |  | 1593 | BONHAM_P | NORTH
[30 empty] | #N/A |  | 1595 | LIPAN_8 | NORTH
[30 empty] | #N/A |  | 1596 | GRAHAMSW | NORTH
[30 empty] | #N/A |  | 1597 | GRAHAMSW | NORTH
[30 empty] | #N/A |  | 1598 | BALSORA_ | NORTH
[30 empty] | #N/A |  | 1599 | BARTON_8 | NORTH
[30 empty] | #N/A |  | 1600 | BARTNWND | NORTH
[30 empty] | #N/A |  | 1601 | GRAHAME_ | NORTH
[30 empty] | #N/A |  | 1602 | GRAHAM_9 | NORTH
[30 empty] | #N/A |  | 1603 | OLNEY_P9 | NORTH
[30 empty] | #N/A |  | 1604 | ANARENE1 | NORTH
[30 empty] | #N/A |  | 1607 | STH_BEND | NORTH
[30 empty] | #N/A |  | 1608 | IVAN_9 | NORTH
[30 empty] | #N/A |  | 1612 | BRECK_N_ | NORTH
[30 empty] | #N/A |  | 1613 | BRECK_T8 | NORTH
[30 empty] | #N/A |  | 1614 | BRECK_8 | NORTH
[30 empty] | #N/A |  | 1615 | BRECK_9 | NORTH
[30 empty] | #N/A |  | 1616 | SUN_ECU_ | NORTH
[30 empty] | #N/A |  | 1617 | SUN_ECU_ | NORTH
[30 empty] | #N/A |  | 1618 | CADDO_8 | NORTH
[30 empty] | #N/A |  | 1619 | COLNYCRK | NORTH
[30 empty] | #N/A |  | 1622 | EASTLAND | NORTH
[30 empty] | #N/A |  | 1623 | MORTNVAL | NORTH
[30 empty] | #N/A |  | 1624 | LEONSW_8 | NORTH
[32 empty] | 1625 | LEON2_9 | NORTH
x | x | x | x | x | x | x | x | x | x | x | xx | x | x | [8 empty] | x | x | x | x | x | x | x | x | x |  | 1626 | LEON5_9 | NORTH
[32 empty] | 1627 | RANGULF_ | NORTH
[32 empty] | 1628 | RANGER_9 | NORTH
[32 empty] | 1629 | OLDEN_P8 | NORTH
[32 empty] | 1630 | GORMAN_9 | NORTH
[32 empty] | 1631 | DELNMAG_ | NORTH
[32 empty] | 1632 | DELNMAG_ | NORTH
[32 empty] | 1633 | DELEON_9 | NORTH
[32 empty] | 1634 | CMYNHM_T | NORTH
[32 empty] | 1635 | CMYNHM_9 | NORTH
[32 empty] | 1636 | DUBLIN1_ | NORTH
[32 empty] | 1637 | DUBLIN1_ | NORTH
[32 empty] | 1638 | SLSTR1PP | NORTH
[32 empty] | 1640 | LINGLVLL | NORTH
[32 empty] | 1641 | STPHNVIL | NORTH
[32 empty] | 1642 | FLATCRK_ | NORTH
[32 empty] | 1643 | SLSTR1PP | NORTH
[32 empty] | 1644 | SELDON_P | NORTH
[32 empty] | 1645 | JOHNSNVL | NORTH
[32 empty] | 1646 | WALNUTSP | NORTH
[32 empty] | 1647 | WALSPTNP | NORTH
[32 empty] | 1649 | HASSE_P8 | NORTH
[32 empty] | 1650 | COMANCHE | NORTH
[32 empty] | 1651 | COMANCHE | NORTH
[32 empty] | 1654 | ZEPHYR_P | NORTH
[32 empty] | 1655 | BRNWDSW_ | NORTH
[32 empty] | 1656 | BRNWD_S_ | NORTH
[32 empty] | 1661 | BRNWD1_8 | NORTH
[32 empty] | 1662 | BRNWD1_9 | NORTH
[32 empty] | 1665 | PROCTOR_ | NORTH
[32 empty] | 1666 | BLANKET_ | NORTH
[32 empty] | 1669 | LKBRNWD_ | NORTH
[32 empty] | 1670 | LKBRNWD_ | NORTH
[32 empty] | 1671 | BANGS_9 | NORTH
[32 empty] | 1675 | PEC_1G | NORTH
[32 empty] | 1676 | PEC_2G | NORTH
[32 empty] | 1677 | PEC_3G | NORTH
[32 empty] | 1678 | LAMARPWR | NORTH
[32 empty] | 1679 | LAMARPWR | NORTH
[32 empty] | 1680 | LAMARPWR | NORTH
[32 empty] | 1681 | LAMARPWR | NORTH
[32 empty] | 1682 | LAMARPWR | NORTH
[32 empty] | 1683 | LAMARPWR | NORTH
[32 empty] | 1684 | LAMARPWR | NORTH
[32 empty] | 1685 | FARMVLSW | NORTH
[32 empty] | 1687 | VALLEY_1 | NORTH
[32 empty] | 1688 | VALLEY_2 | NORTH
[32 empty] | 1689 | VALLEY_3 | NORTH
[32 empty] | 1690 | VALLYSES | NORTH
[32 empty] | 1691 | VALLYSES | NORTH
[32 empty] | 1692 | PARIS_SW | NORTH
[32 empty] | 1693 | PARIS_SW | NORTH
[32 empty] | 1694 | TENASKA_ | NORTH
[32 empty] | 1695 | MOSES_5 | NORTH
[32 empty] | 1696 | MOSES1_T | NORTH
[32 empty] | 1697 | SULSP_SS | NORTH
[32 empty] | 1698 | SULSP_SS | NORTH
[32 empty] | 1701 | MOSES_1G | NORTH
[32 empty] | 1702 | MOSES_2G | NORTH
[32 empty] | 1703 | MOSES_3G | NORTH
[32 empty] | 1704 | SHER_L_M | NORTH
[32 empty] | 1706 | GAINVL_E | NORTH
[32 empty] | 1707 | GAINVL_E | NORTH
[32 empty] | 1708 | GAINVLDX | NORTH
[32 empty] | 1709 | GAINVLDX | NORTH
[32 empty] | 1710 | GAINVL_N | NORTH
[32 empty] | 1712 | MUENSTER | NORTH
[32 empty] | 1713 | MEMC_W_T | NORTH
[32 empty] | 1714 | SHRM_TI_ | NORTH
[32 empty] | 1715 | MEMC_SW_ | NORTH
[32 empty] | 1716 | ST_JO_P9 | NORTH
[32 empty] | 1717 | MEMC_SW_ | NORTH
[32 empty] | 1718 | GAINVL_E | NORTH
[32 empty] | 1719 | GAINVL_T | NORTH
[32 empty] | 1720 | GAINVLNS | NORTH
[32 empty] | 1721 | GAINVLNS | NORTH
[32 empty] | 1722 | GAINVLCH | NORTH
[32 empty] | 1723 | LIBERTY_ | NORTH
[32 empty] | 1724 | WHTBORSE | NORTH
[32 empty] | 1725 | GORDVL_T | NORTH
[32 empty] | 1726 | SADLER_9 | NORTH
[32 empty] | 1727 | GORDVL_9 | NORTH
[32 empty] | 1728 | WHTBOR_9 | NORTH
[32 empty] | 1729 | VAL_STH_ | NORTH
[32 empty] | 1732 | SHER_NW_ | NORTH
[32 empty] | 1733 | PERRIN_T | NORTH
[32 empty] | 1734 | FINK_T8 | NORTH
[32 empty] | 1735 | FINK_8 | NORTH
[32 empty] | 1736 | PERRIN1_ | NORTH
[32 empty] | 1737 | DENISN_W | NORTH
[32 empty] | 1738 | WHTBORSE | NORTH
[32 empty] | 1739 | DENISND_ | NORTH
[32 empty] | 1740 | SHRM_TI_ | NORTH
[32 empty] | 1741 | LKTEXOMA | NORTH
[32 empty] | 1742 | TEXOMA_T | NORTH
[32 empty] | 1743 | DENISN_N | NORTH
[32 empty] | 1745 | DENISN_8 | NORTH
[32 empty] | 1746 | SHER_E_8 | NORTH
[32 empty] | 1747 | CHERYMND | NORTH
[32 empty] | 1749 | SHRM_TI_ | NORTH
[32 empty] | 1750 | SHER_S_8 | NORTH
[32 empty] | 1751 | VAN_AL_E | NORTH
[32 empty] | 1752 | WHTMND_8 | NORTH
[32 empty] | 1753 | MEMC_E_T | NORTH
[32 empty] | 1754 | VAN_AL_8 | NORTH
[32 empty] | 1755 | ECTOR_P8 | NORTH
[32 empty] | 1757 | ALLA_HUB | NORTH
[32 empty] | 1758 | PAYNE1_8 | NORTH
[32 empty] | 1759 | PAYNE1_9 | NORTH
[32 empty] | 1760 | BONHMSS1 | NORTH
[32 empty] | 1761 | BONHMSS_ | NORTH
[32 empty] | 1762 | BONHMNW1 | NORTH
[32 empty] | 1763 | PINKHIL_ | NORTH
[32 empty] | 1764 | BELLS1_9 | NORTH
[32 empty] | 1765 | ECTOR1_9 | NORTH
[32 empty] | 1766 | EXPLR_PL | NORTH
[32 empty] | 1768 | DEPORT_P | NORTH
[32 empty] | 1769 | PARIS_E_ | NORTH
[32 empty] | 1770 | LAMAR_T8 | NORTH
[32 empty] | 1771 | LAMARBM1 | NORTH
[32 empty] | 1772 | LAMARBM1 | NORTH
[32 empty] | 1773 | PARIS_E_ | NORTH
[32 empty] | 1774 | PARIS_N_ | NORTH
[32 empty] | 1776 | PARIS_KC | NORTH
[32 empty] | 1777 | PARIS_8 | NORTH
[32 empty] | 1778 | PARIS_9 | NORTH
[32 empty] | 1779 | LAMARCO_ | NORTH
[32 empty] | 1780 | RIVERCST | NORTH
[32 empty] | 1781 | RIVERCST | NORTH
[32 empty] | 1782 | SHERRY_P | NORTH
[32 empty] | 1783 | RIVERCST | NORTH
[32 empty] | 1784 | CLARKVL_ | NORTH
[32 empty] | 1785 | BAGWELL1 | NORTH
[32 empty] | 1786 | RENO_T8 | NORTH
[32 empty] | 1788 | BRKSTON1 | NORTH
[32 empty] | 1789 | HONEY_GR | NORTH
[32 empty] | 1790 | WINDMSPA | NORTH
[32 empty] | 1791 | MOSESMIN | NORTH
[32 empty] | 1793 | TALCO_W_ | NORTH
[32 empty] | 1794 | MOSES_T8 | NORTH
[32 empty] | 1795 | MOSES1_8 | NORTH
[32 empty] | 1796 | SULBLF1_ | NORTH
[32 empty] | 1797 | R0CKWELL | NORTH
[32 empty] | 1798 | SULSP_E1 | NORTH
[32 empty] | 1799 | ROCKWELL | NORTH
[32 empty] | 1800 | MRTNSPG1 | NORTH
[32 empty] | 1803 | PARS_PMP | NORTH
[32 empty] | 1805 | COOPER_9 | NORTH
[32 empty] | 1806 | ENLOE_T9 | NORTH
[32 empty] | 1808 | BONHAM_8 | NORTH
[32 empty] | 1809 | WOLFECTY | NORTH
[32 empty] | 1810 | WOLFCTY_ | NORTH
[32 empty] | 1812 | CUMBY_9 | NORTH
[32 empty] | 1813 | CUMBY1_T | NORTH
[32 empty] | 1814 | SULSPG_8 | NORTH
[32 empty] | 1815 | CUMBY1_T | NORTH
[32 empty] | 1816 | COMM_SW_ | NORTH
[32 empty] | 1817 | COMM_T8 | NORTH
[32 empty] | 1819 | COMM_S1_ | NORTH
[32 empty] | 1820 | COMMERCE | NORTH
[32 empty] | 1821 | COMMERCE | NORTH
[32 empty] | 1822 | COOPERLK | NORTH
[32 empty] | 1823 | COOPERLK | NORTH
[32 empty] | 1824 | NEYLNDVL | NORTH
[32 empty] | 1826 | CADML_9 | NORTH
[32 empty] | 1827 | CADMLX_T | NORTH
[32 empty] | 1828 | CADMLX_9 | NORTH
[32 empty] | 1829 | BURROW_T | NORTH
[32 empty] | 1830 | ROYSEGIN | NORTH
[32 empty] | 1833 | BRKSTN_T | NORTH
[32 empty] | 1845 | ROANOKE3 | NORTH
[32 empty] | 1847 | ROANOKE1 | NORTH
[32 empty] | 1848 | ROANOKE2 | NORTH
[32 empty] | 1849 | ROANOKE2 | NORTH
[32 empty] | 1850 | ROANOKE1 | NORTH
[32 empty] | 1851 | ROANOKE1 | NORTH
[32 empty] | 1852 | ROANOKE2 | NORTH
[32 empty] | 1853 | ROANOKE2 | NORTH
[32 empty] | 1854 | ROANOKE1 | NORTH
[32 empty] | 1855 | ALLIANCE | NORTH
[32 empty] | 1856 | KELLER1T | NORTH
[32 empty] | 1857 | MCPHERSN | NORTH
[32 empty] | 1858 | PEDANRD_ | NORTH
[32 empty] | 1859 | EAGLEMNT | NORTH
[32 empty] | 1860 | EAGLEMNT | NORTH
[32 empty] | 1861 | EAGLEMNT | NORTH
[32 empty] | 1862 | EAGLEMNT | NORTH
[32 empty] | 1863 | EAGLEMNT | NORTH
[32 empty] | 1866 | ELIZCRK | NORTH
[32 empty] | 1868 | WLFHMDPT | NORTH
[32 empty] | 1869 | BENBRK_A | NORTH
[32 empty] | 1870 | BENBRK_B | NORTH
[32 empty] | 1873 | BENBRK_5 | NORTH
[32 empty] | 1874 | BENBRK_A | NORTH
[32 empty] | 1875 | BENBRK_B | NORTH
[32 empty] | 1876 | WLFHOLW_ | NORTH
[32 empty] | 1877 | WLFHOLW_ | NORTH
[32 empty] | 1878 | WLFHOLW_ | NORTH
[32 empty] | 1879 | WLFHOLW_ | NORTH
[32 empty] | 1880 | ROCKYCRK | NORTH
[32 empty] | 1881 | ROCKYCRK | NORTH
[32 empty] | 1882 | EVRMAN_W | NORTH
[32 empty] | 1883 | EVRMAN_A | NORTH
[32 empty] | 1884 | EVRMAN_B | NORTH
[32 empty] | 1885 | EVRMNTIE | NORTH
[32 empty] | 1886 | EVRMAN_E | NORTH
[32 empty] | 1887 | EVRMNTIE | NORTH
[32 empty] | 1888 | DECRDOVA | NORTH
[32 empty] | 1889 | DECRDOVA | NORTH
[32 empty] | 1890 | DECRDOVA | NORTH
[32 empty] | 1891 | DECRDOVA | NORTH
[32 empty] | 1892 | DECRDOVA | NORTH
[32 empty] | 1893 | DECRDOVA | NORTH
[32 empty] | 1894 | DECRDOVA | NORTH
[32 empty] | 1895 | DECRDOVA | NORTH
[32 empty] | 1898 | COMCHEPK | NORTH
[32 empty] | 1899 | COMCHEPK | NORTH
[32 empty] | 1900 | COMCHPKW | NORTH
[32 empty] | 1902 | JHNSONSW | NORTH
[32 empty] | 1904 | WEBB3_5 | NORTH
[32 empty] | 1905 | GRIFFTH_ | NORTH
[32 empty] | 1906 | VENUS_S5 | NORTH
[32 empty] | 1907 | VENUS_N5 | NORTH
[32 empty] | 1908 | VENUS3_8 | NORTH
[32 empty] | 1909 | VENUS1_8 | NORTH
[32 empty] | 1910 | VENUS2_8 | NORTH
[32 empty] | 1911 | WEBB1_5 | NORTH
[32 empty] | 1912 | MAYFLDN_ | NORTH
[32 empty] | 1913 | MAYFLDN_ | NORTH
[32 empty] | 1914 | MAYFLDS_ | NORTH
[32 empty] | 1916 | LIGGETTA | NORTH
[32 empty] | 1917 | SHRYTAP_ | NORTH
[32 empty] | 1918 | SHRYAUTO | NORTH
[32 empty] | 1919 | SHRY_A8 | NORTH
[32 empty] | 1920 | SHRY_B8 | NORTH
[32 empty] | 1921 | LIGGETTA | NORTH
[32 empty] | 1922 | LIGGETT_ | NORTH
[32 empty] | 1923 | LIGGETTA | NORTH
[32 empty] | 1924 | LIGGETT_ | NORTH
[32 empty] | 1925 | LIGGETTA | NORTH
[32 empty] | 1926 | LIGGETT_ | NORTH
[32 empty] | 1927 | LIGGETT_ | NORTH
[32 empty] | 1928 | LIGGETT_ | NORTH
[32 empty] | 1929 | CENTURY1 | NORTH
[32 empty] | 1930 | CENTURY3 | NORTH
[32 empty] | 1931 | COURTLND | NORTH
[32 empty] | 1932 | KENNDALE | NORTH
[32 empty] | 1934 | SHRYAUTO | NORTH
[32 empty] | 1935 | SYCMRCRK | NORTH
[32 empty] | 1936 | MDLTHELP | NORTH
[32 empty] | 1937 | MDLTHELP | NORTH
[32 empty] | 1938 | MDLTHELP | NORTH
[32 empty] | 1939 | MDLTHELP | NORTH
[32 empty] | 1940 | MDLTHELP | NORTH
[32 empty] | 1941 | MDLTHELP | NORTH
[32 empty] | 1942 | MDLTHELP | NORTH
[32 empty] | 1943 | MDLTHELP | NORTH
[32 empty] | 1944 | MDLTHELP | NORTH
[32 empty] | 1945 | HANDLEY_ | NORTH
[32 empty] | 1946 | HANDLEY_ | NORTH
[32 empty] | 1947 | HANDLEY_ | NORTH
[32 empty] | 1948 | HANDLEY_ | NORTH
[32 empty] | 1949 | HANDLEY_ | NORTH
[32 empty] | 1950 | HANDLEYC | NORTH
[32 empty] | 1951 | HANDLEYD | NORTH
[32 empty] | 1952 | HANDLEY_ | NORTH
[32 empty] | 1955 | CALMONT1 | NORTH
[32 empty] | 1956 | CALMONT1 | NORTH
[32 empty] | 1957 | SAGINAW1 | NORTH
[32 empty] | 1958 | SAGINAW1 | NORTH
[32 empty] | 1961 | NMAIN1_8 | NORTH
[32 empty] | 1962 | ALCON1_8 | NORTH
[32 empty] | 1963 | ALCON2_8 | NORTH
[32 empty] | 1964 | NMAIN1_9 | NORTH
[32 empty] | 1967 | FRSTHILL | NORTH
[32 empty] | 1968 | FRSTHILL | NORTH
[32 empty] | 1970 | HIGHL_E_ | NORTH
[32 empty] | 1972 | LEW_JNS_ | NORTH
[32 empty] | 1984 | ARGYLE1_ | NORTH
[32 empty] | 1985 | CORINTH1 | NORTH
[32 empty] | 1986 | KRUM_T8 | NORTH
[32 empty] | 1987 | KRUM_8 | NORTH
[32 empty] | 1988 | VALVIEW_ | NORTH
[32 empty] | 1989 | KRUM_9 | NORTH
[32 empty] | 1990 | KRUM_P8 | NORTH
[32 empty] | 1993 | ARCO1_8 | NORTH
[32 empty] | 1994 | KRUGRVL1 | NORTH
[32 empty] | 1996 | ATMEL1_T | NORTH
[32 empty] | 1997 | ATMEL2_T | NORTH
[32 empty] | 1998 | ATMEL1_8 | NORTH
[32 empty] | 1999 | ATMEL2_8 | NORTH
[32 empty] | 2001 | IRVNORTH | NORTH
[32 empty] | 2002 | IRVBELT1 | NORTH
[32 empty] | 2003 | IRVBELT1 | NORTH
[32 empty] | 2004 | IRVBELT2 | NORTH
[32 empty] | 2006 | IRVVALVW | NORTH
[32 empty] | 2009 | DFW_SW_8 | NORTH
[32 empty] | 2010 | TRIGAS1_ | NORTH
[32 empty] | 2011 | TRIGAS_8 | NORTH
[32 empty] | 2014 | COPPELTP | NORTH
[32 empty] | 2015 | COPPELL_ | NORTH
[32 empty] | 2016 | EULESS_8 | NORTH
[32 empty] | 2017 | COPELL_S | NORTH
[32 empty] | 2018 | WROANOKE | NORTH
[32 empty] | 2019 | KIMBALL1 | NORTH
[32 empty] | 2020 | STHLAKE1 | NORTH
[32 empty] | 2021 | GV_BALL1 | NORTH
[32 empty] | 2022 | DFW_NW_8 | NORTH
[32 empty] | 2023 | KIMBALL2 | NORTH
[32 empty] | 2024 | MCKAMYRD | NORTH
[32 empty] | 2025 | MCKAMY_T | NORTH
[32 empty] | 2026 | CLYVIL1_ | NORTH
[32 empty] | 2027 | BEARCK1_ | NORTH
[32 empty] | 2028 | CLYVIL2_ | NORTH
[32 empty] | 2029 | CHRYGRV_ | NORTH
[32 empty] | 2030 | FLWRMND_ | NORTH
[32 empty] | 2031 | FLWRMNDS | NORTH
[32 empty] | 2033 | KLR_MAG1 | NORTH
[32 empty] | 2034 | KLR_MAG2 | NORTH
[32 empty] | 2035 | BEARCK3_ | NORTH
[32 empty] | 2036 | KELLER2_ | NORTH
[32 empty] | 2037 | WPKELLR1 | NORTH
[32 empty] | 2038 | WPKELLR2 | NORTH
[32 empty] | 2039 | MEADPRK1 | NORTH
[32 empty] | 2040 | MEADPRK2 | NORTH
[32 empty] | 2041 | SMITHFD1 | NORTH
[32 empty] | 2042 | SMITHFD2 | NORTH
[32 empty] | 2043 | WATAGAN_ | NORTH
[32 empty] | 2044 | WATAGAS_ | NORTH
[32 empty] | 2045 | WATAGA1_ | NORTH
[32 empty] | 2046 | WATAGA2_ | NORTH
[32 empty] | 2047 | HALTOM1_ | NORTH
[32 empty] | 2048 | GEMINI2_ | NORTH
[32 empty] | 2049 | GEMINI1_ | NORTH
[32 empty] | 2050 | BEDFORD1 | NORTH
[32 empty] | 2051 | BD_WDSN1 | NORTH
[32 empty] | 2052 | BD_WDSN2 | NORTH
[32 empty] | 2053 | IRVBELT2 | NORTH
[32 empty] | 2054 | IRVING1_ | NORTH
[32 empty] | 2055 | IRVGRNT1 | NORTH
[32 empty] | 2062 | AZLE1_8 | NORTH
[32 empty] | 2065 | EMCS1_8 | NORTH
[32 empty] | 2066 | ROSEN1_T | NORTH
[32 empty] | 2067 | ROSEN2_T | NORTH
[32 empty] | 2068 | ROSEN1_8 | NORTH
[32 empty] | 2069 | ROSEN2_8 | NORTH
[32 empty] | 2070 | BLUEMD2_ | NORTH
[32 empty] | 2071 | BLUEMD1_ | NORTH
[32 empty] | 2075 | WAGROBT1 | NORTH
[32 empty] | 2077 | FOSLCRK1 | NORTH
[32 empty] | 2085 | SANSOM1_ | NORTH
[32 empty] | 2086 | SANSOM2_ | NORTH
[32 empty] | 2087 | WHILL1_8 | NORTH
[32 empty] | 2088 | WHILL2_8 | NORTH
[32 empty] | 2089 | WHTSTLMN | NORTH
[32 empty] | 2090 | HERTG_D | NORTH
[32 empty] | 2091 | HERTG3_8 | NORTH
[32 empty] | 2092 | HERTG2_8 | NORTH
[32 empty] | 2093 | HERTG1_9 | NORTH
[32 empty] | 2094 | GEN_DYN1 | NORTH
[32 empty] | 2098 | HALTOM2_ | NORTH
[32 empty] | 2099 | RICHLN1_ | NORTH
[32 empty] | 2100 | RICHLN2_ | NORTH
[32 empty] | 2101 | SPRNGDL1 | NORTH
[32 empty] | 2102 | SPRNGDL2 | NORTH
[32 empty] | 2103 | RANDL_W_ | NORTH
[32 empty] | 2104 | RANDL_E_ | NORTH
[32 empty] | 2105 | RANDL1_8 | NORTH
[32 empty] | 2106 | RANDL2_8 | NORTH
[32 empty] | 2109 | WHITE1_T | NORTH
[32 empty] | 2110 | WHITE2_T | NORTH
[32 empty] | 2111 | WHITE1_8 | NORTH
[32 empty] | 2112 | WHITE2_8 | NORTH
[32 empty] | 2113 | TRINITY1 | NORTH
[32 empty] | 2114 | TRINITY3 | NORTH
[32 empty] | 2115 | HURSTN_8 | NORTH
[32 empty] | 2116 | HURSTS_8 | NORTH
[32 empty] | 2117 | DAVIS_T8 | NORTH
[32 empty] | 2121 | EULESS_S | NORTH
[32 empty] | 2123 | PIPELIN1 | NORTH
[32 empty] | 2124 | INT_AIR1 | NORTH
[32 empty] | 2125 | INT_AIR2 | NORTH
[32 empty] | 2128 | WATSON1_ | NORTH
[32 empty] | 2133 | BRKHLW1_ | NORTH
[32 empty] | 2134 | BRKHLW2_ | NORTH
[32 empty] | 2135 | BRKHLW1_ | NORTH
[32 empty] | 2136 | BRKHLW2_ | NORTH
[32 empty] | 2137 | GRT_SW1_ | NORTH
[32 empty] | 2138 | GRT_SW2_ | NORTH
[32 empty] | 2139 | GEN_MOT1 | NORTH
[32 empty] | 2140 | GEN_MOT2 | NORTH
[32 empty] | 2141 | EXECPKWY | NORTH
[32 empty] | 2142 | EXECPKWY | NORTH
[32 empty] | 2146 | AM_MFG_T | NORTH
[32 empty] | 2147 | AM_MFG1_ | NORTH
[32 empty] | 2148 | SPRNGDL_ | NORTH
[32 empty] | 2150 | CURRIE1_ | NORTH
[32 empty] | 2151 | BLACKSTN | NORTH
[32 empty] | 2152 | CARSWELL | NORTH
[32 empty] | 2157 | DENTN_AV | NORTH
[32 empty] | 2158 | DUVAL1_9 | NORTH
[32 empty] | 2159 | BRYN_AV_ | NORTH
[32 empty] | 2160 | BRYN_AV_ | NORTH
[32 empty] | 2161 | MCDONUGH | NORTH
[32 empty] | 2164 | HEMPHILL | NORTH
[32 empty] | 2166 | EPDC_D | NORTH
[32 empty] | 2167 | AYERS1_8 | NORTH
[32 empty] | 2168 | EPDC_ADM | NORTH
[32 empty] | 2169 | EPDC_STH | NORTH
[32 empty] | 2170 | EPDC_FRN | NORTH
[32 empty] | 2172 | MISLTOE1 | NORTH
[32 empty] | 2173 | MISLTOE3 | NORTH
[32 empty] | 2174 | HORNE1_8 | NORTH
[32 empty] | 2175 | HORNE2_8 | NORTH
[32 empty] | 2176 | FARON1_8 | NORTH
[32 empty] | 2177 | FARON2_8 | NORTH
[32 empty] | 2178 | EPDC1_8 | NORTH
[32 empty] | 2179 | EPDC2_8 | NORTH
[32 empty] | 2180 | EPDC3_8 | NORTH
[32 empty] | 2182 | BRYTIRV1 | NORTH
[32 empty] | 2183 | BRYTIRV2 | NORTH
[32 empty] | 2184 | WDGWD_N_ | NORTH
[32 empty] | 2185 | WDGWD_S_ | NORTH
[32 empty] | 2186 | WDGWD1_8 | NORTH
[32 empty] | 2187 | WDGWD2_8 | NORTH
[32 empty] | 2188 | PAFFRD1_ | NORTH
[32 empty] | 2189 | PAFFRD2_ | NORTH
[32 empty] | 2190 | EDGECLF1 | NORTH
[32 empty] | 2191 | EDGECLF2 | NORTH
[32 empty] | 2192 | ROGERS1_ | NORTH
[32 empty] | 2193 | ROGERS2_ | NORTH
[32 empty] | 2194 | ALCON1_T | NORTH
[32 empty] | 2195 | ALCON2_T | NORTH
[32 empty] | 2196 | PRIMRSE1 | NORTH
[32 empty] | 2197 | PRIMRSE3 | NORTH
[32 empty] | 2204 | CRESSON1 | NORTH
[32 empty] | 2205 | CROWLEY1 | NORTH
[32 empty] | 2208 | MANSFLD_ | NORTH
[32 empty] | 2209 | BURLESON | NORTH
[32 empty] | 2210 | JOSHUA_8 | NORTH
[32 empty] | 2211 | ROLLHL1_ | NORTH
[32 empty] | 2212 | ROLLHL2_ | NORTH
[32 empty] | 2213 | TX_STEEL | NORTH
[32 empty] | 2214 | ROLLHL1_ | NORTH
[32 empty] | 2215 | ROLLHL2_ | NORTH
[32 empty] | 2216 | TRWDRLHL | NORTH
[32 empty] | 2219 | BWN_TAT_ | NORTH
[32 empty] | 2220 | TATE_W_T | NORTH
[32 empty] | 2221 | TATE_E_T | NORTH
[32 empty] | 2222 | TATESPG1 | NORTH
[32 empty] | 2223 | TATESPG3 | NORTH
[32 empty] | 2224 | OAKHILL1 | NORTH
[32 empty] | 2225 | OAKHILL2 | NORTH
[32 empty] | 2226 | OAKHILL1 | NORTH
[32 empty] | 2227 | OAKHILL2 | NORTH
[32 empty] | 2232 | BOWEN2_T | NORTH
[32 empty] | 2233 | BOWEN2_8 | NORTH
[32 empty] | 2234 | VILGCRK1 | NORTH
[32 empty] | 2239 | DAVIS1_8 | NORTH
[32 empty] | 2240 | DAVIS2_8 | NORTH
[32 empty] | 2241 | ENNS_W_8 | NORTH
[32 empty] | 2245 | LAKEWD1_ | NORTH
[32 empty] | 2246 | LAKEWD2_ | NORTH
[32 empty] | 2247 | PANTEGO1 | NORTH
[32 empty] | 2248 | BOWEN1_8 | NORTH
[32 empty] | 2250 | BOWEN1_T | NORTH
[32 empty] | 2251 | ARLGTON1 | NORTH
[32 empty] | 2252 | ARLGTON2 | NORTH
[32 empty] | 2257 | PARKROW1 | NORTH
[32 empty] | 2258 | PARKROW2 | NORTH
[32 empty] | 2259 | LTV1_8 | NORTH
[32 empty] | 2260 | POLY_AM1 | NORTH
[32 empty] | 2262 | GRANDPR1 | NORTH
[32 empty] | 2265 | GP_WEST1 | NORTH
[32 empty] | 2270 | SHDYGRV1 | NORTH
[32 empty] | 2271 | IRVHUNT1 | NORTH
[32 empty] | 2272 | BIG3_GP_ | NORTH
[32 empty] | 2273 | IRVHUNT1 | NORTH
[32 empty] | 2274 | DALWRTH1 | NORTH
[32 empty] | 2275 | BIG3_GP_ | NORTH
[32 empty] | 2276 | IRVHUNT2 | NORTH
[32 empty] | 2277 | DCRDVA_D | NORTH
[32 empty] | 2278 | CMPKSTUP | NORTH
[32 empty] | 2279 | CLEBRNSW | NORTH
[32 empty] | 2280 | CLEBRN_N | NORTH
[32 empty] | 2281 | GODLEY_8 | NORTH
[32 empty] | 2283 | AIRLIQD_ | NORTH
[32 empty] | 2290 | CLEBRN_8 | NORTH
[32 empty] | 2291 | CLEBRN_W | NORTH
[32 empty] | 2294 | KEENE_8 | NORTH
[32 empty] | 2297 | ALVARADO | NORTH
[32 empty] | 2298 | ALVARADO | NORTH
[32 empty] | 2300 | CHAPSTL_ | NORTH
[32 empty] | 2301 | CHAPSTLF | NORTH
[32 empty] | 2302 | CHAPSTLF | NORTH
[32 empty] | 2304 | CHAPSTLM | NORTH
[32 empty] | 2305 | AIRPRD_T | NORTH
[32 empty] | 2306 | AIRPRD1_ | NORTH
[32 empty] | 2307 | MDLTHTXI | NORTH
[32 empty] | 2308 | MDLTH_S_ | NORTH
[32 empty] | 2309 | WAX_NW_8 | NORTH
[32 empty] | 2310 | MDLTHTXI | NORTH
[32 empty] | 2311 | MDLTH_N_ | NORTH
[32 empty] | 2312 | TRAILWD_ | NORTH
[32 empty] | 2313 | MDLTH_N_ | NORTH
[32 empty] | 2314 | MDLTHBOX | NORTH
[32 empty] | 2315 | WAX_PMP2 | NORTH
[32 empty] | 2316 | MG_IND_T | NORTH
[32 empty] | 2317 | STERRETT | NORTH
[32 empty] | 2318 | STERRETT | NORTH
[32 empty] | 2319 | WAX_PMP1 | NORTH
[32 empty] | 2320 | WAX_N_8 | NORTH
[32 empty] | 2321 | WAX_8 | NORTH
[32 empty] | 2322 | BARDWELL | NORTH
[32 empty] | 2323 | MG_IND_8 | NORTH
[32 empty] | 2324 | ENNS_S_8 | NORTH
[32 empty] | 2325 | ENNS_8 | NORTH
[32 empty] | 2326 | ENNS_SE_ | NORTH
[32 empty] | 2327 | TRUMBULL | NORTH
[32 empty] | 2328 | RED_OAK1 | NORTH
[32 empty] | 2329 | ENNSSW_8 | NORTH
[32 empty] | 2330 | CRISP1_8 | NORTH
[32 empty] | 2331 | ENNS_PMP | NORTH
[32 empty] | 2332 | TELICO_P | NORTH
[32 empty] | 2335 | WAX_9 | NORTH
[32 empty] | 2336 | FORESTON | NORTH
[32 empty] | 2337 | ITALY_9 | NORTH
[32 empty] | 2338 | MILFRDEX | NORTH
[32 empty] | 2339 | MILFRDEX | NORTH
[32 empty] | 2340 | MELSSA_P | NORTH
[32 empty] | 2342 | FERRISSW | NORTH
[32 empty] | 2343 | WAX_OCF_ | NORTH
[32 empty] | 2344 | PALMER_9 | NORTH
[32 empty] | 2345 | ENNS_9 | NORTH
[32 empty] | 2347 | RICETPL_ | NORTH
[32 empty] | 2348 | RICE_REA | NORTH
[32 empty] | 2349 | ROCKHILL | NORTH
[32 empty] | 2350 | CELINASE | NORTH
[32 empty] | 2351 | INDIA1_9 | NORTH
[32 empty] | 2352 | RNRTPL_W | NORTH
[32 empty] | 2353 | RNRTPL_E | NORTH
[32 empty] | 2354 | RNRTPL1_ | NORTH
[32 empty] | 2355 | RNRTPL1_ | NORTH
[32 empty] | 2356 | RNRDPL_N | NORTH
[32 empty] | 2357 | RNRDPL_S | NORTH
[32 empty] | 2358 | RNRDPL_1 | NORTH
[32 empty] | 2359 | RNRDPL1_ | NORTH
[32 empty] | 2360 | CRLTN_NW | NORTH
[32 empty] | 2361 | CRLTN_NW | NORTH
[32 empty] | 2362 | CRLTN_NW | NORTH
[32 empty] | 2363 | CRLTN_NW | NORTH
[32 empty] | 2364 | COLLIN1_ | NORTH
[32 empty] | 2365 | COLLIN2_ | NORTH
[32 empty] | 2366 | WILSNCRK | NORTH
[32 empty] | 2367 | NTHLK_1T | NORTH
[32 empty] | 2368 | ROLATER2 | NORTH
[32 empty] | 2369 | ROLATER1 | NORTH
[32 empty] | 2370 | COLLINSS | NORTH
[32 empty] | 2371 | COLLIN_1 | NORTH
[32 empty] | 2372 | COLLINSS | NORTH
[32 empty] | 2373 | ANNASW_5 | NORTH
[32 empty] | 2374 | ANNASW_8 | NORTH
[32 empty] | 2376 | HEBRN_P8 | NORTH
[32 empty] | 2377 | AUSRNCH2 | NORTH
[32 empty] | 2378 | AUSRNCH1 | NORTH
[32 empty] | 2381 | NTHLK1_G | NORTH
[32 empty] | 2382 | NTHLK2_G | NORTH
[32 empty] | 2383 | NTHLK3_G | NORTH
[32 empty] | 2385 | NTHLK_S8 | NORTH
[32 empty] | 2386 | NTHLK_N8 | NORTH
[32 empty] | 2387 | HACKBRY1 | NORTH
[32 empty] | 2388 | HACKBRY1 | NORTH
[32 empty] | 2389 | IRV_VR1_ | NORTH
[32 empty] | 2390 | IRV_VR1_ | NORTH
[32 empty] | 2393 | IRV_VR2_ | NORTH
[32 empty] | 2394 | IRVLBJ_W | NORTH
[32 empty] | 2395 | IRVLBJ_E | NORTH
[32 empty] | 2398 | WLEVEE1_ | NORTH
[32 empty] | 2399 | WLEVEE_E | NORTH
[32 empty] | 2400 | WLEVEE_W | NORTH
[32 empty] | 2401 | LKHB_W8 | NORTH
[32 empty] | 2402 | LKHB_E8 | NORTH
[32 empty] | 2403 | LKHB_1T8 | NORTH
[32 empty] | 2404 | NORWD_1T | NORTH
[32 empty] | 2405 | NORWDPL_ | NORTH
[32 empty] | 2406 | NORWD1_5 | NORTH
[32 empty] | 2407 | NORWDPL_ | NORTH
[32 empty] | 2408 | NORWD1_8 | NORTH
[32 empty] | 2409 | NORWD2_8 | NORTH
[32 empty] | 2410 | NORWD_1T | NORTH
[32 empty] | 2411 | MTCK_W8 | NORTH
[32 empty] | 2412 | MTCK_E8 | NORTH
[32 empty] | 2413 | MTCK6_G | NORTH
[32 empty] | 2414 | MTCK7_G | NORTH
[32 empty] | 2415 | MTCK_1T8 | NORTH
[32 empty] | 2416 | MTCK1_9 | NORTH
[32 empty] | 2417 | MTCK8_G | NORTH
[32 empty] | 2418 | MTCK2_G | NORTH
[32 empty] | 2419 | MTCK3_G | NORTH
[32 empty] | 2420 | CHILSW1_ | NORTH
[32 empty] | 2421 | CHILSW_S | NORTH
[32 empty] | 2422 | CHILSW_N | NORTH
[32 empty] | 2423 | NORWD_2T | NORTH
[32 empty] | 2424 | DESSW1_8 | NORTH
[32 empty] | 2425 | DESPKV1_ | NORTH
[32 empty] | 2426 | GLNHGHTS | NORTH
[32 empty] | 2427 | WATMLL_W | NORTH
[32 empty] | 2428 | WATMLL_E | NORTH
[32 empty] | 2429 | WATMLL_E | NORTH
[32 empty] | 2430 | WATMLL_W | NORTH
[32 empty] | 2431 | DESSW1_5 | NORTH
[32 empty] | 2432 | TRICRN1_ | NORTH
[32 empty] | 2433 | SGVLSW1_ | NORTH
[32 empty] | 2434 | SGVLSW1_ | NORTH
[32 empty] | 2435 | WATMLL_1 | NORTH
[32 empty] | 2437 | FRNY1_5 | NORTH
[32 empty] | 2438 | FRNY1_8 | NORTH
[32 empty] | 2439 | CNVLSW_W | NORTH
[32 empty] | 2440 | PARKD_1T | NORTH
[32 empty] | 2441 | PRCKSW1_ | NORTH
[32 empty] | 2442 | PARKDB1_ | NORTH
[32 empty] | 2444 | PARKD1_9 | NORTH
[32 empty] | 2445 | PARKDB2_ | NORTH
[32 empty] | 2450 | CNVLSW_E | NORTH
[32 empty] | 2451 | LKHB1_G | NORTH
[32 empty] | 2452 | LKHB2_G | NORTH
[32 empty] | 2453 | CNVLSW1_ | NORTH
[32 empty] | 2456 | KRKPK_E8 | NORTH
[32 empty] | 2457 | KRKPK_W8 | NORTH
[32 empty] | 2458 | KRKPK_1T | NORTH
[32 empty] | 2459 | KRKPK_2T | NORTH
[32 empty] | 2460 | ROYSE3_8 | NORTH
[32 empty] | 2461 | ROYSE_N5 | NORTH
[32 empty] | 2462 | ROYSE2_8 | NORTH
[32 empty] | 2463 | ROYSE2_9 | NORTH
[32 empty] | 2471 | ROYSE_A8 | NORTH
[32 empty] | 2472 | ROYSE_B8 | NORTH
[32 empty] | 2473 | ROYSE1_8 | NORTH
[32 empty] | 2474 | ROYSE1_T | NORTH
[32 empty] | 2478 | ROYSE_S5 | NORTH
[32 empty] | 2479 | WLEVEE_1 | NORTH
[32 empty] | 2480 | WLEVEE_2 | NORTH
[32 empty] | 2481 | ELEVEE_W | NORTH
[32 empty] | 2482 | ELEVEE_E | NORTH
[32 empty] | 2483 | ROYSE3_5 | NORTH
[32 empty] | 2486 | CCRST_9 | NORTH
[32 empty] | 2487 | DENDR_E8 | NORTH
[32 empty] | 2488 | DENDR_W8 | NORTH
[32 empty] | 2489 | DENDR1_9 | NORTH
[32 empty] | 2490 | DENDR2_9 | NORTH
[32 empty] | 2491 | FSHCRK1_ | NORTH
[32 empty] | 2492 | FSHCRK1_ | NORTH
[32 empty] | 2493 | CCRST_W8 | NORTH
[32 empty] | 2494 | CCRST_E8 | NORTH
[32 empty] | 2495 | CCRST_1T | NORTH
[32 empty] | 2509 | ALLENSW_ | NORTH
[32 empty] | 2510 | ALLENSW_ | NORTH
[32 empty] | 2511 | ALLENSW1 | NORTH
[32 empty] | 2512 | ALLENSW2 | NORTH
[32 empty] | 2513 | ALLENSW1 | NORTH
[32 empty] | 2514 | ALLENSW2 | NORTH
[32 empty] | 2515 | LEBNON_P | NORTH
[32 empty] | 2516 | MCDERMT_ | NORTH
[32 empty] | 2517 | BRIDGES_ | NORTH
[32 empty] | 2518 | COLONY_8 | NORTH
[32 empty] | 2519 | CRLTNFRK | NORTH
[32 empty] | 2520 | ANNAGCEC | NORTH
[32 empty] | 2521 | PL_COIT2 | NORTH
[32 empty] | 2522 | PL_TENNY | NORTH
[32 empty] | 2523 | PL_TENNY | NORTH
[32 empty] | 2524 | PL_COIT1 | NORTH
[32 empty] | 2525 | PL_CUSTR | NORTH
[32 empty] | 2526 | PL_CUSTR | NORTH
[32 empty] | 2527 | STONEYPT | NORTH
[32 empty] | 2528 | ANNASW_T | NORTH
[32 empty] | 2529 | MCKNY1_8 | NORTH
[32 empty] | 2530 | MCKNY_SW | NORTH
[32 empty] | 2531 | ALLEN1_8 | NORTH
[32 empty] | 2532 | MCKNY_TI | NORTH
[32 empty] | 2533 | ALLEN_N1 | NORTH
[32 empty] | 2535 | CRLTNUF1 | NORTH
[32 empty] | 2536 | CRLTNUF2 | NORTH
[32 empty] | 2537 | CRLTN1_8 | NORTH
[32 empty] | 2538 | MONETY1_ | NORTH
[32 empty] | 2539 | MONETY2_ | NORTH
[32 empty] | 2540 | CROWN1_8 | NORTH
[32 empty] | 2541 | CROWN2_8 | NORTH
[32 empty] | 2542 | HENSTL1T | NORTH
[32 empty] | 2543 | HENSTL1_ | NORTH
[32 empty] | 2544 | CHAMBVLE | NORTH
[32 empty] | 2546 | MCKNY2_8 | NORTH
[32 empty] | 2547 | MCKNY_SW | NORTH
[32 empty] | 2548 | ALLEN_N2 | NORTH
[32 empty] | 2549 | ALLEN2_8 | NORTH
[32 empty] | 2550 | LASCOL1_ | NORTH
[32 empty] | 2551 | LASCOL2_ | NORTH
[32 empty] | 2552 | IRVNE1_8 | NORTH
[32 empty] | 2553 | MCKNYWHT | NORTH
[32 empty] | 2555 | CRLTNJSY | NORTH
[32 empty] | 2558 | CRLTNTAR | NORTH
[32 empty] | 2559 | CRLTNTAR | NORTH
[32 empty] | 2560 | MCKNY_TI | NORTH
[32 empty] | 2561 | MCKNYWHT | NORTH
[32 empty] | 2562 | CRLTNRMD | NORTH
[32 empty] | 2564 | N_PARK4_ | NORTH
[32 empty] | 2565 | N_PARK3_ | NORTH
[32 empty] | 2566 | CUSTER1_ | NORTH
[32 empty] | 2567 | CUSTER2_ | NORTH
[32 empty] | 2569 | ADSN1_8 | NORTH
[32 empty] | 2571 | CRLTNCC1 | NORTH
[32 empty] | 2576 | ADSN1T_8 | NORTH
[32 empty] | 2577 | ADSN2T_8 | NORTH
[32 empty] | 2578 | CRLTNE_8 | NORTH
[32 empty] | 2580 | ELMFKN1_ | NORTH
[32 empty] | 2581 | ELMFKN2_ | NORTH
[32 empty] | 2582 | FBGILS1_ | NORTH
[32 empty] | 2583 | FB1_8 | NORTH
[32 empty] | 2586 | ELMFK1T_ | NORTH
[32 empty] | 2587 | ELMFK2T_ | NORTH
[32 empty] | 2588 | ELMFK1_8 | NORTH
[32 empty] | 2589 | ELMFK2_8 | NORTH
[32 empty] | 2590 | NLKPMP1T | NORTH
[32 empty] | 2591 | NLKPMP1_ | NORTH
[32 empty] | 2595 | AIRLIQD1 | NORTH
[32 empty] | 2596 | ALPHA1_8 | NORTH
[32 empty] | 2597 | ALPHA2_8 | NORTH
[32 empty] | 2606 | AIRLIQD1 | NORTH
[32 empty] | 2607 | WALNT1T_ | NORTH
[32 empty] | 2608 | WALNT1_8 | NORTH
[32 empty] | 2609 | WALNT2T_ | NORTH
[32 empty] | 2610 | WALNT2_8 | NORTH
[32 empty] | 2611 | KNLTR2T_ | NORTH
[32 empty] | 2612 | KNLTR1T_ | NORTH
[32 empty] | 2613 | KNLTR2_8 | NORTH
[32 empty] | 2614 | KNLTR1_8 | NORTH
[32 empty] | 2615 | PSTNTH1_ | NORTH
[32 empty] | 2616 | PSTNTH2_ | NORTH
[32 empty] | 2617 | MDWCK1_8 | NORTH
[32 empty] | 2618 | MDWCK2_8 | NORTH
[32 empty] | 2623 | FRNKFD1_ | NORTH
[32 empty] | 2624 | FRNKFD2_ | NORTH
[32 empty] | 2627 | BLTLIN1_ | NORTH
[32 empty] | 2628 | BLTLIN2_ | NORTH
[32 empty] | 2633 | TIDPL1_8 | NORTH
[32 empty] | 2634 | TIDPL2_8 | NORTH
[32 empty] | 2636 | SCHDRD1_ | NORTH
[32 empty] | 2637 | SCHDRD2_ | NORTH
[32 empty] | 2638 | COIT2_8 | NORTH
[32 empty] | 2639 | COIT1_8 | NORTH
[32 empty] | 2640 | JUDD1T_8 | NORTH
[32 empty] | 2642 | JUDD1_8 | NORTH
[32 empty] | 2647 | CENEXP1_ | NORTH
[32 empty] | 2648 | CENEXP2_ | NORTH
[32 empty] | 2651 | BANDRA1T | NORTH
[32 empty] | 2652 | BANDRA2T | NORTH
[32 empty] | 2653 | BANDRA1_ | NORTH
[32 empty] | 2654 | BANDRA2_ | NORTH
[32 empty] | 2657 | NTHHVN_W | NORTH
[32 empty] | 2658 | NTHHVN_E | NORTH
[32 empty] | 2659 | NTHHVN_1 | NORTH
[32 empty] | 2660 | WELCH1_8 | NORTH
[32 empty] | 2661 | WELCH2_8 | NORTH
[32 empty] | 2662 | MARSH1_8 | NORTH
[32 empty] | 2663 | MARSH2_8 | NORTH
[32 empty] | 2664 | SPRNGCRK | NORTH
[32 empty] | 2668 | SPRNGCRK | NORTH
[32 empty] | 2671 | PL_ARCO_ | NORTH
[32 empty] | 2673 | PL_WEST_ | NORTH
[32 empty] | 2674 | PL_8 | NORTH
[32 empty] | 2675 | W_PL_TI2 | NORTH
[32 empty] | 2676 | W_PL_TI1 | NORTH
[32 empty] | 2677 | PL_ALMA_ | NORTH
[32 empty] | 2678 | PL_PARKR | NORTH
[32 empty] | 2679 | W_PL_TI1 | NORTH
[32 empty] | 2680 | W_PL_TI2 | NORTH
[32 empty] | 2683 | RICH1_8 | NORTH
[32 empty] | 2684 | RICH_SV_ | NORTH
[32 empty] | 2685 | RICHCLLN | NORTH
[32 empty] | 2686 | RICHCLLN | NORTH
[32 empty] | 2687 | PL_JUPTR | NORTH
[32 empty] | 2688 | ROMJUARZ | NORTH
[32 empty] | 2689 | RICH_SC_ | NORTH
[32 empty] | 2690 | RICH_E_8 | NORTH
[32 empty] | 2691 | PL_SHILO | NORTH
[32 empty] | 2692 | LAVNPMP2 | NORTH
[32 empty] | 2693 | WYLIE_P8 | NORTH
[32 empty] | 2694 | LAVON1_8 | NORTH
[32 empty] | 2695 | LAVNPMP1 | NORTH
[32 empty] | 2696 | MURPHY1_ | NORTH
[32 empty] | 2697 | NW_WYLIE | NORTH
[32 empty] | 2698 | RICH_WH_ | NORTH
[32 empty] | 2699 | FORSTV1_ | NORTH
[32 empty] | 2700 | GARLW1_8 | NORTH
[32 empty] | 2701 | GARL1_8 | NORTH
[32 empty] | 2702 | RCKWL_8 | NORTH
[32 empty] | 2705 | GDELMGRV | NORTH
[32 empty] | 2707 | PRNCETON | NORTH
[32 empty] | 2708 | CLIMAX_P | NORTH
[32 empty] | 2710 | RCKWL_E1 | NORTH
[32 empty] | 2711 | RCKWL_S1 | NORTH
[32 empty] | 2712 | FORNEY_W | NORTH
[32 empty] | 2713 | BLACKLAN | NORTH
[32 empty] | 2715 | TERRL_N_ | NORTH
[32 empty] | 2716 | NW_TERRL | NORTH
[32 empty] | 2717 | NW_TERRL | NORTH
[32 empty] | 2718 | TERRL_N_ | NORTH
[32 empty] | 2719 | AIRCO_T8 | NORTH
[32 empty] | 2720 | AIRCO_8 | NORTH
[32 empty] | 2721 | TERRLSW_ | NORTH
[32 empty] | 2722 | TERRLSW_ | NORTH
[32 empty] | 2723 | ROSEHILL | NORTH
[32 empty] | 2724 | KAUFMN_8 | NORTH
[32 empty] | 2725 | OAKGROVE | NORTH
[32 empty] | 2726 | KEMP_S_8 | NORTH
[32 empty] | 2727 | CRANDALL | NORTH
[32 empty] | 2728 | KAUFMN_S | NORTH
[32 empty] | 2729 | MUNSON1_ | NORTH
[32 empty] | 2730 | QUINLAN_ | NORTH
[32 empty] | 2731 | TERRL_S1 | NORTH
[32 empty] | 2732 | MARSHLL_ | NORTH
[32 empty] | 2733 | RCKWL_AL | NORTH
[32 empty] | 2735 | DALRCKRD | NORTH
[32 empty] | 2736 | ROWLETT_ | NORTH
[32 empty] | 2739 | GRLBTWN_ | NORTH
[32 empty] | 2740 | GRLDBTWN | NORTH
[32 empty] | 2742 | MSQTN1T_ | NORTH
[32 empty] | 2743 | SCYENE1T | NORTH
[32 empty] | 2744 | SCYENE2T | NORTH
[32 empty] | 2745 | SCYENE1_ | NORTH
[32 empty] | 2746 | SCYENE2_ | NORTH
[32 empty] | 2747 | THRNE1T_ | NORTH
[32 empty] | 2748 | JMLLER1_ | NORTH
[32 empty] | 2750 | THRNE1_8 | NORTH
[32 empty] | 2751 | THRNE2_8 | NORTH
[32 empty] | 2752 | MSQTFR1_ | NORTH
[32 empty] | 2754 | MSQTW1_8 | NORTH
[32 empty] | 2756 | MSQTE1_8 | NORTH
[32 empty] | 2759 | MSQTWE1_ | NORTH
[32 empty] | 2762 | PRCK2_8 | NORTH
[32 empty] | 2763 | PRCK1_8 | NORTH
[32 empty] | 2765 | MSQTTE1_ | NORTH
[32 empty] | 2766 | MSQTN1_8 | NORTH
[32 empty] | 2767 | MESQTE1T | NORTH
[32 empty] | 2769 | ESIDE1T_ | NORTH
[32 empty] | 2770 | ESIDE1_8 | NORTH
[32 empty] | 2771 | ESIDE2T_ | NORTH
[32 empty] | 2772 | ESIDE2_8 | NORTH
[32 empty] | 2775 | MSQT1_8 | NORTH
[32 empty] | 2776 | BCHSPG1T | NORTH
[32 empty] | 2777 | BCHSPG1_ | NORTH
[32 empty] | 2779 | LAWSON1_ | NORTH
[32 empty] | 2780 | MRSNLN1_ | NORTH
[32 empty] | 2781 | MRSNLN2_ | NORTH
[32 empty] | 2782 | MRSN_E8 | NORTH
[32 empty] | 2783 | MRSN_W8 | NORTH
[32 empty] | 2784 | LOMBRY1_ | NORTH
[32 empty] | 2785 | LOMBRY2_ | NORTH
[32 empty] | 2786 | LKMT1T_8 | NORTH
[32 empty] | 2787 | LKMT2T_8 | NORTH
[32 empty] | 2788 | LKMT1_8 | NORTH
[32 empty] | 2789 | LKMT2_8 | NORTH
[32 empty] | 2792 | MAPLE2_9 | NORTH
[32 empty] | 2793 | COLVLE2_ | NORTH
[32 empty] | 2794 | MRSN_1T8 | NORTH
[32 empty] | 2795 | MRSN_2T8 | NORTH
[32 empty] | 2796 | EPCNT1T_ | NORTH
[32 empty] | 2797 | EPCNT2T_ | NORTH
[32 empty] | 2798 | EPCNT1_8 | NORTH
[32 empty] | 2799 | EPCNT2_8 | NORTH
[32 empty] | 2800 | REGRW1_8 | NORTH
[32 empty] | 2801 | REGRW2_8 | NORTH
[32 empty] | 2804 | TRA1_8 | NORTH
[32 empty] | 2805 | IRVHUNT2 | NORTH
[32 empty] | 2806 | 800NET_D | NORTH
[32 empty] | 2807 | 900NET_D | NORTH
[32 empty] | 2808 | 8009001_ | NORTH
[32 empty] | 2809 | 8009002_ | NORTH
[32 empty] | 2810 | 8009003_ | NORTH
[32 empty] | 2811 | CHNLR1_8 | NORTH
[32 empty] | 2812 | CHNLR2_8 | NORTH
[32 empty] | 2813 | RECCRS1_ | NORTH
[32 empty] | 2814 | RECCRS2_ | NORTH
[32 empty] | 2815 | AMELIA1_ | NORTH
[32 empty] | 2816 | AMELIA2_ | NORTH
[32 empty] | 2817 | MAPLE1_8 | NORTH
[32 empty] | 2818 | COLVLE1_ | NORTH
[32 empty] | 2819 | REAGAN1_ | NORTH
[32 empty] | 2820 | REAGAN2_ | NORTH
[32 empty] | 2821 | LEMMON1_ | NORTH
[32 empty] | 2822 | LEMMON2_ | NORTH
[32 empty] | 2823 | UTSWMC1_ | NORTH
[32 empty] | 2824 | UTSWMC2_ | NORTH
[32 empty] | 2828 | LMOALT2_ | NORTH
[32 empty] | 2829 | LMOALT1_ | NORTH
[32 empty] | 2832 | WDAL2T_8 | NORTH
[32 empty] | 2833 | WDAL2_8 | NORTH
[32 empty] | 2836 | TRA2_8 | NORTH
[32 empty] | 2837 | CALUMT2T | NORTH
[32 empty] | 2838 | CALUMT2_ | NORTH
[32 empty] | 2842 | DEALEY1_ | NORTH
[32 empty] | 2845 | WDAL1_8 | NORTH
[32 empty] | 2846 | WMRLDN1_ | NORTH
[32 empty] | 2849 | DAVST1T_ | NORTH
[32 empty] | 2850 | DAVST1_8 | NORTH
[32 empty] | 2851 | TPC1_8 | NORTH
[32 empty] | 2852 | CALUMT1_ | NORTH
[32 empty] | 2857 | DRAGON2_ | NORTH
[32 empty] | 2858 | DRAGON1_ | NORTH
[32 empty] | 2859 | FLYNN_N8 | NORTH
[32 empty] | 2860 | FLYNN_S8 | NORTH
[32 empty] | 2861 | NNET1_8 | NORTH
[32 empty] | 2862 | NNET2_8 | NORTH
[32 empty] | 2863 | NNET3_8 | NORTH
[32 empty] | 2864 | FARMNT1_ | NORTH
[32 empty] | 2865 | FARMNT2_ | NORTH
[32 empty] | 2866 | NNET_D | NORTH
[32 empty] | 2868 | ARMSTG1_ | NORTH
[32 empty] | 2869 | ARMSTG2_ | NORTH
[32 empty] | 2873 | WNET_D | NORTH
[32 empty] | 2874 | WNET1_8 | NORTH
[32 empty] | 2875 | WNET2_8 | NORTH
[32 empty] | 2876 | WNET3_8 | NORTH
[32 empty] | 2882 | GRNVL_W8 | NORTH
[32 empty] | 2883 | GRNVL_E8 | NORTH
[32 empty] | 2884 | BLKWEL1_ | NORTH
[32 empty] | 2885 | BLKWEL2_ | NORTH
[32 empty] | 2886 | JENKNS1_ | NORTH
[32 empty] | 2887 | JENKNS2_ | NORTH
[32 empty] | 2890 | MTLDA1_8 | NORTH
[32 empty] | 2891 | MTLDA2_8 | NORTH
[32 empty] | 2894 | ABRAMS1_ | NORTH
[32 empty] | 2895 | ABRAMS2_ | NORTH
[32 empty] | 2896 | LAWTHR1_ | NORTH
[32 empty] | 2897 | LAWTHR2_ | NORTH
[32 empty] | 2898 | HSKEL1T_ | NORTH
[32 empty] | 2899 | HSKEL1_8 | NORTH
[32 empty] | 2900 | HSKEL2_8 | NORTH
[32 empty] | 2902 | ENET_D | NORTH
[32 empty] | 2903 | ENET1_8 | NORTH
[32 empty] | 2904 | ENET2_8 | NORTH
[32 empty] | 2905 | ENET3_8 | NORTH
[32 empty] | 2906 | NNET1T_8 | NORTH
[32 empty] | 2907 | BRYNST1_ | NORTH
[32 empty] | 2908 | BRYNST2_ | NORTH
[32 empty] | 2913 | WHTRCK1_ | NORTH
[32 empty] | 2914 | WHTRCK2_ | NORTH
[32 empty] | 2915 | EZACH1_8 | NORTH
[32 empty] | 2916 | EZACH2_8 | NORTH
[32 empty] | 2917 | CNVL1_8 | NORTH
[32 empty] | 2918 | CNVL2_8 | NORTH
[32 empty] | 2919 | GARLDPL1 | NORTH
[32 empty] | 2920 | GARLDPL2 | NORTH
[32 empty] | 2921 | PLRD1_8 | NORTH
[32 empty] | 2922 | PLRD2_8 | NORTH
[32 empty] | 2923 | LKHLS1T_ | NORTH
[32 empty] | 2924 | LKHLS2T_ | NORTH
[32 empty] | 2925 | LKHLS1_8 | NORTH
[32 empty] | 2926 | LKHLS2_8 | NORTH
[32 empty] | 2927 | FAIROK1_ | NORTH
[32 empty] | 2928 | FAIROK2_ | NORTH
[32 empty] | 2929 | FORSTV2T | NORTH
[32 empty] | 2930 | FORSTV2_ | NORTH
[32 empty] | 2931 | JUDD2_8 | NORTH
[32 empty] | 2934 | DUCKCK1T | NORTH
[32 empty] | 2935 | DUCKCK1_ | NORTH
[32 empty] | 2936 | LKHBPMP_ | NORTH
[32 empty] | 2939 | STAUG1T_ | NORTH
[32 empty] | 2940 | SARGT_3T | NORTH
[32 empty] | 2941 | SARGT_4T | NORTH
[32 empty] | 2944 | STAUG1_8 | NORTH
[32 empty] | 2945 | LKJN1_8 | NORTH
[32 empty] | 2946 | SARGT1_5 | NORTH
[32 empty] | 2947 | SARGT_1T | NORTH
[32 empty] | 2948 | SARGT_S8 | NORTH
[32 empty] | 2949 | SARGT_N8 | NORTH
[32 empty] | 2950 | SARGT_2T | NORTH
[32 empty] | 2951 | STAUG2T_ | NORTH
[32 empty] | 2952 | PLGRV2T_ | NORTH
[32 empty] | 2953 | PLGRV2_8 | NORTH
[32 empty] | 2954 | MURDCK1T | NORTH
[32 empty] | 2955 | MURDCK1_ | NORTH
[32 empty] | 2956 | STAUG2_8 | NORTH
[32 empty] | 2957 | LKJN2_8 | NORTH
[32 empty] | 2960 | PLGRV1T_ | NORTH
[32 empty] | 2961 | PLGRV1_8 | NORTH
[32 empty] | 2962 | MURDCK2T | NORTH
[32 empty] | 2963 | MURDCK2_ | NORTH
[32 empty] | 2964 | HUTCH1_8 | NORTH
[32 empty] | 2965 | SSWWT1T_ | NORTH
[32 empty] | 2966 | SSWWT1_8 | NORTH
[32 empty] | 2969 | OAKLND1T | NORTH
[32 empty] | 2970 | OAKLND1_ | NORTH
[32 empty] | 2971 | OAKLND2_ | NORTH
[32 empty] | 2972 | SUTHLD1_ | NORTH
[32 empty] | 2973 | SUTHLD2_ | NORTH
[32 empty] | 2974 | INDUST_W | NORTH
[32 empty] | 2975 | INDUST_1 | NORTH
[32 empty] | 2976 | INDUST_E | NORTH
[32 empty] | 2977 | WALLST1_ | NORTH
[32 empty] | 2981 | CMPTON1_ | NORTH
[32 empty] | 2982 | CMPTON2_ | NORTH
[32 empty] | 2983 | WALLST2_ | NORTH
[32 empty] | 2984 | BUNTIN1_ | NORTH
[32 empty] | 2985 | BUNTIN2_ | NORTH
[32 empty] | 2986 | SMPST2T_ | NORTH
[32 empty] | 2987 | SMPST2_8 | NORTH
[32 empty] | 2988 | SMPST1_8 | NORTH
[32 empty] | 2989 | SCLFPMP1 | NORTH
[32 empty] | 2990 | CMPWSD2_ | NORTH
[32 empty] | 2992 | STHTN1_8 | NORTH
[32 empty] | 2993 | STHTN2_8 | NORTH
[32 empty] | 2994 | LVBRD1T_ | NORTH
[32 empty] | 2995 | LVBRD1_8 | NORTH
[32 empty] | 2997 | WATMLL_2 | NORTH
[32 empty] | 2999 | DVIL1_8 | NORTH
[32 empty] | 3004 | WMRLD2_8 | NORTH
[32 empty] | 3009 | HERTG3_T | NORTH
[32 empty] | 3010 | HERTG2_T | NORTH
[32 empty] | 3011 | HERTG1_T | NORTH
[32 empty] | 3014 | CKRELL1_ | NORTH
[32 empty] | 3015 | CKRELL2_ | NORTH
[32 empty] | 3016 | HMPTN1_8 | NORTH
[32 empty] | 3017 | HMPTN2_8 | NORTH
[32 empty] | 3018 | POLK1T_8 | NORTH
[32 empty] | 3019 | POLK2T_8 | NORTH
[32 empty] | 3020 | POLK1_8 | NORTH
[32 empty] | 3021 | POLK2_8 | NORTH
[32 empty] | 3022 | DAVST2_8 | NORTH
[32 empty] | 3023 | SOKCF1_8 | NORTH
[32 empty] | 3024 | SOKCF2_8 | NORTH
[32 empty] | 3032 | LVBRD2T_ | NORTH
[32 empty] | 3035 | LVBRD2_8 | NORTH
[32 empty] | 3042 | WMRLD1_8 | NORTH
[32 empty] | 3043 | LTV1_9 | NORTH
[32 empty] | 3044 | LTV2_9 | NORTH
[32 empty] | 3046 | EGLFD1T_ | NORTH
[32 empty] | 3048 | EGLFD1_8 | NORTH
[32 empty] | 3049 | EGLFD2_8 | NORTH
[32 empty] | 3050 | SORCEY1_ | NORTH
[32 empty] | 3051 | SORCEY2_ | NORTH
[32 empty] | 3052 | DVILS1_8 | NORTH
[32 empty] | 3053 | CHILTPL_ | NORTH
[32 empty] | 3054 | CHCLRKRD | NORTH
[32 empty] | 3055 | CHCLRKRD | NORTH
[32 empty] | 3056 | CHCLRKRD | NORTH
[32 empty] | 3057 | CHILTPL3 | NORTH
[32 empty] | 3058 | CHILTPL4 | NORTH
[32 empty] | 3059 | DESHPR1_ | NORTH
[32 empty] | 3060 | DESPLR1_ | NORTH
[32 empty] | 3066 | LNCST1_8 | NORTH
[32 empty] | 3067 | WITTRD1_ | NORTH
[32 empty] | 3076 | SGVL1_8 | NORTH
[32 empty] | 3077 | KLEBRG1T | NORTH
[32 empty] | 3078 | KLEBRG1_ | NORTH
[32 empty] | 3079 | SSWWT2T_ | NORTH
[32 empty] | 3080 | SSWWT2_8 | NORTH
[32 empty] | 3081 | SSWWT_P9 | NORTH
[32 empty] | 3083 | WILMER1_ | NORTH
[32 empty] | 3084 | WILMER1_ | NORTH
[32 empty] | 3097 | MARTLAKE | NORTH
[32 empty] | 3098 | MARTLAKE | NORTH
[32 empty] | 3099 | MARTLAKE | NORTH
[32 empty] | 3100 | MARTINLK | NORTH
[32 empty] | 3102 | TYLERGND | NORTH
[32 empty] | 3103 | SHAMBRGR | NORTH
[32 empty] | 3104 | SHAMBRGR | NORTH
[32 empty] | 3105 | ELKTON_5 | NORTH
[32 empty] | 3106 | ELKTON_8 | NORTH
[32 empty] | 3107 | STRYKER_ | NORTH
[32 empty] | 3108 | STRYKER_ | NORTH
[32 empty] | 3109 | STRYKER_ | NORTH
[32 empty] | 3110 | STRYKER_ | NORTH
[32 empty] | 3112 | SMRFLDMT | NORTH
[32 empty] | 3114 | PALTALCO | NORTH
[32 empty] | 3116 | MTENTRPR | NORTH
[32 empty] | 3117 | LUFKNSS_ | NORTH
[32 empty] | 3118 | LUFKNSS_ | NORTH
[32 empty] | 3119 | NACOGDSE | NORTH
[32 empty] | 3120 | NACOGDSE | NORTH
[32 empty] | 3123 | TRINDAD1 | NORTH
[32 empty] | 3124 | TRINDAD2 | NORTH
[32 empty] | 3125 | TDADTMOD | NORTH
[32 empty] | 3126 | TRINIDAD | NORTH
[32 empty] | 3127 | TRINIDAD | NORTH
[32 empty] | 3128 | TRINIDAD | NORTH
[32 empty] | 3130 | FOREGROV | NORTH
[32 empty] | 3131 | FOREGROV | NORTH
[32 empty] | 3133 | RICHLND1 | NORTH
[32 empty] | 3134 | RICHLND2 | NORTH
[32 empty] | 3139 | TYLERWES | NORTH
[32 empty] | 3140 | TYLERWES | NORTH
[32 empty] | 3141 | TYLERNW_ | NORTH
[32 empty] | 3142 | TYLERNW_ | NORTH
[32 empty] | 3143 | TYLERSE_ | NORTH
[32 empty] | 3144 | OVERTON_ | NORTH
[32 empty] | 3145 | JAXVLNTA | NORTH
[32 empty] | 3146 | JAXVLNOR | NORTH
[32 empty] | 3147 | TROUPSS_ | NORTH
[32 empty] | 3148 | TROUPSS_ | NORTH
[32 empty] | 3149 | MTSELMAN | NORTH
[32 empty] | 3150 | TROUPMTR | NORTH
[32 empty] | 3151 | TROUP_9 | NORTH
[32 empty] | 3152 | ARPCHIPR | NORTH
[32 empty] | 3153 | ARP_9 | NORTH
[32 empty] | 3154 | DIBOLSP_ | NORTH
[32 empty] | 3155 | DIBOLL_8 | NORTH
[32 empty] | 3160 | DIALVILL | NORTH
[32 empty] | 3161 | DIALVILL | NORTH
[32 empty] | 3162 | RUSK_9 | NORTH
[32 empty] | 3167 | ENTERPRI | NORTH
[32 empty] | 3168 | IRONBRTA | NORTH
[32 empty] | 3169 | IRONBRG_ | NORTH
[32 empty] | 3170 | EMORY_8 | NORTH
[32 empty] | 3171 | EMORYNOR | NORTH
[32 empty] | 3173 | EXPMTR_8 | NORTH
[32 empty] | 3174 | CANTNSW_ | NORTH
[32 empty] | 3175 | CANTON_8 | NORTH
[32 empty] | 3176 | MABANK_8 | NORTH
[32 empty] | 3177 | EUSTACE_ | NORTH
[32 empty] | 3178 | EUSTCSE_ | NORTH
[32 empty] | 3181 | EDGEWOOD | NORTH
[32 empty] | 3182 | EDGEWOOD | NORTH
[32 empty] | 3183 | VAN_8 | NORTH
[32 empty] | 3184 | PRIMROSE | NORTH
[32 empty] | 3185 | IRONBRG_ | NORTH
[32 empty] | 3187 | IRNBRGTA | NORTH
[32 empty] | 3188 | WILLSPNT | NORTH
[32 empty] | 3189 | BTSTARTA | NORTH
[32 empty] | 3190 | BRITSTAR | NORTH
[32 empty] | 3191 | DUCKCVTA | NORTH
[32 empty] | 3192 | DUCKCOVE | NORTH
[32 empty] | 3196 | TYLERSWE | NORTH
[32 empty] | 3197 | TYLERSW_ | NORTH
[32 empty] | 3198 | TYLRKLLY | NORTH
[32 empty] | 3201 | LINDALE_ | NORTH
[32 empty] | 3202 | SWANTWO_ | NORTH
[32 empty] | 3203 | LNDALTAP | NORTH
[32 empty] | 3204 | TYLERPIP | NORTH
[32 empty] | 3205 | HIDAWYLK | NORTH
[32 empty] | 3207 | TYLER_9 | NORTH
[32 empty] | 3208 | DELEKTAP | NORTH
[32 empty] | 3209 | DELEK1_8 | NORTH
[32 empty] | 3210 | TYLERNE_ | NORTH
[32 empty] | 3211 | TYLERE_8 | NORTH
[32 empty] | 3212 | TYLROMNR | NORTH
[32 empty] | 3213 | TYLERGE_ | NORTH
[32 empty] | 3214 | DELEKTAP | NORTH
[32 empty] | 3215 | DELEK2_8 | NORTH
[32 empty] | 3218 | TYLERS_8 | NORTH
[32 empty] | 3219 | TYLRBUL_ | NORTH
[32 empty] | 3221 | GRESHAM_ | NORTH
[32 empty] | 3222 | TEASELVL | NORTH
[32 empty] | 3224 | TEASELMT | NORTH
[32 empty] | 3227 | WHITEHSE | NORTH
[32 empty] | 3230 | SWINYTWN | NORTH
[32 empty] | 3231 | OVERTON_ | NORTH
[32 empty] | 3234 | TYLERSW_ | NORTH
[32 empty] | 3235 | CHADLER_ | NORTH
[32 empty] | 3236 | BRNSBORO | NORTH
[32 empty] | 3238 | ATHENS_8 | NORTH
[32 empty] | 3239 | ATHENS_9 | NORTH
[32 empty] | 3240 | MURCHISN | NORTH
[32 empty] | 3241 | JAXVLSTA | NORTH
[32 empty] | 3242 | JAXVLWTA | NORTH
[32 empty] | 3243 | JAXWEST_ | NORTH
[32 empty] | 3244 | JAXVL_9 | NORTH
[32 empty] | 3245 | REYNLDST | NORTH
[32 empty] | 3247 | ATHENSTA | NORTH
[32 empty] | 3248 | ATHNSNWT | NORTH
[32 empty] | 3249 | BEAUMNTA | NORTH
[32 empty] | 3250 | BEAUMONT | NORTH
[32 empty] | 3251 | FLINTSUB | NORTH
[32 empty] | 3252 | JAXVL1SS | NORTH
[32 empty] | 3253 | JAXVLSW_ | NORTH
[32 empty] | 3254 | JAXVL2SS | NORTH
[32 empty] | 3255 | FRANKSTN | NORTH
[32 empty] | 3256 | POYNOR_9 | NORTH
[32 empty] | 3260 | NIPAKTAP | NORTH
[32 empty] | 3261 | NIPAK_8 | NORTH
[32 empty] | 3262 | CEDRCREK | NORTH
[32 empty] | 3263 | CEDRCKPU | NORTH
[32 empty] | 3264 | SEVENPTS | NORTH
[32 empty] | 3267 | MALAKOFF | NORTH
[32 empty] | 3269 | WILOWSP_ | NORTH
[32 empty] | 3270 | CAROLSPG | NORTH
[32 empty] | 3271 | PALSTNS_ | NORTH
[32 empty] | 3272 | PALESTNE | NORTH
[32 empty] | 3273 | PALESTNE | NORTH
[32 empty] | 3274 | MONTALBA | NORTH
[32 empty] | 3276 | MALAKOFF | NORTH
[32 empty] | 3277 | MSSYLAKE | NORTH
[32 empty] | 3278 | LAKEVIEW | NORTH
[32 empty] | 3279 | LONGLKTA | NORTH
[32 empty] | 3280 | LONGLAKE | NORTH
[32 empty] | 3281 | TENNCLNY | NORTH
[32 empty] | 3282 | BLACKFOT | NORTH
[32 empty] | 3283 | BUTLERMT | NORTH
[32 empty] | 3284 | BETO_8 | NORTH
[32 empty] | 3285 | ELKHART_ | NORTH
[32 empty] | 3286 | GRAPELND | NORTH
[32 empty] | 3289 | CROCKETT | NORTH
[32 empty] | 3290 | ELKGUFTA | NORTH
[32 empty] | 3291 | SLOCUMTA | NORTH
[32 empty] | 3292 | SLOCUM_9 | NORTH
[32 empty] | 3293 | ELKGULF_ | NORTH
[32 empty] | 3296 | NECHESRI | NORTH
[32 empty] | 3299 | CUSHING_ | NORTH
[32 empty] | 3300 | CUSHSE_8 | NORTH
[32 empty] | 3303 | NACGDCHS | NORTH
[32 empty] | 3310 | NACOGNOR | NORTH
[32 empty] | 3311 | NACOSFA_ | NORTH
[32 empty] | 3312 | CHIRENO_ | NORTH
[32 empty] | 3314 | NACOGSW_ | NORTH
[32 empty] | 3315 | NACOGSOU | NORTH
[32 empty] | 3316 | NACOGST_ | NORTH
[32 empty] | 3319 | HERTYNOR | NORTH
[32 empty] | 3320 | HUNTNGTN | NORTH
[32 empty] | 3321 | ZAVPMPTA | NORTH
[32 empty] | 3323 | ETOILE_8 | NORTH
[32 empty] | 3326 | LUFKINE_ | NORTH
[32 empty] | 3327 | DIBOLET_ | NORTH
[32 empty] | 3328 | LUFKINS_ | NORTH
[32 empty] | 3329 | LUFPRSTA | NORTH
[32 empty] | 3330 | LUFPRSHG | NORTH
[32 empty] | 3331 | DIBOLWTA | NORTH
[32 empty] | 3332 | HUDSON_8 | NORTH
[32 empty] | 3333 | LUFTXFND | NORTH
[32 empty] | 3334 | TXFNDRY_ | NORTH
[32 empty] | 3340 | LUFKIN_8 | NORTH
[32 empty] | 3341 | CNTLANG_ | NORTH
[32 empty] | 3342 | BAYOULC_ | NORTH
[32 empty] | 3343 | DOUGLAS_ | NORTH
[32 empty] | 3346 | CHAMPNTA | NORTH
[32 empty] | 3347 | CHAMPION | NORTH
[32 empty] | 3348 | CHAMPION | NORTH
[32 empty] | 3349 | TMPLINLA | NORTH
[32 empty] | 3350 | KENNARD_ | NORTH
[32 empty] | 3351 | BEREA_8 | NORTH
[32 empty] | 3353 | EXPLRPIP | NORTH
[32 empty] | 3354 | CROCKETT | NORTH
[32 empty] | 3355 | GRPLMGTA | NORTH
[32 empty] | 3356 | GRPLNMAG | NORTH
[32 empty] | 3357 | PLSNTSPG | NORTH
[32 empty] | 3358 | CENTVILL | NORTH
[32 empty] | 3380 | BIGBRN__ | NORTH
[32 empty] | 3381 | BBRN_1G | NORTH
[32 empty] | 3382 | BBRN_2G | NORTH
[32 empty] | 3390 | JEWETT_S | NORTH
[32 empty] | 3391 | JEWETT_N | NORTH
[32 empty] | 3392 | JEWETT1_ | NORTH
[32 empty] | 3393 | JEWETT1_ | NORTH
[32 empty] | 3394 | JEWETTA_ | NORTH
[32 empty] | 3396 | NUCOR_ST | NORTH
[32 empty] | 3400 | TWIN_OAK | NORTH
[32 empty] | 3402 | LAKE_CRK | NORTH
[32 empty] | 3403 | THOUSE_1 | NORTH
[32 empty] | 3404 | THOUSE_2 | NORTH
[32 empty] | 3405 | THOUSE__ | NORTH
[32 empty] | 3406 | ELM_MOTT | NORTH
[32 empty] | 3407 | ELM_MOTT | NORTH
[32 empty] | 3408 | ELM_MOTT | NORTH
[32 empty] | 3409 | LAKE_CRK | NORTH
[32 empty] | 3410 | LAKE_CRK | NORTH
[32 empty] | 3411 | LKCK_POD | NORTH
[32 empty] | 3412 | TEMP_PEC | SOUTH
[32 empty] | 3413 | TEMPSSLT | SOUTH
[32 empty] | 3414 | TEMP_SS_ | SOUTH
[32 empty] | 3415 | TEMP_SS_ | SOUTH
[32 empty] | 3416 | LAKE_CRK | NORTH
[32 empty] | 3417 | LAKE_CRK | NORTH
[32 empty] | 3418 | LCTMOD_1 | NORTH
[32 empty] | 3419 | LCTMOD_2 | NORTH
[32 empty] | 3420 | TEMP_PEC | SOUTH
[32 empty] | 3421 | SCOTWHIT | SOUTH
[32 empty] | 3422 | KILL_SS_ | SOUTH
[32 empty] | 3423 | KILL_SS_ | SOUTH
[32 empty] | 3425 | BELLCTY_ | SOUTH
[32 empty] | 3426 | KILELMR1 | SOUTH
[32 empty] | 3427 | KILELMR2 | SOUTH
[32 empty] | 3428 | KILL S | SOUTH
[32 empty] | 3429 | SANDOW__ | SOUTH
[32 empty] | 3430 | SANDOW1_ | SOUTH
[32 empty] | 3431 | SANDOW1_ | SOUTH
[32 empty] | 3432 | SANDOW_4 | SOUTH
[32 empty] | 3434 | BAYLOR_T | NORTH
[32 empty] | 3435 | BAYLOR1_ | NORTH
[32 empty] | 3436 | WACO_W1_ | NORTH
[32 empty] | 3437 | WACO_W1_ | NORTH
[32 empty] | 3438 | WACO_E1_ | NORTH
[32 empty] | 3439 | WACO_E1_ | NORTH
[32 empty] | 3440 | MCGREGPH | NORTH
[32 empty] | 3441 | MCGREGPH | NORTH
[32 empty] | 3442 | LIPSITZ_ | NORTH
[32 empty] | 3452 | WACOLASA | NORTH
[32 empty] | 3453 | CHATF_P_ | NORTH
[32 empty] | 3454 | MONTFTSS | NORTH
[32 empty] | 3455 | CORS1_8 | NORTH
[32 empty] | 3456 | CORSWEST | NORTH
[32 empty] | 3457 | CORS_M0B | NORTH
[32 empty] | 3458 | CORS_MOB | NORTH
[32 empty] | 3459 | CORS_MAG | NORTH
[32 empty] | 3460 | CORS_GL_ | NORTH
[32 empty] | 3461 | CORSGLAS | NORTH
[32 empty] | 3462 | CORSGUAR | NORTH
[32 empty] | 3463 | CORSGUAR | NORTH
[32 empty] | 3464 | EQUIPIPE | NORTH
[32 empty] | 3466 | KERENS _ | NORTH
[32 empty] | 3467 | POWELL1_ | NORTH
[32 empty] | 3468 | CORS__9 | NORTH
[32 empty] | 3470 | BLOOMGRV | NORTH
[32 empty] | 3471 | BARRY1_9 | NORTH
[32 empty] | 3475 | CORSMGSS | NORTH
[32 empty] | 3477 | EUREKA_P | NORTH
[32 empty] | 3478 | NAVARRO1 | NORTH
[32 empty] | 3479 | NAVARRO1 | NORTH
[32 empty] | 3480 | MILDRED2 | NORTH
[32 empty] | 3483 | GOODLOE_ | NORTH
[32 empty] | 3486 | RICHLAND | NORTH
[32 empty] | 3487 | WRTHMPOD | NORTH
[32 empty] | 3488 | WTXGFPOD | NORTH
[32 empty] | 3489 | SIMSMAG1 | NORTH
[32 empty] | 3492 | FRESTONE | NORTH
[32 empty] | 3493 | TEAGUE1_ | NORTH
[32 empty] | 3496 | STSUPRCK | NORTH
[32 empty] | 3497 | STSUPRCK | NORTH
[32 empty] | 3498 | EUREKA1_ | NORTH
[32 empty] | 3499 | BLAKFTAP | NORTH
[32 empty] | 3500 | FARRAR_P | NORTH
[32 empty] | 3501 | SEATEAG_ | NORTH
[32 empty] | 3502 | SEATEAG1 | NORTH
[32 empty] | 3503 | FAIRWPOD | NORTH
[32 empty] | 3504 | FAIRFL_P | NORTH
[32 empty] | 3505 | BIGBRN_T | NORTH
[32 empty] | 3506 | BIGBRNM1 | NORTH
[32 empty] | 3507 | BIGBRNM2 | NORTH
[32 empty] | 3508 | WINKLER_ | NORTH
[32 empty] | 3509 | BBRN_OPN | NORTH
[32 empty] | 3510 | BBRN_OPN | NORTH
[32 empty] | 3511 | NAV_MILS | NORTH
[32 empty] | 3514 | HANEY_P_ | NORTH
[32 empty] | 3515 | HUBBARD_ | NORTH
[32 empty] | 3516 | CHATT_P_ | NORTH
[32 empty] | 3518 | BLUMPUMP | NORTH
[32 empty] | 3521 | BLANTON_ | NORTH
[32 empty] | 3522 | HILLBORO | NORTH
[32 empty] | 3523 | HILLBORO | NORTH
[32 empty] | 3524 | ABBOTT1_ | NORTH
[32 empty] | 3525 | WEST1_9 | NORTH
[32 empty] | 3526 | ROSSSINC | NORTH
[32 empty] | 3527 | ROSSSINC | NORTH
[32 empty] | 3528 | TOURS_T | NORTH
[32 empty] | 3529 | TOURSTXP | NORTH
[32 empty] | 3532 | ITASCA_9 | NORTH
[32 empty] | 3533 | FILE_SIN | NORTH
[32 empty] | 3534 | GRANDVGF | NORTH
[32 empty] | 3535 | FILE_SIN | NORTH
[32 empty] | 3536 | MAYPEARL | NORTH
[32 empty] | 3537 | GRANDVEW | NORTH
[32 empty] | 3538 | MAYPRLTX | NORTH
[32 empty] | 3543 | MERTENS1 | NORTH
[32 empty] | 3546 | WHITNEY_ | NORTH
[32 empty] | 3547 | ROGERS_P | NORTH
[32 empty] | 3550 | WACOBLMD | NORTH
[32 empty] | 3551 | WACO_NE1 | NORTH
[32 empty] | 3552 | WACO_N1_ | NORTH
[32 empty] | 3553 | WACO_NW1 | NORTH
[32 empty] | 3554 | HALLBURG | NORTH
[32 empty] | 3555 | THOUSE_T | NORTH
[32 empty] | 3556 | THOUSE1_ | NORTH
[32 empty] | 3559 | WACOCOLO | NORTH
[32 empty] | 3560 | WACO_S1_ | NORTH
[32 empty] | 3561 | WACOM1PT | NORTH
[32 empty] | 3562 | WACOM2PT | NORTH
[32 empty] | 3563 | WACOMM1T | NORTH
[32 empty] | 3564 | WACO_MM1 | NORTH
[32 empty] | 3565 | WACOMM2T | NORTH
[32 empty] | 3566 | WACO_MM2 | NORTH
[32 empty] | 3567 | ROBINSON | NORTH
[32 empty] | 3568 | ROBSONNW | NORTH
[32 empty] | 3570 | WACOTIRE | NORTH
[32 empty] | 3571 | WACOKATY | NORTH
[32 empty] | 3572 | WACOKATY | NORTH
[32 empty] | 3573 | KATYTNEW | NORTH
[32 empty] | 3574 | WACONCST | NORTH
[32 empty] | 3575 | WACONCST | NORTH
[32 empty] | 3577 | LORENA_P | NORTH
[32 empty] | 3578 | LORENA_9 | NORTH
[32 empty] | 3580 | EDDY1_9 | SOUTH
[32 empty] | 3581 | TROY1_9 | SOUTH
[32 empty] | 3583 | GATESVIL | NORTH
[32 empty] | 3584 | WACOATCO | NORTH
[32 empty] | 3585 | WACOATLS | NORTH
[32 empty] | 3586 | MCGREG1_ | NORTH
[32 empty] | 3587 | GATESVIL | NORTH
[32 empty] | 3588 | GROESBEC | NORTH
[32 empty] | 3589 | MCGREGHE | NORTH
[32 empty] | 3590 | WACOSANG | NORTH
[32 empty] | 3591 | WACOWOOD | NORTH
[32 empty] | 3592 | WACOATCO | NORTH
[32 empty] | 3593 | SPGVALLY | NORTH
[32 empty] | 3594 | MCGREG_T | NORTH
[32 empty] | 3595 | CHINASPG | NORTH
[32 empty] | 3597 | GROESBEC | NORTH
[32 empty] | 3598 | BEARGRAS | NORTH
[32 empty] | 3599 | AMERIGAS | NORTH
[32 empty] | 3600 | AMERIGAS | NORTH
[32 empty] | 3601 | OLETHA_P | NORTH
[32 empty] | 3602 | SCOTWHIT | SOUTH
[32 empty] | 3603 | BROWN1_9 | NORTH
[32 empty] | 3604 | WESTTXGF | NORTH
[32 empty] | 3605 | WORTHAM1 | NORTH
[32 empty] | 3606 | MEXIA2_T | NORTH
[32 empty] | 3607 | TEMPLE1_ | SOUTH
[32 empty] | 3608 | TEMPLE_N | SOUTH
[32 empty] | 3609 | TEMP_NW1 | SOUTH
[32 empty] | 3610 | BELTON1_ | SOUTH
[32 empty] | 3611 | TEMPLE_S | SOUTH
[32 empty] | 3612 | TEMP_SE1 | SOUTH
[32 empty] | 3613 | COOLG_SE | NORTH
[32 empty] | 3614 | MEXIA_NO | NORTH
[32 empty] | 3616 | KILLTAFD | SOUTH
[32 empty] | 3617 | NOLANVIL | SOUTH
[32 empty] | 3618 | HARK_HTS | SOUTH
[32 empty] | 3619 | KILLTAFT | SOUTH
[32 empty] | 3620 | KILCLARR | SOUTH
[32 empty] | 3621 | KILL1_8 | SOUTH
[32 empty] | 3622 | KILLPARK | SOUTH
[32 empty] | 3623 | KILLPARK | SOUTH
[32 empty] | 3624 | LBELTON_ | SOUTH
[32 empty] | 3625 | TEAGUE1_ | NORTH
[32 empty] | 3626 | KILLFTHD | SOUTH
[32 empty] | 3627 | KILLFH_T | SOUTH
[32 empty] | 3628 | KILLCLCK | SOUTH
[32 empty] | 3629 | KILL_FHW | SOUTH
[32 empty] | 3630 | COPPERCV | SOUTH
[32 empty] | 3631 | MEXIA1_1 | NORTH
[32 empty] | 3632 | MEXIA2_1 | NORTH
[32 empty] | 3633 | HARKHTS_ | SOUTH
[32 empty] | 3634 | GROES_SE | NORTH
[32 empty] | 3635 | TXUPOAG_ | SOUTH
[32 empty] | 3636 | TEMPTAYV | SOUTH
[32 empty] | 3637 | OTTO_SE1 | NORTH
[32 empty] | 3638 | MARL_SE1 | NORTH
[32 empty] | 3639 | MARLNOSE | NORTH
[32 empty] | 3640 | SALADO1_ | SOUTH
[32 empty] | 3641 | MARLIN_S | NORTH
[32 empty] | 3642 | LOTT_SE1 | NORTH
[32 empty] | 3643 | TEMP_SS_ | SOUTH
[32 empty] | 3644 | TEMPLE1_ | SOUTH
[32 empty] | 3645 | LITRIVER | SOUTH
[32 empty] | 3646 | HOLLAND_ | SOUTH
[32 empty] | 3647 | BARTLETT | SOUTH
[32 empty] | 3648 | GRANGER1 | SOUTH
[32 empty] | 3649 | TAYLOR1_ | SOUTH
[32 empty] | 3650 | ELGIN_SS | SOUTH
[32 empty] | 3651 | ELGIN_SS | SOUTH
[32 empty] | 3652 | COUPLAND | SOUTH
[32 empty] | 3653 | BRTLT_CB | SOUTH
[32 empty] | 3654 | RNDRCKSE | SOUTH
[32 empty] | 3655 | ELGIN1_9 | SOUTH
[32 empty] | 3658 | TAYLOR1_ | SOUTH
[32 empty] | 3659 | THORNDLN | SOUTH
[32 empty] | 3661 | SALTY_P_ | SOUTH
[32 empty] | 3665 | PFLGRVIL | SOUTH
[32 empty] | 3666 | HUTTOSS1 | SOUTH
[32 empty] | 3668 | RNDROCK1 | SOUTH
[32 empty] | 3669 | RNDRCKWH | SOUTH
[32 empty] | 3670 | RNDRCKNE | SOUTH
[32 empty] | 3671 | LOTT_TSE | NORTH
[32 empty] | 3672 | RNDRCK_S | SOUTH
[32 empty] | 3673 | TAYLOR_W | SOUTH
[32 empty] | 3674 | ELGIN_ET | SOUTH
[32 empty] | 3675 | ROGERS1A | SOUTH
[32 empty] | 3678 | ROCKDALE | SOUTH
[32 empty] | 3679 | TALBERTR | SOUTH
[32 empty] | 3681 | FAIRF_SE | NORTH
[32 empty] | 3682 | MILANO_M | SOUTH
[32 empty] | 3683 | MINERVA1 | SOUTH
[32 empty] | 3684 | MINERVA1 | SOUTH
[32 empty] | 3685 | CAMERON1 | SOUTH
[32 empty] | 3686 | ROCKDALN | SOUTH
[32 empty] | 3688 | JARRELL_ | SOUTH
[32 empty] | 3689 | MARAK1_9 | SOUTH
[32 empty] | 3697 | WACOMMP2 | NORTH
[32 empty] | 3698 | WACOMMP1 | NORTH
[32 empty] | 5000 | ALAMOTP | SOUTH
[32 empty] | 5001 | ALAMO_CM | SOUTH
[32 empty] | 5002 | AMD_SA | SOUTH
[32 empty] | 5003 | ANDERSON | SOUTH
[32 empty] | 5004 | AMD_TP | SOUTH
[32 empty] | 5005 | AUSTIN1 | SOUTH
[32 empty] | 5006 | AUSTIN2 | SOUTH
[32 empty] | 5011 | BALL_PRK | SOUTH
[32 empty] | 5020 | BANDERA | SOUTH
[32 empty] | 5025 | BRAUNIG_ | SOUTH
[32 empty] | 5026 | BRAUNIG_ | SOUTH
[32 empty] | 5027 | BRAUNIG_ | SOUTH
[32 empty] | 5028 | BRAUNIG_ | SOUTH
[32 empty] | 5030 | BRAUNIG_ | SOUTH
[32 empty] | 5035 | BECK_RD | SOUTH
[32 empty] | 5040 | BROADVEW | SOUTH
[32 empty] | 5045 | BROOKS | SOUTH
[32 empty] | 5050 | BUCKEYE | SOUTH
[32 empty] | 5055 | CAGNON_8 | SOUTH
[32 empty] | 5056 | CAGNON_5 | SOUTH
[32 empty] | 5075 | CAPITOL | SOUTH
[32 empty] | 5080 | CASTLE | SOUTH
[32 empty] | 5083 | CASTRVLL | SOUTH
[32 empty] | 5085 | CHAVANEA | SOUTH
[32 empty] | 5090 | CHULIE | SOUTH
[32 empty] | 5093 | CIBILOCR | SOUTH
[32 empty] | 5095 | COLISEUM | SOUTH
[32 empty] | 5110 | JT_DEELY | SOUTH
[32 empty] | 5111 | CALAVER_ | SOUTH
[32 empty] | 5112 | CALAVER_ | SOUTH
[32 empty] | 5125 | DEZAVALA | SOUTH
[32 empty] | 5130 | DRESDEN | SOUTH
[32 empty] | 5132 | EAGLECRK | SOUTH
[32 empty] | 5133 | ELMCREEK | SOUTH
[32 empty] | 5135 | ELMENDRF | SOUTH
[32 empty] | 5140 | ENCINO | SOUTH
[32 empty] | 5145 | FALLSCTY | SOUTH
[32 empty] | 5147 | FERN | SOUTH
[32 empty] | 5150 | FIVE_PTS | SOUTH
[32 empty] | 5155 | FLORESVI | SOUTH
[32 empty] | 5160 | FORT_SAM | SOUTH
[32 empty] | 5165 | FRATT | SOUTH
[32 empty] | 5170 | FRED_RD | SOUTH
[32 empty] | 5175 | GRANDVEW | SOUTH
[32 empty] | 5180 | GREEN_MT | SOUTH
[32 empty] | 5185 | GRISSOM | SOUTH
[32 empty] | 5187 | HAMWOLF | SOUTH
[32 empty] | 5190 | HARLANDA | SOUTH
[32 empty] | 5195 | HARMONY | SOUTH
[32 empty] | 5200 | HELOTES | SOUTH
[32 empty] | 5205 | HIGHLAND | SOUTH
[32 empty] | 5209 | HILLCTYE | SOUTH
[32 empty] | 5210 | HILLCTYW | SOUTH
[32 empty] | 5211 | HILLCTY_ | SOUTH
[32 empty] | 5220 | HOLLYWD | SOUTH
[32 empty] | 5225 | HONDO | SOUTH
[32 empty] | 5230 | HOWARD | SOUTH
[32 empty] | 5245 | KELLY | SOUTH
[32 empty] | 5249 | KIRBY2 | SOUTH
[32 empty] | 5250 | KIRBY | SOUTH
[32 empty] | 5255 | LAREDO1 | SOUTH
[32 empty] | 5257 | LASIERRA | SOUTH
[32 empty] | 5260 | LEON_CRK | SOUTH
[32 empty] | 5261 | LEON_STR | SOUTH
[32 empty] | 5262 | LEON_STR | SOUTH
[32 empty] | 5264 | LEON_LCP | SOUTH
[32 empty] | 5265 | LEON_LCP | SOUTH
[32 empty] | 5266 | LEON_LCP | SOUTH
[32 empty] | 5267 | LEON_LCP | SOUTH
[32 empty] | 5268 | LEON_LCP | SOUTH
[32 empty] | 5269 | LEON_LCP | SOUTH
[32 empty] | 5285 | LA_HTS_A | SOUTH
[32 empty] | 5286 | LA_HTS_B | SOUTH
[32 empty] | 5290 | LYTLE | SOUTH
[32 empty] | 5295 | MARBACH | SOUTH
[32 empty] | 5300 | MED_CTR | SOUTH
[32 empty] | 5305 | MEDINABS | SOUTH
[32 empty] | 5310 | MERIDA | SOUTH
[32 empty] | 5315 | NACDCHES | SOUTH
[32 empty] | 5325 | OLMOS | SOUTH
[32 empty] | 5332 | PARSONS | SOUTH
[32 empty] | 5335 | PEARSAL | SOUTH
[32 empty] | 5345 | PINN_RD | SOUTH
[32 empty] | 5350 | QUINTANA | SOUTH
[32 empty] | 5360 | RANDOLPH | SOUTH
[32 empty] | 5369 | SKYLIN_N | SOUTH
[32 empty] | 5370 | SKYLIN_S | SOUTH
[32 empty] | 5371 | SKYLINE_ | SOUTH
[32 empty] | 5385 | SOUTHSAN | SOUTH
[32 empty] | 5390 | SOMERSET | SOUTH
[32 empty] | 5395 | SOMMERS | SOUTH
[32 empty] | 5396 | CALAVER_ | SOUTH
[32 empty] | 5397 | CALAVER_ | SOUTH
[32 empty] | 5400 | SPRUCE | SOUTH
[32 empty] | 5401 | CALAVER_ | SOUTH
[32 empty] | 5410 | ST_HEDWG | SOUTH
[32 empty] | 5412 | STCKDALE | SOUTH
[32 empty] | 5415 | STONEGAT | SOUTH
[32 empty] | 5417 | STREICH | SOUTH
[32 empty] | 5418 | SUTHRLND | SOUTH
[32 empty] | 5419 | SWRI | SOUTH
[32 empty] | 5420 | TENTH_ST | SOUTH
[32 empty] | 5423 | TCC | SOUTH
[32 empty] | 5425 | TERREL_A | SOUTH
[32 empty] | 5426 | TERREL_B | SOUTH
[32 empty] | 5428 | TOYOTA | SOUTH
[32 empty] | 5430 | TX_RSRCH | SOUTH
[32 empty] | 5435 | TUTTLE | SOUTH
[32 empty] | 5436 | TUTTL_WB | SOUTH
[32 empty] | 5438 | TUTTL_WB | SOUTH
[32 empty] | 5439 | TUTTL_WB | SOUTH
[32 empty] | 5450 | USAA_ATP | SOUTH
[32 empty] | 5451 | USAA_A | SOUTH
[32 empty] | 5452 | USAA_BTP | SOUTH
[32 empty] | 5453 | USAA_B | SOUTH
[32 empty] | 5455 | USAA2TP | SOUTH
[32 empty] | 5456 | USAA2 | SOUTH
[32 empty] | 5460 | UTSA | SOUTH
[32 empty] | 5461 | UTSA_ATP | SOUTH
[32 empty] | 5462 | UTSA_BTP | SOUTH
[32 empty] | 5465 | VALLEY | SOUTH
[32 empty] | 5467 | VLSI | SOUTH
[32 empty] | 5470 | FAIRRA | SOUTH
[32 empty] | 5475 | VON_ROSE | SOUTH
[32 empty] | 5476 | BRA_AVR1 | SOUTH
[32 empty] | 5477 | BRA_AVR1 | SOUTH
[32 empty] | 5478 | BRA_AVR1 | SOUTH
[32 empty] | 5479 | AVR1_M | SOUTH
[32 empty] | 5485 | WALZEM | SOUTH
[32 empty] | 5490 | WSTSIDE | SOUTH
[32 empty] | 5500 | RAYBURN9 | SOUTH
[32 empty] | 5501 | RAYBURN1 | SOUTH
[32 empty] | 5502 | RAYBURN8 | SOUTH
[32 empty] | 5503 | RAYBURNG | SOUTH
[32 empty] | 5504 | NURSERYS | SOUTH
[32 empty] | 5505 | RAYBURNG | SOUTH
[32 empty] | 5506 | RAYBURNG | SOUTH
[32 empty] | 5508 | RAYBURNC | SOUTH
[32 empty] | 5509 | RAYBURNC | SOUTH
[32 empty] | 5510 | FORDTRAN | SOUTH
[32 empty] | 5511 | RAYBURNC | SOUTH
[32 empty] | 5512 | RAYBURNC | SOUTH
[32 empty] | 5513 | RAYBURNP | SOUTH
[32 empty] | 5514 | INEZSUB9 | SOUTH
[32 empty] | 5516 | ELTOROSW | SOUTH
[32 empty] | 5518 | ELTOROSW | SOUTH
[32 empty] | 5520 | ELTOROSU | SOUTH
[32 empty] | 5522 | EDNASUB9 | SOUTH
[32 empty] | 5525 | GANADOSW | SOUTH
[32 empty] | 5526 | GANADOSU | SOUTH
[32 empty] | 5528 | LOUISESU | SOUTH
[32 empty] | 5530 | ROUNDMOT | SOUTH
[32 empty] | 5532 | HILLJESU | SOUTH
[32 empty] | 5534 | ROUNDMOT | SOUTH
[32 empty] | 5536 | NADASUB9 | SOUTH
[32 empty] | 5538 | ELCAMPOS | SOUTH
[32 empty] | 5540 | PLAINVIE | SOUTH
[32 empty] | 5543 | INDSTRLP | SOUTH
[32 empty] | 5544 | DANEVANG | SOUTH
[32 empty] | 5546 | DANEVANG | SOUTH
[32 empty] | 5548 | DANEVANG | SOUTH
[32 empty] | 5549 | CLEMVILL | SOUTH
[32 empty] | 5550 | NCLEMVIL | SOUTH
[32 empty] | 5552 | SCLEMVIL | SOUTH
[32 empty] | 5554 | MARKHAMT | SOUTH
[32 empty] | 5556 | VANVLECK | HOUSTON
[32 empty] | 5558 | VANVLECK | HOUSTON
[32 empty] | 5560 | BAYCITYS | HOUSTON
[32 empty] | 5564 | SARGENTS | HOUSTON
[32 empty] | 5566 | FRANKLNC | HOUSTON
[32 empty] | 5568 | FRANKLNC | HOUSTON
[32 empty] | 5569 | TINTOPSU | SOUTH
[32 empty] | 5570 | PALACIOS | SOUTH
[32 empty] | 5571 | STRUCTUR | SOUTH
[32 empty] | 5573 | CARANCAH | SOUTH
[32 empty] | 5574 | OLIVIASW | SOUTH
[32 empty] | 5576 | OLIVIASU | SOUTH
[32 empty] | 5578 | LOLITASU | SOUTH
[32 empty] | 5580 | VANHUMBL | SOUTH
[32 empty] | 5582 | VANDERBL | SOUTH
[32 empty] | 5584 | VANDERBL | SOUTH
[32 empty] | 5586 | VANDERBL | SOUTH
[32 empty] | 5588 | REDBLUF | SOUTH
[32 empty] | 5590 | PLACEDOS | SOUTH
[32 empty] | 5591 | KAMEYSUB | SOUTH
[32 empty] | 5592 | PORTLAVA | SOUTH
[32 empty] | 5596 | PTOCONNO | SOUTH
[32 empty] | 5600 | LONETREE | SOUTH
[32 empty] | 5601 | AIRPORTS | SOUTH
[32 empty] | 5602 | TWINPINE | SOUTH
[32 empty] | 5603 | TWINPINE | SOUTH
[32 empty] | 5604 | HIGHLAND | SOUTH
[32 empty] | 5605 | WARBURTO | SOUTH
[32 empty] | 5606 | ALOESUB9 | SOUTH
[32 empty] | 5608 | MCFADDIN | SOUTH
[32 empty] | 5610 | REFUGIOS | SOUTH
[32 empty] | 5614 | BONNEVIE | SOUTH
[32 empty] | 5616 | TAFTSUB9 | SOUTH
[32 empty] | 5618 | SODVILLE | SOUTH
[32 empty] | 5620 | WSINTONS | SOUTH
[32 empty] | 5622 | WSINTONS | SOUTH
[32 empty] | 5626 | CALALLEN | SOUTH
[32 empty] | 5632 | RIVERSID | SOUTH
[32 empty] | 5634 | ROBSTOWN | SOUTH
[32 empty] | 5636 | CORPSCHR | SOUTH
[32 empty] | 5638 | CORPSCHR | SOUTH
[32 empty] | 5640 | DRISCOLL | SOUTH
[32 empty] | 5645 | RICARDOS | SOUTH
[32 empty] | 5646 | RIVIERAS | SOUTH
[32 empty] | 5648 | LOYOLASW | SOUTH
[32 empty] | 5650 | LOYOLASW | SOUTH
[32 empty] | 5652 | CENTRALS | SOUTH
[32 empty] | 5654 | SANDIEGO | SOUTH
[32 empty] | 5658 | ORANGEGR | SOUTH
[32 empty] | 5660 | ORANGEGR | SOUTH
[32 empty] | 5662 | ORANGEGR | SOUTH
[32 empty] | 5664 | AGUADULC | SOUTH
[32 empty] | 5666 | SANDIASU | SOUTH
[32 empty] | 5668 | MATHISSU | SOUTH
[32 empty] | 5672 | OLMOSSUB | SOUTH
[32 empty] | 5673 | BEEPRISO | SOUTH
[32 empty] | 5674 | BEEVILLE | SOUTH
[32 empty] | 5676 | GOLIADSW | SOUTH
[32 empty] | 5678 | SCHROEDE | SOUTH
[32 empty] | 5680 | LOOP463S | SOUTH
[32 empty] | 5684 | GEORGEWS | SOUTH
[32 empty] | 5685 | WGORGEWS | SOUTH
[32 empty] | 5686 | GEORGEWS | SOUTH
[32 empty] | 5688 | GEORGEWS | SOUTH
[32 empty] | 5690 | WGRGEWST | SOUTH
[32 empty] | 5695 | SIMMONSS | SOUTH
[32 empty] | 5696 | CALLIHAM | SOUTH
[32 empty] | 5697 | SCALLIHA | SOUTH
[32 empty] | 5698 | NCALLIHA | SOUTH
[32 empty] | 5699 | CHKCANPR | SOUTH
[32 empty] | 5700 | TILDENSU | SOUTH
[32 empty] | 5702 | SNMIGUEL | SOUTH
[32 empty] | 5704 | SNMIGUEL | SOUTH
[32 empty] | 5706 | SNMIGUEL | SOUTH
[32 empty] | 5708 | CHARLOTT | SOUTH
[32 empty] | 5710 | POTEETSU | SOUTH
[32 empty] | 5712 | OAKSSUB8 | SOUTH
[32 empty] | 5713 | OAKSSUB9 | SOUTH
[32 empty] | 5714 | PLEASANT | SOUTH
[32 empty] | 5716 | FASHINGS | SOUTH
[32 empty] | 5718 | ROSSVILL | SOUTH
[32 empty] | 5720 | COYCITYS | SOUTH
[32 empty] | 5722 | KENEDYSU | SOUTH
[32 empty] | 5723 | VERDISUB | SOUTH
[32 empty] | 5725 | PAWNEESW | SOUTH
[32 empty] | 5727 | PAWNEESW | SOUTH
[32 empty] | 5728 | FALCONHY | SOUTH
[32 empty] | 5729 | FALCONHY | SOUTH
[32 empty] | 5730 | FOURCORN | SOUTH
[32 empty] | 5732 | CHARCOSU | SOUTH
[32 empty] | 5735 | MIDFIELD | SOUTH
[32 empty] | 5736 | FANNINSU | SOUTH
[32 empty] | 5805 | QUIHISW9 | SOUTH
[32 empty] | 5806 | WESTBADE | SOUTH
[32 empty] | 5807 | CSTROVIL | SOUTH
[32 empty] | 5808 | CSTROVIL | SOUTH
[32 empty] | 5810 | BADERSUB | SOUTH
[32 empty] | 5811 | PEARSONS | SOUTH
[32 empty] | 5812 | SABINALS | SOUTH
[32 empty] | 5813 | PEARSONS | SOUTH
[32 empty] | 5814 | DHANISSU | SOUTH
[32 empty] | 5816 | HONDOSUB | SOUTH
[32 empty] | 5817 | FERRISSW | SOUTH
[32 empty] | 5818 | FERRISSU | SOUTH
[32 empty] | 5819 | HONDOCRE | SOUTH
[32 empty] | 5820 | UVALDESU | SOUTH
[32 empty] | 5821 | HONDOCRE | SOUTH
[32 empty] | 5822 | LEONASUB | SOUTH
[32 empty] | 5823 | UVALDESW | SOUTH
[32 empty] | 5824 | WSTUVALD | SOUTH
[32 empty] | 5827 | MOORESUB | SOUTH
[32 empty] | 5828 | DEVINESU | SOUTH
[32 empty] | 5830 | MOORESUB | SOUTH
[32 empty] | 5832 | FRIOTOWN | SOUTH
[32 empty] | 5836 | NBATESVI | SOUTH
[32 empty] | 5842 | DERBYSUB | SOUTH
[32 empty] | 5848 | SBATESVI | SOUTH
[32 empty] | 5849 | BATESVIL | SOUTH
[32 empty] | 5851 | BATESVIL | SOUTH
[32 empty] | 5852 | BIGFOOTS | SOUTH
[32 empty] | 5855 | CRYSTLCT | SOUTH
[32 empty] | 5856 | CRYSTLCT | SOUTH
[32 empty] | 5857 | DEVINESW | SOUTH
[32 empty] | 5858 | NATALIAS | SOUTH
[32 empty] | 5859 | TURTLECR | SOUTH
[32 empty] | 5860 | DILLEYSU | SOUTH
[32 empty] | 5861 | DILEYSWS | SOUTH
[32 empty] | 5863 | DILEYSWS | SOUTH
[32 empty] | 5864 | WCRYSTLC | SOUTH
[32 empty] | 5868 | BIGWELLS | SOUTH
[32 empty] | 5870 | BRUNDAGE | SOUTH
[32 empty] | 5872 | CARIZOSP | SOUTH
[32 empty] | 5876 | COTULLAS | SOUTH
[32 empty] | 5878 | HOLLANDS | SOUTH
[32 empty] | 5880 | FREERSUB | SOUTH
[32 empty] | 5883 | DOWNIESU | SOUTH
[32 empty] | 5885 | DOWNIESU | SOUTH
[32 empty] | 5887 | BRUNISUB | SOUTH
[32 empty] | 5888 | BRUNISUB | SOUTH
[32 empty] | 5890 | PEARSALL | SOUTH
[32 empty] | 5891 | PEARSALL | SOUTH
[32 empty] | 5892 | PEARSALL | SOUTH
[32 empty] | 5893 | PEARSALL | SOUTH
[32 empty] | 5895 | PEARSALL | SOUTH
[32 empty] | 5901 | MIGUEL 5 | SOUTH
[32 empty] | 5902 | MIGUEL 8 | SOUTH
[32 empty] | 5903 | SANMIGUE | SOUTH
[32 empty] | 5904 | MIGUESTR | SOUTH
[32 empty] | 5905 | MIGUESTR | SOUTH
[32 empty] | 5908 | SMIGLT1 | SOUTH
[32 empty] | 5909 | SMIGLT2 | SOUTH
[32 empty] | 5911 | STP_GN1_ | HOUSTON
[32 empty] | 5912 | STP_GN2_ | HOUSTON
[32 empty] | 5915 | SO_TEX__ | HOUSTON
[32 empty] | 5920 | WELSHDC1 | NORTH
[32 empty] | 5925 | DCEAST | NORTH
[32 empty] | 5930 | PWRPLT69 | SOUTH
[32 empty] | 5932 | SI_RAY9 | SOUTH
[32 empty] | 5933 | SI_RAY6 | SOUTH
[32 empty] | 5934 | SI_RAY5 | SOUTH
[32 empty] | 5935 | SI_RAY10 | SOUTH
[32 empty] | 5943 | LOMAALTA | SOUTH
[32 empty] | 5944 | CARBIDE | SOUTH
[32 empty] | 5946 | AIRPORT | SOUTH
[32 empty] | 5960 | MILHWY69 | SOUTH
[32 empty] | 5961 | LAREDO69 | SOUTH
[32 empty] | 5962 | LOMAALTA | SOUTH
[32 empty] | 5963 | TITAN | SOUTH
[32 empty] | 5964 | MILH_DUM | SOUTH
[32 empty] | 5965 | PALOALTO | SOUTH
[32 empty] | 6000 | SILVRTP1 | WEST
[32 empty] | 6001 | SAJT2A | WEST
[32 empty] | 6003 | BRNHRTP2 | WEST
[32 empty] | 6004 | ATTA2A | WEST
[32 empty] | 6005 | STAP2A | WEST
[32 empty] | 6006 | BRDY2A | SOUTH
[32 empty] | 6013 | TWB4TERT | WEST
[32 empty] | 6014 | SW_MESA4 | WEST
[32 empty] | 6015 | SWMESA4 | WEST
[32 empty] | 6016 | SWMESA | WEST
[32 empty] | 6019 | ORNNWPT4 | WEST
[32 empty] | 6021 | DSKY1_4 | WEST
[32 empty] | 6022 | DSKY1_T4 | WEST
[32 empty] | 6023 | ESTL2A | WEST
[32 empty] | 6024 | TURK2A | WEST
[32 empty] | 6028 | CHLD2A | WEST
[32 empty] | 6030 | CHLD4A | WEST
[32 empty] | 6031 | CH202A | WEST
[32 empty] | 6032 | CHIL2A | WEST
[32 empty] | 6033 | CHLD20TP | WEST
[32 empty] | 6035 | YUCCA2A | WEST
[32 empty] | 6041 | FLOMTP2A | WEST
[32 empty] | 6042 | FLOM2A | WEST
[32 empty] | 6044 | TURL2A | WEST
[32 empty] | 6048 | PAUL2A | WEST
[32 empty] | 6050 | LKPAULS4 | WEST
[32 empty] | 6051 | QUAN2A | WEST
[32 empty] | 6052 | ACME2A | WEST
[32 empty] | 6053 | KIRK2A | WEST
[32 empty] | 6056 | CHLC_VER | WEST
[32 empty] | 6057 | CHILE2WT | WEST
[32 empty] | 6058 | VERN2A | WEST
[32 empty] | 6060 | VERN4A | WEST
[32 empty] | 6061 | VRCP2A | WEST
[32 empty] | 6062 | SANT2A | WEST
[32 empty] | 6063 | SAND2A | WEST
[32 empty] | 6064 | VERS2A | WEST
[32 empty] | 6066 | VERS4A | WEST
[32 empty] | 6070 | GRAYBAC2 | WEST
[32 empty] | 6071 | GRBC2A | WEST
[32 empty] | 6072 | HARR2A | WEST
[32 empty] | 6075 | WAGR2A | WEST
[32 empty] | 6080 | TRUSEXN2 | WEST
[32 empty] | 6082 | CRWL2A | WEST
[32 empty] | 6084 | EXTR2A | WEST
[32 empty] | 6085 | TRUS2A | WEST
[32 empty] | 6086 | BENJTP2A | WEST
[32 empty] | 6087 | BENJ2A | WEST
[32 empty] | 6096 | NORTHDC7 | WEST
[32 empty] | 6097 | OKLA4A | WEST
[32 empty] | 6098 | OKLA4B | WEST
[32 empty] | 6100 | OKLA7A | WEST
[32 empty] | 6101 | OKLA7STR | WEST
[32 empty] | 6107 | MUND2A | WEST
[32 empty] | 6108 | MUNE2A | WEST
[32 empty] | 6110 | EMUNDY24 | WEST
[32 empty] | 6112 | GILL2A | WEST
[32 empty] | 6113 | KNXC2A | WEST
[32 empty] | 6114 | KNXR2A | WEST
[32 empty] | 6115 | ROCH2A | WEST
[32 empty] | 6117 | EMUNDY14 | WEST
[32 empty] | 6120 | RULE2A | WEST
[32 empty] | 6122 | HSKL2A | WEST
[32 empty] | 6123 | JOSS2A | WEST
[32 empty] | 6124 | HASTXTP2 | WEST
[32 empty] | 6125 | WEIN2A | WEST
[32 empty] | 6126 | TXHS2A | WEST
[32 empty] | 6131 | PADR2A | WEST
[32 empty] | 6132 | PADC2A | WEST
[32 empty] | 6133 | PADU2A | WEST
[32 empty] | 6135 | PADU4A | WEST
[32 empty] | 6140 | MATA2A | WEST
[32 empty] | 6141 | ROAR2A | WEST
[32 empty] | 6142 | AFTO2A | WEST
[32 empty] | 6143 | ESPU2A | WEST
[32 empty] | 6144 | MCADOO1A | WEST
[32 empty] | 6145 | MCADOO4A | WEST
[32 empty] | 6147 | GIRA2A | WEST
[32 empty] | 6148 | SPUR2A | WEST
[32 empty] | 6150 | SPUR4A | WEST
[32 empty] | 6151 | GIRA_TAP | WEST
[32 empty] | 6152 | DKEC2A | WEST
[32 empty] | 6153 | JATN2A | WEST
[32 empty] | 6154 | PEAC2A | WEST
[32 empty] | 6156 | ASPM2A | WEST
[32 empty] | 6158 | ASPM4A | WEST
[32 empty] | 6159 | PAIP2A | WEST
[32 empty] | 6160 | PAIP2STR | WEST
[32 empty] | 6161 | PAIP4A | WEST
[32 empty] | 6165 | CALCRKTP | WEST
[32 empty] | 6166 | CALI_CRK | WEST
[32 empty] | 6169 | PAIP4B | WEST
[32 empty] | 6170 | HASR2A | WEST
[32 empty] | 6171 | HSKELTP2 | WEST
[32 empty] | 6172 | STAM2A | WEST
[32 empty] | 6173 | CORN2A | WEST
[32 empty] | 6174 | HSKREAT2 | WEST
[32 empty] | 6175 | ANSN2A | WEST
[32 empty] | 6176 | ANSO2A | WEST
[32 empty] | 6177 | SWEN2A | WEST
[32 empty] | 6180 | RADM2A | WEST
[32 empty] | 6182 | HAMTXCO2 | WEST
[32 empty] | 6183 | HAMR2A | WEST
[32 empty] | 6184 | HAMTXTP2 | WEST
[32 empty] | 6185 | HAML2A | WEST
[32 empty] | 6186 | SHHA2A | WEST
[32 empty] | 6187 | CONA2A | WEST
[32 empty] | 6191 | EXSHRN4 | WEST
[32 empty] | 6192 | RONDTOP2 | WEST
[32 empty] | 6193 | PLST2A | WEST
[32 empty] | 6194 | RONDTPT2 | WEST
[32 empty] | 6195 | ROBY2A | WEST
[32 empty] | 6196 | ROTN2A | WEST
[32 empty] | 6197 | CLRM2A | WEST
[32 empty] | 6198 | CLARSUN2 | WEST
[32 empty] | 6202 | ALBNY_FD | WEST
[32 empty] | 6204 | WOOD2A | WEST
[32 empty] | 6205 | THRM2A | WEST
[32 empty] | 6206 | BUKB2A | WEST
[32 empty] | 6207 | ALBANY2A | WEST
[32 empty] | 6208 | HUB12A | WEST
[32 empty] | 6209 | MRAN2A | WEST
[32 empty] | 6210 | WCTMWD22 | WEST
[32 empty] | 6211 | ALBANYT2 | WEST
[32 empty] | 6212 | WCTMWD12 | WEST
[32 empty] | 6213 | HUB1_TAP | WEST
[32 empty] | 6214 | ALBANYT1 | WEST
[32 empty] | 6215 | ABRBRSN2 | WEST
[32 empty] | 6216 | BLF_CRK4 | WEST
[32 empty] | 6217 | FTPHPMP2 | WEST
[32 empty] | 6218 | NUGENTR2 | WEST
[32 empty] | 6219 | NUGE2A | WEST
[32 empty] | 6220 | FTFP2A | WEST
[32 empty] | 6221 | ABRC2A | WEST
[32 empty] | 6222 | FTPP4A | WEST
[32 empty] | 6223 | ABRC4A | WEST
[32 empty] | 6224 | ABNW2A | WEST
[32 empty] | 6225 | ABNW2B | WEST
[32 empty] | 6226 | ABEASTP | WEST
[32 empty] | 6228 | ABNW4A | WEST
[32 empty] | 6229 | CALHNTP | WEST
[32 empty] | 6230 | ABMULCE7 | WEST
[32 empty] | 6231 | MULBW RS | WEST
[32 empty] | 6232 | MULBE RS | WEST
[32 empty] | 6233 | ABMULSTR | WEST
[32 empty] | 6235 | ABMULCW7 | WEST
[32 empty] | 6236 | ABON2A | WEST
[32 empty] | 6237 | ONYS2A | WEST
[32 empty] | 6238 | EXHA2A | WEST
[32 empty] | 6239 | ABVT2A | WEST
[32 empty] | 6240 | ABVO2A | WEST
[32 empty] | 6241 | ELYT2A | WEST
[32 empty] | 6242 | MERK2A | WEST
[32 empty] | 6243 | CLFK2A | WEST
[32 empty] | 6244 | ABWALTP2 | WEST
[32 empty] | 6245 | ABRBPRS2 | WEST
[32 empty] | 6246 | MKLT2A | WEST
[32 empty] | 6247 | TRNT2A | WEST
[32 empty] | 6248 | HAWEXXN2 | WEST
[32 empty] | 6249 | DELT2A | WEST
[32 empty] | 6250 | DELK 2 | WEST
[32 empty] | 6251 | ELY9 | WEST
[32 empty] | 6252 | SCOTT9 | WEST
[32 empty] | 6253 | ABEC2A | WEST
[32 empty] | 6254 | ABMULSTR | WEST
[32 empty] | 6255 | ABEC4A | WEST
[32 empty] | 6256 | ABTT4A | WEST
[32 empty] | 6257 | ABRL4A | WEST
[32 empty] | 6258 | ABSO2A | WEST
[32 empty] | 6260 | ABSO4A | WEST
[32 empty] | 6261 | WYLE4A | WEST
[32 empty] | 6265 | ABDYES22 | WEST
[32 empty] | 6266 | ABDYTP22 | WEST
[32 empty] | 6267 | ABHT2A | WEST
[32 empty] | 6268 | ABDYTP12 | WEST
[32 empty] | 6269 | ABDYES12 | WEST
[32 empty] | 6270 | ABSH2A | WEST
[32 empty] | 6271 | ABMM2A | WEST
[32 empty] | 6272 | ABOV2A | WEST
[32 empty] | 6273 | ABDYTP32 | WEST
[32 empty] | 6274 | ABDYES32 | WEST
[32 empty] | 6275 | ABEA4A | WEST
[32 empty] | 6276 | ABEAST12 | WEST
[32 empty] | 6277 | ABEAST22 | WEST
[32 empty] | 6278 | ABPLTTP2 | WEST
[32 empty] | 6281 | ABWA2A | WEST
[32 empty] | 6282 | ABPG2A | WEST
[32 empty] | 6283 | ABOLMLT2 | WEST
[32 empty] | 6284 | ABWTGUT2 | WEST
[32 empty] | 6285 | ABWTXGU2 | WEST
[32 empty] | 6286 | ABOILML2 | WEST
[32 empty] | 6287 | MULBW RL | WEST
[32 empty] | 6288 | MULBE RL | WEST
[32 empty] | 6290 | ABMS4A | WEST
[32 empty] | 6291 | AILN2A | WEST
[32 empty] | 6292 | ABCC4A | WEST
[32 empty] | 6293 | ABCR4A | WEST
[32 empty] | 6295 | SRC1TERT | WEST
[32 empty] | 6300 | DENTONR2 | WEST
[32 empty] | 6301 | ABED2A | WEST
[32 empty] | 6302 | CLYM2A | WEST
[32 empty] | 6303 | WTU_DETP | WEST
[32 empty] | 6304 | CLYDMAG2 | WEST
[32 empty] | 6305 | CLYD2A | WEST
[32 empty] | 6306 | BAIR2A | WEST
[32 empty] | 6307 | PUTN2A | WEST
[32 empty] | 6308 | PUTN2STR | WEST
[32 empty] | 6309 | PUTN2A | WEST
[32 empty] | 6310 | PUTN2B | WEST
[32 empty] | 6311 | CISC2A | NORTH
[32 empty] | 6312 | PUT69 2 | WEST
[32 empty] | 6313 | POTOSI_T | WEST
[32 empty] | 6314 | POTOSI | WEST
[32 empty] | 6315 | SHARP TP | WEST
[32 empty] | 6316 | SHARP | WEST
[32 empty] | 6318 | POTTER | WEST
[32 empty] | 6324 | FTCHAD | WEST
[32 empty] | 6325 | CHAD4A | WEST
[32 empty] | 6326 | ROBRTSR2 | WEST
[32 empty] | 6327 | ABCG2A | WEST
[32 empty] | 6328 | TUSC2A | WEST
[32 empty] | 6329 | GLDBSK9 | WEST
[32 empty] | 6330 | HAPVAL2 | WEST
[32 empty] | 6331 | CLIM2A | WEST
[32 empty] | 6332 | HAPVALT2 | WEST
[32 empty] | 6333 | WINT2A | WEST
[32 empty] | 6334 | HATC2A | WEST
[32 empty] | 6335 | OAKC4A | WEST
[32 empty] | 6337 | BALEXXN2 | WEST
[32 empty] | 6338 | BALG2A | WEST
[32 empty] | 6340 | BALG4A | WEST
[32 empty] | 6341 | BALEXTP2 | WEST
[32 empty] | 6342 | NOVC2A | WEST
[32 empty] | 6343 | TALPATL2 | WEST
[32 empty] | 6344 | VALE2A | WEST
[32 empty] | 6345 | GLDBSKR2 | WEST
[32 empty] | 6346 | COLJ2A | WEST
[32 empty] | 6347 | COLETAP4 | WEST
[32 empty] | 6348 | COLEMAN4 | WEST
[32 empty] | 6349 | NOVICE9 | WEST
[32 empty] | 6350 | DRESSY9 | WEST
[32 empty] | 6351 | NICOLE4A | WEST
[32 empty] | 6352 | SANA_TAP | WEST
[32 empty] | 6353 | SANA2A | WEST
[32 empty] | 6355 | SANA4A | WEST
[32 empty] | 6356 | DRSY2A | WEST
[32 empty] | 6357 | CRPL2A | WEST
[32 empty] | 6358 | RIST2A | WEST
[32 empty] | 6360 | COLE_IVI | WEST
[32 empty] | 6361 | IVEYPMP4 | WEST
[32 empty] | 6362 | IVEYBST4 | WEST
[32 empty] | 6368 | HEXT 2 | SOUTH
[32 empty] | 6369 | PTRK2A | WEST
[32 empty] | 6370 | EOLATP2A | WEST
[32 empty] | 6371 | EOLA2A | WEST
[32 empty] | 6372 | EDEN2A | SOUTH
[32 empty] | 6373 | MENA2A | SOUTH
[32 empty] | 6375 | MENA4A | SOUTH
[32 empty] | 6376 | CRM1TP2A | SOUTH
[32 empty] | 6377 | CRM12A | SOUTH
[32 empty] | 6378 | BRDYSE 2 | SOUTH
[32 empty] | 6379 | BRDS2A | SOUTH
[32 empty] | 6380 | MELV2A | SOUTH
[32 empty] | 6381 | BRADYRE2 | SOUTH
[32 empty] | 6382 | BRADYTP2 | SOUTH
[32 empty] | 6383 | BRADY 2 | SOUTH
[32 empty] | 6384 | MCLC2A | SOUTH
[32 empty] | 6385 | EDENREA2 | SOUTH
[32 empty] | 6386 | CSSB2A | SOUTH
[32 empty] | 6387 | FREDPHIL | SOUTH
[32 empty] | 6389 | CTECMA2A | SOUTH
[32 empty] | 6391 | FRDN2A | SOUTH
[32 empty] | 6392 | PHMT2A | SOUTH
[32 empty] | 6393 | MASN2A | SOUTH
[32 empty] | 6394 | PHMA2A | SOUTH
[32 empty] | 6395 | MASNPH 2 | SOUTH
[32 empty] | 6396 | MASW2A | SOUTH
[32 empty] | 6397 | STRT2A | SOUTH
[32 empty] | 6398 | SHLO2A | SOUTH
[32 empty] | 6399 | KMJC2A | SOUTH
[32 empty] | 6400 | JUNC2A | SOUTH
[32 empty] | 6401 | MENPHTP2 | SOUTH
[32 empty] | 6402 | MENRDPH2 | SOUTH
[32 empty] | 6403 | SHELLON2 | SOUTH
[32 empty] | 6406 | TURKTRAK | WEST
[32 empty] | 6407 | TURKTRAK | WEST
[32 empty] | 6409 | VRBS2A | WEST
[32 empty] | 6410 | MILE2A | WEST
[32 empty] | 6411 | ROWE2A | WEST
[32 empty] | 6412 | HARI2A | WEST
[32 empty] | 6413 | VERIBST2 | WEST
[32 empty] | 6414 | BRONTE 2 | WEST
[32 empty] | 6416 | SAGT2A | WEST
[32 empty] | 6417 | STRLNG9 | WEST
[32 empty] | 6418 | ATBR2A | WEST
[32 empty] | 6419 | AMBR2A | WEST
[32 empty] | 6420 | ROBL2A | WEST
[32 empty] | 6421 | ESPENCT2 | WEST
[32 empty] | 6422 | EDIT2A | WEST
[32 empty] | 6423 | CEDH2A | WEST
[32 empty] | 6425 | CEDH4A | WEST
[32 empty] | 6426 | ESPENCE2 | WEST
[32 empty] | 6427 | SILR2B | WEST
[32 empty] | 6428 | SILR2A | WEST
[32 empty] | 6429 | SPADERN2 | WEST
[32 empty] | 6430 | SILV2A | WEST
[32 empty] | 6431 | SILVRTP2 | WEST
[32 empty] | 6432 | EXPE2A | WEST
[32 empty] | 6433 | SPRH2A | WEST
[32 empty] | 6434 | PANA2A | WEST
[32 empty] | 6435 | STER2A | WEST
[32 empty] | 6436 | STCO2A | WEST
[32 empty] | 6437 | CRBDTP 2 | WEST
[32 empty] | 6438 | CBDREA 2 | WEST
[32 empty] | 6439 | AMCO2A | WEST
[32 empty] | 6440 | AMOCO 2 | WEST
[32 empty] | 6441 | ORNT4A | WEST
[32 empty] | 6442 | SARC4A | WEST
[32 empty] | 6444 | SARC7A | WEST
[32 empty] | 6445 | CRMW5TP2 | WEST
[32 empty] | 6446 | CRMWD5 2 | WEST
[32 empty] | 6447 | PAULANN4 | WEST
[32 empty] | 6448 | SA_HILND | WEST
[32 empty] | 6449 | SACK4A | WEST
[32 empty] | 6450 | SACO2A | WEST
[32 empty] | 6451 | SARC7STR | WEST
[32 empty] | 6452 | SACO4A | WEST
[32 empty] | 6453 | SAST4A | WEST
[32 empty] | 6454 | SASO4A | WEST
[32 empty] | 6455 | SASL2A | WEST
[32 empty] | 6456 | SAJS2A | WEST
[32 empty] | 6457 | SAEM2A | WEST
[32 empty] | 6458 | CRM24A | WEST
[32 empty] | 6459 | CRM32A | WEST
[32 empty] | 6460 | CRM42A | WEST
[32 empty] | 6461 | CRMWD42 | WEST
[32 empty] | 6462 | SANO2A | WEST
[32 empty] | 6463 | SARC7STR | WEST
[32 empty] | 6464 | SANO4A | WEST
[32 empty] | 6465 | SAGC2A | WEST
[32 empty] | 6466 | SAWT2A | WEST
[32 empty] | 6467 | SAWA2A | WEST
[32 empty] | 6468 | SACH2A | WEST
[32 empty] | 6470 | SACH4A | WEST
[32 empty] | 6471 | SAAN2A | WEST
[32 empty] | 6473 | BENF4A | WEST
[32 empty] | 6477 | SAMF2A | WEST
[32 empty] | 6478 | SAPS2A | WEST
[32 empty] | 6479 | SAPS TIE | WEST
[32 empty] | 6480 | SAPS4B | WEST
[32 empty] | 6481 | SASH4A | WEST
[32 empty] | 6482 | SALD4A | WEST
[32 empty] | 6483 | SAPS4A | WEST
[32 empty] | 6484 | ANGORA2A | WEST
[32 empty] | 6488 | ROLLANS2 | WEST
[32 empty] | 6491 | PAW22A | WEST
[32 empty] | 6492 | PAVE4A | WEST
[32 empty] | 6493 | PAVEPAW4 | WEST
[32 empty] | 6494 | PAVEPAW2 | WEST
[32 empty] | 6495 | CRIS2A | WEST
[32 empty] | 6496 | AROT2A | WEST
[32 empty] | 6497 | HULD2A | WEST
[32 empty] | 6498 | LVOK2A | WEST
[32 empty] | 6500 | LIVEOAK4 | WEST
[32 empty] | 6503 | SHBA2A | WEST
[32 empty] | 6505 | ELDO2A | WEST
[32 empty] | 6506 | PAGE2A | WEST
[32 empty] | 6507 | MIDV2A | WEST
[32 empty] | 6508 | FMCK2A | WEST
[32 empty] | 6509 | SHBT2A | WEST
[32 empty] | 6510 | SONO2A | WEST
[32 empty] | 6511 | ATSO2A | WEST
[32 empty] | 6513 | SONR2A | WEST
[32 empty] | 6515 | SONR4A | WEST
[32 empty] | 6524 | MERTZON9 | WEST
[32 empty] | 6526 | MERR2A | WEST
[32 empty] | 6527 | SANW2A | WEST
[32 empty] | 6528 | TANK2A | WEST
[32 empty] | 6529 | MERT2A | WEST
[32 empty] | 6530 | BARN2A | WEST
[32 empty] | 6531 | BRNHRPH2 | WEST
[32 empty] | 6532 | BARNHCV2 | WEST
[32 empty] | 6533 | BGLK2A | WEST
[32 empty] | 6534 | BGLK2B | WEST
[32 empty] | 6535 | BGLK4A | WEST
[32 empty] | 6538 | TEXN2A | WEST
[32 empty] | 6539 | SHPO2A | WEST
[32 empty] | 6540 | SHPO_TAP | WEST
[32 empty] | 6541 | TEXONTP2 | WEST
[32 empty] | 6542 | ATLT2A | WEST
[32 empty] | 6543 | KEMPEXT2 | WEST
[32 empty] | 6544 | HUMT2A | WEST
[32 empty] | 6545 | POWF2A | WEST
[32 empty] | 6546 | PHBL_TAP | WEST
[32 empty] | 6547 | STRS2A | WEST
[32 empty] | 6548 | POWT2A | WEST
[32 empty] | 6549 | MIDW2A | WEST
[32 empty] | 6550 | FDRAN2A | WEST
[32 empty] | 6551 | OZNR2A | WEST
[32 empty] | 6552 | CROCKHT2 | WEST
[32 empty] | 6553 | PHBL2A | WEST
[32 empty] | 6554 | EXKE2A | WEST
[32 empty] | 6555 | ATLB2A | WEST
[32 empty] | 6556 | YATW_SW2 | WEST
[32 empty] | 6560 | OZONA 2 | WEST
[32 empty] | 6562 | FDRAN4A | WEST
[32 empty] | 6565 | ILLN2A | WEST
[32 empty] | 6568 | RGECBVIL | SOUTH
[32 empty] | 6572 | MDSC2A | WEST
[32 empty] | 6574 | MART2A | WEST
[32 empty] | 6575 | IRAN2A | WEST
[32 empty] | 6576 | DSCVYTP2 | WEST
[32 empty] | 6577 | SHEF2A | WEST
[32 empty] | 6578 | FTLCSTR2 | WEST
[32 empty] | 6580 | AIRP2A | WEST
[32 empty] | 6581 | ARPT2A | WEST
[32 empty] | 6583 | MESAVIEW | WEST
[32 empty] | 6584 | INDN4A | WEST
[32 empty] | 6585 | DSCVRY 2 | WEST
[32 empty] | 6586 | MCCAMY4 | WEST
[32 empty] | 6587 | SCROSS2 | WEST
[32 empty] | 6588 | SHLMESA2 | WEST
[32 empty] | 6589 | RANK2A | WEST
[32 empty] | 6590 | SHME2A | WEST
[32 empty] | 6591 | RANK4 2 | WEST
[32 empty] | 6592 | MCAM2A | WEST
[32 empty] | 6594 | SCRS2A | WEST
[32 empty] | 6597 | BOBCAT 2 | WEST
[32 empty] | 6598 | RIOP2A | WEST
[32 empty] | 6599 | BOBCAT T | WEST
[32 empty] | 6600 | CRNAIR T | WEST
[32 empty] | 6601 | RIOP4A | WEST
[32 empty] | 6603 | CRANTP2 | WEST
[32 empty] | 6604 | SAGE2A | WEST
[32 empty] | 6605 | CRANAIR2 | WEST
[32 empty] | 6606 | TXNMPL 2 | WEST
[32 empty] | 6607 | MCELROY2 | WEST
[32 empty] | 6608 | CRANGU12 | WEST
[32 empty] | 6609 | TXNMTP 2 | WEST
[32 empty] | 6610 | CRANGU22 | WEST
[32 empty] | 6611 | DUN22A | WEST
[32 empty] | 6613 | CRAN2A | WEST
[32 empty] | 6614 | DUNETAP2 | WEST
[32 empty] | 6627 | COMC4A | WEST
[32 empty] | 6628 | FTST2A | WEST
[32 empty] | 6630 | FTST4A | WEST
[32 empty] | 6632 | WDWRDTP4 | WEST
[32 empty] | 6633 | WOODWRD1 | WEST
[32 empty] | 6635 | KING_TAP | WEST
[32 empty] | 6636 | SNYDERW4 | WEST
[32 empty] | 6637 | SNYDERW1 | WEST
[32 empty] | 6639 | MCAN4A | WEST
[32 empty] | 6641 | SUNV2A | WEST
[32 empty] | 6642 | MAST2A | WEST
[32 empty] | 6643 | PECV2A | WEST
[32 empty] | 6645 | FTSW2A | WEST
[32 empty] | 6649 | VERH2A | WEST
[32 empty] | 6650 | CCRT2A | WEST
[32 empty] | 6651 | CCRK2A | WEST
[32 empty] | 6652 | SGSA2A | WEST
[32 empty] | 6653 | BARL2A | WEST
[32 empty] | 6655 | BARL4A | WEST
[32 empty] | 6656 | HACKBTAP | WEST
[32 empty] | 6657 | CR101TAP | WEST
[32 empty] | 6658 | MECPLNVW | WEST
[32 empty] | 6659 | SNTXTAP2 | WEST
[32 empty] | 6660 | SNTX12A | WEST
[32 empty] | 6661 | LONGWRTH | WEST
[32 empty] | 6663 | COCS2A | WEST
[32 empty] | 6665 | ALPR2A | WEST
[32 empty] | 6666 | ALPI2A | WEST
[32 empty] | 6667 | PAISANO2 | WEST
[32 empty] | 6668 | ALTUDA2A | WEST
[32 empty] | 6669 | PRSMNGAP | WEST
[32 empty] | 6676 | FTDA2A | WEST
[32 empty] | 6677 | VALT2A | WEST
[32 empty] | 6678 | ALMC2A | WEST
[32 empty] | 6680 | ALMC4A | WEST
[32 empty] | 6681 | MARF2A | WEST
[32 empty] | 6682 | CIEN2A | WEST
[32 empty] | 6683 | SHAF2A | WEST
[32 empty] | 6684 | PRES2A | WEST
[32 empty] | 6688 | CHINATI2 | WEST
[32 empty] | 6689 | BRYR2A | WEST
[32 empty] | 6690 | ATKN2A | WEST
[32 empty] | 6691 | ESPY2A | WEST
[32 empty] | 6692 | POND2A | WEST
[32 empty] | 6700 | DIBL WT4 | NORTH
[32 empty] | 6703 | SFIELD | NORTH
[32 empty] | 6705 | OWTN WT4 | NORTH
[32 empty] | 6707 | BSCM WT4 | NORTH
[32 empty] | 6709 | TSLVILLE | NORTH
[32 empty] | 6710 | SWTN WT4 | NORTH
[32 empty] | 6711 | OKWD WT4 | NORTH
[32 empty] | 6717 | CSNG WT4 | NORTH
[32 empty] | 6719 | CGSE WT4 | NORTH
[32 empty] | 6720 | SHNE WT4 | NORTH
[32 empty] | 6722 | OKRD WT4 | NORTH
[32 empty] | 6723 | HGTN WT4 | NORTH
[32 empty] | 6724 | ZVLA WT4 | NORTH
[32 empty] | 6726 | LFKN WT4 | NORTH
[32 empty] | 6727 | BYLC WT4 | NORTH
[32 empty] | 6736 | PLST WT4 | NORTH
[32 empty] | 6738 | CTVL WT4 | NORTH
[32 empty] | 6742 | TROUPWT2 | NORTH
[32 empty] | 6743 | WALNT | NORTH
[32 empty] | 6752 | OKLA0A | WEST
[32 empty] | 6754 | PTCREK2G | WEST
[32 empty] | 6769 | SRC2TERT | WEST
[32 empty] | 6771 | SABLUFF4 | WEST
[32 empty] | 6772 | ABIP4A | WEST
[32 empty] | 6773 | PCNBYU4A | WEST
[32 empty] | 6774 | SEGOVTP9 | SOUTH
[32 empty] | 6780 | OK1TERT | WEST
[32 empty] | 6788 | AMCETERT | WEST
[32 empty] | 6789 | AMCWTERT | WEST
[32 empty] | 6794 | PM1TERT | WEST
[32 empty] | 6800 | LIBTY RC | NORTH
[32 empty] | 6801 | ROSHILRC | NORTH
[32 empty] | 6802 | SHRLM RC | NORTH
[32 empty] | 6803 | BLUCRKRC | NORTH
[32 empty] | 6804 | WHTBR RC | NORTH
[32 empty] | 6806 | SHRWD RC | NORTH
[32 empty] | 6807 | DCKCVWRC | NORTH
[32 empty] | 6808 | SHERY RC | NORTH
[32 empty] | 6809 | BELLS RC | NORTH
[32 empty] | 6810 | GORDVLRC | NORTH
[32 empty] | 6811 | PNKHL RC | NORTH
[32 empty] | 6812 | DENSE RC | NORTH
[32 empty] | 6813 | ELMNTRC | NORTH
[32 empty] | 6814 | CHERY RC | NORTH
[32 empty] | 6815 | EXPLORRC | NORTH
[32 empty] | 6816 | WHTMD RC | NORTH
[32 empty] | 6817 | ETHELRC | NORTH
[32 empty] | 6818 | EVANALRC | NORTH
[32 empty] | 6819 | ANNA_RC | NORTH
[32 empty] | 6821 | I20SUBRC | NORTH
[32 empty] | 6822 | VAN ALRC | NORTH
[32 empty] | 6823 | KIOWARC | NORTH
[32 empty] | 6824 | RENOS RC | NORTH
[32 empty] | 6826 | ALHUB RC | NORTH
[32 empty] | 6830 | ECTOR RC | NORTH
[32 empty] | 6831 | ABLSPRRC | NORTH
[32 empty] | 6832 | MINTR RC | NORTH
[32 empty] | 6838 | WINDM RC | NORTH
[32 empty] | 6840 | BRKSTNRC | NORTH
[32 empty] | 6842 | COMON RC | NORTH
[32 empty] | 6844 | COOP RC | NORTH
[32 empty] | 6845 | CRNDL RC | NORTH
[32 empty] | 6846 | COPEN RC | NORTH
[32 empty] | 6847 | WINDMLRC | NORTH
[32 empty] | 6848 | BNHMLKRC | NORTH
[32 empty] | 6850 | WLF C RC | NORTH
[32 empty] | 6851 | NW WYLIC | NORTH
[32 empty] | 6852 | SULBF RC | NORTH
[32 empty] | 6853 | CLIMAX | NORTH
[32 empty] | 6854 | COMME RC | NORTH
[32 empty] | 6857 | COMMW RC | NORTH
[32 empty] | 6858 | COMBNTRC | NORTH
[32 empty] | 6859 | MARVIN R | NORTH
[32 empty] | 6861 | CUMBY RC | NORTH
[32 empty] | 6865 | FORNYWRC | NORTH
[32 empty] | 6867 | FRNYE RC | NORTH
[32 empty] | 6868 | COPVL RC | NORTH
[32 empty] | 6869 | SUNYPTRC | NORTH
[32 empty] | 6870 | MCKINWRC | NORTH
[32 empty] | 6871 | LNOK_RC | NORTH
[32 empty] | 6873 | MLSSA RC | NORTH
[32 empty] | 6874 | MCK121RC | NORTH
[32 empty] | 6875 | CHAMB RC | NORTH
[32 empty] | 6876 | MCKINERC | NORTH
[32 empty] | 6877 | STONYRC | NORTH
[32 empty] | 6878 | ALLEN RC | NORTH
[32 empty] | 6879 | PARKR RC | NORTH
[32 empty] | 6880 | LUCAS RC | NORTH
[32 empty] | 6881 | WYLIE RC | NORTH
[32 empty] | 6882 | WIELNDRC | NORTH
[32 empty] | 6883 | MSYLK RC | NORTH
[32 empty] | 6884 | QUINLNDR | NORTH
[32 empty] | 6885 | CHIES RC | NORTH
[32 empty] | 6886 | BLDSW RC | NORTH
[32 empty] | 6887 | CARTR RC | NORTH
[32 empty] | 6888 | WSTMNSNR | NORTH
[32 empty] | 6894 | ROSHILRC | NORTH
[32 empty] | 6896 | OAKGV RC | NORTH
[32 empty] | 6897 | NWTER RC | NORTH
[32 empty] | 6898 | TERRL RC | NORTH
[32 empty] | 6900 | KEMP RC | NORTH
[32 empty] | 6902 | TALTYRC | NORTH
[32 empty] | 6904 | COMBNRC | NORTH
[32 empty] | 6906 | RANDRC | NORTH
[32 empty] | 6908 | SCURYRC | NORTH
[32 empty] | 6909 | ALNN RC | NORTH
[32 empty] | 6910 | MSQT RC | NORTH
[32 empty] | 6911 | MESQT_RC | NORTH
[32 empty] | 6912 | COMMS RC | NORTH
[32 empty] | 6914 | EMORY RC | NORTH
[32 empty] | 6918 | TAWK RC | NORTH
[32 empty] | 6919 | ENTPR RC | NORTH
[32 empty] | 6920 | DCKCV RC | NORTH
[32 empty] | 6922 | COBSW RC | NORTH
[32 empty] | 6924 | POYNR RC | NORTH
[32 empty] | 6926 | SEVPT RC | NORTH
[32 empty] | 6928 | TOOL RC | NORTH
[32 empty] | 6930 | WILOW RC | NORTH
[32 empty] | 6932 | CRLSP RC | NORTH
[32 empty] | 6934 | MNTLB RC | NORTH
[32 empty] | 6935 | LKVEW RC | NORTH
[32 empty] | 6936 | STCYRDRC | NORTH
[32 empty] | 6937 | TUCKRRC | NORTH
[32 empty] | 6938 | MALKF RC | NORTH
[32 empty] | 6940 | MASSYRC | NORTH
[32 empty] | 6942 | NECHS RC | NORTH
[32 empty] | 6943 | CELINA R | NORTH
[32 empty] | 6944 | BUROWRC | NORTH
[32 empty] | 6948 | DENISNDM | NORTH
[32 empty] | 6949 | DENISNDM | NORTH
[32 empty] | 7000 | L_FERGUS | SOUTH
[32 empty] | 7004 | L_SIMGID | SOUTH
[32 empty] | 7005 | L_SIMGID | SOUTH
[32 empty] | 7006 | L_SIMGID | SOUTH
[32 empty] | 7007 | L_LOSTPI | SOUTH
[32 empty] | 7008 | L_LOSTPI | SOUTH
[32 empty] | 7009 | L_LOSTPI | SOUTH
[32 empty] | 7010 | L_FPPYD1 | SOUTH
[32 empty] | 7011 | L_FPPYD1 | SOUTH
[32 empty] | 7012 | L_FPPYD2 | SOUTH
[32 empty] | 7014 | L_HAYSEN | SOUTH
[32 empty] | 7015 | L_HAYSEN | SOUTH
[32 empty] | 7016 | L_HAYSEN | SOUTH
[32 empty] | 7017 | L_HAYSEN | SOUTH
[32 empty] | 7020 | L_AUSTPL | SOUTH
[32 empty] | 7022 | L_BUCHAN | SOUTH
[32 empty] | 7023 | L_BUCHAN | SOUTH
[32 empty] | 7024 | L_BUCHAN | SOUTH
[32 empty] | 7026 | L_INKSDA | SOUTH
[32 empty] | 7028 | L_MARBFA | SOUTH
[32 empty] | 7029 | L_MARBFA | SOUTH
[32 empty] | 7031 | L_MARSFO | SOUTH
[32 empty] | 7032 | L_MARSFO | SOUTH
[32 empty] | 7033 | L_MARSFO | SOUTH
[32 empty] | 7035 | L_WIRTZ_ | SOUTH
[32 empty] | 7036 | L_WIRTZ_ | SOUTH
[32 empty] | 7038 | L_DELAWA | WEST
[32 empty] | 7040 | L_AUSTRO | SOUTH
[32 empty] | 7042 | L_ZORN__ | SOUTH
[32 empty] | 7043 | L_HAYSEN | SOUTH
[32 empty] | 7044 | L_MARION | SOUTH
[32 empty] | 7045 | L_ZORN__ | SOUTH
[32 empty] | 7046 | L_KENDAL | SOUTH
[32 empty] | 7047 | L_GUADGE | SOUTH
[32 empty] | 7048 | L_GARFIE | SOUTH
[32 empty] | 7049 | L_MAHACR | SOUTH
[32 empty] | 7050 | L_CLEASP | SOUTH
[32 empty] | 7051 | L_RIONOG | SOUTH
[32 empty] | 7055 | L_FPPYD2 | SOUTH
[32 empty] | 7056 | L_FPPYD1 | SOUTH
[32 empty] | 7057 | L_FAYETT | SOUTH
[32 empty] | 7058 | L_SALEM_ | SOUTH
[32 empty] | 7060 | L_EBABSM | SOUTH
[32 empty] | 7061 | L_COPPCO | SOUTH
[32 empty] | 7062 | L_KEMPNE | SOUTH
[32 empty] | 7063 | L_NARUNA | SOUTH
[32 empty] | 7064 | L_LAMPAS | SOUTH
[32 empty] | 7066 | L_ADAMSV | SOUTH
[32 empty] | 7068 | L_EVANT_ | SOUTH
[32 empty] | 7070 | L_GOLDTH | SOUTH
[32 empty] | 7073 | L_GOLDTH | SOUTH
[32 empty] | 7074 | L_SASASW | SOUTH
[32 empty] | 7075 | L_TERRY_ | SOUTH
[32 empty] | 7076 | L_RICHSP | SOUTH
[32 empty] | 7078 | L_SANSAB | SOUTH
[32 empty] | 7080 | L_LOMETA | SOUTH
[32 empty] | 7082 | L_LAMPAS | SOUTH
[32 empty] | 7084 | L_GRAPMI | SOUTH
[32 empty] | 7087 | L_CORONA | SOUTH
[32 empty] | 7092 | L_BUCHAN | SOUTH
[32 empty] | 7093 | L_CORONA | SOUTH
[32 empty] | 7094 | L_INKSDA | SOUTH
[32 empty] | 7097 | L_BURNET | SOUTH
[32 empty] | 7100 | L_BURNET | SOUTH
[32 empty] | 7101 | L_CTECBU | SOUTH
[32 empty] | 7102 | L_SHERSH | SOUTH
[32 empty] | 7104 | L_WIRTZ_ | SOUTH
[32 empty] | 7107 | L_WIRTZ_ | SOUTH
[32 empty] | 7110 | L_WIRTZ_ | SOUTH
[32 empty] | 7111 | L_FLATRO | SOUTH
[32 empty] | 7112 | L_WIRTZ_ | SOUTH
[32 empty] | 7114 | L_CASTEL | SOUTH
[32 empty] | 7116 | L_SANDMO | SOUTH
[32 empty] | 7119 | L_PITSBU | SOUTH
[32 empty] | 7120 | L_PITSBU | SOUTH
[32 empty] | 7121 | L_SANDCR | SOUTH
[32 empty] | 7122 | L_ECKERT | SOUTH
[32 empty] | 7124 | L_NEBO__ | SOUTH
[32 empty] | 7126 | L_FERGUS | SOUTH
[32 empty] | 7127 | L_SANDCR | SOUTH
[32 empty] | 7128 | L_HORSBA | SOUTH
[32 empty] | 7130 | L_GILLES | SOUTH
[32 empty] | 7132 | L_GILLES | SOUTH
[32 empty] | 7133 | L_NIMITZ | SOUTH
[32 empty] | 7134 | L_WOLFCR | SOUTH
[32 empty] | 7136 | L_KERRST | SOUTH
[32 empty] | 7138 | L_KERRST | SOUTH
[32 empty] | 7140 | L_HARPRO | SOUTH
[32 empty] | 7142 | L_INGRAM | SOUTH
[32 empty] | 7143 | L_RIMROC | SOUTH
[32 empty] | 7144 | L_HUNT__ | SOUTH
[32 empty] | 7146 | L_VERDCR | SOUTH
[32 empty] | 7147 | L_KENDCT | SOUTH
[32 empty] | 7148 | L_MOUNTO | SOUTH
[32 empty] | 7149 | L_FREDER | SOUTH
[32 empty] | 7150 | L_KENDAL | SOUTH
[32 empty] | 7151 | L_CICO__ | SOUTH
[32 empty] | 7152 | L_KENDAL | SOUTH
[32 empty] | 7153 | L_WELFAR | SOUTH
[32 empty] | 7155 | L_COMFOR | SOUTH
[32 empty] | 7156 | L_CYPRCR | SOUTH
[32 empty] | 7158 | L_RAYMBA | SOUTH
[32 empty] | 7159 | L_RAYMBA | SOUTH
[32 empty] | 7160 | L_LEGION | SOUTH
[32 empty] | 7162 | L_TRAVIS | SOUTH
[32 empty] | 7168 | L_BOERNE | SOUTH
[32 empty] | 7169 | L_FAIROA | SOUTH
[32 empty] | 7170 | L_BERGHE | SOUTH
[32 empty] | 7171 | L_ANTLER | SOUTH
[32 empty] | 7172 | L_HENNE_ | SOUTH
[32 empty] | 7173 | L_RIVEOA | SOUTH
[32 empty] | 7174 | L_HENNE_ | SOUTH
[32 empty] | 7175 | L_HORTON | SOUTH
[32 empty] | 7176 | L_COMAL_ | SOUTH
[32 empty] | 7177 | L_HI46WE | SOUTH
[32 empty] | 7178 | L_MARION | SOUTH
[32 empty] | 7180 | L_ZORN__ | SOUTH
[32 empty] | 7181 | L_ZORN__ | SOUTH
[32 empty] | 7182 | L_MCCALA | SOUTH
[32 empty] | 7184 | L_MCCALA | SOUTH
[32 empty] | 7186 | L_RARO12 | SOUTH
[32 empty] | 7188 | L_REDWOO | SOUTH
[32 empty] | 7190 | L_HILLTO | SOUTH
[32 empty] | 7191 | L_SANMAR | SOUTH
[32 empty] | 7192 | L_SANMAR | SOUTH
[32 empty] | 7193 | L_STRAHA | SOUTH
[32 empty] | 7194 | L_REEDTA | SOUTH
[32 empty] | 7196 | L_CAMPGA | SOUTH
[32 empty] | 7197 | L_LEHIGH | SOUTH
[32 empty] | 7198 | L_LEHIGH | SOUTH
[32 empty] | 7200 | L_CANYON | SOUTH
[32 empty] | 7202 | L_HICROS | SOUTH
[32 empty] | 7204 | L_DUMPHI | SOUTH
[32 empty] | 7206 | L_DALE__ | SOUTH
[32 empty] | 7208 | L_COLTON | SOUTH
[32 empty] | 7212 | L_WOLFLA | SOUTH
[32 empty] | 7215 | L_LOCKHA | SOUTH
[32 empty] | 7216 | L_LOCKHA | SOUTH
[32 empty] | 7218 | L_MAGNME | SOUTH
[32 empty] | 7220 | L_LULIMA | SOUTH
[32 empty] | 7223 | L_LULING | SOUTH
[32 empty] | 7224 | L_LULING | SOUTH
[32 empty] | 7225 | L_HICKFO | SOUTH
[32 empty] | 7226 | L_CUSHMA | SOUTH
[32 empty] | 7228 | L_SEGUIN | SOUTH
[32 empty] | 7229 | L_SEGUWE | SOUTH
[32 empty] | 7230 | L_HARWOO | SOUTH
[32 empty] | 7231 | L_THOMPS | SOUTH
[32 empty] | 7232 | L_WAELDE | SOUTH
[32 empty] | 7235 | L_SWEETH | SOUTH
[32 empty] | 7236 | L_MOULTO | SOUTH
[32 empty] | 7237 | L_HENKAU | SOUTH
[32 empty] | 7238 | L_SHINER | SOUTH
[32 empty] | 7239 | L_WESER_ | SOUTH
[32 empty] | 7240 | L_FORDTR | SOUTH
[32 empty] | 7241 | L_YOAKUM | SOUTH
[32 empty] | 7242 | L_YOAKUM | SOUTH
[32 empty] | 7244 | L_CUERO_ | SOUTH
[32 empty] | 7245 | L_GONZAL | SOUTH
[32 empty] | 7246 | L_HALLET | SOUTH
[32 empty] | 7247 | L_FLATON | SOUTH
[32 empty] | 7248 | L_FLATON | SOUTH
[32 empty] | 7250 | L_ENGLE_ | SOUTH
[32 empty] | 7252 | L_SCHULE | SOUTH
[32 empty] | 7254 | L_WEIMAR | SOUTH
[32 empty] | 7257 | L_GLIDDE | SOUTH
[32 empty] | 7258 | L_GLIDDE | SOUTH
[32 empty] | 7263 | L_FRELSB | SOUTH
[32 empty] | 7269 | L_BELLSO | SOUTH
[32 empty] | 7270 | L_BELLSO | SOUTH
[32 empty] | 7271 | L_NEWBRE | SOUTH
[32 empty] | 7272 | L_WALLER | SOUTH
[32 empty] | 7273 | L_WILLSP | SOUTH
[32 empty] | 7274 | L_PLUM__ | SOUTH
[32 empty] | 7275 | L_RIVERS | SOUTH
[32 empty] | 7276 | L_LAGRAN | SOUTH
[32 empty] | 7278 | L_FAYEPL | SOUTH
[32 empty] | 7280 | L_FARIPU | SOUTH
[32 empty] | 7282 | L_FASHPU | SOUTH
[32 empty] | 7286 | L_FAYETT | SOUTH
[32 empty] | 7287 | L_BELLNO | SOUTH
[32 empty] | 7288 | L_WELLBR | SOUTH
[32 empty] | 7289 | L_SALEM_ | SOUTH
[32 empty] | 7291 | L_HIGH36 | SOUTH
[32 empty] | 7292 | L_BRENHA | SOUTH
[32 empty] | 7294 | L_BRENNO | SOUTH
[32 empty] | 7296 | L_PISEK_ | SOUTH
[32 empty] | 7297 | L_ROTOTA | SOUTH
[32 empty] | 7299 | L_ROUNTO | SOUTH
[32 empty] | 7302 | L_GIDDIN | SOUTH
[32 empty] | 7306 | L_WINCHE | SOUTH
[32 empty] | 7308 | L_PAIGE_ | SOUTH
[32 empty] | 7310 | L_SIMGID | SOUTH
[32 empty] | 7312 | L_WARDA_ | SOUTH
[32 empty] | 7314 | L_SMITHV | SOUTH
[32 empty] | 7315 | L_SMITHV | SOUTH
[32 empty] | 7318 | L_ALCRSW | SOUTH
[32 empty] | 7322 | L_BASTCI | SOUTH
[32 empty] | 7324 | L_BUTLER | SOUTH
[32 empty] | 7325 | L_MENDOZ | SOUTH
[32 empty] | 7326 | L_CAMPSW | SOUTH
[32 empty] | 7327 | L_ELTPTU | SOUTH
[32 empty] | 7328 | L_AUSTRO | SOUTH
[32 empty] | 7329 | L_WEBBER | SOUTH
[32 empty] | 7330 | L_MANOR_ | SOUTH
[32 empty] | 7331 | L_CEDAHI | SOUTH
[32 empty] | 7333 | L_HARRBR | SOUTH
[32 empty] | 7334 | L_MCNEIL | SOUTH
[32 empty] | 7335 | L_HOLATA | SOUTH
[32 empty] | 7336 | L_GILLCR | SOUTH
[32 empty] | 7339 | L_AUSTPL | SOUTH
[32 empty] | 7343 | L_GEORGE | SOUTH
[32 empty] | 7345 | L_GABRIE | SOUTH
[32 empty] | 7346 | L_GABRIE | SOUTH
[32 empty] | 7347 | L_RIVERY | SOUTH
[32 empty] | 7348 | L_MARBFA | SOUTH
[32 empty] | 7349 | L_LAKETP | SOUTH
[32 empty] | 7350 | L_MORMMI | SOUTH
[32 empty] | 7351 | L_STARCK | SOUTH
[32 empty] | 7352 | L_LAGOVI | SOUTH
[32 empty] | 7353 | L_VISTA_ | SOUTH
[32 empty] | 7354 | L_MARSFO | SOUTH
[32 empty] | 7355 | L_SEGOVI | SOUTH
[32 empty] | 7356 | L_MARSFO | SOUTH
[32 empty] | 7359 | L_MARSFO | SOUTH
[32 empty] | 7360 | L_MARSFO | SOUTH
[32 empty] | 7362 | L_MARSFO | SOUTH
[32 empty] | 7366 | L_CHIEBR | SOUTH
[32 empty] | 7386 | L_CAMPBO | NORTH
[32 empty] | 7387 | L_KUNITZ | WEST
[32 empty] | 7400 | L_SUNRBE | SOUTH
[32 empty] | 7402 | L_KINGS2 | SOUTH
[32 empty] | 7404 | L_KINGS1 | SOUTH
[32 empty] | 7406 | L_BLUFFT | SOUTH
[32 empty] | 7408 | L_DOSS__ | SOUTH
[32 empty] | 7410 | L_HARPER | SOUTH
[32 empty] | 7412 | L_LIVEOA | SOUTH
[32 empty] | 7413 | L_GOEHTA | SOUTH
[32 empty] | 7414 | L_GOEHLA | SOUTH
[32 empty] | 7415 | L_FREDER | SOUTH
[32 empty] | 7426 | L_LEAKEY | SOUTH
[32 empty] | 7428 | L_UTOPIA | SOUTH
[32 empty] | 7430 | L_MEDICI | SOUTH
[32 empty] | 7432 | L_MEDILA | SOUTH
[32 empty] | 7436 | L_PIPECR | SOUTH
[32 empty] | 7437 | L_PIPECR | SOUTH
[32 empty] | 7438 | L_BANDER | SOUTH
[32 empty] | 7439 | L_BANDER | SOUTH
[32 empty] | 7440 | L_TARPLE | SOUTH
[32 empty] | 7441 | L_MASOCR | SOUTH
[32 empty] | 7442 | L_TURTCR | SOUTH
[32 empty] | 7454 | L_TEXIND | SOUTH
[32 empty] | 7456 | L_LOP337 | SOUTH
[32 empty] | 7458 | L_GPI___ | SOUTH
[32 empty] | 7459 | L_GPISWI | SOUTH
[32 empty] | 7460 | L_SHERPO | SOUTH
[32 empty] | 7461 | L_WEIDER | SOUTH
[32 empty] | 7462 | L_FREIHE | SOUTH
[32 empty] | 7474 | L_GRANMO | SOUTH
[32 empty] | 7476 | L_PALEFA | SOUTH
[32 empty] | 7477 | L_PALEPE | SOUTH
[32 empty] | 7478 | L_PHJOCI | SOUTH
[32 empty] | 7479 | L_MILLER | SOUTH
[32 empty] | 7480 | L_MOUNTO | SOUTH
[32 empty] | 7482 | L_BLANCO | SOUTH
[32 empty] | 7484 | L_DEVIHI | SOUTH
[32 empty] | 7487 | L_CANYHY | SOUTH
[32 empty] | 7488 | L_SATTLE | SOUTH
[32 empty] | 7490 | L_CRANMI | SOUTH
[32 empty] | 7491 | L_HUNTER | SOUTH
[32 empty] | 7492 | L_FISCHE | SOUTH
[32 empty] | 7493 | L_DEVIHI | SOUTH
[32 empty] | 7496 | L_WIMBER | SOUTH
[32 empty] | 7498 | L_BUDA__ | SOUTH
[32 empty] | 7499 | L_BUDA__ | SOUTH
[32 empty] | 7500 | L_TURNER | SOUTH
[32 empty] | 7501 | L_GOFORT | SOUTH
[32 empty] | 7502 | L_KYLE__ | SOUTH
[32 empty] | 7504 | L_MANCHA | SOUTH
[32 empty] | 7506 | L_CEDAVA | SOUTH
[32 empty] | 7507 | L_FRIEND | SOUTH
[32 empty] | 7508 | L_CENTEX | SOUTH
[32 empty] | 7509 | L_RUTHER | SOUTH
[32 empty] | 7510 | L_MILRCR | SOUTH
[32 empty] | 7512 | L_DRIPSP | SOUTH
[32 empty] | 7513 | L_HENLY_ | SOUTH
[32 empty] | 7514 | L_BLANTA | SOUTH
[32 empty] | 7515 | L_ROHR__ | SOUTH
[32 empty] | 7516 | L_JOHNCI | SOUTH
[32 empty] | 7518 | L_FAIRLA | SOUTH
[32 empty] | 7520 | L_BERTRA | SOUTH
[32 empty] | 7521 | L_ANDICE | SOUTH
[32 empty] | 7522 | L_ANDICE | SOUTH
[32 empty] | 7523 | L_GLASSC | SOUTH
[32 empty] | 7524 | L_SEWARD | SOUTH
[32 empty] | 7525 | L_LEANDE | SOUTH
[32 empty] | 7526 | L_NAMELE | SOUTH
[32 empty] | 7527 | L_BLOCKH | SOUTH
[32 empty] | 7528 | L_GEOREA | SOUTH
[32 empty] | 7529 | L_WHITES | SOUTH
[32 empty] | 7530 | L_KENTST | SOUTH
[32 empty] | 7531 | L_BUTTER | SOUTH
[32 empty] | 7532 | L_GEORSO | SOUTH
[32 empty] | 7533 | L_BALCON | SOUTH
[32 empty] | 7534 | L_AVERRA | SOUTH
[32 empty] | 7538 | L_LAKEWA | SOUTH
[32 empty] | 7540 | L_BEECRE | SOUTH
[32 empty] | 7542 | L_SPICEW | SOUTH
[32 empty] | 7545 | L_HIGH32 | SOUTH
[32 empty] | 7546 | L_HIGH32 | SOUTH
[32 empty] | 7554 | L_MARTIN | SOUTH
[32 empty] | 7555 | L_BASTWE | SOUTH
[32 empty] | 7556 | L_BLUEBO | SOUTH
[32 empty] | 7557 | L_NEROTA | SOUTH
[32 empty] | 7558 | L_NEWROS | SOUTH
[32 empty] | 7559 | L_NEROPU | SOUTH
[32 empty] | 7560 | L_REDROC | SOUTH
[32 empty] | 7564 | L_GUYBUR | SOUTH
[32 empty] | 7565 | L_MILLCR | SOUTH
[32 empty] | 7567 | L_DEANVI | SOUTH
[32 empty] | 7570 | L_SANDHI | SOUTH
[32 empty] | 7571 | L_LEXING | SOUTH
[32 empty] | 7572 | L_GAYHIL | SOUTH
[32 empty] | 7573 | L_LYONS_ | SOUTH
[32 empty] | 7574 | L_CHAPHI | SOUTH
[32 empty] | 7576 | L_HILBIG | SOUTH
[32 empty] | 7577 | L_WELCOM | SOUTH
[32 empty] | 7586 | L_HALLGV | SOUTH
[32 empty] | 7588 | L_MOULGV | SOUTH
[32 empty] | 7590 | L_SHINGV | SOUTH
[32 empty] | 7592 | L_GONZGV | SOUTH
[32 empty] | 7594 | L_OTTINE | SOUTH
[32 empty] | 7596 | L_NASHCR | SOUTH
[32 empty] | 7598 | L_CAPOTE | SOUTH
[32 empty] | 7600 | L_SEGUIN | SOUTH
[32 empty] | 7602 | L_STMEIN | SOUTH
[32 empty] | 7604 | L_GERONI | SOUTH
[32 empty] | 7605 | L_MCQUEE | SOUTH
[32 empty] | 7606 | L_MCQUEE | SOUTH
[32 empty] | 7608 | L_CIBOLO | SOUTH
[32 empty] | 7609 | L_SCHUMA | SOUTH
[32 empty] | 7610 | L_SCHERT | SOUTH
[32 empty] | 7611 | L_PARKWA | SOUTH
[32 empty] | 7612 | L_NEWBER | SOUTH
[32 empty] | 7613 | L_OLMOSW | SOUTH
[32 empty] | 7614 | L_LAVERN | SOUTH
[32 empty] | 7615 | L_WILSON | SOUTH
[32 empty] | 7616 | L_NIXOGV | SOUTH
[32 empty] | 7617 | L_NIXON1 | SOUTH
[32 empty] | 7618 | L_SMILGO | SOUTH
[32 empty] | 7619 | L_OLMOSW | SOUTH
[32 empty] | 7620 | L_SMILEY | SOUTH
[32 empty] | 7622 | L_COST__ | SOUTH
[32 empty] | 7624 | L_LAKEWO | SOUTH
[32 empty] | 7625 | L_LAKETA | SOUTH
[32 empty] | 7626 | L_GONZAL | SOUTH
[32 empty] | 7636 | L_COLORA | SOUTH
[32 empty] | 7638 | L_SHELPL | SOUTH
[32 empty] | 7639 | L_SHERID | SOUTH
[32 empty] | 7640 | L_ROCKIS | SOUTH
[32 empty] | 7642 | L_SBBETA | SOUTH
[32 empty] | 7644 | L_THORSW | SOUTH
[32 empty] | 7646 | L_THOTA1 | SOUTH
[32 empty] | 7648 | L_PARKBR | SOUTH
[32 empty] | 7650 | L_THOTA2 | SOUTH
[32 empty] | 7654 | L_BERNAR | SOUTH
[32 empty] | 7656 | L_BELLSB | SOUTH
[32 empty] | 7658 | L_BETASB | SOUTH
[32 empty] | 7660 | L_QUANSW | SOUTH
[32 empty] | 7662 | L_QUANEX | SOUTH
[32 empty] | 7663 | L_MECRTA | SOUTH
[32 empty] | 7664 | L_SUNNYS | SOUTH
[32 empty] | 7665 | L_MENGCR | SOUTH
[32 empty] | 7666 | L_PRAIVI | SOUTH
[32 empty] | 7668 | L_PRAIVI | SOUTH
[32 empty] | 7670 | L_SEAWAY | SOUTH
[32 empty] | 7671 | L_MACEDO | HOUSTON
[32 empty] | 7672 | L_ESCARP | SOUTH
[32 empty] | 7680 | L_CLEASP | SOUTH
[32 empty] | 7800 | L_GUADGE | SOUTH
[32 empty] | 7801 | L_GUADGE | SOUTH
[32 empty] | 7802 | L_GUADGE | SOUTH
[32 empty] | 7803 | L_GUADGE | SOUTH
[32 empty] | 7804 | L_GUADGE | SOUTH
[32 empty] | 7805 | L_GUADGE | SOUTH
[32 empty] | 7807 | L_BASTEN | SOUTH
[32 empty] | 7808 | L_BASTEN | SOUTH
[32 empty] | 7809 | L_BASTEN | SOUTH
[32 empty] | 7810 | L_RIONOG | SOUTH
[32 empty] | 7811 | L_RIONOG | SOUTH
[32 empty] | 7812 | L_RIONOG | SOUTH
[32 empty] | 7813 | L_RIONOG | SOUTH
[32 empty] | 8032 | AMISTADH | SOUTH
[32 empty] | 8033 | AMISTADH | SOUTH
[32 empty] | 8048 | FALCONHY | SOUTH
[32 empty] | 8062 | NBRE#1 | SOUTH
[32 empty] | 8063 | NBRE#2 | SOUTH
[32 empty] | 8064 | NBRE#3 | SOUTH
[32 empty] | 8066 | DUP1V#1 | SOUTH
[32 empty] | 8100 | EL_CAMPO | SOUTH
[32 empty] | 8102 | EL_CAMPO | SOUTH
[32 empty] | 8104 | LANCTYPM | HOUSTON
[32 empty] | 8105 | EAGLE_LK | SOUTH
[32 empty] | 8106 | ALTAIR2A | SOUTH
[32 empty] | 8107 | TCC-GLN2 | SOUTH
[32 empty] | 8109 | TCC-GLN4 | SOUTH
[32 empty] | 8111 | COLUMBUS | SOUTH
[32 empty] | 8113 | BAY_CITY | HOUSTON
[32 empty] | 8114 | CONOCO4A | HOUSTON
[32 empty] | 8115 | WADSWORT | HOUSTON
[32 empty] | 8116 | CELANEBC | HOUSTON
[32 empty] | 8117 | GANADO4A | SOUTH
[32 empty] | 8118 | EDNA4A | SOUTH
[32 empty] | 8119 | BLESSING | SOUTH
[32 empty] | 8121 | BLESSING | SOUTH
[32 empty] | 8123 | BLESSNG6 | SOUTH
[32 empty] | 8125 | LOLITA4A | SOUTH
[32 empty] | 8126 | FORMOSA4 | SOUTH
[32 empty] | 8127 | LAN_CTY4 | HOUSTON
[32 empty] | 8131 | PALACIOS | SOUTH
[32 empty] | 8132 | P.CMFT 2 | SOUTH
[32 empty] | 8133 | BROOKHOL | SOUTH
[32 empty] | 8134 | FOR #1 | SOUTH
[32 empty] | 8135 | P_LAVACA | SOUTH
[32 empty] | 8136 | PLACEDO2 | SOUTH
[32 empty] | 8137 | ALCOA 4 | SOUTH
[32 empty] | 8138 | FOR #2 | SOUTH
[32 empty] | 8139 | JOS #1 | SOUTH
[32 empty] | 8140 | JOSLIN4A | SOUTH
[32 empty] | 8141 | GOHLKE4A | SOUTH
[32 empty] | 8143 | V_DUPSW4 | SOUTH
[32 empty] | 8144 | AIRCO44A | SOUTH
[32 empty] | 8145 | VISTRON4 | SOUTH
[32 empty] | 8146 | BIGTRE4A | SOUTH
[32 empty] | 8147 | UCAR #2 | SOUTH
[32 empty] | 8148 | UCAR #1 | SOUTH
[32 empty] | 8149 | NCARBIDE | SOUTH
[32 empty] | 8152 | NCARBIDE | SOUTH
[32 empty] | 8153 | FOR #3 | SOUTH
[32 empty] | 8154 | FOR #4 | SOUTH
[32 empty] | 8155 | FOR #5 | SOUTH
[32 empty] | 8156 | FOR #6 | SOUTH
[32 empty] | 8157 | FOR #7 | SOUTH
[32 empty] | 8159 | GREENLK2 | SOUTH
[32 empty] | 8160 | CC1TERT | SOUTH
[32 empty] | 8161 | COLETO0A | SOUTH
[32 empty] | 8162 | COLETO4A | SOUTH
[32 empty] | 8164 | COLETO7A | SOUTH
[32 empty] | 8165 | COLETSTR | SOUTH
[32 empty] | 8166 | CSABLK2A | SOUTH
[32 empty] | 8167 | GEWST4A | SOUTH
[32 empty] | 8168 | COLETSTR | SOUTH
[32 empty] | 8169 | VICTORIA | SOUTH
[32 empty] | 8172 | VICTORIA | SOUTH
[32 empty] | 8173 | VICEC51A | SOUTH
[32 empty] | 8174 | VICEC61A | SOUTH
[32 empty] | 8177 | MAGRUDER | SOUTH
[32 empty] | 8178 | N_VICT2A | SOUTH
[32 empty] | 8179 | FOSTER_T | SOUTH
[32 empty] | 8180 | FOSTER2A | SOUTH
[32 empty] | 8181 | CC2TERT | SOUTH
[32 empty] | 8182 | LEARY_LN | SOUTH
[32 empty] | 8183 | THOMASTN | SOUTH
[32 empty] | 8184 | KENEDYSW | SOUTH
[32 empty] | 8186 | KENEDYSW | SOUTH
[32 empty] | 8188 | KENEDY2A | SOUTH
[32 empty] | 8189 | CUECPL2A | SOUTH
[32 empty] | 8190 | C.LCRA 2 | SOUTH
[32 empty] | 8192 | CUELCA4A | SOUTH
[32 empty] | 8195 | DARST_CR | SOUTH
[32 empty] | 8198 | BEEVILLE | SOUTH
[32 empty] | 8199 | LULNG M4 | SOUTH
[32 empty] | 8200 | PLEASANT | SOUTH
[32 empty] | 8203 | PLEASANT | SOUTH
[32 empty] | 8206 | CHARLOTT | SOUTH
[32 empty] | 8208 | DILLEY22 | SOUTH
[32 empty] | 8210 | DILLEYSW | SOUTH
[32 empty] | 8212 | DILLEYSW | SOUTH
[32 empty] | 8216 | PEARSAL2 | SOUTH
[32 empty] | 8218 | BIG_FOOT | SOUTH
[32 empty] | 8221 | BIG_FOOT | SOUTH
[32 empty] | 8223 | DEVINE2A | SOUTH
[32 empty] | 8225 | MOORE4A | SOUTH
[32 empty] | 8229 | BATSVL4 | SOUTH
[32 empty] | 8231 | UVALDE2A | SOUTH
[32 empty] | 8234 | UVALDE4A | SOUTH
[32 empty] | 8235 | ROCK_ATL | SOUTH
[32 empty] | 8236 | W_BATESV | SOUTH
[32 empty] | 8237 | KIMBLE2A | SOUTH
[32 empty] | 8238 | ROCKSPRS | SOUTH
[32 empty] | 8239 | FRIR2A | WEST
[32 empty] | 8242 | CRYSTAL2 | SOUTH
[32 empty] | 8243 | TURTLCR2 | SOUTH
[32 empty] | 8244 | CARRIZO2 | SOUTH
[32 empty] | 8246 | ASPHALT4 | SOUTH
[32 empty] | 8252 | BRACKVL4 | SOUTH
[32 empty] | 8253 | HAMILTON | SOUTH
[32 empty] | 8255 | HAMILTN4 | SOUTH
[32 empty] | 8257 | HAMIL_P4 | SOUTH
[32 empty] | 8258 | AMISTAD4 | SOUTH
[32 empty] | 8259 | CAUTHORN | WEST
[32 empty] | 8260 | ESCONDID | SOUTH
[32 empty] | 8262 | ELPS | SOUTH
[32 empty] | 8263 | EPASS H4 | SOUTH
[32 empty] | 8264 | EP.H TP4 | SOUTH
[32 empty] | 8270 | EAGLE_PS | SOUTH
[32 empty] | 8273 | PUEBLO4A | SOUTH
[32 empty] | 8274 | W_CONOCO | SOUTH
[32 empty] | 8280 | ASHERTON | SOUTH
[32 empty] | 8283 | ASHERTON | SOUTH
[32 empty] | 8285 | LAR #1 | SOUTH
[32 empty] | 8287 | LAR #2 | SOUTH
[32 empty] | 8288 | LAR #3 | SOUTH
[32 empty] | 8290 | LAREDO2A | SOUTH
[32 empty] | 8293 | LAREDO4A | SOUTH
[32 empty] | 8295 | WORMSER4 | SOUTH
[32 empty] | 8297 | BRUNI44A | SOUTH
[32 empty] | 8299 | ZAPATA4A | SOUTH
[32 empty] | 8300 | RAYVILE2 | SOUTH
[32 empty] | 8302 | RAYVILE4 | SOUTH
[32 empty] | 8310 | LAPALM 2 | SOUTH
[32 empty] | 8314 | LAPALM 4 | SOUTH
[32 empty] | 8317 | LAPALM 6 | SOUTH
[32 empty] | 8318 | RIOHONDO | SOUTH
[32 empty] | 8319 | RIOHONDO | SOUTH
[32 empty] | 8320 | W HGN 2 | SOUTH
[32 empty] | 8321 | HGN-1 2 | SOUTH
[32 empty] | 8322 | HAINEDR4 | SOUTH
[32 empty] | 8323 | E_HARRIS | SOUTH
[32 empty] | 8324 | LAPALSTR | SOUTH
[32 empty] | 8325 | HARLINSW | SOUTH
[32 empty] | 8326 | RIOHOSTR | SOUTH
[32 empty] | 8327 | HARLINSW | SOUTH
[32 empty] | 8328 | LP3TERT | SOUTH
[32 empty] | 8329 | L.FRES 2 | SOUTH
[32 empty] | 8330 | RIOHOSTR | SOUTH
[32 empty] | 8331 | BRWN CY2 | SOUTH
[32 empty] | 8332 | BRWN SW2 | SOUTH
[32 empty] | 8334 | CAVAZOS2 | SOUTH
[32 empty] | 8335 | S_PADRE4 | SOUTH
[32 empty] | 8336 | RH1TERT | SOUTH
[32 empty] | 8337 | SCARBIDE | SOUTH
[32 empty] | 8338 | P.ISABL4 | SOUTH
[32 empty] | 8339 | MIL.HWY4 | SOUTH
[32 empty] | 8341 | ED1TERT | SOUTH
[32 empty] | 8347 | WESMER 4 | SOUTH
[32 empty] | 8348 | WES UNT4 | SOUTH
[32 empty] | 8354 | WESLCSW4 | SOUTH
[32 empty] | 8355 | GOODWIN4 | SOUTH
[32 empty] | 8356 | HECB 4 | SOUTH
[32 empty] | 8357 | NWESLACO | SOUTH
[32 empty] | 8358 | N_MERCED | SOUTH
[32 empty] | 8359 | SS.ROSA | SOUTH
[32 empty] | 8360 | ELSA 4 | SOUTH
[32 empty] | 8367 | WMCALN 4 | SOUTH
[32 empty] | 8368 | NMCALN 4 | SOUTH
[32 empty] | 8371 | SMCALN 4 | SOUTH
[32 empty] | 8372 | PHARR 4 | SOUTH
[32 empty] | 8373 | POLK 4 | SOUTH
[32 empty] | 8374 | SE EDNB4 | SOUTH
[32 empty] | 8377 | NEDIN2A | SOUTH
[32 empty] | 8380 | NEDIN4A | SOUTH
[32 empty] | 8383 | NEDIN7A | SOUTH
[32 empty] | 8384 | NEDINSTR | SOUTH
[32 empty] | 8387 | PALMVW 4 | SOUTH
[32 empty] | 8388 | BATES0A | SOUTH
[32 empty] | 8390 | BATES 2 | SOUTH
[32 empty] | 8391 | SHLND 4 | SOUTH
[32 empty] | 8392 | BATES 4 | SOUTH
[32 empty] | 8393 | BATES0B | SOUTH
[32 empty] | 8395 | FALCON 4 | SOUTH
[32 empty] | 8397 | GARZA 2 | SOUTH
[32 empty] | 8399 | GARZA 4 | SOUTH
[32 empty] | 8400 | THREE_RI | SOUTH
[32 empty] | 8403 | THREE_RI | SOUTH
[32 empty] | 8404 | SIGMOR4A | SOUTH
[32 empty] | 8405 | SKIDMORE | SOUTH
[32 empty] | 8407 | MATHIS2A | SOUTH
[32 empty] | 8408 | EDROY2A | SOUTH
[32 empty] | 8409 | GRETA2A | SOUTH
[32 empty] | 8410 | REFUGIO2 | SOUTH
[32 empty] | 8413 | SINTON2A | SOUTH
[32 empty] | 8414 | PORTLAND | SOUTH
[32 empty] | 8416 | RINCON2A | SOUTH
[32 empty] | 8418 | RINCON4A | SOUTH
[32 empty] | 8421 | GREGORY2 | SOUTH
[32 empty] | 8422 | I_DUPSW4 | SOUTH
[32 empty] | 8425 | INGLESID | SOUTH
[32 empty] | 8426 | CITGO_NO | SOUTH
[32 empty] | 8427 | ARANSAS2 | SOUTH
[32 empty] | 8430 | ARANSAS4 | SOUTH
[32 empty] | 8431 | LIVE_OAK | SOUTH
[32 empty] | 8432 | ROCKPORT | SOUTH
[32 empty] | 8434 | ROCKPORT | SOUTH
[32 empty] | 8435 | SEAWALL2 | SOUTH
[32 empty] | 8436 | PORT_A2A | SOUTH
[32 empty] | 8437 | NUECES_B | SOUTH
[32 empty] | 8438 | NUECES_B | SOUTH
[32 empty] | 8439 | NUECES_B | SOUTH
[32 empty] | 8441 | NUECES_B | SOUTH
[32 empty] | 8442 | NUECES_B | SOUTH
[32 empty] | 8448 | LON_HILL | SOUTH
[32 empty] | 8452 | LON_HILL | SOUTH
[32 empty] | 8455 | LON_HILL | SOUTH
[32 empty] | 8456 | COSW#1 | SOUTH
[32 empty] | 8457 | COSW#2 | SOUTH
[32 empty] | 8458 | B_DAVIS4 | SOUTH
[32 empty] | 8459 | B_DAVIS0 | SOUTH
[32 empty] | 8460 | B_DAVIS0 | SOUTH
[32 empty] | 8461 | KOCH_UP0 | SOUTH
[32 empty] | 8462 | LON_HSTR | SOUTH
[32 empty] | 8463 | COASTSTE | SOUTH
[32 empty] | 8464 | COASTAL2 | SOUTH
[32 empty] | 8465 | INDUSTRI | SOUTH
[32 empty] | 8466 | CANTWELL | SOUTH
[32 empty] | 8467 | KOCH_UP4 | SOUTH
[32 empty] | 8468 | HIWAY_92 | SOUTH
[32 empty] | 8469 | KOCH_UP2 | SOUTH
[32 empty] | 8470 | HIWAY_94 | SOUTH
[32 empty] | 8471 | LON_HSTR | SOUTH
[32 empty] | 8474 | MORRIS4A | SOUTH
[32 empty] | 8475 | JAVELINA | SOUTH
[32 empty] | 8476 | CITGO_W4 | SOUTH
[32 empty] | 8477 | VALERO2A | SOUTH
[32 empty] | 8478 | OXY_CC4A | SOUTH
[32 empty] | 8479 | CLARK_WD | SOUTH
[32 empty] | 8481 | KOCH_HF4 | SOUTH
[32 empty] | 8482 | WEIL_TRC | SOUTH
[32 empty] | 8483 | SOUTH_SI | SOUTH
[32 empty] | 8484 | WEST_OSO | SOUTH
[32 empty] | 8485 | WESTSIDE | SOUTH
[32 empty] | 8486 | HOLLY44A | SOUTH
[32 empty] | 8487 | AIRLINE2 | SOUTH
[32 empty] | 8490 | AIRLINE4 | SOUTH
[32 empty] | 8492 | WOOLRIDG | SOUTH
[32 empty] | 8493 | PHARAOH4 | SOUTH
[32 empty] | 8494 | LAGUNA2A | SOUTH
[32 empty] | 8495 | NAVAL_BS | SOUTH
[32 empty] | 8496 | ARCADIA4 | SOUTH
[32 empty] | 8498 | BISHOP2A | SOUTH
[32 empty] | 8499 | LH3TERT | SOUTH
[32 empty] | 8500 | ALICE2A | SOUTH
[32 empty] | 8502 | LH4TERT | SOUTH
[32 empty] | 8503 | ALICE4A | SOUTH
[32 empty] | 8505 | FREER2A | SOUTH
[32 empty] | 8506 | VAL #1 | SOUTH
[32 empty] | 8507 | VAL #2 | SOUTH
[32 empty] | 8508 | FALFUR2A | SOUTH
[32 empty] | 8510 | FALFUR4A | SOUTH
[32 empty] | 8511 | OXY_CC0A | SOUTH
[32 empty] | 8512 | STRATN 2 | SOUTH
[32 empty] | 8514 | STRATTON | SOUTH
[32 empty] | 8515 | ALAZAN4A | SOUTH
[32 empty] | 8516 | CELANEBI | SOUTH
[32 empty] | 8517 | CELANEBI | SOUTH
[32 empty] | 8518 | KINGSVIL | SOUTH
[32 empty] | 8519 | KLEBERG4 | SOUTH
[32 empty] | 8520 | STAFFORD | SOUTH
[32 empty] | 8523 | PRAIRPMP | SOUTH
[32 empty] | 8524 | P.PMP T2 | SOUTH
[32 empty] | 8526 | R.SIDET2 | SOUTH
[32 empty] | 8527 | RIVER_SD | SOUTH
[32 empty] | 8528 | PKR TP 2 | SOUTH
[32 empty] | 8529 | PARKER2A | SOUTH
[32 empty] | 8530 | GARWDTAP | SOUTH
[32 empty] | 8531 | GARWDPMP | SOUTH
[32 empty] | 8532 | IDEAL_TP | SOUTH
[32 empty] | 8533 | GARWDRLF | SOUTH
[32 empty] | 8534 | TXI_TP2A | SOUTH
[32 empty] | 8535 | PIONEERS | SOUTH
[32 empty] | 8536 | PV_TAP2A | SOUTH
[32 empty] | 8537 | IDEAL_2A | SOUTH
[32 empty] | 8538 | GARWOOD2 | SOUTH
[32 empty] | 8539 | L STR T2 | SOUTH
[32 empty] | 8541 | LONE_STR | SOUTH
[32 empty] | 8542 | MATTHEWS | SOUTH
[32 empty] | 8543 | LAKESIDP | SOUTH
[32 empty] | 8545 | BC-TP 2 | SOUTH
[32 empty] | 8546 | BCPMPTP2 | SOUTH
[32 empty] | 8547 | BYCTYPM1 | SOUTH
[32 empty] | 8549 | BYCTYPM3 | SOUTH
[32 empty] | 8550 | MARKHAM2 | SOUTH
[32 empty] | 8552 | MIDFLD_T | SOUTH
[32 empty] | 8555 | CARANCUA | SOUTH
[32 empty] | 8556 | CLMVL T2 | SOUTH
[32 empty] | 8557 | CLEMVILL | SOUTH
[32 empty] | 8558 | STP PTP4 | HOUSTON
[32 empty] | 8559 | STP-CON4 | HOUSTON
[32 empty] | 8560 | CNOPGT1 | SOUTH
[32 empty] | 8561 | CNOPGT2 | SOUTH
[32 empty] | 8562 | CNOPST1 | SOUTH
[32 empty] | 8563 | STPFACHL | HOUSTON
[32 empty] | 8564 | DUP1-V 4 | SOUTH
[32 empty] | 8565 | DUP2-V 4 | SOUTH
[32 empty] | 8572 | WEAVERRD | SOUTH
[32 empty] | 8573 | RUNGE2A | SOUTH
[32 empty] | 8574 | NORDHEIM | SOUTH
[32 empty] | 8575 | YORKTOWN | SOUTH
[32 empty] | 8577 | HOCH.TP2 | SOUTH
[32 empty] | 8578 | HOCHEIM2 | SOUTH
[32 empty] | 8579 | MALONE2A | SOUTH
[32 empty] | 8580 | NIXON2A | SOUTH
[32 empty] | 8581 | MAG.TP 2 | SOUTH
[32 empty] | 8582 | NIXONLCR | SOUTH
[32 empty] | 8583 | MAGNOLA2 | SOUTH
[32 empty] | 8584 | CHASETAP | SOUTH
[32 empty] | 8585 | CHASEFLD | SOUTH
[32 empty] | 8586 | BERCLAIR | SOUTH
[32 empty] | 8587 | GOLIAD2A | SOUTH
[32 empty] | 8589 | FANNIN2A | SOUTH
[32 empty] | 8591 | OCONNER2 | SOUTH
[32 empty] | 8592 | NORMANNA | SOUTH
[32 empty] | 8593 | PETTUS2A | SOUTH
[32 empty] | 8598 | COY CTY2 | SOUTH
[32 empty] | 8599 | FASHING2 | SOUTH
[32 empty] | 8600 | COY_CITY | SOUTH
[32 empty] | 8603 | IMOGNTAP | SOUTH
[32 empty] | 8604 | IMOGNE 2 | SOUTH
[32 empty] | 8607 | JOURDNTN | SOUTH
[32 empty] | 8610 | COTULLA4 | SOUTH
[32 empty] | 8613 | BIG_WELL | SOUTH
[32 empty] | 8619 | ENCINAL4 | SOUTH
[32 empty] | 8622 | LYTLE22A | SOUTH
[32 empty] | 8628 | KNIPPA2A | SOUTH
[32 empty] | 8630 | SABINAL2 | SOUTH
[32 empty] | 8633 | CAMPWOOD | SOUTH
[32 empty] | 8635 | ZACATE4A | SOUTH
[32 empty] | 8637 | ANNA ST4 | SOUTH
[32 empty] | 8641 | SIEVISTA | SOUTH
[32 empty] | 8642 | WASH_ST2 | SOUTH
[32 empty] | 8643 | MINES_RD | SOUTH
[32 empty] | 8645 | DEL_MAR4 | SOUTH
[32 empty] | 8646 | RIO_BRAV | SOUTH
[32 empty] | 8647 | UNIV44A | SOUTH
[32 empty] | 8648 | GATEWAY4 | SOUTH
[32 empty] | 8649 | GATEWAE4 | SOUTH
[32 empty] | 8650 | GATEWAW4 | SOUTH
[32 empty] | 8653 | ST_NINO4 | SOUTH
[32 empty] | 8664 | HUMBPMP2 | SOUTH
[32 empty] | 8672 | LA_PRYOR | SOUTH
[32 empty] | 8681 | HAMILRGE | SOUTH
[32 empty] | 8682 | COMSTOCK | SOUTH
[32 empty] | 8684 | PICACHO4 | SOUTH
[32 empty] | 8686 | AMSIBWC4 | SOUTH
[32 empty] | 8688 | BUENA_VI | SOUTH
[32 empty] | 8690 | DEL_RIO4 | SOUTH
[32 empty] | 8692 | MAVERICK | SOUTH
[32 empty] | 8694 | CONOCO_L | SOUTH
[32 empty] | 8695 | CRESTONI | SOUTH
[32 empty] | 8699 | RANDADO4 | SOUTH
[32 empty] | 8700 | RAYVL1-2 | SOUTH
[32 empty] | 8702 | YTURRIAS | SOUTH
[32 empty] | 8704 | LASARASU | SOUTH
[32 empty] | 8705 | ERAYMNDV | SOUTH
[32 empty] | 8708 | MONTECRI | SOUTH
[32 empty] | 8710 | SBENITO2 | SOUTH
[32 empty] | 8744 | CAUSWAY4 | SOUTH
[32 empty] | 8747 | RNGRVILL | SOUTH
[32 empty] | 8748 | RNGRVLE2 | SOUTH
[32 empty] | 8751 | RIORICO2 | SOUTH
[32 empty] | 8752 | MERRETTS | SOUTH
[32 empty] | 8753 | DOEDYNSU | SOUTH
[32 empty] | 8754 | ADERHOLD | SOUTH
[32 empty] | 8755 | GANDYSUB | SOUTH
[32 empty] | 8756 | LAURELES | SOUTH
[32 empty] | 8758 | LASMILPA | SOUTH
[32 empty] | 8759 | ALBERTAR | SOUTH
[32 empty] | 8760 | H.ACRES4 | SOUTH
[32 empty] | 8762 | PHARRSUB | SOUTH
[32 empty] | 8763 | BURNSSUB | SOUTH
[32 empty] | 8764 | ERIOHOND | SOUTH
[32 empty] | 8765 | HEIDLBRG | SOUTH
[32 empty] | 8766 | CNTRLAVE | SOUTH
[32 empty] | 8767 | HIWAY511 | SOUTH
[32 empty] | 8768 | WESLACOS | SOUTH
[32 empty] | 8769 | VALVERDE | SOUTH
[32 empty] | 8771 | WEDINBUR | SOUTH
[32 empty] | 8772 | ALTONSUB | SOUTH
[32 empty] | 8773 | KEYSS4 | SOUTH
[32 empty] | 8774 | PALMHURS | SOUTH
[32 empty] | 8778 | HILINESU | SOUTH
[32 empty] | 8779 | LSEBANOS | SOUTH
[32 empty] | 8782 | MVFAYSW | SOUTH
[32 empty] | 8783 | MCCOOKNO | SOUTH
[32 empty] | 8785 | MCCOOKNO | SOUTH
[32 empty] | 8786 | FAYSVILL | SOUTH
[32 empty] | 8789 | SOUTHMOS | SOUTH
[32 empty] | 8790 | RAYMONDV | SOUTH
[32 empty] | 8792 | SIOUXSUB | SOUTH
[32 empty] | 8793 | RIO_GRAN | SOUTH
[32 empty] | 8795 | ROMATP4 | SOUTH
[32 empty] | 8796 | ROMA 4 | SOUTH
[32 empty] | 8797 | RIO_GRAN | SOUTH
[32 empty] | 8798 | L_GRULLA | SOUTH
[32 empty] | 8799 | CONTINL2 | SOUTH
[32 empty] | 8800 | TATTON2A | SOUTH
[32 empty] | 8802 | HEARD T2 | SOUTH
[32 empty] | 8803 | HEARD 2 | SOUTH
[32 empty] | 8804 | WOODSBOR | SOUTH
[32 empty] | 8805 | BONIVIEW | SOUTH
[32 empty] | 8808 | HOMEPORT | SOUTH
[32 empty] | 8810 | ODEM2A | SOUTH
[32 empty] | 8812 | TAFT2A | SOUTH
[32 empty] | 8814 | MID_WAYT | SOUTH
[32 empty] | 8815 | MIDWPUMP | SOUTH
[32 empty] | 8817 | I_DUPP14 | SOUTH
[32 empty] | 8818 | OXY_INGL | SOUTH
[32 empty] | 8819 | I_DUPP14 | SOUTH
[32 empty] | 8820 | OXY_INGL | SOUTH
[32 empty] | 8821 | SLUTALR4 | SOUTH
[32 empty] | 8822 | SLUBENT4 | SOUTH
[32 empty] | 8824 | RAILROAD | SOUTH
[32 empty] | 8825 | SURRCFE4 | SOUTH
[32 empty] | 8832 | REYSHERW | SOUTH
[32 empty] | 8839 | FULTONCP | SOUTH
[32 empty] | 8841 | FULTONCP | SOUTH
[32 empty] | 8847 | MUSTANG2 | SOUTH
[32 empty] | 8856 | N_PADRE2 | SOUTH
[32 empty] | 8858 | MCKENZIE | SOUTH
[32 empty] | 8859 | VALERO_E | SOUTH
[32 empty] | 8860 | HEARN_RD | SOUTH
[32 empty] | 8862 | STEVENS2 | SOUTH
[32 empty] | 8864 | STEVENS2 | SOUTH
[32 empty] | 8865 | CAL_WWKS | SOUTH
[32 empty] | 8866 | SMITH2A | SOUTH
[32 empty] | 8867 | CUNINGWW | SOUTH
[32 empty] | 8868 | KARON T2 | SOUTH
[32 empty] | 8869 | KARON 2 | SOUTH
[32 empty] | 8870 | AVRYP2-2 | SOUTH
[32 empty] | 8871 | AVRYP1-2 | SOUTH
[32 empty] | 8878 | N_ELLA2A | SOUTH
[32 empty] | 8882 | CABANISS | SOUTH
[32 empty] | 8883 | RODD_FLD | SOUTH
[32 empty] | 8884 | RBSTN T2 | SOUTH
[32 empty] | 8885 | CTYOFRBS | SOUTH
[32 empty] | 8886 | ROB_CPL2 | SOUTH
[32 empty] | 8887 | LOYOLA44 | SOUTH
[32 empty] | 8888 | BANQUETE | SOUTH
[32 empty] | 8889 | STADIUM2 | SOUTH
[32 empty] | 8890 | SAN_DIEG | SOUTH
[32 empty] | 8891 | GOVTWELL | SOUTH
[32 empty] | 8894 | PREMONT2 | SOUTH
[32 empty] | 8896 | RACHAL4A | SOUTH
[32 empty] | 8899 | ARMSTRON | SOUTH
[32 empty] | 8901 | LHEDM | SOUTH
[32 empty] | 8902 | LHRHL | SOUTH
[32 empty] | 8903 | LHRHM | SOUTH
[32 empty] | 8904 | CHAS_TAP | SOUTH
[32 empty] | 8905 | LHEDL | SOUTH
[32 empty] | 8906 | ALAMO | SOUTH
[32 empty] | 8907 | WRBRTN4 | SOUTH
[32 empty] | 8908 | MCCOLL 4 | SOUTH
[32 empty] | 8909 | NLARSWW4 | SOUTH
[32 empty] | 8911 | BLKBYU4A | SOUTH
[32 empty] | 8912 | MEDIOCR4 | SOUTH
[32 empty] | 8914 | COFEPRT4 | SOUTH
[32 empty] | 8917 | SUNCHSE4 | SOUTH
[32 empty] | 8918 | MILO4A | SOUTH
[32 empty] | 8923 | GARCEN 4 | SOUTH
[32 empty] | 8924 | B_GRAVEL | SOUTH
[32 empty] | 8925 | LGE4A | SOUTH
[32 empty] | 8926 | LGE_GT10 | SOUTH
[32 empty] | 8927 | LGE_GT20 | SOUTH
[32 empty] | 8928 | LGE_STG0 | SOUTH
[32 empty] | 8930 | ICPGN10A | SOUTH
[32 empty] | 8931 | ICPGN20A | SOUTH
[32 empty] | 8932 | ICPGN30A | SOUTH
[32 empty] | 8933 | FGNTS001 | SOUTH
[32 empty] | 8934 | FGNTS101 | SOUTH
[32 empty] | 8935 | FGNTS201 | SOUTH
[32 empty] | 8936 | MVGN#1 | SOUTH
[32 empty] | 8937 | MVGN#2 | SOUTH
[32 empty] | 8938 | MVGN#3 | SOUTH
[32 empty] | 8949 | STEWART2 | SOUTH
[32 empty] | 8950 | OLMITO4 | SOUTH
[32 empty] | 8951 | STEWART4 | SOUTH
[32 empty] | 8956 | WHITEPT | SOUTH
[32 empty] | 8957 | MECLOPN4 | SOUTH
[32 empty] | 8958 | MECBRUTP | SOUTH
[32 empty] | 8959 | AIR_LIQC | SOUTH
[32 empty] | 8960 | WHITEPT2 | SOUTH
[32 empty] | 8961 | WHITEPT4 | SOUTH
[32 empty] | 8963 | HEC 4 | SOUTH
[32 empty] | 8968 | INGLCOSW | SOUTH
[32 empty] | 8969 | MVGN#1 | SOUTH
[32 empty] | 8970 | MVGN#2 | SOUTH
[32 empty] | 8971 | MVGN#3 | SOUTH
[32 empty] | 8978 | AIR_LIQS | SOUTH
[32 empty] | 8979 | AIR_LIQI | SOUTH
[32 empty] | 8980 | FRONT | SOUTH
[32 empty] | 8981 | HECN1 | SOUTH
[32 empty] | 8982 | HECN2 | SOUTH
[32 empty] | 8983 | HECN3 | SOUTH
[32 empty] | 8984 | MARKHMTP | SOUTH
[32 empty] | 8985 | S_YGANCI | SOUTH
[32 empty] | 8997 | FRTTS001 | SOUTH
[32 empty] | 8998 | FRTTS101 | SOUTH
[32 empty] | 8999 | FRTTS201 | SOUTH
[32 empty] | 9000 | DECKR_G1 | SOUTH
[32 empty] | 9001 | DECKR_G2 | SOUTH
[32 empty] | 9002 | DECKR_G3 | SOUTH
[32 empty] | 9003 | DECKR_G4 | SOUTH
[32 empty] | 9004 | DECKR_G5 | SOUTH
[32 empty] | 9005 | DECKR_G6 | SOUTH
[32 empty] | 9016 | SANDH_G1 | SOUTH
[32 empty] | 9017 | SANDH_G2 | SOUTH
[32 empty] | 9018 | SANDH_G3 | SOUTH
[32 empty] | 9019 | SANDH_G4 | SOUTH
[32 empty] | 9020 | SANDHG5A | SOUTH
[32 empty] | 9021 | SANDHG5C | SOUTH
[32 empty] | 9025 | HP_STATC | SOUTH
[32 empty] | 9040 | AUSTROP | SOUTH
[32 empty] | 9041 | LOSTPN34 | SOUTH
[32 empty] | 9071 | GARFIELD | SOUTH
[32 empty] | 9073 | HOLMAN | SOUTH
[32 empty] | 9074 | LYTTON34 | SOUTH
[32 empty] | 9075 | LYTTON13 | SOUTH
[32 empty] | 9076 | MCNEILW | SOUTH
[32 empty] | 9077 | MCNEILS | SOUTH
[32 empty] | 9079 | MCNEILN | SOUTH
[32 empty] | 9080 | MCNEIL | SOUTH
[32 empty] | 9118 | PE_MB2 | SOUTH
[32 empty] | 9119 | PE_MB1 | SOUTH
[32 empty] | 9120 | BURLES13 | SOUTH
[32 empty] | 9121 | BURLES69 | SOUTH
[32 empty] | 9122 | KINGSMB1 | SOUTH
[32 empty] | 9123 | KINGSDB | SOUTH
[32 empty] | 9125 | KINGSBRY | SOUTH
[32 empty] | 9128 | NORTHL13 | SOUTH
[32 empty] | 9129 | NORTHL69 | SOUTH
[32 empty] | 9130 | NL_TERTY | SOUTH
[32 empty] | 9131 | NORTHSTR | SOUTH
[32 empty] | 9132 | SEAHM8 | SOUTH
[32 empty] | 9139 | AUSTNDAM | SOUTH
[32 empty] | 9147 | HICRSMB2 | SOUTH
[32 empty] | 9148 | HICRSMB1 | SOUTH
[32 empty] | 9151 | AMD | SOUTH
[32 empty] | 9155 | ANGUSVAL | SOUTH
[32 empty] | 9158 | BARTON | SOUTH
[32 empty] | 9160 | BEECREEK | SOUTH
[32 empty] | 9163 | BERGSTRM | SOUTH
[32 empty] | 9164 | METCENTR | SOUTH
[32 empty] | 9166 | BRACK | SOUTH
[32 empty] | 9169 | BRODIE | SOUTH
[32 empty] | 9171 | CAMERON | SOUTH
[32 empty] | 9175 | CARSON | SOUTH
[32 empty] | 9179 | CARDINAL | SOUTH
[32 empty] | 9183 | COMMONFD | SOUTH
[32 empty] | 9184 | DAFFIN_G | SOUTH
[32 empty] | 9187 | DECK_MB1 | SOUTH
[32 empty] | 9188 | DECK_MB3 | SOUTH
[32 empty] | 9190 | TECHRIDG | SOUTH
[32 empty] | 9193 | DESSAU | SOUTH
[32 empty] | 9196 | ED_BLUE | SOUTH
[32 empty] | 9199 | FISKVILL | SOUTH
[32 empty] | 9200 | GROVE | SOUTH
[32 empty] | 9202 | HAMILMB2 | SOUTH
[32 empty] | 9203 | HAMILMB1 | SOUTH
[32 empty] | 9204 | HARRIS | SOUTH
[32 empty] | 9207 | HIDDENVL | SOUTH
[32 empty] | 9212 | HOLLYMB1 | SOUTH
[32 empty] | 9213 | HOLLYMB2 | SOUTH
[32 empty] | 9214 | HOLLYMB3 | SOUTH
[32 empty] | 9215 | HOLLYMB4 | SOUTH
[32 empty] | 9216 | SANDHSYD | SOUTH
[32 empty] | 9217 | HOWARDLN | SOUTH
[32 empty] | 9220 | JETT | SOUTH
[32 empty] | 9223 | JOLLYVIL | SOUTH
[32 empty] | 9225 | JUSTINLN | SOUTH
[32 empty] | 9227 | KOENIG | SOUTH
[32 empty] | 9228 | LAKESHOR | SOUTH
[32 empty] | 9235 | LAKEWAY | SOUTH
[32 empty] | 9238 | MAGPLANT | SOUTH
[32 empty] | 9244 | FIESTA | SOUTH
[32 empty] | 9245 | NORTHWES | SOUTH
[32 empty] | 9247 | OAKHILL | SOUTH
[32 empty] | 9251 | ONION_CK | SOUTH
[32 empty] | 9253 | PATTONLN | SOUTH
[32 empty] | 9257 | PEDERNAL | SOUTH
[32 empty] | 9259 | PILOT_KB | SOUTH
[32 empty] | 9260 | RIVERPLS | SOUTH
[32 empty] | 9263 | SALEMWLK | SOUTH
[32 empty] | 9267 | SLAUGHTR | SOUTH
[32 empty] | 9269 | CENTAUS | SOUTH
[32 empty] | 9271 | SPRINKLE | SOUTH
[32 empty] | 9275 | STECK | SOUTH
[32 empty] | 9279 | SUMMITN | SOUTH
[32 empty] | 9280 | SUMMITS | SOUTH
[32 empty] | 9282 | TRADPOST | SOUTH
[32 empty] | 9283 | UTBALC | SOUTH
[32 empty] | 9284 | WALNUTCK | SOUTH
[32 empty] | 9285 | VEGA | SOUTH
[32 empty] | 9286 | WARREN | SOUTH
[32 empty] | 9288 | WELLSBR | SOUTH
[32 empty] | 9291 | WHELESS | SOUTH
[32 empty] | 9295 | WILIAMSN | SOUTH
[32 empty] | 9400 | ACKEYLYN | WEST
[32 empty] | 9402 | ARVANA_8 | WEST
[32 empty] | 9404 | GAILPT_8 | WEST
[32 empty] | 9406 | KEYSW_8 | WEST
[32 empty] | 9408 | NORTLAME | WEST
[32 empty] | 9410 | PUNKING_ | WEST
[32 empty] | 9412 | SLAMESA_ | WEST
[32 empty] | 9414 | WELCH_9 | WEST
[32 empty] | 9416 | WLAMESA_ | WEST
[32 empty] | 9451 | NOLANW_9 | WEST
[32 empty] | 9453 | SWEETH20 | WEST
[32 empty] | 9471 | SOHERMIG | WEST
[32 empty] | 9491 | GOLDSCG_ | WEST
[32 empty] | 11001 | NAV1CT | WEST
[32 empty] | 11002 | NAV1CSTR | WEST
[32 empty] | 11009 | NAV2CT | WEST
[32 empty] | 11011 | NAV3ST | WEST
[32 empty] | 11012 | NAV4CT | WEST
[32 empty] | 11013 | NAV5CT | WEST
[32 empty] | 11014 | NAV6ST | WEST
[32 empty] | 11016 | QUAILSW_ | WEST
[32 empty] | 11017 | NAVTAP_5 | WEST
[32 empty] | 11020 | TIEHVSG_ | WEST
[32 empty] | 11021 | TIEHVCG_ | WEST
[32 empty] | 11022 | TIEHVCG_ | WEST
[32 empty] | 11023 | TIEHVCG_ | WEST
[32 empty] | 11024 | TIEHVCG_ | WEST
[32 empty] | 11025 | TIEHVSG_ | WEST
[32 empty] | 11056 | ROSCOE_1 | WEST
[32 empty] | 11057 | CHAMPION | WEST
[32 empty] | 11058 | PYRON_1G | WEST
[32 empty] | 11059 | INADALE_ | WEST
[32 empty] | 11146 | NOTREES2 | WEST
[32 empty] | 11147 | NOTREES_ | WEST
[32 empty] | 11309 | BULLCREK | WEST
[32 empty] | 11310 | BULLCREK | WEST
[32 empty] | 11311 | BULLCREK | WEST
[32 empty] | 11312 | BULLCREK | WEST
[32 empty] | 11313 | BULLCREK | WEST
[32 empty] | 11320 | COYOTE_1 | WEST
[32 empty] | 11321 | COYOTE_8 | WEST
[32 empty] | 11690 | KIOWA_5 | NORTH
[32 empty] | 11691 | KMICHICT | NORTH
[32 empty] | 11692 | KMICHICT | NORTH
[32 empty] | 11693 | KMICHIST | NORTH
[32 empty] | 11694 | KMICHICT | NORTH
[32 empty] | 11695 | KMICHICT | NORTH
[32 empty] | 11696 | KMICHIST | NORTH
[32 empty] | 11697 | KIOWAPP_ | NORTH
[32 empty] | 12021 | GV_360_1 | NORTH
[32 empty] | 12022 | GV_360_2 | NORTH
[32 empty] | 12026 | CLYVIL1_ | NORTH
[32 empty] | 12028 | CLYVIL2_ | NORTH
[32 empty] | 12033 | HRTAG1_T | NORTH
[32 empty] | 12034 | HRTAG2_T | NORTH
[32 empty] | 12036 | KEL_MAG2 | NORTH
[32 empty] | 12051 | BD_WDSN1 | NORTH
[32 empty] | 12052 | BD_WDSN2 | NORTH
[32 empty] | 12065 | EGLMTLAK | NORTH
[32 empty] | 12094 | GEN_DYN2 | NORTH
[32 empty] | 12313 | ASHGRVE_ | NORTH
[32 empty] | 12322 | ENNSTRAC | NORTH
[32 empty] | 12323 | ENNSTRAC | NORTH
[32 empty] | 12410 | FPLEFRB1 | NORTH
[32 empty] | 12411 | FPLEFR1A | NORTH
[32 empty] | 12412 | FPLEFR1B | NORTH
[32 empty] | 12413 | FPLEFR1C | NORTH
[32 empty] | 12414 | FPLEFR1S | NORTH
[32 empty] | 12420 | FPLEFRB2 | NORTH
[32 empty] | 12421 | FPLEFR2A | NORTH
[32 empty] | 12422 | FPLEFR2B | NORTH
[32 empty] | 12423 | FPLEFR2C | NORTH
[32 empty] | 12424 | FPLEFR2S | NORTH
[32 empty] | 12425 | DESPKV2_ | NORTH
[32 empty] | 12441 | PARKD_1E | NORTH
[32 empty] | 12442 | PARKD_2E | NORTH
[32 empty] | 12443 | PARKD_3E | NORTH
[32 empty] | 12672 | TWINSTAR | NORTH
[32 empty] | 13116 | TGATEWAY | NORTH
[32 empty] | 13117 | TGATEWAY | NORTH
[32 empty] | 13118 | TGATEWAY | NORTH
[32 empty] | 13119 | TGATEWAY | NORTH
[32 empty] | 13131 | CALFREST | NORTH
[32 empty] | 13132 | CALFREST | NORTH
[32 empty] | 13133 | CALFREST | NORTH
[32 empty] | 13134 | CALFREST | NORTH
[32 empty] | 13135 | CALFREST | NORTH
[32 empty] | 13136 | CALFREST | NORTH
[32 empty] | 13426 | KILELMR1 | SOUTH
[32 empty] | 13429 | SAND_TXU | SOUTH
[32 empty] | 13430 | SAND_TXU | SOUTH
[32 empty] | 13431 | SANDTXUP | SOUTH
[32 empty] | 13432 | SANDOW_5 | SOUTH
[32 empty] | 13434 | SAND_TXU | SOUTH
[32 empty] | 13591 | COTTONW_ | NORTH
[32 empty] | 13610 | BELTONSW | SOUTH
[32 empty] | 13620 | KILCLARR | SOUTH
[32 empty] | 13662 | TEMPELMC | SOUTH
[32 empty] | 13681 | REED_M1_ | NORTH
[32 empty] | 32000 | CSST | NORTH
[32 empty] | 32001 | CSPT | NORTH
[32 empty] | 32002 | CSSV | NORTH
[32 empty] | 32003 | CSGP | NORTH
[32 empty] | 32004 | CSSC | NORTH
[32 empty] | 32005 | DOWLNGRD | NORTH
[32 empty] | 32798 | BRYN_TAM | NORTH
[32 empty] | 32799 | BRYN_TAM | NORTH
[32 empty] | 32858 | BRYN_BCR | NORTH
[32 empty] | 32859 | BRYN_JK_ | NORTH
[32 empty] | 32862 | BRYN_ATK | NORTH
[32 empty] | 32864 | BRYN_ATK | NORTH
[32 empty] | 32865 | BRYN_SNO | NORTH
[32 empty] | 32866 | BRYN_STE | NORTH
[32 empty] | 32867 | BRYN_ATK | NORTH
[32 empty] | 32868 | BRYN_ANN | NORTH
[32 empty] | 32869 | BRYN_NOR | NORTH
[32 empty] | 32870 | BRYN_TAB | NORTH
[32 empty] | 32871 | BRYN_BUS | NORTH
[32 empty] | 32872 | BRYN_NAL | NORTH
[32 empty] | 32873 | BRYN_SHA | NORTH
[32 empty] | 32874 | BRYN_EAS | NORTH
[32 empty] | 32875 | BRYN_DSB | NORTH
[32 empty] | 32876 | BRYN_IP | NORTH
[32 empty] | 32877 | BRYN_BRC | NORTH
[32 empty] | 32878 | BRYN_GRN | NORTH
[32 empty] | 32879 | BRYN_STP | NORTH
[32 empty] | 32880 | BRYN_SOU | NORTH
[32 empty] | 32881 | BRYN_KUR | NORTH
[32 empty] | 32882 | BRYN_TAB | NORTH
[32 empty] | 32883 | BRYN_DNS | NORTH
[32 empty] | 32884 | BRYN_DNS | NORTH
[32 empty] | 32885 | BRYN_GRP | NORTH
[32 empty] | 32886 | BRYN_ATK | NORTH
[32 empty] | 32887 | BRYN_ATK | NORTH
[32 empty] | 32888 | BRYN_ATK | NORTH
[32 empty] | 32889 | BRYN_MIL | NORTH
[32 empty] | 32890 | BRYN_ATK | NORTH
[32 empty] | 32891 | BRYN_ATK | NORTH
[32 empty] | 32892 | BRYN_DNS | NORTH
[32 empty] | 32893 | BRYN_SWT | NORTH
[32 empty] | 32894 | BRYN_BOW | NORTH
[32 empty] | 32896 | BRYN_EAS | NORTH
[32 empty] | 32897 | BRYN_DSB | NORTH
[32 empty] | 36998 | RDCNYNG1 | WEST
[32 empty] | 36999 | RDCANYON | WEST
[32 empty] | 37010 | TNLAKEPN | NORTH
[32 empty] | 37011 | TNBIOENR | NORTH
[32 empty] | 37030 | TNJONES_ | NORTH
[32 empty] | 37050 | TNHIGHLA | NORTH
[32 empty] | 37060 | TNLWVLWE | NORTH
[32 empty] | 37080 | TNLWVLTI | NORTH
[32 empty] | 37100 | TNLWVLST | NORTH
[32 empty] | 37120 | TNKRUGRV | NORTH
[32 empty] | 37140 | TNBELLS_ | NORTH
[32 empty] | 37160 | TNWHITEW | NORTH
[32 empty] | 37180 | TNFRNTRT | NORTH
[32 empty] | 37190 | TNFRONTI | NORTH
[32 empty] | 37200 | TNTRENTO | NORTH
[32 empty] | 37220 | TNLEONAR | NORTH
[32 empty] | 37240 | TNBLUERD | NORTH
[32 empty] | 37250 | TNLONGNE | NORTH
[32 empty] | 37260 | TNCLIMAX | NORTH
[32 empty] | 37280 | TNCLIMAX | NORTH
[32 empty] | 37290 | TNFRMRSV | NORTH
[32 empty] | 37300 | TNEMORY_ | NORTH
[32 empty] | 37320 | TNTALCOW | NORTH
[32 empty] | 37340 | TNDEPORT | NORTH
[32 empty] | 37350 | TNRED_RI | NORTH
[32 empty] | 37360 | TNLONE_O | NORTH
[32 empty] | 37370 | TNSAINT_ | NORTH
[32 empty] | 37380 | TNNOCONA | NORTH
[32 empty] | 37390 | TNPETROL | NORTH
[32 empty] | 37410 | TNLKWHIT | NORTH
[32 empty] | 37420 | TNLKWHIT | NORTH
[32 empty] | 37440 | TNWHITNE | NORTH
[32 empty] | 37460 | TNOLSEN_ | NORTH
[32 empty] | 37470 | TNOLSEN_ | NORTH
[32 empty] | 37490 | TNHNDLYT | NORTH
[32 empty] | 37500 | TNHANDLE | NORTH
[32 empty] | 37510 | TNVLLYMI | NORTH
[32 empty] | 37520 | TNSYCAMO | NORTH
[32 empty] | 37530 | TNCORYEL | NORTH
[32 empty] | 37550 | TNGATESV | NORTH
[32 empty] | 37570 | TNGATESV | NORTH
[32 empty] | 37590 | TNJNESBO | NORTH
[32 empty] | 37600 | TNCLIFTO | NORTH
[32 empty] | 37620 | TNCLFTNT | NORTH
[32 empty] | 37630 | TNCLIFTO | NORTH
[32 empty] | 37650 | TNMERDNT | NORTH
[32 empty] | 37660 | TNMERIDI | NORTH
[32 empty] | 37680 | TNWALNTS | NORTH
[32 empty] | 37700 | TNGLENRO | NORTH
[32 empty] | 37705 | TNSQUAW_ | NORTH
[32 empty] | 37710 | TNTOLAR_ | NORTH
[32 empty] | 37740 | TNHICOTA | NORTH
[32 empty] | 37750 | TNHICO__ | NORTH
[32 empty] | 37770 | TNHAMLTN | NORTH
[32 empty] | 37790 | TNHAMILT | NORTH
[32 empty] | 37810 | TNHILL_C | NORTH
[32 empty] | 37830 | TNOLNEY_ | NORTH
[32 empty] | 37850 | TNTHURBE | NORTH
[32 empty] | 37860 | TNSTHBEN | NORTH
[32 empty] | 37870 | TNGRAHAM | NORTH
[32 empty] | 37890 | TNBRYSON | NORTH
[32 empty] | 37900 | TNWINK__ | WEST
[32 empty] | 37920 | TNWINK__ | WEST
[32 empty] | 37940 | TNCALIFR | WEST
[32 empty] | 37960 | TNWNKLRC | WEST
[32 empty] | 37980 | TNWICKET | WEST
[32 empty] | 38000 | TNPYOTE_ | WEST
[32 empty] | 38020 | TNWORSHA | WEST
[32 empty] | 38040 | TNIH20__ | WEST
[32 empty] | 38050 | TNSTAFBL | WEST
[32 empty] | 38070 | TNFLATTO | WEST
[32 empty] | 38090 | TNPECOS_ | WEST
[32 empty] | 38120 | TNREEVSC | WEST
[32 empty] | 38140 | TNTOYAH_ | WEST
[32 empty] | 38160 | TNCOCHIS | WEST
[32 empty] | 38180 | TNLONEST | WEST
[32 empty] | 38200 | TNLONEST | WEST
[32 empty] | 38230 | TNAAPIPE | WEST
[32 empty] | 38250 | TNKERMIT | WEST
[32 empty] | 38280 | TNKERMIT | WEST
[32 empty] | 38290 | TNKEYSTO | WEST
[32 empty] | 38310 | TN16TH_S | WEST
[32 empty] | 38320 | TN16TH_S | WEST
[32 empty] | 38330 | TNWDWRDT | WEST
[32 empty] | 38331 | TNWDWRD4 | WEST
[32 empty] | 38332 | TNWDWRDU | WEST
[32 empty] | 38340 | TNAIRPOR | WEST
[32 empty] | 38350 | TNFTSTKT | WEST
[32 empty] | 38360 | TNFTSTCK | WEST
[32 empty] | 38365 | TNPINON_ | WEST
[32 empty] | 38370 | TNHACKBE | WEST
[32 empty] | 38375 | TNCTYRD1 | WEST
[32 empty] | 38380 | TNPUCKTT | WEST
[32 empty] | 38390 | TNARMDLO | WEST
[32 empty] | 38400 | TNSANDRS | WEST
[32 empty] | 38420 | TNWHITEB | WEST
[32 empty] | 38430 | TNWHITEB | WEST
[32 empty] | 38435 | TNSRBNME | WEST
[32 empty] | 38437 | TNSRBNME | WEST
[32 empty] | 38440 | TNNRTHNN | WEST
[32 empty] | 38460 | TNPUCKTF | WEST
[32 empty] | 38470 | TNGOMEZ_ | WEST
[32 empty] | 38490 | TNBELDIN | WEST
[32 empty] | 38500 | TNISP___ | HOUSTON
[32 empty] | 38530 | TNTEJAS_ | HOUSTON
[32 empty] | 38560 | TNCOMANC | HOUSTON
[32 empty] | 38570 | TNBP____ | HOUSTON
[32 empty] | 38575 | TNGRENBE | HOUSTON
[32 empty] | 38580 | TNBP_CGN | HOUSTON
[32 empty] | 38590 | TNBP_CGN | HOUSTON
[32 empty] | 38600 | TNBP_CGN | HOUSTON
[32 empty] | 38611 | TNBPAMCG | HOUSTON
[32 empty] | 38612 | TNBPAMCG | HOUSTON
[32 empty] | 38613 | TNBPAMCG | HOUSTON
[32 empty] | 38614 | TNBPAMCG | HOUSTON
[32 empty] | 38615 | TNBPAMCG | HOUSTON
[32 empty] | 38620 | TNAMOCO_ | HOUSTON
[32 empty] | 38650 | TNAMOCO_ | HOUSTON
[32 empty] | 38660 | TNBAYVIE | HOUSTON
[32 empty] | 38690 | TNBP_CGN | HOUSTON
[32 empty] | 38710 | TNCADDO_ | HOUSTON
[32 empty] | 38711 | TNTXCTY1 | HOUSTON
[32 empty] | 38712 | TNTXCTY2 | HOUSTON
[32 empty] | 38713 | TNTXCTY3 | HOUSTON
[32 empty] | 38714 | TNTXCTY4 | HOUSTON
[32 empty] | 38715 | TNCGNR__ | HOUSTON
[32 empty] | 38720 | TNAPACHE | HOUSTON
[32 empty] | 38730 | TNDOW_CO | HOUSTON
[32 empty] | 38740 | TNHEIGHT | HOUSTON
[32 empty] | 38770 | TNHEIGHT | HOUSTON
[32 empty] | 38820 | TNFRWYPA | HOUSTON
[32 empty] | 38850 | TNDICKNS | HOUSTON
[32 empty] | 38890 | TNSOUSHO | HOUSTON
[32 empty] | 38900 | TNNDICKN | HOUSTON
[32 empty] | 38920 | TNLEAGCI | HOUSTON
[32 empty] | 38950 | TNMAGNOL | HOUSTON
[32 empty] | 38980 | TNFRDSWO | HOUSTON
[32 empty] | 38990 | TNSEMINO | HOUSTON
[32 empty] | 39010 | TNHASTIN | HOUSTON
[32 empty] | 39015 | TNALVINT | HOUSTON
[32 empty] | 39030 | TNALVIN_ | HOUSTON
[32 empty] | 39040 | TNMAINLA | HOUSTON
[32 empty] | 39070 | TNTERMIN | HOUSTON
[32 empty] | 39075 | TNCHEROK | HOUSTON
[32 empty] | 39090 | TNMARTHN | HOUSTON
[32 empty] | 39095 | TNCHOCTA | HOUSTON
[32 empty] | 39096 | TNCHOCTA | HOUSTON
[32 empty] | 39110 | TNVALERO | HOUSTON
[32 empty] | 39140 | TNTXCITY | HOUSTON
[32 empty] | 39180 | TNSLCOGE | HOUSTON
[32 empty] | 39190 | TNSLCGN1 | HOUSTON
[32 empty] | 39200 | TNSTRLNG | HOUSTON
[32 empty] | 39220 | TNNTHSDT | HOUSTON
[32 empty] | 39250 | TNNORTHS | HOUSTON
[32 empty] | 39280 | TNTXCITY | HOUSTON
[32 empty] | 39310 | TNINTRCI | HOUSTON
[32 empty] | 39340 | TNLAMARQ | HOUSTON
[32 empty] | 39345 | TNPRXAIR | HOUSTON
[32 empty] | 39346 | TNPRXAIR | HOUSTON
[32 empty] | 39360 | TNCARBID | HOUSTON
[32 empty] | 39380 | TNLINDE_ | HOUSTON
[32 empty] | 39400 | TNGRANTA | HOUSTON
[32 empty] | 39410 | TNARCOPL | HOUSTON
[32 empty] | 39430 | TNLIQDCA | HOUSTON
[32 empty] | 39431 | TNTEPPCO | HOUSTON
[32 empty] | 39440 | TNMARTHN | HOUSTON
[32 empty] | 39470 | TNDOWCGN | HOUSTON
[32 empty] | 39480 | TNDOWCGN | HOUSTON
[32 empty] | 39500 | TNWCOLMA | HOUSTON
[32 empty] | 39530 | TNWCOLLO | HOUSTON
[32 empty] | 39560 | TNANGLET | HOUSTON
[32 empty] | 39600 | TNBRAZOR | HOUSTON
[32 empty] | 39630 | TNBRAZOR | HOUSTON
[32 empty] | 39650 | TNDOW_PU | HOUSTON
[32 empty] | 39670 | TNCLMNST | HOUSTON
[32 empty] | 39680 | TNCLEMEN | HOUSTON
[32 empty] | 39700 | TNSWEENY | HOUSTON
[32 empty] | 39720 | TNP662__ | HOUSTON
[32 empty] | 39730 | TNP663__ | HOUSTON
[32 empty] | 39750 | TNOLDOCE | HOUSTON
[32 empty] | 39760 | TNSCLP1_ | HOUSTON
[32 empty] | 39770 | TNSCLP2_ | HOUSTON
[32 empty] | 39775 | TNSCLP4_ | HOUSTON
[32 empty] | 39790 | TNSCLP3_ | HOUSTON
[32 empty] | 39810 | TNHILCOR | HOUSTON
[32 empty] | 39860 | TNSCLPCO | HOUSTON
[32 empty] | 39870 | TNPHILLP | HOUSTON
[32 empty] | 39880 | TNSCLPCO | HOUSTON
[32 empty] | 39890 | TNPHILLP | HOUSTON
[32 empty] | 39910 | TNPHILLP | HOUSTON
[32 empty] | 39930 | TNPHLLPS | HOUSTON
[32 empty] | 39940 | TNPHLLPS | HOUSTON
[32 empty] | 39950 | TNTNP_ON | NORTH
[32 empty] | 39960 | TNTNPONE | NORTH
[32 empty] | 39970 | TNTNPONE | NORTH
[32 empty] | 40000 | CEDARP__ | HOUSTON
[32 empty] | 40010 | CEDARP__ | HOUSTON
[32 empty] | 40011 | CEDAR03_ | HOUSTON
[32 empty] | 40012 | CEDAR84_ | HOUSTON
[32 empty] | 40015 | CEDARP__ | HOUSTON
[32 empty] | 40051 | AGRI____ | HOUSTON
[32 empty] | 40070 | AIRPRO__ | HOUSTON
[32 empty] | 40081 | ALEX_I55 | HOUSTON
[32 empty] | 40082 | ALEX_I16 | HOUSTON
[32 empty] | 40100 | ANBUSH__ | HOUSTON
[32 empty] | 40110 | APLIED__ | HOUSTON
[32 empty] | 40111 | OPNAPD__ | HOUSTON
[32 empty] | 40120 | ARITEK__ | HOUSTON
[32 empty] | 40130 | ATASCO__ | HOUSTON
[32 empty] | 40140 | BARBUR__ | HOUSTON
[32 empty] | 40150 | BARHIL__ | HOUSTON
[32 empty] | 40155 | BENDER_8 | HOUSTON
[32 empty] | 40160 | BTNENY__ | HOUSTON
[32 empty] | 40170 | BAYTWN__ | HOUSTON
[32 empty] | 40171 | BAYTWN88 | HOUSTON
[32 empty] | 40172 | BAYTWN66 | HOUSTON
[32 empty] | 40180 | BERTWD__ | HOUSTON
[32 empty] | 40190 | BIGVUE__ | HOUSTON
[32 empty] | 40200 | BIMONT__ | HOUSTON
[32 empty] | 40210 | BORDEN__ | HOUSTON
[32 empty] | 40220 | BRINE___ | HOUSTON
[32 empty] | 40231 | BUSCH10_ | HOUSTON
[32 empty] | 40232 | BUSCH38_ | HOUSTON
[32 empty] | 40240 | CENTER__ | HOUSTON
[32 empty] | 40250 | CASTEN__ | HOUSTON
[32 empty] | 40255 | CHAMBR__ | HOUSTON
[32 empty] | 40260 | CHAMON__ | HOUSTON
[32 empty] | 40270 | CHANEL__ | HOUSTON
[32 empty] | 40280 | CHANLV__ | HOUSTON
[32 empty] | 40281 | CHANLV__ | HOUSTON
[32 empty] | 40282 | CCHANLV_ | HOUSTON
[32 empty] | 40300 | CHEV____ | HOUSTON
[32 empty] | 40310 | CHOATE | HOUSTON
[32 empty] | 40320 | CHORIN__ | HOUSTON
[32 empty] | 40330 | CITFIL__ | HOUSTON
[32 empty] | 40340 | CITIES__ | HOUSTON
[32 empty] | 40351 | CLINTN__ | HOUSTON
[32 empty] | 40352 | CLINTN__ | HOUSTON
[32 empty] | 40370 | CONIAL__ | HOUSTON
[32 empty] | 40380 | CROSBY__ | HOUSTON
[32 empty] | 40390 | CROSBY__ | HOUSTON
[32 empty] | 40391 | CCROSBY_ | HOUSTON
[32 empty] | 40392 | SVC_CROS | HOUSTON
[32 empty] | 40400 | CROWN___ | HOUSTON
[32 empty] | 40420 | DAVSON__ | HOUSTON
[32 empty] | 40425 | OPNDAY__ | HOUSTON
[32 empty] | 40430 | DECKER__ | HOUSTON
[32 empty] | 40431 | CAPEMUT1 | HOUSTON
[32 empty] | 40441 | DEERPK21 | HOUSTON
[32 empty] | 40442 | DEERPK96 | HOUSTON
[32 empty] | 40450 | DEPWTR__ | HOUSTON
[32 empty] | 40460 | DEPWTR__ | HOUSTON
[32 empty] | 40470 | DEPWTR__ | HOUSTON
[32 empty] | 40475 | DEUSEN__ | HOUSTON
[32 empty] | 40480 | DS_BAT__ | HOUSTON
[32 empty] | 40490 | DOWLAP__ | HOUSTON
[32 empty] | 40500 | EAGLE___ | HOUSTON
[32 empty] | 40510 | ENPROD__ | HOUSTON
[32 empty] | 40520 | EPOTH___ | HOUSTON
[32 empty] | 40530 | ESBELT__ | HOUSTON
[32 empty] | 40540 | ESFORK__ | HOUSTON
[32 empty] | 40550 | ETHYL___ | HOUSTON
[32 empty] | 40551 | ET_CLR1 | HOUSTON
[32 empty] | 40552 | ET_CLR2 | HOUSTON
[32 empty] | 40560 | EXPLOR__ | HOUSTON
[32 empty] | 40570 | EXXON___ | HOUSTON
[32 empty] | 40571 | EXXONSTR | HOUSTON
[32 empty] | 40572 | EXXONSTR | HOUSTON
[32 empty] | 40573 | EXXONSTR | HOUSTON
[32 empty] | 40575 | EXXON | HOUSTON
[32 empty] | 40580 | CAPEMUT5 | HOUSTON
[32 empty] | 40590 | FDLITY__ | HOUSTON
[32 empty] | 40600 | ROANS___ | NORTH
[32 empty] | 40610 | GALENA__ | HOUSTON
[32 empty] | 40611 | GALENA__ | HOUSTON
[32 empty] | 40612 | GALENA__ | HOUSTON
[32 empty] | 40620 | GLENWD__ | HOUSTON
[32 empty] | 40650 | GDYEAR__ | HOUSTON
[32 empty] | 40700 | GRNBYU__ | HOUSTON
[32 empty] | 40710 | GRNBYU__ | HOUSTON
[32 empty] | 40715 | GRNBYU__ | HOUSTON
[32 empty] | 40716 | GRNBYU__ | HOUSTON
[32 empty] | 40717 | CGRNBYU_ | HOUSTON
[32 empty] | 40720 | GRNBYU__ | HOUSTON
[32 empty] | 40725 | GRNBYU__ | HOUSTON
[32 empty] | 40751 | GYPSUM__ | HOUSTON
[32 empty] | 40752 | GYPSUM | HOUSTON
[32 empty] | 40770 | HACHER__ | HOUSTON
[32 empty] | 40780 | HADEN___ | HOUSTON
[32 empty] | 40790 | HANEY___ | HOUSTON
[32 empty] | 40800 | HARRIS__ | HOUSTON
[32 empty] | 40811 | HILAND08 | HOUSTON
[32 empty] | 40812 | HILAND43 | HOUSTON
[32 empty] | 40830 | HUMBLE__ | HOUSTON
[32 empty] | 40831 | CHUMBLE_ | HOUSTON
[32 empty] | 40841 | INDUST84 | HOUSTON
[32 empty] | 40842 | INDUST38 | HOUSTON
[32 empty] | 40860 | JACNTO__ | HOUSTON
[32 empty] | 40870 | KENNY14_ | HOUSTON
[32 empty] | 40871 | KENNY03_ | HOUSTON
[32 empty] | 40900 | KING____ | HOUSTON
[32 empty] | 40911 | KING_T3_ | HOUSTON
[32 empty] | 40912 | KING_T4_ | HOUSTON
[32 empty] | 40930 | KINGWD__ | HOUSTON
[32 empty] | 40941 | LAPORT96 | HOUSTON
[32 empty] | 40942 | LAPORT79 | HOUSTON
[32 empty] | 40961 | LIBRTY03 | HOUSTON
[32 empty] | 40962 | LIBRTY21 | HOUSTON
[32 empty] | 40980 | LUBZOL__ | HOUSTON
[32 empty] | 40990 | LYCHEM__ | HOUSTON
[32 empty] | 41000 | LYDELL__ | HOUSTON
[32 empty] | 41010 | LYNCH___ | HOUSTON
[32 empty] | 41021 | LYONDL03 | HOUSTON
[32 empty] | 41022 | LYONDL08 | HOUSTON
[32 empty] | 41040 | MCDONO__ | HOUSTON
[32 empty] | 41050 | METALS__ | HOUSTON
[32 empty] | 41061 | MINING__ | HOUSTON
[32 empty] | 41080 | MOCHEM__ | HOUSTON
[32 empty] | 41090 | MOMENT__ | HOUSTON
[32 empty] | 41100 | MORGPT__ | HOUSTON
[32 empty] | 41111 | MT_BEL__ | HOUSTON
[32 empty] | 41112 | MT_BEL__ | HOUSTON
[32 empty] | 41150 | NEWPRT__ | HOUSTON
[32 empty] | 41160 | NINTH___ | HOUSTON
[32 empty] | 41165 | NOBEL___ | HOUSTON
[32 empty] | 41171 | NORMDY77 | HOUSTON
[32 empty] | 41172 | NORMDY94 | HOUSTON
[32 empty] | 41191 | OATES08_ | HOUSTON
[32 empty] | 41192 | OATES38_ | HOUSTON
[32 empty] | 41205 | ORION___ | HOUSTON
[32 empty] | 41210 | PAIR____ | HOUSTON
[32 empty] | 41221 | PARKWY95 | HOUSTON
[32 empty] | 41222 | PARKWY94 | HOUSTON
[32 empty] | 41240 | JEFFER__ | HOUSTON
[32 empty] | 41250 | PHILIP__ | HOUSTON
[32 empty] | 41260 | PORT____ | HOUSTON
[32 empty] | 41300 | PSARCO__ | HOUSTON
[32 empty] | 41310 | QUANAB__ | HOUSTON
[32 empty] | 41330 | QUANUM__ | HOUSTON
[32 empty] | 41340 | REED____ | HOUSTON
[32 empty] | 41350 | ROHMAS__ | HOUSTON
[32 empty] | 41360 | ROLLEN__ | HOUSTON
[32 empty] | 41370 | S_CHAN__ | HOUSTON
[32 empty] | 41371 | CS_CHAN_ | HOUSTON
[32 empty] | 41380 | S_CHAN__ | HOUSTON
[32 empty] | 41383 | CAPEMUT6 | HOUSTON
[32 empty] | 41400 | S_R_B___ | HOUSTON
[32 empty] | 41405 | S_R_B___ | HOUSTON
[32 empty] | 41410 | S_R_B___ | HOUSTON
[32 empty] | 41415 | S_R_B___ | HOUSTON
[32 empty] | 41420 | S_R_B___ | HOUSTON
[32 empty] | 41430 | SHELDN__ | HOUSTON
[32 empty] | 41450 | SHELL___ | HOUSTON
[32 empty] | 41480 | SOLMER__ | HOUSTON
[32 empty] | 41490 | STATE___ | HOUSTON
[32 empty] | 41500 | STRANG__ | HOUSTON
[32 empty] | 41510 | STRAW___ | HOUSTON
[32 empty] | 41520 | SYLVAN__ | HOUSTON
[32 empty] | 41530 | TAYLOR__ | HOUSTON
[32 empty] | 41550 | TEXAS___ | HOUSTON
[32 empty] | 41560 | TXPET___ | HOUSTON
[32 empty] | 41570 | TEXWAL__ | HOUSTON
[32 empty] | 41580 | TIDAL___ | HOUSTON
[32 empty] | 41590 | TRAVIS__ | HOUSTON
[32 empty] | 41600 | TRIBAY__ | HOUSTON
[32 empty] | 41610 | TRINTY__ | HOUSTON
[32 empty] | 41615 | CAPEMUT2 | HOUSTON
[32 empty] | 41620 | TUCKER__ | HOUSTON
[32 empty] | 41631 | UNDRWD06 | HOUSTON
[32 empty] | 41632 | UNDRWD21 | HOUSTON
[32 empty] | 41651 | UVALDE08 | HOUSTON
[32 empty] | 41652 | UVALDE03 | HOUSTON
[32 empty] | 41670 | WABURN__ | HOUSTON
[32 empty] | 41681 | WALSVL61 | HOUSTON
[32 empty] | 41682 | WALSVL10 | HOUSTON
[32 empty] | 41700 | WARVUE__ | HOUSTON
[32 empty] | 41711 | WITTER94 | HOUSTON
[32 empty] | 41712 | WITTER21 | HOUSTON
[32 empty] | 42000 | P_H_R___ | HOUSTON
[32 empty] | 42010 | P_H_R___ | HOUSTON
[32 empty] | 42011 | CP_H_R__ | HOUSTON
[32 empty] | 42013 | P_H_R79_ | HOUSTON
[32 empty] | 42014 | P_H_R96_ | HOUSTON
[32 empty] | 42015 | P_H_R___ | HOUSTON
[32 empty] | 42020 | P_H_R___ | HOUSTON
[32 empty] | 42041 | ALMEDA26 | HOUSTON
[32 empty] | 42042 | ALMEDA07 | HOUSTON
[32 empty] | 42061 | ALTA_L93 | HOUSTON
[32 empty] | 42062 | ALTA_L53 | HOUSTON
[32 empty] | 42080 | ALVIN___ | HOUSTON
[32 empty] | 42090 | AMOCO___ | HOUSTON
[32 empty] | 42110 | ANGLTN__ | HOUSTON
[32 empty] | 42120 | ARMAND__ | HOUSTON
[32 empty] | 42130 | AVAUTO__ | HOUSTON
[32 empty] | 42150 | BASF____ | HOUSTON
[32 empty] | 42160 | BAYOU___ | HOUSTON
[32 empty] | 42170 | BAYWAY__ | HOUSTON
[32 empty] | 42180 | BIGBAY__ | HOUSTON
[32 empty] | 42190 | BIPORT__ | HOUSTON
[32 empty] | 42195 | BOOSTR__ | HOUSTON
[32 empty] | 42200 | BRYAN___ | HOUSTON
[32 empty] | 42210 | BRZPRT__ | HOUSTON
[32 empty] | 42220 | BYPARK__ | HOUSTON
[32 empty] | 42230 | CAPTOL__ | HOUSTON
[32 empty] | 42241 | CARDIF84 | HOUSTON
[32 empty] | 42242 | CARDIF95 | HOUSTON
[32 empty] | 42260 | CELNEC__ | HOUSTON
[32 empty] | 42271 | CHOC_B26 | HOUSTON
[32 empty] | 42272 | CHOC_B07 | HOUSTON
[32 empty] | 42291 | CLEAR95_ | HOUSTON
[32 empty] | 42292 | CLEAR35_ | HOUSTON
[32 empty] | 42311 | COLEGE94 | HOUSTON
[32 empty] | 42312 | COLEGE06 | HOUSTON
[32 empty] | 42330 | CW_COL__ | HOUSTON
[32 empty] | 42340 | DAMON___ | HOUSTON
[32 empty] | 42500 | DOW_____ | HOUSTON
[32 empty] | 42501 | DOW__STR | HOUSTON
[32 empty] | 42502 | DOW__STR | HOUSTON
[32 empty] | 42510 | DOW_____ | HOUSTON
[32 empty] | 42515 | DOW_____ | HOUSTON
[32 empty] | 42550 | DROUET__ | HOUSTON
[32 empty] | 42551 | DROUET_T | HOUSTON
[32 empty] | 42561 | ELDORA91 | HOUSTON
[32 empty] | 42562 | ELDORA92 | HOUSTON
[32 empty] | 42581 | ELLING07 | HOUSTON
[32 empty] | 42582 | ELLING91 | HOUSTON
[32 empty] | 42600 | EXTER___ | HOUSTON
[32 empty] | 42610 | FAIRMT__ | HOUSTON
[32 empty] | 42611 | FAIRMT95 | HOUSTON
[32 empty] | 42612 | FAIRMT00 | HOUSTON
[32 empty] | 42640 | FREEPT__ | HOUSTON
[32 empty] | 42651 | FRIEND05 | HOUSTON
[32 empty] | 42652 | FRIEND04 | HOUSTON
[32 empty] | 42670 | GALVES__ | HOUSTON
[32 empty] | 42680 | GARDEN__ | HOUSTON
[32 empty] | 42690 | GARDEN__ | HOUSTON
[32 empty] | 42700 | CGARDEN_ | HOUSTON
[32 empty] | 42711 | GENOA95_ | HOUSTON
[32 empty] | 42712 | GENOA35_ | HOUSTON
[32 empty] | 42741 | GULFGT91 | HOUSTON
[32 empty] | 42742 | GULFGT06 | HOUSTON
[32 empty] | 42761 | HALL_06_ | HOUSTON
[32 empty] | 42762 | HALL_91_ | HOUSTON
[32 empty] | 42780 | HANNA___ | HOUSTON
[32 empty] | 42790 | HIMONT__ | HOUSTON
[32 empty] | 42800 | HITCOK__ | HOUSTON
[32 empty] | 42810 | HOFMAN__ | HOUSTON
[32 empty] | 42820 | HASTNG__ | HOUSTON
[32 empty] | 42830 | HUNTER__ | HOUSTON
[32 empty] | 42841 | KEMAH95_ | HOUSTON
[32 empty] | 42842 | KEMAH92_ | HOUSTON
[32 empty] | 42860 | LAMARQ__ | HOUSTON
[32 empty] | 42861 | LAMARQ__ | HOUSTON
[32 empty] | 42862 | CAPEMUT3 | HOUSTON
[32 empty] | 42870 | LIVRPL__ | HOUSTON
[32 empty] | 42880 | LKJACK__ | HOUSTON
[32 empty] | 42890 | LOMAX___ | HOUSTON
[32 empty] | 42900 | LUZBAY__ | HOUSTON
[32 empty] | 42910 | LYNPOL__ | HOUSTON
[32 empty] | 42921 | MARYCK06 | HOUSTON
[32 empty] | 42922 | MARYCK91 | HOUSTON
[32 empty] | 42940 | MONSAN__ | HOUSTON
[32 empty] | 42945 | MONSAN | HOUSTON
[32 empty] | 42950 | MOODY63_ | HOUSTON
[32 empty] | 42951 | TERM_A__ | HOUSTON
[32 empty] | 42952 | OPN_T_A_ | HOUSTON
[32 empty] | 42953 | TERM_B__ | HOUSTON
[32 empty] | 42955 | TRMNAL__ | HOUSTON
[32 empty] | 42960 | MUSTNG__ | HOUSTON
[32 empty] | 42970 | NASA____ | HOUSTON
[32 empty] | 42981 | NASH_02_ | HOUSTON
[32 empty] | 42982 | NASH_45_ | HOUSTON
[32 empty] | 42985 | DYANN | HOUSTON
[32 empty] | 43000 | NEEDVL__ | HOUSTON
[32 empty] | 43011 | NEWGLF04 | HOUSTON
[32 empty] | 43012 | NEWGLF60 | HOUSTON
[32 empty] | 43035 | OASIS___ | HOUSTON
[32 empty] | 43040 | PASDNA__ | HOUSTON
[32 empty] | 43051 | PEARLD06 | HOUSTON
[32 empty] | 43052 | PEARLD91 | HOUSTON
[32 empty] | 43070 | PETSON__ | HOUSTON
[32 empty] | 43081 | PILGRM06 | HOUSTON
[32 empty] | 43082 | PILGRM07 | HOUSTON
[32 empty] | 43101 | PLARIS95 | HOUSTON
[32 empty] | 43102 | PLARIS35 | HOUSTON
[32 empty] | 43120 | PLEDGR__ | HOUSTON
[32 empty] | 43130 | POWELL__ | HOUSTON
[32 empty] | 43135 | QNTANA | HOUSTON
[32 empty] | 43140 | RETREV__ | HOUSTON
[32 empty] | 43150 | RIWOOD__ | HOUSTON
[32 empty] | 43170 | S_HOUS__ | HOUSTON
[32 empty] | 43171 | S_HOUS31 | HOUSTON
[32 empty] | 43172 | S_HOUS13 | HOUSTON
[32 empty] | 43173 | S_HOUS12 | HOUSTON
[32 empty] | 43174 | S_HOUS21 | HOUSTON
[32 empty] | 43190 | S_LANE__ | HOUSTON
[32 empty] | 43201 | SEAWAL01 | HOUSTON
[32 empty] | 43202 | SEAWAL63 | HOUSTON
[32 empty] | 43220 | SEAWAY__ | HOUSTON
[32 empty] | 43225 | SEPTON__ | HOUSTON
[32 empty] | 43230 | SHORE___ | HOUSTON
[32 empty] | 43240 | SINTEK__ | HOUSTON
[32 empty] | 43250 | SOUTH___ | HOUSTON
[32 empty] | 43260 | SOWYCK__ | HOUSTON
[32 empty] | 43271 | SPENCR06 | HOUSTON
[32 empty] | 43272 | SPENCR92 | HOUSTON
[32 empty] | 43290 | STEWRT__ | HOUSTON
[32 empty] | 43300 | STRATT__ | HOUSTON
[32 empty] | 43310 | SURFSI__ | HOUSTON
[32 empty] | 43321 | TELPHN06 | HOUSTON
[32 empty] | 43322 | TELPHN91 | HOUSTON
[32 empty] | 43330 | CAVERN__ | HOUSTON
[32 empty] | 43340 | TXGLF___ | HOUSTON
[32 empty] | 43350 | TEXWES__ | HOUSTON
[32 empty] | 43355 | TIKIS___ | HOUSTON
[32 empty] | 43356 | CAPEMUT4 | HOUSTON
[32 empty] | 43360 | VLASCO__ | HOUSTON
[32 empty] | 43370 | VLASCO__ | HOUSTON
[32 empty] | 43380 | W_COL___ | HOUSTON
[32 empty] | 43390 | W_COL___ | HOUSTON
[32 empty] | 43400 | W_GALV__ | HOUSTON
[32 empty] | 43401 | TEMP_BYP | HOUSTON
[32 empty] | 43403 | WEST_G_M | HOUSTON
[32 empty] | 43500 | WEBSTR__ | HOUSTON
[32 empty] | 43501 | WEBSTR93 | HOUSTON
[32 empty] | 43502 | WEBSTTR2 | HOUSTON
[32 empty] | 43503 | WEBSTR35 | HOUSTON
[32 empty] | 43504 | WEBSTR92 | HOUSTON
[32 empty] | 43507 | CWEBSTR_ | HOUSTON
[32 empty] | 43510 | WEBSTR__ | HOUSTON
[32 empty] | 43520 | WESTBY_5 | HOUSTON
[32 empty] | 43521 | WESTBY_4 | HOUSTON
[32 empty] | 43570 | WHARTN__ | HOUSTON
[32 empty] | 44000 | W_A_P___ | HOUSTON
[32 empty] | 44010 | W_A_P___ | HOUSTON
[32 empty] | 44020 | ALIEF___ | HOUSTON
[32 empty] | 44031 | ARCOLA80 | HOUSTON
[32 empty] | 44032 | ARCOLA82 | HOUSTON
[32 empty] | 44051 | BARKER78 | HOUSTON
[32 empty] | 44052 | BARKER73 | HOUSTON
[32 empty] | 44070 | BG_CRK__ | HOUSTON
[32 empty] | 44081 | BLURIG05 | HOUSTON
[32 empty] | 44082 | BLURIG02 | HOUSTON
[32 empty] | 44100 | BRAZOS__ | HOUSTON
[32 empty] | 44110 | BRISCO__ | HOUSTON
[32 empty] | 44120 | BRITMR__ | HOUSTON
[32 empty] | 44130 | CANEY___ | HOUSTON
[32 empty] | 44131 | CANEY___ | HOUSTON
[32 empty] | 44140 | CLODIN__ | HOUSTON
[32 empty] | 44150 | CCLODIN_ | HOUSTON
[32 empty] | 44160 | COLLIN__ | HOUSTON
[32 empty] | 44170 | CRABB___ | HOUSTON
[32 empty] | 44180 | DEWALT__ | HOUSTON
[32 empty] | 44190 | E_BERN__ | HOUSTON
[32 empty] | 44200 | HILLJE | HOUSTON
[32 empty] | 44210 | ECHO_73_ | HOUSTON
[32 empty] | 44211 | ECHO_13_ | HOUSTON
[32 empty] | 44212 | ECHO_31_ | HOUSTON
[32 empty] | 44213 | ECHO_14_ | HOUSTON
[32 empty] | 44214 | ECHO_41_ | HOUSTON
[32 empty] | 44215 | ECHO_81_ | HOUSTON
[32 empty] | 44230 | FLEWLN__ | HOUSTON
[32 empty] | 44231 | CFLEWLN_ | HOUSTON
[32 empty] | 44240 | FLEWLN__ | HOUSTON
[32 empty] | 44250 | FOSTER__ | HOUSTON
[32 empty] | 44261 | FRANZ09_ | HOUSTON
[32 empty] | 44262 | FRANZ66_ | HOUSTON
[32 empty] | 44280 | FTBEND__ | HOUSTON
[32 empty] | 44290 | FTBEND__ | HOUSTON
[32 empty] | 44300 | CFTBEND_ | HOUSTON
[32 empty] | 44310 | HAYES___ | HOUSTON
[32 empty] | 44311 | HAYES24_ | HOUSTON
[32 empty] | 44312 | HAYES09_ | HOUSTON
[32 empty] | 44341 | IMPERL80 | HOUSTON
[32 empty] | 44342 | IMPERL05 | HOUSTON
[32 empty] | 44361 | INTERM05 | HOUSTON
[32 empty] | 44362 | INTERM26 | HOUSTON
[32 empty] | 44380 | JULIFF__ | HOUSTON
[32 empty] | 44390 | KARSTN__ | HOUSTON
[32 empty] | 44400 | KARSTN__ | HOUSTON
[32 empty] | 44410 | CKARSTN_ | HOUSTON
[32 empty] | 44421 | KATY_09_ | HOUSTON
[32 empty] | 44422 | KATY_66_ | HOUSTON
[32 empty] | 44440 | MANVEL__ | HOUSTON
[32 empty] | 44450 | MASON___ | HOUSTON
[32 empty] | 44461 | MEMORL81 | HOUSTON
[32 empty] | 44462 | MEMORL73 | HOUSTON
[32 empty] | 44481 | MOCITY__ | HOUSTON
[32 empty] | 44482 | MOCITY__ | HOUSTON
[32 empty] | 44490 | MULA____ | HOUSTON
[32 empty] | 44500 | OBRIEN__ | HOUSTON
[32 empty] | 44510 | OBRIEN__ | HOUSTON
[32 empty] | 44511 | OBRIEN25 | HOUSTON
[32 empty] | 44512 | OBRIEN73 | HOUSTON
[32 empty] | 44540 | ORCHRD__ | HOUSTON
[32 empty] | 44551 | QUAIL02_ | HOUSTON
[32 empty] | 44552 | QUAIL26_ | HOUSTON
[32 empty] | 44570 | READNG__ | HOUSTON
[32 empty] | 44580 | RICHMN__ | HOUSTON
[32 empty] | 44590 | ROARK___ | HOUSTON
[32 empty] | 44600 | ROSHRN__ | HOUSTON
[32 empty] | 44610 | ROSNBG__ | HOUSTON
[32 empty] | 44620 | SAUER81_ | HOUSTON
[32 empty] | 44621 | SAUER14_ | HOUSTON
[32 empty] | 44622 | SAUER41_ | HOUSTON
[32 empty] | 44623 | SAUER23_ | HOUSTON
[32 empty] | 44624 | SAUER32_ | HOUSTON
[32 empty] | 44625 | SAUER73_ | HOUSTON
[32 empty] | 44626 | SAUDP81 | HOUSTON
[32 empty] | 44627 | SAUDP73 | HOUSTON
[32 empty] | 44640 | SEALY___ | HOUSTON
[32 empty] | 44645 | SNGLTN_3 | HOUSTON
[32 empty] | 44650 | SMTHRS__ | HOUSTON
[32 empty] | 44651 | SIENNA02 | HOUSTON
[32 empty] | 44652 | SIENNA05 | HOUSTON
[32 empty] | 44656 | SLRDP81 | HOUSTON
[32 empty] | 44657 | SLRDP73 | HOUSTON
[32 empty] | 44671 | STAFRD09 | HOUSTON
[32 empty] | 44672 | STAFRD05 | HOUSTON
[32 empty] | 44691 | TELVEW02 | HOUSTON
[32 empty] | 44692 | TELVEW26 | HOUSTON
[32 empty] | 44710 | TXINS___ | HOUSTON
[32 empty] | 44721 | THOMSN80 | HOUSTON
[32 empty] | 44722 | THOMSN82 | HOUSTON
[32 empty] | 44740 | WALLIS__ | HOUSTON
[32 empty] | 44760 | WCHASE__ | HOUSTON
[32 empty] | 44761 | WCHASE05 | HOUSTON
[32 empty] | 44762 | WCHASE24 | HOUSTON
[32 empty] | 44780 | WESTIM__ | HOUSTON
[32 empty] | 44790 | WIRT_73_ | HOUSTON
[32 empty] | 44791 | WIRT_13_ | HOUSTON
[32 empty] | 44792 | WIRT_31_ | HOUSTON
[32 empty] | 44793 | WIRT_23_ | HOUSTON
[32 empty] | 44794 | WIRT_32_ | HOUSTON
[32 empty] | 44795 | WIRT_81_ | HOUSTON
[32 empty] | 44801 | WOODCK81 | HOUSTON
[32 empty] | 44802 | WOODCK73 | HOUSTON
[32 empty] | 45500 | T_H_W___ | HOUSTON
[32 empty] | 45510 | T_H_W___ | HOUSTON
[32 empty] | 45511 | T_H_W81_ | HOUSTON
[32 empty] | 45512 | T_H_W95_ | HOUSTON
[32 empty] | 45515 | T_H_W___ | HOUSTON
[32 empty] | 45520 | T_H_W___ | HOUSTON
[32 empty] | 45530 | T_H_W___ | HOUSTON
[32 empty] | 45600 | ADICKS__ | HOUSTON
[32 empty] | 45610 | ADICKS__ | HOUSTON
[32 empty] | 45611 | ADICKS__ | HOUSTON
[32 empty] | 45620 | CADICKS_ | HOUSTON
[32 empty] | 45630 | AIRLIN__ | HOUSTON
[32 empty] | 45640 | ALDINE__ | HOUSTON
[32 empty] | 45651 | BAMMEL__ | HOUSTON
[32 empty] | 45670 | BERRY___ | HOUSTON
[32 empty] | 45681 | CAMBEL09 | HOUSTON
[32 empty] | 45682 | CAMBEL21 | HOUSTON
[32 empty] | 45700 | CAMRON__ | HOUSTON
[32 empty] | 45711 | CYFAIR21 | HOUSTON
[32 empty] | 45712 | CYFAIR76 | HOUSTON
[32 empty] | 45730 | DEIHL___ | HOUSTON
[32 empty] | 45740 | DRILCO__ | HOUSTON
[32 empty] | 45750 | EUREKA__ | HOUSTON
[32 empty] | 45760 | FAIRBK__ | HOUSTON
[32 empty] | 45770 | FREMAN__ | HOUSTON
[32 empty] | 45781 | GEARS67_ | HOUSTON
[32 empty] | 45782 | GEARS95_ | HOUSTON
[32 empty] | 45801 | GERTIE21 | HOUSTON
[32 empty] | 45802 | GERTIE76 | HOUSTON
[32 empty] | 45821 | GREENS86 | HOUSTON
[32 empty] | 45822 | GREENS90 | HOUSTON
[32 empty] | 45840 | HARDY___ | HOUSTON
[32 empty] | 45850 | C_HARDY_ | HOUSTON
[32 empty] | 45861 | HIDDEN67 | HOUSTON
[32 empty] | 45862 | HIDDEN95 | HOUSTON
[32 empty] | 45880 | HOCKLY__ | HOUSTON
[32 empty] | 45885 | CHOCKLY_ | HOUSTON
[32 empty] | 45890 | HOCKLY__ | HOUSTON
[32 empty] | 45900 | INTEQ___ | HOUSTON
[32 empty] | 45910 | INTER___ | HOUSTON
[32 empty] | 45921 | JESTER67 | HOUSTON
[32 empty] | 45922 | JESTER81 | HOUSTON
[32 empty] | 45940 | KLEIN___ | HOUSTON
[32 empty] | 45952 | KLUGE___ | HOUSTON
[32 empty] | 45953 | CKLUGE__ | HOUSTON
[32 empty] | 45971 | KUYDAL74 | HOUSTON
[32 empty] | 45972 | KUYDAL75 | HOUSTON
[32 empty] | 45990 | L_YORK__ | HOUSTON
[32 empty] | 46001 | LAUDER90 | HOUSTON
[32 empty] | 46002 | LAUDER95 | HOUSTON
[32 empty] | 46020 | LIMEST__ | NORTH
[32 empty] | 46031 | LOCKWD90 | HOUSTON
[32 empty] | 46032 | LOCKWD86 | HOUSTON
[32 empty] | 46051 | LOUETA66 | HOUSTON
[32 empty] | 46052 | LOUETA81 | HOUSTON
[32 empty] | 46100 | N_BELT__ | HOUSTON
[32 empty] | 46110 | N_BELT__ | HOUSTON
[32 empty] | 46111 | CN_BEL95 | HOUSTON
[32 empty] | 46112 | CN_BEL90 | HOUSTON
[32 empty] | 46220 | PETERS__ | HOUSTON
[32 empty] | 46230 | PETERS__ | HOUSTON
[32 empty] | 46240 | PINHUR__ | HOUSTON
[32 empty] | 46250 | RACOON__ | HOUSTON
[32 empty] | 46261 | RAYFRD66 | HOUSTON
[32 empty] | 46262 | RAYFRD81 | HOUSTON
[32 empty] | 46281 | RITTEN86 | HOUSTON
[32 empty] | 46282 | RITTEN95 | HOUSTON
[32 empty] | 46300 | SATSUM__ | HOUSTON
[32 empty] | 46301 | SATSUM24 | HOUSTON
[32 empty] | 46302 | SATSUM76 | HOUSTON
[32 empty] | 46331 | SCENIC86 | HOUSTON
[32 empty] | 46332 | SCENIC90 | HOUSTON
[32 empty] | 46351 | TODD_21_ | HOUSTON
[32 empty] | 46352 | TODD_09_ | HOUSTON
[32 empty] | 46500 | TOMBAL__ | HOUSTON
[32 empty] | 46510 | TOMBAL__ | HOUSTON
[32 empty] | 46511 | TOMBAL66 | HOUSTON
[32 empty] | 46512 | TOMBAL81 | HOUSTON
[32 empty] | 46520 | CTOMBAL_ | HOUSTON
[32 empty] | 46550 | TRSWIG__ | HOUSTON
[32 empty] | 46551 | VETRAN67 | HOUSTON
[32 empty] | 46552 | VETRAN81 | HOUSTON
[32 empty] | 46560 | WALLER__ | HOUSTON
[32 empty] | 46570 | WESFLD__ | HOUSTON
[32 empty] | 46571 | CWESFLD_ | HOUSTON
[32 empty] | 46600 | WHITOK__ | HOUSTON
[32 empty] | 46610 | WHITOK__ | HOUSTON
[32 empty] | 46611 | WHITOK73 | HOUSTON
[32 empty] | 46612 | WHITOK09 | HOUSTON
[32 empty] | 46615 | WHITOK__ | HOUSTON
[32 empty] | 46616 | CWHITOK_ | HOUSTON
[32 empty] | 46620 | WHITOK__ | HOUSTON
[32 empty] | 46660 | WILLOW__ | HOUSTON
[32 empty] | 47000 | BELAIR__ | HOUSTON
[32 empty] | 47010 | BELAIR__ | HOUSTON
[32 empty] | 47011 | BELAIR35 | HOUSTON
[32 empty] | 47012 | BELAIR24 | HOUSTON
[32 empty] | 47013 | CBELAIR_ | HOUSTON
[32 empty] | 47015 | BELAIR__ | HOUSTON
[32 empty] | 47016 | SVC_BELA | HOUSTON
[32 empty] | 47050 | BRAYS___ | HOUSTON
[32 empty] | 47071 | DUNVAL05 | HOUSTON
[32 empty] | 47072 | DUNVAL24 | HOUSTON
[32 empty] | 47090 | FANNIN__ | HOUSTON
[32 empty] | 47100 | FONDRN__ | HOUSTON
[32 empty] | 47110 | GRANT___ | HOUSTON
[32 empty] | 47150 | H_O_C___ | HOUSTON
[32 empty] | 47155 | CH_O_C__ | HOUSTON
[32 empty] | 47160 | H_O_C___ | HOUSTON
[32 empty] | 47165 | H_O_C___ | HOUSTON
[32 empty] | 47170 | CH_O_C__ | HOUSTON
[32 empty] | 47191 | HILCRF24 | HOUSTON
[32 empty] | 47192 | HILCRF05 | HOUSTON
[32 empty] | 47210 | HOLMES__ | HOUSTON
[32 empty] | 47300 | JENETA__ | HOUSTON
[32 empty] | 47310 | JENETA__ | HOUSTON
[32 empty] | 47320 | KIRBY___ | HOUSTON
[32 empty] | 47331 | KNIGHT08 | HOUSTON
[32 empty] | 47332 | KNIGHT06 | HOUSTON
[32 empty] | 47350 | PLAZA___ | HOUSTON
[32 empty] | 47380 | SANFLP__ | HOUSTON
[32 empty] | 47381 | SANFLP36 | HOUSTON
[32 empty] | 47382 | SANFLP78 | HOUSTON
[32 empty] | 47383 | SANFLP87 | HOUSTON
[32 empty] | 47384 | SANFLP63 | HOUSTON
[32 empty] | 47411 | SHARPS05 | HOUSTON
[32 empty] | 47412 | SHARPS25 | HOUSTON
[32 empty] | 47420 | STADIM__ | HOUSTON
[32 empty] | 47430 | TECO____ | HOUSTON
[32 empty] | 47441 | ULRICH35 | HOUSTON
[32 empty] | 47442 | ULRICH24 | HOUSTON
[32 empty] | 47461 | WESTWD3_ | HOUSTON
[32 empty] | 47462 | WESTWD2_ | HOUSTON
[32 empty] | 47500 | DWNTWN__ | HOUSTON
[32 empty] | 47510 | DWNTWN__ | HOUSTON
[32 empty] | 47521 | BLOGET37 | HOUSTON
[32 empty] | 47522 | BLOGET46 | HOUSTON
[32 empty] | 47540 | BRING___ | HOUSTON
[32 empty] | 47550 | BROWN___ | HOUSTON
[32 empty] | 47560 | COUGAR__ | HOUSTON
[32 empty] | 47570 | CRCKET__ | HOUSTON
[32 empty] | 47580 | DUNLVY__ | HOUSTON
[32 empty] | 47600 | E_SIDE__ | HOUSTON
[32 empty] | 47610 | CESTSIDE | HOUSTON
[32 empty] | 47620 | FRAKLN__ | HOUSTON
[32 empty] | 47630 | GABLE___ | HOUSTON
[32 empty] | 47640 | GABLE___ | HOUSTON
[32 empty] | 47660 | GARROT__ | HOUSTON
[32 empty] | 47670 | GENRAL__ | HOUSTON
[32 empty] | 47680 | HIGHTS__ | HOUSTON
[32 empty] | 47690 | HYDEPK__ | HOUSTON
[32 empty] | 47700 | MAG_PK__ | HOUSTON
[32 empty] | 47701 | MAG_PK__ | HOUSTON
[32 empty] | 47705 | MIDTWN__ | HOUSTON
[32 empty] | 47707 | MIDRCLS_ | HOUSTON
[32 empty] | 47711 | N_SIDE91 | HOUSTON
[32 empty] | 47712 | N_SIDE21 | HOUSTON
[32 empty] | 47730 | POLK____ | HOUSTON
[32 empty] | 47750 | UNIVER__ | HOUSTON
[32 empty] | 47751 | UNIVER__ | HOUSTON
[32 empty] | 47752 | UNIVER__ | HOUSTON
[32 empty] | 48500 | APD_GT1_ | HOUSTON
[32 empty] | 48510 | AK_GT1__ | HOUSTON
[32 empty] | 48511 | LPE_GT1_ | HOUSTON
[32 empty] | 48512 | LPE_GT2_ | HOUSTON
[32 empty] | 48513 | LPE_GT3_ | HOUSTON
[32 empty] | 48514 | LPE_GT4_ | HOUSTON
[32 empty] | 48520 | BSF_GT1_ | HOUSTON
[32 empty] | 48521 | BVE_GT1_ | HOUSTON
[32 empty] | 48522 | BVE_GT2_ | HOUSTON
[32 empty] | 48523 | BVE_ST1_ | HOUSTON
[32 empty] | 48531 | BYU_GT1_ | HOUSTON
[32 empty] | 48532 | BYU_GT2_ | HOUSTON
[32 empty] | 48533 | BYU_GT3_ | HOUSTON
[32 empty] | 48534 | BYU_GT4_ | HOUSTON
[32 empty] | 48551 | CAL_GT1_ | HOUSTON
[32 empty] | 48552 | CAL_ST1_ | HOUSTON
[32 empty] | 48561 | CTL_GT2_ | HOUSTON
[32 empty] | 48562 | CTL_GT3_ | HOUSTON
[32 empty] | 48563 | CTL_GT4_ | HOUSTON
[32 empty] | 48564 | CTL_GN1_ | HOUSTON
[32 empty] | 48565 | CTL_GN2_ | HOUSTON
[32 empty] | 48581 | CBY_GN1_ | HOUSTON
[32 empty] | 48582 | CBY_GN2_ | HOUSTON
[32 empty] | 48591 | CHE_GT2_ | HOUSTON
[32 empty] | 48593 | CHE_GT1_ | HOUSTON
[32 empty] | 48594 | CHE_GN4_ | HOUSTON
[32 empty] | 48595 | BTE_GT2_ | HOUSTON
[32 empty] | 48596 | BTE_GT3_ | HOUSTON
[32 empty] | 48597 | BTE_GT4_ | HOUSTON
[32 empty] | 48598 | BTE_ST1_ | HOUSTON
[32 empty] | 48611 | DIB_GT1_ | HOUSTON
[32 empty] | 48612 | DIB_GT2_ | HOUSTON
[32 empty] | 48613 | DIB_ST1_ | HOUSTON
[32 empty] | 48614 | DIB_GT3_ | HOUSTON
[32 empty] | 48641 | DPEC_GT1 | HOUSTON
[32 empty] | 48642 | DPEC_GT2 | HOUSTON
[32 empty] | 48643 | DPEC_GT3 | HOUSTON
[32 empty] | 48644 | DPEC_GT4 | HOUSTON
[32 empty] | 48645 | DPEC_ST5 | HOUSTON
[32 empty] | 48651 | EP_1_2 | HOUSTON
[32 empty] | 48671 | FTR_GT1_ | NORTH
[32 empty] | 48672 | FTR_GT2_ | NORTH
[32 empty] | 48673 | FTR_GT3_ | NORTH
[32 empty] | 48674 | FTR_CN4_ | NORTH
[32 empty] | 48690 | GBY_GN5_ | HOUSTON
[32 empty] | 48691 | GBY_7374 | HOUSTON
[32 empty] | 48692 | GBY_8182 | HOUSTON
[32 empty] | 48693 | GBY_8384 | HOUSTON
[32 empty] | 48721 | LEG_1___ | NORTH
[32 empty] | 48722 | LEG_2___ | NORTH
[32 empty] | 48730 | MNS_GT | HOUSTON
[32 empty] | 48731 | CBE_GT1 | HOUSTON
[32 empty] | 48732 | CBE_GT2 | HOUSTON
[32 empty] | 48733 | CBE_ST12 | HOUSTON
[32 empty] | 48734 | CBE_GT3 | HOUSTON
[32 empty] | 48735 | CBE_GT4 | HOUSTON
[32 empty] | 48736 | CBE_ST34 | HOUSTON
[32 empty] | 48740 | PSG_GN2_ | HOUSTON
[32 empty] | 48741 | PSG_GT2_ | HOUSTON
[32 empty] | 48742 | PSG_GT3_ | HOUSTON
[32 empty] | 48761 | PR_GT1__ | HOUSTON
[32 empty] | 48772 | PHR_GN2_ | HOUSTON
[32 empty] | 48791 | PSA_GT1_ | HOUSTON
[32 empty] | 48792 | PSA_GT2_ | HOUSTON
[32 empty] | 48793 | PSA_GT3_ | HOUSTON
[32 empty] | 48794 | PSA_GT4_ | HOUSTON
[32 empty] | 48795 | PSA_GT5_ | HOUSTON
[32 empty] | 48796 | PSA_GN1_ | HOUSTON
[32 empty] | 48797 | PSA_GT6_ | HOUSTON
[32 empty] | 48811 | CVC_GT3_ | HOUSTON
[32 empty] | 48812 | CVC_GT2_ | HOUSTON
[32 empty] | 48813 | CVC_GT1_ | HOUSTON
[32 empty] | 48814 | CVC_ST5_ | HOUSTON
[32 empty] | 48815 | CVC_GT4_ | HOUSTON
[32 empty] | 48816 | CVC_GSTR | HOUSTON
[32 empty] | 48820 | SHELLG1_ | HOUSTON
[32 empty] | 48821 | SHELLG2 | HOUSTON
[32 empty] | 48822 | SHELLG3_ | HOUSTON
[32 empty] | 48841 | SJS_GT1_ | HOUSTON
[32 empty] | 48842 | SJS_GT2_ | HOUSTON
[32 empty] | 48845 | SOL_GT1 | HOUSTON
[32 empty] | 48851 | SRB_GN1_ | HOUSTON
[32 empty] | 48852 | SRB_GN2_ | HOUSTON
[32 empty] | 48853 | SRB_GN3_ | HOUSTON
[32 empty] | 48854 | SRB_GN4_ | HOUSTON
[32 empty] | 48855 | SRB_GT21 | HOUSTON
[32 empty] | 48873 | THW_ST3_ | HOUSTON
[32 empty] | 48874 | THW_ST4_ | HOUSTON
[32 empty] | 48875 | THW_3132 | HOUSTON
[32 empty] | 48877 | THW_3334 | HOUSTON
[32 empty] | 48879 | THW_4142 | HOUSTON
[32 empty] | 48881 | THW_4344 | HOUSTON
[32 empty] | 48883 | THW_GT1_ | HOUSTON
[32 empty] | 48885 | THW_5152 | HOUSTON
[32 empty] | 48886 | THW_5354 | HOUSTON
[32 empty] | 48887 | THW_5556 | HOUSTON
[32 empty] | 48911 | TGF_GT1_ | HOUSTON
[32 empty] | 48921 | WAP_GN1_ | HOUSTON
[32 empty] | 48922 | WAP_GN2_ | HOUSTON
[32 empty] | 48923 | WAP_GN3_ | HOUSTON
[32 empty] | 48924 | WAP_GN4_ | HOUSTON
[32 empty] | 48925 | WAP_GN5_ | HOUSTON
[32 empty] | 48926 | WAP_GN6_ | HOUSTON
[32 empty] | 48927 | WAP_GN7_ | HOUSTON
[32 empty] | 48928 | WAP_GN8_ | HOUSTON
[32 empty] | 48929 | WAPGT21_ | HOUSTON
[32 empty] | 49801 | EXN_4 | HOUSTON
[32 empty] | 49802 | EXN_11 | HOUSTON
[32 empty] | 49803 | EXN_15GT | HOUSTON
[32 empty] | 49804 | EXN_16GT | HOUSTON
[32 empty] | 49805 | EXN_17GT | HOUSTON
[32 empty] | 49806 | EXN_21 | HOUSTON
[32 empty] | 49807 | EXN_121 | HOUSTON
[32 empty] | 49808 | EXN_129 | HOUSTON
[32 empty] | 49809 | EXN_R1 | HOUSTON
[32 empty] | 49810 | EXN_R2 | HOUSTON
[32 empty] | 49811 | EXN_399 | HOUSTON
[32 empty] | 49812 | EXN_411 | HOUSTON
[32 empty] | 49813 | EXN_440 | HOUSTON
[32 empty] | 49814 | EXN_441 | HOUSTON
[32 empty] | 49815 | EXN_460 | HOUSTON
[32 empty] | 49816 | EXN_461 | HOUSTON
[32 empty] | 49817 | EXN_470 | HOUSTON
[32 empty] | 49818 | EXN_471 | HOUSTON
[32 empty] | 49819 | EXN_660 | HOUSTON
[32 empty] | 49820 | EXN_661 | HOUSTON
[32 empty] | 49821 | EXN_698 | HOUSTON
[32 empty] | 49822 | EXN_930 | HOUSTON
[32 empty] | 49823 | EXN_931 | HOUSTON
[32 empty] | 49824 | EXN935GT | HOUSTON
[32 empty] | 49825 | EXN937GT | HOUSTON
[32 empty] | 49826 | EXN938GT | HOUSTON
[32 empty] | 49827 | EXN_940 | HOUSTON
[32 empty] | 49828 | EXN941GT | HOUSTON
[32 empty] | 49829 | EXN942GT | HOUSTON
[32 empty] | 49830 | EXN943GT | HOUSTON
[32 empty] | 49831 | EXN944GT | HOUSTON
[32 empty] | 49832 | EXN945GT | HOUSTON
[32 empty] | 49833 | EXN_946 | HOUSTON
[32 empty] | 49834 | EXN_947 | HOUSTON
[32 empty] | 49835 | EXN_948 | HOUSTON
[32 empty] | 49836 | EXN_949 | HOUSTON
[32 empty] | 49837 | EXN_GT | HOUSTON
[32 empty] | 49838 | EXN_14GT | HOUSTON
[32 empty] | 49839 | EXN_929 | HOUSTON
[32 empty] | 49851 | DOW17000 | HOUSTON
[32 empty] | 49852 | DOW17132 | HOUSTON
[32 empty] | 49853 | DOW20000 | HOUSTON
[32 empty] | 49854 | DOW20990 | HOUSTON
[32 empty] | 49855 | DOW21998 | HOUSTON
[32 empty] | 49856 | DOW29999 | HOUSTON
[32 empty] | 49857 | DOW38000 | HOUSTON
[32 empty] | 49858 | DOW38100 | HOUSTON
[32 empty] | 49859 | DOW38200 | HOUSTON
[32 empty] | 49860 | DOW38300 | HOUSTON
[32 empty] | 49861 | DOW39000 | HOUSTON
[32 empty] | 49862 | DOW39100 | HOUSTON
[32 empty] | 49863 | DOW39200 | HOUSTON
[32 empty] | 49864 | DOW40000 | HOUSTON
[32 empty] | 49865 | DOW41000 | HOUSTON
[32 empty] | 49866 | DOW42000 | HOUSTON
[32 empty] | 49867 | DOW44600 | HOUSTON
[32 empty] | 49868 | DOW45100 | HOUSTON
[32 empty] | 49869 | DOW49000 | HOUSTON
[32 empty] | 49870 | DOW61000 | HOUSTON
[32 empty] | 49871 | DOW62000 | HOUSTON
[32 empty] | 49872 | DOW63000 | HOUSTON
[32 empty] | 49873 | DOW64000 | HOUSTON
[32 empty] | 49874 | DOW64100 | HOUSTON
[32 empty] | 49875 | DOW64110 | HOUSTON
[32 empty] | 49876 | DOW65000 | HOUSTON
[32 empty] | 49877 | DOW66000 | HOUSTON
[32 empty] | 49878 | DOW67000 | HOUSTON
[32 empty] | 49879 | DOW68000 | HOUSTON
[32 empty] | 49880 | DOW69000 | HOUSTON
[32 empty] | 49881 | DOW69099 | HOUSTON
[32 empty] | 49882 | DOW81000 | HOUSTON
[32 empty] | 49883 | DOW81990 | HOUSTON
[32 empty] | 49884 | DOW82000 | HOUSTON
[32 empty] | 49885 | DOW83000 | HOUSTON
[32 empty] | 49886 | DOW84000 | HOUSTON
[32 empty] | 49887 | DOW89996 | HOUSTON
[32 empty] | 49984 | DOW_A3_T | HOUSTON
[32 empty] | 49985 | DOW_A4_T | HOUSTON
[32 empty] | 49986 | EXXON_T1 | HOUSTON
[32 empty] | 49987 | EXXON_T2 | HOUSTON
[32 empty] | 49998 | EXXON_T3 | HOUSTON
[32 empty] | 59300 | PWRPLANT | SOUTH
[32 empty] | 59400 | FM_802 | SOUTH
[32 empty] | 59410 | PRICE_RD | SOUTH
[32 empty] | 59420 | FILTER_P | SOUTH
[32 empty] | 59450 | WATERPRT | SOUTH
[32 empty] | 59460 | AIRPORT8 | SOUTH
[32 empty] | 59480 | SIXTH_ST | SOUTH
[32 empty] | 59490 | MIDTOWN | SOUTH
[32 empty] | 59500 | SOUTH_PL | SOUTH
[32 empty] | 60000 | DSKY2 | WEST
[32 empty] | 60001 | DSKY2_4 | WEST
[32 empty] | 60002 | KING_SW4 | WEST
[32 empty] | 60003 | KING_NE1 | WEST
[32 empty] | 60004 | KM NEP4 | WEST
[32 empty] | 60005 | KING_SE1 | WEST
[32 empty] | 60006 | KING_SE4 | WEST
[32 empty] | 60007 | KING_SW1 | WEST
[32 empty] | 60008 | KING_SW4 | WEST
[32 empty] | 60009 | KINGTAP2 | WEST
[32 empty] | 60011 | DSKY2_T4 | WEST
[32 empty] | 60014 | SPUD4A | WEST
[32 empty] | 60016 | WOODWRD1 | WEST
[32 empty] | 60017 | ORNNWP1 | WEST
[32 empty] | 60018 | DSKY1 | WEST
[32 empty] | 60019 | KING_NW1 | WEST
[32 empty] | 60021 | KM NWP4 | WEST
[32 empty] | 60035 | BLF SVC1 | WEST
[32 empty] | 60040 | BLF_CRK7 | WEST
[32 empty] | 60041 | BLFTERT1 | WEST
[32 empty] | 60042 | BLF_CSTR | WEST
[32 empty] | 60043 | BLFTERT2 | WEST
[32 empty] | 60044 | BLF_CSTR | WEST
[32 empty] | 60056 | CALLAHAN | WEST
[32 empty] | 60057 | CALLAHAN | WEST
[32 empty] | 60058 | BUFF_GAP | WEST
[32 empty] | 60059 | BUFF_GAP | WEST
[32 empty] | 60060 | CIRELLO | WEST
[32 empty] | 60061 | CIRELLO | WEST
[32 empty] | 60063 | BUFF_GAP | WEST
[32 empty] | 60066 | H_HOLLOW | WEST
[32 empty] | 60067 | H_HOLLOW | WEST
[32 empty] | 60068 | HHOLLOW2 | WEST
[32 empty] | 60069 | HRSHOL2 | WEST
[32 empty] | 60070 | HHOLLOW3 | WEST
[32 empty] | 60071 | HHOLLOW3 | WEST
[32 empty] | 60072 | HHOLLOW4 | WEST
[32 empty] | 60073 | HRSHOL4 | WEST
[32 empty] | 60080 | WHRLWIND | WEST
[32 empty] | 60081 | WHRLWIND | WEST
[32 empty] | 60201 | RIO DRCS | WEST
[32 empty] | 60202 | FRNDDRCS | WEST
[32 empty] | 66216 | BLF_CRK4 | WEST
[32 empty] | 66217 | BLF_CRK4 | WEST
[32 empty] | 71050 | L_BITTCR | WEST
[32 empty] | 71051 | L_BITTCR | WEST
[32 empty] | 71052 | L_BITTCR | WEST
[32 empty] | 71053 | L_SWEETW | WEST
[32 empty] | 71054 | L_SWEETW | WEST
[32 empty] | 71055 | L_BITTCR | WEST
[32 empty] | 71056 | L_SWEETW | WEST
[32 empty] | 71057 | L_SWEETW | WEST
[32 empty] | 71058 | L_SWEETW | WEST
[32 empty] | 71059 | L_SWEETW | WEST
[32 empty] | 71060 | L_SWEETW | WEST
[32 empty] | 71061 | L_SWEETW | WEST
[32 empty] | 76009 | L_TWINBU | WEST
[32 empty] | 76011 | L_TWINBU | WEST
[32 empty] | 76012 | L_TWISTR | WEST
[32 empty] | 76013 | L_WEYASW | WEST
[32 empty] | 76030 | L_GASCCR | WEST
[32 empty] | 76031 | L_GASCCR | WEST
[32 empty] | 76032 | L_NORTMC | WEST
[32 empty] | 76090 | L_DIVIDE | WEST
[32 empty] | 76091 | L_DIVIDE | WEST
[32 empty] | 76092 | L_DIVIDE | WEST
[32 empty] | 76093 | L_CAPRSI | WEST
[32 empty] | 76094 | L_CAPRGE | WEST
[32 empty] | 76095 | L_CAPRSI | WEST
[32 empty] | 76096 | L_CAPRSI | WEST
[32 empty] | 76097 | L_CAPRGE | WEST
[32 empty] | 76317 | L_POTTTA | WEST
[32 empty] | 76319 | L_MCELMU | WEST
[32 empty] | 76320 | L_SCHKAD | WEST
[32 empty] | 76388 | L_FORTMA | WEST
[32 empty] | 76390 | L_FORTMA | WEST
[32 empty] | 76579 | L_FORTLA | WEST
[32 empty] | 76582 | L_MEVISW | WEST
[32 empty] | 76595 | L_NORTMC | WEST
[32 empty] | 76615 | L_CRANE | WEST
[32 empty] | 78015 | L_ROSICR | SOUTH
[32 empty] | 80000 | EPLV | SOUTH
[32 empty] | 80003 | MILHWYS | SOUTH
[32 empty] | 80004 | CCENRCTR | SOUTH
[32 empty] | 80010 | EPLVT1 | SOUTH
[32 empty] | 80012 | LAR | SOUTH
[32 empty] | 80013 | LARVFTN1 | SOUTH
[32 empty] | 80014 | LARVFTN2 | SOUTH
[32 empty] | 80020 | HEIGHTS4 | SOUTH
[32 empty] | 80021 | LARSTCOM | SOUTH
[32 empty] | 80051 | FOR #8 | SOUTH
[32 empty] | 80052 | FOR #9 | SOUTH
[32 empty] | 80053 | FOR #10 | SOUTH
[32 empty] | 80054 | FOR A | SOUTH
[32 empty] | 80055 | FOR B | SOUTH
[32 empty] | 80064 | CHOCBAYU | SOUTH
[32 empty] | 80071 | ZORILLO7 | SOUTH
[32 empty] | 80076 | AJO7A | SOUTH
[32 empty] | 80078 | GULFWIND | SOUTH
[32 empty] | 80080 | GWINDT11 | SOUTH
[32 empty] | 80081 | GWINDT21 | SOUTH
[32 empty] | 80106 | FALCONSS | SOUTH
[32 empty] | 80107 | PLMHSTT1 | SOUTH
[32 empty] | 80108 | PLMHSTT2 | SOUTH
[32 empty] | 80117 | MOORE F | SOUTH
[32 empty] | 80118 | PALMHURS | SOUTH
[32 empty] | 80121 | S_MISSIN | SOUTH
[32 empty] | 80123 | CITRUSCY | SOUTH
[32 empty] | 80128 | WHPTR1 | SOUTH
[32 empty] | 80129 | WHPTR2 | SOUTH
[32 empty] | 80135 | CSDBUS2 | SOUTH
[32 empty] | 80136 | CSDRBUS | SOUTH
[32 empty] | 80137 | CSDR89 | SOUTH
[32 empty] | 80138 | CSDR7 | SOUTH
[32 empty] | 80139 | CSDR56 | SOUTH
[32 empty] | 80140 | CSDR11 | SOUTH
[32 empty] | 80141 | CSDR11 | SOUTH
[32 empty] | 80148 | RH2TERT | SOUTH
[32 empty] | 80153 | CSDE | SOUTH
[32 empty] | 80154 | CSDW | SOUTH
[32 empty] | 80155 | MHSTCOM | SOUTH
[32 empty] | 80165 | LARDOVFT | SOUTH
[32 empty] | 80168 | LARVFTS | SOUTH
[32 empty] | 80169 | LARVFTS | SOUTH
[32 empty] | 80170 | LARVFTS | SOUTH
[32 empty] | 80171 | SARITA7A | SOUTH
[32 empty] | 80178 | PENASCAL | SOUTH
[32 empty] | 80180 | PNSCALT1 | SOUTH
[32 empty] | 80181 | PNSCALT2 | SOUTH
[32 empty] | 80223 | REYSHR G | SOUTH
[32 empty] | 80224 | VISTRONG | SOUTH
[32 empty] | 80225 | VISTRONG | SOUTH
[32 empty] | 80226 | ALCOA G | SOUTH
[32 empty] | 80227 | AIRCO G | SOUTH
[32 empty] | 80228 | KRGP | SOUTH
[32 empty] | 80230 | CELANEBI | SOUTH
[32 empty] | 80265 | LARECU40 | SOUTH
[32 empty] | 80266 | LARECU50 | SOUTH
[32 empty] | 80267 | LARECU44 | SOUTH
[32 empty] | 80268 | LARECU54 | SOUTH
[32 empty] | 80375 | LAKSDTP2 | SOUTH
[32 empty] | 80540 | VICEC54A | SOUTH
[32 empty] | 80541 | VICEC64A | SOUTH
[32 empty] | 85000 | SHARPE6 | SOUTH
[32 empty] | 85001 | N_SHARPE | SOUTH
[32 empty] | 85002 | N_SHARPE | SOUTH
[32 empty] | 85006 | HIDALGO4 | SOUTH
[32 empty] | 86104 | CID-138 | SOUTH
[32 empty] | 86105 | CID-230 | SOUTH
[32 empty] | 86106 | CUF-230 | SOUTH
[32 empty] | 86107 | CUF-138 | SOUTH
[32 empty] | 88198 | BEEVILLE | SOUTH
[32 empty] | 88253 | HAMILTON | SOUTH
[32 empty] | 88299 | ZAPATA | SOUTH
[32 empty] | 88508 | FALFURRI | SOUTH
[32 empty] | 88909 | NLARSSL | SOUTH
Note on AJ4: this column converts a power world area name to the current zone name
Movable ONLY generators that are ready to be copied to the Base GSFs worksheet
Step 1: set up movable ONLY generators

## Bus_Zone Map
Get final bus mapping from ERCOT after the BOARD
approves a final scenario
2009 Bus Mapping
Number | Name | Scenario 3i CM Zone
1 | ROANSPRA | NORTH
2 | KEITHSW | NORTH
4 | IOLA | NORTH
9 | BEDIAS | NORTH
13 | KEITH | NORTH
17 | CARLOSSW | NORTH
21 | CARLOS | NORTH
25 | NORTHZUL | NORTH
29 | BOONEVIL | NORTH
31 | HEARNECI | NORTH
32 | ROBERTSO | NORTH
33 | WATSONCH | NORTH
34 | CALVERTM | NORTH
35 | HEARNE8 | NORTH
36 | HEARNE9 | NORTH
37 | RIDGE | NORTH
38 | SUTTON | NORTH
40 | JEWETT | NORTH
43 | HILTPLKS | NORTH
45 | OLETHA | NORTH
46 | FARRAR | NORTH
47 | HILTOPLK | NORTH
48 | HILTOPLK | NORTH
53 | ELLIOTT | NORTH
57 | FRANKLIN | NORTH
61 | BRANCHVI | NORTH
64 | MILANO | SOUTH
65 | SILVERCI | NORTH
69 | BARCLAY | SOUTH
73 | CALVERTS | NORTH
75 | PETTIBON | SOUTH
77 | CALVERT | NORTH
81 | PLESNTGR | NORTH
85 | KOSSESWC | NORTH
86 | BEARGRAS | NORTH
89 | KOSSE | NORTH
91 | PERRY8 | NORTH
92 | PERRY9 | NORTH
93 | PETTEWAY | NORTH
95 | HALLSBUR | NORTH
99 | BENHUR | NORTH
103 | GROESBEC | NORTH
104 | BUTLER | NORTH
107 | PRAIRIEH | NORTH
110 | BUCKHOLT | NORTH
114 | BARTLETT | SOUTH
115 | DINGDONG | SOUTH
116 | SALTY | SOUTH
117 | CEDARVAL | SOUTH
118 | BARTLETT | SOUTH
120 | TALBRTRI | SOUTH
122 | SCHWERTN | SOUTH
123 | JARREL | SOUTH
125 | STLHOSHO | SOUTH
126 | POAGE | SOUTH
127 | THRNDALN | SOUTH
130 | SEATON8 | SOUTH
131 | SEATON9 | SOUTH
132 | BELLCNTY | SOUTH
133 | BELLCNTY | SOUTH
136 | TRIMMIER | SOUTH
137 | MOODY | SOUTH
139 | LAKEBELT | SOUTH
141 | MOFFAT | SOUTH
142 | TUGTSVIL | NORTH
145 | LEONJUNC | NORTH
146 | SPRINGVA | NORTH
147 | LORENA | NORTH
149 | SANTAFES | NORTH
153 | SANTAFE | NORTH
157 | GATESVIL | NORTH
158 | PANCAKE | NORTH
160 | MOSHEIM | NORTH
161 | MCGREGOR | NORTH
164 | PATTON | NORTH
165 | WINDSORS | NORTH
169 | WINDSOR | NORTH
170 | COTTONBE | NORTH
173 | CRAWFORD | NORTH
175 | CHINASPR | NORTH
177 | BOSQUE | NORTH
181 | CAYOTE | NORTH
185 | MIDWAY | NORTH
186 | NAVAROMI | NORTH
190 | DAWSON | NORTH
192 | TELICO | NORTH
193 | BARRY | NORTH
194 | PURDON | NORTH
195 | FREESTON | NORTH
196 | FAIRFIEL | NORTH
197 | OAKGROVE | NORTH
198 | EMMETT | NORTH
200 | CHATFIEL | NORTH
202 | SARDIS9 | NORTH
203 | SARDIS8 | NORTH
204 | BETHEL | NORTH
205 | HIGHWY22 | NORTH
206 | POWELLMP | NORTH
207 | SIMSBORO | NORTH
208 | EUREKA | NORTH
210 | REAGORSP | NORTH
211 | GOODLOE | NORTH
212 | WINKLER | NORTH
213 | HANEY | NORTH
214 | ROCKETTS | NORTH
215 | INDIA | NORTH
216 | ENNIS | NORTH
217 | GLNHEIGH | NORTH
218 | ROCKETT | NORTH
220 | CEDARHIL | NORTH
221 | TRUMBULL | NORTH
222 | TRUMBULL | NORTH
223 | SAINTPAU | NORTH
224 | ITASCA | NORTH
225 | FORRESTO | NORTH
228 | PEORIA | NORTH
230 | DWUSSWW | NORTH
232 | LAMPOSTS | NORTH
234 | CHATT | NORTH
236 | LAMPOST | NORTH
237 | BLANTON | NORTH
238 | BOSQUESW | NORTH
239 | BOSQUESW | NORTH
240 | WHITNEY5 | NORTH
241 | WHITNEY8 | NORTH
242 | WHITNEYD | NORTH
243 | WHITNEYS | NORTH
244 | WHITNYDM | NORTH
245 | WHITNYDM | NORTH
246 | BOSQUESW | NORTH
247 | BOSQUESW | NORTH
249 | ROGERSHL | NORTH
250 | FRTGATES | NORTH
251 | BOSQUESW | NORTH
252 | BOSQUESW | NORTH
253 | BOSQUESW | NORTH
254 | FORTGATE | NORTH
258 | HAMILTON | NORTH
260 | KEMPNER | SOUTH
262 | INDIANGA | NORTH
265 | ENERGYSW | NORTH
269 | ENERGY | NORTH
270 | MORTONVA | NORTH
273 | GUSTINE | NORTH
274 | GORMAN | NORTH
275 | LEONPLNT | NORTH
276 | HGHWY101 | NORTH
277 | HASSE | NORTH
279 | OLDEN | NORTH
281 | DOWNING | NORTH
282 | EOLIANRD | NORTH
283 | ZEPHYR | NORTH
284 | EARLY | NORTH
285 | RISINGST | NORTH
289 | NIMROD | NORTH
290 | SHILOH | NORTH
291 | DELEON | NORTH
292 | HOLDER8 | NORTH
293 | HOLDER9 | NORTH
294 | MOUNTARY | NORTH
295 | STEPHENV | NORTH
296 | STPHNVLT | NORTH
297 | CARLTONS | NORTH
298 | CARLTON | NORTH
299 | STEPHNVI | NORTH
300 | JOHNSVIL | NORTH
301 | LINGLEVI | NORTH
302 | SELDEN | NORTH
303 | NORFORK | NORTH
304 | WRIGHT | NORTH
305 | BLUFFDAL | NORTH
306 | BUNKER | NORTH
307 | GRANBURY | NORTH
308 | BUNKER01 | NORTH
309 | TOLARTAP | NORTH
310 | IVAN | NORTH
311 | HILLCITY | NORTH
315 | GLENROSE | NORTH
319 | MERIDIAN | NORTH
322 | LIPAN | NORTH
323 | CRANFILS | NORTH
327 | POWELL | NORTH
331 | RWMILLER | NORTH
332 | RWMILLER | NORTH
333 | RWMILLER | NORTH
334 | RWMILLER | NORTH
335 | RWMILLER | NORTH
336 | RWMILLER | NORTH
343 | MRSSHPRD | NORTH
344 | MRSSHPRD | NORTH
345 | MRSSHPRD | NORTH
350 | ABBYBEND | NORTH
352 | PROTROYA | NORTH
356 | SPUNKY8 | NORTH
357 | SPUNKY9 | NORTH
363 | HOOD8 | NORTH
364 | HOOD | NORTH
366 | JNSNCNTY | NORTH
367 | JNSNCNTY | NORTH
370 | JNSNCNTY | NORTH
373 | ACTON | NORTH
377 | FALLCREE | NORTH
380 | FRIENDSH | NORTH
384 | GEORGESC | NORTH
385 | LITTLEHO | NORTH
387 | NEWHOPE | NORTH
391 | BONO | NORTH
393 | CONCORD | NORTH
394 | CONCORD | NORTH
395 | DOMINO | NORTH
398 | JOSHUA | NORTH
399 | CROWLEY | NORTH
404 | JESSICA | NORTH
405 | EGAN | NORTH
412 | BURLESON | NORTH
415 | KEENE | NORTH
419 | LILLIAN8 | NORTH
420 | LILLIAN9 | NORTH
428 | VALLYBRN | NORTH
429 | RETTA | NORTH
430 | TIMBERGR | NORTH
432 | CONLEY | NORTH
433 | WILDCAT | NORTH
435 | LKALVARA | NORTH
436 | GRANDVIE | NORTH
440 | GRIFFITH | NORTH
441 | VENUS | NORTH
443 | SANDFLAT | NORTH
444 | COVINGTO | NORTH
447 | SANDFLAT | NORTH
451 | NASAUBAY | NORTH
455 | NASSAUBA | NORTH
466 | WAPLES9 | NORTH
467 | WAPLES8 | NORTH
470 | FAIRVIEW | NORTH
471 | LAKEWOOD | NORTH
473 | THORPSPR | NORTH
475 | STOCKTNB | NORTH
477 | FOX8 | NORTH
478 | FOX9 | NORTH
484 | SODASPRN | NORTH
487 | BROCK | NORTH
489 | STHBROCK | NORTH
491 | SOUTHBRO | NORTH
494 | TINTOP | NORTH
495 | RAILROAD | NORTH
498 | LIVEOAK | NORTH
501 | HILLTOP8 | NORTH
502 | NTHTEXAS | NORTH
503 | NTHTEXAS | NORTH
504 | NTHTEXAS | NORTH
505 | NTHTEXAS | NORTH
506 | HILLTOP9 | NORTH
509 | WTHFRDLK | NORTH
511 | AGNESSWT | NORTH
512 | NRTHWTHF | NORTH
514 | DUBLTRAN | NORTH
515 | SHADYGRO | NORTH
518 | ADVANCE | NORTH
519 | WHITT | NORTH
520 | ALEDOTAP | NORTH
522 | HUDSONOA | NORTH
526 | DICEY | NORTH
527 | ALEDO | NORTH
530 | SPRINGTO | NORTH
531 | FLATROCK | NORTH
532 | AGNES | NORTH
533 | FALTROCK | NORTH
534 | WETHFORD | NORTH
537 | CNTERPOI | NORTH
541 | RENO | NORTH
545 | BRIAR | NORTH
548 | BOYD | NORTH
555 | GRAPEVIN | NORTH
556 | IBM | NORTH
559 | HERITAGE | NORTH
562 | JOPLIN | NORTH
565 | KELLER | NORTH
566 | CHERRYGR | NORTH
567 | WIZARDWE | NORTH
568 | PEDENROA | NORTH
570 | WISECNTY | NORTH
572 | AURORA | NORTH
573 | NEWARK | NORTH
576 | RHOME | NORTH
578 | ALLISON | NORTH
579 | JCKCNTY8 | NORTH
580 | JCKCNTY8 | NORTH
581 | JCKCNTY8 | NORTH
582 | JCKCNTY8 | NORTH
583 | DECATUR | NORTH
584 | WOODIE | NORTH
585 | CHISOLM | NORTH
587 | GREENWOO | NORTH
588 | WILLOW | NORTH
590 | PERCHHIL | NORTH
595 | KEETER | NORTH
596 | COTTONDA | NORTH
598 | ELNA | NORTH
600 | BRIDGEPO | NORTH
601 | EBRIDGPO | NORTH
608 | CRAFTON | NORTH
616 | CARTER | NORTH
618 | LONESTAR | NORTH
620 | BOWIE8 | NORTH
621 | BOWIE9 | NORTH
628 | SPRNGCRE | NORTH
629 | ROMANJUA | NORTH
631 | NEWPORT | NORTH
632 | JOHNSONS | NORTH
633 | MONTAGUE | NORTH
634 | AUDUBONS | NORTH
635 | AUDUBON | NORTH
636 | JOHNSON | NORTH
640 | ROANOKE | NORTH
645 | LEWISVLS | NORTH
646 | LEWISVLS | NORTH
648 | COPPELL | NORTH
649 | PNTHRCRE | NORTH
651 | LEBANON | NORTH
652 | AUBREY | NORTH
653 | CUSTER2 | NORTH
655 | CUSTER | NORTH
656 | MOUND | NORTH
657 | KIMBALRO | NORTH
658 | MCKAMY | NORTH
659 | BRIDGES | NORTH
660 | LEWISVIL | NORTH
661 | CROSTIMB | NORTH
662 | NAVO | NORTH
663 | HEBRON | NORTH
664 | HIGHLAND | NORTH
668 | CANYON | NORTH
670 | KRUM | NORTH
671 | LAKEDALL | NORTH
672 | RECTORRO | NORTH
673 | KRUMSW | NORTH
675 | ROCKHILL | NORTH
679 | MCPHERSO | NORTH
680 | NRTHSANG | NORTH
681 | FRISCO | NORTH
684 | SPRING | NORTH
691 | VALLEYVI | NORTH
695 | MUENSTER | NORTH
698 | SALEM | NORTH
704 | MTNSPRNG | NORTH
705 | HAWKINS9 | NORTH
706 | WOODBINE | NORTH
707 | HAWKINS8 | NORTH
708 | KIOWA | NORTH
709 | CALLISBU | NORTH
718 | WHTSBRSW | NORTH
722 | JORDAN | NORTH
724 | SMS SW | WEST
725 | SIVLSBND | NORTH
726 | GAINESVI | NORTH
727 | SIVELSBE | NORTH
728 | WOLFRIDG | NORTH
729 | SCURRYSW | WEST
730 | WOLFRIDG | NORTH
731 | HENRY | WEST
732 | BRYSON | NORTH
733 | PADUCAH | WEST
734 | MCADAMS | WEST
735 | REDRIVER | NORTH
736 | LIBERTY | WEST
737 | SMS | WEST
738 | SINCLAIR | NORTH
739 | CHILDRES | WEST
741 | DYEMOUND | NORTH
742 | SINCLAIR | NORTH
743 | SALTCREE | WEST
744 | WALNUTBE | NORTH
745 | KING | WEST
746 | STJO | NORTH
747 | KALGARY | WEST
748 | JAYTON | WEST
749 | GLENN | WEST
750 | STJO | NORTH
751 | ESPUELA | WEST
752 | CLAIRMON | WEST
753 | BISSETT | WEST
754 | CAPSCORN | NORTH
755 | ASPERMON | WEST
756 | NOCONA | NORTH
757 | BUSHKNOB | WEST
758 | ALCORN | NORTH
759 | MORAN | WEST
760 | ALBANY | WEST
761 | TRUSCOTT | WEST
762 | HARDYSW | NORTH
763 | ROCHESTE | WEST
764 | MUNDAY | WEST
765 | KNOX | WEST
766 | HARDY | NORTH
767 | HENRIETA | NORTH
768 | JOY | NORTH
769 | POSTOAKS | NORTH
770 | ARROWHEA | NORTH
771 | POSTOAK | NORTH
772 | SHANNON | NORTH
773 | SCOTLAND | NORTH
774 | KATZP | WEST
775 | LANHAM | NORTH
776 | BRIDWELL | NORTH
777 | GOREE | WEST
778 | GILLESPI | WEST
779 | SEYMOUR | NORTH
780 | ELBERT | NORTH
781 | ELBERTSW | NORTH
782 | LAKEKEMP | NORTH
783 | LAKEKEMP | NORTH
784 | WESTOVER | NORTH
785 | ORAN | NORTH
786 | BOMARTON | WEST
787 | OLNEY8 | NORTH
788 | OLNEY9 | NORTH
789 | SEYMORMP | NORTH
790 | BENJAMIN | WEST
791 | JEAN | NORTH
792 | MURRAY | NORTH
794 | JACKSBOR | NORTH
795 | STHBENDS | NORTH
796 | SOUTHBEN | NORTH
797 | MARKLEY | NORTH
800 | APOLLO_9 | NORTH
801 | KRAFTTAP | NORTH
802 | APOLLO | NORTH
803 | COLLEGE9 | NORTH
804 | RAYTHEON | NORTH
805 | FAIRDALE | NORTH
806 | JUPITER | NORTH
807 | PRAXAIR | NORTH
808 | PLASTIPA | NORTH
809 | OAKLAND | NORTH
810 | CENTRVIL | NORTH
812 | SWINDELL | NORTH
813 | WYNNJOYC | NORTH
814 | NEWMAN9 | NORTH
815 | LAWLERT | NORTH
816 | OLINGER_ | NORTH
817 | ROSEHILL | NORTH
818 | OLINGER | NORTH
819 | LYONS | NORTH
820 | LAWLER | NORTH
821 | FIREWHEE | NORTH
822 | PRAXAIRT | NORTH
823 | WALNUT | NORTH
825 | NAAMAN | NORTH
826 | CASTLE_D | NORTH
827 | BRAND | NORTH
829 | COLLEGE8 | NORTH
830 | SHILOH | NORTH
831 | OATES | NORTH
832 | MCCREE9 | NORTH
834 | MCCREE8 | NORTH
836 | KRAFT | NORTH
837 | NEWMAN_G | NORTH
842 | OLINGER_ | NORTH
843 | OLINGER_ | NORTH
844 | OLINGER_ | NORTH
845 | OLINGER_ | NORTH
848 | MARQUIS | NORTH
849 | NEWMAN8 | NORTH
850 | CRIST | NORTH
852 | MARQUIS9 | NORTH
853 | GPLTEMP | NORTH
855 | ELMGROVE | NORTH
901 | WOODROW6 | NORTH
902 | POLES315 | NORTH
903 | POLE_SP1 | NORTH
904 | POLESPL2 | NORTH
908 | SPNCR_SW | NORTH
909 | KINGSROW | NORTH
910 | HICKORY6 | NORTH
911 | DENARCO1 | NORTH
912 | N_DENT69 | NORTH
913 | INDSTRL1 | NORTH
914 | LOCUST69 | NORTH
915 | NLAKES69 | NORTH
916 | JMCRSTL1 | NORTH
917 | POCKRUS1 | NORTH
918 | TEASLEY1 | NORTH
920 | SPNCRGEN | NORTH
923 | SPENCER_ | NORTH
924 | SPENCER_ | NORTH
930 | RDWELLS1 | NORTH
932 | RDWELLS6 | NORTH
936 | DIESEL_D | NORTH
937 | STEAM_D | NORTH
938 | LTV_D | NORTH
939 | TERREL_D | NORTH
940 | IND_PK_D | NORTH
945 | MAMIE_D | NORTH
946 | DENT_RD_ | NORTH
947 | ONEAL_D | NORTH
948 | STEAM1 | NORTH
949 | STEAM2 | NORTH
950 | STEAM3 | NORTH
952 | DIESELA | NORTH
956 | DN_STEAM | NORTH
957 | GREENV_I | NORTH
958 | GREENV_I | NORTH
959 | N_DENT_T | NORTH
960 | SHELBY1 | NORTH
961 | SHELBY2 | NORTH
962 | BRYAN_E_ | NORTH
963 | SHELBY3 | NORTH
964 | GIBN_CRE | NORTH
965 | GIBN_CRE | NORTH
966 | GIBN_CRE | NORTH
967 | GIBN_CRE | NORTH
968 | BENDAVIS | NORTH
969 | GIBN_CRE | NORTH
970 | BENDAVIS | NORTH
971 | PRUITT_8 | NORTH
972 | W_DENT_T | NORTH
973 | MCCREE_5 | NORTH
974 | MCCREE1_ | NORTH
975 | JKCREEK1 | NORTH
976 | SHELBSTR | NORTH
977 | GREENV_I | NORTH
978 | JKCREEK3 | NORTH
979 | GREENV_I | NORTH
980 | GIBN_STR | NORTH
981 | SPNCRINT | NORTH
982 | DN_STEAM | NORTH
983 | ARCO_T_8 | NORTH
984 | W_DENT_T | NORTH
985 | N_DENT_8 | NORTH
986 | W_DENT_8 | NORTH
987 | GIBN_STR | NORTH
988 | W_DENT_5 | NORTH
989 | GIBN_STR | NORTH
990 | GIBN_CRE | NORTH
991 | BOWIE_T_ | NORTH
992 | BRIDGE_P | NORTH
993 | BENDAVIS | NORTH
994 | BENDAVIS | NORTH
995 | BENDASTR | NORTH
996 | BENDASTR | NORTH
997 | MCCRESTR | NORTH
998 | JKCRESTR | NORTH
999 | GREENSTR | NORTH
1000 | GREENSTR | NORTH
1001 | DN_STSTR | NORTH
1002 | PBCTAGE_ | WEST
1003 | PBCTBGE_ | WEST
1004 | PBCTCGE_ | WEST
1005 | PBCTDGE_ | WEST
1006 | PBCTEGE_ | WEST
1007 | PB5GEN_6 | WEST
1008 | PB6GEN_7 | WEST
1009 | N_DENSTR | WEST
1010 | PERMIANB | WEST
1011 | W_DENSTR | WEST
1012 | W_DENSTR | WEST
1015 | PERMIANB | WEST
1018 | MOSS_5 | WEST
1019 | MOSS_8 | WEST
1020 | ECTORTIE | WEST
1021 | MIDLET_5 | WEST
1022 | MIDLNDE_ | WEST
1023 | MIDLNDE_ | WEST
1024 | FSCOGEN_ | WEST
1025 | FSCOGEN_ | WEST
1026 | ECTORTIE | WEST
1027 | ODESEHV_ | WEST
1028 | ODESEHV_ | WEST
1030 | MRGNCRK_ | WEST
1031 | MRGN6G_6 | WEST
1032 | MRGNCRK_ | WEST
1033 | MRGNCRK_ | WEST
1034 | MCTMODEL | WEST
1037 | MORGAN5G | WEST
1039 | MRGNAG_1 | WEST
1040 | MRGNBG_2 | WEST
1041 | MRGNCG_3 | WEST
1042 | MRGNDG_4 | WEST
1043 | MRGNEG_5 | WEST
1044 | MRGNFG_6 | WEST
1045 | CALENG1G | WEST
1046 | CALENG2G | WEST
1047 | CALENG3G | WEST
1048 | TONKAWA_ | WEST
1049 | ROSCOE_5 | WEST
1051 | HUNTSMAN | WEST
1052 | REXALL_8 | WEST
1053 | GENRUBR_ | WEST
1054 | OLFNNSHL | WEST
1055 | NYLONTAP | WEST
1056 | NYLON_8 | WEST
1057 | CHAMPION | WEST
1058 | LONGSHOR | WEST
1059 | MIDESSA_ | WEST
1060 | PYRON_5 | WEST
1061 | CIELOGEN | WEST
1062 | CIELOGEN | WEST
1063 | CIELOWIN | WEST
1064 | SUN_8 | WEST
1065 | KINDERML | WEST
1066 | KINDERML | WEST
1067 | GOLDENSW | WEST
1068 | SCURRYCW | WEST
1069 | KINDERMG | WEST
1070 | KINDERMG | WEST
1071 | KINDERMG | WEST
1072 | INADALE_ | WEST
1073 | SCURRYCW | WEST
1074 | WINKSS_8 | WEST
1075 | WINKSS_9 | WEST
1087 | WRDGLFTA | WEST
1088 | WICKETT_ | WEST
1089 | WICKETAP | WEST
1091 | WARDGULF | WEST
1092 | LOVING_8 | WEST
1093 | ELMAR_8 | WEST
1094 | MASON_8 | WEST
1095 | SCRWBEAN | WEST
1096 | BLACKRVR | WEST
1097 | TWPPMTR_ | WEST
1098 | KWINDRO_ | WEST
1099 | SWPORTAP | WEST
1100 | SWPORTLA | WEST
1101 | EDWARDS_ | WEST
1102 | JUDKINS_ | WEST
1103 | SANDHLTA | WEST
1104 | SANDHILL | WEST
1105 | MONAHTAP | WEST
1106 | MONAHN1_ | WEST
1107 | MONAHTAP | WEST
1108 | MONAHN2_ | WEST
1109 | CULBESON | WEST
1111 | BIG3ODTA | WEST
1112 | BIG3OD_8 | WEST
1113 | ODESASW_ | WEST
1116 | WINDWOOD | WEST
1117 | MIDLANDW | WEST
1118 | CRMWD8TA | WEST
1119 | CRMWD8_8 | WEST
1120 | MIDLAIRP | WEST
1121 | GLENHAVN | WEST
1122 | ODESSANO | WEST
1123 | ODESSANO | WEST
1126 | ODESSA2_ | WEST
1127 | ODESSA1_ | WEST
1128 | LIQDAIR_ | WEST
1129 | WESTOVER | WEST
1130 | AMOSFOST | WEST
1132 | MIDLDWNT | WEST
1137 | TEXINSTA | WEST
1138 | TEXASINS | WEST
1141 | HOLTSS_8 | WEST
1142 | HOLTSS_9 | WEST
1143 | AMOCNCTA | WEST
1144 | AMNCOWD_ | WEST
1145 | AMGLDSMI | WEST
1146 | NOTREES1 | WEST
1147 | CHEYENTA | WEST
1148 | CHEYENNE | WEST
1149 | DOLRHIDE | WEST
1150 | AMOCO3BA | WEST
1152 | UNOCALDH | WEST
1155 | ANDREWTA | WEST
1156 | ANDREWS_ | WEST
1158 | SLMSALE_ | WEST
1159 | NOANDREW | WEST
1160 | NOANDREW | WEST
1161 | UNPKRBK_ | WEST
1163 | LAMESA_8 | WEST
1164 | LAMESA_9 | WEST
1165 | EXMEANTA | WEST
1166 | EXNMEANS | WEST
1167 | MUSTANG_ | WEST
1168 | PAULDTAP | WEST
1169 | PAULDAVS | WEST
1176 | GRANDVEW | WEST
1177 | TEXMABEE | WEST
1178 | ADOBEMEW | WEST
1179 | TEXMATAP | WEST
1180 | ECTRHILL | WEST
1182 | MOCKNBRD | WEST
1184 | GODDARD_ | WEST
1198 | CRANE_9 | WEST
1199 | ARCOCTAP | WEST
1201 | ARCOCRN_ | WEST
1202 | WARDSS_9 | WEST
1203 | BARNSLEY | WEST
1204 | EXNJCTAP | WEST
1205 | EXONJUAN | WEST
1206 | CRNATLTA | WEST
1207 | CRANATLC | WEST
1210 | MIDKIFF_ | WEST
1211 | MIDKIFF_ | WEST
1212 | UPTON_8 | WEST
1213 | PEMBRKTA | WEST
1214 | CRANEAST | WEST
1215 | PEMBROOK | WEST
1216 | REAGNSHE | WEST
1217 | GLASCOCK | WEST
1218 | GARDCITY | WEST
1221 | TEXHARVY | WEST
1222 | PECKTAP_ | WEST
1223 | PECK_9 | WEST
1226 | MDGULFTA | WEST
1227 | MIDLGULF | WEST
1228 | MIDBASIN | WEST
1229 | STANTON_ | WEST
1232 | CRANEHUM | WEST
1233 | GETTY_9 | WEST
1234 | PGASUSTA | WEST
1235 | PEGASUS_ | WEST
1236 | SPEGSTAP | WEST
1237 | SOPGASUS | WEST
1238 | ROYALTY_ | WEST
1239 | COYANOSA | WEST
1240 | WFCAMPTA | WEST
1241 | WOLFCAMP | WEST
1242 | NNATURAL | WEST
1245 | WINKBAWT | WEST
1246 | WINKBASN | WEST
1249 | KEYSTONE | WEST
1252 | VEST_9 | WEST
1253 | MIDWAY_9 | WEST
1254 | ODBASSS_ | WEST
1255 | ODESBASN | WEST
1256 | GOLDSMTH | WEST
1257 | ECTRSHEL | WEST
1259 | NTCOWDEN | WEST
1262 | EMMATAP_ | WEST
1263 | EMMA_9 | WEST
1264 | SANADTAP | WEST
1265 | SANANDRS | WEST
1266 | MIDFARMS | WEST
1267 | ANDREWS_ | WEST
1270 | FRNKLCTY | WEST
1273 | PHILANDS | WEST
1274 | FULERTON | WEST
1275 | EXXONFUL | WEST
1277 | BAKKETAP | WEST
1280 | BAKKE_9 | WEST
1281 | AMMIDFTA | WEST
1282 | AMOMIDFM | WEST
1285 | MEANS_9 | WEST
1292 | ECTRHARP | WEST
1295 | WICKETT_ | WEST
1296 | NORTHWRD | WEST
1297 | WICKETAP | WEST
1300 | EXSHARNR | WEST
1301 | WILLOWVA | WEST
1302 | MULESHOE | WEST
1305 | SNYDER_8 | WEST
1306 | SNYDER_9 | WEST
1307 | KEYLYNTE | WEST
1308 | GAILLYNT | WEST
1309 | BLUFCKTA | WEST
1310 | KNAPP_8 | WEST
1311 | SACROC_8 | WEST
1312 | SCURYCHV | WEST
1313 | ENISCKTA | WEST
1314 | ENNISCK_ | WEST
1315 | BRAND_8 | WEST
1317 | COAHOMAN | WEST
1318 | CHINAGRV | WEST
1319 | CHINAGRV | WEST
1320 | BSP 1 | WEST
1321 | CARBONSW | WEST
1322 | BIGSPRIG | WEST
1323 | BIGSPRIG | WEST
1324 | BIGSPGWE | WEST
1325 | AIRPARK_ | WEST
1326 | STANTONW | WEST
1327 | WILDHRSE | WEST
1328 | OCOTILLO | WEST
1329 | SPRABERY | WEST
1330 | SPRABERY | WEST
1331 | DRUMRIGT | WEST
1332 | COSDEN_8 | WEST
1333 | MCDDONAL | WEST
1334 | CHNGOWNR | WEST
1335 | FORSANTA | WEST
1336 | FORSAN_8 | WEST
1337 | CRMWDTAP | WEST
1338 | CRMWDSVN | WEST
1339 | ESKOTA_8 | WEST
1340 | ESKOTA_9 | WEST
1341 | SWTRDTAP | WEST
1342 | SWEETWTD | WEST
1343 | TRENTIPP | WEST
1345 | COAHOMA_ | WEST
1346 | IATHOWTA | WEST
1347 | IATNHOW_ | WEST
1348 | WSTBROOK | WEST
1349 | WESTXWIN | WEST
1350 | NWPWRG1_ | WEST
1351 | BSPGGULF | WEST
1352 | CHALK_9 | WEST
1353 | NWPWRTAP | WEST
1354 | AEPWIND_ | WEST
1355 | ACKRLYVE | WEST
1356 | ACKRLYVE | WEST
1357 | BIGCRMWD | WEST
1358 | KNOTT_9 | WEST
1359 | ACKCHEV_ | WEST
1360 | GUNSIGHT | WEST
1362 | ACKERLY_ | WEST
1363 | ACKRLNTC | WEST
1364 | SPARNBRG | WEST
1367 | IRA_9 | WEST
1368 | SCURRY_9 | WEST
1369 | LKTHOMAS | WEST
1370 | SANTAFE_ | WEST
1371 | MURRY_P8 | NORTH
1373 | COLBASIN | WEST
1374 | CHGRGULF | WEST
1375 | AMOCO_9 | WEST
1376 | AMOCOTAP | WEST
1378 | COLOCITY | WEST
1379 | LORAINE_ | WEST
1380 | ROSCOE_9 | WEST
1381 | SWEETWTR | WEST
1382 | USGYPSTA | WEST
1383 | USGYPTWO | WEST
1384 | USGYPONE | WEST
1385 | FLINTKOT | WEST
1386 | FLINTST_ | WEST
1387 | USGYPTAP | WEST
1389 | WELCHTAP | WEST
1390 | WELCH_9 | WEST
1391 | DAWSON_9 | WEST
1392 | OXYUSA_9 | WEST
1394 | GTTYVTAP | WEST
1395 | GETTYVLM | WEST
1398 | RADIUMMT | WEST
1400 | TXCOCOGD | WEST
1401 | COGDELTA | WEST
1402 | COGDELL_ | WEST
1406 | OAKCREEK | WEST
1407 | LONESTAR | WEST
1409 | NOLANWTA | WEST
1410 | ENSCRKSS | WEST
1411 | ENSCRKSS | WEST
1412 | PLAINVTA | WEST
1416 | SWETWATR | WEST
1417 | SWETWATR | WEST
1418 | SWETWATR | WEST
1419 | SWETWATR | WEST
1420 | SWEETWTR | WEST
1421 | WILLOWCK | NORTH
1422 | BOWMAN_5 | NORTH
1423 | BOWMAN_A | NORTH
1424 | BOWMAN_B | NORTH
1425 | FISHRDSS | NORTH
1426 | FISHRDSS | NORTH
1427 | FISHERRD | NORTH
1429 | JACKSBRO | NORTH
1430 | GRHAMSES | NORTH
1431 | GRHAMSES | NORTH
1432 | GRHAMSES | NORTH
1433 | GRHAMSES | NORTH
1434 | WCPWRCO_ | NORTH
1435 | LONGCREK | NORTH
1436 | PARKER_5 | NORTH
1437 | MESQUITW | NORTH
1438 | MESQUITW | NORTH
1439 | LONCREK2 | NORTH
1440 | COMCHESS | NORTH
1441 | COMCHESS | NORTH
1442 | COKFIELD | NORTH
1446 | LKWICHIT | NORTH
1447 | LKWICHIT | NORTH
1448 | WCHTFLLS | NORTH
1449 | WCHTFLLS | NORTH
1450 | PLEASVAL | NORTH
1451 | PLEASVAL | NORTH
1452 | LANHAM_T | NORTH
1453 | WCPWRCO_ | NORTH
1454 | WCPWRCO_ | NORTH
1455 | WCPWRCO_ | NORTH
1464 | WFALLS_S | NORTH
1467 | NORTHSTR | NORTH
1468 | LKAROWHD | NORTH
1469 | SUNSETSW | NORTH
1470 | NEWPRT_P | NORTH
1471 | CARTR_P8 | NORTH
1472 | NAVYKSS1 | NORTH
1473 | NAVYKSS1 | NORTH
1474 | SCOTLD_P | NORTH
1475 | WINDTHOR | NORTH
1476 | MARKLY_8 | NORTH
1477 | RICESW_8 | NORTH
1478 | ARROWHD_ | NORTH
1479 | WFCOGEN_ | NORTH
1480 | RATHGBER | NORTH
1482 | WFCOGEN_ | NORTH
1483 | CITYVIEW | NORTH
1484 | PPG_8 | NORTH
1485 | CERAMIC_ | NORTH
1486 | BOOMTOWN | NORTH
1489 | SIKES_8 | NORTH
1492 | RIVERBND | NORTH
1493 | ARTHURST | NORTH
1494 | WFSTHOSP | NORTH
1496 | CERTEED2 | NORTH
1497 | CERTEED1 | NORTH
1498 | WFCOGEN_ | NORTH
1499 | PARKWAY2 | NORTH
1500 | PARKWAY1 | NORTH
1503 | WFALLS_N | NORTH
1504 | WFLSNBYP | NORTH
1507 | SHPFIELD | NORTH
1508 | WFLLSBSN | NORTH
1509 | PETROLIA | NORTH
1511 | WFBASIN_ | NORTH
1512 | DIAMNDSH | NORTH
1514 | SHPFIELD | NORTH
1515 | SHPFIELD | NORTH
1516 | IOWAPARK | NORTH
1517 | BURKBURN | NORTH
1518 | IOWAPARK | NORTH
1519 | CRYOVAC_ | NORTH
1520 | CRYOVAC_ | NORTH
1522 | NAVYKPOO | NORTH
1525 | ARCHCITY | NORTH
1526 | BLACKWEL | NORTH
1527 | HOLLIDAY | NORTH
1530 | BAYLR_9 | NORTH
1531 | SEYMRBAS | NORTH
1532 | SEYMOUR_ | NORTH
1533 | BOMARTON | WEST
1536 | KMA_T9 | NORTH
1537 | KMA_9 | NORTH
1538 | ELECTRA_ | NORTH
1541 | ROBNTECH | NORTH
1543 | HENRITAW | NORTH
1544 | HENRIETA | NORTH
1545 | RINGMAG_ | NORTH
1546 | RINGMAG_ | NORTH
1547 | BELLEVUE | NORTH
1548 | MONTAGUE | NORTH
1549 | BOWIESVC | NORTH
1550 | BOWIE1_9 | NORTH
1552 | WZRDWLLS | NORTH
1553 | CHCOWEST | NORTH
1554 | CHCOCSER | NORTH
1555 | JACKAMCO | NORTH
1556 | JACKSBOR | NORTH
1557 | JACKSINC | NORTH
1558 | JACKSINC | NORTH
1561 | ALVORD1_ | NORTH
1562 | CHCOWEST | NORTH
1563 | CHCOWEST | NORTH
1564 | CHCOGHLL | NORTH
1565 | BRDGPORT | NORTH
1566 | DECATUR_ | NORTH
1567 | DECATUR1 | NORTH
1568 | ALLISON_ | NORTH
1570 | RHOME_8 | NORTH
1571 | ORAN1_8 | NORTH
1572 | ORAN1_9 | NORTH
1574 | PALOPNTO | NORTH
1575 | MINWLLSW | NORTH
1576 | PALOPNTO | NORTH
1577 | MINWLLS2 | NORTH
1579 | ALEDO1_9 | NORTH
1580 | MINWLLS1 | NORTH
1581 | GRAFORD_ | NORTH
1583 | LIVEOAK1 | NORTH
1584 | MINWLLSE | NORTH
1585 | WTHFORDW | NORTH
1586 | WTHFORD_ | NORTH
1587 | WTHFORDE | NORTH
1588 | LGNVISTA | NORTH
1589 | WTHFORDW | NORTH
1591 | SPRGTOWN | NORTH
1592 | WTHFRDSS | NORTH
1593 | BONHAM_P | NORTH
1595 | LIPAN_8 | NORTH
1596 | GRAHAMSW | NORTH
1597 | GRAHAMSW | NORTH
1598 | BALSORA_ | NORTH
1599 | BARTON_8 | NORTH
1600 | BARTNWND | NORTH
1601 | GRAHAME_ | NORTH
1602 | GRAHAM_9 | NORTH
1603 | OLNEY_P9 | NORTH
1604 | ANARENE1 | NORTH
1607 | STH_BEND | NORTH
1608 | IVAN_9 | NORTH
1612 | BRECK_N_ | NORTH
1613 | BRECK_T8 | NORTH
1614 | BRECK_8 | NORTH
1615 | BRECK_9 | NORTH
1616 | SUN_ECU_ | NORTH
1617 | SUN_ECU_ | NORTH
1618 | CADDO_8 | NORTH
1619 | COLNYCRK | NORTH
1622 | EASTLAND | NORTH
1623 | MORTNVAL | NORTH
1624 | LEONSW_8 | NORTH
1625 | LEON2_9 | NORTH
1626 | LEON5_9 | NORTH
1627 | RANGULF_ | NORTH
1628 | RANGER_9 | NORTH
1629 | OLDEN_P8 | NORTH
1630 | GORMAN_9 | NORTH
1631 | DELNMAG_ | NORTH
1632 | DELNMAG_ | NORTH
1633 | DELEON_9 | NORTH
1634 | CMYNHM_T | NORTH
1635 | CMYNHM_9 | NORTH
1636 | DUBLIN1_ | NORTH
1637 | DUBLIN1_ | NORTH
1638 | SLSTR1PP | NORTH
1640 | LINGLVLL | NORTH
1641 | STPHNVIL | NORTH
1642 | FLATCRK_ | NORTH
1643 | SLSTR1PP | NORTH
1644 | SELDON_P | NORTH
1645 | JOHNSNVL | NORTH
1646 | WALNUTSP | NORTH
1647 | WALSPTNP | NORTH
1649 | HASSE_P8 | NORTH
1650 | COMANCHE | NORTH
1651 | COMANCHE | NORTH
1654 | ZEPHYR_P | NORTH
1655 | BRNWDSW_ | NORTH
1656 | BRNWD_S_ | NORTH
1661 | BRNWD1_8 | NORTH
1662 | BRNWD1_9 | NORTH
1665 | PROCTOR_ | NORTH
1666 | BLANKET_ | NORTH
1669 | LKBRNWD_ | NORTH
1670 | LKBRNWD_ | NORTH
1671 | BANGS_9 | NORTH
1675 | PEC_1G | NORTH
1676 | PEC_2G | NORTH
1677 | PEC_3G | NORTH
1678 | LAMARPWR | NORTH
1679 | LAMARPWR | NORTH
1680 | LAMARPWR | NORTH
1681 | LAMARPWR | NORTH
1682 | LAMARPWR | NORTH
1683 | LAMARPWR | NORTH
1684 | LAMARPWR | NORTH
1685 | FARMVLSW | NORTH
1687 | VALLEY_1 | NORTH
1688 | VALLEY_2 | NORTH
1689 | VALLEY_3 | NORTH
1690 | VALLYSES | NORTH
1691 | VALLYSES | NORTH
1692 | PARIS_SW | NORTH
1693 | PARIS_SW | NORTH
1694 | TENASKA_ | NORTH
1695 | MOSES_5 | NORTH
1696 | MOSES1_T | NORTH
1697 | SULSP_SS | NORTH
1698 | SULSP_SS | NORTH
1701 | MOSES_1G | NORTH
1702 | MOSES_2G | NORTH
1703 | MOSES_3G | NORTH
1704 | SHER_L_M | NORTH
1706 | GAINVL_E | NORTH
1707 | GAINVL_E | NORTH
1708 | GAINVLDX | NORTH
1709 | GAINVLDX | NORTH
1710 | GAINVL_N | NORTH
1712 | MUENSTER | NORTH
1713 | MEMC_W_T | NORTH
1714 | SHRM_TI_ | NORTH
1715 | MEMC_SW_ | NORTH
1716 | ST_JO_P9 | NORTH
1717 | MEMC_SW_ | NORTH
1718 | GAINVL_E | NORTH
1719 | GAINVL_T | NORTH
1720 | GAINVLNS | NORTH
1721 | GAINVLNS | NORTH
1722 | GAINVLCH | NORTH
1723 | LIBERTY_ | NORTH
1724 | WHTBORSE | NORTH
1725 | GORDVL_T | NORTH
1726 | SADLER_9 | NORTH
1727 | GORDVL_9 | NORTH
1728 | WHTBOR_9 | NORTH
1729 | VAL_STH_ | NORTH
1732 | SHER_NW_ | NORTH
1733 | PERRIN_T | NORTH
1734 | FINK_T8 | NORTH
1735 | FINK_8 | NORTH
1736 | PERRIN1_ | NORTH
1737 | DENISN_W | NORTH
1738 | WHTBORSE | NORTH
1739 | DENISND_ | NORTH
1740 | SHRM_TI_ | NORTH
1741 | LKTEXOMA | NORTH
1742 | TEXOMA_T | NORTH
1743 | DENISN_N | NORTH
1745 | DENISN_8 | NORTH
1746 | SHER_E_8 | NORTH
1747 | CHERYMND | NORTH
1749 | SHRM_TI_ | NORTH
1750 | SHER_S_8 | NORTH
1751 | VAN_AL_E | NORTH
1752 | WHTMND_8 | NORTH
1753 | MEMC_E_T | NORTH
1754 | VAN_AL_8 | NORTH
1755 | ECTOR_P8 | NORTH
1757 | ALLA_HUB | NORTH
1758 | PAYNE1_8 | NORTH
1759 | PAYNE1_9 | NORTH
1760 | BONHMSS1 | NORTH
1761 | BONHMSS_ | NORTH
1762 | BONHMNW1 | NORTH
1763 | PINKHIL_ | NORTH
1764 | BELLS1_9 | NORTH
1765 | ECTOR1_9 | NORTH
1766 | EXPLR_PL | NORTH
1768 | DEPORT_P | NORTH
1769 | PARIS_E_ | NORTH
1770 | LAMAR_T8 | NORTH
1771 | LAMARBM1 | NORTH
1772 | LAMARBM1 | NORTH
1773 | PARIS_E_ | NORTH
1774 | PARIS_N_ | NORTH
1776 | PARIS_KC | NORTH
1777 | PARIS_8 | NORTH
1778 | PARIS_9 | NORTH
1779 | LAMARCO_ | NORTH
1780 | RIVERCST | NORTH
1781 | RIVERCST | NORTH
1782 | SHERRY_P | NORTH
1783 | RIVERCST | NORTH
1784 | CLARKVL_ | NORTH
1785 | BAGWELL1 | NORTH
1786 | RENO_T8 | NORTH
1788 | BRKSTON1 | NORTH
1789 | HONEY_GR | NORTH
1790 | WINDMSPA | NORTH
1791 | MOSESMIN | NORTH
1793 | TALCO_W_ | NORTH
1794 | MOSES_T8 | NORTH
1795 | MOSES1_8 | NORTH
1796 | SULBLF1_ | NORTH
1797 | R0CKWELL | NORTH
1798 | SULSP_E1 | NORTH
1799 | ROCKWELL | NORTH
1800 | MRTNSPG1 | NORTH
1803 | PARS_PMP | NORTH
1805 | COOPER_9 | NORTH
1806 | ENLOE_T9 | NORTH
1808 | BONHAM_8 | NORTH
1809 | WOLFECTY | NORTH
1810 | WOLFCTY_ | NORTH
1812 | CUMBY_9 | NORTH
1813 | CUMBY1_T | NORTH
1814 | SULSPG_8 | NORTH
1815 | CUMBY1_T | NORTH
1816 | COMM_SW_ | NORTH
1817 | COMM_T8 | NORTH
1819 | COMM_S1_ | NORTH
1820 | COMMERCE | NORTH
1821 | COMMERCE | NORTH
1822 | COOPERLK | NORTH
1823 | COOPERLK | NORTH
1824 | NEYLNDVL | NORTH
1826 | CADML_9 | NORTH
1827 | CADMLX_T | NORTH
1828 | CADMLX_9 | NORTH
1829 | BURROW_T | NORTH
1830 | ROYSEGIN | NORTH
1833 | BRKSTN_T | NORTH
1845 | ROANOKE3 | NORTH
1847 | ROANOKE1 | NORTH
1848 | ROANOKE2 | NORTH
1849 | ROANOKE2 | NORTH
1850 | ROANOKE1 | NORTH
1851 | ROANOKE1 | NORTH
1852 | ROANOKE2 | NORTH
1853 | ROANOKE2 | NORTH
1854 | ROANOKE1 | NORTH
1855 | ALLIANCE | NORTH
1856 | KELLER1T | NORTH
1857 | MCPHERSN | NORTH
1858 | PEDANRD_ | NORTH
1859 | EAGLEMNT | NORTH
1860 | EAGLEMNT | NORTH
1861 | EAGLEMNT | NORTH
1862 | EAGLEMNT | NORTH
1863 | EAGLEMNT | NORTH
1866 | ELIZCRK | NORTH
1868 | WLFHMDPT | NORTH
1869 | BENBRK_A | NORTH
1870 | BENBRK_B | NORTH
1873 | BENBRK_5 | NORTH
1874 | BENBRK_A | NORTH
1875 | BENBRK_B | NORTH
1876 | WLFHOLW_ | NORTH
1877 | WLFHOLW_ | NORTH
1878 | WLFHOLW_ | NORTH
1879 | WLFHOLW_ | NORTH
1880 | ROCKYCRK | NORTH
1881 | ROCKYCRK | NORTH
1882 | EVRMAN_W | NORTH
1883 | EVRMAN_A | NORTH
1884 | EVRMAN_B | NORTH
1885 | EVRMNTIE | NORTH
1886 | EVRMAN_E | NORTH
1887 | EVRMNTIE | NORTH
1888 | DECRDOVA | NORTH
1889 | DECRDOVA | NORTH
1890 | DECRDOVA | NORTH
1891 | DECRDOVA | NORTH
1892 | DECRDOVA | NORTH
1893 | DECRDOVA | NORTH
1894 | DECRDOVA | NORTH
1895 | DECRDOVA | NORTH
1898 | COMCHEPK | NORTH
1899 | COMCHEPK | NORTH
1900 | COMCHPKW | NORTH
1902 | JHNSONSW | NORTH
1904 | WEBB3_5 | NORTH
1905 | GRIFFTH_ | NORTH
1906 | VENUS_S5 | NORTH
1907 | VENUS_N5 | NORTH
1908 | VENUS3_8 | NORTH
1909 | VENUS1_8 | NORTH
1910 | VENUS2_8 | NORTH
1911 | WEBB1_5 | NORTH
1912 | MAYFLDN_ | NORTH
1913 | MAYFLDN_ | NORTH
1914 | MAYFLDS_ | NORTH
1916 | LIGGETTA | NORTH
1917 | SHRYTAP_ | NORTH
1918 | SHRYAUTO | NORTH
1919 | SHRY_A8 | NORTH
1920 | SHRY_B8 | NORTH
1921 | LIGGETTA | NORTH
1922 | LIGGETT_ | NORTH
1923 | LIGGETTA | NORTH
1924 | LIGGETT_ | NORTH
1925 | LIGGETTA | NORTH
1926 | LIGGETT_ | NORTH
1927 | LIGGETT_ | NORTH
1928 | LIGGETT_ | NORTH
1929 | CENTURY1 | NORTH
1930 | CENTURY3 | NORTH
1931 | COURTLND | NORTH
1932 | KENNDALE | NORTH
1934 | SHRYAUTO | NORTH
1935 | SYCMRCRK | NORTH
1936 | MDLTHELP | NORTH
1937 | MDLTHELP | NORTH
1938 | MDLTHELP | NORTH
1939 | MDLTHELP | NORTH
1940 | MDLTHELP | NORTH
1941 | MDLTHELP | NORTH
1942 | MDLTHELP | NORTH
1943 | MDLTHELP | NORTH
1944 | MDLTHELP | NORTH
1945 | HANDLEY_ | NORTH
1946 | HANDLEY_ | NORTH
1947 | HANDLEY_ | NORTH
1948 | HANDLEY_ | NORTH
1949 | HANDLEY_ | NORTH
1950 | HANDLEYC | NORTH
1951 | HANDLEYD | NORTH
1952 | HANDLEY_ | NORTH
1955 | CALMONT1 | NORTH
1956 | CALMONT1 | NORTH
1957 | SAGINAW1 | NORTH
1958 | SAGINAW1 | NORTH
1961 | NMAIN1_8 | NORTH
1962 | ALCON1_8 | NORTH
1963 | ALCON2_8 | NORTH
1964 | NMAIN1_9 | NORTH
1967 | FRSTHILL | NORTH
1968 | FRSTHILL | NORTH
1970 | HIGHL_E_ | NORTH
1972 | LEW_JNS_ | NORTH
1984 | ARGYLE1_ | NORTH
1985 | CORINTH1 | NORTH
1986 | KRUM_T8 | NORTH
1987 | KRUM_8 | NORTH
1988 | VALVIEW_ | NORTH
1989 | KRUM_9 | NORTH
1990 | KRUM_P8 | NORTH
1993 | ARCO1_8 | NORTH
1994 | KRUGRVL1 | NORTH
1996 | ATMEL1_T | NORTH
1997 | ATMEL2_T | NORTH
1998 | ATMEL1_8 | NORTH
1999 | ATMEL2_8 | NORTH
2001 | IRVNORTH | NORTH
2002 | IRVBELT1 | NORTH
2003 | IRVBELT1 | NORTH
2004 | IRVBELT2 | NORTH
2006 | IRVVALVW | NORTH
2009 | DFW_SW_8 | NORTH
2010 | TRIGAS1_ | NORTH
2011 | TRIGAS_8 | NORTH
2014 | COPPELTP | NORTH
2015 | COPPELL_ | NORTH
2016 | EULESS_8 | NORTH
2017 | COPELL_S | NORTH
2018 | WROANOKE | NORTH
2019 | KIMBALL1 | NORTH
2020 | STHLAKE1 | NORTH
2021 | GV_BALL1 | NORTH
2022 | DFW_NW_8 | NORTH
2023 | KIMBALL2 | NORTH
2024 | MCKAMYRD | NORTH
2025 | MCKAMY_T | NORTH
2026 | CLYVIL1_ | NORTH
2027 | BEARCK1_ | NORTH
2028 | CLYVIL2_ | NORTH
2029 | CHRYGRV_ | NORTH
2030 | FLWRMND_ | NORTH
2031 | FLWRMNDS | NORTH
2033 | KLR_MAG1 | NORTH
2034 | KLR_MAG2 | NORTH
2035 | BEARCK3_ | NORTH
2036 | KELLER2_ | NORTH
2037 | WPKELLR1 | NORTH
2038 | WPKELLR2 | NORTH
2039 | MEADPRK1 | NORTH
2040 | MEADPRK2 | NORTH
2041 | SMITHFD1 | NORTH
2042 | SMITHFD2 | NORTH
2043 | WATAGAN_ | NORTH
2044 | WATAGAS_ | NORTH
2045 | WATAGA1_ | NORTH
2046 | WATAGA2_ | NORTH
2047 | HALTOM1_ | NORTH
2048 | GEMINI2_ | NORTH
2049 | GEMINI1_ | NORTH
2050 | BEDFORD1 | NORTH
2051 | BD_WDSN1 | NORTH
2052 | BD_WDSN2 | NORTH
2053 | IRVBELT2 | NORTH
2054 | IRVING1_ | NORTH
2055 | IRVGRNT1 | NORTH
2062 | AZLE1_8 | NORTH
2065 | EMCS1_8 | NORTH
2066 | ROSEN1_T | NORTH
2067 | ROSEN2_T | NORTH
2068 | ROSEN1_8 | NORTH
2069 | ROSEN2_8 | NORTH
2070 | BLUEMD2_ | NORTH
2071 | BLUEMD1_ | NORTH
2075 | WAGROBT1 | NORTH
2077 | FOSLCRK1 | NORTH
2085 | SANSOM1_ | NORTH
2086 | SANSOM2_ | NORTH
2087 | WHILL1_8 | NORTH
2088 | WHILL2_8 | NORTH
2089 | WHTSTLMN | NORTH
2090 | HERTG_D | NORTH
2091 | HERTG3_8 | NORTH
2092 | HERTG2_8 | NORTH
2093 | HERTG1_9 | NORTH
2094 | GEN_DYN1 | NORTH
2098 | HALTOM2_ | NORTH
2099 | RICHLN1_ | NORTH
2100 | RICHLN2_ | NORTH
2101 | SPRNGDL1 | NORTH
2102 | SPRNGDL2 | NORTH
2103 | RANDL_W_ | NORTH
2104 | RANDL_E_ | NORTH
2105 | RANDL1_8 | NORTH
2106 | RANDL2_8 | NORTH
2109 | WHITE1_T | NORTH
2110 | WHITE2_T | NORTH
2111 | WHITE1_8 | NORTH
2112 | WHITE2_8 | NORTH
2113 | TRINITY1 | NORTH
2114 | TRINITY3 | NORTH
2115 | HURSTN_8 | NORTH
2116 | HURSTS_8 | NORTH
2117 | DAVIS_T8 | NORTH
2121 | EULESS_S | NORTH
2123 | PIPELIN1 | NORTH
2124 | INT_AIR1 | NORTH
2125 | INT_AIR2 | NORTH
2128 | WATSON1_ | NORTH
2133 | BRKHLW1_ | NORTH
2134 | BRKHLW2_ | NORTH
2135 | BRKHLW1_ | NORTH
2136 | BRKHLW2_ | NORTH
2137 | GRT_SW1_ | NORTH
2138 | GRT_SW2_ | NORTH
2139 | GEN_MOT1 | NORTH
2140 | GEN_MOT2 | NORTH
2141 | EXECPKWY | NORTH
2142 | EXECPKWY | NORTH
2146 | AM_MFG_T | NORTH
2147 | AM_MFG1_ | NORTH
2148 | SPRNGDL_ | NORTH
2150 | CURRIE1_ | NORTH
2151 | BLACKSTN | NORTH
2152 | CARSWELL | NORTH
2157 | DENTN_AV | NORTH
2158 | DUVAL1_9 | NORTH
2159 | BRYN_AV_ | NORTH
2160 | BRYN_AV_ | NORTH
2161 | MCDONUGH | NORTH
2164 | HEMPHILL | NORTH
2166 | EPDC_D | NORTH
2167 | AYERS1_8 | NORTH
2168 | EPDC_ADM | NORTH
2169 | EPDC_STH | NORTH
2170 | EPDC_FRN | NORTH
2172 | MISLTOE1 | NORTH
2173 | MISLTOE3 | NORTH
2174 | HORNE1_8 | NORTH
2175 | HORNE2_8 | NORTH
2176 | FARON1_8 | NORTH
2177 | FARON2_8 | NORTH
2178 | EPDC1_8 | NORTH
2179 | EPDC2_8 | NORTH
2180 | EPDC3_8 | NORTH
2182 | BRYTIRV1 | NORTH
2183 | BRYTIRV2 | NORTH
2184 | WDGWD_N_ | NORTH
2185 | WDGWD_S_ | NORTH
2186 | WDGWD1_8 | NORTH
2187 | WDGWD2_8 | NORTH
2188 | PAFFRD1_ | NORTH
2189 | PAFFRD2_ | NORTH
2190 | EDGECLF1 | NORTH
2191 | EDGECLF2 | NORTH
2192 | ROGERS1_ | NORTH
2193 | ROGERS2_ | NORTH
2194 | ALCON1_T | NORTH
2195 | ALCON2_T | NORTH
2196 | PRIMRSE1 | NORTH
2197 | PRIMRSE3 | NORTH
2204 | CRESSON1 | NORTH
2205 | CROWLEY1 | NORTH
2208 | MANSFLD_ | NORTH
2209 | BURLESON | NORTH
2210 | JOSHUA_8 | NORTH
2211 | ROLLHL1_ | NORTH
2212 | ROLLHL2_ | NORTH
2213 | TX_STEEL | NORTH
2214 | ROLLHL1_ | NORTH
2215 | ROLLHL2_ | NORTH
2216 | TRWDRLHL | NORTH
2219 | BWN_TAT_ | NORTH
2220 | TATE_W_T | NORTH
2221 | TATE_E_T | NORTH
2222 | TATESPG1 | NORTH
2223 | TATESPG3 | NORTH
2224 | OAKHILL1 | NORTH
2225 | OAKHILL2 | NORTH
2226 | OAKHILL1 | NORTH
2227 | OAKHILL2 | NORTH
2232 | BOWEN2_T | NORTH
2233 | BOWEN2_8 | NORTH
2234 | VILGCRK1 | NORTH
2239 | DAVIS1_8 | NORTH
2240 | DAVIS2_8 | NORTH
2241 | ENNS_W_8 | NORTH
2245 | LAKEWD1_ | NORTH
2246 | LAKEWD2_ | NORTH
2247 | PANTEGO1 | NORTH
2248 | BOWEN1_8 | NORTH
2250 | BOWEN1_T | NORTH
2251 | ARLGTON1 | NORTH
2252 | ARLGTON2 | NORTH
2257 | PARKROW1 | NORTH
2258 | PARKROW2 | NORTH
2259 | LTV1_8 | NORTH
2260 | POLY_AM1 | NORTH
2262 | GRANDPR1 | NORTH
2265 | GP_WEST1 | NORTH
2270 | SHDYGRV1 | NORTH
2271 | IRVHUNT1 | NORTH
2272 | BIG3_GP_ | NORTH
2273 | IRVHUNT1 | NORTH
2274 | DALWRTH1 | NORTH
2275 | BIG3_GP_ | NORTH
2276 | IRVHUNT2 | NORTH
2277 | DCRDVA_D | NORTH
2278 | CMPKSTUP | NORTH
2279 | CLEBRNSW | NORTH
2280 | CLEBRN_N | NORTH
2281 | GODLEY_8 | NORTH
2283 | AIRLIQD_ | NORTH
2290 | CLEBRN_8 | NORTH
2291 | CLEBRN_W | NORTH
2294 | KEENE_8 | NORTH
2297 | ALVARADO | NORTH
2298 | ALVARADO | NORTH
2300 | CHAPSTL_ | NORTH
2301 | CHAPSTLF | NORTH
2302 | CHAPSTLF | NORTH
2304 | CHAPSTLM | NORTH
2305 | AIRPRD_T | NORTH
2306 | AIRPRD1_ | NORTH
2307 | MDLTHTXI | NORTH
2308 | MDLTH_S_ | NORTH
2309 | WAX_NW_8 | NORTH
2310 | MDLTHTXI | NORTH
2311 | MDLTH_N_ | NORTH
2312 | TRAILWD_ | NORTH
2313 | MDLTH_N_ | NORTH
2314 | MDLTHBOX | NORTH
2315 | WAX_PMP2 | NORTH
2316 | MG_IND_T | NORTH
2317 | STERRETT | NORTH
2318 | STERRETT | NORTH
2319 | WAX_PMP1 | NORTH
2320 | WAX_N_8 | NORTH
2321 | WAX_8 | NORTH
2322 | BARDWELL | NORTH
2323 | MG_IND_8 | NORTH
2324 | ENNS_S_8 | NORTH
2325 | ENNS_8 | NORTH
2326 | ENNS_SE_ | NORTH
2327 | TRUMBULL | NORTH
2328 | RED_OAK1 | NORTH
2329 | ENNSSW_8 | NORTH
2330 | CRISP1_8 | NORTH
2331 | ENNS_PMP | NORTH
2332 | TELICO_P | NORTH
2335 | WAX_9 | NORTH
2336 | FORESTON | NORTH
2337 | ITALY_9 | NORTH
2338 | MILFRDEX | NORTH
2339 | MILFRDEX | NORTH
2340 | MELSSA_P | NORTH
2342 | FERRISSW | NORTH
2343 | WAX_OCF_ | NORTH
2344 | PALMER_9 | NORTH
2345 | ENNS_9 | NORTH
2347 | RICETPL_ | NORTH
2348 | RICE_REA | NORTH
2349 | ROCKHILL | NORTH
2350 | CELINASE | NORTH
2351 | INDIA1_9 | NORTH
2352 | RNRTPL_W | NORTH
2353 | RNRTPL_E | NORTH
2354 | RNRTPL1_ | NORTH
2355 | RNRTPL1_ | NORTH
2356 | RNRDPL_N | NORTH
2357 | RNRDPL_S | NORTH
2358 | RNRDPL_1 | NORTH
2359 | RNRDPL1_ | NORTH
2360 | CRLTN_NW | NORTH
2361 | CRLTN_NW | NORTH
2362 | CRLTN_NW | NORTH
2363 | CRLTN_NW | NORTH
2364 | COLLIN1_ | NORTH
2365 | COLLIN2_ | NORTH
2366 | WILSNCRK | NORTH
2367 | NTHLK_1T | NORTH
2368 | ROLATER2 | NORTH
2369 | ROLATER1 | NORTH
2370 | COLLINSS | NORTH
2371 | COLLIN_1 | NORTH
2372 | COLLINSS | NORTH
2373 | ANNASW_5 | NORTH
2374 | ANNASW_8 | NORTH
2376 | HEBRN_P8 | NORTH
2377 | AUSRNCH2 | NORTH
2378 | AUSRNCH1 | NORTH
2381 | NTHLK1_G | NORTH
2382 | NTHLK2_G | NORTH
2383 | NTHLK3_G | NORTH
2385 | NTHLK_S8 | NORTH
2386 | NTHLK_N8 | NORTH
2387 | HACKBRY1 | NORTH
2388 | HACKBRY1 | NORTH
2389 | IRV_VR1_ | NORTH
2390 | IRV_VR1_ | NORTH
2393 | IRV_VR2_ | NORTH
2394 | IRVLBJ_W | NORTH
2395 | IRVLBJ_E | NORTH
2398 | WLEVEE1_ | NORTH
2399 | WLEVEE_E | NORTH
2400 | WLEVEE_W | NORTH
2401 | LKHB_W8 | NORTH
2402 | LKHB_E8 | NORTH
2403 | LKHB_1T8 | NORTH
2404 | NORWD_1T | NORTH
2405 | NORWDPL_ | NORTH
2406 | NORWD1_5 | NORTH
2407 | NORWDPL_ | NORTH
2408 | NORWD1_8 | NORTH
2409 | NORWD2_8 | NORTH
2410 | NORWD_1T | NORTH
2411 | MTCK_W8 | NORTH
2412 | MTCK_E8 | NORTH
2413 | MTCK6_G | NORTH
2414 | MTCK7_G | NORTH
2415 | MTCK_1T8 | NORTH
2416 | MTCK1_9 | NORTH
2417 | MTCK8_G | NORTH
2418 | MTCK2_G | NORTH
2419 | MTCK3_G | NORTH
2420 | CHILSW1_ | NORTH
2421 | CHILSW_S | NORTH
2422 | CHILSW_N | NORTH
2423 | NORWD_2T | NORTH
2424 | DESSW1_8 | NORTH
2425 | DESPKV1_ | NORTH
2426 | GLNHGHTS | NORTH
2427 | WATMLL_W | NORTH
2428 | WATMLL_E | NORTH
2429 | WATMLL_E | NORTH
2430 | WATMLL_W | NORTH
2431 | DESSW1_5 | NORTH
2432 | TRICRN1_ | NORTH
2433 | SGVLSW1_ | NORTH
2434 | SGVLSW1_ | NORTH
2435 | WATMLL_1 | NORTH
2437 | FRNY1_5 | NORTH
2438 | FRNY1_8 | NORTH
2439 | CNVLSW_W | NORTH
2440 | PARKD_1T | NORTH
2441 | PRCKSW1_ | NORTH
2442 | PARKDB1_ | NORTH
2444 | PARKD1_9 | NORTH
2445 | PARKDB2_ | NORTH
2450 | CNVLSW_E | NORTH
2451 | LKHB1_G | NORTH
2452 | LKHB2_G | NORTH
2453 | CNVLSW1_ | NORTH
2456 | KRKPK_E8 | NORTH
2457 | KRKPK_W8 | NORTH
2458 | KRKPK_1T | NORTH
2459 | KRKPK_2T | NORTH
2460 | ROYSE3_8 | NORTH
2461 | ROYSE_N5 | NORTH
2462 | ROYSE2_8 | NORTH
2463 | ROYSE2_9 | NORTH
2471 | ROYSE_A8 | NORTH
2472 | ROYSE_B8 | NORTH
2473 | ROYSE1_8 | NORTH
2474 | ROYSE1_T | NORTH
2478 | ROYSE_S5 | NORTH
2479 | WLEVEE_1 | NORTH
2480 | WLEVEE_2 | NORTH
2481 | ELEVEE_W | NORTH
2482 | ELEVEE_E | NORTH
2483 | ROYSE3_5 | NORTH
2486 | CCRST_9 | NORTH
2487 | DENDR_E8 | NORTH
2488 | DENDR_W8 | NORTH
2489 | DENDR1_9 | NORTH
2490 | DENDR2_9 | NORTH
2491 | FSHCRK1_ | NORTH
2492 | FSHCRK1_ | NORTH
2493 | CCRST_W8 | NORTH
2494 | CCRST_E8 | NORTH
2495 | CCRST_1T | NORTH
2509 | ALLENSW_ | NORTH
2510 | ALLENSW_ | NORTH
2511 | ALLENSW1 | NORTH
2512 | ALLENSW2 | NORTH
2513 | ALLENSW1 | NORTH
2514 | ALLENSW2 | NORTH
2515 | LEBNON_P | NORTH
2516 | MCDERMT_ | NORTH
2517 | BRIDGES_ | NORTH
2518 | COLONY_8 | NORTH
2519 | CRLTNFRK | NORTH
2520 | ANNAGCEC | NORTH
2521 | PL_COIT2 | NORTH
2522 | PL_TENNY | NORTH
2523 | PL_TENNY | NORTH
2524 | PL_COIT1 | NORTH
2525 | PL_CUSTR | NORTH
2526 | PL_CUSTR | NORTH
2527 | STONEYPT | NORTH
2528 | ANNASW_T | NORTH
2529 | MCKNY1_8 | NORTH
2530 | MCKNY_SW | NORTH
2531 | ALLEN1_8 | NORTH
2532 | MCKNY_TI | NORTH
2533 | ALLEN_N1 | NORTH
2535 | CRLTNUF1 | NORTH
2536 | CRLTNUF2 | NORTH
2537 | CRLTN1_8 | NORTH
2538 | MONETY1_ | NORTH
2539 | MONETY2_ | NORTH
2540 | CROWN1_8 | NORTH
2541 | CROWN2_8 | NORTH
2542 | HENSTL1T | NORTH
2543 | HENSTL1_ | NORTH
2544 | CHAMBVLE | NORTH
2546 | MCKNY2_8 | NORTH
2547 | MCKNY_SW | NORTH
2548 | ALLEN_N2 | NORTH
2549 | ALLEN2_8 | NORTH
2550 | LASCOL1_ | NORTH
2551 | LASCOL2_ | NORTH
2552 | IRVNE1_8 | NORTH
2553 | MCKNYWHT | NORTH
2555 | CRLTNJSY | NORTH
2558 | CRLTNTAR | NORTH
2559 | CRLTNTAR | NORTH
2560 | MCKNY_TI | NORTH
2561 | MCKNYWHT | NORTH
2562 | CRLTNRMD | NORTH
2564 | N_PARK4_ | NORTH
2565 | N_PARK3_ | NORTH
2566 | CUSTER1_ | NORTH
2567 | CUSTER2_ | NORTH
2569 | ADSN1_8 | NORTH
2571 | CRLTNCC1 | NORTH
2576 | ADSN1T_8 | NORTH
2577 | ADSN2T_8 | NORTH
2578 | CRLTNE_8 | NORTH
2580 | ELMFKN1_ | NORTH
2581 | ELMFKN2_ | NORTH
2582 | FBGILS1_ | NORTH
2583 | FB1_8 | NORTH
2586 | ELMFK1T_ | NORTH
2587 | ELMFK2T_ | NORTH
2588 | ELMFK1_8 | NORTH
2589 | ELMFK2_8 | NORTH
2590 | NLKPMP1T | NORTH
2591 | NLKPMP1_ | NORTH
2595 | AIRLIQD1 | NORTH
2596 | ALPHA1_8 | NORTH
2597 | ALPHA2_8 | NORTH
2606 | AIRLIQD1 | NORTH
2607 | WALNT1T_ | NORTH
2608 | WALNT1_8 | NORTH
2609 | WALNT2T_ | NORTH
2610 | WALNT2_8 | NORTH
2611 | KNLTR2T_ | NORTH
2612 | KNLTR1T_ | NORTH
2613 | KNLTR2_8 | NORTH
2614 | KNLTR1_8 | NORTH
2615 | PSTNTH1_ | NORTH
2616 | PSTNTH2_ | NORTH
2617 | MDWCK1_8 | NORTH
2618 | MDWCK2_8 | NORTH
2623 | FRNKFD1_ | NORTH
2624 | FRNKFD2_ | NORTH
2627 | BLTLIN1_ | NORTH
2628 | BLTLIN2_ | NORTH
2633 | TIDPL1_8 | NORTH
2634 | TIDPL2_8 | NORTH
2636 | SCHDRD1_ | NORTH
2637 | SCHDRD2_ | NORTH
2638 | COIT2_8 | NORTH
2639 | COIT1_8 | NORTH
2640 | JUDD1T_8 | NORTH
2642 | JUDD1_8 | NORTH
2647 | CENEXP1_ | NORTH
2648 | CENEXP2_ | NORTH
2651 | BANDRA1T | NORTH
2652 | BANDRA2T | NORTH
2653 | BANDRA1_ | NORTH
2654 | BANDRA2_ | NORTH
2657 | NTHHVN_W | NORTH
2658 | NTHHVN_E | NORTH
2659 | NTHHVN_1 | NORTH
2660 | WELCH1_8 | NORTH
2661 | WELCH2_8 | NORTH
2662 | MARSH1_8 | NORTH
2663 | MARSH2_8 | NORTH
2664 | SPRNGCRK | NORTH
2668 | SPRNGCRK | NORTH
2671 | PL_ARCO_ | NORTH
2673 | PL_WEST_ | NORTH
2674 | PL_8 | NORTH
2675 | W_PL_TI2 | NORTH
2676 | W_PL_TI1 | NORTH
2677 | PL_ALMA_ | NORTH
2678 | PL_PARKR | NORTH
2679 | W_PL_TI1 | NORTH
2680 | W_PL_TI2 | NORTH
2683 | RICH1_8 | NORTH
2684 | RICH_SV_ | NORTH
2685 | RICHCLLN | NORTH
2686 | RICHCLLN | NORTH
2687 | PL_JUPTR | NORTH
2688 | ROMJUARZ | NORTH
2689 | RICH_SC_ | NORTH
2690 | RICH_E_8 | NORTH
2691 | PL_SHILO | NORTH
2692 | LAVNPMP2 | NORTH
2693 | WYLIE_P8 | NORTH
2694 | LAVON1_8 | NORTH
2695 | LAVNPMP1 | NORTH
2696 | MURPHY1_ | NORTH
2697 | NW_WYLIE | NORTH
2698 | RICH_WH_ | NORTH
2699 | FORSTV1_ | NORTH
2700 | GARLW1_8 | NORTH
2701 | GARL1_8 | NORTH
2702 | RCKWL_8 | NORTH
2705 | GDELMGRV | NORTH
2707 | PRNCETON | NORTH
2708 | CLIMAX_P | NORTH
2710 | RCKWL_E1 | NORTH
2711 | RCKWL_S1 | NORTH
2712 | FORNEY_W | NORTH
2713 | BLACKLAN | NORTH
2715 | TERRL_N_ | NORTH
2716 | NW_TERRL | NORTH
2717 | NW_TERRL | NORTH
2718 | TERRL_N_ | NORTH
2719 | AIRCO_T8 | NORTH
2720 | AIRCO_8 | NORTH
2721 | TERRLSW_ | NORTH
2722 | TERRLSW_ | NORTH
2723 | ROSEHILL | NORTH
2724 | KAUFMN_8 | NORTH
2725 | OAKGROVE | NORTH
2726 | KEMP_S_8 | NORTH
2727 | CRANDALL | NORTH
2728 | KAUFMN_S | NORTH
2729 | MUNSON1_ | NORTH
2730 | QUINLAN_ | NORTH
2731 | TERRL_S1 | NORTH
2732 | MARSHLL_ | NORTH
2733 | RCKWL_AL | NORTH
2735 | DALRCKRD | NORTH
2736 | ROWLETT_ | NORTH
2739 | GRLBTWN_ | NORTH
2740 | GRLDBTWN | NORTH
2742 | MSQTN1T_ | NORTH
2743 | SCYENE1T | NORTH
2744 | SCYENE2T | NORTH
2745 | SCYENE1_ | NORTH
2746 | SCYENE2_ | NORTH
2747 | THRNE1T_ | NORTH
2748 | JMLLER1_ | NORTH
2750 | THRNE1_8 | NORTH
2751 | THRNE2_8 | NORTH
2752 | MSQTFR1_ | NORTH
2754 | MSQTW1_8 | NORTH
2756 | MSQTE1_8 | NORTH
2759 | MSQTWE1_ | NORTH
2762 | PRCK2_8 | NORTH
2763 | PRCK1_8 | NORTH
2765 | MSQTTE1_ | NORTH
2766 | MSQTN1_8 | NORTH
2767 | MESQTE1T | NORTH
2769 | ESIDE1T_ | NORTH
2770 | ESIDE1_8 | NORTH
2771 | ESIDE2T_ | NORTH
2772 | ESIDE2_8 | NORTH
2775 | MSQT1_8 | NORTH
2776 | BCHSPG1T | NORTH
2777 | BCHSPG1_ | NORTH
2779 | LAWSON1_ | NORTH
2780 | MRSNLN1_ | NORTH
2781 | MRSNLN2_ | NORTH
2782 | MRSN_E8 | NORTH
2783 | MRSN_W8 | NORTH
2784 | LOMBRY1_ | NORTH
2785 | LOMBRY2_ | NORTH
2786 | LKMT1T_8 | NORTH
2787 | LKMT2T_8 | NORTH
2788 | LKMT1_8 | NORTH
2789 | LKMT2_8 | NORTH
2792 | MAPLE2_9 | NORTH
2793 | COLVLE2_ | NORTH
2794 | MRSN_1T8 | NORTH
2795 | MRSN_2T8 | NORTH
2796 | EPCNT1T_ | NORTH
2797 | EPCNT2T_ | NORTH
2798 | EPCNT1_8 | NORTH
2799 | EPCNT2_8 | NORTH
2800 | REGRW1_8 | NORTH
2801 | REGRW2_8 | NORTH
2804 | TRA1_8 | NORTH
2805 | IRVHUNT2 | NORTH
2806 | 800NET_D | NORTH
2807 | 900NET_D | NORTH
2808 | 8009001_ | NORTH
2809 | 8009002_ | NORTH
2810 | 8009003_ | NORTH
2811 | CHNLR1_8 | NORTH
2812 | CHNLR2_8 | NORTH
2813 | RECCRS1_ | NORTH
2814 | RECCRS2_ | NORTH
2815 | AMELIA1_ | NORTH
2816 | AMELIA2_ | NORTH
2817 | MAPLE1_8 | NORTH
2818 | COLVLE1_ | NORTH
2819 | REAGAN1_ | NORTH
2820 | REAGAN2_ | NORTH
2821 | LEMMON1_ | NORTH
2822 | LEMMON2_ | NORTH
2823 | UTSWMC1_ | NORTH
2824 | UTSWMC2_ | NORTH
2828 | LMOALT2_ | NORTH
2829 | LMOALT1_ | NORTH
2832 | WDAL2T_8 | NORTH
2833 | WDAL2_8 | NORTH
2836 | TRA2_8 | NORTH
2837 | CALUMT2T | NORTH
2838 | CALUMT2_ | NORTH
2842 | DEALEY1_ | NORTH
2845 | WDAL1_8 | NORTH
2846 | WMRLDN1_ | NORTH
2849 | DAVST1T_ | NORTH
2850 | DAVST1_8 | NORTH
2851 | TPC1_8 | NORTH
2852 | CALUMT1_ | NORTH
2857 | DRAGON2_ | NORTH
2858 | DRAGON1_ | NORTH
2859 | FLYNN_N8 | NORTH
2860 | FLYNN_S8 | NORTH
2861 | NNET1_8 | NORTH
2862 | NNET2_8 | NORTH
2863 | NNET3_8 | NORTH
2864 | FARMNT1_ | NORTH
2865 | FARMNT2_ | NORTH
2866 | NNET_D | NORTH
2868 | ARMSTG1_ | NORTH
2869 | ARMSTG2_ | NORTH
2873 | WNET_D | NORTH
2874 | WNET1_8 | NORTH
2875 | WNET2_8 | NORTH
2876 | WNET3_8 | NORTH
2882 | GRNVL_W8 | NORTH
2883 | GRNVL_E8 | NORTH
2884 | BLKWEL1_ | NORTH
2885 | BLKWEL2_ | NORTH
2886 | JENKNS1_ | NORTH
2887 | JENKNS2_ | NORTH
2890 | MTLDA1_8 | NORTH
2891 | MTLDA2_8 | NORTH
2894 | ABRAMS1_ | NORTH
2895 | ABRAMS2_ | NORTH
2896 | LAWTHR1_ | NORTH
2897 | LAWTHR2_ | NORTH
2898 | HSKEL1T_ | NORTH
2899 | HSKEL1_8 | NORTH
2900 | HSKEL2_8 | NORTH
2902 | ENET_D | NORTH
2903 | ENET1_8 | NORTH
2904 | ENET2_8 | NORTH
2905 | ENET3_8 | NORTH
2906 | NNET1T_8 | NORTH
2907 | BRYNST1_ | NORTH
2908 | BRYNST2_ | NORTH
2913 | WHTRCK1_ | NORTH
2914 | WHTRCK2_ | NORTH
2915 | EZACH1_8 | NORTH
2916 | EZACH2_8 | NORTH
2917 | CNVL1_8 | NORTH
2918 | CNVL2_8 | NORTH
2919 | GARLDPL1 | NORTH
2920 | GARLDPL2 | NORTH
2921 | PLRD1_8 | NORTH
2922 | PLRD2_8 | NORTH
2923 | LKHLS1T_ | NORTH
2924 | LKHLS2T_ | NORTH
2925 | LKHLS1_8 | NORTH
2926 | LKHLS2_8 | NORTH
2927 | FAIROK1_ | NORTH
2928 | FAIROK2_ | NORTH
2929 | FORSTV2T | NORTH
2930 | FORSTV2_ | NORTH
2931 | JUDD2_8 | NORTH
2934 | DUCKCK1T | NORTH
2935 | DUCKCK1_ | NORTH
2936 | LKHBPMP_ | NORTH
2939 | STAUG1T_ | NORTH
2940 | SARGT_3T | NORTH
2941 | SARGT_4T | NORTH
2944 | STAUG1_8 | NORTH
2945 | LKJN1_8 | NORTH
2946 | SARGT1_5 | NORTH
2947 | SARGT_1T | NORTH
2948 | SARGT_S8 | NORTH
2949 | SARGT_N8 | NORTH
2950 | SARGT_2T | NORTH
2951 | STAUG2T_ | NORTH
2952 | PLGRV2T_ | NORTH
2953 | PLGRV2_8 | NORTH
2954 | MURDCK1T | NORTH
2955 | MURDCK1_ | NORTH
2956 | STAUG2_8 | NORTH
2957 | LKJN2_8 | NORTH
2960 | PLGRV1T_ | NORTH
2961 | PLGRV1_8 | NORTH
2962 | MURDCK2T | NORTH
2963 | MURDCK2_ | NORTH
2964 | HUTCH1_8 | NORTH
2965 | SSWWT1T_ | NORTH
2966 | SSWWT1_8 | NORTH
2969 | OAKLND1T | NORTH
2970 | OAKLND1_ | NORTH
2971 | OAKLND2_ | NORTH
2972 | SUTHLD1_ | NORTH
2973 | SUTHLD2_ | NORTH
2974 | INDUST_W | NORTH
2975 | INDUST_1 | NORTH
2976 | INDUST_E | NORTH
2977 | WALLST1_ | NORTH
2981 | CMPTON1_ | NORTH
2982 | CMPTON2_ | NORTH
2983 | WALLST2_ | NORTH
2984 | BUNTIN1_ | NORTH
2985 | BUNTIN2_ | NORTH
2986 | SMPST2T_ | NORTH
2987 | SMPST2_8 | NORTH
2988 | SMPST1_8 | NORTH
2989 | SCLFPMP1 | NORTH
2990 | CMPWSD2_ | NORTH
2992 | STHTN1_8 | NORTH
2993 | STHTN2_8 | NORTH
2994 | LVBRD1T_ | NORTH
2995 | LVBRD1_8 | NORTH
2997 | WATMLL_2 | NORTH
2999 | DVIL1_8 | NORTH
3004 | WMRLD2_8 | NORTH
3009 | HERTG3_T | NORTH
3010 | HERTG2_T | NORTH
3011 | HERTG1_T | NORTH
3014 | CKRELL1_ | NORTH
3015 | CKRELL2_ | NORTH
3016 | HMPTN1_8 | NORTH
3017 | HMPTN2_8 | NORTH
3018 | POLK1T_8 | NORTH
3019 | POLK2T_8 | NORTH
3020 | POLK1_8 | NORTH
3021 | POLK2_8 | NORTH
3022 | DAVST2_8 | NORTH
3023 | SOKCF1_8 | NORTH
3024 | SOKCF2_8 | NORTH
3032 | LVBRD2T_ | NORTH
3035 | LVBRD2_8 | NORTH
3042 | WMRLD1_8 | NORTH
3043 | LTV1_9 | NORTH
3044 | LTV2_9 | NORTH
3046 | EGLFD1T_ | NORTH
3048 | EGLFD1_8 | NORTH
3049 | EGLFD2_8 | NORTH
3050 | SORCEY1_ | NORTH
3051 | SORCEY2_ | NORTH
3052 | DVILS1_8 | NORTH
3053 | CHILTPL_ | NORTH
3054 | CHCLRKRD | NORTH
3055 | CHCLRKRD | NORTH
3056 | CHCLRKRD | NORTH
3057 | CHILTPL3 | NORTH
3058 | CHILTPL4 | NORTH
3059 | DESHPR1_ | NORTH
3060 | DESPLR1_ | NORTH
3066 | LNCST1_8 | NORTH
3067 | WITTRD1_ | NORTH
3076 | SGVL1_8 | NORTH
3077 | KLEBRG1T | NORTH
3078 | KLEBRG1_ | NORTH
3079 | SSWWT2T_ | NORTH
3080 | SSWWT2_8 | NORTH
3081 | SSWWT_P9 | NORTH
3083 | WILMER1_ | NORTH
3084 | WILMER1_ | NORTH
3097 | MARTLAKE | NORTH
3098 | MARTLAKE | NORTH
3099 | MARTLAKE | NORTH
3100 | MARTINLK | NORTH
3102 | TYLERGND | NORTH
3103 | SHAMBRGR | NORTH
3104 | SHAMBRGR | NORTH
3105 | ELKTON_5 | NORTH
3106 | ELKTON_8 | NORTH
3107 | STRYKER_ | NORTH
3108 | STRYKER_ | NORTH
3109 | STRYKER_ | NORTH
3110 | STRYKER_ | NORTH
3112 | SMRFLDMT | NORTH
3114 | PALTALCO | NORTH
3116 | MTENTRPR | NORTH
3117 | LUFKNSS_ | NORTH
3118 | LUFKNSS_ | NORTH
3119 | NACOGDSE | NORTH
3120 | NACOGDSE | NORTH
3123 | TRINDAD1 | NORTH
3124 | TRINDAD2 | NORTH
3125 | TDADTMOD | NORTH
3126 | TRINIDAD | NORTH
3127 | TRINIDAD | NORTH
3128 | TRINIDAD | NORTH
3130 | FOREGROV | NORTH
3131 | FOREGROV | NORTH
3133 | RICHLND1 | NORTH
3134 | RICHLND2 | NORTH
3139 | TYLERWES | NORTH
3140 | TYLERWES | NORTH
3141 | TYLERNW_ | NORTH
3142 | TYLERNW_ | NORTH
3143 | TYLERSE_ | NORTH
3144 | OVERTON_ | NORTH
3145 | JAXVLNTA | NORTH
3146 | JAXVLNOR | NORTH
3147 | TROUPSS_ | NORTH
3148 | TROUPSS_ | NORTH
3149 | MTSELMAN | NORTH
3150 | TROUPMTR | NORTH
3151 | TROUP_9 | NORTH
3152 | ARPCHIPR | NORTH
3153 | ARP_9 | NORTH
3154 | DIBOLSP_ | NORTH
3155 | DIBOLL_8 | NORTH
3160 | DIALVILL | NORTH
3161 | DIALVILL | NORTH
3162 | RUSK_9 | NORTH
3167 | ENTERPRI | NORTH
3168 | IRONBRTA | NORTH
3169 | IRONBRG_ | NORTH
3170 | EMORY_8 | NORTH
3171 | EMORYNOR | NORTH
3173 | EXPMTR_8 | NORTH
3174 | CANTNSW_ | NORTH
3175 | CANTON_8 | NORTH
3176 | MABANK_8 | NORTH
3177 | EUSTACE_ | NORTH
3178 | EUSTCSE_ | NORTH
3181 | EDGEWOOD | NORTH
3182 | EDGEWOOD | NORTH
3183 | VAN_8 | NORTH
3184 | PRIMROSE | NORTH
3185 | IRONBRG_ | NORTH
3187 | IRNBRGTA | NORTH
3188 | WILLSPNT | NORTH
3189 | BTSTARTA | NORTH
3190 | BRITSTAR | NORTH
3191 | DUCKCVTA | NORTH
3192 | DUCKCOVE | NORTH
3196 | TYLERSWE | NORTH
3197 | TYLERSW_ | NORTH
3198 | TYLRKLLY | NORTH
3201 | LINDALE_ | NORTH
3202 | SWANTWO_ | NORTH
3203 | LNDALTAP | NORTH
3204 | TYLERPIP | NORTH
3205 | HIDAWYLK | NORTH
3207 | TYLER_9 | NORTH
3208 | DELEKTAP | NORTH
3209 | DELEK1_8 | NORTH
3210 | TYLERNE_ | NORTH
3211 | TYLERE_8 | NORTH
3212 | TYLROMNR | NORTH
3213 | TYLERGE_ | NORTH
3214 | DELEKTAP | NORTH
3215 | DELEK2_8 | NORTH
3218 | TYLERS_8 | NORTH
3219 | TYLRBUL_ | NORTH
3221 | GRESHAM_ | NORTH
3222 | TEASELVL | NORTH
3224 | TEASELMT | NORTH
3227 | WHITEHSE | NORTH
3230 | SWINYTWN | NORTH
3231 | OVERTON_ | NORTH
3234 | TYLERSW_ | NORTH
3235 | CHADLER_ | NORTH
3236 | BRNSBORO | NORTH
3238 | ATHENS_8 | NORTH
3239 | ATHENS_9 | NORTH
3240 | MURCHISN | NORTH
3241 | JAXVLSTA | NORTH
3242 | JAXVLWTA | NORTH
3243 | JAXWEST_ | NORTH
3244 | JAXVL_9 | NORTH
3245 | REYNLDST | NORTH
3247 | ATHENSTA | NORTH
3248 | ATHNSNWT | NORTH
3249 | BEAUMNTA | NORTH
3250 | BEAUMONT | NORTH
3251 | FLINTSUB | NORTH
3252 | JAXVL1SS | NORTH
3253 | JAXVLSW_ | NORTH
3254 | JAXVL2SS | NORTH
3255 | FRANKSTN | NORTH
3256 | POYNOR_9 | NORTH
3260 | NIPAKTAP | NORTH
3261 | NIPAK_8 | NORTH
3262 | CEDRCREK | NORTH
3263 | CEDRCKPU | NORTH
3264 | SEVENPTS | NORTH
3267 | MALAKOFF | NORTH
3269 | WILOWSP_ | NORTH
3270 | CAROLSPG | NORTH
3271 | PALSTNS_ | NORTH
3272 | PALESTNE | NORTH
3273 | PALESTNE | NORTH
3274 | MONTALBA | NORTH
3276 | MALAKOFF | NORTH
3277 | MSSYLAKE | NORTH
3278 | LAKEVIEW | NORTH
3279 | LONGLKTA | NORTH
3280 | LONGLAKE | NORTH
3281 | TENNCLNY | NORTH
3282 | BLACKFOT | NORTH
3283 | BUTLERMT | NORTH
3284 | BETO_8 | NORTH
3285 | ELKHART_ | NORTH
3286 | GRAPELND | NORTH
3289 | CROCKETT | NORTH
3290 | ELKGUFTA | NORTH
3291 | SLOCUMTA | NORTH
3292 | SLOCUM_9 | NORTH
3293 | ELKGULF_ | NORTH
3296 | NECHESRI | NORTH
3299 | CUSHING_ | NORTH
3300 | CUSHSE_8 | NORTH
3303 | NACGDCHS | NORTH
3310 | NACOGNOR | NORTH
3311 | NACOSFA_ | NORTH
3312 | CHIRENO_ | NORTH
3314 | NACOGSW_ | NORTH
3315 | NACOGSOU | NORTH
3316 | NACOGST_ | NORTH
3319 | HERTYNOR | NORTH
3320 | HUNTNGTN | NORTH
3321 | ZAVPMPTA | NORTH
3323 | ETOILE_8 | NORTH
3326 | LUFKINE_ | NORTH
3327 | DIBOLET_ | NORTH
3328 | LUFKINS_ | NORTH
3329 | LUFPRSTA | NORTH
3330 | LUFPRSHG | NORTH
3331 | DIBOLWTA | NORTH
3332 | HUDSON_8 | NORTH
3333 | LUFTXFND | NORTH
3334 | TXFNDRY_ | NORTH
3340 | LUFKIN_8 | NORTH
3341 | CNTLANG_ | NORTH
3342 | BAYOULC_ | NORTH
3343 | DOUGLAS_ | NORTH
3346 | CHAMPNTA | NORTH
3347 | CHAMPION | NORTH
3348 | CHAMPION | NORTH
3349 | TMPLINLA | NORTH
3350 | KENNARD_ | NORTH
3351 | BEREA_8 | NORTH
3353 | EXPLRPIP | NORTH
3354 | CROCKETT | NORTH
3355 | GRPLMGTA | NORTH
3356 | GRPLNMAG | NORTH
3357 | PLSNTSPG | NORTH
3358 | CENTVILL | NORTH
3380 | BIGBRN__ | NORTH
3381 | BBRN_1G | NORTH
3382 | BBRN_2G | NORTH
3390 | JEWETT_S | NORTH
3391 | JEWETT_N | NORTH
3392 | JEWETT1_ | NORTH
3393 | JEWETT1_ | NORTH
3394 | JEWETTA_ | NORTH
3396 | NUCOR_ST | NORTH
3400 | TWIN_OAK | NORTH
3402 | LAKE_CRK | NORTH
3403 | THOUSE_1 | NORTH
3404 | THOUSE_2 | NORTH
3405 | THOUSE__ | NORTH
3406 | ELM_MOTT | NORTH
3407 | ELM_MOTT | NORTH
3408 | ELM_MOTT | NORTH
3409 | LAKE_CRK | NORTH
3410 | LAKE_CRK | NORTH
3411 | LKCK_POD | NORTH
3412 | TEMP_PEC | SOUTH
3413 | TEMPSSLT | SOUTH
3414 | TEMP_SS_ | SOUTH
3415 | TEMP_SS_ | SOUTH
3416 | LAKE_CRK | NORTH
3417 | LAKE_CRK | NORTH
3418 | LCTMOD_1 | NORTH
3419 | LCTMOD_2 | NORTH
3420 | TEMP_PEC | SOUTH
3421 | SCOTWHIT | SOUTH
3422 | KILL_SS_ | SOUTH
3423 | KILL_SS_ | SOUTH
3425 | BELLCTY_ | SOUTH
3426 | KILELMR1 | SOUTH
3427 | KILELMR2 | SOUTH
3428 | KILL S | SOUTH
3429 | SANDOW__ | SOUTH
3430 | SANDOW1_ | SOUTH
3431 | SANDOW1_ | SOUTH
3432 | SANDOW_4 | SOUTH
3434 | BAYLOR_T | NORTH
3435 | BAYLOR1_ | NORTH
3436 | WACO_W1_ | NORTH
3437 | WACO_W1_ | NORTH
3438 | WACO_E1_ | NORTH
3439 | WACO_E1_ | NORTH
3440 | MCGREGPH | NORTH
3441 | MCGREGPH | NORTH
3442 | LIPSITZ_ | NORTH
3452 | WACOLASA | NORTH
3453 | CHATF_P_ | NORTH
3454 | MONTFTSS | NORTH
3455 | CORS1_8 | NORTH
3456 | CORSWEST | NORTH
3457 | CORS_M0B | NORTH
3458 | CORS_MOB | NORTH
3459 | CORS_MAG | NORTH
3460 | CORS_GL_ | NORTH
3461 | CORSGLAS | NORTH
3462 | CORSGUAR | NORTH
3463 | CORSGUAR | NORTH
3464 | EQUIPIPE | NORTH
3466 | KERENS _ | NORTH
3467 | POWELL1_ | NORTH
3468 | CORS__9 | NORTH
3470 | BLOOMGRV | NORTH
3471 | BARRY1_9 | NORTH
3475 | CORSMGSS | NORTH
3477 | EUREKA_P | NORTH
3478 | NAVARRO1 | NORTH
3479 | NAVARRO1 | NORTH
3480 | MILDRED2 | NORTH
3483 | GOODLOE_ | NORTH
3486 | RICHLAND | NORTH
3487 | WRTHMPOD | NORTH
3488 | WTXGFPOD | NORTH
3489 | SIMSMAG1 | NORTH
3492 | FRESTONE | NORTH
3493 | TEAGUE1_ | NORTH
3496 | STSUPRCK | NORTH
3497 | STSUPRCK | NORTH
3498 | EUREKA1_ | NORTH
3499 | BLAKFTAP | NORTH
3500 | FARRAR_P | NORTH
3501 | SEATEAG_ | NORTH
3502 | SEATEAG1 | NORTH
3503 | FAIRWPOD | NORTH
3504 | FAIRFL_P | NORTH
3505 | BIGBRN_T | NORTH
3506 | BIGBRNM1 | NORTH
3507 | BIGBRNM2 | NORTH
3508 | WINKLER_ | NORTH
3509 | BBRN_OPN | NORTH
3510 | BBRN_OPN | NORTH
3511 | NAV_MILS | NORTH
3514 | HANEY_P_ | NORTH
3515 | HUBBARD_ | NORTH
3516 | CHATT_P_ | NORTH
3518 | BLUMPUMP | NORTH
3521 | BLANTON_ | NORTH
3522 | HILLBORO | NORTH
3523 | HILLBORO | NORTH
3524 | ABBOTT1_ | NORTH
3525 | WEST1_9 | NORTH
3526 | ROSSSINC | NORTH
3527 | ROSSSINC | NORTH
3528 | TOURS_T | NORTH
3529 | TOURSTXP | NORTH
3532 | ITASCA_9 | NORTH
3533 | FILE_SIN | NORTH
3534 | GRANDVGF | NORTH
3535 | FILE_SIN | NORTH
3536 | MAYPEARL | NORTH
3537 | GRANDVEW | NORTH
3538 | MAYPRLTX | NORTH
3543 | MERTENS1 | NORTH
3546 | WHITNEY_ | NORTH
3547 | ROGERS_P | NORTH
3550 | WACOBLMD | NORTH
3551 | WACO_NE1 | NORTH
3552 | WACO_N1_ | NORTH
3553 | WACO_NW1 | NORTH
3554 | HALLBURG | NORTH
3555 | THOUSE_T | NORTH
3556 | THOUSE1_ | NORTH
3559 | WACOCOLO | NORTH
3560 | WACO_S1_ | NORTH
3561 | WACOM1PT | NORTH
3562 | WACOM2PT | NORTH
3563 | WACOMM1T | NORTH
3564 | WACO_MM1 | NORTH
3565 | WACOMM2T | NORTH
3566 | WACO_MM2 | NORTH
3567 | ROBINSON | NORTH
3568 | ROBSONNW | NORTH
3570 | WACOTIRE | NORTH
3571 | WACOKATY | NORTH
3572 | WACOKATY | NORTH
3573 | KATYTNEW | NORTH
3574 | WACONCST | NORTH
3575 | WACONCST | NORTH
3577 | LORENA_P | NORTH
3578 | LORENA_9 | NORTH
3580 | EDDY1_9 | SOUTH
3581 | TROY1_9 | SOUTH
3583 | GATESVIL | NORTH
3584 | WACOATCO | NORTH
3585 | WACOATLS | NORTH
3586 | MCGREG1_ | NORTH
3587 | GATESVIL | NORTH
3588 | GROESBEC | NORTH
3589 | MCGREGHE | NORTH
3590 | WACOSANG | NORTH
3591 | WACOWOOD | NORTH
3592 | WACOATCO | NORTH
3593 | SPGVALLY | NORTH
3594 | MCGREG_T | NORTH
3595 | CHINASPG | NORTH
3597 | GROESBEC | NORTH
3598 | BEARGRAS | NORTH
3599 | AMERIGAS | NORTH
3600 | AMERIGAS | NORTH
3601 | OLETHA_P | NORTH
3602 | SCOTWHIT | SOUTH
3603 | BROWN1_9 | NORTH
3604 | WESTTXGF | NORTH
3605 | WORTHAM1 | NORTH
3606 | MEXIA2_T | NORTH
3607 | TEMPLE1_ | SOUTH
3608 | TEMPLE_N | SOUTH
3609 | TEMP_NW1 | SOUTH
3610 | BELTON1_ | SOUTH
3611 | TEMPLE_S | SOUTH
3612 | TEMP_SE1 | SOUTH
3613 | COOLG_SE | NORTH
3614 | MEXIA_NO | NORTH
3616 | KILLTAFD | SOUTH
3617 | NOLANVIL | SOUTH
3618 | HARK_HTS | SOUTH
3619 | KILLTAFT | SOUTH
3620 | KILCLARR | SOUTH
3621 | KILL1_8 | SOUTH
3622 | KILLPARK | SOUTH
3623 | KILLPARK | SOUTH
3624 | LBELTON_ | SOUTH
3625 | TEAGUE1_ | NORTH
3626 | KILLFTHD | SOUTH
3627 | KILLFH_T | SOUTH
3628 | KILLCLCK | SOUTH
3629 | KILL_FHW | SOUTH
3630 | COPPERCV | SOUTH
3631 | MEXIA1_1 | NORTH
3632 | MEXIA2_1 | NORTH
3633 | HARKHTS_ | SOUTH
3634 | GROES_SE | NORTH
3635 | TXUPOAG_ | SOUTH
3636 | TEMPTAYV | SOUTH
3637 | OTTO_SE1 | NORTH
3638 | MARL_SE1 | NORTH
3639 | MARLNOSE | NORTH
3640 | SALADO1_ | SOUTH
3641 | MARLIN_S | NORTH
3642 | LOTT_SE1 | NORTH
3643 | TEMP_SS_ | SOUTH
3644 | TEMPLE1_ | SOUTH
3645 | LITRIVER | SOUTH
3646 | HOLLAND_ | SOUTH
3647 | BARTLETT | SOUTH
3648 | GRANGER1 | SOUTH
3649 | TAYLOR1_ | SOUTH
3650 | ELGIN_SS | SOUTH
3651 | ELGIN_SS | SOUTH
3652 | COUPLAND | SOUTH
3653 | BRTLT_CB | SOUTH
3654 | RNDRCKSE | SOUTH
3655 | ELGIN1_9 | SOUTH
3658 | TAYLOR1_ | SOUTH
3659 | THORNDLN | SOUTH
3661 | SALTY_P_ | SOUTH
3665 | PFLGRVIL | SOUTH
3666 | HUTTOSS1 | SOUTH
3668 | RNDROCK1 | SOUTH
3669 | RNDRCKWH | SOUTH
3670 | RNDRCKNE | SOUTH
3671 | LOTT_TSE | NORTH
3672 | RNDRCK_S | SOUTH
3673 | TAYLOR_W | SOUTH
3674 | ELGIN_ET | SOUTH
3675 | ROGERS1A | SOUTH
3678 | ROCKDALE | SOUTH
3679 | TALBERTR | SOUTH
3681 | FAIRF_SE | NORTH
3682 | MILANO_M | SOUTH
3683 | MINERVA1 | SOUTH
3684 | MINERVA1 | SOUTH
3685 | CAMERON1 | SOUTH
3686 | ROCKDALN | SOUTH
3688 | JARRELL_ | SOUTH
3689 | MARAK1_9 | SOUTH
3697 | WACOMMP2 | NORTH
3698 | WACOMMP1 | NORTH
5000 | ALAMOTP | SOUTH
5001 | ALAMO_CM | SOUTH
5002 | AMD_SA | SOUTH
5003 | ANDERSON | SOUTH
5004 | AMD_TP | SOUTH
5005 | AUSTIN1 | SOUTH
5006 | AUSTIN2 | SOUTH
5011 | BALL_PRK | SOUTH
5020 | BANDERA | SOUTH
5025 | BRAUNIG_ | SOUTH
5026 | BRAUNIG_ | SOUTH
5027 | BRAUNIG_ | SOUTH
5028 | BRAUNIG_ | SOUTH
5030 | BRAUNIG_ | SOUTH
5035 | BECK_RD | SOUTH
5040 | BROADVEW | SOUTH
5045 | BROOKS | SOUTH
5050 | BUCKEYE | SOUTH
5055 | CAGNON_8 | SOUTH
5056 | CAGNON_5 | SOUTH
5075 | CAPITOL | SOUTH
5080 | CASTLE | SOUTH
5083 | CASTRVLL | SOUTH
5085 | CHAVANEA | SOUTH
5090 | CHULIE | SOUTH
5093 | CIBILOCR | SOUTH
5095 | COLISEUM | SOUTH
5110 | JT_DEELY | SOUTH
5111 | CALAVER_ | SOUTH
5112 | CALAVER_ | SOUTH
5125 | DEZAVALA | SOUTH
5130 | DRESDEN | SOUTH
5132 | EAGLECRK | SOUTH
5133 | ELMCREEK | SOUTH
5135 | ELMENDRF | SOUTH
5140 | ENCINO | SOUTH
5145 | FALLSCTY | SOUTH
5147 | FERN | SOUTH
5150 | FIVE_PTS | SOUTH
5155 | FLORESVI | SOUTH
5160 | FORT_SAM | SOUTH
5165 | FRATT | SOUTH
5170 | FRED_RD | SOUTH
5175 | GRANDVEW | SOUTH
5180 | GREEN_MT | SOUTH
5185 | GRISSOM | SOUTH
5187 | HAMWOLF | SOUTH
5190 | HARLANDA | SOUTH
5195 | HARMONY | SOUTH
5200 | HELOTES | SOUTH
5205 | HIGHLAND | SOUTH
5209 | HILLCTYE | SOUTH
5210 | HILLCTYW | SOUTH
5211 | HILLCTY_ | SOUTH
5220 | HOLLYWD | SOUTH
5225 | HONDO | SOUTH
5230 | HOWARD | SOUTH
5245 | KELLY | SOUTH
5249 | KIRBY2 | SOUTH
5250 | KIRBY | SOUTH
5255 | LAREDO1 | SOUTH
5257 | LASIERRA | SOUTH
5260 | LEON_CRK | SOUTH
5261 | LEON_STR | SOUTH
5262 | LEON_STR | SOUTH
5264 | LEON_LCP | SOUTH
5265 | LEON_LCP | SOUTH
5266 | LEON_LCP | SOUTH
5267 | LEON_LCP | SOUTH
5268 | LEON_LCP | SOUTH
5269 | LEON_LCP | SOUTH
5285 | LA_HTS_A | SOUTH
5286 | LA_HTS_B | SOUTH
5290 | LYTLE | SOUTH
5295 | MARBACH | SOUTH
5300 | MED_CTR | SOUTH
5305 | MEDINABS | SOUTH
5310 | MERIDA | SOUTH
5315 | NACDCHES | SOUTH
5325 | OLMOS | SOUTH
5332 | PARSONS | SOUTH
5335 | PEARSAL | SOUTH
5345 | PINN_RD | SOUTH
5350 | QUINTANA | SOUTH
5360 | RANDOLPH | SOUTH
5369 | SKYLIN_N | SOUTH
5370 | SKYLIN_S | SOUTH
5371 | SKYLINE_ | SOUTH
5385 | SOUTHSAN | SOUTH
5390 | SOMERSET | SOUTH
5395 | SOMMERS | SOUTH
5396 | CALAVER_ | SOUTH
5397 | CALAVER_ | SOUTH
5400 | SPRUCE | SOUTH
5401 | CALAVER_ | SOUTH
5410 | ST_HEDWG | SOUTH
5412 | STCKDALE | SOUTH
5415 | STONEGAT | SOUTH
5417 | STREICH | SOUTH
5418 | SUTHRLND | SOUTH
5419 | SWRI | SOUTH
5420 | TENTH_ST | SOUTH
5423 | TCC | SOUTH
5425 | TERREL_A | SOUTH
5426 | TERREL_B | SOUTH
5428 | TOYOTA | SOUTH
5430 | TX_RSRCH | SOUTH
5435 | TUTTLE | SOUTH
5436 | TUTTL_WB | SOUTH
5438 | TUTTL_WB | SOUTH
5439 | TUTTL_WB | SOUTH
5450 | USAA_ATP | SOUTH
5451 | USAA_A | SOUTH
5452 | USAA_BTP | SOUTH
5453 | USAA_B | SOUTH
5455 | USAA2TP | SOUTH
5456 | USAA2 | SOUTH
5460 | UTSA | SOUTH
5461 | UTSA_ATP | SOUTH
5462 | UTSA_BTP | SOUTH
5465 | VALLEY | SOUTH
5467 | VLSI | SOUTH
5470 | FAIRRA | SOUTH
5475 | VON_ROSE | SOUTH
5476 | BRA_AVR1 | SOUTH
5477 | BRA_AVR1 | SOUTH
5478 | BRA_AVR1 | SOUTH
5479 | AVR1_M | SOUTH
5485 | WALZEM | SOUTH
5490 | WSTSIDE | SOUTH
5500 | RAYBURN9 | SOUTH
5501 | RAYBURN1 | SOUTH
5502 | RAYBURN8 | SOUTH
5503 | RAYBURNG | SOUTH
5504 | NURSERYS | SOUTH
5505 | RAYBURNG | SOUTH
5506 | RAYBURNG | SOUTH
5508 | RAYBURNC | SOUTH
5509 | RAYBURNC | SOUTH
5510 | FORDTRAN | SOUTH
5511 | RAYBURNC | SOUTH
5512 | RAYBURNC | SOUTH
5513 | RAYBURNP | SOUTH
5514 | INEZSUB9 | SOUTH
5516 | ELTOROSW | SOUTH
5518 | ELTOROSW | SOUTH
5520 | ELTOROSU | SOUTH
5522 | EDNASUB9 | SOUTH
5525 | GANADOSW | SOUTH
5526 | GANADOSU | SOUTH
5528 | LOUISESU | SOUTH
5530 | ROUNDMOT | SOUTH
5532 | HILLJESU | SOUTH
5534 | ROUNDMOT | SOUTH
5536 | NADASUB9 | SOUTH
5538 | ELCAMPOS | SOUTH
5540 | PLAINVIE | SOUTH
5543 | INDSTRLP | SOUTH
5544 | DANEVANG | SOUTH
5546 | DANEVANG | SOUTH
5548 | DANEVANG | SOUTH
5549 | CLEMVILL | SOUTH
5550 | NCLEMVIL | SOUTH
5552 | SCLEMVIL | SOUTH
5554 | MARKHAMT | SOUTH
5556 | VANVLECK | HOUSTON
5558 | VANVLECK | HOUSTON
5560 | BAYCITYS | HOUSTON
5564 | SARGENTS | HOUSTON
5566 | FRANKLNC | HOUSTON
5568 | FRANKLNC | HOUSTON
5569 | TINTOPSU | SOUTH
5570 | PALACIOS | SOUTH
5571 | STRUCTUR | SOUTH
5573 | CARANCAH | SOUTH
5574 | OLIVIASW | SOUTH
5576 | OLIVIASU | SOUTH
5578 | LOLITASU | SOUTH
5580 | VANHUMBL | SOUTH
5582 | VANDERBL | SOUTH
5584 | VANDERBL | SOUTH
5586 | VANDERBL | SOUTH
5588 | REDBLUF | SOUTH
5590 | PLACEDOS | SOUTH
5591 | KAMEYSUB | SOUTH
5592 | PORTLAVA | SOUTH
5596 | PTOCONNO | SOUTH
5600 | LONETREE | SOUTH
5601 | AIRPORTS | SOUTH
5602 | TWINPINE | SOUTH
5603 | TWINPINE | SOUTH
5604 | HIGHLAND | SOUTH
5605 | WARBURTO | SOUTH
5606 | ALOESUB9 | SOUTH
5608 | MCFADDIN | SOUTH
5610 | REFUGIOS | SOUTH
5614 | BONNEVIE | SOUTH
5616 | TAFTSUB9 | SOUTH
5618 | SODVILLE | SOUTH
5620 | WSINTONS | SOUTH
5622 | WSINTONS | SOUTH
5626 | CALALLEN | SOUTH
5632 | RIVERSID | SOUTH
5634 | ROBSTOWN | SOUTH
5636 | CORPSCHR | SOUTH
5638 | CORPSCHR | SOUTH
5640 | DRISCOLL | SOUTH
5645 | RICARDOS | SOUTH
5646 | RIVIERAS | SOUTH
5648 | LOYOLASW | SOUTH
5650 | LOYOLASW | SOUTH
5652 | CENTRALS | SOUTH
5654 | SANDIEGO | SOUTH
5658 | ORANGEGR | SOUTH
5660 | ORANGEGR | SOUTH
5662 | ORANGEGR | SOUTH
5664 | AGUADULC | SOUTH
5666 | SANDIASU | SOUTH
5668 | MATHISSU | SOUTH
5672 | OLMOSSUB | SOUTH
5673 | BEEPRISO | SOUTH
5674 | BEEVILLE | SOUTH
5676 | GOLIADSW | SOUTH
5678 | SCHROEDE | SOUTH
5680 | LOOP463S | SOUTH
5684 | GEORGEWS | SOUTH
5685 | WGORGEWS | SOUTH
5686 | GEORGEWS | SOUTH
5688 | GEORGEWS | SOUTH
5690 | WGRGEWST | SOUTH
5695 | SIMMONSS | SOUTH
5696 | CALLIHAM | SOUTH
5697 | SCALLIHA | SOUTH
5698 | NCALLIHA | SOUTH
5699 | CHKCANPR | SOUTH
5700 | TILDENSU | SOUTH
5702 | SNMIGUEL | SOUTH
5704 | SNMIGUEL | SOUTH
5706 | SNMIGUEL | SOUTH
5708 | CHARLOTT | SOUTH
5710 | POTEETSU | SOUTH
5712 | OAKSSUB8 | SOUTH
5713 | OAKSSUB9 | SOUTH
5714 | PLEASANT | SOUTH
5716 | FASHINGS | SOUTH
5718 | ROSSVILL | SOUTH
5720 | COYCITYS | SOUTH
5722 | KENEDYSU | SOUTH
5723 | VERDISUB | SOUTH
5725 | PAWNEESW | SOUTH
5727 | PAWNEESW | SOUTH
5728 | FALCONHY | SOUTH
5729 | FALCONHY | SOUTH
5730 | FOURCORN | SOUTH
5732 | CHARCOSU | SOUTH
5735 | MIDFIELD | SOUTH
5736 | FANNINSU | SOUTH
5805 | QUIHISW9 | SOUTH
5806 | WESTBADE | SOUTH
5807 | CSTROVIL | SOUTH
5808 | CSTROVIL | SOUTH
5810 | BADERSUB | SOUTH
5811 | PEARSONS | SOUTH
5812 | SABINALS | SOUTH
5813 | PEARSONS | SOUTH
5814 | DHANISSU | SOUTH
5816 | HONDOSUB | SOUTH
5817 | FERRISSW | SOUTH
5818 | FERRISSU | SOUTH
5819 | HONDOCRE | SOUTH
5820 | UVALDESU | SOUTH
5821 | HONDOCRE | SOUTH
5822 | LEONASUB | SOUTH
5823 | UVALDESW | SOUTH
5824 | WSTUVALD | SOUTH
5827 | MOORESUB | SOUTH
5828 | DEVINESU | SOUTH
5830 | MOORESUB | SOUTH
5832 | FRIOTOWN | SOUTH
5836 | NBATESVI | SOUTH
5842 | DERBYSUB | SOUTH
5848 | SBATESVI | SOUTH
5849 | BATESVIL | SOUTH
5851 | BATESVIL | SOUTH
5852 | BIGFOOTS | SOUTH
5855 | CRYSTLCT | SOUTH
5856 | CRYSTLCT | SOUTH
5857 | DEVINESW | SOUTH
5858 | NATALIAS | SOUTH
5859 | TURTLECR | SOUTH
5860 | DILLEYSU | SOUTH
5861 | DILEYSWS | SOUTH
5863 | DILEYSWS | SOUTH
5864 | WCRYSTLC | SOUTH
5868 | BIGWELLS | SOUTH
5870 | BRUNDAGE | SOUTH
5872 | CARIZOSP | SOUTH
5876 | COTULLAS | SOUTH
5878 | HOLLANDS | SOUTH
5880 | FREERSUB | SOUTH
5883 | DOWNIESU | SOUTH
5885 | DOWNIESU | SOUTH
5887 | BRUNISUB | SOUTH
5888 | BRUNISUB | SOUTH
5890 | PEARSALL | SOUTH
5891 | PEARSALL | SOUTH
5892 | PEARSALL | SOUTH
5893 | PEARSALL | SOUTH
5895 | PEARSALL | SOUTH
5901 | MIGUEL 5 | SOUTH
5902 | MIGUEL 8 | SOUTH
5903 | SANMIGUE | SOUTH
5904 | MIGUESTR | SOUTH
5905 | MIGUESTR | SOUTH
5908 | SMIGLT1 | SOUTH
5909 | SMIGLT2 | SOUTH
5911 | STP_GN1_ | HOUSTON
5912 | STP_GN2_ | HOUSTON
5915 | SO_TEX__ | HOUSTON
5920 | WELSHDC1 | NORTH
5925 | DCEAST | NORTH
5930 | PWRPLT69 | SOUTH
5932 | SI_RAY9 | SOUTH
5933 | SI_RAY6 | SOUTH
5934 | SI_RAY5 | SOUTH
5935 | SI_RAY10 | SOUTH
5943 | LOMAALTA | SOUTH
5944 | CARBIDE | SOUTH
5946 | AIRPORT | SOUTH
5960 | MILHWY69 | SOUTH
5961 | LAREDO69 | SOUTH
5962 | LOMAALTA | SOUTH
5963 | TITAN | SOUTH
5964 | MILH_DUM | SOUTH
5965 | PALOALTO | SOUTH
6000 | SILVRTP1 | WEST
6001 | SAJT2A | WEST
6003 | BRNHRTP2 | WEST
6004 | ATTA2A | WEST
6005 | STAP2A | WEST
6006 | BRDY2A | SOUTH
6013 | TWB4TERT | WEST
6014 | SW_MESA4 | WEST
6015 | SWMESA4 | WEST
6016 | SWMESA | WEST
6019 | ORNNWPT4 | WEST
6021 | DSKY1_4 | WEST
6022 | DSKY1_T4 | WEST
6023 | ESTL2A | WEST
6024 | TURK2A | WEST
6028 | CHLD2A | WEST
6030 | CHLD4A | WEST
6031 | CH202A | WEST
6032 | CHIL2A | WEST
6033 | CHLD20TP | WEST
6035 | YUCCA2A | WEST
6041 | FLOMTP2A | WEST
6042 | FLOM2A | WEST
6044 | TURL2A | WEST
6048 | PAUL2A | WEST
6050 | LKPAULS4 | WEST
6051 | QUAN2A | WEST
6052 | ACME2A | WEST
6053 | KIRK2A | WEST
6056 | CHLC_VER | WEST
6057 | CHILE2WT | WEST
6058 | VERN2A | WEST
6060 | VERN4A | WEST
6061 | VRCP2A | WEST
6062 | SANT2A | WEST
6063 | SAND2A | WEST
6064 | VERS2A | WEST
6066 | VERS4A | WEST
6070 | GRAYBAC2 | WEST
6071 | GRBC2A | WEST
6072 | HARR2A | WEST
6075 | WAGR2A | WEST
6080 | TRUSEXN2 | WEST
6082 | CRWL2A | WEST
6084 | EXTR2A | WEST
6085 | TRUS2A | WEST
6086 | BENJTP2A | WEST
6087 | BENJ2A | WEST
6096 | NORTHDC7 | WEST
6097 | OKLA4A | WEST
6098 | OKLA4B | WEST
6100 | OKLA7A | WEST
6101 | OKLA7STR | WEST
6107 | MUND2A | WEST
6108 | MUNE2A | WEST
6110 | EMUNDY24 | WEST
6112 | GILL2A | WEST
6113 | KNXC2A | WEST
6114 | KNXR2A | WEST
6115 | ROCH2A | WEST
6117 | EMUNDY14 | WEST
6120 | RULE2A | WEST
6122 | HSKL2A | WEST
6123 | JOSS2A | WEST
6124 | HASTXTP2 | WEST
6125 | WEIN2A | WEST
6126 | TXHS2A | WEST
6131 | PADR2A | WEST
6132 | PADC2A | WEST
6133 | PADU2A | WEST
6135 | PADU4A | WEST
6140 | MATA2A | WEST
6141 | ROAR2A | WEST
6142 | AFTO2A | WEST
6143 | ESPU2A | WEST
6144 | MCADOO1A | WEST
6145 | MCADOO4A | WEST
6147 | GIRA2A | WEST
6148 | SPUR2A | WEST
6150 | SPUR4A | WEST
6151 | GIRA_TAP | WEST
6152 | DKEC2A | WEST
6153 | JATN2A | WEST
6154 | PEAC2A | WEST
6156 | ASPM2A | WEST
6158 | ASPM4A | WEST
6159 | PAIP2A | WEST
6160 | PAIP2STR | WEST
6161 | PAIP4A | WEST
6165 | CALCRKTP | WEST
6166 | CALI_CRK | WEST
6169 | PAIP4B | WEST
6170 | HASR2A | WEST
6171 | HSKELTP2 | WEST
6172 | STAM2A | WEST
6173 | CORN2A | WEST
6174 | HSKREAT2 | WEST
6175 | ANSN2A | WEST
6176 | ANSO2A | WEST
6177 | SWEN2A | WEST
6180 | RADM2A | WEST
6182 | HAMTXCO2 | WEST
6183 | HAMR2A | WEST
6184 | HAMTXTP2 | WEST
6185 | HAML2A | WEST
6186 | SHHA2A | WEST
6187 | CONA2A | WEST
6191 | EXSHRN4 | WEST
6192 | RONDTOP2 | WEST
6193 | PLST2A | WEST
6194 | RONDTPT2 | WEST
6195 | ROBY2A | WEST
6196 | ROTN2A | WEST
6197 | CLRM2A | WEST
6198 | CLARSUN2 | WEST
6202 | ALBNY_FD | WEST
6204 | WOOD2A | WEST
6205 | THRM2A | WEST
6206 | BUKB2A | WEST
6207 | ALBANY2A | WEST
6208 | HUB12A | WEST
6209 | MRAN2A | WEST
6210 | WCTMWD22 | WEST
6211 | ALBANYT2 | WEST
6212 | WCTMWD12 | WEST
6213 | HUB1_TAP | WEST
6214 | ALBANYT1 | WEST
6215 | ABRBRSN2 | WEST
6216 | BLF_CRK4 | WEST
6217 | FTPHPMP2 | WEST
6218 | NUGENTR2 | WEST
6219 | NUGE2A | WEST
6220 | FTFP2A | WEST
6221 | ABRC2A | WEST
6222 | FTPP4A | WEST
6223 | ABRC4A | WEST
6224 | ABNW2A | WEST
6225 | ABNW2B | WEST
6226 | ABEASTP | WEST
6228 | ABNW4A | WEST
6229 | CALHNTP | WEST
6230 | ABMULCE7 | WEST
6231 | MULBW RS | WEST
6232 | MULBE RS | WEST
6233 | ABMULSTR | WEST
6235 | ABMULCW7 | WEST
6236 | ABON2A | WEST
6237 | ONYS2A | WEST
6238 | EXHA2A | WEST
6239 | ABVT2A | WEST
6240 | ABVO2A | WEST
6241 | ELYT2A | WEST
6242 | MERK2A | WEST
6243 | CLFK2A | WEST
6244 | ABWALTP2 | WEST
6245 | ABRBPRS2 | WEST
6246 | MKLT2A | WEST
6247 | TRNT2A | WEST
6248 | HAWEXXN2 | WEST
6249 | DELT2A | WEST
6250 | DELK 2 | WEST
6251 | ELY9 | WEST
6252 | SCOTT9 | WEST
6253 | ABEC2A | WEST
6254 | ABMULSTR | WEST
6255 | ABEC4A | WEST
6256 | ABTT4A | WEST
6257 | ABRL4A | WEST
6258 | ABSO2A | WEST
6260 | ABSO4A | WEST
6261 | WYLE4A | WEST
6265 | ABDYES22 | WEST
6266 | ABDYTP22 | WEST
6267 | ABHT2A | WEST
6268 | ABDYTP12 | WEST
6269 | ABDYES12 | WEST
6270 | ABSH2A | WEST
6271 | ABMM2A | WEST
6272 | ABOV2A | WEST
6273 | ABDYTP32 | WEST
6274 | ABDYES32 | WEST
6275 | ABEA4A | WEST
6276 | ABEAST12 | WEST
6277 | ABEAST22 | WEST
6278 | ABPLTTP2 | WEST
6281 | ABWA2A | WEST
6282 | ABPG2A | WEST
6283 | ABOLMLT2 | WEST
6284 | ABWTGUT2 | WEST
6285 | ABWTXGU2 | WEST
6286 | ABOILML2 | WEST
6287 | MULBW RL | WEST
6288 | MULBE RL | WEST
6290 | ABMS4A | WEST
6291 | AILN2A | WEST
6292 | ABCC4A | WEST
6293 | ABCR4A | WEST
6295 | SRC1TERT | WEST
6300 | DENTONR2 | WEST
6301 | ABED2A | WEST
6302 | CLYM2A | WEST
6303 | WTU_DETP | WEST
6304 | CLYDMAG2 | WEST
6305 | CLYD2A | WEST
6306 | BAIR2A | WEST
6307 | PUTN2A | WEST
6308 | PUTN2STR | WEST
6309 | PUTN2A | WEST
6310 | PUTN2B | WEST
6311 | CISC2A | NORTH
6312 | PUT69 2 | WEST
6313 | POTOSI_T | WEST
6314 | POTOSI | WEST
6315 | SHARP TP | WEST
6316 | SHARP | WEST
6318 | POTTER | WEST
6324 | FTCHAD | WEST
6325 | CHAD4A | WEST
6326 | ROBRTSR2 | WEST
6327 | ABCG2A | WEST
6328 | TUSC2A | WEST
6329 | GLDBSK9 | WEST
6330 | HAPVAL2 | WEST
6331 | CLIM2A | WEST
6332 | HAPVALT2 | WEST
6333 | WINT2A | WEST
6334 | HATC2A | WEST
6335 | OAKC4A | WEST
6337 | BALEXXN2 | WEST
6338 | BALG2A | WEST
6340 | BALG4A | WEST
6341 | BALEXTP2 | WEST
6342 | NOVC2A | WEST
6343 | TALPATL2 | WEST
6344 | VALE2A | WEST
6345 | GLDBSKR2 | WEST
6346 | COLJ2A | WEST
6347 | COLETAP4 | WEST
6348 | COLEMAN4 | WEST
6349 | NOVICE9 | WEST
6350 | DRESSY9 | WEST
6351 | NICOLE4A | WEST
6352 | SANA_TAP | WEST
6353 | SANA2A | WEST
6355 | SANA4A | WEST
6356 | DRSY2A | WEST
6357 | CRPL2A | WEST
6358 | RIST2A | WEST
6360 | COLE_IVI | WEST
6361 | IVEYPMP4 | WEST
6362 | IVEYBST4 | WEST
6368 | HEXT 2 | SOUTH
6369 | PTRK2A | WEST
6370 | EOLATP2A | WEST
6371 | EOLA2A | WEST
6372 | EDEN2A | SOUTH
6373 | MENA2A | SOUTH
6375 | MENA4A | SOUTH
6376 | CRM1TP2A | SOUTH
6377 | CRM12A | SOUTH
6378 | BRDYSE 2 | SOUTH
6379 | BRDS2A | SOUTH
6380 | MELV2A | SOUTH
6381 | BRADYRE2 | SOUTH
6382 | BRADYTP2 | SOUTH
6383 | BRADY 2 | SOUTH
6384 | MCLC2A | SOUTH
6385 | EDENREA2 | SOUTH
6386 | CSSB2A | SOUTH
6387 | FREDPHIL | SOUTH
6389 | CTECMA2A | SOUTH
6391 | FRDN2A | SOUTH
6392 | PHMT2A | SOUTH
6393 | MASN2A | SOUTH
6394 | PHMA2A | SOUTH
6395 | MASNPH 2 | SOUTH
6396 | MASW2A | SOUTH
6397 | STRT2A | SOUTH
6398 | SHLO2A | SOUTH
6399 | KMJC2A | SOUTH
6400 | JUNC2A | SOUTH
6401 | MENPHTP2 | SOUTH
6402 | MENRDPH2 | SOUTH
6403 | SHELLON2 | SOUTH
6406 | TURKTRAK | WEST
6407 | TURKTRAK | WEST
6409 | VRBS2A | WEST
6410 | MILE2A | WEST
6411 | ROWE2A | WEST
6412 | HARI2A | WEST
6413 | VERIBST2 | WEST
6414 | BRONTE 2 | WEST
6416 | SAGT2A | WEST
6417 | STRLNG9 | WEST
6418 | ATBR2A | WEST
6419 | AMBR2A | WEST
6420 | ROBL2A | WEST
6421 | ESPENCT2 | WEST
6422 | EDIT2A | WEST
6423 | CEDH2A | WEST
6425 | CEDH4A | WEST
6426 | ESPENCE2 | WEST
6427 | SILR2B | WEST
6428 | SILR2A | WEST
6429 | SPADERN2 | WEST
6430 | SILV2A | WEST
6431 | SILVRTP2 | WEST
6432 | EXPE2A | WEST
6433 | SPRH2A | WEST
6434 | PANA2A | WEST
6435 | STER2A | WEST
6436 | STCO2A | WEST
6437 | CRBDTP 2 | WEST
6438 | CBDREA 2 | WEST
6439 | AMCO2A | WEST
6440 | AMOCO 2 | WEST
6441 | ORNT4A | WEST
6442 | SARC4A | WEST
6444 | SARC7A | WEST
6445 | CRMW5TP2 | WEST
6446 | CRMWD5 2 | WEST
6447 | PAULANN4 | WEST
6448 | SA_HILND | WEST
6449 | SACK4A | WEST
6450 | SACO2A | WEST
6451 | SARC7STR | WEST
6452 | SACO4A | WEST
6453 | SAST4A | WEST
6454 | SASO4A | WEST
6455 | SASL2A | WEST
6456 | SAJS2A | WEST
6457 | SAEM2A | WEST
6458 | CRM24A | WEST
6459 | CRM32A | WEST
6460 | CRM42A | WEST
6461 | CRMWD42 | WEST
6462 | SANO2A | WEST
6463 | SARC7STR | WEST
6464 | SANO4A | WEST
6465 | SAGC2A | WEST
6466 | SAWT2A | WEST
6467 | SAWA2A | WEST
6468 | SACH2A | WEST
6470 | SACH4A | WEST
6471 | SAAN2A | WEST
6473 | BENF4A | WEST
6477 | SAMF2A | WEST
6478 | SAPS2A | WEST
6479 | SAPS TIE | WEST
6480 | SAPS4B | WEST
6481 | SASH4A | WEST
6482 | SALD4A | WEST
6483 | SAPS4A | WEST
6484 | ANGORA2A | WEST
6488 | ROLLANS2 | WEST
6491 | PAW22A | WEST
6492 | PAVE4A | WEST
6493 | PAVEPAW4 | WEST
6494 | PAVEPAW2 | WEST
6495 | CRIS2A | WEST
6496 | AROT2A | WEST
6497 | HULD2A | WEST
6498 | LVOK2A | WEST
6500 | LIVEOAK4 | WEST
6503 | SHBA2A | WEST
6505 | ELDO2A | WEST
6506 | PAGE2A | WEST
6507 | MIDV2A | WEST
6508 | FMCK2A | WEST
6509 | SHBT2A | WEST
6510 | SONO2A | WEST
6511 | ATSO2A | WEST
6513 | SONR2A | WEST
6515 | SONR4A | WEST
6524 | MERTZON9 | WEST
6526 | MERR2A | WEST
6527 | SANW2A | WEST
6528 | TANK2A | WEST
6529 | MERT2A | WEST
6530 | BARN2A | WEST
6531 | BRNHRPH2 | WEST
6532 | BARNHCV2 | WEST
6533 | BGLK2A | WEST
6534 | BGLK2B | WEST
6535 | BGLK4A | WEST
6538 | TEXN2A | WEST
6539 | SHPO2A | WEST
6540 | SHPO_TAP | WEST
6541 | TEXONTP2 | WEST
6542 | ATLT2A | WEST
6543 | KEMPEXT2 | WEST
6544 | HUMT2A | WEST
6545 | POWF2A | WEST
6546 | PHBL_TAP | WEST
6547 | STRS2A | WEST
6548 | POWT2A | WEST
6549 | MIDW2A | WEST
6550 | FDRAN2A | WEST
6551 | OZNR2A | WEST
6552 | CROCKHT2 | WEST
6553 | PHBL2A | WEST
6554 | EXKE2A | WEST
6555 | ATLB2A | WEST
6556 | YATW_SW2 | WEST
6560 | OZONA 2 | WEST
6562 | FDRAN4A | WEST
6565 | ILLN2A | WEST
6568 | RGECBVIL | SOUTH
6572 | MDSC2A | WEST
6574 | MART2A | WEST
6575 | IRAN2A | WEST
6576 | DSCVYTP2 | WEST
6577 | SHEF2A | WEST
6578 | FTLCSTR2 | WEST
6580 | AIRP2A | WEST
6581 | ARPT2A | WEST
6583 | MESAVIEW | WEST
6584 | INDN4A | WEST
6585 | DSCVRY 2 | WEST
6586 | MCCAMY4 | WEST
6587 | SCROSS2 | WEST
6588 | SHLMESA2 | WEST
6589 | RANK2A | WEST
6590 | SHME2A | WEST
6591 | RANK4 2 | WEST
6592 | MCAM2A | WEST
6594 | SCRS2A | WEST
6597 | BOBCAT 2 | WEST
6598 | RIOP2A | WEST
6599 | BOBCAT T | WEST
6600 | CRNAIR T | WEST
6601 | RIOP4A | WEST
6603 | CRANTP2 | WEST
6604 | SAGE2A | WEST
6605 | CRANAIR2 | WEST
6606 | TXNMPL 2 | WEST
6607 | MCELROY2 | WEST
6608 | CRANGU12 | WEST
6609 | TXNMTP 2 | WEST
6610 | CRANGU22 | WEST
6611 | DUN22A | WEST
6613 | CRAN2A | WEST
6614 | DUNETAP2 | WEST
6627 | COMC4A | WEST
6628 | FTST2A | WEST
6630 | FTST4A | WEST
6632 | WDWRDTP4 | WEST
6633 | WOODWRD1 | WEST
6635 | KING_TAP | WEST
6636 | SNYDERW4 | WEST
6637 | SNYDERW1 | WEST
6639 | MCAN4A | WEST
6641 | SUNV2A | WEST
6642 | MAST2A | WEST
6643 | PECV2A | WEST
6645 | FTSW2A | WEST
6649 | VERH2A | WEST
6650 | CCRT2A | WEST
6651 | CCRK2A | WEST
6652 | SGSA2A | WEST
6653 | BARL2A | WEST
6655 | BARL4A | WEST
6656 | HACKBTAP | WEST
6657 | CR101TAP | WEST
6658 | MECPLNVW | WEST
6659 | SNTXTAP2 | WEST
6660 | SNTX12A | WEST
6661 | LONGWRTH | WEST
6663 | COCS2A | WEST
6665 | ALPR2A | WEST
6666 | ALPI2A | WEST
6667 | PAISANO2 | WEST
6668 | ALTUDA2A | WEST
6669 | PRSMNGAP | WEST
6676 | FTDA2A | WEST
6677 | VALT2A | WEST
6678 | ALMC2A | WEST
6680 | ALMC4A | WEST
6681 | MARF2A | WEST
6682 | CIEN2A | WEST
6683 | SHAF2A | WEST
6684 | PRES2A | WEST
6688 | CHINATI2 | WEST
6689 | BRYR2A | WEST
6690 | ATKN2A | WEST
6691 | ESPY2A | WEST
6692 | POND2A | WEST
6700 | DIBL WT4 | NORTH
6703 | SFIELD | NORTH
6705 | OWTN WT4 | NORTH
6707 | BSCM WT4 | NORTH
6709 | TSLVILLE | NORTH
6710 | SWTN WT4 | NORTH
6711 | OKWD WT4 | NORTH
6717 | CSNG WT4 | NORTH
6719 | CGSE WT4 | NORTH
6720 | SHNE WT4 | NORTH
6722 | OKRD WT4 | NORTH
6723 | HGTN WT4 | NORTH
6724 | ZVLA WT4 | NORTH
6726 | LFKN WT4 | NORTH
6727 | BYLC WT4 | NORTH
6736 | PLST WT4 | NORTH
6738 | CTVL WT4 | NORTH
6742 | TROUPWT2 | NORTH
6743 | WALNT | NORTH
6752 | OKLA0A | WEST
6754 | PTCREK2G | WEST
6769 | SRC2TERT | WEST
6771 | SABLUFF4 | WEST
6772 | ABIP4A | WEST
6773 | PCNBYU4A | WEST
6774 | SEGOVTP9 | SOUTH
6780 | OK1TERT | WEST
6788 | AMCETERT | WEST
6789 | AMCWTERT | WEST
6794 | PM1TERT | WEST
6800 | LIBTY RC | NORTH
6801 | ROSHILRC | NORTH
6802 | SHRLM RC | NORTH
6803 | BLUCRKRC | NORTH
6804 | WHTBR RC | NORTH
6806 | SHRWD RC | NORTH
6807 | DCKCVWRC | NORTH
6808 | SHERY RC | NORTH
6809 | BELLS RC | NORTH
6810 | GORDVLRC | NORTH
6811 | PNKHL RC | NORTH
6812 | DENSE RC | NORTH
6813 | ELMNTRC | NORTH
6814 | CHERY RC | NORTH
6815 | EXPLORRC | NORTH
6816 | WHTMD RC | NORTH
6817 | ETHELRC | NORTH
6818 | EVANALRC | NORTH
6819 | ANNA_RC | NORTH
6821 | I20SUBRC | NORTH
6822 | VAN ALRC | NORTH
6823 | KIOWARC | NORTH
6824 | RENOS RC | NORTH
6826 | ALHUB RC | NORTH
6830 | ECTOR RC | NORTH
6831 | ABLSPRRC | NORTH
6832 | MINTR RC | NORTH
6838 | WINDM RC | NORTH
6840 | BRKSTNRC | NORTH
6842 | COMON RC | NORTH
6844 | COOP RC | NORTH
6845 | CRNDL RC | NORTH
6846 | COPEN RC | NORTH
6847 | WINDMLRC | NORTH
6848 | BNHMLKRC | NORTH
6850 | WLF C RC | NORTH
6851 | NW WYLIC | NORTH
6852 | SULBF RC | NORTH
6853 | CLIMAX | NORTH
6854 | COMME RC | NORTH
6857 | COMMW RC | NORTH
6858 | COMBNTRC | NORTH
6859 | MARVIN R | NORTH
6861 | CUMBY RC | NORTH
6865 | FORNYWRC | NORTH
6867 | FRNYE RC | NORTH
6868 | COPVL RC | NORTH
6869 | SUNYPTRC | NORTH
6870 | MCKINWRC | NORTH
6871 | LNOK_RC | NORTH
6873 | MLSSA RC | NORTH
6874 | MCK121RC | NORTH
6875 | CHAMB RC | NORTH
6876 | MCKINERC | NORTH
6877 | STONYRC | NORTH
6878 | ALLEN RC | NORTH
6879 | PARKR RC | NORTH
6880 | LUCAS RC | NORTH
6881 | WYLIE RC | NORTH
6882 | WIELNDRC | NORTH
6883 | MSYLK RC | NORTH
6884 | QUINLNDR | NORTH
6885 | CHIES RC | NORTH
6886 | BLDSW RC | NORTH
6887 | CARTR RC | NORTH
6888 | WSTMNSNR | NORTH
6894 | ROSHILRC | NORTH
6896 | OAKGV RC | NORTH
6897 | NWTER RC | NORTH
6898 | TERRL RC | NORTH
6900 | KEMP RC | NORTH
6902 | TALTYRC | NORTH
6904 | COMBNRC | NORTH
6906 | RANDRC | NORTH
6908 | SCURYRC | NORTH
6909 | ALNN RC | NORTH
6910 | MSQT RC | NORTH
6911 | MESQT_RC | NORTH
6912 | COMMS RC | NORTH
6914 | EMORY RC | NORTH
6918 | TAWK RC | NORTH
6919 | ENTPR RC | NORTH
6920 | DCKCV RC | NORTH
6922 | COBSW RC | NORTH
6924 | POYNR RC | NORTH
6926 | SEVPT RC | NORTH
6928 | TOOL RC | NORTH
6930 | WILOW RC | NORTH
6932 | CRLSP RC | NORTH
6934 | MNTLB RC | NORTH
6935 | LKVEW RC | NORTH
6936 | STCYRDRC | NORTH
6937 | TUCKRRC | NORTH
6938 | MALKF RC | NORTH
6940 | MASSYRC | NORTH
6942 | NECHS RC | NORTH
6943 | CELINA R | NORTH
6944 | BUROWRC | NORTH
6948 | DENISNDM | NORTH
6949 | DENISNDM | NORTH
7000 | L_FERGUS | SOUTH
7004 | L_SIMGID | SOUTH
7005 | L_SIMGID | SOUTH
7006 | L_SIMGID | SOUTH
7007 | L_LOSTPI | SOUTH
7008 | L_LOSTPI | SOUTH
7009 | L_LOSTPI | SOUTH
7010 | L_FPPYD1 | SOUTH
7011 | L_FPPYD1 | SOUTH
7012 | L_FPPYD2 | SOUTH
7014 | L_HAYSEN | SOUTH
7015 | L_HAYSEN | SOUTH
7016 | L_HAYSEN | SOUTH
7017 | L_HAYSEN | SOUTH
7020 | L_AUSTPL | SOUTH
7022 | L_BUCHAN | SOUTH
7023 | L_BUCHAN | SOUTH
7024 | L_BUCHAN | SOUTH
7026 | L_INKSDA | SOUTH
7028 | L_MARBFA | SOUTH
7029 | L_MARBFA | SOUTH
7031 | L_MARSFO | SOUTH
7032 | L_MARSFO | SOUTH
7033 | L_MARSFO | SOUTH
7035 | L_WIRTZ_ | SOUTH
7036 | L_WIRTZ_ | SOUTH
7038 | L_DELAWA | WEST
7040 | L_AUSTRO | SOUTH
7042 | L_ZORN__ | SOUTH
7043 | L_HAYSEN | SOUTH
7044 | L_MARION | SOUTH
7045 | L_ZORN__ | SOUTH
7046 | L_KENDAL | SOUTH
7047 | L_GUADGE | SOUTH
7048 | L_GARFIE | SOUTH
7049 | L_MAHACR | SOUTH
7050 | L_CLEASP | SOUTH
7051 | L_RIONOG | SOUTH
7055 | L_FPPYD2 | SOUTH
7056 | L_FPPYD1 | SOUTH
7057 | L_FAYETT | SOUTH
7058 | L_SALEM_ | SOUTH
7060 | L_EBABSM | SOUTH
7061 | L_COPPCO | SOUTH
7062 | L_KEMPNE | SOUTH
7063 | L_NARUNA | SOUTH
7064 | L_LAMPAS | SOUTH
7066 | L_ADAMSV | SOUTH
7068 | L_EVANT_ | SOUTH
7070 | L_GOLDTH | SOUTH
7073 | L_GOLDTH | SOUTH
7074 | L_SASASW | SOUTH
7075 | L_TERRY_ | SOUTH
7076 | L_RICHSP | SOUTH
7078 | L_SANSAB | SOUTH
7080 | L_LOMETA | SOUTH
7082 | L_LAMPAS | SOUTH
7084 | L_GRAPMI | SOUTH
7087 | L_CORONA | SOUTH
7092 | L_BUCHAN | SOUTH
7093 | L_CORONA | SOUTH
7094 | L_INKSDA | SOUTH
7097 | L_BURNET | SOUTH
7100 | L_BURNET | SOUTH
7101 | L_CTECBU | SOUTH
7102 | L_SHERSH | SOUTH
7104 | L_WIRTZ_ | SOUTH
7107 | L_WIRTZ_ | SOUTH
7110 | L_WIRTZ_ | SOUTH
7111 | L_FLATRO | SOUTH
7112 | L_WIRTZ_ | SOUTH
7114 | L_CASTEL | SOUTH
7116 | L_SANDMO | SOUTH
7119 | L_PITSBU | SOUTH
7120 | L_PITSBU | SOUTH
7121 | L_SANDCR | SOUTH
7122 | L_ECKERT | SOUTH
7124 | L_NEBO__ | SOUTH
7126 | L_FERGUS | SOUTH
7127 | L_SANDCR | SOUTH
7128 | L_HORSBA | SOUTH
7130 | L_GILLES | SOUTH
7132 | L_GILLES | SOUTH
7133 | L_NIMITZ | SOUTH
7134 | L_WOLFCR | SOUTH
7136 | L_KERRST | SOUTH
7138 | L_KERRST | SOUTH
7140 | L_HARPRO | SOUTH
7142 | L_INGRAM | SOUTH
7143 | L_RIMROC | SOUTH
7144 | L_HUNT__ | SOUTH
7146 | L_VERDCR | SOUTH
7147 | L_KENDCT | SOUTH
7148 | L_MOUNTO | SOUTH
7149 | L_FREDER | SOUTH
7150 | L_KENDAL | SOUTH
7151 | L_CICO__ | SOUTH
7152 | L_KENDAL | SOUTH
7153 | L_WELFAR | SOUTH
7155 | L_COMFOR | SOUTH
7156 | L_CYPRCR | SOUTH
7158 | L_RAYMBA | SOUTH
7159 | L_RAYMBA | SOUTH
7160 | L_LEGION | SOUTH
7162 | L_TRAVIS | SOUTH
7168 | L_BOERNE | SOUTH
7169 | L_FAIROA | SOUTH
7170 | L_BERGHE | SOUTH
7171 | L_ANTLER | SOUTH
7172 | L_HENNE_ | SOUTH
7173 | L_RIVEOA | SOUTH
7174 | L_HENNE_ | SOUTH
7175 | L_HORTON | SOUTH
7176 | L_COMAL_ | SOUTH
7177 | L_HI46WE | SOUTH
7178 | L_MARION | SOUTH
7180 | L_ZORN__ | SOUTH
7181 | L_ZORN__ | SOUTH
7182 | L_MCCALA | SOUTH
7184 | L_MCCALA | SOUTH
7186 | L_RARO12 | SOUTH
7188 | L_REDWOO | SOUTH
7190 | L_HILLTO | SOUTH
7191 | L_SANMAR | SOUTH
7192 | L_SANMAR | SOUTH
7193 | L_STRAHA | SOUTH
7194 | L_REEDTA | SOUTH
7196 | L_CAMPGA | SOUTH
7197 | L_LEHIGH | SOUTH
7198 | L_LEHIGH | SOUTH
7200 | L_CANYON | SOUTH
7202 | L_HICROS | SOUTH
7204 | L_DUMPHI | SOUTH
7206 | L_DALE__ | SOUTH
7208 | L_COLTON | SOUTH
7212 | L_WOLFLA | SOUTH
7215 | L_LOCKHA | SOUTH
7216 | L_LOCKHA | SOUTH
7218 | L_MAGNME | SOUTH
7220 | L_LULIMA | SOUTH
7223 | L_LULING | SOUTH
7224 | L_LULING | SOUTH
7225 | L_HICKFO | SOUTH
7226 | L_CUSHMA | SOUTH
7228 | L_SEGUIN | SOUTH
7229 | L_SEGUWE | SOUTH
7230 | L_HARWOO | SOUTH
7231 | L_THOMPS | SOUTH
7232 | L_WAELDE | SOUTH
7235 | L_SWEETH | SOUTH
7236 | L_MOULTO | SOUTH
7237 | L_HENKAU | SOUTH
7238 | L_SHINER | SOUTH
7239 | L_WESER_ | SOUTH
7240 | L_FORDTR | SOUTH
7241 | L_YOAKUM | SOUTH
7242 | L_YOAKUM | SOUTH
7244 | L_CUERO_ | SOUTH
7245 | L_GONZAL | SOUTH
7246 | L_HALLET | SOUTH
7247 | L_FLATON | SOUTH
7248 | L_FLATON | SOUTH
7250 | L_ENGLE_ | SOUTH
7252 | L_SCHULE | SOUTH
7254 | L_WEIMAR | SOUTH
7257 | L_GLIDDE | SOUTH
7258 | L_GLIDDE | SOUTH
7263 | L_FRELSB | SOUTH
7269 | L_BELLSO | SOUTH
7270 | L_BELLSO | SOUTH
7271 | L_NEWBRE | SOUTH
7272 | L_WALLER | SOUTH
7273 | L_WILLSP | SOUTH
7274 | L_PLUM__ | SOUTH
7275 | L_RIVERS | SOUTH
7276 | L_LAGRAN | SOUTH
7278 | L_FAYEPL | SOUTH
7280 | L_FARIPU | SOUTH
7282 | L_FASHPU | SOUTH
7286 | L_FAYETT | SOUTH
7287 | L_BELLNO | SOUTH
7288 | L_WELLBR | SOUTH
7289 | L_SALEM_ | SOUTH
7291 | L_HIGH36 | SOUTH
7292 | L_BRENHA | SOUTH
7294 | L_BRENNO | SOUTH
7296 | L_PISEK_ | SOUTH
7297 | L_ROTOTA | SOUTH
7299 | L_ROUNTO | SOUTH
7302 | L_GIDDIN | SOUTH
7306 | L_WINCHE | SOUTH
7308 | L_PAIGE_ | SOUTH
7310 | L_SIMGID | SOUTH
7312 | L_WARDA_ | SOUTH
7314 | L_SMITHV | SOUTH
7315 | L_SMITHV | SOUTH
7318 | L_ALCRSW | SOUTH
7322 | L_BASTCI | SOUTH
7324 | L_BUTLER | SOUTH
7325 | L_MENDOZ | SOUTH
7326 | L_CAMPSW | SOUTH
7327 | L_ELTPTU | SOUTH
7328 | L_AUSTRO | SOUTH
7329 | L_WEBBER | SOUTH
7330 | L_MANOR_ | SOUTH
7331 | L_CEDAHI | SOUTH
7333 | L_HARRBR | SOUTH
7334 | L_MCNEIL | SOUTH
7335 | L_HOLATA | SOUTH
7336 | L_GILLCR | SOUTH
7339 | L_AUSTPL | SOUTH
7343 | L_GEORGE | SOUTH
7345 | L_GABRIE | SOUTH
7346 | L_GABRIE | SOUTH
7347 | L_RIVERY | SOUTH
7348 | L_MARBFA | SOUTH
7349 | L_LAKETP | SOUTH
7350 | L_MORMMI | SOUTH
7351 | L_STARCK | SOUTH
7352 | L_LAGOVI | SOUTH
7353 | L_VISTA_ | SOUTH
7354 | L_MARSFO | SOUTH
7355 | L_SEGOVI | SOUTH
7356 | L_MARSFO | SOUTH
7359 | L_MARSFO | SOUTH
7360 | L_MARSFO | SOUTH
7362 | L_MARSFO | SOUTH
7366 | L_CHIEBR | SOUTH
7386 | L_CAMPBO | NORTH
7387 | L_KUNITZ | WEST
7400 | L_SUNRBE | SOUTH
7402 | L_KINGS2 | SOUTH
7404 | L_KINGS1 | SOUTH
7406 | L_BLUFFT | SOUTH
7408 | L_DOSS__ | SOUTH
7410 | L_HARPER | SOUTH
7412 | L_LIVEOA | SOUTH
7413 | L_GOEHTA | SOUTH
7414 | L_GOEHLA | SOUTH
7415 | L_FREDER | SOUTH
7426 | L_LEAKEY | SOUTH
7428 | L_UTOPIA | SOUTH
7430 | L_MEDICI | SOUTH
7432 | L_MEDILA | SOUTH
7436 | L_PIPECR | SOUTH
7437 | L_PIPECR | SOUTH
7438 | L_BANDER | SOUTH
7439 | L_BANDER | SOUTH
7440 | L_TARPLE | SOUTH
7441 | L_MASOCR | SOUTH
7442 | L_TURTCR | SOUTH
7454 | L_TEXIND | SOUTH
7456 | L_LOP337 | SOUTH
7458 | L_GPI___ | SOUTH
7459 | L_GPISWI | SOUTH
7460 | L_SHERPO | SOUTH
7461 | L_WEIDER | SOUTH
7462 | L_FREIHE | SOUTH
7474 | L_GRANMO | SOUTH
7476 | L_PALEFA | SOUTH
7477 | L_PALEPE | SOUTH
7478 | L_PHJOCI | SOUTH
7479 | L_MILLER | SOUTH
7480 | L_MOUNTO | SOUTH
7482 | L_BLANCO | SOUTH
7484 | L_DEVIHI | SOUTH
7487 | L_CANYHY | SOUTH
7488 | L_SATTLE | SOUTH
7490 | L_CRANMI | SOUTH
7491 | L_HUNTER | SOUTH
7492 | L_FISCHE | SOUTH
7493 | L_DEVIHI | SOUTH
7496 | L_WIMBER | SOUTH
7498 | L_BUDA__ | SOUTH
7499 | L_BUDA__ | SOUTH
7500 | L_TURNER | SOUTH
7501 | L_GOFORT | SOUTH
7502 | L_KYLE__ | SOUTH
7504 | L_MANCHA | SOUTH
7506 | L_CEDAVA | SOUTH
7507 | L_FRIEND | SOUTH
7508 | L_CENTEX | SOUTH
7509 | L_RUTHER | SOUTH
7510 | L_MILRCR | SOUTH
7512 | L_DRIPSP | SOUTH
7513 | L_HENLY_ | SOUTH
7514 | L_BLANTA | SOUTH
7515 | L_ROHR__ | SOUTH
7516 | L_JOHNCI | SOUTH
7518 | L_FAIRLA | SOUTH
7520 | L_BERTRA | SOUTH
7521 | L_ANDICE | SOUTH
7522 | L_ANDICE | SOUTH
7523 | L_GLASSC | SOUTH
7524 | L_SEWARD | SOUTH
7525 | L_LEANDE | SOUTH
7526 | L_NAMELE | SOUTH
7527 | L_BLOCKH | SOUTH
7528 | L_GEOREA | SOUTH
7529 | L_WHITES | SOUTH
7530 | L_KENTST | SOUTH
7531 | L_BUTTER | SOUTH
7532 | L_GEORSO | SOUTH
7533 | L_BALCON | SOUTH
7534 | L_AVERRA | SOUTH
7538 | L_LAKEWA | SOUTH
7540 | L_BEECRE | SOUTH
7542 | L_SPICEW | SOUTH
7545 | L_HIGH32 | SOUTH
7546 | L_HIGH32 | SOUTH
7554 | L_MARTIN | SOUTH
7555 | L_BASTWE | SOUTH
7556 | L_BLUEBO | SOUTH
7557 | L_NEROTA | SOUTH
7558 | L_NEWROS | SOUTH
7559 | L_NEROPU | SOUTH
7560 | L_REDROC | SOUTH
7564 | L_GUYBUR | SOUTH
7565 | L_MILLCR | SOUTH
7567 | L_DEANVI | SOUTH
7570 | L_SANDHI | SOUTH
7571 | L_LEXING | SOUTH
7572 | L_GAYHIL | SOUTH
7573 | L_LYONS_ | SOUTH
7574 | L_CHAPHI | SOUTH
7576 | L_HILBIG | SOUTH
7577 | L_WELCOM | SOUTH
7586 | L_HALLGV | SOUTH
7588 | L_MOULGV | SOUTH
7590 | L_SHINGV | SOUTH
7592 | L_GONZGV | SOUTH
7594 | L_OTTINE | SOUTH
7596 | L_NASHCR | SOUTH
7598 | L_CAPOTE | SOUTH
7600 | L_SEGUIN | SOUTH
7602 | L_STMEIN | SOUTH
7604 | L_GERONI | SOUTH
7605 | L_MCQUEE | SOUTH
7606 | L_MCQUEE | SOUTH
7608 | L_CIBOLO | SOUTH
7609 | L_SCHUMA | SOUTH
7610 | L_SCHERT | SOUTH
7611 | L_PARKWA | SOUTH
7612 | L_NEWBER | SOUTH
7613 | L_OLMOSW | SOUTH
7614 | L_LAVERN | SOUTH
7615 | L_WILSON | SOUTH
7616 | L_NIXOGV | SOUTH
7617 | L_NIXON1 | SOUTH
7618 | L_SMILGO | SOUTH
7619 | L_OLMOSW | SOUTH
7620 | L_SMILEY | SOUTH
7622 | L_COST__ | SOUTH
7624 | L_LAKEWO | SOUTH
7625 | L_LAKETA | SOUTH
7626 | L_GONZAL | SOUTH
7636 | L_COLORA | SOUTH
7638 | L_SHELPL | SOUTH
7639 | L_SHERID | SOUTH
7640 | L_ROCKIS | SOUTH
7642 | L_SBBETA | SOUTH
7644 | L_THORSW | SOUTH
7646 | L_THOTA1 | SOUTH
7648 | L_PARKBR | SOUTH
7650 | L_THOTA2 | SOUTH
7654 | L_BERNAR | SOUTH
7656 | L_BELLSB | SOUTH
7658 | L_BETASB | SOUTH
7660 | L_QUANSW | SOUTH
7662 | L_QUANEX | SOUTH
7663 | L_MECRTA | SOUTH
7664 | L_SUNNYS | SOUTH
7665 | L_MENGCR | SOUTH
7666 | L_PRAIVI | SOUTH
7668 | L_PRAIVI | SOUTH
7670 | L_SEAWAY | SOUTH
7671 | L_MACEDO | HOUSTON
7672 | L_ESCARP | SOUTH
7680 | L_CLEASP | SOUTH
7800 | L_GUADGE | SOUTH
7801 | L_GUADGE | SOUTH
7802 | L_GUADGE | SOUTH
7803 | L_GUADGE | SOUTH
7804 | L_GUADGE | SOUTH
7805 | L_GUADGE | SOUTH
7807 | L_BASTEN | SOUTH
7808 | L_BASTEN | SOUTH
7809 | L_BASTEN | SOUTH
7810 | L_RIONOG | SOUTH
7811 | L_RIONOG | SOUTH
7812 | L_RIONOG | SOUTH
7813 | L_RIONOG | SOUTH
8032 | AMISTADH | SOUTH
8033 | AMISTADH | SOUTH
8048 | FALCONHY | SOUTH
8062 | NBRE#1 | SOUTH
8063 | NBRE#2 | SOUTH
8064 | NBRE#3 | SOUTH
8066 | DUP1V#1 | SOUTH
8100 | EL_CAMPO | SOUTH
8102 | EL_CAMPO | SOUTH
8104 | LANCTYPM | HOUSTON
8105 | EAGLE_LK | SOUTH
8106 | ALTAIR2A | SOUTH
8107 | TCC-GLN2 | SOUTH
8109 | TCC-GLN4 | SOUTH
8111 | COLUMBUS | SOUTH
8113 | BAY_CITY | HOUSTON
8114 | CONOCO4A | HOUSTON
8115 | WADSWORT | HOUSTON
8116 | CELANEBC | HOUSTON
8117 | GANADO4A | SOUTH
8118 | EDNA4A | SOUTH
8119 | BLESSING | SOUTH
8121 | BLESSING | SOUTH
8123 | BLESSNG6 | SOUTH
8125 | LOLITA4A | SOUTH
8126 | FORMOSA4 | SOUTH
8127 | LAN_CTY4 | HOUSTON
8131 | PALACIOS | SOUTH
8132 | P.CMFT 2 | SOUTH
8133 | BROOKHOL | SOUTH
8134 | FOR #1 | SOUTH
8135 | P_LAVACA | SOUTH
8136 | PLACEDO2 | SOUTH
8137 | ALCOA 4 | SOUTH
8138 | FOR #2 | SOUTH
8139 | JOS #1 | SOUTH
8140 | JOSLIN4A | SOUTH
8141 | GOHLKE4A | SOUTH
8143 | V_DUPSW4 | SOUTH
8144 | AIRCO44A | SOUTH
8145 | VISTRON4 | SOUTH
8146 | BIGTRE4A | SOUTH
8147 | UCAR #2 | SOUTH
8148 | UCAR #1 | SOUTH
8149 | NCARBIDE | SOUTH
8152 | NCARBIDE | SOUTH
8153 | FOR #3 | SOUTH
8154 | FOR #4 | SOUTH
8155 | FOR #5 | SOUTH
8156 | FOR #6 | SOUTH
8157 | FOR #7 | SOUTH
8159 | GREENLK2 | SOUTH
8160 | CC1TERT | SOUTH
8161 | COLETO0A | SOUTH
8162 | COLETO4A | SOUTH
8164 | COLETO7A | SOUTH
8165 | COLETSTR | SOUTH
8166 | CSABLK2A | SOUTH
8167 | GEWST4A | SOUTH
8168 | COLETSTR | SOUTH
8169 | VICTORIA | SOUTH
8172 | VICTORIA | SOUTH
8173 | VICEC51A | SOUTH
8174 | VICEC61A | SOUTH
8177 | MAGRUDER | SOUTH
8178 | N_VICT2A | SOUTH
8179 | FOSTER_T | SOUTH
8180 | FOSTER2A | SOUTH
8181 | CC2TERT | SOUTH
8182 | LEARY_LN | SOUTH
8183 | THOMASTN | SOUTH
8184 | KENEDYSW | SOUTH
8186 | KENEDYSW | SOUTH
8188 | KENEDY2A | SOUTH
8189 | CUECPL2A | SOUTH
8190 | C.LCRA 2 | SOUTH
8192 | CUELCA4A | SOUTH
8195 | DARST_CR | SOUTH
8198 | BEEVILLE | SOUTH
8199 | LULNG M4 | SOUTH
8200 | PLEASANT | SOUTH
8203 | PLEASANT | SOUTH
8206 | CHARLOTT | SOUTH
8208 | DILLEY22 | SOUTH
8210 | DILLEYSW | SOUTH
8212 | DILLEYSW | SOUTH
8216 | PEARSAL2 | SOUTH
8218 | BIG_FOOT | SOUTH
8221 | BIG_FOOT | SOUTH
8223 | DEVINE2A | SOUTH
8225 | MOORE4A | SOUTH
8229 | BATSVL4 | SOUTH
8231 | UVALDE2A | SOUTH
8234 | UVALDE4A | SOUTH
8235 | ROCK_ATL | SOUTH
8236 | W_BATESV | SOUTH
8237 | KIMBLE2A | SOUTH
8238 | ROCKSPRS | SOUTH
8239 | FRIR2A | WEST
8242 | CRYSTAL2 | SOUTH
8243 | TURTLCR2 | SOUTH
8244 | CARRIZO2 | SOUTH
8246 | ASPHALT4 | SOUTH
8252 | BRACKVL4 | SOUTH
8253 | HAMILTON | SOUTH
8255 | HAMILTN4 | SOUTH
8257 | HAMIL_P4 | SOUTH
8258 | AMISTAD4 | SOUTH
8259 | CAUTHORN | WEST
8260 | ESCONDID | SOUTH
8262 | ELPS | SOUTH
8263 | EPASS H4 | SOUTH
8264 | EP.H TP4 | SOUTH
8270 | EAGLE_PS | SOUTH
8273 | PUEBLO4A | SOUTH
8274 | W_CONOCO | SOUTH
8280 | ASHERTON | SOUTH
8283 | ASHERTON | SOUTH
8285 | LAR #1 | SOUTH
8287 | LAR #2 | SOUTH
8288 | LAR #3 | SOUTH
8290 | LAREDO2A | SOUTH
8293 | LAREDO4A | SOUTH
8295 | WORMSER4 | SOUTH
8297 | BRUNI44A | SOUTH
8299 | ZAPATA4A | SOUTH
8300 | RAYVILE2 | SOUTH
8302 | RAYVILE4 | SOUTH
8310 | LAPALM 2 | SOUTH
8314 | LAPALM 4 | SOUTH
8317 | LAPALM 6 | SOUTH
8318 | RIOHONDO | SOUTH
8319 | RIOHONDO | SOUTH
8320 | W HGN 2 | SOUTH
8321 | HGN-1 2 | SOUTH
8322 | HAINEDR4 | SOUTH
8323 | E_HARRIS | SOUTH
8324 | LAPALSTR | SOUTH
8325 | HARLINSW | SOUTH
8326 | RIOHOSTR | SOUTH
8327 | HARLINSW | SOUTH
8328 | LP3TERT | SOUTH
8329 | L.FRES 2 | SOUTH
8330 | RIOHOSTR | SOUTH
8331 | BRWN CY2 | SOUTH
8332 | BRWN SW2 | SOUTH
8334 | CAVAZOS2 | SOUTH
8335 | S_PADRE4 | SOUTH
8336 | RH1TERT | SOUTH
8337 | SCARBIDE | SOUTH
8338 | P.ISABL4 | SOUTH
8339 | MIL.HWY4 | SOUTH
8341 | ED1TERT | SOUTH
8347 | WESMER 4 | SOUTH
8348 | WES UNT4 | SOUTH
8354 | WESLCSW4 | SOUTH
8355 | GOODWIN4 | SOUTH
8356 | HECB 4 | SOUTH
8357 | NWESLACO | SOUTH
8358 | N_MERCED | SOUTH
8359 | SS.ROSA | SOUTH
8360 | ELSA 4 | SOUTH
8367 | WMCALN 4 | SOUTH
8368 | NMCALN 4 | SOUTH
8371 | SMCALN 4 | SOUTH
8372 | PHARR 4 | SOUTH
8373 | POLK 4 | SOUTH
8374 | SE EDNB4 | SOUTH
8377 | NEDIN2A | SOUTH
8380 | NEDIN4A | SOUTH
8383 | NEDIN7A | SOUTH
8384 | NEDINSTR | SOUTH
8387 | PALMVW 4 | SOUTH
8388 | BATES0A | SOUTH
8390 | BATES 2 | SOUTH
8391 | SHLND 4 | SOUTH
8392 | BATES 4 | SOUTH
8393 | BATES0B | SOUTH
8395 | FALCON 4 | SOUTH
8397 | GARZA 2 | SOUTH
8399 | GARZA 4 | SOUTH
8400 | THREE_RI | SOUTH
8403 | THREE_RI | SOUTH
8404 | SIGMOR4A | SOUTH
8405 | SKIDMORE | SOUTH
8407 | MATHIS2A | SOUTH
8408 | EDROY2A | SOUTH
8409 | GRETA2A | SOUTH
8410 | REFUGIO2 | SOUTH
8413 | SINTON2A | SOUTH
8414 | PORTLAND | SOUTH
8416 | RINCON2A | SOUTH
8418 | RINCON4A | SOUTH
8421 | GREGORY2 | SOUTH
8422 | I_DUPSW4 | SOUTH
8425 | INGLESID | SOUTH
8426 | CITGO_NO | SOUTH
8427 | ARANSAS2 | SOUTH
8430 | ARANSAS4 | SOUTH
8431 | LIVE_OAK | SOUTH
8432 | ROCKPORT | SOUTH
8434 | ROCKPORT | SOUTH
8435 | SEAWALL2 | SOUTH
8436 | PORT_A2A | SOUTH
8437 | NUECES_B | SOUTH
8438 | NUECES_B | SOUTH
8439 | NUECES_B | SOUTH
8441 | NUECES_B | SOUTH
8442 | NUECES_B | SOUTH
8448 | LON_HILL | SOUTH
8452 | LON_HILL | SOUTH
8455 | LON_HILL | SOUTH
8456 | COSW#1 | SOUTH
8457 | COSW#2 | SOUTH
8458 | B_DAVIS4 | SOUTH
8459 | B_DAVIS0 | SOUTH
8460 | B_DAVIS0 | SOUTH
8461 | KOCH_UP0 | SOUTH
8462 | LON_HSTR | SOUTH
8463 | COASTSTE | SOUTH
8464 | COASTAL2 | SOUTH
8465 | INDUSTRI | SOUTH
8466 | CANTWELL | SOUTH
8467 | KOCH_UP4 | SOUTH
8468 | HIWAY_92 | SOUTH
8469 | KOCH_UP2 | SOUTH
8470 | HIWAY_94 | SOUTH
8471 | LON_HSTR | SOUTH
8474 | MORRIS4A | SOUTH
8475 | JAVELINA | SOUTH
8476 | CITGO_W4 | SOUTH
8477 | VALERO2A | SOUTH
8478 | OXY_CC4A | SOUTH
8479 | CLARK_WD | SOUTH
8481 | KOCH_HF4 | SOUTH
8482 | WEIL_TRC | SOUTH
8483 | SOUTH_SI | SOUTH
8484 | WEST_OSO | SOUTH
8485 | WESTSIDE | SOUTH
8486 | HOLLY44A | SOUTH
8487 | AIRLINE2 | SOUTH
8490 | AIRLINE4 | SOUTH
8492 | WOOLRIDG | SOUTH
8493 | PHARAOH4 | SOUTH
8494 | LAGUNA2A | SOUTH
8495 | NAVAL_BS | SOUTH
8496 | ARCADIA4 | SOUTH
8498 | BISHOP2A | SOUTH
8499 | LH3TERT | SOUTH
8500 | ALICE2A | SOUTH
8502 | LH4TERT | SOUTH
8503 | ALICE4A | SOUTH
8505 | FREER2A | SOUTH
8506 | VAL #1 | SOUTH
8507 | VAL #2 | SOUTH
8508 | FALFUR2A | SOUTH
8510 | FALFUR4A | SOUTH
8511 | OXY_CC0A | SOUTH
8512 | STRATN 2 | SOUTH
8514 | STRATTON | SOUTH
8515 | ALAZAN4A | SOUTH
8516 | CELANEBI | SOUTH
8517 | CELANEBI | SOUTH
8518 | KINGSVIL | SOUTH
8519 | KLEBERG4 | SOUTH
8520 | STAFFORD | SOUTH
8523 | PRAIRPMP | SOUTH
8524 | P.PMP T2 | SOUTH
8526 | R.SIDET2 | SOUTH
8527 | RIVER_SD | SOUTH
8528 | PKR TP 2 | SOUTH
8529 | PARKER2A | SOUTH
8530 | GARWDTAP | SOUTH
8531 | GARWDPMP | SOUTH
8532 | IDEAL_TP | SOUTH
8533 | GARWDRLF | SOUTH
8534 | TXI_TP2A | SOUTH
8535 | PIONEERS | SOUTH
8536 | PV_TAP2A | SOUTH
8537 | IDEAL_2A | SOUTH
8538 | GARWOOD2 | SOUTH
8539 | L STR T2 | SOUTH
8541 | LONE_STR | SOUTH
8542 | MATTHEWS | SOUTH
8543 | LAKESIDP | SOUTH
8545 | BC-TP 2 | SOUTH
8546 | BCPMPTP2 | SOUTH
8547 | BYCTYPM1 | SOUTH
8549 | BYCTYPM3 | SOUTH
8550 | MARKHAM2 | SOUTH
8552 | MIDFLD_T | SOUTH
8555 | CARANCUA | SOUTH
8556 | CLMVL T2 | SOUTH
8557 | CLEMVILL | SOUTH
8558 | STP PTP4 | HOUSTON
8559 | STP-CON4 | HOUSTON
8560 | CNOPGT1 | SOUTH
8561 | CNOPGT2 | SOUTH
8562 | CNOPST1 | SOUTH
8563 | STPFACHL | HOUSTON
8564 | DUP1-V 4 | SOUTH
8565 | DUP2-V 4 | SOUTH
8572 | WEAVERRD | SOUTH
8573 | RUNGE2A | SOUTH
8574 | NORDHEIM | SOUTH
8575 | YORKTOWN | SOUTH
8577 | HOCH.TP2 | SOUTH
8578 | HOCHEIM2 | SOUTH
8579 | MALONE2A | SOUTH
8580 | NIXON2A | SOUTH
8581 | MAG.TP 2 | SOUTH
8582 | NIXONLCR | SOUTH
8583 | MAGNOLA2 | SOUTH
8584 | CHASETAP | SOUTH
8585 | CHASEFLD | SOUTH
8586 | BERCLAIR | SOUTH
8587 | GOLIAD2A | SOUTH
8589 | FANNIN2A | SOUTH
8591 | OCONNER2 | SOUTH
8592 | NORMANNA | SOUTH
8593 | PETTUS2A | SOUTH
8598 | COY CTY2 | SOUTH
8599 | FASHING2 | SOUTH
8600 | COY_CITY | SOUTH
8603 | IMOGNTAP | SOUTH
8604 | IMOGNE 2 | SOUTH
8607 | JOURDNTN | SOUTH
8610 | COTULLA4 | SOUTH
8613 | BIG_WELL | SOUTH
8619 | ENCINAL4 | SOUTH
8622 | LYTLE22A | SOUTH
8628 | KNIPPA2A | SOUTH
8630 | SABINAL2 | SOUTH
8633 | CAMPWOOD | SOUTH
8635 | ZACATE4A | SOUTH
8637 | ANNA ST4 | SOUTH
8641 | SIEVISTA | SOUTH
8642 | WASH_ST2 | SOUTH
8643 | MINES_RD | SOUTH
8645 | DEL_MAR4 | SOUTH
8646 | RIO_BRAV | SOUTH
8647 | UNIV44A | SOUTH
8648 | GATEWAY4 | SOUTH
8649 | GATEWAE4 | SOUTH
8650 | GATEWAW4 | SOUTH
8653 | ST_NINO4 | SOUTH
8664 | HUMBPMP2 | SOUTH
8672 | LA_PRYOR | SOUTH
8681 | HAMILRGE | SOUTH
8682 | COMSTOCK | SOUTH
8684 | PICACHO4 | SOUTH
8686 | AMSIBWC4 | SOUTH
8688 | BUENA_VI | SOUTH
8690 | DEL_RIO4 | SOUTH
8692 | MAVERICK | SOUTH
8694 | CONOCO_L | SOUTH
8695 | CRESTONI | SOUTH
8699 | RANDADO4 | SOUTH
8700 | RAYVL1-2 | SOUTH
8702 | YTURRIAS | SOUTH
8704 | LASARASU | SOUTH
8705 | ERAYMNDV | SOUTH
8708 | MONTECRI | SOUTH
8710 | SBENITO2 | SOUTH
8744 | CAUSWAY4 | SOUTH
8747 | RNGRVILL | SOUTH
8748 | RNGRVLE2 | SOUTH
8751 | RIORICO2 | SOUTH
8752 | MERRETTS | SOUTH
8753 | DOEDYNSU | SOUTH
8754 | ADERHOLD | SOUTH
8755 | GANDYSUB | SOUTH
8756 | LAURELES | SOUTH
8758 | LASMILPA | SOUTH
8759 | ALBERTAR | SOUTH
8760 | H.ACRES4 | SOUTH
8762 | PHARRSUB | SOUTH
8763 | BURNSSUB | SOUTH
8764 | ERIOHOND | SOUTH
8765 | HEIDLBRG | SOUTH
8766 | CNTRLAVE | SOUTH
8767 | HIWAY511 | SOUTH
8768 | WESLACOS | SOUTH
8769 | VALVERDE | SOUTH
8771 | WEDINBUR | SOUTH
8772 | ALTONSUB | SOUTH
8773 | KEYSS4 | SOUTH
8774 | PALMHURS | SOUTH
8778 | HILINESU | SOUTH
8779 | LSEBANOS | SOUTH
8782 | MVFAYSW | SOUTH
8783 | MCCOOKNO | SOUTH
8785 | MCCOOKNO | SOUTH
8786 | FAYSVILL | SOUTH
8789 | SOUTHMOS | SOUTH
8790 | RAYMONDV | SOUTH
8792 | SIOUXSUB | SOUTH
8793 | RIO_GRAN | SOUTH
8795 | ROMATP4 | SOUTH
8796 | ROMA 4 | SOUTH
8797 | RIO_GRAN | SOUTH
8798 | L_GRULLA | SOUTH
8799 | CONTINL2 | SOUTH
8800 | TATTON2A | SOUTH
8802 | HEARD T2 | SOUTH
8803 | HEARD 2 | SOUTH
8804 | WOODSBOR | SOUTH
8805 | BONIVIEW | SOUTH
8808 | HOMEPORT | SOUTH
8810 | ODEM2A | SOUTH
8812 | TAFT2A | SOUTH
8814 | MID_WAYT | SOUTH
8815 | MIDWPUMP | SOUTH
8817 | I_DUPP14 | SOUTH
8818 | OXY_INGL | SOUTH
8819 | I_DUPP14 | SOUTH
8820 | OXY_INGL | SOUTH
8821 | SLUTALR4 | SOUTH
8822 | SLUBENT4 | SOUTH
8824 | RAILROAD | SOUTH
8825 | SURRCFE4 | SOUTH
8832 | REYSHERW | SOUTH
8839 | FULTONCP | SOUTH
8841 | FULTONCP | SOUTH
8847 | MUSTANG2 | SOUTH
8856 | N_PADRE2 | SOUTH
8858 | MCKENZIE | SOUTH
8859 | VALERO_E | SOUTH
8860 | HEARN_RD | SOUTH
8862 | STEVENS2 | SOUTH
8864 | STEVENS2 | SOUTH
8865 | CAL_WWKS | SOUTH
8866 | SMITH2A | SOUTH
8867 | CUNINGWW | SOUTH
8868 | KARON T2 | SOUTH
8869 | KARON 2 | SOUTH
8870 | AVRYP2-2 | SOUTH
8871 | AVRYP1-2 | SOUTH
8878 | N_ELLA2A | SOUTH
8882 | CABANISS | SOUTH
8883 | RODD_FLD | SOUTH
8884 | RBSTN T2 | SOUTH
8885 | CTYOFRBS | SOUTH
8886 | ROB_CPL2 | SOUTH
8887 | LOYOLA44 | SOUTH
8888 | BANQUETE | SOUTH
8889 | STADIUM2 | SOUTH
8890 | SAN_DIEG | SOUTH
8891 | GOVTWELL | SOUTH
8894 | PREMONT2 | SOUTH
8896 | RACHAL4A | SOUTH
8899 | ARMSTRON | SOUTH
8901 | LHEDM | SOUTH
8902 | LHRHL | SOUTH
8903 | LHRHM | SOUTH
8904 | CHAS_TAP | SOUTH
8905 | LHEDL | SOUTH
8906 | ALAMO | SOUTH
8907 | WRBRTN4 | SOUTH
8908 | MCCOLL 4 | SOUTH
8909 | NLARSWW4 | SOUTH
8911 | BLKBYU4A | SOUTH
8912 | MEDIOCR4 | SOUTH
8914 | COFEPRT4 | SOUTH
8917 | SUNCHSE4 | SOUTH
8918 | MILO4A | SOUTH
8923 | GARCEN 4 | SOUTH
8924 | B_GRAVEL | SOUTH
8925 | LGE4A | SOUTH
8926 | LGE_GT10 | SOUTH
8927 | LGE_GT20 | SOUTH
8928 | LGE_STG0 | SOUTH
8930 | ICPGN10A | SOUTH
8931 | ICPGN20A | SOUTH
8932 | ICPGN30A | SOUTH
8933 | FGNTS001 | SOUTH
8934 | FGNTS101 | SOUTH
8935 | FGNTS201 | SOUTH
8936 | MVGN#1 | SOUTH
8937 | MVGN#2 | SOUTH
8938 | MVGN#3 | SOUTH
8949 | STEWART2 | SOUTH
8950 | OLMITO4 | SOUTH
8951 | STEWART4 | SOUTH
8956 | WHITEPT | SOUTH
8957 | MECLOPN4 | SOUTH
8958 | MECBRUTP | SOUTH
8959 | AIR_LIQC | SOUTH
8960 | WHITEPT2 | SOUTH
8961 | WHITEPT4 | SOUTH
8963 | HEC 4 | SOUTH
8968 | INGLCOSW | SOUTH
8969 | MVGN#1 | SOUTH
8970 | MVGN#2 | SOUTH
8971 | MVGN#3 | SOUTH
8978 | AIR_LIQS | SOUTH
8979 | AIR_LIQI | SOUTH
8980 | FRONT | SOUTH
8981 | HECN1 | SOUTH
8982 | HECN2 | SOUTH
8983 | HECN3 | SOUTH
8984 | MARKHMTP | SOUTH
8985 | S_YGANCI | SOUTH
8997 | FRTTS001 | SOUTH
8998 | FRTTS101 | SOUTH
8999 | FRTTS201 | SOUTH
9000 | DECKR_G1 | SOUTH
9001 | DECKR_G2 | SOUTH
9002 | DECKR_G3 | SOUTH
9003 | DECKR_G4 | SOUTH
9004 | DECKR_G5 | SOUTH
9005 | DECKR_G6 | SOUTH
9016 | SANDH_G1 | SOUTH
9017 | SANDH_G2 | SOUTH
9018 | SANDH_G3 | SOUTH
9019 | SANDH_G4 | SOUTH
9020 | SANDHG5A | SOUTH
9021 | SANDHG5C | SOUTH
9025 | HP_STATC | SOUTH
9040 | AUSTROP | SOUTH
9041 | LOSTPN34 | SOUTH
9071 | GARFIELD | SOUTH
9073 | HOLMAN | SOUTH
9074 | LYTTON34 | SOUTH
9075 | LYTTON13 | SOUTH
9076 | MCNEILW | SOUTH
9077 | MCNEILS | SOUTH
9079 | MCNEILN | SOUTH
9080 | MCNEIL | SOUTH
9118 | PE_MB2 | SOUTH
9119 | PE_MB1 | SOUTH
9120 | BURLES13 | SOUTH
9121 | BURLES69 | SOUTH
9122 | KINGSMB1 | SOUTH
9123 | KINGSDB | SOUTH
9125 | KINGSBRY | SOUTH
9128 | NORTHL13 | SOUTH
9129 | NORTHL69 | SOUTH
9130 | NL_TERTY | SOUTH
9131 | NORTHSTR | SOUTH
9132 | SEAHM8 | SOUTH
9139 | AUSTNDAM | SOUTH
9147 | HICRSMB2 | SOUTH
9148 | HICRSMB1 | SOUTH
9151 | AMD | SOUTH
9155 | ANGUSVAL | SOUTH
9158 | BARTON | SOUTH
9160 | BEECREEK | SOUTH
9163 | BERGSTRM | SOUTH
9164 | METCENTR | SOUTH
9166 | BRACK | SOUTH
9169 | BRODIE | SOUTH
9171 | CAMERON | SOUTH
9175 | CARSON | SOUTH
9179 | CARDINAL | SOUTH
9183 | COMMONFD | SOUTH
9184 | DAFFIN_G | SOUTH
9187 | DECK_MB1 | SOUTH
9188 | DECK_MB3 | SOUTH
9190 | TECHRIDG | SOUTH
9193 | DESSAU | SOUTH
9196 | ED_BLUE | SOUTH
9199 | FISKVILL | SOUTH
9200 | GROVE | SOUTH
9202 | HAMILMB2 | SOUTH
9203 | HAMILMB1 | SOUTH
9204 | HARRIS | SOUTH
9207 | HIDDENVL | SOUTH
9212 | HOLLYMB1 | SOUTH
9213 | HOLLYMB2 | SOUTH
9214 | HOLLYMB3 | SOUTH
9215 | HOLLYMB4 | SOUTH
9216 | SANDHSYD | SOUTH
9217 | HOWARDLN | SOUTH
9220 | JETT | SOUTH
9223 | JOLLYVIL | SOUTH
9225 | JUSTINLN | SOUTH
9227 | KOENIG | SOUTH
9228 | LAKESHOR | SOUTH
9235 | LAKEWAY | SOUTH
9238 | MAGPLANT | SOUTH
9244 | FIESTA | SOUTH
9245 | NORTHWES | SOUTH
9247 | OAKHILL | SOUTH
9251 | ONION_CK | SOUTH
9253 | PATTONLN | SOUTH
9257 | PEDERNAL | SOUTH
9259 | PILOT_KB | SOUTH
9260 | RIVERPLS | SOUTH
9263 | SALEMWLK | SOUTH
9267 | SLAUGHTR | SOUTH
9269 | CENTAUS | SOUTH
9271 | SPRINKLE | SOUTH
9275 | STECK | SOUTH
9279 | SUMMITN | SOUTH
9280 | SUMMITS | SOUTH
9282 | TRADPOST | SOUTH
9283 | UTBALC | SOUTH
9284 | WALNUTCK | SOUTH
9285 | VEGA | SOUTH
9286 | WARREN | SOUTH
9288 | WELLSBR | SOUTH
9291 | WHELESS | SOUTH
9295 | WILIAMSN | SOUTH
9400 | ACKEYLYN | WEST
9402 | ARVANA_8 | WEST
9404 | GAILPT_8 | WEST
9406 | KEYSW_8 | WEST
9408 | NORTLAME | WEST
9410 | PUNKING_ | WEST
9412 | SLAMESA_ | WEST
9414 | WELCH_9 | WEST
9416 | WLAMESA_ | WEST
9451 | NOLANW_9 | WEST
9453 | SWEETH20 | WEST
9471 | SOHERMIG | WEST
9491 | GOLDSCG_ | WEST
11001 | NAV1CT | WEST
11002 | NAV1CSTR | WEST
11009 | NAV2CT | WEST
11011 | NAV3ST | WEST
11012 | NAV4CT | WEST
11013 | NAV5CT | WEST
11014 | NAV6ST | WEST
11016 | QUAILSW_ | WEST
11017 | NAVTAP_5 | WEST
11020 | TIEHVSG_ | WEST
11021 | TIEHVCG_ | WEST
11022 | TIEHVCG_ | WEST
11023 | TIEHVCG_ | WEST
11024 | TIEHVCG_ | WEST
11025 | TIEHVSG_ | WEST
11056 | ROSCOE_1 | WEST
11057 | CHAMPION | WEST
11058 | PYRON_1G | WEST
11059 | INADALE_ | WEST
11146 | NOTREES2 | WEST
11147 | NOTREES_ | WEST
11309 | BULLCREK | WEST
11310 | BULLCREK | WEST
11311 | BULLCREK | WEST
11312 | BULLCREK | WEST
11313 | BULLCREK | WEST
11320 | COYOTE_1 | WEST
11321 | COYOTE_8 | WEST
11690 | KIOWA_5 | NORTH
11691 | KMICHICT | NORTH
11692 | KMICHICT | NORTH
11693 | KMICHIST | NORTH
11694 | KMICHICT | NORTH
11695 | KMICHICT | NORTH
11696 | KMICHIST | NORTH
11697 | KIOWAPP_ | NORTH
12021 | GV_360_1 | NORTH
12022 | GV_360_2 | NORTH
12026 | CLYVIL1_ | NORTH
12028 | CLYVIL2_ | NORTH
12033 | HRTAG1_T | NORTH
12034 | HRTAG2_T | NORTH
12036 | KEL_MAG2 | NORTH
12051 | BD_WDSN1 | NORTH
12052 | BD_WDSN2 | NORTH
12065 | EGLMTLAK | NORTH
12094 | GEN_DYN2 | NORTH
12313 | ASHGRVE_ | NORTH
12322 | ENNSTRAC | NORTH
12323 | ENNSTRAC | NORTH
12410 | FPLEFRB1 | NORTH
12411 | FPLEFR1A | NORTH
12412 | FPLEFR1B | NORTH
12413 | FPLEFR1C | NORTH
12414 | FPLEFR1S | NORTH
12420 | FPLEFRB2 | NORTH
12421 | FPLEFR2A | NORTH
12422 | FPLEFR2B | NORTH
12423 | FPLEFR2C | NORTH
12424 | FPLEFR2S | NORTH
12425 | DESPKV2_ | NORTH
12441 | PARKD_1E | NORTH
12442 | PARKD_2E | NORTH
12443 | PARKD_3E | NORTH
12672 | TWINSTAR | NORTH
13116 | TGATEWAY | NORTH
13117 | TGATEWAY | NORTH
13118 | TGATEWAY | NORTH
13119 | TGATEWAY | NORTH
13131 | CALFREST | NORTH
13132 | CALFREST | NORTH
13133 | CALFREST | NORTH
13134 | CALFREST | NORTH
13135 | CALFREST | NORTH
13136 | CALFREST | NORTH
13426 | KILELMR1 | SOUTH
13429 | SAND_TXU | SOUTH
13430 | SAND_TXU | SOUTH
13431 | SANDTXUP | SOUTH
13432 | SANDOW_5 | SOUTH
13434 | SAND_TXU | SOUTH
13591 | COTTONW_ | NORTH
13610 | BELTONSW | SOUTH
13620 | KILCLARR | SOUTH
13662 | TEMPELMC | SOUTH
13681 | REED_M1_ | NORTH
32000 | CSST | NORTH
32001 | CSPT | NORTH
32002 | CSSV | NORTH
32003 | CSGP | NORTH
32004 | CSSC | NORTH
32005 | DOWLNGRD | NORTH
32798 | BRYN_TAM | NORTH
32799 | BRYN_TAM | NORTH
32858 | BRYN_BCR | NORTH
32859 | BRYN_JK_ | NORTH
32862 | BRYN_ATK | NORTH
32864 | BRYN_ATK | NORTH
32865 | BRYN_SNO | NORTH
32866 | BRYN_STE | NORTH
32867 | BRYN_ATK | NORTH
32868 | BRYN_ANN | NORTH
32869 | BRYN_NOR | NORTH
32870 | BRYN_TAB | NORTH
32871 | BRYN_BUS | NORTH
32872 | BRYN_NAL | NORTH
32873 | BRYN_SHA | NORTH
32874 | BRYN_EAS | NORTH
32875 | BRYN_DSB | NORTH
32876 | BRYN_IP | NORTH
32877 | BRYN_BRC | NORTH
32878 | BRYN_GRN | NORTH
32879 | BRYN_STP | NORTH
32880 | BRYN_SOU | NORTH
32881 | BRYN_KUR | NORTH
32882 | BRYN_TAB | NORTH
32883 | BRYN_DNS | NORTH
32884 | BRYN_DNS | NORTH
32885 | BRYN_GRP | NORTH
32886 | BRYN_ATK | NORTH
32887 | BRYN_ATK | NORTH
32888 | BRYN_ATK | NORTH
32889 | BRYN_MIL | NORTH
32890 | BRYN_ATK | NORTH
32891 | BRYN_ATK | NORTH
32892 | BRYN_DNS | NORTH
32893 | BRYN_SWT | NORTH
32894 | BRYN_BOW | NORTH
32896 | BRYN_EAS | NORTH
32897 | BRYN_DSB | NORTH
36998 | RDCNYNG1 | WEST
36999 | RDCANYON | WEST
37010 | TNLAKEPN | NORTH
37011 | TNBIOENR | NORTH
37030 | TNJONES_ | NORTH
37050 | TNHIGHLA | NORTH
37060 | TNLWVLWE | NORTH
37080 | TNLWVLTI | NORTH
37100 | TNLWVLST | NORTH
37120 | TNKRUGRV | NORTH
37140 | TNBELLS_ | NORTH
37160 | TNWHITEW | NORTH
37180 | TNFRNTRT | NORTH
37190 | TNFRONTI | NORTH
37200 | TNTRENTO | NORTH
37220 | TNLEONAR | NORTH
37240 | TNBLUERD | NORTH
37250 | TNLONGNE | NORTH
37260 | TNCLIMAX | NORTH
37280 | TNCLIMAX | NORTH
37290 | TNFRMRSV | NORTH
37300 | TNEMORY_ | NORTH
37320 | TNTALCOW | NORTH
37340 | TNDEPORT | NORTH
37350 | TNRED_RI | NORTH
37360 | TNLONE_O | NORTH
37370 | TNSAINT_ | NORTH
37380 | TNNOCONA | NORTH
37390 | TNPETROL | NORTH
37410 | TNLKWHIT | NORTH
37420 | TNLKWHIT | NORTH
37440 | TNWHITNE | NORTH
37460 | TNOLSEN_ | NORTH
37470 | TNOLSEN_ | NORTH
37490 | TNHNDLYT | NORTH
37500 | TNHANDLE | NORTH
37510 | TNVLLYMI | NORTH
37520 | TNSYCAMO | NORTH
37530 | TNCORYEL | NORTH
37550 | TNGATESV | NORTH
37570 | TNGATESV | NORTH
37590 | TNJNESBO | NORTH
37600 | TNCLIFTO | NORTH
37620 | TNCLFTNT | NORTH
37630 | TNCLIFTO | NORTH
37650 | TNMERDNT | NORTH
37660 | TNMERIDI | NORTH
37680 | TNWALNTS | NORTH
37700 | TNGLENRO | NORTH
37705 | TNSQUAW_ | NORTH
37710 | TNTOLAR_ | NORTH
37740 | TNHICOTA | NORTH
37750 | TNHICO__ | NORTH
37770 | TNHAMLTN | NORTH
37790 | TNHAMILT | NORTH
37810 | TNHILL_C | NORTH
37830 | TNOLNEY_ | NORTH
37850 | TNTHURBE | NORTH
37860 | TNSTHBEN | NORTH
37870 | TNGRAHAM | NORTH
37890 | TNBRYSON | NORTH
37900 | TNWINK__ | WEST
37920 | TNWINK__ | WEST
37940 | TNCALIFR | WEST
37960 | TNWNKLRC | WEST
37980 | TNWICKET | WEST
38000 | TNPYOTE_ | WEST
38020 | TNWORSHA | WEST
38040 | TNIH20__ | WEST
38050 | TNSTAFBL | WEST
38070 | TNFLATTO | WEST
38090 | TNPECOS_ | WEST
38120 | TNREEVSC | WEST
38140 | TNTOYAH_ | WEST
38160 | TNCOCHIS | WEST
38180 | TNLONEST | WEST
38200 | TNLONEST | WEST
38230 | TNAAPIPE | WEST
38250 | TNKERMIT | WEST
38280 | TNKERMIT | WEST
38290 | TNKEYSTO | WEST
38310 | TN16TH_S | WEST
38320 | TN16TH_S | WEST
38330 | TNWDWRDT | WEST
38331 | TNWDWRD4 | WEST
38332 | TNWDWRDU | WEST
38340 | TNAIRPOR | WEST
38350 | TNFTSTKT | WEST
38360 | TNFTSTCK | WEST
38365 | TNPINON_ | WEST
38370 | TNHACKBE | WEST
38375 | TNCTYRD1 | WEST
38380 | TNPUCKTT | WEST
38390 | TNARMDLO | WEST
38400 | TNSANDRS | WEST
38420 | TNWHITEB | WEST
38430 | TNWHITEB | WEST
38435 | TNSRBNME | WEST
38437 | TNSRBNME | WEST
38440 | TNNRTHNN | WEST
38460 | TNPUCKTF | WEST
38470 | TNGOMEZ_ | WEST
38490 | TNBELDIN | WEST
38500 | TNISP___ | HOUSTON
38530 | TNTEJAS_ | HOUSTON
38560 | TNCOMANC | HOUSTON
38570 | TNBP____ | HOUSTON
38575 | TNGRENBE | HOUSTON
38580 | TNBP_CGN | HOUSTON
38590 | TNBP_CGN | HOUSTON
38600 | TNBP_CGN | HOUSTON
38611 | TNBPAMCG | HOUSTON
38612 | TNBPAMCG | HOUSTON
38613 | TNBPAMCG | HOUSTON
38614 | TNBPAMCG | HOUSTON
38615 | TNBPAMCG | HOUSTON
38620 | TNAMOCO_ | HOUSTON
38650 | TNAMOCO_ | HOUSTON
38660 | TNBAYVIE | HOUSTON
38690 | TNBP_CGN | HOUSTON
38710 | TNCADDO_ | HOUSTON
38711 | TNTXCTY1 | HOUSTON
38712 | TNTXCTY2 | HOUSTON
38713 | TNTXCTY3 | HOUSTON
38714 | TNTXCTY4 | HOUSTON
38715 | TNCGNR__ | HOUSTON
38720 | TNAPACHE | HOUSTON
38730 | TNDOW_CO | HOUSTON
38740 | TNHEIGHT | HOUSTON
38770 | TNHEIGHT | HOUSTON
38820 | TNFRWYPA | HOUSTON
38850 | TNDICKNS | HOUSTON
38890 | TNSOUSHO | HOUSTON
38900 | TNNDICKN | HOUSTON
38920 | TNLEAGCI | HOUSTON
38950 | TNMAGNOL | HOUSTON
38980 | TNFRDSWO | HOUSTON
38990 | TNSEMINO | HOUSTON
39010 | TNHASTIN | HOUSTON
39015 | TNALVINT | HOUSTON
39030 | TNALVIN_ | HOUSTON
39040 | TNMAINLA | HOUSTON
39070 | TNTERMIN | HOUSTON
39075 | TNCHEROK | HOUSTON
39090 | TNMARTHN | HOUSTON
39095 | TNCHOCTA | HOUSTON
39096 | TNCHOCTA | HOUSTON
39110 | TNVALERO | HOUSTON
39140 | TNTXCITY | HOUSTON
39180 | TNSLCOGE | HOUSTON
39190 | TNSLCGN1 | HOUSTON
39200 | TNSTRLNG | HOUSTON
39220 | TNNTHSDT | HOUSTON
39250 | TNNORTHS | HOUSTON
39280 | TNTXCITY | HOUSTON
39310 | TNINTRCI | HOUSTON
39340 | TNLAMARQ | HOUSTON
39345 | TNPRXAIR | HOUSTON
39346 | TNPRXAIR | HOUSTON
39360 | TNCARBID | HOUSTON
39380 | TNLINDE_ | HOUSTON
39400 | TNGRANTA | HOUSTON
39410 | TNARCOPL | HOUSTON
39430 | TNLIQDCA | HOUSTON
39431 | TNTEPPCO | HOUSTON
39440 | TNMARTHN | HOUSTON
39470 | TNDOWCGN | HOUSTON
39480 | TNDOWCGN | HOUSTON
39500 | TNWCOLMA | HOUSTON
39530 | TNWCOLLO | HOUSTON
39560 | TNANGLET | HOUSTON
39600 | TNBRAZOR | HOUSTON
39630 | TNBRAZOR | HOUSTON
39650 | TNDOW_PU | HOUSTON
39670 | TNCLMNST | HOUSTON
39680 | TNCLEMEN | HOUSTON
39700 | TNSWEENY | HOUSTON
39720 | TNP662__ | HOUSTON
39730 | TNP663__ | HOUSTON
39750 | TNOLDOCE | HOUSTON
39760 | TNSCLP1_ | HOUSTON
39770 | TNSCLP2_ | HOUSTON
39775 | TNSCLP4_ | HOUSTON
39790 | TNSCLP3_ | HOUSTON
39810 | TNHILCOR | HOUSTON
39860 | TNSCLPCO | HOUSTON
39870 | TNPHILLP | HOUSTON
39880 | TNSCLPCO | HOUSTON
39890 | TNPHILLP | HOUSTON
39910 | TNPHILLP | HOUSTON
39930 | TNPHLLPS | HOUSTON
39940 | TNPHLLPS | HOUSTON
39950 | TNTNP_ON | NORTH
39960 | TNTNPONE | NORTH
39970 | TNTNPONE | NORTH
40000 | CEDARP__ | HOUSTON
40010 | CEDARP__ | HOUSTON
40011 | CEDAR03_ | HOUSTON
40012 | CEDAR84_ | HOUSTON
40015 | CEDARP__ | HOUSTON
40051 | AGRI____ | HOUSTON
40070 | AIRPRO__ | HOUSTON
40081 | ALEX_I55 | HOUSTON
40082 | ALEX_I16 | HOUSTON
40100 | ANBUSH__ | HOUSTON
40110 | APLIED__ | HOUSTON
40111 | OPNAPD__ | HOUSTON
40120 | ARITEK__ | HOUSTON
40130 | ATASCO__ | HOUSTON
40140 | BARBUR__ | HOUSTON
40150 | BARHIL__ | HOUSTON
40155 | BENDER_8 | HOUSTON
40160 | BTNENY__ | HOUSTON
40170 | BAYTWN__ | HOUSTON
40171 | BAYTWN88 | HOUSTON
40172 | BAYTWN66 | HOUSTON
40180 | BERTWD__ | HOUSTON
40190 | BIGVUE__ | HOUSTON
40200 | BIMONT__ | HOUSTON
40210 | BORDEN__ | HOUSTON
40220 | BRINE___ | HOUSTON
40231 | BUSCH10_ | HOUSTON
40232 | BUSCH38_ | HOUSTON
40240 | CENTER__ | HOUSTON
40250 | CASTEN__ | HOUSTON
40255 | CHAMBR__ | HOUSTON
40260 | CHAMON__ | HOUSTON
40270 | CHANEL__ | HOUSTON
40280 | CHANLV__ | HOUSTON
40281 | CHANLV__ | HOUSTON
40282 | CCHANLV_ | HOUSTON
40300 | CHEV____ | HOUSTON
40310 | CHOATE | HOUSTON
40320 | CHORIN__ | HOUSTON
40330 | CITFIL__ | HOUSTON
40340 | CITIES__ | HOUSTON
40351 | CLINTN__ | HOUSTON
40352 | CLINTN__ | HOUSTON
40370 | CONIAL__ | HOUSTON
40380 | CROSBY__ | HOUSTON
40390 | CROSBY__ | HOUSTON
40391 | CCROSBY_ | HOUSTON
40392 | SVC_CROS | HOUSTON
40400 | CROWN___ | HOUSTON
40420 | DAVSON__ | HOUSTON
40425 | OPNDAY__ | HOUSTON
40430 | DECKER__ | HOUSTON
40431 | CAPEMUT1 | HOUSTON
40441 | DEERPK21 | HOUSTON
40442 | DEERPK96 | HOUSTON
40450 | DEPWTR__ | HOUSTON
40460 | DEPWTR__ | HOUSTON
40470 | DEPWTR__ | HOUSTON
40475 | DEUSEN__ | HOUSTON
40480 | DS_BAT__ | HOUSTON
40490 | DOWLAP__ | HOUSTON
40500 | EAGLE___ | HOUSTON
40510 | ENPROD__ | HOUSTON
40520 | EPOTH___ | HOUSTON
40530 | ESBELT__ | HOUSTON
40540 | ESFORK__ | HOUSTON
40550 | ETHYL___ | HOUSTON
40551 | ET_CLR1 | HOUSTON
40552 | ET_CLR2 | HOUSTON
40560 | EXPLOR__ | HOUSTON
40570 | EXXON___ | HOUSTON
40571 | EXXONSTR | HOUSTON
40572 | EXXONSTR | HOUSTON
40573 | EXXONSTR | HOUSTON
40575 | EXXON | HOUSTON
40580 | CAPEMUT5 | HOUSTON
40590 | FDLITY__ | HOUSTON
40600 | ROANS___ | NORTH
40610 | GALENA__ | HOUSTON
40611 | GALENA__ | HOUSTON
40612 | GALENA__ | HOUSTON
40620 | GLENWD__ | HOUSTON
40650 | GDYEAR__ | HOUSTON
40700 | GRNBYU__ | HOUSTON
40710 | GRNBYU__ | HOUSTON
40715 | GRNBYU__ | HOUSTON
40716 | GRNBYU__ | HOUSTON
40717 | CGRNBYU_ | HOUSTON
40720 | GRNBYU__ | HOUSTON
40725 | GRNBYU__ | HOUSTON
40751 | GYPSUM__ | HOUSTON
40752 | GYPSUM | HOUSTON
40770 | HACHER__ | HOUSTON
40780 | HADEN___ | HOUSTON
40790 | HANEY___ | HOUSTON
40800 | HARRIS__ | HOUSTON
40811 | HILAND08 | HOUSTON
40812 | HILAND43 | HOUSTON
40830 | HUMBLE__ | HOUSTON
40831 | CHUMBLE_ | HOUSTON
40841 | INDUST84 | HOUSTON
40842 | INDUST38 | HOUSTON
40860 | JACNTO__ | HOUSTON
40870 | KENNY14_ | HOUSTON
40871 | KENNY03_ | HOUSTON
40900 | KING____ | HOUSTON
40911 | KING_T3_ | HOUSTON
40912 | KING_T4_ | HOUSTON
40930 | KINGWD__ | HOUSTON
40941 | LAPORT96 | HOUSTON
40942 | LAPORT79 | HOUSTON
40961 | LIBRTY03 | HOUSTON
40962 | LIBRTY21 | HOUSTON
40980 | LUBZOL__ | HOUSTON
40990 | LYCHEM__ | HOUSTON
41000 | LYDELL__ | HOUSTON
41010 | LYNCH___ | HOUSTON
41021 | LYONDL03 | HOUSTON
41022 | LYONDL08 | HOUSTON
41040 | MCDONO__ | HOUSTON
41050 | METALS__ | HOUSTON
41061 | MINING__ | HOUSTON
41080 | MOCHEM__ | HOUSTON
41090 | MOMENT__ | HOUSTON
41100 | MORGPT__ | HOUSTON
41111 | MT_BEL__ | HOUSTON
41112 | MT_BEL__ | HOUSTON
41150 | NEWPRT__ | HOUSTON
41160 | NINTH___ | HOUSTON
41165 | NOBEL___ | HOUSTON
41171 | NORMDY77 | HOUSTON
41172 | NORMDY94 | HOUSTON
41191 | OATES08_ | HOUSTON
41192 | OATES38_ | HOUSTON
41205 | ORION___ | HOUSTON
41210 | PAIR____ | HOUSTON
41221 | PARKWY95 | HOUSTON
41222 | PARKWY94 | HOUSTON
41240 | JEFFER__ | HOUSTON
41250 | PHILIP__ | HOUSTON
41260 | PORT____ | HOUSTON
41300 | PSARCO__ | HOUSTON
41310 | QUANAB__ | HOUSTON
41330 | QUANUM__ | HOUSTON
41340 | REED____ | HOUSTON
41350 | ROHMAS__ | HOUSTON
41360 | ROLLEN__ | HOUSTON
41370 | S_CHAN__ | HOUSTON
41371 | CS_CHAN_ | HOUSTON
41380 | S_CHAN__ | HOUSTON
41383 | CAPEMUT6 | HOUSTON
41400 | S_R_B___ | HOUSTON
41405 | S_R_B___ | HOUSTON
41410 | S_R_B___ | HOUSTON
41415 | S_R_B___ | HOUSTON
41420 | S_R_B___ | HOUSTON
41430 | SHELDN__ | HOUSTON
41450 | SHELL___ | HOUSTON
41480 | SOLMER__ | HOUSTON
41490 | STATE___ | HOUSTON
41500 | STRANG__ | HOUSTON
41510 | STRAW___ | HOUSTON
41520 | SYLVAN__ | HOUSTON
41530 | TAYLOR__ | HOUSTON
41550 | TEXAS___ | HOUSTON
41560 | TXPET___ | HOUSTON
41570 | TEXWAL__ | HOUSTON
41580 | TIDAL___ | HOUSTON
41590 | TRAVIS__ | HOUSTON
41600 | TRIBAY__ | HOUSTON
41610 | TRINTY__ | HOUSTON
41615 | CAPEMUT2 | HOUSTON
41620 | TUCKER__ | HOUSTON
41631 | UNDRWD06 | HOUSTON
41632 | UNDRWD21 | HOUSTON
41651 | UVALDE08 | HOUSTON
41652 | UVALDE03 | HOUSTON
41670 | WABURN__ | HOUSTON
41681 | WALSVL61 | HOUSTON
41682 | WALSVL10 | HOUSTON
41700 | WARVUE__ | HOUSTON
41711 | WITTER94 | HOUSTON
41712 | WITTER21 | HOUSTON
42000 | P_H_R___ | HOUSTON
42010 | P_H_R___ | HOUSTON
42011 | CP_H_R__ | HOUSTON
42013 | P_H_R79_ | HOUSTON
42014 | P_H_R96_ | HOUSTON
42015 | P_H_R___ | HOUSTON
42020 | P_H_R___ | HOUSTON
42041 | ALMEDA26 | HOUSTON
42042 | ALMEDA07 | HOUSTON
42061 | ALTA_L93 | HOUSTON
42062 | ALTA_L53 | HOUSTON
42080 | ALVIN___ | HOUSTON
42090 | AMOCO___ | HOUSTON
42110 | ANGLTN__ | HOUSTON
42120 | ARMAND__ | HOUSTON
42130 | AVAUTO__ | HOUSTON
42150 | BASF____ | HOUSTON
42160 | BAYOU___ | HOUSTON
42170 | BAYWAY__ | HOUSTON
42180 | BIGBAY__ | HOUSTON
42190 | BIPORT__ | HOUSTON
42195 | BOOSTR__ | HOUSTON
42200 | BRYAN___ | HOUSTON
42210 | BRZPRT__ | HOUSTON
42220 | BYPARK__ | HOUSTON
42230 | CAPTOL__ | HOUSTON
42241 | CARDIF84 | HOUSTON
42242 | CARDIF95 | HOUSTON
42260 | CELNEC__ | HOUSTON
42271 | CHOC_B26 | HOUSTON
42272 | CHOC_B07 | HOUSTON
42291 | CLEAR95_ | HOUSTON
42292 | CLEAR35_ | HOUSTON
42311 | COLEGE94 | HOUSTON
42312 | COLEGE06 | HOUSTON
42330 | CW_COL__ | HOUSTON
42340 | DAMON___ | HOUSTON
42500 | DOW_____ | HOUSTON
42501 | DOW__STR | HOUSTON
42502 | DOW__STR | HOUSTON
42510 | DOW_____ | HOUSTON
42515 | DOW_____ | HOUSTON
42550 | DROUET__ | HOUSTON
42551 | DROUET_T | HOUSTON
42561 | ELDORA91 | HOUSTON
42562 | ELDORA92 | HOUSTON
42581 | ELLING07 | HOUSTON
42582 | ELLING91 | HOUSTON
42600 | EXTER___ | HOUSTON
42610 | FAIRMT__ | HOUSTON
42611 | FAIRMT95 | HOUSTON
42612 | FAIRMT00 | HOUSTON
42640 | FREEPT__ | HOUSTON
42651 | FRIEND05 | HOUSTON
42652 | FRIEND04 | HOUSTON
42670 | GALVES__ | HOUSTON
42680 | GARDEN__ | HOUSTON
42690 | GARDEN__ | HOUSTON
42700 | CGARDEN_ | HOUSTON
42711 | GENOA95_ | HOUSTON
42712 | GENOA35_ | HOUSTON
42741 | GULFGT91 | HOUSTON
42742 | GULFGT06 | HOUSTON
42761 | HALL_06_ | HOUSTON
42762 | HALL_91_ | HOUSTON
42780 | HANNA___ | HOUSTON
42790 | HIMONT__ | HOUSTON
42800 | HITCOK__ | HOUSTON
42810 | HOFMAN__ | HOUSTON
42820 | HASTNG__ | HOUSTON
42830 | HUNTER__ | HOUSTON
42841 | KEMAH95_ | HOUSTON
42842 | KEMAH92_ | HOUSTON
42860 | LAMARQ__ | HOUSTON
42861 | LAMARQ__ | HOUSTON
42862 | CAPEMUT3 | HOUSTON
42870 | LIVRPL__ | HOUSTON
42880 | LKJACK__ | HOUSTON
42890 | LOMAX___ | HOUSTON
42900 | LUZBAY__ | HOUSTON
42910 | LYNPOL__ | HOUSTON
42921 | MARYCK06 | HOUSTON
42922 | MARYCK91 | HOUSTON
42940 | MONSAN__ | HOUSTON
42945 | MONSAN | HOUSTON
42950 | MOODY63_ | HOUSTON
42951 | TERM_A__ | HOUSTON
42952 | OPN_T_A_ | HOUSTON
42953 | TERM_B__ | HOUSTON
42955 | TRMNAL__ | HOUSTON
42960 | MUSTNG__ | HOUSTON
42970 | NASA____ | HOUSTON
42981 | NASH_02_ | HOUSTON
42982 | NASH_45_ | HOUSTON
42985 | DYANN | HOUSTON
43000 | NEEDVL__ | HOUSTON
43011 | NEWGLF04 | HOUSTON
43012 | NEWGLF60 | HOUSTON
43035 | OASIS___ | HOUSTON
43040 | PASDNA__ | HOUSTON
43051 | PEARLD06 | HOUSTON
43052 | PEARLD91 | HOUSTON
43070 | PETSON__ | HOUSTON
43081 | PILGRM06 | HOUSTON
43082 | PILGRM07 | HOUSTON
43101 | PLARIS95 | HOUSTON
43102 | PLARIS35 | HOUSTON
43120 | PLEDGR__ | HOUSTON
43130 | POWELL__ | HOUSTON
43135 | QNTANA | HOUSTON
43140 | RETREV__ | HOUSTON
43150 | RIWOOD__ | HOUSTON
43170 | S_HOUS__ | HOUSTON
43171 | S_HOUS31 | HOUSTON
43172 | S_HOUS13 | HOUSTON
43173 | S_HOUS12 | HOUSTON
43174 | S_HOUS21 | HOUSTON
43190 | S_LANE__ | HOUSTON
43201 | SEAWAL01 | HOUSTON
43202 | SEAWAL63 | HOUSTON
43220 | SEAWAY__ | HOUSTON
43225 | SEPTON__ | HOUSTON
43230 | SHORE___ | HOUSTON
43240 | SINTEK__ | HOUSTON
43250 | SOUTH___ | HOUSTON
43260 | SOWYCK__ | HOUSTON
43271 | SPENCR06 | HOUSTON
43272 | SPENCR92 | HOUSTON
43290 | STEWRT__ | HOUSTON
43300 | STRATT__ | HOUSTON
43310 | SURFSI__ | HOUSTON
43321 | TELPHN06 | HOUSTON
43322 | TELPHN91 | HOUSTON
43330 | CAVERN__ | HOUSTON
43340 | TXGLF___ | HOUSTON
43350 | TEXWES__ | HOUSTON
43355 | TIKIS___ | HOUSTON
43356 | CAPEMUT4 | HOUSTON
43360 | VLASCO__ | HOUSTON
43370 | VLASCO__ | HOUSTON
43380 | W_COL___ | HOUSTON
43390 | W_COL___ | HOUSTON
43400 | W_GALV__ | HOUSTON
43401 | TEMP_BYP | HOUSTON
43403 | WEST_G_M | HOUSTON
43500 | WEBSTR__ | HOUSTON
43501 | WEBSTR93 | HOUSTON
43502 | WEBSTTR2 | HOUSTON
43503 | WEBSTR35 | HOUSTON
43504 | WEBSTR92 | HOUSTON
43507 | CWEBSTR_ | HOUSTON
43510 | WEBSTR__ | HOUSTON
43520 | WESTBY_5 | HOUSTON
43521 | WESTBY_4 | HOUSTON
43570 | WHARTN__ | HOUSTON
44000 | W_A_P___ | HOUSTON
44010 | W_A_P___ | HOUSTON
44020 | ALIEF___ | HOUSTON
44031 | ARCOLA80 | HOUSTON
44032 | ARCOLA82 | HOUSTON
44051 | BARKER78 | HOUSTON
44052 | BARKER73 | HOUSTON
44070 | BG_CRK__ | HOUSTON
44081 | BLURIG05 | HOUSTON
44082 | BLURIG02 | HOUSTON
44100 | BRAZOS__ | HOUSTON
44110 | BRISCO__ | HOUSTON
44120 | BRITMR__ | HOUSTON
44130 | CANEY___ | HOUSTON
44131 | CANEY___ | HOUSTON
44140 | CLODIN__ | HOUSTON
44150 | CCLODIN_ | HOUSTON
44160 | COLLIN__ | HOUSTON
44170 | CRABB___ | HOUSTON
44180 | DEWALT__ | HOUSTON
44190 | E_BERN__ | HOUSTON
44200 | HILLJE | HOUSTON
44210 | ECHO_73_ | HOUSTON
44211 | ECHO_13_ | HOUSTON
44212 | ECHO_31_ | HOUSTON
44213 | ECHO_14_ | HOUSTON
44214 | ECHO_41_ | HOUSTON
44215 | ECHO_81_ | HOUSTON
44230 | FLEWLN__ | HOUSTON
44231 | CFLEWLN_ | HOUSTON
44240 | FLEWLN__ | HOUSTON
44250 | FOSTER__ | HOUSTON
44261 | FRANZ09_ | HOUSTON
44262 | FRANZ66_ | HOUSTON
44280 | FTBEND__ | HOUSTON
44290 | FTBEND__ | HOUSTON
44300 | CFTBEND_ | HOUSTON
44310 | HAYES___ | HOUSTON
44311 | HAYES24_ | HOUSTON
44312 | HAYES09_ | HOUSTON
44341 | IMPERL80 | HOUSTON
44342 | IMPERL05 | HOUSTON
44361 | INTERM05 | HOUSTON
44362 | INTERM26 | HOUSTON
44380 | JULIFF__ | HOUSTON
44390 | KARSTN__ | HOUSTON
44400 | KARSTN__ | HOUSTON
44410 | CKARSTN_ | HOUSTON
44421 | KATY_09_ | HOUSTON
44422 | KATY_66_ | HOUSTON
44440 | MANVEL__ | HOUSTON
44450 | MASON___ | HOUSTON
44461 | MEMORL81 | HOUSTON
44462 | MEMORL73 | HOUSTON
44481 | MOCITY__ | HOUSTON
44482 | MOCITY__ | HOUSTON
44490 | MULA____ | HOUSTON
44500 | OBRIEN__ | HOUSTON
44510 | OBRIEN__ | HOUSTON
44511 | OBRIEN25 | HOUSTON
44512 | OBRIEN73 | HOUSTON
44540 | ORCHRD__ | HOUSTON
44551 | QUAIL02_ | HOUSTON
44552 | QUAIL26_ | HOUSTON
44570 | READNG__ | HOUSTON
44580 | RICHMN__ | HOUSTON
44590 | ROARK___ | HOUSTON
44600 | ROSHRN__ | HOUSTON
44610 | ROSNBG__ | HOUSTON
44620 | SAUER81_ | HOUSTON
44621 | SAUER14_ | HOUSTON
44622 | SAUER41_ | HOUSTON
44623 | SAUER23_ | HOUSTON
44624 | SAUER32_ | HOUSTON
44625 | SAUER73_ | HOUSTON
44626 | SAUDP81 | HOUSTON
44627 | SAUDP73 | HOUSTON
44640 | SEALY___ | HOUSTON
44645 | SNGLTN_3 | HOUSTON
44650 | SMTHRS__ | HOUSTON
44651 | SIENNA02 | HOUSTON
44652 | SIENNA05 | HOUSTON
44656 | SLRDP81 | HOUSTON
44657 | SLRDP73 | HOUSTON
44671 | STAFRD09 | HOUSTON
44672 | STAFRD05 | HOUSTON
44691 | TELVEW02 | HOUSTON
44692 | TELVEW26 | HOUSTON
44710 | TXINS___ | HOUSTON
44721 | THOMSN80 | HOUSTON
44722 | THOMSN82 | HOUSTON
44740 | WALLIS__ | HOUSTON
44760 | WCHASE__ | HOUSTON
44761 | WCHASE05 | HOUSTON
44762 | WCHASE24 | HOUSTON
44780 | WESTIM__ | HOUSTON
44790 | WIRT_73_ | HOUSTON
44791 | WIRT_13_ | HOUSTON
44792 | WIRT_31_ | HOUSTON
44793 | WIRT_23_ | HOUSTON
44794 | WIRT_32_ | HOUSTON
44795 | WIRT_81_ | HOUSTON
44801 | WOODCK81 | HOUSTON
44802 | WOODCK73 | HOUSTON
45500 | T_H_W___ | HOUSTON
45510 | T_H_W___ | HOUSTON
45511 | T_H_W81_ | HOUSTON
45512 | T_H_W95_ | HOUSTON
45515 | T_H_W___ | HOUSTON
45520 | T_H_W___ | HOUSTON
45530 | T_H_W___ | HOUSTON
45600 | ADICKS__ | HOUSTON
45610 | ADICKS__ | HOUSTON
45611 | ADICKS__ | HOUSTON
45620 | CADICKS_ | HOUSTON
45630 | AIRLIN__ | HOUSTON
45640 | ALDINE__ | HOUSTON
45651 | BAMMEL__ | HOUSTON
45670 | BERRY___ | HOUSTON
45681 | CAMBEL09 | HOUSTON
45682 | CAMBEL21 | HOUSTON
45700 | CAMRON__ | HOUSTON
45711 | CYFAIR21 | HOUSTON
45712 | CYFAIR76 | HOUSTON
45730 | DEIHL___ | HOUSTON
45740 | DRILCO__ | HOUSTON
45750 | EUREKA__ | HOUSTON
45760 | FAIRBK__ | HOUSTON
45770 | FREMAN__ | HOUSTON
45781 | GEARS67_ | HOUSTON
45782 | GEARS95_ | HOUSTON
45801 | GERTIE21 | HOUSTON
45802 | GERTIE76 | HOUSTON
45821 | GREENS86 | HOUSTON
45822 | GREENS90 | HOUSTON
45840 | HARDY___ | HOUSTON
45850 | C_HARDY_ | HOUSTON
45861 | HIDDEN67 | HOUSTON
45862 | HIDDEN95 | HOUSTON
45880 | HOCKLY__ | HOUSTON
45885 | CHOCKLY_ | HOUSTON
45890 | HOCKLY__ | HOUSTON
45900 | INTEQ___ | HOUSTON
45910 | INTER___ | HOUSTON
45921 | JESTER67 | HOUSTON
45922 | JESTER81 | HOUSTON
45940 | KLEIN___ | HOUSTON
45952 | KLUGE___ | HOUSTON
45953 | CKLUGE__ | HOUSTON
45971 | KUYDAL74 | HOUSTON
45972 | KUYDAL75 | HOUSTON
45990 | L_YORK__ | HOUSTON
46001 | LAUDER90 | HOUSTON
46002 | LAUDER95 | HOUSTON
46020 | LIMEST__ | NORTH
46031 | LOCKWD90 | HOUSTON
46032 | LOCKWD86 | HOUSTON
46051 | LOUETA66 | HOUSTON
46052 | LOUETA81 | HOUSTON
46100 | N_BELT__ | HOUSTON
46110 | N_BELT__ | HOUSTON
46111 | CN_BEL95 | HOUSTON
46112 | CN_BEL90 | HOUSTON
46220 | PETERS__ | HOUSTON
46230 | PETERS__ | HOUSTON
46240 | PINHUR__ | HOUSTON
46250 | RACOON__ | HOUSTON
46261 | RAYFRD66 | HOUSTON
46262 | RAYFRD81 | HOUSTON
46281 | RITTEN86 | HOUSTON
46282 | RITTEN95 | HOUSTON
46300 | SATSUM__ | HOUSTON
46301 | SATSUM24 | HOUSTON
46302 | SATSUM76 | HOUSTON
46331 | SCENIC86 | HOUSTON
46332 | SCENIC90 | HOUSTON
46351 | TODD_21_ | HOUSTON
46352 | TODD_09_ | HOUSTON
46500 | TOMBAL__ | HOUSTON
46510 | TOMBAL__ | HOUSTON
46511 | TOMBAL66 | HOUSTON
46512 | TOMBAL81 | HOUSTON
46520 | CTOMBAL_ | HOUSTON
46550 | TRSWIG__ | HOUSTON
46551 | VETRAN67 | HOUSTON
46552 | VETRAN81 | HOUSTON
46560 | WALLER__ | HOUSTON
46570 | WESFLD__ | HOUSTON
46571 | CWESFLD_ | HOUSTON
46600 | WHITOK__ | HOUSTON
46610 | WHITOK__ | HOUSTON
46611 | WHITOK73 | HOUSTON
46612 | WHITOK09 | HOUSTON
46615 | WHITOK__ | HOUSTON
46616 | CWHITOK_ | HOUSTON
46620 | WHITOK__ | HOUSTON
46660 | WILLOW__ | HOUSTON
47000 | BELAIR__ | HOUSTON
47010 | BELAIR__ | HOUSTON
47011 | BELAIR35 | HOUSTON
47012 | BELAIR24 | HOUSTON
47013 | CBELAIR_ | HOUSTON
47015 | BELAIR__ | HOUSTON
47016 | SVC_BELA | HOUSTON
47050 | BRAYS___ | HOUSTON
47071 | DUNVAL05 | HOUSTON
47072 | DUNVAL24 | HOUSTON
47090 | FANNIN__ | HOUSTON
47100 | FONDRN__ | HOUSTON
47110 | GRANT___ | HOUSTON
47150 | H_O_C___ | HOUSTON
47155 | CH_O_C__ | HOUSTON
47160 | H_O_C___ | HOUSTON
47165 | H_O_C___ | HOUSTON
47170 | CH_O_C__ | HOUSTON
47191 | HILCRF24 | HOUSTON
47192 | HILCRF05 | HOUSTON
47210 | HOLMES__ | HOUSTON
47300 | JENETA__ | HOUSTON
47310 | JENETA__ | HOUSTON
47320 | KIRBY___ | HOUSTON
47331 | KNIGHT08 | HOUSTON
47332 | KNIGHT06 | HOUSTON
47350 | PLAZA___ | HOUSTON
47380 | SANFLP__ | HOUSTON
47381 | SANFLP36 | HOUSTON
47382 | SANFLP78 | HOUSTON
47383 | SANFLP87 | HOUSTON
47384 | SANFLP63 | HOUSTON
47411 | SHARPS05 | HOUSTON
47412 | SHARPS25 | HOUSTON
47420 | STADIM__ | HOUSTON
47430 | TECO____ | HOUSTON
47441 | ULRICH35 | HOUSTON
47442 | ULRICH24 | HOUSTON
47461 | WESTWD3_ | HOUSTON
47462 | WESTWD2_ | HOUSTON
47500 | DWNTWN__ | HOUSTON
47510 | DWNTWN__ | HOUSTON
47521 | BLOGET37 | HOUSTON
47522 | BLOGET46 | HOUSTON
47540 | BRING___ | HOUSTON
47550 | BROWN___ | HOUSTON
47560 | COUGAR__ | HOUSTON
47570 | CRCKET__ | HOUSTON
47580 | DUNLVY__ | HOUSTON
47600 | E_SIDE__ | HOUSTON
47610 | CESTSIDE | HOUSTON
47620 | FRAKLN__ | HOUSTON
47630 | GABLE___ | HOUSTON
47640 | GABLE___ | HOUSTON
47660 | GARROT__ | HOUSTON
47670 | GENRAL__ | HOUSTON
47680 | HIGHTS__ | HOUSTON
47690 | HYDEPK__ | HOUSTON
47700 | MAG_PK__ | HOUSTON
47701 | MAG_PK__ | HOUSTON
47705 | MIDTWN__ | HOUSTON
47707 | MIDRCLS_ | HOUSTON
47711 | N_SIDE91 | HOUSTON
47712 | N_SIDE21 | HOUSTON
47730 | POLK____ | HOUSTON
47750 | UNIVER__ | HOUSTON
47751 | UNIVER__ | HOUSTON
47752 | UNIVER__ | HOUSTON
48500 | APD_GT1_ | HOUSTON
48510 | AK_GT1__ | HOUSTON
48511 | LPE_GT1_ | HOUSTON
48512 | LPE_GT2_ | HOUSTON
48513 | LPE_GT3_ | HOUSTON
48514 | LPE_GT4_ | HOUSTON
48520 | BSF_GT1_ | HOUSTON
48521 | BVE_GT1_ | HOUSTON
48522 | BVE_GT2_ | HOUSTON
48523 | BVE_ST1_ | HOUSTON
48531 | BYU_GT1_ | HOUSTON
48532 | BYU_GT2_ | HOUSTON
48533 | BYU_GT3_ | HOUSTON
48534 | BYU_GT4_ | HOUSTON
48551 | CAL_GT1_ | HOUSTON
48552 | CAL_ST1_ | HOUSTON
48561 | CTL_GT2_ | HOUSTON
48562 | CTL_GT3_ | HOUSTON
48563 | CTL_GT4_ | HOUSTON
48564 | CTL_GN1_ | HOUSTON
48565 | CTL_GN2_ | HOUSTON
48581 | CBY_GN1_ | HOUSTON
48582 | CBY_GN2_ | HOUSTON
48591 | CHE_GT2_ | HOUSTON
48593 | CHE_GT1_ | HOUSTON
48594 | CHE_GN4_ | HOUSTON
48595 | BTE_GT2_ | HOUSTON
48596 | BTE_GT3_ | HOUSTON
48597 | BTE_GT4_ | HOUSTON
48598 | BTE_ST1_ | HOUSTON
48611 | DIB_GT1_ | HOUSTON
48612 | DIB_GT2_ | HOUSTON
48613 | DIB_ST1_ | HOUSTON
48614 | DIB_GT3_ | HOUSTON
48641 | DPEC_GT1 | HOUSTON
48642 | DPEC_GT2 | HOUSTON
48643 | DPEC_GT3 | HOUSTON
48644 | DPEC_GT4 | HOUSTON
48645 | DPEC_ST5 | HOUSTON
48651 | EP_1_2 | HOUSTON
48671 | FTR_GT1_ | NORTH
48672 | FTR_GT2_ | NORTH
48673 | FTR_GT3_ | NORTH
48674 | FTR_CN4_ | NORTH
48690 | GBY_GN5_ | HOUSTON
48691 | GBY_7374 | HOUSTON
48692 | GBY_8182 | HOUSTON
48693 | GBY_8384 | HOUSTON
48721 | LEG_1___ | NORTH
48722 | LEG_2___ | NORTH
48730 | MNS_GT | HOUSTON
48731 | CBE_GT1 | HOUSTON
48732 | CBE_GT2 | HOUSTON
48733 | CBE_ST12 | HOUSTON
48734 | CBE_GT3 | HOUSTON
48735 | CBE_GT4 | HOUSTON
48736 | CBE_ST34 | HOUSTON
48740 | PSG_GN2_ | HOUSTON
48741 | PSG_GT2_ | HOUSTON
48742 | PSG_GT3_ | HOUSTON
48761 | PR_GT1__ | HOUSTON
48772 | PHR_GN2_ | HOUSTON
48791 | PSA_GT1_ | HOUSTON
48792 | PSA_GT2_ | HOUSTON
48793 | PSA_GT3_ | HOUSTON
48794 | PSA_GT4_ | HOUSTON
48795 | PSA_GT5_ | HOUSTON
48796 | PSA_GN1_ | HOUSTON
48797 | PSA_GT6_ | HOUSTON
48811 | CVC_GT3_ | HOUSTON
48812 | CVC_GT2_ | HOUSTON
48813 | CVC_GT1_ | HOUSTON
48814 | CVC_ST5_ | HOUSTON
48815 | CVC_GT4_ | HOUSTON
48816 | CVC_GSTR | HOUSTON
48820 | SHELLG1_ | HOUSTON
48821 | SHELLG2 | HOUSTON
48822 | SHELLG3_ | HOUSTON
48841 | SJS_GT1_ | HOUSTON
48842 | SJS_GT2_ | HOUSTON
48845 | SOL_GT1 | HOUSTON
48851 | SRB_GN1_ | HOUSTON
48852 | SRB_GN2_ | HOUSTON
48853 | SRB_GN3_ | HOUSTON
48854 | SRB_GN4_ | HOUSTON
48855 | SRB_GT21 | HOUSTON
48873 | THW_ST3_ | HOUSTON
48874 | THW_ST4_ | HOUSTON
48875 | THW_3132 | HOUSTON
48877 | THW_3334 | HOUSTON
48879 | THW_4142 | HOUSTON
48881 | THW_4344 | HOUSTON
48883 | THW_GT1_ | HOUSTON
48885 | THW_5152 | HOUSTON
48886 | THW_5354 | HOUSTON
48887 | THW_5556 | HOUSTON
48911 | TGF_GT1_ | HOUSTON
48921 | WAP_GN1_ | HOUSTON
48922 | WAP_GN2_ | HOUSTON
48923 | WAP_GN3_ | HOUSTON
48924 | WAP_GN4_ | HOUSTON
48925 | WAP_GN5_ | HOUSTON
48926 | WAP_GN6_ | HOUSTON
48927 | WAP_GN7_ | HOUSTON
48928 | WAP_GN8_ | HOUSTON
48929 | WAPGT21_ | HOUSTON
49801 | EXN_4 | HOUSTON
49802 | EXN_11 | HOUSTON
49803 | EXN_15GT | HOUSTON
49804 | EXN_16GT | HOUSTON
49805 | EXN_17GT | HOUSTON
49806 | EXN_21 | HOUSTON
49807 | EXN_121 | HOUSTON
49808 | EXN_129 | HOUSTON
49809 | EXN_R1 | HOUSTON
49810 | EXN_R2 | HOUSTON
49811 | EXN_399 | HOUSTON
49812 | EXN_411 | HOUSTON
49813 | EXN_440 | HOUSTON
49814 | EXN_441 | HOUSTON
49815 | EXN_460 | HOUSTON
49816 | EXN_461 | HOUSTON
49817 | EXN_470 | HOUSTON
49818 | EXN_471 | HOUSTON
49819 | EXN_660 | HOUSTON
49820 | EXN_661 | HOUSTON
49821 | EXN_698 | HOUSTON
49822 | EXN_930 | HOUSTON
49823 | EXN_931 | HOUSTON
49824 | EXN935GT | HOUSTON
49825 | EXN937GT | HOUSTON
49826 | EXN938GT | HOUSTON
49827 | EXN_940 | HOUSTON
49828 | EXN941GT | HOUSTON
49829 | EXN942GT | HOUSTON
49830 | EXN943GT | HOUSTON
49831 | EXN944GT | HOUSTON
49832 | EXN945GT | HOUSTON
49833 | EXN_946 | HOUSTON
49834 | EXN_947 | HOUSTON
49835 | EXN_948 | HOUSTON
49836 | EXN_949 | HOUSTON
49837 | EXN_GT | HOUSTON
49838 | EXN_14GT | HOUSTON
49839 | EXN_929 | HOUSTON
49851 | DOW17000 | HOUSTON
49852 | DOW17132 | HOUSTON
49853 | DOW20000 | HOUSTON
49854 | DOW20990 | HOUSTON
49855 | DOW21998 | HOUSTON
49856 | DOW29999 | HOUSTON
49857 | DOW38000 | HOUSTON
49858 | DOW38100 | HOUSTON
49859 | DOW38200 | HOUSTON
49860 | DOW38300 | HOUSTON
49861 | DOW39000 | HOUSTON
49862 | DOW39100 | HOUSTON
49863 | DOW39200 | HOUSTON
49864 | DOW40000 | HOUSTON
49865 | DOW41000 | HOUSTON
49866 | DOW42000 | HOUSTON
49867 | DOW44600 | HOUSTON
49868 | DOW45100 | HOUSTON
49869 | DOW49000 | HOUSTON
49870 | DOW61000 | HOUSTON
49871 | DOW62000 | HOUSTON
49872 | DOW63000 | HOUSTON
49873 | DOW64000 | HOUSTON
49874 | DOW64100 | HOUSTON
49875 | DOW64110 | HOUSTON
49876 | DOW65000 | HOUSTON
49877 | DOW66000 | HOUSTON
49878 | DOW67000 | HOUSTON
49879 | DOW68000 | HOUSTON
49880 | DOW69000 | HOUSTON
49881 | DOW69099 | HOUSTON
49882 | DOW81000 | HOUSTON
49883 | DOW81990 | HOUSTON
49884 | DOW82000 | HOUSTON
49885 | DOW83000 | HOUSTON
49886 | DOW84000 | HOUSTON
49887 | DOW89996 | HOUSTON
49984 | DOW_A3_T | HOUSTON
49985 | DOW_A4_T | HOUSTON
49986 | EXXON_T1 | HOUSTON
49987 | EXXON_T2 | HOUSTON
49998 | EXXON_T3 | HOUSTON
59300 | PWRPLANT | SOUTH
59400 | FM_802 | SOUTH
59410 | PRICE_RD | SOUTH
59420 | FILTER_P | SOUTH
59450 | WATERPRT | SOUTH
59460 | AIRPORT8 | SOUTH
59480 | SIXTH_ST | SOUTH
59490 | MIDTOWN | SOUTH
59500 | SOUTH_PL | SOUTH
60000 | DSKY2 | WEST
60001 | DSKY2_4 | WEST
60002 | KING_SW4 | WEST
60003 | KING_NE1 | WEST
60004 | KM NEP4 | WEST
60005 | KING_SE1 | WEST
60006 | KING_SE4 | WEST
60007 | KING_SW1 | WEST
60008 | KING_SW4 | WEST
60009 | KINGTAP2 | WEST
60011 | DSKY2_T4 | WEST
60014 | SPUD4A | WEST
60016 | WOODWRD1 | WEST
60017 | ORNNWP1 | WEST
60018 | DSKY1 | WEST
60019 | KING_NW1 | WEST
60021 | KM NWP4 | WEST
60035 | BLF SVC1 | WEST
60040 | BLF_CRK7 | WEST
60041 | BLFTERT1 | WEST
60042 | BLF_CSTR | WEST
60043 | BLFTERT2 | WEST
60044 | BLF_CSTR | WEST
60056 | CALLAHAN | WEST
60057 | CALLAHAN | WEST
60058 | BUFF_GAP | WEST
60059 | BUFF_GAP | WEST
60060 | CIRELLO | WEST
60061 | CIRELLO | WEST
60063 | BUFF_GAP | WEST
60066 | H_HOLLOW | WEST
60067 | H_HOLLOW | WEST
60068 | HHOLLOW2 | WEST
60069 | HRSHOL2 | WEST
60070 | HHOLLOW3 | WEST
60071 | HHOLLOW3 | WEST
60072 | HHOLLOW4 | WEST
60073 | HRSHOL4 | WEST
60080 | WHRLWIND | WEST
60081 | WHRLWIND | WEST
60201 | RIO DRCS | WEST
60202 | FRNDDRCS | WEST
66216 | BLF_CRK4 | WEST
66217 | BLF_CRK4 | WEST
71050 | L_BITTCR | WEST
71051 | L_BITTCR | WEST
71052 | L_BITTCR | WEST
71053 | L_SWEETW | WEST
71054 | L_SWEETW | WEST
71055 | L_BITTCR | WEST
71056 | L_SWEETW | WEST
71057 | L_SWEETW | WEST
71058 | L_SWEETW | WEST
71059 | L_SWEETW | WEST
71060 | L_SWEETW | WEST
71061 | L_SWEETW | WEST
76009 | L_TWINBU | WEST
76011 | L_TWINBU | WEST
76012 | L_TWISTR | WEST
76013 | L_WEYASW | WEST
76030 | L_GASCCR | WEST
76031 | L_GASCCR | WEST
76032 | L_NORTMC | WEST
76090 | L_DIVIDE | WEST
76091 | L_DIVIDE | WEST
76092 | L_DIVIDE | WEST
76093 | L_CAPRSI | WEST
76094 | L_CAPRGE | WEST
76095 | L_CAPRSI | WEST
76096 | L_CAPRSI | WEST
76097 | L_CAPRGE | WEST
76317 | L_POTTTA | WEST
76319 | L_MCELMU | WEST
76320 | L_SCHKAD | WEST
76388 | L_FORTMA | WEST
76390 | L_FORTMA | WEST
76579 | L_FORTLA | WEST
76582 | L_MEVISW | WEST
76595 | L_NORTMC | WEST
76615 | L_CRANE | WEST
78015 | L_ROSICR | SOUTH
80000 | EPLV | SOUTH
80003 | MILHWYS | SOUTH
80004 | CCENRCTR | SOUTH
80010 | EPLVT1 | SOUTH
80012 | LAR | SOUTH
80013 | LARVFTN1 | SOUTH
80014 | LARVFTN2 | SOUTH
80020 | HEIGHTS4 | SOUTH
80021 | LARSTCOM | SOUTH
80051 | FOR #8 | SOUTH
80052 | FOR #9 | SOUTH
80053 | FOR #10 | SOUTH
80054 | FOR A | SOUTH
80055 | FOR B | SOUTH
80064 | CHOCBAYU | SOUTH
80071 | ZORILLO7 | SOUTH
80076 | AJO7A | SOUTH
80078 | GULFWIND | SOUTH
80080 | GWINDT11 | SOUTH
80081 | GWINDT21 | SOUTH
80106 | FALCONSS | SOUTH
80107 | PLMHSTT1 | SOUTH
80108 | PLMHSTT2 | SOUTH
80117 | MOORE F | SOUTH
80118 | PALMHURS | SOUTH
80121 | S_MISSIN | SOUTH
80123 | CITRUSCY | SOUTH
80128 | WHPTR1 | SOUTH
80129 | WHPTR2 | SOUTH
80135 | CSDBUS2 | SOUTH
80136 | CSDRBUS | SOUTH
80137 | CSDR89 | SOUTH
80138 | CSDR7 | SOUTH
80139 | CSDR56 | SOUTH
80140 | CSDR11 | SOUTH
80141 | CSDR11 | SOUTH
80148 | RH2TERT | SOUTH
80153 | CSDE | SOUTH
80154 | CSDW | SOUTH
80155 | MHSTCOM | SOUTH
80165 | LARDOVFT | SOUTH
80168 | LARVFTS | SOUTH
80169 | LARVFTS | SOUTH
80170 | LARVFTS | SOUTH
80171 | SARITA7A | SOUTH
80178 | PENASCAL | SOUTH
80180 | PNSCALT1 | SOUTH
80181 | PNSCALT2 | SOUTH
80223 | REYSHR G | SOUTH
80224 | VISTRONG | SOUTH
80225 | VISTRONG | SOUTH
80226 | ALCOA G | SOUTH
80227 | AIRCO G | SOUTH
80228 | KRGP | SOUTH
80230 | CELANEBI | SOUTH
80265 | LARECU40 | SOUTH
80266 | LARECU50 | SOUTH
80267 | LARECU44 | SOUTH
80268 | LARECU54 | SOUTH
80375 | LAKSDTP2 | SOUTH
80540 | VICEC54A | SOUTH
80541 | VICEC64A | SOUTH
85000 | SHARPE6 | SOUTH
85001 | N_SHARPE | SOUTH
85002 | N_SHARPE | SOUTH
85006 | HIDALGO4 | SOUTH
86104 | CID-138 | SOUTH
86105 | CID-230 | SOUTH
86106 | CUF-230 | SOUTH
86107 | CUF-138 | SOUTH
88198 | BEEVILLE | SOUTH
88253 | HAMILTON | SOUTH
88299 | ZAPATA | SOUTH
88508 | FALFURRI | SOUTH
88909 | NLARSSL | SOUTH
3309 | ASPN_G | NORTH
7303 | L_WPPGS12_1Y | SOUTH
7303 | L_WPPGS12_1Y | SOUTH
7305 | L_WPPGS34_1Y | SOUTH
7305 | L_WPPGS34_1Y | SOUTH
11065 | ELBOWCK_1G | WEST
12440 | PARKD_1SVC8 | NORTH
12449 | PARKD_2SVC8 | NORTH
48583 | CBY_GT4_1 | HOUSTON
48584 | CBY_GT4_2 | HOUSTON
48585 | CBY_ST4_1 | HOUSTON
48940 | WARVUE_GT1 | HOUSTON
58909 | PEARSALLSCG1 | HOUSTON
58909 | PEARSALLSCG1 | HOUSTON
58909 | PEARSALLSCG1 | HOUSTON
58909 | PEARSALLSCG1 | HOUSTON
58909 | PEARSALLSCG1 | HOUSTON
58909 | PEARSALLSCG1 | HOUSTON
58919 | PEARSALLSCG2 | HOUSTON
58919 | PEARSALLSCG2 | HOUSTON
58919 | PEARSALLSCG2 | HOUSTON
58919 | PEARSALLSCG2 | HOUSTON
58919 | PEARSALLSCG2 | HOUSTON
58919 | PEARSALLSCG2 | HOUSTON
58929 | PEARSALLSCG3 | HOUSTON
58929 | PEARSALLSCG3 | HOUSTON
58929 | PEARSALLSCG3 | HOUSTON
58929 | PEARSALLSCG3 | HOUSTON
58929 | PEARSALLSCG3 | HOUSTON
58929 | PEARSALLSCG3 | HOUSTON
58949 | PEARSALLSCG4 | HOUSTON
58949 | PEARSALLSCG4 | HOUSTON
58949 | PEARSALLSCG4 | HOUSTON
58949 | PEARSALLSCG4 | HOUSTON
58949 | PEARSALLSCG4 | HOUSTON
58949 | PEARSALLSCG4 | HOUSTON
80263 | B_DAVIS31A | HOUSTON
80264 | B_DAVIS41A | HOUSTON

## Non-Movable gens
BUS_NAM | BUS_NUM | UNIT_ID | Unique | Yes
AES1 | 48500 | 1 | 485001 | y
AIRCO G | 80227 | 1 | 802271 | y
ALCOA G | 80226 | 1 | 802261 | y
AMCHMCGN | 38690 | 3 | 386903 | y
AMO1 | 48510 | 1 | 485101 | y
AMOLCGN1 | 38580 | 1 | 385801 | y
AMOLCGN2 | 38590 | 2 | 385902 | y
AMOLCGN3 | 38600 | 5 | 386005 | y
BASF1 | 48520 | 1 | 485201 | y
BASF1 | 48520 | 2 | 485202 | y
BAT #1 | 8388 | MB | 8388MB | y
BAT #2 | 8393 | MB | 8393MB | y
BBRN 1 G | 3381 | 1 | 33811 | y
BBRN 2 G | 3382 | 2 | 33822 | y
BRYN_TAM | 32798 | 1 | 327981 | y
BSP 1 | 1320 | 1 | 13201 | y
BTE GT1 | 48595 | 1 | 485951 | y
BTE GT2 | 48596 | 2 | 485962 | y
BTE GT3 | 48597 | 3 | 485973 | y
BTE ST1 | 48598 | 4 | 485984 | y
CALGT1 | 48551 | 1 | 485511 | y
CALST1 | 48552 | 2 | 485522 | y
CAP1 | 48561 | 1 | 485611 | y
CAP2 | 48562 | 2 | 485622 | y
CAP3 | 48563 | 3 | 485633 | y
CAP4 | 48564 | 4 | 485644 | y
CAP5 | 48565 | 5 | 485655 | y
CEC GT1 | 48593 | 1 | 485931 | y
CEL-B #1 | 8517 | 1 | 85171 | y
CHAMPN G | 3348 | MB | 3348MB | y
CIDINDUS | 86104 | EQ | 86104EQ | y
CIDINDUS | 86105 | EQ | 86105EQ | y
CLO #1 | 8161 | 1 | 81611 | y
CMPK 1 G | 1898 | 1 | 18981 | y
CMPK 2 G | 1899 | 2 | 18992 | y
COSW#1 | 8456 | 1 | 84561 | y
COSW#2 | 8457 | 2 | 84572 | y
CSDR11 | 80140 | 11 | 8014011 | y
CSDR56 | 80139 | 5 | 801395 | y
CSDR56 | 80139 | 6 | 801396 | y
CSDR7 | 80138 | 7 | 801387 | y
CSDR89 | 80137 | 8 | 801378 | y
CSDR89 | 80137 | 9 | 801379 | y
CUF-138 | 86107 | EQ | 86107EQ | y
CUF-230 | 86106 | EQ | 86106EQ | y
DIB_GT3_ | 48614 | 4 | 486144 | y
DIB1 | 48611 | 1 | 486111 | y
DIB2 | 48612 | 2 | 486122 | y
DIB3 | 48613 | 3 | 486133 | y
DOW17000 | 49851 | 37 | 4985137 | y
DOW38100 | 49858 | 31 | 4985831 | y
DOW38200 | 49859 | 33 | 4985933 | y
DOW38300 | 49860 | 32 | 4986032 | y
DOW39100 | 49862 | 36 | 4986236 | y
DOW39200 | 49863 | 35 | 4986335 | y
DOW41000 | 49865 | 41 | 4986541 | y
DOW42000 | 49866 | 42 | 4986642 | y
DOW49000 | 49869 | 45 | 4986945 | y
DOW61000 | 49870 | 61 | 4987061 | y
DOW62000 | 49871 | 62 | 4987162 | y
DOW63000 | 49872 | 63 | 4987263 | y
DOW64000 | 49873 | 64 | 4987364 | y
DOW65000 | 49876 | 65 | 4987665 | y
DOW66000 | 49877 | 66 | 4987766 | y
DOW67000 | 49878 | 67 | 4987867 | y
DOW81000 | 49882 | 81 | 4988281 | y
DOW82000 | 49884 | 82 | 4988482 | y
DOW83000 | 49885 | 83 | 4988583 | y
DOW84000 | 49886 | 84 | 4988684 | y
DUP1V#1 | 8066 | 1 | 80661 | y
EP1 | 48651 | 1 | 486511 | y
EP1 | 48651 | 2 | 486512 | y
EXN 15GT | 49803 | 1 | 498031 | y
EXN 16GT | 49804 | 2 | 498042 | y
EXN 17GT | 49805 | 3 | 498053 | y
EXN GT | 49837 | 4 | 498374 | y
EXN_14GT | 49838 | 14 | 4983814 | y
EXN938GT | 49826 | 5 | 498265 | y
EXN941GT | 49828 | 10 | 4982810 | y
EXN942GT | 49829 | 11 | 4982911 | y
EXN943GT | 49830 | 12 | 4983012 | y
EXN944GT | 49831 | 13 | 4983113 | y
EXN945GT | 49832 | 9 | 498329 | y
FOR #1 | 8134 | 1 | 81341 | y
FOR #10 | 80053 | 10 | 8005310 | y
FOR #2 | 8138 | 2 | 81382 | y
FOR #3 | 8153 | 3 | 81533 | y
FOR #4 | 8154 | 4 | 81544 | y
FOR #5 | 8155 | 5 | 81555 | y
FOR #6 | 8156 | 6 | 81566 | y
FOR #7 | 8157 | 7 | 81577 | y
FOR #8 | 80051 | 8 | 800518 | y
FOR #9 | 80052 | 9 | 800529 | y
FPP G1 | 7010 | 1 | 70101 | y
FPP G2 | 7011 | 2 | 70112 | y
FPP G3 | 7012 | 3 | 70123 | y
GIBCRK | 990 | 1 | 9901 | y
JKS1 | 5401 | 1 | 54011 | y
JOS #1 | 8139 | MB | 8139MB | y
JTD1 | 5111 | 1 | 51111 | y
JTD2 | 5112 | 2 | 51122 | y
KINDERMG | 1069 | 1 | 10691 | y
KINDERMG | 1070 | 1 | 10701 | y
KINDERMG | 1071 | 1 | 10711 | y
KOCHREF2 | 8461 | 1 | 84611 | y
LAR #1 | 8285 | MB | 8285MB | y
LAR #2 | 8287 | MB | 8287MB | y
LAR #3 | 8288 | MB | 8288MB | y
LIM1 | 48721 | 1 | 487211 | y
LIM2 | 48722 | 2 | 487222 | y
MNSN1 | 48730 | 1 | 487301 | y
MOSES1 G | 1701 | 1 | 17011 | y
MOSES2 G | 1702 | 2 | 17022 | y
MOSES3 G | 1703 | 3 | 17033 | y
MTNLK 1G | 3097 | 1 | 30971 | y
MTNLK 2G | 3098 | 2 | 30982 | y
MTNLK 3G | 3099 | 3 | 30993 | y
NBY #5 | 8437 | MB | 8437MB | y
NBY #6 | 8438 | MB | 8438MB | y
NBY #7 | 8442 | MB | 8442MB | y
NORTHDC7 | 6096 | EQ | 6096EQ | y
OKLAUN1G | 6752 | 1 | 67521 | y
PET1 | 48761 | 1 | 487611 | y
PWR1 | 48791 | 1 | 487911 | y
PWR2 | 48792 | 2 | 487922 | y
PWR3 | 48793 | 3 | 487933 | y
PWR4 | 48794 | 4 | 487944 | y
PWR5 | 48795 | 5 | 487955 | y
PWR6 | 48796 | 1 | 487961 | y
PWR8 | 48797 | 6 | 487976 | y
REYSHR G | 80223 | 1 | 802231 | y
S&LCGN1 | 39190 | 1 | 391901 | y
SAND 4 G | 3432 | 4 | 34324 | y
SANDOW_5 | 13432 | 5 | 134325 | y
SANMIGUE | 5903 | 1 | 59031 | y
SHELL_ | 48820 | 1 | 488201 | y
SHELL_ | 48821 | 2 | 488212 | y
SHL_CPS | 48822 | 1 | 488221 | y
SHL_CPS | 48822 | 2 | 488222 | y
SHLDNST1 | 48814 | 1 | 488141 | y
SI RAY5 | 5934 | 5 | 59345 | y
SOL1 | 48845 | 1 | 488451 | y
STARCO#1 | 8511 | 1 | 85111 | y
STP1 | 5911 | 1 | 59111 | y
STP2 | 5912 | 2 | 59122 | y
TNPONE#1 | 39960 | 1 | 399601 | y
TNPONE#2 | 39970 | 1 | 399701 | y
UCAR #1 | 8148 | 2 | 81482 | y
UCAR #2 | 8147 | 10 | 814710 | y
UCCCGNGG | 39480 | 1 | 394801 | y
UCCCGNSG | 39470 | 1 | 394701 | y
VAL #1 | 8506 | 1 | 85061 | y
VAL #2 | 8507 | 2 | 85072 | y
VISTRONG | 80224 | 1 | 802241 | y
VISTRONG | 80225 | 2 | 802252 | y
WAP5 | 48925 | 5 | 489255 | y
WAP6 | 48926 | 6 | 489266 | y
WAP7 | 48927 | 7 | 489277 | y
WAP8 | 48928 | 8 | 489288 | y
WELSHDC1 | 5920 | EQ | 5920EQ | y

## N_H Contingencies
| ontingency | 'TOMBALL | TO | KING | REIT | 345KV'
1 | OPEN | LINE | FROM | BUS | 46500 | TO | BUS | 45971 | CKT | 74
| OPEN | LINE | FROM | BUS | 45972 | TO | BUS | 40900 | CKT | 75
2 | Contingency | 'GIBBON | CRK | - | SNG | 345KV | (4/20/09)'
| OPEN | LINE | FROM | BUS | 967 | TO | BUS | 44645 | CKT | 75
| OPEN | LINE | FROM | BUS | 967 | TO | BUS | 44645 | CKT | 99
3 | Contingency | 'GIBCRK | CRK | TO | SNG | 345kv | (3/23/09)'
| OPEN | LINE | FROM | BUS | 967 | TO | BUS | 44645 | CKT | 75
4 | Contingency | 'GIBCRK | - | SNG | 345 | KV | '
| OPEN | LINE | FROM | BUS | 967 | TO | BUS | 44645 | CKT | 99
5 | Contingency | 'JEWETT | TO | SNG | 345KV | (3/31/09)'
| OPEN | LINE | FROM | BUS | 3390 | TO | BUS | 44645 | CKT | 1
| OPEN | LINE | FROM | BUS | 3391 | TO | BUS | 44645 | CKT | 1
6 | Contingency | 'JEWET | TO | SNG | 345KV | (3/23/09-Line | :240_A)'
| OPEN | LINE | FROM | BUS | 3390 | TO | BUS | 44645 | CKT | 1
7 | Contingency | 'JEWET-SNG | 345KV | '
| OPEN | LINE | FROM | BUS | 3391 | TO | BUS | 44645 | CKT | 1
8 | Contingency | 'SNG-_OB | & | SNG-THW | 345 | '
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 45500 | CKT | 98
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 44500 | CKT | 99
9 | Contingency | 'SNG | TO | _OB | 345 | KV | '
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 44500 | CKT | 99
10 | Contingency | 'SNG | TO | THW | 345 | KV | (3/17/09)'
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 45500 | CKT | 98
11 | Contingency | 'RNS-KG | & | SNG-_TB | 345 | (4/09/09)'
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 46500 | CKT | 74
| OPEN | LINE | FROM | BUS | 45972 | TO | BUS | 40600 | CKT | 75
| OPEN | LINE | FROM | BUS | 45972 | TO | BUS | 40900 | CKT | 75
12 | Contingency | 'SNG-RNS | 345 | KV | (4/15/09)'
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 40600 | CKT | 75
13 | Contingency | 'SNG | TO | _TB | 345 | KV | (3/09/09)'
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 46500 | CKT | 74
14 | Contingency | 'O'BRIEN | #NAME? | & | - | SINGLETON | 345KV | '
| OPEN | LINE | FROM | BUS | 967 | TO | BUS | 44645 | CKT | 99
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 44500 | CKT | 99
| OPEN | LINE | FROM | BUS | 44500 | TO | BUS | 45500 | CKT | 71
15 | Contingency | 'GIBCRK-OB | & | SNG-THW | 345 | (3/17/09)'
| OPEN | LINE | FROM | BUS | 967 | TO | BUS | 44645 | CKT | 99
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 44500 | CKT | 99
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 45500 | CKT | 98
16 | Contingency | 'THW-SNG | & | THW-OB | 345 | (3/17/09)'
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 45500 | CKT | 98
| OPEN | LINE | FROM | BUS | 44500 | TO | BUS | 45500 | CKT | 71
17 | Contingency | 'GIBCRK-OB | & | TO | SNG | 345 | (4/19/09)'
| OPEN | LINE | FROM | BUS | 967 | TO | BUS | 44645 | CKT | 75
| OPEN | LINE | FROM | BUS | 967 | TO | BUS | 44645 | CKT | 99
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 44500 | CKT | 99
18 | Contingency | '_OB-THW | & | _OB-SNG | 345 | KV | '
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 44500 | CKT | 99
| OPEN | LINE | FROM | BUS | 44500 | TO | BUS | 45500 | CKT | 71
19 | Contingency | 'SNG-_TB | & | SNG-RNS | 345KV | (4/15/09)'
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 46500 | CKT | 74
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 40600 | CKT | 75
20 | Contingency | 'SNG-TB | & | #NAME? | #NAME? | 345 | KV | '
| OPEN | LINE | FROM | BUS | 44645 | TO | BUS | 46500 | CKT | 74
| OPEN | LINE | FROM | BUS | 46500 | TO | BUS | 45971 | CKT | 74
| OPEN | LINE | FROM | BUS | 45971 | TO | BUS | 40900 | CKT | 74
21 | Contingency | 'KING-KDL-TB | & | KING-KDL-ROANS | PR | REIT | 345KV'
| OPEN | LINE | FROM | BUS | 40900 | TO | BUS | 45972 | CKT | 75
| OPEN | LINE | FROM | BUS | 45972 | TO | BUS | 40600 | CKT | 75