## Set up
Step 1 | Go to the Zones worksheet in this workbook. Make sure that the source and sink zones are set correctly and the "1"s and "-1"s are correct |  | Summary of Key Data points | Value
File Description:
Step 2 | Open Dennis' file that needs to have the data transferred, same file that is listed in cell K27 |  | Number of units | 0
|  |  | Dec PTDF cutoff point | 0
Step 3 | Copy columns J:X from an old Dennis' Sheet to the new sheet (if first round of a new alaysis) |  | Dec PTDF cutoff unit | Name of Bus
|  |  | Dec 10% unit | Name of Bus
Step 4 | Mark the contingencies and monitored element set by a "y" in column K of Dennis' sheet, if there are a match on the filename use something to make unique |  | Dec max cumltv zone impact - cumltv zone share | 0
|  |  | Dec max cumltv zone impact - cumltv zone share pt | 0
Step 5 | Enter Dennis' file name into cell K27 |  | Dec max cumltv zone impact - cumltv zone share unit | 0
|  |  | North Zonal weighted AWGSF | 0.14171
Step 6 | click the step one button |  | South Zonal weighted AWGSF | -0.16719
|  |  | Inc PTDF cutoff point | 0
Step 7 | Enter the line ratings in Dennis' workbook, the Input worksheet, in the cells |  | Inc PTDF cutoff unit | Name of Bus
| X6:X30, or to the end of the selected list. |  | Inc 10% unit | Name of Bus
|  |  | Inc max cumltv zone impact - cumltv zone share | 0
Step 8 | Check to see that the number of generators in Dennis' file matches the length |  | Inc max cumltv zone impact - cumltv zone share pt | 0
| of the formulas in columns L:V (Distributed Slack - Dec) have been copied through to the apporpriate number of rows |  | Inc max cumltv zone impact - cumltv zone share unit | 0
| If Dennis' sheet data is less than this file then clear any old unit data in columns A:K of this workbook to match the correct leng |  | North Zonal weighted AWGSF | 0.14171
| It is only necessary to match the Distributed Slack - Dec worksheet. |  | South Zonal weighted AWGSF | -0.16719
|  |  | Min of zone correlation | -0.27351
Step 9 | Click the step 2 button |  | Bounary gen in South Zone | 0
| The last file saved will still be open, yopu will need to close this file. |  | Bounary gen in soucre zone as % of line | 0%
| This sheet willno longer be open. |  | Bounary gen in North Zone | 0
|  |  | Bounary gen in soucre zone as % of line | 0
|  |  | OL element line rating | 956
|  |  | North Zonal weighted AWGSF | -0.077468
|  | SN_043009automation.xls | South Zonal weighted AWGSF | 0.11295
Copy Dennis' data step 1
Copy Dennis' Data Step 2

## Distributed Slack - Dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3403 | THOUSE_1G | 1 | North | YES | 0.36247 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.52966 | 563 | 563 | 204.0712 | 563 |  |  | 0.52966 | 298.1973 | 563 | 298.1973
3404 | THOUSE_2G | 2 | North | YES | 0.36247 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.52966 | 807 | 807 | 292.5141 | 807 |  |  | 0.52966 | 427.4338 | 1370 | 725.631
238 | BOSQUESW505 | 1 | North | YES | 0.22295 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.39013 | 255 | 255 | 56.851 | 255 |  |  | 0.39013 | 99.4836 | 1625 | 825.1146
239 | BOSQUESW502 | 1 | North | YES | 0.22295 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.39013 | 149 | 149 | 33.2188 | 149 |  |  | 0.39013 | 58.1296 | 1774 | 883.2443 | Weighted Shift Factors
247 | BOSQUESW501 | 2 | North | YES | 0.22295 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.39013 | 156 | 156 | 34.7794 | 156 |  |  | 0.39013 | 60.8605 | 1930 | 944.1048 | North | 0.14171
1941 | MDLTHELP_1G | 1 | North | YES | 0.18107 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.34826 | 216.4 | 216.4 | 39.1838 | 216.4 |  |  | 0.34826 | 75.363 |  |  | South | -0.16719
1942 | MDLTHELP_2G | 2 | North | YES | 0.18107 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.34826 | 216.1 | 216.1 | 39.1294 | 216.1 |  |  | 0.34826 | 75.2585 |  |  |  | 0.3089
1937 | MDLTHELP_5G | 5 | North | YES | 0.18086 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.34805 | 224 | 224 | 40.5131 | 224 |  |  | 0.34805 | 77.9629
1938 | MDLTHELP_6G | 6 | North | YES | 0.18086 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.34805 | 226 | 226 | 40.8748 | 226 |  |  | 0.34805 | 78.659 |  |  | Line Cap | 956
1943 | MDLTHELP_3G | 3 | North | YES | 0.18086 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.34805 | 212 | 212 | 38.3427 | 212 |  |  | 0.34805 | 73.7863 |  |  | Conc Gen | 1930
1944 | MDLTHELP_4G | 4 | North | YES | 0.18086 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.34805 | 211 | 211 | 38.1619 | 211 |  |  | 0.34805 | 73.4383 |  |  | Weighted Imp. | 944.1048
366 | JNSNCNTY802 | 1 | North | YES | 0.16688 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.33407 | 0 | 0 | 0 | 0 |  |  | 0.33407 | 0 |  |  | PTDF | 0.48917
367 | JNSNCNTY802 | 2 | North | YES | 0.16688 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.33407 | 0 | 0 | 0 | 0 |  |  | 0.33407 | 0
1947 | HANDLEY_3G | 3 | North | YES | 0.16683 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.33401 | 395 | 395 | 65.8959 | 395 |  |  | 0.33401 | 131.9346 |  |  | Concentration | 1.5836
1949 | HANDLEY_5G | 5 | North | YES | 0.16683 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.33401 | 435 | 435 | 72.5689 | 435 |  |  | 0.33401 | 145.2951
1948 | HANDLEY_4G | 4 | North | YES | 0.16607 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.33326 | 435 | 435 | 72.2413 | 435 |  |  | 0.33326 | 144.9675 |  |  |  | Pass
1945 | HANDLEY_1G | MB | North | YES | 0.16583 | 0 | 25 | 36 |  | 0.986 | #N/A | 1 | 0.33301 | 36 | 36 | 5.9698 | 36 |  |  | 0.33301 | 11.9885
1946 | HANDLEY_2G | MB | North | YES | 0.16583 | 0 | 30 | 68 |  | 0.986 | #N/A | 1 | 0.33301 | 68 | 68 | 11.2763 | 68 |  |  | 0.33301 | 22.645
1889 | DECRDOVA_1G | 1 | North | YES | 0.1652 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.33239 | 779 | 779 | 128.6947 | 779 |  |  | 0.33239 | 258.9331
1877 | WLFHOLW_1G | 1 | North | YES | 0.1652 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.33239 | 217.3 | 217.3 | 35.898 | 217.3 |  |  | 0.33239 | 72.2276
1878 | WLFHOLW_2G | 2 | North | YES | 0.1652 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.33239 | 215.7 | 215.7 | 35.6336 | 215.7 |  |  | 0.33239 | 71.6958
1879 | WLFHOLW_3G | 3 | North | YES | 0.1652 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.33239 | 272.4 | 272.4 | 45.0005 | 272.4 |  |  | 0.33239 | 90.5421
1898 | COMCHEPK_1G | 1 | North | YES | 0.16435 | 1159 | 1150 | 1159 | 0 | 1.032 | Nuc | 1 | 0.33154 | 0 | 0 | 0 | 0 |  |  | 0.33154 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.16435 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.33154 | 0 | 0 | 0 | 0 |  |  | 0.33154 | 0
1892 | DECRDOVA_2G | A | North | YES | 0.16307 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.33026 | 70 | 70 | 11.4152 | 70 |  |  | 0.33026 | 23.1182
1893 | DECRDOVA_3G | B | North | YES | 0.16307 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.33026 | 69 | 69 | 11.2521 | 69 |  |  | 0.33026 | 22.788
1894 | DECRDOVA_4G | C | North | YES | 0.16307 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.33026 | 69 | 69 | 11.2521 | 69 |  |  | 0.33026 | 22.788
1895 | DECRDOVA_5G | D | North | YES | 0.16307 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.33026 | 68 | 68 | 11.089 | 68 |  |  | 0.33026 | 22.4577
1861 | EAGLEMNT_1G | MB | North | YES | 0.16195 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.32913 | 0 | 0 | 0 | 0 |  |  | 0.32913 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.16195 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.32913 | 0 | 0 | 0 | 0 |  |  | 0.32913 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.16195 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.32913 | 0 | 0 | 0 | 0 |  |  | 0.32913 | 0
580 | JCKCNTY801 | 1 | North | YES | 0.15807 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.32526 | 288 | 288 | 45.5256 | 288 |  |  | 0.32526 | 93.6754
581 | JCKCNTY802 | 2 | North | YES | 0.15807 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.32526 | 147 | 147 | 23.237 | 147 |  |  | 0.32526 | 47.8135
582 | JCKCNTY803 | 3 | North | YES | 0.15807 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.32526 | 147 | 147 | 23.237 | 147 |  |  | 0.32526 | 47.8135
503 | NTHTEXAS01 | 1 | North | YES | 0.15804 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.32522 | 18 | 18 | 2.8447 | 18 |  |  | 0.32522 | 5.854
504 | NTHTEXAS02 | 2 | North | YES | 0.15804 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.32522 | 18 | 18 | 2.8447 | 18 |  |  | 0.32522 | 5.854
505 | NTHTEXAS03 | 3 | North | YES | 0.15804 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.32522 | 38 | 38 | 6.0054 | 38 |  |  | 0.32522 | 12.3585
1453 | WCPWRCO_1G | 1 | North | YES | 0.15785 | 204 | 50 | 204 |  | 1.02 | CC | 1 | 0.32504 | 204 | 204 | 32.2014 | 204 |  |  | 0.32504 | 66.3075
1454 | WCPWRCO_2G | 2 | North | YES | 0.15785 | 204 | 50 | 204 |  | 1.02 | CC | 1 | 0.32504 | 204 | 204 | 32.2014 | 204 |  |  | 0.32504 | 66.3075
1455 | WCPWRCO_3G | 3 | North | YES | 0.15785 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.32504 | 242 | 242 | 38.1997 | 242 |  |  | 0.32504 | 78.6589
251 | BOSQUESW803 | 2 | North | YES | 0.15777 | 150 | 0 | 150 |  | 1.032 | CC | 1 | 0.32496 | 150 | 150 | 23.6659 | 150 |  |  | 0.32496 | 48.744
253 | BOSQUESW804 | 2 | North | YES | 0.15777 | 80 | 0 | 80 |  | 1.032 | CC | 1 | 0.32496 | 80 | 80 | 12.6218 | 80 |  |  | 0.32496 | 25.9968
923 | SPENCER_G4 | 1 | North | YES | 0.1567 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.32389 | 61 | 61 | 9.5589 | 61 |  |  | 0.32389 | 19.7573
924 | SPENCER_G5 | 1 | North | YES | 0.1567 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.32389 | 66 | 66 | 10.3424 | 66 |  |  | 0.32389 | 21.3767
2418 | MTCK2_G | 2 | North | YES | 0.15634 | 0 | 10 | 23 |  | 0.971 | #N/A | 1 | 0.32352 | 23 | 23 | 3.5958 | 23 |  |  | 0.32352 | 7.441
2419 | MTCK3_G | MB | North | YES | 0.15634 | 0 | 10 | 63 |  | 0.971 | #N/A | 1 | 0.32352 | 63 | 63 | 9.8492 | 63 |  |  | 0.32352 | 20.382
728 | WOLFRIDGE801 | 1 | North | YES | 0.15629 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.32347 | 0 | 112.5 | 17.5821 | 112.5 |  |  | 0.32347 | 36.3906
2381 | NTHLK1_G | 1 | North | YES | 0.15593 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.32312 | 156 | 156 | 24.3259 | 156 |  |  | 0.32312 | 50.407
2382 | NTHLK2_G | 2 | North | YES | 0.15593 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.32312 | 181 | 181 | 28.2242 | 181 |  |  | 0.32312 | 58.485
2383 | NTHLK3_G | 3 | North | YES | 0.15593 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.32312 | 329 | 329 | 51.3026 | 329 |  |  | 0.32312 | 106.307
244 | WHITNYDM01 | 1 | North | YES | 0.15549 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.32267 | 0 | 0 | 0 | 0 |  |  | 0.32267 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.15549 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.32267 | 0 | 0 | 0 | 0 |  |  | 0.32267 | 0
332 | RWMILLER01 | 1 | North | YES | 0.15523 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.32242 | 73 | 73 | 11.3319 | 73 |  |  | 0.32242 | 23.5365
333 | RWMILLER02 | 2 | North | YES | 0.15523 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.32242 | 119 | 119 | 18.4725 | 119 |  |  | 0.32242 | 38.3677
334 | RWMILLER03 | 3 | North | YES | 0.15523 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.32242 | 208 | 208 | 32.288 | 208 |  |  | 0.32242 | 67.0629
335 | RWMILLER04 | 4 | North | YES | 0.15523 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.32242 | 102 | 102 | 15.8336 | 102 |  |  | 0.32242 | 32.8866
336 | RWMILLER05 | 5 | North | YES | 0.15523 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.32242 | 101 | 101 | 15.6783 | 101 |  |  | 0.32242 | 32.5642
344 | MRSSHPRD | 1 | North | YES | 0.15515 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.32233 | 0 | 0 | 0 | 0 |  |  | 0.32233 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.15515 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.32233 | 0 | 0 | 0 | 0 |  |  | 0.32233 | 0
1600 | BARTNWND_1G | 1 | North | YES | 0.15482 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.32201 | 0 | 120 | 18.5783 | 120 |  |  | 0.32201 | 38.6407
2413 | MTCK6_G | 6 | North | YES | 0.1539 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.32109 | 118 | 118 | 18.1608 | 118 |  |  | 0.32109 | 37.8888
2414 | MTCK7_G | 7 | North | YES | 0.1539 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.32109 | 115 | 115 | 17.6991 | 115 |  |  | 0.32109 | 36.9255
2417 | MTCK8_G | 8 | North | YES | 0.1539 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.32109 | 556 | 556 | 85.5712 | 556 |  |  | 0.32109 | 178.527
2371 | COLLIN_1G | MB | North | YES | 0.15349 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.32068 | 0 | 0 | 0 | 0 |  |  | 0.32068 | 0
1432 | GRHAMSES_2G | 2 | North | YES | 0.15324 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.32043 | 366 | 366 | 56.0858 | 366 |  |  | 0.32043 | 117.2762
1479 | WFCOGEN_1G | 2 | North | YES | 0.15289 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.32008 | 0 | 0 | 0 | 0 |  |  | 0.32008 | 0
1479 | WFCOGEN_1G | 1 | North | YES | 0.15289 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.32008 | 0 | 0 | 0 | 0 |  |  | 0.32008 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.15289 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.32008 | 0 | 0 | 0 | 0 |  |  | 0.32008 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.15289 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.32008 | 0 | 0 | 0 | 0 |  |  | 0.32008 | 0
1433 | GRHAMSES_1G | 1 | North | YES | 0.15193 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.31911 | 242 | 242 | 36.7661 | 242 |  |  | 0.31911 | 77.2253
6948 | DENISNDM | 2 | North | YES | 0.15123 | 31 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.31841 | 0 | 0 | 0 | 0 |  |  | 0.31841 | 0
6948 | DENISNDM | 1 | North | YES | 0.15123 | 40 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.31841 | 0 | 0 | 0 | 0 |  |  | 0.31841 | 0
1687 | VALLEY_1G | 1 | North | YES | 0.15075 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.31793 | 170 | 170 | 25.627 | 170 |  |  | 0.31793 | 54.0487
1688 | VALLEY_2G | 2 | North | YES | 0.15075 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.31793 | 527 | 527 | 79.4437 | 527 |  |  | 0.31793 | 167.5511
1689 | VALLEY_3G | 3 | North | YES | 0.15022 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.31741 | 375 | 375 | 56.3332 | 375 |  |  | 0.31741 | 119.0283
11691 | KMICHICT1_G | 1 | North | YES | 0.15022 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.31741 | 144 | 144 | 21.632 | 144 |  |  | 0.31741 | 45.7069
11692 | KMICHICT2_G | 2 | North | YES | 0.15022 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.31741 | 146 | 146 | 21.9324 | 146 |  |  | 0.31741 | 46.3417
11693 | KMICHIST3_G | 3 | North | YES | 0.15022 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.31741 | 312 | 312 | 46.8693 | 312 |  |  | 0.31741 | 99.0315
11694 | KMICHICT4_G | 4 | North | YES | 0.15022 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.31741 | 144 | 144 | 21.632 | 144 |  |  | 0.31741 | 45.7069
11695 | KMICHICT5_G | 5 | North | YES | 0.15022 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.31741 | 148 | 148 | 22.2329 | 148 |  |  | 0.31741 | 46.9765
11696 | KMICHIST6_G | 6 | North | YES | 0.15022 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.31741 | 310 | 310 | 46.5688 | 310 |  |  | 0.31741 | 98.3967
1678 | LAMARPWR_1G | 1 | North | YES | 0.14984 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.31703 | 160 | 160 | 23.9746 | 160 |  |  | 0.31703 | 50.7244
1679 | LAMARPWR_2G | 2 | North | YES | 0.14984 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.31703 | 156 | 156 | 23.3752 | 156 |  |  | 0.31703 | 49.4563
1680 | LAMARPWR_3G | 3 | North | YES | 0.14984 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.31703 | 196 | 196 | 29.3688 | 196 |  |  | 0.31703 | 62.1374
1681 | LAMARPWR_4G | 4 | North | YES | 0.14984 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.31703 | 156 | 156 | 23.3752 | 156 |  |  | 0.31703 | 49.4563
1682 | LAMARPWR_5G | 5 | North | YES | 0.14984 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.31703 | 157 | 157 | 23.525 | 157 |  |  | 0.31703 | 49.7733
1683 | LAMARPWR_6G | 6 | North | YES | 0.14984 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.31703 | 198 | 198 | 29.6685 | 198 |  |  | 0.31703 | 62.7715
1675 | PEC_1G | 1 | North | YES | 0.14948 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.31667 | 0 | 0 | 0 | 0 |  |  | 0.31667 | 0
1676 | PEC_2G | 2 | North | YES | 0.14948 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.31667 | 0 | 0 | 0 | 0 |  |  | 0.31667 | 0
1677 | PEC_3G | 3 | North | YES | 0.14948 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.31667 | 0 | 0 | 0 | 0 |  |  | 0.31667 | 0
1701 | MOSES_1G | 1 | North | YES | 0.14924 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.31643 | 0 | 558 | 83.2759 | 558 |  |  | 0.31643 | 176.5661
1702 | MOSES_2G | 2 | North | YES | 0.14924 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.31643 | 0 | 579 | 86.41 | 579 |  |  | 0.31643 | 183.2111
1703 | MOSES_3G | 3 | North | YES | 0.14924 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.31643 | 0 | 808 | 120.5859 | 808 |  |  | 0.31643 | 255.6728
5925 | DCEAST | EQ | North | YES | 0.14924 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.31643 | 0 | 0 | 0 | 0 |  |  | 0.31643 | 0
6100 | OKLA7A | EQ | West | YES | 0.14893 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.31612 | 0 | 0 |  |  |  |  | 0.31612 | 0
6752 | OKLA0A | 1 | West | YES | 0.14893 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.31612 | 0 | 649.7 |  |  |  |  | 0.31612 | 205.3836
842 | OLINGER_G1 | 1 | North | YES | 0.14836 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.31555 | 79 | 79 | 11.7205 | 79 |  |  | 0.31555 | 24.9283
843 | OLINGER_G2 | 1 | North | YES | 0.14836 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.31555 | 110 | 110 | 16.3197 | 110 |  |  | 0.31555 | 34.7102
844 | OLINGER_G3 | 1 | North | YES | 0.14836 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.31555 | 150 | 150 | 22.2541 | 150 |  |  | 0.31555 | 47.3322
845 | OLINGER_G4 | 1 | North | YES | 0.14836 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.31555 | 76 | 76 | 11.2754 | 76 |  |  | 0.31555 | 23.9816
12440 | PARKD_1SVC8 | 1 | North | YES | 0.14835 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.31554 | 0 | 0 | 0 | 0 |  |  | 0.31554 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.14835 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.31554 | 0 | 0 | 0 | 0 |  |  | 0.31554 | 0
837 | NEWMAN_G5 | 1 | North | YES | 0.14808 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.31526 | 40 | 40 | 5.923 | 40 |  |  | 0.31526 | 12.6105
1442 | COKFIELD_5 | 1 | North | YES | 0.14795 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.31514 | 0 | 165 | 24.4121 | 165 |  |  | 0.31514 | 51.9979
949 | STEAM2 | 1 | North | YES | 0.14779 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.31497 | 26 | 26 | 3.8425 | 26 |  |  | 0.31497 | 8.1893
950 | STEAM3 | 1 | North | YES | 0.14779 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.31497 | 42 | 42 | 6.2071 | 42 |  |  | 0.31497 | 13.2289
948 | STEAM1 | 1 | North | YES | 0.14779 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.31497 | 20 | 20 | 2.9557 | 20 |  |  | 0.31497 | 6.2995
2451 | LKHB1_G | 1 | North | YES | 0.14757 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.31476 | 391 | 391 | 57.7003 | 391 |  |  | 0.31476 | 123.0703
2452 | LKHB2_G | 2 | North | YES | 0.14757 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.31476 | 516 | 516 | 76.1466 | 516 |  |  | 0.31476 | 162.415
1643 | SLSTR1PP_1G | 1 | North | YES | 0.14657 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.31376 | 0 | 60 | 8.7943 | 60 |  |  | 0.31376 | 18.8255
1438 | MESQUITW_2G | 1 | North | YES | 0.14628 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.31347 | 0 | 236 | 34.5228 | 236 |  |  | 0.31347 | 73.9788
1437 | MESQUITW_1G | 1 | North | YES | 0.14627 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.31346 | 0 | 400 | 58.5092 | 400 |  |  | 0.31346 | 125.3839
12411 | FPLEFR1A_G | 1 | North | YES | 0.1451 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.31228 | 161 | 161 | 23.3606 | 161 |  |  | 0.31228 | 50.2777
12412 | FPLEFR1B_G | 2 | North | YES | 0.1451 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.31228 | 164 | 164 | 23.7959 | 164 |  |  | 0.31228 | 51.2145
12413 | FPLEFR1C_G | 3 | North | YES | 0.1451 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.31228 | 164 | 164 | 23.7959 | 164 |  |  | 0.31228 | 51.2145
12414 | FPLEFR1S_G | 4 | North | YES | 0.1451 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.31228 | 414 | 414 | 60.0702 | 414 |  |  | 0.31228 | 129.2855
12421 | FPLEFR2A_G | 1 | North | YES | 0.1451 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.31228 | 162 | 162 | 23.5057 | 162 |  |  | 0.31228 | 50.59
12422 | FPLEFR2B_G | 2 | North | YES | 0.1451 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.31228 | 161 | 161 | 23.3606 | 161 |  |  | 0.31228 | 50.2777
12423 | FPLEFR2C_G | 3 | North | YES | 0.1451 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.31228 | 163 | 163 | 23.6508 | 163 |  |  | 0.31228 | 50.9022
12424 | FPLEFR2S_G | 4 | North | YES | 0.1451 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.31228 | 415 | 415 | 60.2153 | 415 |  |  | 0.31228 | 129.5977
12322 | ENNSTRAC_1G | 1 | North | YES | 0.14463 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.31182 | 196 | 196 | 28.3481 | 196 |  |  | 0.31182 | 61.1167
12323 | ENNSTRAC_2G | 2 | North | YES | 0.14463 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.31182 | 116 | 116 | 16.7774 | 116 |  |  | 0.31182 | 36.1711
60052 | WILDHRS11A | 1 | West | YES | 0.14403 | 25.3 | 0 | 126.5 | 0 | 1.005 | #N/A | 1 | 0.31122 | 126.5 | 126.5 |  |  |  |  | 0.31122 | 39.3688
60053 | WILDHRS21A | 1 | West | YES | 0.14403 | 7.8 | 0 | 39 | 0 | 1.025 | #N/A | 1 | 0.31122 | 39 | 39 |  |  |  |  | 0.31122 | 12.1374
60081 | WHRLWIND1A | 1 | West | YES | 0.14286 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.31004 | 0 | 60 |  |  |  |  | 0.31004 | 18.6025
1416 | SWETWATR_1G | 1 | West | YES | 0.14217 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.30936 | 30 | 30 |  |  |  |  | 0.30936 | 9.2809
1417 | SWETWATR_2G | 2 | West | YES | 0.14217 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.30936 | 72 | 72 |  |  |  |  | 0.30936 | 22.274
1418 | SWETWATR_3G | 3 | West | YES | 0.14217 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.30936 | 68 | 68 |  |  |  |  | 0.30936 | 21.0366
1419 | SWETWATR_4G | 4 | West | YES | 0.14217 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.30936 | 61 | 61 |  |  |  |  | 0.30936 | 18.8711
1049 | ROSCOEWI_5 | 1 | West | YES | 0.14132 | 41.8 | 0 | 209 |  | 1.01 | #N/A | 1 | 0.30851 | 209 | 209 |  |  |  |  | 0.30851 | 64.4777
1057 | ROSCOEWI_5 | 2 | West | YES | 0.14132 | 25.3 | 0 | 126.5 |  | 1.01 | #N/A | 1 | 0.30851 | 126.5 | 126.5 |  |  |  |  | 0.30851 | 39.026
1060 | ROSCOEWI_5 | 3 | West | YES | 0.14132 | 39.4 | 0 | 197 | 0 | 1.01 | #N/A | 1 | 0.30851 | 197 | 197 |  |  |  |  | 0.30851 | 60.7756
1072 | ROSCOEWI_5 | 4 | West | YES | 0.14132 | 63.6 | 0 | 318 | 0 | 1.01 | #N/A | 1 | 0.30851 | 318 | 318 |  |  |  |  | 0.30851 | 98.1048
71051 | L_BITTCR1_1N | W1 | West | YES | 0.14112 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.3083 | 0 | 37.5 |  |  |  |  | 0.3083 | 11.5614
71054 | L_SWEETW1_1N | W1 | West | YES | 0.14112 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.3083 | 0 | 107.5 |  |  |  |  | 0.3083 | 33.1428
71057 | L_SWEETW1_2N | W1 | West | YES | 0.14112 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.3083 | 0 | 135 |  |  |  |  | 0.3083 | 41.6211
71059 | L_SWEETW1_3N | W1 | West | YES | 0.14112 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.3083 | 0 | 119 |  |  |  |  | 0.3083 | 36.6883
71060 | L_SWEETW1_4N | W1 | West | YES | 0.14112 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.3083 | 0 | 105 |  |  |  |  | 0.3083 | 32.372
6144 | MCADOO1A | 1 | West | YES | 0.14102 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.30821 | 0 | 150 |  |  |  |  | 0.30821 | 46.2316
36998 | RDCNYNG1 | 1 | West | YES | 0.13972 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.30691 | 0 | 84 |  |  |  |  | 0.30691 | 25.7805
1061 | CIELOGEN_1G | 1 | West | YES | 0.13943 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.30661 | 0 | 99 |  |  |  |  | 0.30661 | 30.3548
1062 | CIELOGEN_2G | 1 | West | YES | 0.13943 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.30661 | 0 | 61 |  |  |  |  | 0.30661 | 18.7034
1069 | KINDERMG_1G | 1 | West | YES | 0.13943 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.30661 | 0 | 0 |  |  |  |  | 0.30661 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.13943 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30661 | 0 | 0 |  |  |  |  | 0.30661 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.13943 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30661 | 0 | 0 |  |  |  |  | 0.30661 | 0
1068 | SCURRYCW_1G | 1 | West | YES | 0.13941 | 28.2 | 1.3 | 141 |  | 1.01 | Wind | 1 | 0.3066 | 0 | 141 |  |  |  |  | 0.3066 | 43.2301
1073 | SCURRYCW_2G | 2 | West | YES | 0.13941 | 24 | 0 | 120 | 0 | 1.017 | Wind | 1 | 0.3066 | 0 | 120 |  |  |  |  | 0.3066 | 36.7916
6637 | SNYDERW1A | 1 | West | YES | 0.13929 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.30647 | 0 | 63 |  |  |  |  | 0.30647 | 19.3079
1037 | MORGAN5G_5G | 5 | West | YES | 0.13922 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.30641 | 137 | 137 |  |  |  |  | 0.30641 | 41.9777
1039 | MRGNAG_1G | A | West | YES | 0.13922 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.30641 | 69 | 69 |  |  |  |  | 0.30641 | 21.1421
1040 | MRGNBG_2G | B | West | YES | 0.13922 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.30641 | 71 | 71 |  |  |  |  | 0.30641 | 21.7549
1041 | MRGNCG_3G | C | West | YES | 0.13922 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.30641 | 70 | 70 |  |  |  |  | 0.30641 | 21.4485
1042 | MRGNDG_4G | D | West | YES | 0.13922 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.30641 | 68 | 68 |  |  |  |  | 0.30641 | 20.8357
1043 | MRGNEG_5G | E | West | YES | 0.13922 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.30641 | 70 | 70 |  |  |  |  | 0.30641 | 21.4485
1044 | MRGNFG_6G | F | West | YES | 0.13922 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.30641 | 66 | 66 |  |  |  |  | 0.30641 | 20.2228
1343 | TRENTIPP_8 | 1 | West | YES | 0.13914 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.30632 | 0 | 150 |  |  |  |  | 0.30632 | 45.9486
1354 | AEPWIND_8 | 1 | West | YES | 0.13914 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.30632 | 0 | 101 |  |  |  |  | 0.30632 | 30.9387
1058 | LONGSHORE_5 | 3 | West | YES | 0.13906 | 23.4 | 0 | 117 |  | 1.01 | Wind | 1 | 0.30624 | 0 | 117 |  |  |  |  | 0.30624 | 35.8306
1058 | LONGSHORE_5 | 2 | West | YES | 0.13906 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.30624 | 0 | 220 |  |  |  |  | 0.30624 | 67.3738
1058 | LONGSHORE_5 | 1 | West | YES | 0.13906 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.30624 | 0 | 150 |  |  |  |  | 0.30624 | 45.9367
1301 | BULLCREK_8 | 1 | West | YES | 0.13901 | 36 | 0 | 180 | 0 | 1.017 | #N/A | 1 | 0.30619 | 180 | 180 |  |  |  |  | 0.30619 | 55.1149
60058 | BUFF_GAP1A | 1 | West | YES | 0.13886 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.30604 | 0 | 120 |  |  |  |  | 0.30604 | 36.725
60060 | CIRELLO | 1 | West | YES | 0.13886 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.30604 | 0 | 233 |  |  |  |  | 0.30604 | 71.3077
60063 | BUFF_GAP1B | 1 | West | YES | 0.13886 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.30604 | 0 | 170.2 |  |  |  |  | 0.30604 | 52.0883
60066 | H_HOLLOW1A | 1 | West | YES | 0.13886 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.30604 | 0 | 222 |  |  |  |  | 0.30604 | 67.9413
60068 | HHOLLOW21A | 1 | West | YES | 0.13886 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.30604 | 0 | 184 |  |  |  |  | 0.30604 | 56.3117
60070 | HHOLLOW31A | 1 | West | YES | 0.13886 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.30604 | 0 | 224 |  |  |  |  | 0.30604 | 68.5533
60072 | HHOLLOW41A | 1 | West | YES | 0.13886 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.30604 | 0 | 115 |  |  |  |  | 0.30604 | 35.1948
1045 | CALENG1G_1G | 1 | West | YES | 0.13872 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30591 | 0 | 0 |  |  |  |  | 0.30591 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.13872 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30591 | 0 | 0 |  |  |  |  | 0.30591 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.13872 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.30591 | 0 | 0 |  |  |  |  | 0.30591 | 0
1302 | COYOTEWG_8 | 1 | West | YES | 0.13852 | 45 | 0 | 225 |  | 1.01 | #N/A | 1 | 0.30571 | 225 | 225 |  |  |  |  | 0.30571 | 68.7849
1360 | GUNSIGHT_8 | 1 | West | YES | 0.13822 | 24 | 0 | 120 | 0 | 1.01 | Wind | 1 | 0.30541 | 0 | 120 |  |  |  |  | 0.30541 | 36.6492
1327 | WILDHRSE_1G | 1 | West | YES | 0.13819 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.30537 | 0 | 120 |  |  |  |  | 0.30537 | 36.6448
1170 | AIRLAMESA_1G | 1 | West | YES | 0.13785 | 0 | 0 | 180 |  | 1 | #N/A | 1 | 0.30504 | 180 | 180 |  |  |  |  | 0.30504 | 54.907
1333 | MCDDONAL_8 | 1 | West | YES | 0.13749 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.30468 | 0 | 214.2 |  |  |  |  | 0.30468 | 65.2617
11001 | NAV1CT | 1 | West | YES | 0.13728 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.30447 | 70.4 | 70.4 |  |  |  |  | 0.30447 | 21.4347
11009 | NAV2CT | 1 | West | YES | 0.13728 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.30447 | 71.4 | 71.4 |  |  |  |  | 0.30447 | 21.7391
11011 | NAV3ST | 1 | West | YES | 0.13728 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.30447 | 92.8 | 92.8 |  |  |  |  | 0.30447 | 28.2548
11012 | NAV4CT | 1 | West | YES | 0.13728 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30447 | 80 | 80 |  |  |  |  | 0.30447 | 24.3576
11013 | NAV5CT | 1 | West | YES | 0.13728 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30447 | 80 | 80 |  |  |  |  | 0.30447 | 24.3576
11014 | NAV6ST | 1 | West | YES | 0.13728 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.30447 | 115 | 115 |  |  |  |  | 0.30447 | 35.014
1326 | STANTONW_8 | 1 | West | YES | 0.13726 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.30445 | 0 | 100.5 |  |  |  |  | 0.30445 | 30.5972
11020 | TIEHVSG_1G | 1 | West | YES | 0.13726 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.30445 | 208.2 | 208.2 |  |  |  |  | 0.30445 | 63.3858
11021 | TIEHVCG_1G | 1 | West | YES | 0.13726 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.30445 | 142.1 | 142.1 |  |  |  |  | 0.30445 | 43.2619
11022 | TIEHVCG_2G | 1 | West | YES | 0.13726 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.30445 | 132.4 | 132.4 |  |  |  |  | 0.30445 | 40.3087
11023 | TIEHVCG_3G | 1 | West | YES | 0.13726 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.30445 | 137.4 | 137.4 |  |  |  |  | 0.30445 | 41.831
11024 | TIEHVCG_4G | 1 | West | YES | 0.13726 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.30445 | 147 | 147 |  |  |  |  | 0.30445 | 44.7537
11025 | TIEHVSG_2G | 1 | West | YES | 0.13726 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.30445 | 213.2 | 213.2 |  |  |  |  | 0.30445 | 64.908
1320 | BSP 1 | 1 | West | YES | 0.13723 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.30442 | 0 | 0 |  |  |  |  | 0.30442 | 0
1328 | OCOTILLO_1G | 1 | West | YES | 0.13721 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.3044 | 0 | 58 |  |  |  |  | 0.3044 | 17.655
60057 | CALLAHAN1A | 1 | West | YES | 0.13634 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.30352 | 0 | 114 |  |  |  |  | 0.30352 | 34.6017
76031 | L_GASCCR1_1N | W1 | West | YES | 0.13595 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.30314 | 0 | 150 |  |  |  |  | 0.30314 | 45.4713
1146 | NOTREES_1G | 1 | West | YES | 0.13584 | 29.8 | 0 | 149 | 0 | 1.017 | #N/A | 1 | 0.30303 | 149 | 149 |  |  |  |  | 0.30303 | 45.1517
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.13561 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.3028 | 0 | 35 |  |  |  |  | 0.3028 | 10.598
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.13561 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.3028 | 0 | 30 |  |  |  |  | 0.3028 | 9.084
1002 | PBCTAGE_1G | A | West | YES | 0.13549 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.30268 | 66 | 66 |  |  |  |  | 0.30268 | 19.9767
1003 | PBCTBGE_2G | B | West | YES | 0.13549 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.30268 | 66 | 66 |  |  |  |  | 0.30268 | 19.9767
1004 | PBCTCGE_3G | C | West | YES | 0.13549 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.30268 | 67 | 67 |  |  |  |  | 0.30268 | 20.2793
1005 | PBCTDGE_4G | D | West | YES | 0.13549 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.30268 | 68 | 68 |  |  |  |  | 0.30268 | 20.582
1006 | PBCTEGE_5G | E | West | YES | 0.13549 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.30268 | 67 | 67 |  |  |  |  | 0.30268 | 20.2793
1007 | PB5GEN_6G | 5 | West | YES | 0.13549 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.30268 | 114 | 114 |  |  |  |  | 0.30268 | 34.5051
1008 | PB6GEN_7G | 6 | West | YES | 0.13549 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.30268 | 515 | 515 |  |  |  |  | 0.30268 | 155.8785
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.13526 | 110 | 0 | 550 | 0 | 1.02 | Wind | 1 | 0.30244 | 0 | 550 |  |  |  |  | 0.30244 | 166.344
1349 | WESTXWIN_1G | 1 | West | YES | 0.13491 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.3021 | 0 | 6.6 |  |  |  |  | 0.3021 | 1.9938
1350 | NWPWRG1_1G | 1 | West | YES | 0.13491 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.3021 | 0 | 34.3 |  |  |  |  | 0.3021 | 10.362
3097 | MARTLAKE_1G | 1 | North | YES | 0.13248 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.29966 | 0 | 790 | 104.656 | 790 |  |  | 0.29966 | 236.7335
3098 | MARTLAKE_2G | 2 | North | YES | 0.13248 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.29966 | 0 | 795 | 105.3184 | 795 |  |  | 0.29966 | 238.2318
3099 | MARTLAKE_3G | 3 | North | YES | 0.13248 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.29966 | 0 | 804 | 106.5107 | 804 |  |  | 0.29966 | 240.9288
6407 | TURKTRAK1A | 1 | West | YES | 0.13167 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.29885 | 0 | 169.5 |  |  |  |  | 0.29885 | 50.6557
13116 | TGATEWAY_1G | 1 | North | YES | 0.13091 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.2981 | 151 | 151 | 19.7679 | 151 |  |  | 0.2981 | 45.0131
13117 | TGATEWAY_2G | 2 | North | YES | 0.13091 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.2981 | 130 | 130 | 17.0187 | 130 |  |  | 0.2981 | 38.753
13118 | TGATEWAY_3G | 3 | North | YES | 0.13091 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.2981 | 148 | 148 | 19.3751 | 148 |  |  | 0.2981 | 44.1188
13119 | TGATEWAY_4G | 4 | North | YES | 0.13091 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.2981 | 399 | 399 | 52.2343 | 399 |  |  | 0.2981 | 118.9418
3348 | CHAMPION_1G | MB | North | YES | 0.12867 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.29585 | 0 | 0 | 0 | 0 |  |  | 0.29585 | 0
3113 | LUFKINWB_1G | 1 | North | YES | 0.12858 | 0 | 0 | 50 |  | 1.01 | #N/A | 1 | 0.29577 | 50 | 50 | 6.429 | 50 |  |  | 0.29577 | 14.7883
3107 | STRYKER_1G | 1 | North | YES | 0.12614 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.29332 | 182 | 182 | 22.9568 | 182 |  |  | 0.29332 | 53.3847
3108 | STRYKER_2G | 2 | North | YES | 0.12614 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.29332 | 484 | 484 | 61.0498 | 484 |  |  | 0.29332 | 141.9682
3126 | TRINIDAD_6G | 1 | North | YES | 0.12423 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.29142 | 224 | 224 | 27.8284 | 224 |  |  | 0.29142 | 65.2782
60007 | KING_SW1A | 1 | West | YES | 0.12379 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.29098 | 0 | 80 |  |  |  |  | 0.29098 | 23.2781
60019 | KING_NW1A | 1 | West | YES | 0.12379 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.29098 | 0 | 80 |  |  |  |  | 0.29098 | 23.2781
60201 | RIO DRCS | F | West | YES | 0.12285 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.29003 | 0 | 0 |  |  |  |  | 0.29003 | 0
60016 | WOODWRD11A | 1 | West | YES | 0.12276 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.28995 | 0 | 80 |  |  |  |  | 0.28995 | 23.1959
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.12273 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.28992 | 0 | 80 |  |  |  |  | 0.28992 | 23.1937
38437 | TNSRBNMESA9 | 1 | West | YES | 0.12265 | 37.5 | 0 | 150 |  | 1.02 | Wind | 1 | 0.28984 | 0 | 150 |  |  |  |  | 0.28984 | 43.4755
6016 | SWMESA | 1 | West | YES | 0.12224 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.28942 | 0 | 75 |  |  |  |  | 0.28942 | 21.7067
60003 | KING_NE1A | 1 | West | YES | 0.12224 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.28942 | 0 | 80 |  |  |  |  | 0.28942 | 23.1538
60005 | KING_SE1A | 1 | West | YES | 0.12224 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.28942 | 0 | 40 |  |  |  |  | 0.28942 | 11.5769
60000 | DSKY2 | 1 | West | YES | 0.12071 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.2879 | 0 | 76.5 |  |  |  |  | 0.2879 | 22.0241
60017 | ORNNWP1 | 1 | West | YES | 0.11987 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.28706 | 0 | 80 |  |  |  |  | 0.28706 | 22.9648
60018 | DSKY1 | 1 | West | YES | 0.11895 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.28613 | 0 | 84 |  |  |  |  | 0.28613 | 24.0351
13134 | CALFREST_4G | 4 | North | YES | 0.11536 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.28255 | 151.5 | 151.5 | 17.4772 | 151.5 |  |  | 0.28255 | 42.806
13135 | CALFREST_5G | 5 | North | YES | 0.11536 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.28255 | 152.3 | 152.3 | 17.5695 | 152.3 |  |  | 0.28255 | 43.032
13136 | CALFREST_6G | 6 | North | YES | 0.11536 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.28255 | 177.5 | 177.5 | 20.4766 | 177.5 |  |  | 0.28255 | 50.1522
13131 | CALFREST_1G | 1 | North | YES | 0.11507 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.28225 | 150.7 | 150.7 | 17.3403 | 150.7 |  |  | 0.28225 | 42.5353
13132 | CALFREST_2G | 2 | North | YES | 0.11507 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.28225 | 151 | 151 | 17.3748 | 151 |  |  | 0.28225 | 42.62
13133 | CALFREST_3G | 3 | North | YES | 0.11507 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.28225 | 177.4 | 177.4 | 20.4125 | 177.4 |  |  | 0.28225 | 50.0715
3381 | BBRN_1G | 1 | North | YES | 0.11149 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.27867 | 0 | 618 | 68.8983 | 618 |  |  | 0.27867 | 172.2197
3382 | BBRN_2G | 2 | North | YES | 0.11149 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.27867 | 0 | 589 | 65.6653 | 589 |  |  | 0.27867 | 164.1382
60202 | FRNDDRCS | F | West | YES | 0.10021 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.2674 | 0 | 0 |  |  |  |  | 0.2674 | 0
48721 | LEG_1___1 | 1 | North | YES | 0.068969 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.23616 | 0 | 827 | 57.0374 | 827 |  |  | 0.23616 | 195.3008
48722 | LEG_2___2 | 2 | North | YES | 0.068969 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.23616 | 0 | 819 | 56.4856 | 819 |  |  | 0.23616 | 193.4115
39960 | TNTNPONE_18 | 1 | North | YES | 0.054304 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.22149 | 0 | 152.3 | 8.2705 | 152.3 |  |  | 0.22149 | 33.733
39970 | TNTNPONE_28 | 1 | North | YES | 0.054304 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.22149 | 0 | 153 | 8.3085 | 153 |  |  | 0.22149 | 33.8881
990 | GIBN_CREK_G1 | 1 | North | YES | 0.020701 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.18789 | 0 | 463 | 9.5846 | 463 |  |  | 0.18789 | 86.992
48671 | FTR_GT1_5105 | 1 | North | YES | 0.012112 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.1793 | 154.2 | 154.2 | 1.8677 | 154.2 |  |  | 0.1793 | 27.6479
48672 | FTR_GT2_5110 | 2 | North | YES | 0.012112 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.1793 | 159 | 159 | 1.9258 | 159 |  |  | 0.1793 | 28.5085
48673 | FTR_GT3_5085 | 3 | North | YES | 0.012112 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.1793 | 158 | 158 | 1.9137 | 158 |  |  | 0.1793 | 28.3292
48674 | FTR_CN4_5095 | 4 | North | YES | 0.012112 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.1793 | 380 | 380 | 4.6026 | 380 |  |  | 0.1793 | 68.1335
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.00583 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.17302 | 32 | 32 | 0.18656 | 32 |  |  | 0.17302 | 5.5365
32886 | BRYN_ATKINS3 | MB | North | YES | 0.00154 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.16873 | 0 | 0 | 0 | 0 |  |  | 0.16873 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.00154 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.16873 | 0 | 0 | 0 | 0 |  |  | 0.16873 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.00154 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.16873 | 17 | 17 | 0.02618 | 17 |  |  | 0.16873 | 2.8684
32890 | BRYN_ATKINS4 | MB | North | YES | 0.00154 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.16873 | 0 | 0 | 0 | 0 |  |  | 0.16873 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.00154 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.16873 | 0 | 0 | 0 | 0 |  |  | 0.16873 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | -2.1e-05 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.16717 | 48 | 48 | -0.001008 | 48 |  |  | 0.16717 | 8.024
32884 | BRYN_DNSBY13 | 1 | North | YES | -2.1e-05 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.16717 | 46 | 46 | -0.000966 | 46 |  |  | 0.16717 | 7.6896
32892 | BRYN_DNSBY14 | 1 | North | YES | -2.1e-05 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.16717 | 105 | 105 | -0.002205 | 105 |  |  | 0.16717 | 17.5524
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.14171 | 15 | 15 |  |  | 0 | 15 | -0.14171 | -2.1257
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8442 | NUECES_B0A | MB | South | YES | 0 | 0 | 81 | 367 |  | 1.03 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.14171 | 0 | 0 |  |  |  |  | -0.14171 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.033793 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.17551 | 0 | 0 |  |  |  |  | -0.17551 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.033793 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.17551 | 0 | 0 |  |  |  |  | -0.17551 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.033793 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.17551 | 0 | 0 |  |  |  |  | -0.17551 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.033793 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.17551 | 0 | 0 |  |  |  |  | -0.17551 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.033793 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.17551 | 0 | 0 |  |  |  |  | -0.17551 | 0
48885 | THW_5152 | A | Houston | YES | -0.038871 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.18058 | 58 | 58 |  |  |  |  | -0.18058 | -10.4738
48885 | THW_5152 | B | Houston | YES | -0.038871 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.18058 | 59 | 59 |  |  |  |  | -0.18058 | -10.6544
48886 | THW_5354 | D | Houston | YES | -0.038871 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.18058 | 58 | 58 |  |  |  |  | -0.18058 | -10.4738
48886 | THW_5354 | C | Houston | YES | -0.038871 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.18058 | 57 | 57 |  |  |  |  | -0.18058 | -10.2932
48887 | THW_5556 | E | Houston | YES | -0.038871 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.18058 | 59 | 59 |  |  |  |  | -0.18058 | -10.6544
48887 | THW_5556 | F | Houston | YES | -0.038871 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.18058 | 57 | 57 |  |  |  |  | -0.18058 | -10.2932
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.039234 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.18095 | 398 | 398 |  |  |  |  | -0.18095 | -72.0165
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.039482 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.18119 | 162.8 | 162.8 |  |  |  |  | -0.18119 | -29.4984
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.039482 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.18119 | 161.4 | 161.4 |  |  |  |  | -0.18119 | -29.2447
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.039482 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.18119 | 158.9 | 158.9 |  |  |  |  | -0.18119 | -28.7917
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.039482 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.18119 | 269.2 | 269.2 |  |  |  |  | -0.18119 | -48.7774
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.040314 | 172 | 0 | 172 | 0 | 1.026 | GSC | -1 | 0.18203 | 172 | 172 |  |  |  |  | -0.18203 | -31.3085
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.040314 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.18203 | 172 | 172 |  |  |  |  | -0.18203 | -31.3085
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.040314 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.18203 | 172 | 172 |  |  |  |  | -0.18203 | -31.3085
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.040472 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.18218 | 0 | 0 |  |  |  |  | -0.18218 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.040685 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.1824 | 744 | 744 |  |  |  |  | -0.1824 | -135.7034
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.040737 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.040737 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.040737 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.040737 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.040737 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.040737 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.040737 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.040749 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.18246 | 0 | 0 |  |  |  |  | -0.18246 | 0
48651 | EP_1_2 | 2 | Houston | YES | -0.040749 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.18246 | 0 | 0 |  |  |  |  | -0.18246 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.041397 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.18311 | 12 | 12 |  |  |  |  | -0.18311 | -2.1973
49803 | EXN_15GT | 1 | Houston | YES | -0.041534 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.041534 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.041534 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.041534 | 43 | 9.2 | 45.9 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.041534 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.041534 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.041534 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.041534 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.041534 | 18.5 | 9.2 | 18.5 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.041534 | 81 | 21.3 | 85.4 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.041534 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.041822 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.18353 | 746 | 746 |  |  |  |  | -0.18353 | -136.9164
3416 | LAKE_CRK1_G | 1 | North | YES | -0.35082 | 60 | 33 | 75 |  | 1.029 | GST | 1 | -0.18364 | 75 | 75 | -26.3117 | 75 |  |  | -0.18364 | -13.7727
3417 | LAKE_CRK2_G | 2 | North | YES | -0.35082 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | -0.18364 | 222 | 222 | -77.8827 | 222 |  |  | -0.18364 | -40.7673
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.042504 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.18422 | 107 | 107 |  |  |  |  | -0.18422 | -19.7111
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.042504 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.18422 | 108 | 108 |  |  |  |  | -0.18422 | -19.8953
48875 | THW_3132 | A | Houston | YES | -0.042504 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.18422 | 55 | 55 |  |  |  |  | -0.18422 | -10.1319
48875 | THW_3132 | B | Houston | YES | -0.042504 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.18422 | 53 | 53 |  |  |  |  | -0.18422 | -9.7634
48877 | THW_3334 | D | Houston | YES | -0.042504 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.18422 | 57 | 57 |  |  |  |  | -0.18422 | -10.5003
48877 | THW_3334 | C | Houston | YES | -0.042504 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.18422 | 55 | 55 |  |  |  |  | -0.18422 | -10.1319
48879 | THW_4142 | E | Houston | YES | -0.042504 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.18422 | 56 | 56 |  |  |  |  | -0.18422 | -10.3161
48879 | THW_4142 | F | Houston | YES | -0.042504 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.18422 | 55 | 55 |  |  |  |  | -0.18422 | -10.1319
48881 | THW_4344 | G | Houston | YES | -0.042504 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.18422 | 58 | 58 |  |  |  |  | -0.18422 | -10.6845
48881 | THW_4344 | H | Houston | YES | -0.042504 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.18422 | 58 | 58 |  |  |  |  | -0.18422 | -10.6845
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.043408 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.18512 | 0 | 0 |  |  |  |  | -0.18512 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.043408 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.18512 | 0 | 0 |  |  |  |  | -0.18512 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.04353 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.18524 | 42 | 42 |  |  |  |  | -0.18524 | -7.7802
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.04353 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.18524 | 42 | 42 |  |  |  |  | -0.18524 | -7.7802
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.04353 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.18524 | 39 | 39 |  |  |  |  | -0.18524 | -7.2244
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.04353 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.18524 | 39 | 39 |  |  |  |  | -0.18524 | -7.2244
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.043643 | 137.6 | 54.6 | 137.6 |  | 1.0362 | Cogen | -1 | 0.18536 | 0 | 0 |  |  |  |  | -0.18536 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.044274 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.18599 | 0 | 0 |  |  |  |  | -0.18599 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.044274 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.18599 | 0 | 0 |  |  |  |  | -0.18599 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.044274 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.18599 | 0 | 0 |  |  |  |  | -0.18599 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.044274 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.18599 | 0 | 0 |  |  |  |  | -0.18599 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.04471 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.18642 | 0 | 0 |  |  |  |  | -0.18642 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.04471 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.18642 | 0 | 0 |  |  |  |  | -0.18642 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.04471 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.18642 | 0 | 0 |  |  |  |  | -0.18642 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.044714 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.18643 | 228 | 228 |  |  |  |  | -0.18643 | -42.5051
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.044724 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.18644 | 0 | 0 |  |  |  |  | -0.18644 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.044724 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.18644 | 0 | 0 |  |  |  |  | -0.18644 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.044724 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.18644 | 0 | 0 |  |  |  |  | -0.18644 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.044724 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.18644 | 0 | 0 |  |  |  |  | -0.18644 | 0
48845 | SOL_GT1 | 1 | Houston | YES | -0.044728 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.18644 | 16.2 | 16.2 |  |  |  |  | -0.18644 | -3.0203
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.044735 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.18645 | 213 | 213 |  |  |  |  | -0.18645 | -39.7132
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.044806 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.18652 | 0 | 0 |  |  |  |  | -0.18652 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.044806 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.18652 | 0 | 0 |  |  |  |  | -0.18652 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.044817 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.18653 | 165 | 165 |  |  |  |  | -0.18653 | -30.7773
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.044841 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.18655 | 176 | 176 |  |  |  |  | -0.18655 | -32.8333
48855 | SRB_GT211035 | B2 | Houston | YES | -0.044859 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.18657 | 12 | 12 |  |  |  |  | -0.18657 | -2.2389
48855 | SRB_GT211035 | B1 | Houston | YES | -0.044859 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.18657 | 18 | 18 |  |  |  |  | -0.18657 | -3.3583
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.045172 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.18688 | 0 | 0 |  |  |  |  | -0.18688 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.045465 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.18718 | 163.2 | 163.2 |  |  |  |  | -0.18718 | -30.5473
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.045465 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.18718 | 157.1 | 157.1 |  |  |  |  | -0.18718 | -29.4055
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.045465 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.18718 | 157.5 | 157.5 |  |  |  |  | -0.18718 | -29.4804
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.045465 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.18718 | 157 | 157 |  |  |  |  | -0.18718 | -29.3868
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.045465 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.18718 | 282 | 282 |  |  |  |  | -0.18718 | -52.7839
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.045809 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.18752 | 0 | 0 |  |  |  |  | -0.18752 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.045809 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.18752 | 0 | 0 |  |  |  |  | -0.18752 | 0
48691 | GBY_73741085 | B | Houston | YES | -0.04623 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.18794 | 47 | 47 |  |  |  |  | -0.18794 | -8.8333
48691 | GBY_73741085 | A | Houston | YES | -0.04623 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.18794 | 47 | 47 |  |  |  |  | -0.18794 | -8.8333
48692 | GBY_81821075 | D | Houston | YES | -0.04623 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.18794 | 55 | 55 |  |  |  |  | -0.18794 | -10.3368
48692 | GBY_81821075 | C | Houston | YES | -0.04623 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.18794 | 47 | 47 |  |  |  |  | -0.18794 | -8.8333
48693 | GBY_83841065 | E | Houston | YES | -0.04623 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.18794 | 57 | 57 |  |  |  |  | -0.18794 | -10.7127
48693 | GBY_83841065 | F | Houston | YES | -0.04623 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.18794 | 54 | 54 |  |  |  |  | -0.18794 | -10.1489
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.047085 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.1888 | 0 | 0 |  |  |  |  | -0.1888 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.047085 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.1888 | 0 | 0 |  |  |  |  | -0.1888 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.047085 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.1888 | 0 | 0 |  |  |  |  | -0.1888 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.047085 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.1888 | 0 | 0 |  |  |  |  | -0.1888 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.047763 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.18948 | 0 | 0 |  |  |  |  | -0.18948 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.047763 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.18948 | 0 | 0 |  |  |  |  | -0.18948 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.047763 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.18948 | 0 | 0 |  |  |  |  | -0.18948 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.047763 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.18948 | 0 | 0 |  |  |  |  | -0.18948 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.047763 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.18948 | 0 | 0 |  |  |  |  | -0.18948 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.049536 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.19125 | 0 | 0 |  |  |  |  | -0.19125 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.052078 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.052078 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.052078 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.052078 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.052078 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.052078 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.052078 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.052078 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.052078 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.052078 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.052078 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.052078 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.052078 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.052078 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.052078 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.058127 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.19984 | 166 | 166 |  |  |  |  | -0.19984 | -33.1733
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.058127 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.19984 | 166 | 166 |  |  |  |  | -0.19984 | -33.1733
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.058127 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.19984 | 248 | 248 |  |  |  |  | -0.19984 | -49.5601
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.058127 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.19984 | 546 | 546 |  |  |  |  | -0.19984 | -109.1121
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.058127 | 598.9 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.19984 | 0 | 654 |  |  |  |  | -0.19984 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.058127 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.19984 | 13 | 13 |  |  |  |  | -0.19984 | -2.5979
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.058249 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.19996 | 0 | 0 |  |  |  |  | -0.19996 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.059545 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.20126 | 167.7 | 167.7 |  |  |  |  | -0.20126 | -33.7508
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.059545 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.20126 | 166.4 | 166.4 |  |  |  |  | -0.20126 | -33.4892
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.059545 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.20126 | 252.4 | 252.4 |  |  |  |  | -0.20126 | -50.7973
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.059622 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.20133 | 0 | 651 |  |  |  |  | -0.20133 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.059622 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.20133 | 0 | 564 |  |  |  |  | -0.20133 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.059622 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.20133 | 0 | 603 |  |  |  |  | -0.20133 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.059641 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.20135 | 0 | 0 |  |  |  |  | -0.20135 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.061492 | 33 | 13 | 33 | 0 | 1.0375 | Hydro | -1 | 0.2032 | 0 | 0 |  |  | 0 | 0 | -0.2032 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.061492 | 25 | 13 | 25 | 0 | 1.0375 | Hydro | -1 | 0.2032 | 0 | 0 |  |  | 0 | 0 | -0.2032 | 0
88253 | HAMILTON | F | South | YES | -0.061492 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.2032 | 0 | 0 |  |  | 0 | 0 | -0.2032 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.068879 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.21059 | 0 | 0 |  |  |  |  | -0.21059 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.068879 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.21059 | 0 | 0 |  |  |  |  | -0.21059 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.068879 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.21059 | 0 | 0 |  |  |  |  | -0.21059 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.068879 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.21059 | 0 | 0 |  |  |  |  | -0.21059 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.07143 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.21314 | 0 | 0 |  |  |  |  | -0.21314 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.07143 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.21314 | 0 | 0 |  |  |  |  | -0.21314 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.074659 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.074659 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.074659 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.074659 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.074659 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.074659 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.074659 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.074659 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.074659 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.074659 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.074659 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.074659 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.074659 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.074659 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.074659 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.074659 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.074659 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.074659 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.074659 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.074659 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
8262 | ELPS | 1 | South | YES | -0.084976 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.22669 | 0 | 0 |  |  | 0 | 0 | -0.22669 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.087415 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.22913 | 0 | 0 |  |  |  |  | -0.22913 | 0
80010 | EPLVT1 | F | South | YES | -0.090438 | 0 | 0 | 0 |  | 1.0376 | #N/A | -1 | 0.23215 | 0 | 0 |  |  | 0 | 0 | -0.23215 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.091652 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.23336 | 76 | 76 |  |  |  |  | -0.23336 | -17.7357
48732 | CBE_GT2 | 1 | Houston | YES | -0.091652 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.23336 | 76 | 76 |  |  |  |  | -0.23336 | -17.7357
48733 | CBE_ST12 | 1 | Houston | YES | -0.091652 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.23336 | 105 | 105 |  |  |  |  | -0.23336 | -24.5032
48734 | CBE_GT3 | 1 | Houston | YES | -0.091652 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.23336 | 76 | 76 |  |  |  |  | -0.23336 | -17.7357
48735 | CBE_GT4 | 1 | Houston | YES | -0.091652 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.23336 | 76 | 76 |  |  |  |  | -0.23336 | -17.7357
48736 | CBE_ST34 | 1 | Houston | YES | -0.091652 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.23336 | 105 | 105 |  |  |  |  | -0.23336 | -24.5032
5911 | STP_GN1___1 | 1 | Houston | YES | -0.092237 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.23395 | 0 | 0 |  |  |  |  | -0.23395 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.092237 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.23395 | 0 | 0 |  |  |  |  | -0.23395 | 0
8134 | FOR #1 | 1 | South | YES | -0.12545 | 54.1 | 45 | 79 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
8138 | FOR #2 | 2 | South | YES | -0.12545 | 63.1 | 45 | 81 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
8153 | FOR #3 | 3 | South | YES | -0.12545 | 63.1 | 45 | 79.9 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
8154 | FOR #4 | 4 | South | YES | -0.12545 | 63.1 | 60 | 80 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
8155 | FOR #5 | 5 | South | YES | -0.12545 | 63.1 | 60 | 78.4 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
8156 | FOR #6 | 6 | South | YES | -0.12545 | 24.9 | 5 | 25 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
8157 | FOR #7 | 7 | South | YES | -0.12545 | 28.8 | 5 | 46 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
80051 | FOR #8 | 8 | South | YES | -0.12545 | 28 | 28 | 28 | 0 | 1.016 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
80052 | FOR #9 | 9 | South | YES | -0.12545 | 29.7 | 5 | 43.6 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
80053 | FOR #10 | 10 | South | YES | -0.12545 | 68.4 | 45 | 75 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
80226 | ALCOA G | 1 | South | YES | -0.12637 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.26809 | 0 | 0 |  |  | 0 | 0 | -0.26809 | 0
8147 | UCAR #2 | 10 | South | YES | -0.12946 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
8148 | UCAR #1 | 2 | South | YES | -0.12946 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80137 | CSDR89 | 9 | South | YES | -0.12946 | 0 | 0 | 15 |  | 1.003 | DCTie | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80137 | CSDR89 | 8 | South | YES | -0.12946 | 33.9 | 0 | 39 |  | 1.003 | DCTie | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80138 | CSDR7 | 7 | South | YES | -0.12946 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80139 | CSDR56 | 6 | South | YES | -0.12946 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80139 | CSDR56 | 5 | South | YES | -0.12946 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80140 | CSDR11 | 11 | South | YES | -0.12946 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80227 | AIRCO G | 1 | South | YES | -0.12981 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.27152 | 0 | 0 |  |  | 0 | 0 | -0.27152 | 0
80265 | LARECU40A | 4 | South | YES | -0.13012 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.27184 | 100 | 100 |  |  | -13.0125 | 100 | -0.27184 | -27.1837
80266 | LARECU50A | 5 | South | YES | -0.13012 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.27184 | 100 | 100 |  |  | -13.0125 | 100 | -0.27184 | -27.1837
80012 | LAR | F | South | YES | -0.13013 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.27184 | 0 | 0 |  |  | 0 | 0 | -0.27184 | 0
80224 | VISTRONG1 | 1 | South | YES | -0.13064 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.27235 | 0 | 0 |  |  | 0 | 0 | -0.27235 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.13064 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.27235 | 0 | 0 |  |  | 0 | 0 | -0.27235 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.13164 | 17.6 | 6 | 22 | 0 | 1.0223 | GST | -1 | 0.27335 | 22 | 22 |  |  | -2.8961 | 22 | -0.27335 | -6.0138
5505 | RAYBURNGEN1 | 1 | South | YES | -0.13164 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.27335 | 11 | 11 |  |  | -1.4481 | 11 | -0.27335 | -3.0069
5506 | RAYBURNGEN2 | 1 | South | YES | -0.13164 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.27335 | 11 | 11 |  |  | -1.4481 | 11 | -0.27335 | -3.0069
88299 | ZAPATA | F | South | YES | -0.13184 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.27356 | 0 | 0 |  |  | 0 | 0 | -0.27356 | 0
5508 | RAYBURNCC9 | 1 | South | YES | -0.13273 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.27444 | 47.7 | 47.7 |  |  | -6.3312 | 47.7 | -0.27444 | -13.0909
5509 | RAYBURNCC10 | 1 | South | YES | -0.13273 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.27444 | 37.3 | 37.3 |  |  | -4.9508 | 37.3 | -0.27444 | -10.2367
5511 | RAYBURNCC7 | 1 | South | YES | -0.13273 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.27444 | 47.5 | 47.5 |  |  | -6.3047 | 47.5 | -0.27444 | -13.036
5512 | RAYBURNCC8 | 1 | South | YES | -0.13273 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.27444 | 49.3 | 49.3 |  |  | -6.5436 | 49.3 | -0.27444 | -13.53
8066 | DUP1V#1 | 1 | South | YES | -0.13287 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.13287 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.13287 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.13287 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
8930 | ICPGN10A | 1 | South | YES | -0.13287 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
8931 | ICPGN20A | 2 | South | YES | -0.13287 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
8932 | ICPGN30A | 3 | South | YES | -0.13287 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
80223 | REYSHR G | 1 | South | YES | -0.13287 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | -0.13303 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.27474 | 0 | 0 |  |  | 0 | 0 | -0.27474 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.13303 | 11 | 0 | 11 | 0 | 1.0227 | Hydro | -1 | 0.27474 | 0 | 0 |  |  | 0 | 0 | -0.27474 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.13303 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.27474 | 0 | 0 |  |  | 0 | 0 | -0.27474 | 0
88508 | FALFURRI | F | South | YES | -0.13369 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.2754 | 0 | 0 |  |  | 0 | 0 | -0.2754 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.13393 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.27564 | 0 | 0 |  |  | 0 | 0 | -0.27564 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.13393 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.27564 | 0 | 0 |  |  | 0 | 0 | -0.27564 | 0
8562 | CNOPST1 | 3 | South | YES | -0.13393 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.27564 | 0 | 0 |  |  | 0 | 0 | -0.27564 | 0
8456 | COSW#1 | 1 | South | YES | -0.13399 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.2757 | 0 | 0 |  |  | 0 | 0 | -0.2757 | 0
8457 | COSW#2 | 2 | South | YES | -0.13399 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.2757 | 0 | 0 |  |  | 0 | 0 | -0.2757 | 0
8459 | B_DAVIS0B | MB | South | YES | -0.13412 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.27584 | 0 | 0 |  |  | 0 | 0 | -0.27584 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.13412 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.27584 | 0 | 0 |  |  | 0 | 0 | -0.27584 | 0
8173 | VICEC51A | 5 | South | YES | -0.13415 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.27586 | 144 | 144 |  |  | -19.317 | 144 | -0.27586 | -39.7236
8174 | VICEC61A | 6 | South | YES | -0.13415 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.27586 | 188 | 188 |  |  | -25.2194 | 188 | -0.27586 | -51.8613
8506 | VAL #1 | 1 | South | YES | -0.13419 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.27591 | 0 | 0 |  |  | 0 | 0 | -0.27591 | 0
8507 | VAL #2 | 2 | South | YES | -0.13419 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.27591 | 0 | 0 |  |  | 0 | 0 | -0.27591 | 0
8933 | FGNTS001 | 1 | South | YES | -0.13427 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.27598 | 146.5 | 146.5 |  |  | -19.6701 | 146.5 | -0.27598 | -40.4309
8934 | FGNTS101 | 2 | South | YES | -0.13427 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.27598 | 147.9 | 147.9 |  |  | -19.8581 | 147.9 | -0.27598 | -40.8173
8935 | FGNTS201 | 3 | South | YES | -0.13427 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.27598 | 173 | 173 |  |  | -23.2282 | 173 | -0.27598 | -47.7444
8511 | OXY_CC0A | 1 | South | YES | -0.1343 | 30.3 | 0 | 38 |  | 1.027 | Cogen | -1 | 0.27602 | 0 | 0 |  |  | 0 | 0 | -0.27602 | 0
8461 | KOCH_UP0A | 1 | South | YES | -0.13431 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.27602 | 0 | 0 |  |  | 0 | 0 | -0.27602 | 0
8936 | MVGN#1 | 1 | South | YES | -0.13447 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.27618 | 216.6 | 216.6 |  |  | -29.126 | 216.6 | -0.27618 | -59.8208
8937 | MVGN#2 | 2 | South | YES | -0.13447 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.27618 | 216.7 | 216.7 |  |  | -29.1394 | 216.7 | -0.27618 | -59.8484
8938 | MVGN#3 | 3 | South | YES | -0.13447 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.27618 | 250.9 | 250.9 |  |  | -33.7383 | 250.9 | -0.27618 | -69.2938
8981 | HECN1 | 1 | South | YES | -0.13447 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.27618 | 144.8 | 144.8 |  |  | -19.4713 | 144.8 | -0.27618 | -39.9912
8982 | HECN2 | 2 | South | YES | -0.13447 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.27618 | 144.1 | 144.1 |  |  | -19.3771 | 144.1 | -0.27618 | -39.7978
8983 | HECN3 | 3 | South | YES | -0.13447 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.27618 | 171.9 | 171.9 |  |  | -23.1154 | 171.9 | -0.27618 | -47.4757
5932 | SI_RAY9 | 9 | South | YES | -0.13462 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.27633 | 38 | 38 |  |  | -5.1156 | 38 | -0.27633 | -10.5006
5933 | SI_RAY6 | 6 | South | YES | -0.13462 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.27633 | 19.3 | 19.3 |  |  | -2.5982 | 19.3 | -0.27633 | -5.3332
5935 | SI_RAY10 | 10 | South | YES | -0.13462 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.27633 | 47 | 47 |  |  | -6.3271 | 47 | -0.27633 | -12.9876
80003 | MILHWYS | F | South | YES | -0.13462 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.27633 | 0 | 0 |  |  | 0 | 0 | -0.27633 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.13466 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.27637 | 0 | 0 |  |  | 0 | 0 | -0.27637 | 0
80080 | GWINDT11A | 2 | South | YES | -0.1347 | 17.7 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 41 |  |  | 0 | 0 | -0.27642 | 0
80080 | GWINDT11A | 3 | South | YES | -0.1347 | 16.4 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 38 |  |  | 0 | 0 | -0.27642 | 0
80080 | GWINDT11A | 4 | South | YES | -0.1347 | 8.2 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 19 |  |  | 0 | 0 | -0.27642 | 0
80080 | GWINDT11A | 1 | South | YES | -0.1347 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 94 |  |  | 0 | 0 | -0.27642 | 0
80081 | GWINDT21A | 3 | South | YES | -0.1347 | 18.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 43 |  |  | 0 | 0 | -0.27642 | 0
80081 | GWINDT21A | 2 | South | YES | -0.1347 | 15.5 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 36 |  |  | 0 | 0 | -0.27642 | 0
80081 | GWINDT21A | 1 | South | YES | -0.1347 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 94 |  |  | 0 | 0 | -0.27642 | 0
80081 | GWINDT21A | 4 | South | YES | -0.1347 | 9.5 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 22 |  |  | 0 | 0 | -0.27642 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.1347 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 50 |  |  | 0 | 0 | -0.27642 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.1347 | 63 | 0 | 146 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 146 |  |  | 0 | 0 | -0.27642 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.1347 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 50 |  |  | 0 | 0 | -0.27642 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.1347 | 23.7 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 55 |  |  | 0 | 0 | -0.27642 | 0
8161 | COLETO0A | 1 | South | YES | -0.13959 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.2813 | 0 | 633 |  |  | 0 | 0 | -0.2813 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.14078 | 19.2 | 6 | 24 | 0 | 1.0161 | GST | -1 | 0.28249 | 24 | 24 |  |  | -3.3786 | 24 | -0.28249 | -6.7797
5891 | PEARSALLGEN2 | 1 | South | YES | -0.14078 | 19.4 | 6 | 24.3 | 0 | 1.0161 | GST | -1 | 0.28249 | 24.3 | 24.3 |  |  | -3.4209 | 24.3 | -0.28249 | -6.8645
5892 | PEARSALLGEN3 | 1 | South | YES | -0.14078 | 19.1 | 6 | 23.9 | 0 | 1.0161 | GST | -1 | 0.28249 | 23.9 | 23.9 |  |  | -3.3646 | 23.9 | -0.28249 | -6.7515
88198 | BEEVILLE | F | South | YES | -0.14085 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.28256 | 0 | 0 |  |  | 0 | 0 | -0.28256 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.1513 | 396.3 | 180 | 396.3 | 0 | 1.0331 | LIGCO | -1 | 0.29301 | 0 | 396.3 |  |  | 0 | 0 | -0.29301 | 0
8189 | CUECPL2A | 1 | South | YES | -0.15753 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.29925 | 0 | 0 |  |  | 0 | 0 | -0.29925 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.15828 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.29999 | 58 | 58 |  |  | -9.18 | 58 | -0.29999 | -17.3993
5265 | LEON_LCP4G4 | 4 | South | YES | -0.15828 | 71.2 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.29999 | 89 | 89 |  |  | -14.0866 | 89 | -0.29999 | -26.6989
5266 | LEON_LCPCT1 | 1 | South | YES | -0.15828 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.29999 | 44 | 44 |  |  | -6.9641 | 44 | -0.29999 | -13.1995
5267 | LEON_LCPCT2 | 2 | South | YES | -0.15828 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.29999 | 44 | 44 |  |  | -6.9641 | 44 | -0.29999 | -13.1995
5268 | LEON_LCPCT3 | 3 | South | YES | -0.15828 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.29999 | 43 | 43 |  |  | -6.8059 | 43 | -0.29999 | -12.8995
5269 | LEON_LCPCT4 | 4 | South | YES | -0.15828 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.29999 | 45 | 45 |  |  | -7.1224 | 45 | -0.29999 | -13.4995
5401 | CALAVER_JKS1 | 1 | South | YES | -0.15868 | 562 | 100 | 562 | 0 | 1.018 | LIGCO | -1 | 0.3004 | 0 | 562 |  |  | 0 | 0 | -0.3004 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.15927 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.30098 | 407 | 407 |  |  | -64.8221 | 407 | -0.30098 | -122.4989
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.15932 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.30104 | 155 | 155 |  |  | -24.6954 | 155 | -0.30104 | -46.6607
5477 | BRA_AVR1_ST1 | 1 | South | YES | -0.15932 | 174 | 138 | 174 | 0 | 1.017 | CC | -1 | 0.30104 | 174 | 174 |  |  | -27.7225 | 174 | -0.30104 | -52.3804
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.15932 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.30104 | 155 | 155 |  |  | -24.6954 | 155 | -0.30104 | -46.6607
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.15937 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.30108 | 215 | 215 |  |  | -34.2641 | 215 | -0.30108 | -64.7322
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.15937 | 172.8 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.30108 | 216 | 216 |  |  | -34.4235 | 216 | -0.30108 | -65.0333
5031 | BRA_VHBCT1 | 1 | South | YES | -0.15937 | 44 | 24 | 44 | 0 | 1.0192 | #N/A | -1 | 0.30108 | 44 | 44 |  |  | -7.0122 | 44 | -0.30108 | -13.2475
5032 | BRA_VHBCT2 | 2 | South | YES | -0.15937 | 44 | 24 | 44 | 0 | 1.0192 | #N/A | -1 | 0.30108 | 44 | 44 |  |  | -7.0122 | 44 | -0.30108 | -13.2475
5033 | BRA_VHBCT3 | 3 | South | YES | -0.15937 | 43 | 24 | 43 | 0 | 1.0192 | #N/A | -1 | 0.30108 | 43 | 43 |  |  | -6.8528 | 43 | -0.30108 | -12.9464
5034 | BRA_VHBCT4 | 4 | South | YES | -0.15937 | 45 | 24 | 45 | 0 | 1.0192 | #N/A | -1 | 0.30108 | 45 | 45 |  |  | -7.1716 | 45 | -0.30108 | -13.5486
5396 | CALAVER_OWS1 | 1 | South | YES | -0.15955 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.30127 | 418 | 418 |  |  | -66.6932 | 418 | -0.30127 | -125.9288
5397 | CALAVER_OWS2 | 2 | South | YES | -0.15955 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.30127 | 400 | 400 |  |  | -63.8212 | 400 | -0.30127 | -120.506
5111 | CALAVER_JTD1 | 1 | South | YES | -0.15971 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.30142 | 0 | 430 |  |  | 0 | 0 | -0.30142 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.15971 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.30142 | 0 | 430 |  |  | 0 | 0 | -0.30142 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.16028 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.302 | 61 | 61 |  |  | -9.7773 | 61 | -0.302 | -18.4218
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.16028 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.302 | 95 | 95 |  |  | -15.227 | 95 | -0.302 | -28.6896
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.16028 | 120.8 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.302 | 151 | 151 |  |  | -24.2029 | 151 | -0.302 | -45.6014
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.164 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.30572 | 147 | 147 |  |  | -24.1084 | 147 | -0.30572 | -44.9401
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.164 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.30572 | 138 | 138 |  |  | -22.6324 | 138 | -0.30572 | -42.1887
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.164 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.30572 | 146 | 146 |  |  | -23.9444 | 146 | -0.30572 | -44.6344
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.164 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.30572 | 149 | 149 |  |  | -24.4364 | 149 | -0.30572 | -45.5515
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.164 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.30572 | 182 | 182 |  |  | -29.8485 | 182 | -0.30572 | -55.6401
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.164 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.30572 | 203 | 203 |  |  | -33.2926 | 203 | -0.30572 | -62.0601
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.16584 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.30755 | 0 | 0 |  |  | 0 | 0 | -0.30755 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.16665 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.30837 | 0 | 0 |  |  | 0 | 0 | -0.30837 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.16665 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.30837 | 0 | 0 |  |  | 0 | 0 | -0.30837 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.16735 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.30906 | 0 | 0 |  |  | 0 | 0 | -0.30906 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.16928 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.311 | 0 | 0 |  |  | 0 | 0 | -0.311 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.16928 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.311 | 0 | 0 |  |  | 0 | 0 | -0.311 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.16928 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.311 | 0 | 0 |  |  | 0 | 0 | -0.311 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.16952 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.31124 | 148 | 148 |  |  | -25.0894 | 148 | -0.31124 | -46.0628
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.16952 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.31124 | 148 | 148 |  |  | -25.0894 | 148 | -0.31124 | -46.0628
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.16952 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.31124 | 154 | 154 |  |  | -26.1065 | 154 | -0.31124 | -47.9302
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.16952 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.31124 | 293 | 293 |  |  | -49.6702 | 293 | -0.31124 | -91.1919
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.17228 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.314 | 423.3 | 423.3 |  |  | -72.9278 | 423.3 | -0.314 | -132.9145
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.17284 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.31455 | 0 | 0 |  |  | 0 | 0 | -0.31455 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.17284 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.31455 | 0 | 0 |  |  | 0 | 0 | -0.31455 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.17284 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.31455 | 0 | 0 |  |  | 0 | 0 | -0.31455 | 0
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.17375 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.31546 | 0 | 0 |  |  | 0 | 0 | -0.31546 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.17375 | 23 | 0 | 29.8 |  | 1 | Hydro | -1 | 0.31546 | 0 | 0 |  |  | 0 | 0 | -0.31546 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.17538 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.31709 | 223.9 | 223.9 |  |  | -39.2671 | 223.9 | -0.31709 | -70.9965
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.17538 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.31709 | 225 | 225 |  |  | -39.4601 | 225 | -0.31709 | -71.3453
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.17538 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.31709 | 224.6 | 224.6 |  |  | -39.3899 | 224.6 | -0.31709 | -71.2184
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.17538 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.31709 | 226.7 | 226.7 |  |  | -39.7582 | 226.7 | -0.31709 | -71.8843
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.17737 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.31909 | 0 | 0 |  |  | 0 | 0 | -0.31909 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.17859 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.3203 | 0 | 0 |  |  | 0 | 0 | -0.3203 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.17859 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.3203 | 0 | 0 |  |  | 0 | 0 | -0.3203 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.17975 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.32147 | 50 | 50 |  |  | -8.9878 | 50 | -0.32147 | -16.0734
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.17975 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.32147 | 50 | 50 |  |  | -8.9878 | 50 | -0.32147 | -16.0734
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.17975 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.32147 | 50 | 50 |  |  | -8.9878 | 50 | -0.32147 | -16.0734
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.17975 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.32147 | 50 | 50 |  |  | -8.9878 | 50 | -0.32147 | -16.0734
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.18022 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.32194 | 0 | 436 |  |  | 0 | 0 | -0.32194 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.18039 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.3221 | 0 | 606 |  |  | 0 | 0 | -0.3221 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.18039 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.3221 | 0 | 598 |  |  | 0 | 0 | -0.3221 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.19288 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.3346 | 0 | 0 |  |  | 0 | 0 | -0.3346 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.19288 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.3346 | 0 | 0 |  |  | 0 | 0 | -0.3346 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.19288 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.3346 | 0 | 0 |  |  | 0 | 0 | -0.3346 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.19419 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.3359 | 132 | 132 |  |  | -25.6332 | 132 | -0.3359 | -44.3392
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.19419 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.3359 | 139 | 139 |  |  | -26.9925 | 139 | -0.3359 | -46.6905
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.19419 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.3359 | 329 | 329 |  |  | -63.8888 | 329 | -0.3359 | -110.5121
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.1997 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.34141 | 0 | 0 |  |  | 0 | 0 | -0.34141 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.1997 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.34141 | 0 | 0 |  |  | 0 | 0 | -0.34141 | 0
9016 | SANDH_G1 | 1 | South | YES | -0.19973 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.34145 | 49 | 49 |  |  | -9.787 | 49 | -0.34145 | -16.7309
9017 | SANDH_G2 | 2 | South | YES | -0.19973 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.34145 | 46 | 46 |  |  | -9.1878 | 46 | -0.34145 | -15.7066
9018 | SANDH_G3 | 3 | South | YES | -0.19973 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.34145 | 46 | 46 |  |  | -9.1878 | 46 | -0.34145 | -15.7066
9019 | SANDH_G4 | 4 | South | YES | -0.19973 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.34145 | 47 | 47 |  |  | -9.3875 | 47 | -0.34145 | -16.048
9020 | SANDHG5A | 5A | South | YES | -0.19973 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.34145 | 155 | 155 |  |  | -30.9589 | 155 | -0.34145 | -52.9243
9021 | SANDHG5C | 5C | South | YES | -0.19973 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.34145 | 148 | 148 |  |  | -29.5608 | 148 | -0.34145 | -50.5342
9000 | DECKR_G1 | 1 | South | YES | -0.20105 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.34276 | 321 | 321 |  |  | -64.5377 | 321 | -0.34276 | -110.0272
9001 | DECKR_G2 | 2 | South | YES | -0.20105 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.34276 | 426 | 426 |  |  | -85.6482 | 426 | -0.34276 | -146.0175
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.2013 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.34301 | 158 | 158 |  |  | -31.8051 | 158 | -0.34301 | -54.1956
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.2013 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.34301 | 160 | 160 |  |  | -32.2077 | 160 | -0.34301 | -54.8816
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.2013 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.34301 | 175 | 175 |  |  | -35.2272 | 175 | -0.34301 | -60.0268
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.20189 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.3436 | 152.5 | 152.5 |  |  | -30.7882 | 152.5 | -0.3436 | -52.3993
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.20189 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.3436 | 149.5 | 149.5 |  |  | -30.1826 | 149.5 | -0.3436 | -51.3685
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.20189 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.3436 | 232.6 | 232.6 |  |  | -46.9596 | 232.6 | -0.3436 | -79.9218
9002 | DECKR_G3 | 3 | South | YES | -0.20292 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.34464 | 42 | 42 |  |  | -8.5229 | 42 | -0.34464 | -14.4748
9003 | DECKR_G4 | 4 | South | YES | -0.20292 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.34464 | 44 | 44 |  |  | -8.9287 | 44 | -0.34464 | -15.164
9004 | DECKR_G5 | 5 | South | YES | -0.20292 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.34464 | 44 | 44 |  |  | -8.9287 | 44 | -0.34464 | -15.164
9005 | DECKR_G6 | 6 | South | YES | -0.20292 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.34464 | 47 | 47 |  |  | -9.5375 | 47 | -0.34464 | -16.1979
3432 | SANDOW_4G | 4 | South | YES | -0.2471 | 580 | 225 | 580 | 0 | 1.029 | LIGCO | -1 | 0.38881 | 0 | 580 |  |  | 0 | 0 | -0.38881 | 0
13432 | SANDOW_5G | 5 | South | YES | -0.2471 | 581 | 225 | 581 | 0 | 1.029 | LIGCO | -1 | 0.38881 | 0 | 581 |  |  | 0 | 0 | -0.38881 | 0
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4G | 4 | South | YES | -0.2471 | 580 | 225 | 580 | 0 | 1.029 | LIGCO | -1 | 0.38881 | 0 | 580 |  |  | 0 | 0 | -0.38881 | 0 | 0 | 0
13432 | SANDOW_5G | 5 | South | YES | -0.2471 | 581 | 225 | 581 | 0 | 1.029 | LIGCO | -1 | 0.38881 | 0 | 581 |  |  | 0 | 0 | -0.38881 | 0 | 0 | 0
9002 | DECKR_G3 | 3 | South | YES | -0.20292 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.34464 | 42 | 42 |  |  | -8.5229 | 42 | -0.34464 | -14.4748 | 42 | 14.4748
9003 | DECKR_G4 | 4 | South | YES | -0.20292 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.34464 | 44 | 44 |  |  | -8.9287 | 44 | -0.34464 | -15.164 | 86 | 29.6388 | Weighted Shift Factors
9004 | DECKR_G5 | 5 | South | YES | -0.20292 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.34464 | 44 | 44 |  |  | -8.9287 | 44 | -0.34464 | -15.164 | 130 | 44.8028 | North | 0.14171
9005 | DECKR_G6 | 6 | South | YES | -0.20292 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.34464 | 47 | 47 |  |  | -9.5375 | 47 | -0.34464 | -16.1979 | 177 | 61.0007 | South | -0.16719
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.20189 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.3436 | 152.5 | 152.5 |  |  | -30.7882 | 152.5 | -0.3436 | -52.3993 | 329.5 | 113.4001 |  | 0.3089
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.20189 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.3436 | 149.5 | 149.5 |  |  | -30.1826 | 149.5 | -0.3436 | -51.3685 | 479 | 164.7686
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.20189 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.3436 | 232.6 | 232.6 |  |  | -46.9596 | 232.6 | -0.3436 | -79.9218 | 711.6 | 244.6904 | Line Cap | 956
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.2013 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.34301 | 158 | 158 |  |  | -31.8051 | 158 | -0.34301 | -54.1956 | 869.6 | 298.886 | Conc Gen | 1951.6
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.2013 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.34301 | 160 | 160 |  |  | -32.2077 | 160 | -0.34301 | -54.8816 | 1029.6 | 353.7676 | Weighted Imp. | 669.839
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.2013 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.34301 | 175 | 175 |  |  | -35.2272 | 175 | -0.34301 | -60.0268 | 1204.6 | 413.7943 | PTDF | 0.34323
9000 | DECKR_G1 | 1 | South | YES | -0.20105 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.34276 | 321 | 321 |  |  | -64.5377 | 321 | -0.34276 | -110.0272 | 1525.6 | 523.8216
9001 | DECKR_G2 | 2 | South | YES | -0.20105 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.34276 | 426 | 426 |  |  | -85.6482 | 426 | -0.34276 | -146.0175 | 1951.6 | 669.839 | Concentration | 1.1111
9016 | SANDH_G1 | 1 | South | YES | -0.19973 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.34145 | 49 | 49 |  |  | -9.787 | 49 | -0.34145 | -16.7309
9017 | SANDH_G2 | 2 | South | YES | -0.19973 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.34145 | 46 | 46 |  |  | -9.1878 | 46 | -0.34145 | -15.7066 |  |  |  | Pass
9018 | SANDH_G3 | 3 | South | YES | -0.19973 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.34145 | 46 | 46 |  |  | -9.1878 | 46 | -0.34145 | -15.7066
9019 | SANDH_G4 | 4 | South | YES | -0.19973 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.34145 | 47 | 47 |  |  | -9.3875 | 47 | -0.34145 | -16.048
9020 | SANDHG5A | 5A | South | YES | -0.19973 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.34145 | 155 | 155 |  |  | -30.9589 | 155 | -0.34145 | -52.9243
9021 | SANDHG5C | 5C | South | YES | -0.19973 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.34145 | 148 | 148 |  |  | -29.5608 | 148 | -0.34145 | -50.5342
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.1997 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.34141 | 0 | 0 |  |  | 0 | 0 | -0.34141 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.1997 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.34141 | 0 | 0 |  |  | 0 | 0 | -0.34141 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.19419 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.3359 | 132 | 132 |  |  | -25.6332 | 132 | -0.3359 | -44.3392
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.19419 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.3359 | 139 | 139 |  |  | -26.9925 | 139 | -0.3359 | -46.6905
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.19419 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.3359 | 329 | 329 |  |  | -63.8888 | 329 | -0.3359 | -110.5121
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.19288 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.3346 | 0 | 0 |  |  | 0 | 0 | -0.3346 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.19288 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.3346 | 0 | 0 |  |  | 0 | 0 | -0.3346 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.19288 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.3346 | 0 | 0 |  |  | 0 | 0 | -0.3346 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.18039 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.3221 | 0 | 606 |  |  | 0 | 0 | -0.3221 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.18039 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.3221 | 0 | 598 |  |  | 0 | 0 | -0.3221 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.18022 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.32194 | 0 | 436 |  |  | 0 | 0 | -0.32194 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.17975 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.32147 | 50 | 50 |  |  | -8.9878 | 50 | -0.32147 | -16.0734
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.17975 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.32147 | 50 | 50 |  |  | -8.9878 | 50 | -0.32147 | -16.0734
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.17975 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.32147 | 50 | 50 |  |  | -8.9878 | 50 | -0.32147 | -16.0734
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.17975 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.32147 | 50 | 50 |  |  | -8.9878 | 50 | -0.32147 | -16.0734
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.17859 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.3203 | 0 | 0 |  |  | 0 | 0 | -0.3203 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.17859 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.3203 | 0 | 0 |  |  | 0 | 0 | -0.3203 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.17737 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.31909 | 0 | 0 |  |  | 0 | 0 | -0.31909 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.17538 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.31709 | 223.9 | 223.9 |  |  | -39.2671 | 223.9 | -0.31709 | -70.9965
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.17538 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.31709 | 225 | 225 |  |  | -39.4601 | 225 | -0.31709 | -71.3453
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.17538 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.31709 | 224.6 | 224.6 |  |  | -39.3899 | 224.6 | -0.31709 | -71.2184
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.17538 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.31709 | 226.7 | 226.7 |  |  | -39.7582 | 226.7 | -0.31709 | -71.8843
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.17375 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.31546 | 0 | 0 |  |  | 0 | 0 | -0.31546 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.17375 | 23 | 0 | 29.8 |  | 1 | Hydro | -1 | 0.31546 | 0 | 0 |  |  | 0 | 0 | -0.31546 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.17284 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.31455 | 0 | 0 |  |  | 0 | 0 | -0.31455 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.17284 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.31455 | 0 | 0 |  |  | 0 | 0 | -0.31455 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.17284 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.31455 | 0 | 0 |  |  | 0 | 0 | -0.31455 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.17228 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.314 | 423.3 | 423.3 |  |  | -72.9278 | 423.3 | -0.314 | -132.9145
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.16952 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.31124 | 148 | 148 |  |  | -25.0894 | 148 | -0.31124 | -46.0628
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.16952 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.31124 | 148 | 148 |  |  | -25.0894 | 148 | -0.31124 | -46.0628
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.16952 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.31124 | 154 | 154 |  |  | -26.1065 | 154 | -0.31124 | -47.9302
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.16952 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.31124 | 293 | 293 |  |  | -49.6702 | 293 | -0.31124 | -91.1919
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.16928 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.311 | 0 | 0 |  |  | 0 | 0 | -0.311 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.16928 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.311 | 0 | 0 |  |  | 0 | 0 | -0.311 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.16928 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.311 | 0 | 0 |  |  | 0 | 0 | -0.311 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.16735 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.30906 | 0 | 0 |  |  | 0 | 0 | -0.30906 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.16665 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.30837 | 0 | 0 |  |  | 0 | 0 | -0.30837 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.16665 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.30837 | 0 | 0 |  |  | 0 | 0 | -0.30837 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.16584 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.30755 | 0 | 0 |  |  | 0 | 0 | -0.30755 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.164 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.30572 | 147 | 147 |  |  | -24.1084 | 147 | -0.30572 | -44.9401
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.164 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.30572 | 138 | 138 |  |  | -22.6324 | 138 | -0.30572 | -42.1887
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.164 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.30572 | 146 | 146 |  |  | -23.9444 | 146 | -0.30572 | -44.6344
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.164 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.30572 | 149 | 149 |  |  | -24.4364 | 149 | -0.30572 | -45.5515
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.164 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.30572 | 182 | 182 |  |  | -29.8485 | 182 | -0.30572 | -55.6401
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.164 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.30572 | 203 | 203 |  |  | -33.2926 | 203 | -0.30572 | -62.0601
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.16028 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.302 | 61 | 61 |  |  | -9.7773 | 61 | -0.302 | -18.4218
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.16028 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.302 | 95 | 95 |  |  | -15.227 | 95 | -0.302 | -28.6896
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.16028 | 120.8 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.302 | 151 | 151 |  |  | -24.2029 | 151 | -0.302 | -45.6014
5111 | CALAVER_JTD1 | 1 | South | YES | -0.15971 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.30142 | 0 | 430 |  |  | 0 | 0 | -0.30142 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.15971 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.30142 | 0 | 430 |  |  | 0 | 0 | -0.30142 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | -0.15955 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.30127 | 418 | 418 |  |  | -66.6932 | 418 | -0.30127 | -125.9288
5397 | CALAVER_OWS2 | 2 | South | YES | -0.15955 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.30127 | 400 | 400 |  |  | -63.8212 | 400 | -0.30127 | -120.506
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.15937 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.30108 | 215 | 215 |  |  | -34.2641 | 215 | -0.30108 | -64.7322
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.15937 | 172.8 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.30108 | 216 | 216 |  |  | -34.4235 | 216 | -0.30108 | -65.0333
5031 | BRA_VHBCT1 | 1 | South | YES | -0.15937 | 44 | 24 | 44 | 0 | 1.0192 | #N/A | -1 | 0.30108 | 44 | 44 |  |  | -7.0122 | 44 | -0.30108 | -13.2475
5032 | BRA_VHBCT2 | 2 | South | YES | -0.15937 | 44 | 24 | 44 | 0 | 1.0192 | #N/A | -1 | 0.30108 | 44 | 44 |  |  | -7.0122 | 44 | -0.30108 | -13.2475
5033 | BRA_VHBCT3 | 3 | South | YES | -0.15937 | 43 | 24 | 43 | 0 | 1.0192 | #N/A | -1 | 0.30108 | 43 | 43 |  |  | -6.8528 | 43 | -0.30108 | -12.9464
5034 | BRA_VHBCT4 | 4 | South | YES | -0.15937 | 45 | 24 | 45 | 0 | 1.0192 | #N/A | -1 | 0.30108 | 45 | 45 |  |  | -7.1716 | 45 | -0.30108 | -13.5486
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.15932 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.30104 | 155 | 155 |  |  | -24.6954 | 155 | -0.30104 | -46.6607
5477 | BRA_AVR1_ST1 | 1 | South | YES | -0.15932 | 174 | 138 | 174 | 0 | 1.017 | CC | -1 | 0.30104 | 174 | 174 |  |  | -27.7225 | 174 | -0.30104 | -52.3804
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.15932 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.30104 | 155 | 155 |  |  | -24.6954 | 155 | -0.30104 | -46.6607
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.15927 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.30098 | 407 | 407 |  |  | -64.8221 | 407 | -0.30098 | -122.4989
5401 | CALAVER_JKS1 | 1 | South | YES | -0.15868 | 562 | 100 | 562 | 0 | 1.018 | LIGCO | -1 | 0.3004 | 0 | 562 |  |  | 0 | 0 | -0.3004 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.15828 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.29999 | 58 | 58 |  |  | -9.18 | 58 | -0.29999 | -17.3993
5265 | LEON_LCP4G4 | 4 | South | YES | -0.15828 | 71.2 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.29999 | 89 | 89 |  |  | -14.0866 | 89 | -0.29999 | -26.6989
5266 | LEON_LCPCT1 | 1 | South | YES | -0.15828 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.29999 | 44 | 44 |  |  | -6.9641 | 44 | -0.29999 | -13.1995
5267 | LEON_LCPCT2 | 2 | South | YES | -0.15828 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.29999 | 44 | 44 |  |  | -6.9641 | 44 | -0.29999 | -13.1995
5268 | LEON_LCPCT3 | 3 | South | YES | -0.15828 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.29999 | 43 | 43 |  |  | -6.8059 | 43 | -0.29999 | -12.8995
5269 | LEON_LCPCT4 | 4 | South | YES | -0.15828 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.29999 | 45 | 45 |  |  | -7.1224 | 45 | -0.29999 | -13.4995
8189 | CUECPL2A | 1 | South | YES | -0.15753 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.29925 | 0 | 0 |  |  | 0 | 0 | -0.29925 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.1513 | 396.3 | 180 | 396.3 | 0 | 1.0331 | LIGCO | -1 | 0.29301 | 0 | 396.3 |  |  | 0 | 0 | -0.29301 | 0
88198 | BEEVILLE | F | South | YES | -0.14085 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.28256 | 0 | 0 |  |  | 0 | 0 | -0.28256 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.14078 | 19.2 | 6 | 24 | 0 | 1.0161 | GST | -1 | 0.28249 | 24 | 24 |  |  | -3.3786 | 24 | -0.28249 | -6.7797
5891 | PEARSALLGEN2 | 1 | South | YES | -0.14078 | 19.4 | 6 | 24.3 | 0 | 1.0161 | GST | -1 | 0.28249 | 24.3 | 24.3 |  |  | -3.4209 | 24.3 | -0.28249 | -6.8645
5892 | PEARSALLGEN3 | 1 | South | YES | -0.14078 | 19.1 | 6 | 23.9 | 0 | 1.0161 | GST | -1 | 0.28249 | 23.9 | 23.9 |  |  | -3.3646 | 23.9 | -0.28249 | -6.7515
8161 | COLETO0A | 1 | South | YES | -0.13959 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.2813 | 0 | 633 |  |  | 0 | 0 | -0.2813 | 0
80080 | GWINDT11A | 2 | South | YES | -0.1347 | 17.7 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 41 |  |  | 0 | 0 | -0.27642 | 0
80080 | GWINDT11A | 3 | South | YES | -0.1347 | 16.4 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 38 |  |  | 0 | 0 | -0.27642 | 0
80080 | GWINDT11A | 4 | South | YES | -0.1347 | 8.2 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 19 |  |  | 0 | 0 | -0.27642 | 0
80080 | GWINDT11A | 1 | South | YES | -0.1347 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 94 |  |  | 0 | 0 | -0.27642 | 0
80081 | GWINDT21A | 3 | South | YES | -0.1347 | 18.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 43 |  |  | 0 | 0 | -0.27642 | 0
80081 | GWINDT21A | 2 | South | YES | -0.1347 | 15.5 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 36 |  |  | 0 | 0 | -0.27642 | 0
80081 | GWINDT21A | 1 | South | YES | -0.1347 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 94 |  |  | 0 | 0 | -0.27642 | 0
80081 | GWINDT21A | 4 | South | YES | -0.1347 | 9.5 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 22 |  |  | 0 | 0 | -0.27642 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.1347 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 50 |  |  | 0 | 0 | -0.27642 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.1347 | 63 | 0 | 146 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 146 |  |  | 0 | 0 | -0.27642 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.1347 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 50 |  |  | 0 | 0 | -0.27642 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.1347 | 23.7 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.27642 | 0 | 55 |  |  | 0 | 0 | -0.27642 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.13466 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.27637 | 0 | 0 |  |  | 0 | 0 | -0.27637 | 0
5932 | SI_RAY9 | 9 | South | YES | -0.13462 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.27633 | 38 | 38 |  |  | -5.1156 | 38 | -0.27633 | -10.5006
5933 | SI_RAY6 | 6 | South | YES | -0.13462 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.27633 | 19.3 | 19.3 |  |  | -2.5982 | 19.3 | -0.27633 | -5.3332
5935 | SI_RAY10 | 10 | South | YES | -0.13462 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.27633 | 47 | 47 |  |  | -6.3271 | 47 | -0.27633 | -12.9876
80003 | MILHWYS | F | South | YES | -0.13462 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.27633 | 0 | 0 |  |  | 0 | 0 | -0.27633 | 0
8981 | HECN1 | 1 | South | YES | -0.13447 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.27618 | 144.8 | 144.8 |  |  | -19.4713 | 144.8 | -0.27618 | -39.9912
8982 | HECN2 | 2 | South | YES | -0.13447 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.27618 | 144.1 | 144.1 |  |  | -19.3771 | 144.1 | -0.27618 | -39.7978
8983 | HECN3 | 3 | South | YES | -0.13447 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.27618 | 171.9 | 171.9 |  |  | -23.1154 | 171.9 | -0.27618 | -47.4757
8936 | MVGN#1 | 1 | South | YES | -0.13447 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.27618 | 216.6 | 216.6 |  |  | -29.126 | 216.6 | -0.27618 | -59.8208
8937 | MVGN#2 | 2 | South | YES | -0.13447 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.27618 | 216.7 | 216.7 |  |  | -29.1394 | 216.7 | -0.27618 | -59.8484
8938 | MVGN#3 | 3 | South | YES | -0.13447 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.27618 | 250.9 | 250.9 |  |  | -33.7383 | 250.9 | -0.27618 | -69.2938
8461 | KOCH_UP0A | 1 | South | YES | -0.13431 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.27602 | 0 | 0 |  |  | 0 | 0 | -0.27602 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.1343 | 30.3 | 0 | 38 |  | 1.027 | Cogen | -1 | 0.27602 | 0 | 0 |  |  | 0 | 0 | -0.27602 | 0
8933 | FGNTS001 | 1 | South | YES | -0.13427 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.27598 | 146.5 | 146.5 |  |  | -19.6701 | 146.5 | -0.27598 | -40.4309
8934 | FGNTS101 | 2 | South | YES | -0.13427 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.27598 | 147.9 | 147.9 |  |  | -19.8581 | 147.9 | -0.27598 | -40.8173
8935 | FGNTS201 | 3 | South | YES | -0.13427 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.27598 | 173 | 173 |  |  | -23.2282 | 173 | -0.27598 | -47.7444
8506 | VAL #1 | 1 | South | YES | -0.13419 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.27591 | 0 | 0 |  |  | 0 | 0 | -0.27591 | 0
8507 | VAL #2 | 2 | South | YES | -0.13419 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.27591 | 0 | 0 |  |  | 0 | 0 | -0.27591 | 0
8173 | VICEC51A | 5 | South | YES | -0.13415 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.27586 | 144 | 144 |  |  | -19.317 | 144 | -0.27586 | -39.7236
8174 | VICEC61A | 6 | South | YES | -0.13415 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.27586 | 188 | 188 |  |  | -25.2194 | 188 | -0.27586 | -51.8613
8459 | B_DAVIS0B | MB | South | YES | -0.13412 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.27584 | 0 | 0 |  |  | 0 | 0 | -0.27584 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.13412 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.27584 | 0 | 0 |  |  | 0 | 0 | -0.27584 | 0
8456 | COSW#1 | 1 | South | YES | -0.13399 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.2757 | 0 | 0 |  |  | 0 | 0 | -0.2757 | 0
8457 | COSW#2 | 2 | South | YES | -0.13399 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.2757 | 0 | 0 |  |  | 0 | 0 | -0.2757 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.13393 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.27564 | 0 | 0 |  |  | 0 | 0 | -0.27564 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.13393 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.27564 | 0 | 0 |  |  | 0 | 0 | -0.27564 | 0
8562 | CNOPST1 | 3 | South | YES | -0.13393 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.27564 | 0 | 0 |  |  | 0 | 0 | -0.27564 | 0
88508 | FALFURRI | F | South | YES | -0.13369 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.2754 | 0 | 0 |  |  | 0 | 0 | -0.2754 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | -0.13303 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.27474 | 0 | 0 |  |  | 0 | 0 | -0.27474 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.13303 | 11 | 0 | 11 | 0 | 1.0227 | Hydro | -1 | 0.27474 | 0 | 0 |  |  | 0 | 0 | -0.27474 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.13303 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.27474 | 0 | 0 |  |  | 0 | 0 | -0.27474 | 0
8066 | DUP1V#1 | 1 | South | YES | -0.13287 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.13287 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.13287 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.13287 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
8930 | ICPGN10A | 1 | South | YES | -0.13287 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
8931 | ICPGN20A | 2 | South | YES | -0.13287 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
8932 | ICPGN30A | 3 | South | YES | -0.13287 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
80223 | REYSHR G | 1 | South | YES | -0.13287 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.27459 | 0 | 0 |  |  | 0 | 0 | -0.27459 | 0
5508 | RAYBURNCC9 | 1 | South | YES | -0.13273 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.27444 | 47.7 | 47.7 |  |  | -6.3312 | 47.7 | -0.27444 | -13.0909
5509 | RAYBURNCC10 | 1 | South | YES | -0.13273 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.27444 | 37.3 | 37.3 |  |  | -4.9508 | 37.3 | -0.27444 | -10.2367
5511 | RAYBURNCC7 | 1 | South | YES | -0.13273 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.27444 | 47.5 | 47.5 |  |  | -6.3047 | 47.5 | -0.27444 | -13.036
5512 | RAYBURNCC8 | 1 | South | YES | -0.13273 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.27444 | 49.3 | 49.3 |  |  | -6.5436 | 49.3 | -0.27444 | -13.53
88299 | ZAPATA | F | South | YES | -0.13184 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.27356 | 0 | 0 |  |  | 0 | 0 | -0.27356 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.13164 | 17.6 | 6 | 22 | 0 | 1.0223 | GST | -1 | 0.27335 | 22 | 22 |  |  | -2.8961 | 22 | -0.27335 | -6.0138
5505 | RAYBURNGEN1 | 1 | South | YES | -0.13164 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.27335 | 11 | 11 |  |  | -1.4481 | 11 | -0.27335 | -3.0069
5506 | RAYBURNGEN2 | 1 | South | YES | -0.13164 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.27335 | 11 | 11 |  |  | -1.4481 | 11 | -0.27335 | -3.0069
80224 | VISTRONG1 | 1 | South | YES | -0.13064 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.27235 | 0 | 0 |  |  | 0 | 0 | -0.27235 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.13064 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.27235 | 0 | 0 |  |  | 0 | 0 | -0.27235 | 0
80012 | LAR | F | South | YES | -0.13013 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.27184 | 0 | 0 |  |  | 0 | 0 | -0.27184 | 0
80265 | LARECU40A | 4 | South | YES | -0.13012 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.27184 | 100 | 100 |  |  | -13.0125 | 100 | -0.27184 | -27.1837
80266 | LARECU50A | 5 | South | YES | -0.13012 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.27184 | 100 | 100 |  |  | -13.0125 | 100 | -0.27184 | -27.1837
80227 | AIRCO G | 1 | South | YES | -0.12981 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.27152 | 0 | 0 |  |  | 0 | 0 | -0.27152 | 0
8147 | UCAR #2 | 10 | South | YES | -0.12946 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
8148 | UCAR #1 | 2 | South | YES | -0.12946 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80137 | CSDR89 | 9 | South | YES | -0.12946 | 0 | 0 | 15 |  | 1.003 | DCTie | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80137 | CSDR89 | 8 | South | YES | -0.12946 | 33.9 | 0 | 39 |  | 1.003 | DCTie | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80138 | CSDR7 | 7 | South | YES | -0.12946 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80139 | CSDR56 | 6 | South | YES | -0.12946 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80139 | CSDR56 | 5 | South | YES | -0.12946 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80140 | CSDR11 | 11 | South | YES | -0.12946 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.27117 | 0 | 0 |  |  | 0 | 0 | -0.27117 | 0
80226 | ALCOA G | 1 | South | YES | -0.12637 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.26809 | 0 | 0 |  |  | 0 | 0 | -0.26809 | 0
8134 | FOR #1 | 1 | South | YES | -0.12545 | 54.1 | 45 | 79 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
8138 | FOR #2 | 2 | South | YES | -0.12545 | 63.1 | 45 | 81 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
8153 | FOR #3 | 3 | South | YES | -0.12545 | 63.1 | 45 | 79.9 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
8154 | FOR #4 | 4 | South | YES | -0.12545 | 63.1 | 60 | 80 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
8155 | FOR #5 | 5 | South | YES | -0.12545 | 63.1 | 60 | 78.4 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
8156 | FOR #6 | 6 | South | YES | -0.12545 | 24.9 | 5 | 25 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
8157 | FOR #7 | 7 | South | YES | -0.12545 | 28.8 | 5 | 46 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
80051 | FOR #8 | 8 | South | YES | -0.12545 | 28 | 28 | 28 | 0 | 1.016 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
80052 | FOR #9 | 9 | South | YES | -0.12545 | 29.7 | 5 | 43.6 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
80053 | FOR #10 | 10 | South | YES | -0.12545 | 68.4 | 45 | 75 | 0 | 1.03 | Cogen | -1 | 0.26716 | 0 | 0 |  |  | 0 | 0 | -0.26716 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | -0.092237 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.23395 | 0 | 0 |  |  |  |  | -0.23395 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.092237 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.23395 | 0 | 0 |  |  |  |  | -0.23395 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.091652 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.23336 | 76 | 76 |  |  |  |  | -0.23336 | -17.7357
48732 | CBE_GT2 | 1 | Houston | YES | -0.091652 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.23336 | 76 | 76 |  |  |  |  | -0.23336 | -17.7357
48733 | CBE_ST12 | 1 | Houston | YES | -0.091652 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.23336 | 105 | 105 |  |  |  |  | -0.23336 | -24.5032
48734 | CBE_GT3 | 1 | Houston | YES | -0.091652 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.23336 | 76 | 76 |  |  |  |  | -0.23336 | -17.7357
48735 | CBE_GT4 | 1 | Houston | YES | -0.091652 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.23336 | 76 | 76 |  |  |  |  | -0.23336 | -17.7357
48736 | CBE_ST34 | 1 | Houston | YES | -0.091652 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.23336 | 105 | 105 |  |  |  |  | -0.23336 | -24.5032
80010 | EPLVT1 | F | South | YES | -0.090438 | 0 | 0 | 0 |  | 1.0376 | #N/A | -1 | 0.23215 | 0 | 0 |  |  | 0 | 0 | -0.23215 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.087415 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.22913 | 0 | 0 |  |  |  |  | -0.22913 | 0
8262 | ELPS | 1 | South | YES | -0.084976 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.22669 | 0 | 0 |  |  | 0 | 0 | -0.22669 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.074659 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.074659 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.074659 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.074659 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.074659 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.074659 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.074659 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.074659 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.074659 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.074659 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.074659 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.074659 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.074659 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.074659 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.074659 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.074659 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.074659 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.074659 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.074659 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.074659 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.21637 | 0 | 0 |  |  |  |  | -0.21637 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.07143 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.21314 | 0 | 0 |  |  |  |  | -0.21314 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.07143 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.21314 | 0 | 0 |  |  |  |  | -0.21314 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.068879 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.21059 | 0 | 0 |  |  |  |  | -0.21059 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.068879 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.21059 | 0 | 0 |  |  |  |  | -0.21059 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.068879 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.21059 | 0 | 0 |  |  |  |  | -0.21059 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.068879 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.21059 | 0 | 0 |  |  |  |  | -0.21059 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.061492 | 33 | 13 | 33 | 0 | 1.0375 | Hydro | -1 | 0.2032 | 0 | 0 |  |  | 0 | 0 | -0.2032 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.061492 | 25 | 13 | 25 | 0 | 1.0375 | Hydro | -1 | 0.2032 | 0 | 0 |  |  | 0 | 0 | -0.2032 | 0
88253 | HAMILTON | F | South | YES | -0.061492 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.2032 | 0 | 0 |  |  | 0 | 0 | -0.2032 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.059641 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.20135 | 0 | 0 |  |  |  |  | -0.20135 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.059622 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.20133 | 0 | 651 |  |  |  |  | -0.20133 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.059622 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.20133 | 0 | 564 |  |  |  |  | -0.20133 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.059622 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.20133 | 0 | 603 |  |  |  |  | -0.20133 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.059545 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.20126 | 167.7 | 167.7 |  |  |  |  | -0.20126 | -33.7508
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.059545 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.20126 | 166.4 | 166.4 |  |  |  |  | -0.20126 | -33.4892
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.059545 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.20126 | 252.4 | 252.4 |  |  |  |  | -0.20126 | -50.7973
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.058249 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.19996 | 0 | 0 |  |  |  |  | -0.19996 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.058127 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.19984 | 166 | 166 |  |  |  |  | -0.19984 | -33.1733
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.058127 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.19984 | 166 | 166 |  |  |  |  | -0.19984 | -33.1733
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.058127 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.19984 | 248 | 248 |  |  |  |  | -0.19984 | -49.5601
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.058127 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.19984 | 546 | 546 |  |  |  |  | -0.19984 | -109.1121
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.058127 | 598.9 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.19984 | 0 | 654 |  |  |  |  | -0.19984 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.058127 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.19984 | 13 | 13 |  |  |  |  | -0.19984 | -2.5979
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.052078 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.052078 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.052078 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.052078 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.052078 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.052078 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.052078 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.052078 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.052078 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.052078 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.052078 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.052078 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.052078 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.052078 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.052078 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.19379 | 0 | 0 |  |  |  |  | -0.19379 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.049536 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.19125 | 0 | 0 |  |  |  |  | -0.19125 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.047763 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.18948 | 0 | 0 |  |  |  |  | -0.18948 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.047763 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.18948 | 0 | 0 |  |  |  |  | -0.18948 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.047763 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.18948 | 0 | 0 |  |  |  |  | -0.18948 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.047763 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.18948 | 0 | 0 |  |  |  |  | -0.18948 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.047763 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.18948 | 0 | 0 |  |  |  |  | -0.18948 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.047085 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.1888 | 0 | 0 |  |  |  |  | -0.1888 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.047085 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.1888 | 0 | 0 |  |  |  |  | -0.1888 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.047085 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.1888 | 0 | 0 |  |  |  |  | -0.1888 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.047085 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.1888 | 0 | 0 |  |  |  |  | -0.1888 | 0
48691 | GBY_73741085 | B | Houston | YES | -0.04623 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.18794 | 47 | 47 |  |  |  |  | -0.18794 | -8.8333
48691 | GBY_73741085 | A | Houston | YES | -0.04623 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.18794 | 47 | 47 |  |  |  |  | -0.18794 | -8.8333
48692 | GBY_81821075 | D | Houston | YES | -0.04623 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.18794 | 55 | 55 |  |  |  |  | -0.18794 | -10.3368
48692 | GBY_81821075 | C | Houston | YES | -0.04623 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.18794 | 47 | 47 |  |  |  |  | -0.18794 | -8.8333
48693 | GBY_83841065 | E | Houston | YES | -0.04623 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.18794 | 57 | 57 |  |  |  |  | -0.18794 | -10.7127
48693 | GBY_83841065 | F | Houston | YES | -0.04623 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.18794 | 54 | 54 |  |  |  |  | -0.18794 | -10.1489
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.045809 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.18752 | 0 | 0 |  |  |  |  | -0.18752 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.045809 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.18752 | 0 | 0 |  |  |  |  | -0.18752 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.045465 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.18718 | 163.2 | 163.2 |  |  |  |  | -0.18718 | -30.5473
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.045465 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.18718 | 157.1 | 157.1 |  |  |  |  | -0.18718 | -29.4055
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.045465 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.18718 | 157.5 | 157.5 |  |  |  |  | -0.18718 | -29.4804
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.045465 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.18718 | 157 | 157 |  |  |  |  | -0.18718 | -29.3868
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.045465 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.18718 | 282 | 282 |  |  |  |  | -0.18718 | -52.7839
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.045172 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.18688 | 0 | 0 |  |  |  |  | -0.18688 | 0
48855 | SRB_GT211035 | B2 | Houston | YES | -0.044859 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.18657 | 12 | 12 |  |  |  |  | -0.18657 | -2.2389
48855 | SRB_GT211035 | B1 | Houston | YES | -0.044859 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.18657 | 18 | 18 |  |  |  |  | -0.18657 | -3.3583
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.044841 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.18655 | 176 | 176 |  |  |  |  | -0.18655 | -32.8333
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.044817 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.18653 | 165 | 165 |  |  |  |  | -0.18653 | -30.7773
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.044806 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.18652 | 0 | 0 |  |  |  |  | -0.18652 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.044806 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.18652 | 0 | 0 |  |  |  |  | -0.18652 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.044735 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.18645 | 213 | 213 |  |  |  |  | -0.18645 | -39.7132
48845 | SOL_GT1 | 1 | Houston | YES | -0.044728 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.18644 | 16.2 | 16.2 |  |  |  |  | -0.18644 | -3.0203
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.044724 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.18644 | 0 | 0 |  |  |  |  | -0.18644 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.044724 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.18644 | 0 | 0 |  |  |  |  | -0.18644 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.044724 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.18644 | 0 | 0 |  |  |  |  | -0.18644 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.044724 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.18644 | 0 | 0 |  |  |  |  | -0.18644 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.044714 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.18643 | 228 | 228 |  |  |  |  | -0.18643 | -42.5051
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.04471 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.18642 | 0 | 0 |  |  |  |  | -0.18642 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.04471 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.18642 | 0 | 0 |  |  |  |  | -0.18642 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.04471 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.18642 | 0 | 0 |  |  |  |  | -0.18642 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.044274 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.18599 | 0 | 0 |  |  |  |  | -0.18599 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.044274 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.18599 | 0 | 0 |  |  |  |  | -0.18599 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.044274 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.18599 | 0 | 0 |  |  |  |  | -0.18599 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.044274 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.18599 | 0 | 0 |  |  |  |  | -0.18599 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.043643 | 137.6 | 54.6 | 137.6 |  | 1.0362 | Cogen | -1 | 0.18536 | 0 | 0 |  |  |  |  | -0.18536 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.04353 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.18524 | 42 | 42 |  |  |  |  | -0.18524 | -7.7802
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.04353 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.18524 | 42 | 42 |  |  |  |  | -0.18524 | -7.7802
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.04353 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.18524 | 39 | 39 |  |  |  |  | -0.18524 | -7.2244
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.04353 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.18524 | 39 | 39 |  |  |  |  | -0.18524 | -7.2244
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.043408 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.18512 | 0 | 0 |  |  |  |  | -0.18512 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.043408 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.18512 | 0 | 0 |  |  |  |  | -0.18512 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.042504 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.18422 | 107 | 107 |  |  |  |  | -0.18422 | -19.7111
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.042504 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.18422 | 108 | 108 |  |  |  |  | -0.18422 | -19.8953
48875 | THW_3132 | A | Houston | YES | -0.042504 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.18422 | 55 | 55 |  |  |  |  | -0.18422 | -10.1319
48875 | THW_3132 | B | Houston | YES | -0.042504 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.18422 | 53 | 53 |  |  |  |  | -0.18422 | -9.7634
48877 | THW_3334 | D | Houston | YES | -0.042504 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.18422 | 57 | 57 |  |  |  |  | -0.18422 | -10.5003
48877 | THW_3334 | C | Houston | YES | -0.042504 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.18422 | 55 | 55 |  |  |  |  | -0.18422 | -10.1319
48879 | THW_4142 | E | Houston | YES | -0.042504 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.18422 | 56 | 56 |  |  |  |  | -0.18422 | -10.3161
48879 | THW_4142 | F | Houston | YES | -0.042504 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.18422 | 55 | 55 |  |  |  |  | -0.18422 | -10.1319
48881 | THW_4344 | G | Houston | YES | -0.042504 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.18422 | 58 | 58 |  |  |  |  | -0.18422 | -10.6845
48881 | THW_4344 | H | Houston | YES | -0.042504 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.18422 | 58 | 58 |  |  |  |  | -0.18422 | -10.6845
3416 | LAKE_CRK1_G | 1 | North | YES | -0.35082 | 60 | 33 | 75 |  | 1.029 | GST | 1 | -0.18364 | 75 | 75 | -26.3117 | 75 |  |  | -0.18364 | -13.7727
3417 | LAKE_CRK2_G | 2 | North | YES | -0.35082 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | -0.18364 | 222 | 222 | -77.8827 | 222 |  |  | -0.18364 | -40.7673
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.041822 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.18353 | 746 | 746 |  |  |  |  | -0.18353 | -136.9164
49803 | EXN_15GT | 1 | Houston | YES | -0.041534 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.041534 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.041534 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.041534 | 43 | 9.2 | 45.9 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.041534 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.041534 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.041534 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.041534 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.041534 | 18.5 | 9.2 | 18.5 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.041534 | 81 | 21.3 | 85.4 | 0 | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.041534 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.18325 | 0 | 0 |  |  |  |  | -0.18325 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.041397 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.18311 | 12 | 12 |  |  |  |  | -0.18311 | -2.1973
48651 | EP_1_2 | 1 | Houston | YES | -0.040749 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.18246 | 0 | 0 |  |  |  |  | -0.18246 | 0
48651 | EP_1_2 | 2 | Houston | YES | -0.040749 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.18246 | 0 | 0 |  |  |  |  | -0.18246 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.040737 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.040737 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.040737 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.040737 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.040737 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.040737 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.040737 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.18245 | 0 | 0 |  |  |  |  | -0.18245 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.040685 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.1824 | 744 | 744 |  |  |  |  | -0.1824 | -135.7034
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.040472 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.18218 | 0 | 0 |  |  |  |  | -0.18218 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.040314 | 172 | 0 | 172 | 0 | 1.026 | GSC | -1 | 0.18203 | 172 | 172 |  |  |  |  | -0.18203 | -31.3085
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.040314 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.18203 | 172 | 172 |  |  |  |  | -0.18203 | -31.3085
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.040314 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.18203 | 172 | 172 |  |  |  |  | -0.18203 | -31.3085
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.039482 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.18119 | 162.8 | 162.8 |  |  |  |  | -0.18119 | -29.4984
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.039482 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.18119 | 161.4 | 161.4 |  |  |  |  | -0.18119 | -29.2447
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.039482 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.18119 | 158.9 | 158.9 |  |  |  |  | -0.18119 | -28.7917
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.039482 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.18119 | 269.2 | 269.2 |  |  |  |  | -0.18119 | -48.7774
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.039234 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.18095 | 398 | 398 |  |  |  |  | -0.18095 | -72.0165
48885 | THW_5152 | A | Houston | YES | -0.038871 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.18058 | 58 | 58 |  |  |  |  | -0.18058 | -10.4738
48885 | THW_5152 | B | Houston | YES | -0.038871 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.18058 | 59 | 59 |  |  |  |  | -0.18058 | -10.6544
48886 | THW_5354 | D | Houston | YES | -0.038871 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.18058 | 58 | 58 |  |  |  |  | -0.18058 | -10.4738
48886 | THW_5354 | C | Houston | YES | -0.038871 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.18058 | 57 | 57 |  |  |  |  | -0.18058 | -10.2932
48887 | THW_5556 | E | Houston | YES | -0.038871 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.18058 | 59 | 59 |  |  |  |  | -0.18058 | -10.6544
48887 | THW_5556 | F | Houston | YES | -0.038871 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.18058 | 57 | 57 |  |  |  |  | -0.18058 | -10.2932
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.033793 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.17551 | 0 | 0 |  |  |  |  | -0.17551 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.033793 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.17551 | 0 | 0 |  |  |  |  | -0.17551 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.033793 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.17551 | 0 | 0 |  |  |  |  | -0.17551 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.033793 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.17551 | 0 | 0 |  |  |  |  | -0.17551 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.033793 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.17551 | 0 | 0 |  |  |  |  | -0.17551 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.14171 | 15 | 15 |  |  | 0 | 15 | -0.14171 | -2.1257
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
8442 | NUECES_B0A | MB | South | YES | 0 | 0 | 81 | 367 |  | 1.03 | GST | -1 | 0.14171 | 0 | 0 |  |  | 0 | 0 | -0.14171 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.14171 | 0 | 0 |  |  |  |  | -0.14171 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | -2.1e-05 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.16717 | 48 | 48 | -0.001008 | 48 |  |  | 0.16717 | 8.024
32884 | BRYN_DNSBY13 | 1 | North | YES | -2.1e-05 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.16717 | 46 | 46 | -0.000966 | 46 |  |  | 0.16717 | 7.6896
32892 | BRYN_DNSBY14 | 1 | North | YES | -2.1e-05 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.16717 | 105 | 105 | -0.002205 | 105 |  |  | 0.16717 | 17.5524
32886 | BRYN_ATKINS3 | MB | North | YES | 0.00154 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.16873 | 0 | 0 | 0 | 0 |  |  | 0.16873 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.00154 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.16873 | 0 | 0 | 0 | 0 |  |  | 0.16873 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.00154 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.16873 | 17 | 17 | 0.02618 | 17 |  |  | 0.16873 | 2.8684
32890 | BRYN_ATKINS4 | MB | North | YES | 0.00154 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.16873 | 0 | 0 | 0 | 0 |  |  | 0.16873 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.00154 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.16873 | 0 | 0 | 0 | 0 |  |  | 0.16873 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.00583 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.17302 | 32 | 32 | 0.18656 | 32 |  |  | 0.17302 | 5.5365
48671 | FTR_GT1_5105 | 1 | North | YES | 0.012112 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.1793 | 154.2 | 154.2 | 1.8677 | 154.2 |  |  | 0.1793 | 27.6479
48672 | FTR_GT2_5110 | 2 | North | YES | 0.012112 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.1793 | 159 | 159 | 1.9258 | 159 |  |  | 0.1793 | 28.5085
48673 | FTR_GT3_5085 | 3 | North | YES | 0.012112 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.1793 | 158 | 158 | 1.9137 | 158 |  |  | 0.1793 | 28.3292
48674 | FTR_CN4_5095 | 4 | North | YES | 0.012112 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.1793 | 380 | 380 | 4.6026 | 380 |  |  | 0.1793 | 68.1335
990 | GIBN_CREK_G1 | 1 | North | YES | 0.020701 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.18789 | 0 | 463 | 9.5846 | 463 |  |  | 0.18789 | 86.992
39960 | TNTNPONE_18 | 1 | North | YES | 0.054304 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.22149 | 0 | 152.3 | 8.2705 | 152.3 |  |  | 0.22149 | 33.733
39970 | TNTNPONE_28 | 1 | North | YES | 0.054304 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.22149 | 0 | 153 | 8.3085 | 153 |  |  | 0.22149 | 33.8881
48721 | LEG_1___1 | 1 | North | YES | 0.068969 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.23616 | 0 | 827 | 57.0374 | 827 |  |  | 0.23616 | 195.3008
48722 | LEG_2___2 | 2 | North | YES | 0.068969 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.23616 | 0 | 819 | 56.4856 | 819 |  |  | 0.23616 | 193.4115
60202 | FRNDDRCS | F | West | YES | 0.10021 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.2674 | 0 | 0 |  |  |  |  | 0.2674 | 0
3381 | BBRN_1G | 1 | North | YES | 0.11149 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.27867 | 0 | 618 | 68.8983 | 618 |  |  | 0.27867 | 172.2197
3382 | BBRN_2G | 2 | North | YES | 0.11149 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.27867 | 0 | 589 | 65.6653 | 589 |  |  | 0.27867 | 164.1382
13131 | CALFREST_1G | 1 | North | YES | 0.11507 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.28225 | 150.7 | 150.7 | 17.3403 | 150.7 |  |  | 0.28225 | 42.5353
13132 | CALFREST_2G | 2 | North | YES | 0.11507 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.28225 | 151 | 151 | 17.3748 | 151 |  |  | 0.28225 | 42.62
13133 | CALFREST_3G | 3 | North | YES | 0.11507 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.28225 | 177.4 | 177.4 | 20.4125 | 177.4 |  |  | 0.28225 | 50.0715
13134 | CALFREST_4G | 4 | North | YES | 0.11536 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.28255 | 151.5 | 151.5 | 17.4772 | 151.5 |  |  | 0.28255 | 42.806
13135 | CALFREST_5G | 5 | North | YES | 0.11536 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.28255 | 152.3 | 152.3 | 17.5695 | 152.3 |  |  | 0.28255 | 43.032
13136 | CALFREST_6G | 6 | North | YES | 0.11536 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.28255 | 177.5 | 177.5 | 20.4766 | 177.5 |  |  | 0.28255 | 50.1522
60018 | DSKY1 | 1 | West | YES | 0.11895 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.28613 | 0 | 84 |  |  |  |  | 0.28613 | 24.0351
60017 | ORNNWP1 | 1 | West | YES | 0.11987 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.28706 | 0 | 80 |  |  |  |  | 0.28706 | 22.9648
60000 | DSKY2 | 1 | West | YES | 0.12071 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.2879 | 0 | 76.5 |  |  |  |  | 0.2879 | 22.0241
6016 | SWMESA | 1 | West | YES | 0.12224 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.28942 | 0 | 75 |  |  |  |  | 0.28942 | 21.7067
60003 | KING_NE1A | 1 | West | YES | 0.12224 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.28942 | 0 | 80 |  |  |  |  | 0.28942 | 23.1538
60005 | KING_SE1A | 1 | West | YES | 0.12224 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.28942 | 0 | 40 |  |  |  |  | 0.28942 | 11.5769
38437 | TNSRBNMESA9 | 1 | West | YES | 0.12265 | 37.5 | 0 | 150 |  | 1.02 | Wind | 1 | 0.28984 | 0 | 150 |  |  |  |  | 0.28984 | 43.4755
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.12273 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.28992 | 0 | 80 |  |  |  |  | 0.28992 | 23.1937
60016 | WOODWRD11A | 1 | West | YES | 0.12276 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.28995 | 0 | 80 |  |  |  |  | 0.28995 | 23.1959
60201 | RIO DRCS | F | West | YES | 0.12285 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.29003 | 0 | 0 |  |  |  |  | 0.29003 | 0
60007 | KING_SW1A | 1 | West | YES | 0.12379 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.29098 | 0 | 80 |  |  |  |  | 0.29098 | 23.2781
60019 | KING_NW1A | 1 | West | YES | 0.12379 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.29098 | 0 | 80 |  |  |  |  | 0.29098 | 23.2781
3126 | TRINIDAD_6G | 1 | North | YES | 0.12423 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.29142 | 224 | 224 | 27.8284 | 224 |  |  | 0.29142 | 65.2782
3107 | STRYKER_1G | 1 | North | YES | 0.12614 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.29332 | 182 | 182 | 22.9568 | 182 |  |  | 0.29332 | 53.3847
3108 | STRYKER_2G | 2 | North | YES | 0.12614 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.29332 | 484 | 484 | 61.0498 | 484 |  |  | 0.29332 | 141.9682
3113 | LUFKINWB_1G | 1 | North | YES | 0.12858 | 0 | 0 | 50 |  | 1.01 | #N/A | 1 | 0.29577 | 50 | 50 | 6.429 | 50 |  |  | 0.29577 | 14.7883
3348 | CHAMPION_1G | MB | North | YES | 0.12867 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.29585 | 0 | 0 | 0 | 0 |  |  | 0.29585 | 0
13116 | TGATEWAY_1G | 1 | North | YES | 0.13091 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.2981 | 151 | 151 | 19.7679 | 151 |  |  | 0.2981 | 45.0131
13117 | TGATEWAY_2G | 2 | North | YES | 0.13091 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.2981 | 130 | 130 | 17.0187 | 130 |  |  | 0.2981 | 38.753
13118 | TGATEWAY_3G | 3 | North | YES | 0.13091 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.2981 | 148 | 148 | 19.3751 | 148 |  |  | 0.2981 | 44.1188
13119 | TGATEWAY_4G | 4 | North | YES | 0.13091 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.2981 | 399 | 399 | 52.2343 | 399 |  |  | 0.2981 | 118.9418
6407 | TURKTRAK1A | 1 | West | YES | 0.13167 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.29885 | 0 | 169.5 |  |  |  |  | 0.29885 | 50.6557
3097 | MARTLAKE_1G | 1 | North | YES | 0.13248 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.29966 | 0 | 790 | 104.656 | 790 |  |  | 0.29966 | 236.7335
3098 | MARTLAKE_2G | 2 | North | YES | 0.13248 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.29966 | 0 | 795 | 105.3184 | 795 |  |  | 0.29966 | 238.2318
3099 | MARTLAKE_3G | 3 | North | YES | 0.13248 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.29966 | 0 | 804 | 106.5107 | 804 |  |  | 0.29966 | 240.9288
1349 | WESTXWIN_1G | 1 | West | YES | 0.13491 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.3021 | 0 | 6.6 |  |  |  |  | 0.3021 | 1.9938
1350 | NWPWRG1_1G | 1 | West | YES | 0.13491 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.3021 | 0 | 34.3 |  |  |  |  | 0.3021 | 10.362
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.13526 | 110 | 0 | 550 | 0 | 1.02 | Wind | 1 | 0.30244 | 0 | 550 |  |  |  |  | 0.30244 | 166.344
1002 | PBCTAGE_1G | A | West | YES | 0.13549 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.30268 | 66 | 66 |  |  |  |  | 0.30268 | 19.9767
1003 | PBCTBGE_2G | B | West | YES | 0.13549 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.30268 | 66 | 66 |  |  |  |  | 0.30268 | 19.9767
1004 | PBCTCGE_3G | C | West | YES | 0.13549 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.30268 | 67 | 67 |  |  |  |  | 0.30268 | 20.2793
1005 | PBCTDGE_4G | D | West | YES | 0.13549 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.30268 | 68 | 68 |  |  |  |  | 0.30268 | 20.582
1006 | PBCTEGE_5G | E | West | YES | 0.13549 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.30268 | 67 | 67 |  |  |  |  | 0.30268 | 20.2793
1007 | PB5GEN_6G | 5 | West | YES | 0.13549 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.30268 | 114 | 114 |  |  |  |  | 0.30268 | 34.5051
1008 | PB6GEN_7G | 6 | West | YES | 0.13549 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.30268 | 515 | 515 |  |  |  |  | 0.30268 | 155.8785
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.13561 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.3028 | 0 | 35 |  |  |  |  | 0.3028 | 10.598
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.13561 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.3028 | 0 | 30 |  |  |  |  | 0.3028 | 9.084
1146 | NOTREES_1G | 1 | West | YES | 0.13584 | 29.8 | 0 | 149 | 0 | 1.017 | #N/A | 1 | 0.30303 | 149 | 149 |  |  |  |  | 0.30303 | 45.1517
76031 | L_GASCCR1_1N | W1 | West | YES | 0.13595 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.30314 | 0 | 150 |  |  |  |  | 0.30314 | 45.4713
60057 | CALLAHAN1A | 1 | West | YES | 0.13634 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.30352 | 0 | 114 |  |  |  |  | 0.30352 | 34.6017
1328 | OCOTILLO_1G | 1 | West | YES | 0.13721 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.3044 | 0 | 58 |  |  |  |  | 0.3044 | 17.655
1320 | BSP 1 | 1 | West | YES | 0.13723 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.30442 | 0 | 0 |  |  |  |  | 0.30442 | 0
11020 | TIEHVSG_1G | 1 | West | YES | 0.13726 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.30445 | 208.2 | 208.2 |  |  |  |  | 0.30445 | 63.3858
11021 | TIEHVCG_1G | 1 | West | YES | 0.13726 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.30445 | 142.1 | 142.1 |  |  |  |  | 0.30445 | 43.2619
11022 | TIEHVCG_2G | 1 | West | YES | 0.13726 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.30445 | 132.4 | 132.4 |  |  |  |  | 0.30445 | 40.3087
11023 | TIEHVCG_3G | 1 | West | YES | 0.13726 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.30445 | 137.4 | 137.4 |  |  |  |  | 0.30445 | 41.831
11024 | TIEHVCG_4G | 1 | West | YES | 0.13726 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.30445 | 147 | 147 |  |  |  |  | 0.30445 | 44.7537
11025 | TIEHVSG_2G | 1 | West | YES | 0.13726 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.30445 | 213.2 | 213.2 |  |  |  |  | 0.30445 | 64.908
1326 | STANTONW_8 | 1 | West | YES | 0.13726 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.30445 | 0 | 100.5 |  |  |  |  | 0.30445 | 30.5972
11001 | NAV1CT | 1 | West | YES | 0.13728 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.30447 | 70.4 | 70.4 |  |  |  |  | 0.30447 | 21.4347
11009 | NAV2CT | 1 | West | YES | 0.13728 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.30447 | 71.4 | 71.4 |  |  |  |  | 0.30447 | 21.7391
11011 | NAV3ST | 1 | West | YES | 0.13728 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.30447 | 92.8 | 92.8 |  |  |  |  | 0.30447 | 28.2548
11012 | NAV4CT | 1 | West | YES | 0.13728 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30447 | 80 | 80 |  |  |  |  | 0.30447 | 24.3576
11013 | NAV5CT | 1 | West | YES | 0.13728 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.30447 | 80 | 80 |  |  |  |  | 0.30447 | 24.3576
11014 | NAV6ST | 1 | West | YES | 0.13728 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.30447 | 115 | 115 |  |  |  |  | 0.30447 | 35.014
1333 | MCDDONAL_8 | 1 | West | YES | 0.13749 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.30468 | 0 | 214.2 |  |  |  |  | 0.30468 | 65.2617
1170 | AIRLAMESA_1G | 1 | West | YES | 0.13785 | 0 | 0 | 180 |  | 1 | #N/A | 1 | 0.30504 | 180 | 180 |  |  |  |  | 0.30504 | 54.907
1327 | WILDHRSE_1G | 1 | West | YES | 0.13819 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.30537 | 0 | 120 |  |  |  |  | 0.30537 | 36.6448
1360 | GUNSIGHT_8 | 1 | West | YES | 0.13822 | 24 | 0 | 120 | 0 | 1.01 | Wind | 1 | 0.30541 | 0 | 120 |  |  |  |  | 0.30541 | 36.6492
1302 | COYOTEWG_8 | 1 | West | YES | 0.13852 | 45 | 0 | 225 |  | 1.01 | #N/A | 1 | 0.30571 | 225 | 225 |  |  |  |  | 0.30571 | 68.7849
1045 | CALENG1G_1G | 1 | West | YES | 0.13872 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30591 | 0 | 0 |  |  |  |  | 0.30591 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.13872 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.30591 | 0 | 0 |  |  |  |  | 0.30591 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.13872 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.30591 | 0 | 0 |  |  |  |  | 0.30591 | 0
60058 | BUFF_GAP1A | 1 | West | YES | 0.13886 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.30604 | 0 | 120 |  |  |  |  | 0.30604 | 36.725
60060 | CIRELLO | 1 | West | YES | 0.13886 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.30604 | 0 | 233 |  |  |  |  | 0.30604 | 71.3077
60063 | BUFF_GAP1B | 1 | West | YES | 0.13886 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.30604 | 0 | 170.2 |  |  |  |  | 0.30604 | 52.0883
60066 | H_HOLLOW1A | 1 | West | YES | 0.13886 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.30604 | 0 | 222 |  |  |  |  | 0.30604 | 67.9413
60068 | HHOLLOW21A | 1 | West | YES | 0.13886 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.30604 | 0 | 184 |  |  |  |  | 0.30604 | 56.3117
60070 | HHOLLOW31A | 1 | West | YES | 0.13886 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.30604 | 0 | 224 |  |  |  |  | 0.30604 | 68.5533
60072 | HHOLLOW41A | 1 | West | YES | 0.13886 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.30604 | 0 | 115 |  |  |  |  | 0.30604 | 35.1948
1301 | BULLCREK_8 | 1 | West | YES | 0.13901 | 36 | 0 | 180 | 0 | 1.017 | #N/A | 1 | 0.30619 | 180 | 180 |  |  |  |  | 0.30619 | 55.1149
1058 | LONGSHORE_5 | 3 | West | YES | 0.13906 | 23.4 | 0 | 117 |  | 1.01 | Wind | 1 | 0.30624 | 0 | 117 |  |  |  |  | 0.30624 | 35.8306
1058 | LONGSHORE_5 | 2 | West | YES | 0.13906 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.30624 | 0 | 220 |  |  |  |  | 0.30624 | 67.3738
1058 | LONGSHORE_5 | 1 | West | YES | 0.13906 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.30624 | 0 | 150 |  |  |  |  | 0.30624 | 45.9367
1343 | TRENTIPP_8 | 1 | West | YES | 0.13914 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.30632 | 0 | 150 |  |  |  |  | 0.30632 | 45.9486
1354 | AEPWIND_8 | 1 | West | YES | 0.13914 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.30632 | 0 | 101 |  |  |  |  | 0.30632 | 30.9387
1037 | MORGAN5G_5G | 5 | West | YES | 0.13922 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.30641 | 137 | 137 |  |  |  |  | 0.30641 | 41.9777
1039 | MRGNAG_1G | A | West | YES | 0.13922 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.30641 | 69 | 69 |  |  |  |  | 0.30641 | 21.1421
1040 | MRGNBG_2G | B | West | YES | 0.13922 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.30641 | 71 | 71 |  |  |  |  | 0.30641 | 21.7549
1041 | MRGNCG_3G | C | West | YES | 0.13922 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.30641 | 70 | 70 |  |  |  |  | 0.30641 | 21.4485
1042 | MRGNDG_4G | D | West | YES | 0.13922 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.30641 | 68 | 68 |  |  |  |  | 0.30641 | 20.8357
1043 | MRGNEG_5G | E | West | YES | 0.13922 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.30641 | 70 | 70 |  |  |  |  | 0.30641 | 21.4485
1044 | MRGNFG_6G | F | West | YES | 0.13922 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.30641 | 66 | 66 |  |  |  |  | 0.30641 | 20.2228
6637 | SNYDERW1A | 1 | West | YES | 0.13929 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.30647 | 0 | 63 |  |  |  |  | 0.30647 | 19.3079
1068 | SCURRYCW_1G | 1 | West | YES | 0.13941 | 28.2 | 1.3 | 141 |  | 1.01 | Wind | 1 | 0.3066 | 0 | 141 |  |  |  |  | 0.3066 | 43.2301
1073 | SCURRYCW_2G | 2 | West | YES | 0.13941 | 24 | 0 | 120 | 0 | 1.017 | Wind | 1 | 0.3066 | 0 | 120 |  |  |  |  | 0.3066 | 36.7916
1061 | CIELOGEN_1G | 1 | West | YES | 0.13943 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.30661 | 0 | 99 |  |  |  |  | 0.30661 | 30.3548
1062 | CIELOGEN_2G | 1 | West | YES | 0.13943 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.30661 | 0 | 61 |  |  |  |  | 0.30661 | 18.7034
1069 | KINDERMG_1G | 1 | West | YES | 0.13943 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.30661 | 0 | 0 |  |  |  |  | 0.30661 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.13943 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30661 | 0 | 0 |  |  |  |  | 0.30661 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.13943 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.30661 | 0 | 0 |  |  |  |  | 0.30661 | 0
36998 | RDCNYNG1 | 1 | West | YES | 0.13972 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.30691 | 0 | 84 |  |  |  |  | 0.30691 | 25.7805
6144 | MCADOO1A | 1 | West | YES | 0.14102 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.30821 | 0 | 150 |  |  |  |  | 0.30821 | 46.2316
71051 | L_BITTCR1_1N | W1 | West | YES | 0.14112 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.3083 | 0 | 37.5 |  |  |  |  | 0.3083 | 11.5614
71054 | L_SWEETW1_1N | W1 | West | YES | 0.14112 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.3083 | 0 | 107.5 |  |  |  |  | 0.3083 | 33.1428
71057 | L_SWEETW1_2N | W1 | West | YES | 0.14112 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.3083 | 0 | 135 |  |  |  |  | 0.3083 | 41.6211
71059 | L_SWEETW1_3N | W1 | West | YES | 0.14112 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.3083 | 0 | 119 |  |  |  |  | 0.3083 | 36.6883
71060 | L_SWEETW1_4N | W1 | West | YES | 0.14112 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.3083 | 0 | 105 |  |  |  |  | 0.3083 | 32.372
1049 | ROSCOEWI_5 | 1 | West | YES | 0.14132 | 41.8 | 0 | 209 |  | 1.01 | #N/A | 1 | 0.30851 | 209 | 209 |  |  |  |  | 0.30851 | 64.4777
1057 | ROSCOEWI_5 | 2 | West | YES | 0.14132 | 25.3 | 0 | 126.5 |  | 1.01 | #N/A | 1 | 0.30851 | 126.5 | 126.5 |  |  |  |  | 0.30851 | 39.026
1060 | ROSCOEWI_5 | 3 | West | YES | 0.14132 | 39.4 | 0 | 197 | 0 | 1.01 | #N/A | 1 | 0.30851 | 197 | 197 |  |  |  |  | 0.30851 | 60.7756
1072 | ROSCOEWI_5 | 4 | West | YES | 0.14132 | 63.6 | 0 | 318 | 0 | 1.01 | #N/A | 1 | 0.30851 | 318 | 318 |  |  |  |  | 0.30851 | 98.1048
1416 | SWETWATR_1G | 1 | West | YES | 0.14217 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.30936 | 30 | 30 |  |  |  |  | 0.30936 | 9.2809
1417 | SWETWATR_2G | 2 | West | YES | 0.14217 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.30936 | 72 | 72 |  |  |  |  | 0.30936 | 22.274
1418 | SWETWATR_3G | 3 | West | YES | 0.14217 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.30936 | 68 | 68 |  |  |  |  | 0.30936 | 21.0366
1419 | SWETWATR_4G | 4 | West | YES | 0.14217 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.30936 | 61 | 61 |  |  |  |  | 0.30936 | 18.8711
60081 | WHRLWIND1A | 1 | West | YES | 0.14286 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.31004 | 0 | 60 |  |  |  |  | 0.31004 | 18.6025
60052 | WILDHRS11A | 1 | West | YES | 0.14403 | 25.3 | 0 | 126.5 | 0 | 1.005 | #N/A | 1 | 0.31122 | 126.5 | 126.5 |  |  |  |  | 0.31122 | 39.3688
60053 | WILDHRS21A | 1 | West | YES | 0.14403 | 7.8 | 0 | 39 | 0 | 1.025 | #N/A | 1 | 0.31122 | 39 | 39 |  |  |  |  | 0.31122 | 12.1374
12322 | ENNSTRAC_1G | 1 | North | YES | 0.14463 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.31182 | 196 | 196 | 28.3481 | 196 |  |  | 0.31182 | 61.1167
12323 | ENNSTRAC_2G | 2 | North | YES | 0.14463 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.31182 | 116 | 116 | 16.7774 | 116 |  |  | 0.31182 | 36.1711
12411 | FPLEFR1A_G | 1 | North | YES | 0.1451 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.31228 | 161 | 161 | 23.3606 | 161 |  |  | 0.31228 | 50.2777
12412 | FPLEFR1B_G | 2 | North | YES | 0.1451 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.31228 | 164 | 164 | 23.7959 | 164 |  |  | 0.31228 | 51.2145
12413 | FPLEFR1C_G | 3 | North | YES | 0.1451 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.31228 | 164 | 164 | 23.7959 | 164 |  |  | 0.31228 | 51.2145
12414 | FPLEFR1S_G | 4 | North | YES | 0.1451 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.31228 | 414 | 414 | 60.0702 | 414 |  |  | 0.31228 | 129.2855
12421 | FPLEFR2A_G | 1 | North | YES | 0.1451 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.31228 | 162 | 162 | 23.5057 | 162 |  |  | 0.31228 | 50.59
12422 | FPLEFR2B_G | 2 | North | YES | 0.1451 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.31228 | 161 | 161 | 23.3606 | 161 |  |  | 0.31228 | 50.2777
12423 | FPLEFR2C_G | 3 | North | YES | 0.1451 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.31228 | 163 | 163 | 23.6508 | 163 |  |  | 0.31228 | 50.9022
12424 | FPLEFR2S_G | 4 | North | YES | 0.1451 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.31228 | 415 | 415 | 60.2153 | 415 |  |  | 0.31228 | 129.5977
1437 | MESQUITW_1G | 1 | North | YES | 0.14627 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.31346 | 0 | 400 | 58.5092 | 400 |  |  | 0.31346 | 125.3839
1438 | MESQUITW_2G | 1 | North | YES | 0.14628 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.31347 | 0 | 236 | 34.5228 | 236 |  |  | 0.31347 | 73.9788
1643 | SLSTR1PP_1G | 1 | North | YES | 0.14657 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.31376 | 0 | 60 | 8.7943 | 60 |  |  | 0.31376 | 18.8255
2451 | LKHB1_G | 1 | North | YES | 0.14757 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.31476 | 391 | 391 | 57.7003 | 391 |  |  | 0.31476 | 123.0703
2452 | LKHB2_G | 2 | North | YES | 0.14757 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.31476 | 516 | 516 | 76.1466 | 516 |  |  | 0.31476 | 162.415
948 | STEAM1 | 1 | North | YES | 0.14779 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.31497 | 20 | 20 | 2.9557 | 20 |  |  | 0.31497 | 6.2995
949 | STEAM2 | 1 | North | YES | 0.14779 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.31497 | 26 | 26 | 3.8425 | 26 |  |  | 0.31497 | 8.1893
950 | STEAM3 | 1 | North | YES | 0.14779 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.31497 | 42 | 42 | 6.2071 | 42 |  |  | 0.31497 | 13.2289
1442 | COKFIELD_5 | 1 | North | YES | 0.14795 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.31514 | 0 | 165 | 24.4121 | 165 |  |  | 0.31514 | 51.9979
837 | NEWMAN_G5 | 1 | North | YES | 0.14808 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.31526 | 40 | 40 | 5.923 | 40 |  |  | 0.31526 | 12.6105
12440 | PARKD_1SVC8 | 1 | North | YES | 0.14835 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.31554 | 0 | 0 | 0 | 0 |  |  | 0.31554 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.14835 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.31554 | 0 | 0 | 0 | 0 |  |  | 0.31554 | 0
842 | OLINGER_G1 | 1 | North | YES | 0.14836 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.31555 | 79 | 79 | 11.7205 | 79 |  |  | 0.31555 | 24.9283
843 | OLINGER_G2 | 1 | North | YES | 0.14836 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.31555 | 110 | 110 | 16.3197 | 110 |  |  | 0.31555 | 34.7102
844 | OLINGER_G3 | 1 | North | YES | 0.14836 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.31555 | 150 | 150 | 22.2541 | 150 |  |  | 0.31555 | 47.3322
845 | OLINGER_G4 | 1 | North | YES | 0.14836 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.31555 | 76 | 76 | 11.2754 | 76 |  |  | 0.31555 | 23.9816
6100 | OKLA7A | EQ | West | YES | 0.14893 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.31612 | 0 | 0 |  |  |  |  | 0.31612 | 0
6752 | OKLA0A | 1 | West | YES | 0.14893 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.31612 | 0 | 649.7 |  |  |  |  | 0.31612 | 205.3836
1701 | MOSES_1G | 1 | North | YES | 0.14924 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.31643 | 0 | 558 | 83.2759 | 558 |  |  | 0.31643 | 176.5661
1702 | MOSES_2G | 2 | North | YES | 0.14924 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.31643 | 0 | 579 | 86.41 | 579 |  |  | 0.31643 | 183.2111
1703 | MOSES_3G | 3 | North | YES | 0.14924 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.31643 | 0 | 808 | 120.5859 | 808 |  |  | 0.31643 | 255.6728
5925 | DCEAST | EQ | North | YES | 0.14924 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.31643 | 0 | 0 | 0 | 0 |  |  | 0.31643 | 0
1675 | PEC_1G | 1 | North | YES | 0.14948 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.31667 | 0 | 0 | 0 | 0 |  |  | 0.31667 | 0
1676 | PEC_2G | 2 | North | YES | 0.14948 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.31667 | 0 | 0 | 0 | 0 |  |  | 0.31667 | 0
1677 | PEC_3G | 3 | North | YES | 0.14948 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.31667 | 0 | 0 | 0 | 0 |  |  | 0.31667 | 0
1678 | LAMARPWR_1G | 1 | North | YES | 0.14984 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.31703 | 160 | 160 | 23.9746 | 160 |  |  | 0.31703 | 50.7244
1679 | LAMARPWR_2G | 2 | North | YES | 0.14984 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.31703 | 156 | 156 | 23.3752 | 156 |  |  | 0.31703 | 49.4563
1680 | LAMARPWR_3G | 3 | North | YES | 0.14984 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.31703 | 196 | 196 | 29.3688 | 196 |  |  | 0.31703 | 62.1374
1681 | LAMARPWR_4G | 4 | North | YES | 0.14984 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.31703 | 156 | 156 | 23.3752 | 156 |  |  | 0.31703 | 49.4563
1682 | LAMARPWR_5G | 5 | North | YES | 0.14984 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.31703 | 157 | 157 | 23.525 | 157 |  |  | 0.31703 | 49.7733
1683 | LAMARPWR_6G | 6 | North | YES | 0.14984 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.31703 | 198 | 198 | 29.6685 | 198 |  |  | 0.31703 | 62.7715
1689 | VALLEY_3G | 3 | North | YES | 0.15022 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.31741 | 375 | 375 | 56.3332 | 375 |  |  | 0.31741 | 119.0283
11691 | KMICHICT1_G | 1 | North | YES | 0.15022 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.31741 | 144 | 144 | 21.632 | 144 |  |  | 0.31741 | 45.7069
11692 | KMICHICT2_G | 2 | North | YES | 0.15022 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.31741 | 146 | 146 | 21.9324 | 146 |  |  | 0.31741 | 46.3417
11693 | KMICHIST3_G | 3 | North | YES | 0.15022 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.31741 | 312 | 312 | 46.8693 | 312 |  |  | 0.31741 | 99.0315
11694 | KMICHICT4_G | 4 | North | YES | 0.15022 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.31741 | 144 | 144 | 21.632 | 144 |  |  | 0.31741 | 45.7069
11695 | KMICHICT5_G | 5 | North | YES | 0.15022 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.31741 | 148 | 148 | 22.2329 | 148 |  |  | 0.31741 | 46.9765
11696 | KMICHIST6_G | 6 | North | YES | 0.15022 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.31741 | 310 | 310 | 46.5688 | 310 |  |  | 0.31741 | 98.3967
1687 | VALLEY_1G | 1 | North | YES | 0.15075 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.31793 | 170 | 170 | 25.627 | 170 |  |  | 0.31793 | 54.0487
1688 | VALLEY_2G | 2 | North | YES | 0.15075 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.31793 | 527 | 527 | 79.4437 | 527 |  |  | 0.31793 | 167.5511
6948 | DENISNDM | 2 | North | YES | 0.15123 | 31 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.31841 | 0 | 0 | 0 | 0 |  |  | 0.31841 | 0
6948 | DENISNDM | 1 | North | YES | 0.15123 | 40 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.31841 | 0 | 0 | 0 | 0 |  |  | 0.31841 | 0
1433 | GRHAMSES_1G | 1 | North | YES | 0.15193 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.31911 | 242 | 242 | 36.7661 | 242 |  |  | 0.31911 | 77.2253
1479 | WFCOGEN_1G | 2 | North | YES | 0.15289 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.32008 | 0 | 0 | 0 | 0 |  |  | 0.32008 | 0
1479 | WFCOGEN_1G | 1 | North | YES | 0.15289 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.32008 | 0 | 0 | 0 | 0 |  |  | 0.32008 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.15289 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.32008 | 0 | 0 | 0 | 0 |  |  | 0.32008 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.15289 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.32008 | 0 | 0 | 0 | 0 |  |  | 0.32008 | 0
1432 | GRHAMSES_2G | 2 | North | YES | 0.15324 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.32043 | 366 | 366 | 56.0858 | 366 |  |  | 0.32043 | 117.2762
2371 | COLLIN_1G | MB | North | YES | 0.15349 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.32068 | 0 | 0 | 0 | 0 |  |  | 0.32068 | 0
2413 | MTCK6_G | 6 | North | YES | 0.1539 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.32109 | 118 | 118 | 18.1608 | 118 |  |  | 0.32109 | 37.8888
2414 | MTCK7_G | 7 | North | YES | 0.1539 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.32109 | 115 | 115 | 17.6991 | 115 |  |  | 0.32109 | 36.9255
2417 | MTCK8_G | 8 | North | YES | 0.1539 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.32109 | 556 | 556 | 85.5712 | 556 |  |  | 0.32109 | 178.527
1600 | BARTNWND_1G | 1 | North | YES | 0.15482 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.32201 | 0 | 120 | 18.5783 | 120 |  |  | 0.32201 | 38.6407
344 | MRSSHPRD | 1 | North | YES | 0.15515 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.32233 | 0 | 0 | 0 | 0 |  |  | 0.32233 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.15515 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.32233 | 0 | 0 | 0 | 0 |  |  | 0.32233 | 0
332 | RWMILLER01 | 1 | North | YES | 0.15523 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.32242 | 73 | 73 | 11.3319 | 73 |  |  | 0.32242 | 23.5365
333 | RWMILLER02 | 2 | North | YES | 0.15523 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.32242 | 119 | 119 | 18.4725 | 119 |  |  | 0.32242 | 38.3677
334 | RWMILLER03 | 3 | North | YES | 0.15523 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.32242 | 208 | 208 | 32.288 | 208 |  |  | 0.32242 | 67.0629
335 | RWMILLER04 | 4 | North | YES | 0.15523 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.32242 | 102 | 102 | 15.8336 | 102 |  |  | 0.32242 | 32.8866
336 | RWMILLER05 | 5 | North | YES | 0.15523 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.32242 | 101 | 101 | 15.6783 | 101 |  |  | 0.32242 | 32.5642
244 | WHITNYDM01 | 1 | North | YES | 0.15549 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.32267 | 0 | 0 | 0 | 0 |  |  | 0.32267 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.15549 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.32267 | 0 | 0 | 0 | 0 |  |  | 0.32267 | 0
2381 | NTHLK1_G | 1 | North | YES | 0.15593 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.32312 | 156 | 156 | 24.3259 | 156 |  |  | 0.32312 | 50.407
2382 | NTHLK2_G | 2 | North | YES | 0.15593 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.32312 | 181 | 181 | 28.2242 | 181 |  |  | 0.32312 | 58.485
2383 | NTHLK3_G | 3 | North | YES | 0.15593 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.32312 | 329 | 329 | 51.3026 | 329 |  |  | 0.32312 | 106.307
728 | WOLFRIDGE801 | 1 | North | YES | 0.15629 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.32347 | 0 | 112.5 | 17.5821 | 112.5 |  |  | 0.32347 | 36.3906
2418 | MTCK2_G | 2 | North | YES | 0.15634 | 0 | 10 | 23 |  | 0.971 | #N/A | 1 | 0.32352 | 23 | 23 | 3.5958 | 23 |  |  | 0.32352 | 7.441
2419 | MTCK3_G | MB | North | YES | 0.15634 | 0 | 10 | 63 |  | 0.971 | #N/A | 1 | 0.32352 | 63 | 63 | 9.8492 | 63 |  |  | 0.32352 | 20.382
923 | SPENCER_G4 | 1 | North | YES | 0.1567 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.32389 | 61 | 61 | 9.5589 | 61 |  |  | 0.32389 | 19.7573
924 | SPENCER_G5 | 1 | North | YES | 0.1567 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.32389 | 66 | 66 | 10.3424 | 66 |  |  | 0.32389 | 21.3767
251 | BOSQUESW803 | 2 | North | YES | 0.15777 | 150 | 0 | 150 |  | 1.032 | CC | 1 | 0.32496 | 150 | 150 | 23.6659 | 150 |  |  | 0.32496 | 48.744
253 | BOSQUESW804 | 2 | North | YES | 0.15777 | 80 | 0 | 80 |  | 1.032 | CC | 1 | 0.32496 | 80 | 80 | 12.6218 | 80 |  |  | 0.32496 | 25.9968
1453 | WCPWRCO_1G | 1 | North | YES | 0.15785 | 204 | 50 | 204 |  | 1.02 | CC | 1 | 0.32504 | 204 | 204 | 32.2014 | 204 |  |  | 0.32504 | 66.3075
1454 | WCPWRCO_2G | 2 | North | YES | 0.15785 | 204 | 50 | 204 |  | 1.02 | CC | 1 | 0.32504 | 204 | 204 | 32.2014 | 204 |  |  | 0.32504 | 66.3075
1455 | WCPWRCO_3G | 3 | North | YES | 0.15785 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.32504 | 242 | 242 | 38.1997 | 242 |  |  | 0.32504 | 78.6589
503 | NTHTEXAS01 | 1 | North | YES | 0.15804 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.32522 | 18 | 18 | 2.8447 | 18 |  |  | 0.32522 | 5.854
504 | NTHTEXAS02 | 2 | North | YES | 0.15804 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.32522 | 18 | 18 | 2.8447 | 18 |  |  | 0.32522 | 5.854
505 | NTHTEXAS03 | 3 | North | YES | 0.15804 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.32522 | 38 | 38 | 6.0054 | 38 |  |  | 0.32522 | 12.3585
580 | JCKCNTY801 | 1 | North | YES | 0.15807 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.32526 | 288 | 288 | 45.5256 | 288 |  |  | 0.32526 | 93.6754
581 | JCKCNTY802 | 2 | North | YES | 0.15807 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.32526 | 147 | 147 | 23.237 | 147 |  |  | 0.32526 | 47.8135
582 | JCKCNTY803 | 3 | North | YES | 0.15807 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.32526 | 147 | 147 | 23.237 | 147 |  |  | 0.32526 | 47.8135
1861 | EAGLEMNT_1G | MB | North | YES | 0.16195 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.32913 | 0 | 0 | 0 | 0 |  |  | 0.32913 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.16195 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.32913 | 0 | 0 | 0 | 0 |  |  | 0.32913 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.16195 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.32913 | 0 | 0 | 0 | 0 |  |  | 0.32913 | 0
1892 | DECRDOVA_2G | A | North | YES | 0.16307 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.33026 | 70 | 70 | 11.4152 | 70 |  |  | 0.33026 | 23.1182
1893 | DECRDOVA_3G | B | North | YES | 0.16307 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.33026 | 69 | 69 | 11.2521 | 69 |  |  | 0.33026 | 22.788
1894 | DECRDOVA_4G | C | North | YES | 0.16307 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.33026 | 69 | 69 | 11.2521 | 69 |  |  | 0.33026 | 22.788
1895 | DECRDOVA_5G | D | North | YES | 0.16307 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.33026 | 68 | 68 | 11.089 | 68 |  |  | 0.33026 | 22.4577
1898 | COMCHEPK_1G | 1 | North | YES | 0.16435 | 1159 | 1150 | 1159 | 0 | 1.032 | Nuc | 1 | 0.33154 | 0 | 0 | 0 | 0 |  |  | 0.33154 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.16435 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.33154 | 0 | 0 | 0 | 0 |  |  | 0.33154 | 0
1877 | WLFHOLW_1G | 1 | North | YES | 0.1652 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.33239 | 217.3 | 217.3 | 35.898 | 217.3 |  |  | 0.33239 | 72.2276
1878 | WLFHOLW_2G | 2 | North | YES | 0.1652 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.33239 | 215.7 | 215.7 | 35.6336 | 215.7 |  |  | 0.33239 | 71.6958
1879 | WLFHOLW_3G | 3 | North | YES | 0.1652 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.33239 | 272.4 | 272.4 | 45.0005 | 272.4 |  |  | 0.33239 | 90.5421
1889 | DECRDOVA_1G | 1 | North | YES | 0.1652 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.33239 | 779 | 779 | 128.6947 | 779 |  |  | 0.33239 | 258.9331
1945 | HANDLEY_1G | MB | North | YES | 0.16583 | 0 | 25 | 36 |  | 0.986 | #N/A | 1 | 0.33301 | 36 | 36 | 5.9698 | 36 |  |  | 0.33301 | 11.9885
1946 | HANDLEY_2G | MB | North | YES | 0.16583 | 0 | 30 | 68 |  | 0.986 | #N/A | 1 | 0.33301 | 68 | 68 | 11.2763 | 68 |  |  | 0.33301 | 22.645
1948 | HANDLEY_4G | 4 | North | YES | 0.16607 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.33326 | 435 | 435 | 72.2413 | 435 |  |  | 0.33326 | 144.9675
1947 | HANDLEY_3G | 3 | North | YES | 0.16683 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.33401 | 395 | 395 | 65.8959 | 395 |  |  | 0.33401 | 131.9346
1949 | HANDLEY_5G | 5 | North | YES | 0.16683 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.33401 | 435 | 435 | 72.5689 | 435 |  |  | 0.33401 | 145.2951
366 | JNSNCNTY802 | 1 | North | YES | 0.16688 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.33407 | 0 | 0 | 0 | 0 |  |  | 0.33407 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.16688 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.33407 | 0 | 0 | 0 | 0 |  |  | 0.33407 | 0
1937 | MDLTHELP_5G | 5 | North | YES | 0.18086 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.34805 | 224 | 224 | 40.5131 | 224 |  |  | 0.34805 | 77.9629
1938 | MDLTHELP_6G | 6 | North | YES | 0.18086 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.34805 | 226 | 226 | 40.8748 | 226 |  |  | 0.34805 | 78.659
1943 | MDLTHELP_3G | 3 | North | YES | 0.18086 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.34805 | 212 | 212 | 38.3427 | 212 |  |  | 0.34805 | 73.7863
1944 | MDLTHELP_4G | 4 | North | YES | 0.18086 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.34805 | 211 | 211 | 38.1619 | 211 |  |  | 0.34805 | 73.4383
1941 | MDLTHELP_1G | 1 | North | YES | 0.18107 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.34826 | 216.4 | 216.4 | 39.1838 | 216.4 |  |  | 0.34826 | 75.363
1942 | MDLTHELP_2G | 2 | North | YES | 0.18107 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.34826 | 216.1 | 216.1 | 39.1294 | 216.1 |  |  | 0.34826 | 75.2585
238 | BOSQUESW505 | 1 | North | YES | 0.22295 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.39013 | 255 | 255 | 56.851 | 255 |  |  | 0.39013 | 99.4836
239 | BOSQUESW502 | 1 | North | YES | 0.22295 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.39013 | 149 | 149 | 33.2188 | 149 |  |  | 0.39013 | 58.1296
247 | BOSQUESW501 | 2 | North | YES | 0.22295 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.39013 | 156 | 156 | 34.7794 | 156 |  |  | 0.39013 | 60.8605
3403 | THOUSE_1G | 1 | North | YES | 0.36247 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.52966 | 563 | 563 | 204.0712 | 563 |  |  | 0.52966 | 298.1973
3404 | THOUSE_2G | 2 | North | YES | 0.36247 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.52966 | 807 | 807 | 292.5141 | 807 |  |  | 0.52966 | 427.4338
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Bound Gen
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | max of zone correlation | -0.27351 |  |  | Neg PTDF weight | Pos PTDF weight
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | -0.077468 | 0 | 0 |  |  | 0 | 0 | 0.077468 | 0 |  |  |  |  | 0 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | -0.077468 | 0 | 0 |  |  | 0 | 0 | 0.077468 | 0 |  |  |  |  | 0 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | -0.077468 | 0 | 0 |  |  | 0 | 0 | 0.077468 | 0 |  |  |  |  | 0 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | -0.077468 | 0 | 0 |  |  | 0 | 0 | 0.077468 | 0 |  |  | Weighted Shift Factors |  | 0 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | -0.077468 | 0 | 0 |  |  | 0 | 0 | 0.077468 | 0 |  |  | North | -0.077468 | 0 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | -0.077468 | 0 | 0 |  |  | 0 | 0 | 0.077468 | 0 |  |  | South | 0.11295 | 0 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | -0.077468 | 0 | 0 |  |  | 0 | 0 | 0.077468 | 0 |  |  |  |  | 0 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | -0.077468 | 0 | 0 |  |  | 0 | 0 | 0.077468 | 0 | South |  |  |  | 0 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | -0.077468 | 0 | 0 |  |  |  |  | 0.077468 | 0 | Line Rating |  | 956 |  | 0 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | -0.077468 | 15 | 15 |  |  | 0 | 15 | 0.077468 | 1.162 | Impact Counter to Zone: |  | 0 |  | 0 | 1.162
48591 | CHE_GT2_5030 | 2 | Houston | YES | 0.018069 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | -0.095537 | 0 | 0 |  |  |  |  | 0.095537 | 0 |  |  | 0% |  | 0 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | 0.018069 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | -0.095537 | 0 | 0 |  |  |  |  | 0.095537 | 0 |  |  |  |  | 0 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | 0.018069 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | -0.095537 | 0 | 0 |  |  |  |  | 0.095537 | 0 | North |  |  |  | 0 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | 0.018069 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | -0.095537 | 0 | 0 |  |  |  |  | 0.095537 | 0 | Line Rating |  | 956 |  | 0 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | 0.018069 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | -0.095537 | 0 | 0 |  |  |  |  | 0.095537 | 0 | Impact Counter to Zone: |  | 0 |  | 0 | 0
48886 | THW_5354 | C | Houston | YES | 0.021892 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | -0.09936 | 57 | 57 |  |  |  |  | 0.09936 | 5.6635 |  |  | 0% |  | 0 | 5.6635
48887 | THW_5556 | F | Houston | YES | 0.021892 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | -0.09936 | 57 | 57 |  |  |  |  | 0.09936 | 5.6635 |  |  |  |  | 0 | 5.6635
48885 | THW_5152 | A | Houston | YES | 0.021892 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | -0.09936 | 58 | 58 |  |  |  |  | 0.09936 | 5.7629 |  |  |  |  | 0 | 5.7629
48886 | THW_5354 | D | Houston | YES | 0.021892 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | -0.09936 | 58 | 58 |  |  |  |  | 0.09936 | 5.7629 |  |  |  |  | 0 | 5.7629
48885 | THW_5152 | B | Houston | YES | 0.021892 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | -0.09936 | 59 | 59 |  |  |  |  | 0.09936 | 5.8623 |  |  |  |  | 0 | 5.8623
48887 | THW_5556 | E | Houston | YES | 0.021892 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | -0.09936 | 59 | 59 |  |  |  |  | 0.09936 | 5.8623 |  |  |  |  | 0 | 5.8623
48690 | GBY_GN5_5 | 5 | Houston | YES | 0.022163 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | -0.099631 | 398 | 398 |  |  |  |  | 0.099631 | 39.6533 |  |  |  |  | 0 | 39.6533
48597 | BTE_GT4_8055 | 3 | Houston | YES | 0.022361 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | -0.099829 | 158.9 | 158.9 |  |  |  |  | 0.099829 | 15.8629 |  |  |  |  | 0 | 15.8629
48596 | BTE_GT3_8045 | 2 | Houston | YES | 0.022361 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | -0.099829 | 161.4 | 161.4 |  |  |  |  | 0.099829 | 16.1125 |  |  |  |  | 0 | 16.1125
48595 | BTE_GT2_8075 | 1 | Houston | YES | 0.022361 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | -0.099829 | 162.8 | 162.8 |  |  |  |  | 0.099829 | 16.2522 |  |  |  |  | 0 | 16.2522
48598 | BTE_ST1_8070 | 4 | Houston | YES | 0.022361 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | -0.099829 | 269.2 | 269.2 |  |  |  |  | 0.099829 | 26.8741 |  |  |  |  | 0 | 26.8741
48583 | CBY_GT4_1 | 1 | Houston | YES | 0.022988 | 172 | 0 | 172 | 0 | 1.027 | GSC | -1 | -0.10046 | 172 | 172 |  |  |  |  | 0.10046 | 17.2785 |  |  |  |  | 0 | 17.2785
48584 | CBY_GT4_2 | 2 | Houston | YES | 0.022988 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | -0.10046 | 172 | 172 |  |  |  |  | 0.10046 | 17.2785 |  |  |  |  | 0 | 17.2785
48585 | CBY_ST4_1 | 3 | Houston | YES | 0.022988 | 172 | 0 | 172 | 0 | 1.027 | CC | -1 | -0.10046 | 172 | 172 |  |  |  |  | 0.10046 | 17.2785 |  |  |  |  | 0 | 17.2785
48815 | CVC_GT4_8005 | 4 | Houston | YES | 0.023096 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | -0.10056 | 0 | 0 |  |  |  |  | 0.10056 | 0 |  |  |  |  | 0 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | 0.023295 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | -0.10076 | 0 | 0 |  |  |  |  | 0.10076 | 0 |  |  |  |  | 0 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | 0.023295 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | -0.10076 | 0 | 0 |  |  |  |  | 0.10076 | 0 |  |  |  |  | 0 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | 0.023295 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | -0.10076 | 0 | 0 |  |  |  |  | 0.10076 | 0 |  |  |  |  | 0 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | 0.023295 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | -0.10076 | 0 | 0 |  |  |  |  | 0.10076 | 0 |  |  |  |  | 0 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | 0.023295 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | -0.10076 | 0 | 0 |  |  |  |  | 0.10076 | 0 |  |  |  |  | 0 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | 0.023295 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | -0.10076 | 0 | 0 |  |  |  |  | 0.10076 | 0 |  |  |  |  | 0 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | 0.023295 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | -0.10076 | 0 | 0 |  |  |  |  | 0.10076 | 0 |  |  |  |  | 0 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | 0.023307 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | -0.10078 | 744 | 744 |  |  |  |  | 0.10078 | 74.9769 |  |  |  |  | 0 | 74.9769
48940 | WARVUE_GT1 | G1 | Houston | YES | 0.02332 | 15 | 0 | 15 |  | 1.021 | Cogen | -1 | -0.10079 | 0 | 0 |  |  |  |  | 0.10079 | 0 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 1 | Houston | YES | 0.023331 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | -0.1008 | 0 | 0 |  |  |  |  | 0.1008 | 0 |  |  |  |  | 0 | 0
48651 | EP_1_2 | 2 | Houston | YES | 0.023331 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | -0.1008 | 0 | 0 |  |  |  |  | 0.1008 | 0 |  |  |  |  | 0 | 0
49803 | EXN_15GT | 1 | Houston | YES | 0.023691 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | -0.10116 | 0 | 0 |  |  |  |  | 0.10116 | 0 |  |  |  |  | 0 | 0
49804 | EXN_16GT | 2 | Houston | YES | 0.023691 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | -0.10116 | 0 | 0 |  |  |  |  | 0.10116 | 0 |  |  |  |  | 0 | 0
49805 | EXN_17GT | 3 | Houston | YES | 0.023691 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | -0.10116 | 0 | 0 |  |  |  |  | 0.10116 | 0 |  |  |  |  | 0 | 0
49826 | EXN938GT | 5 | Houston | YES | 0.023691 | 43 | 9.2 | 45.9 |  | 1.0326 | Cogen | -1 | -0.10116 | 0 | 0 |  |  |  |  | 0.10116 | 0 |  |  |  |  | 0 | 0
49828 | EXN941GT | 10 | Houston | YES | 0.023691 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | -0.10116 | 0 | 0 |  |  |  |  | 0.10116 | 0 |  |  |  |  | 0 | 0
49829 | EXN942GT | 11 | Houston | YES | 0.023691 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | -0.10116 | 0 | 0 |  |  |  |  | 0.10116 | 0 |  |  |  |  | 0 | 0
49830 | EXN943GT | 12 | Houston | YES | 0.023691 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | -0.10116 | 0 | 0 |  |  |  |  | 0.10116 | 0 |  |  |  |  | 0 | 0
49831 | EXN944GT | 13 | Houston | YES | 0.023691 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | -0.10116 | 0 | 0 |  |  |  |  | 0.10116 | 0 |  |  |  |  | 0 | 0
49832 | EXN945GT | 9 | Houston | YES | 0.023691 | 18.5 | 9.2 | 18.5 |  | 1.0326 | Cogen | -1 | -0.10116 | 0 | 0 |  |  |  |  | 0.10116 | 0 |  |  |  |  | 0 | 0
49837 | EXN_GT | 4 | Houston | YES | 0.023691 | 81 | 21.3 | 85.4 |  | 1.0326 | Cogen | -1 | -0.10116 | 0 | 0 |  |  |  |  | 0.10116 | 0 |  |  |  |  | 0 | 0
49838 | EXN_14GT | 14 | Houston | YES | 0.023691 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | -0.10116 | 0 | 0 |  |  |  |  | 0.10116 | 0 |  |  |  |  | 0 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | 0.023792 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | -0.10126 | 12 | 12 |  |  |  |  | 0.10126 | 1.2151 |  |  |  |  | 0 | 1.2151
48582 | CBY_GN2_2 | 2 | Houston | YES | 0.024063 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | -0.10153 | 746 | 746 |  |  |  |  | 0.10153 | 75.7424 |  |  |  |  | 0 | 75.7424
48875 | THW_3132 | B | Houston | YES | 0.024625 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | -0.10209 | 53 | 53 |  |  |  |  | 0.10209 | 5.4109 |  |  |  |  | 0 | 5.4109
48875 | THW_3132 | A | Houston | YES | 0.024625 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | -0.10209 | 55 | 55 |  |  |  |  | 0.10209 | 5.6151 |  |  |  |  | 0 | 5.6151
48877 | THW_3334 | C | Houston | YES | 0.024625 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | -0.10209 | 55 | 55 |  |  |  |  | 0.10209 | 5.6151 |  |  |  |  | 0 | 5.6151
48879 | THW_4142 | F | Houston | YES | 0.024625 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | -0.10209 | 55 | 55 |  |  |  |  | 0.10209 | 5.6151 |  |  |  |  | 0 | 5.6151
48879 | THW_4142 | E | Houston | YES | 0.024625 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | -0.10209 | 56 | 56 |  |  |  |  | 0.10209 | 5.7172 |  |  |  |  | 0 | 5.7172
48877 | THW_3334 | D | Houston | YES | 0.024625 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | -0.10209 | 57 | 57 |  |  |  |  | 0.10209 | 5.8193 |  |  |  |  | 0 | 5.8193
48881 | THW_4344 | G | Houston | YES | 0.024625 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | -0.10209 | 58 | 58 |  |  |  |  | 0.10209 | 5.9214 |  |  |  |  | 0 | 5.9214
48881 | THW_4344 | H | Houston | YES | 0.024625 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | -0.10209 | 58 | 58 |  |  |  |  | 0.10209 | 5.9214 |  |  |  |  | 0 | 5.9214
48873 | THW_ST3_ST_3 | 3 | Houston | YES | 0.024625 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | -0.10209 | 107 | 107 |  |  |  |  | 0.10209 | 10.924 |  |  |  |  | 0 | 10.924
48874 | THW_ST4_ST_4 | 4 | Houston | YES | 0.024625 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | -0.10209 | 108 | 108 |  |  |  |  | 0.10209 | 11.0261 |  |  |  |  | 0 | 11.0261
48593 | CHE_GT1_8015 | 1 | Houston | YES | 0.025305 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | -0.10277 | 0 | 0 |  |  |  |  | 0.10277 | 0 |  |  |  |  | 0 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | 0.025305 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | -0.10277 | 0 | 0 |  |  |  |  | 0.10277 | 0 |  |  |  |  | 0 | 0
48513 | LPE_GT3_8080 | 3 | Houston | YES | 0.025373 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | -0.10284 | 39 | 39 |  |  |  |  | 0.10284 | 4.0108 |  |  |  |  | 0 | 4.0108
48514 | LPE_GT4_8085 | 4 | Houston | YES | 0.025373 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | -0.10284 | 39 | 39 |  |  |  |  | 0.10284 | 4.0108 |  |  |  |  | 0 | 4.0108
48511 | LPE_GT1_8070 | 1 | Houston | YES | 0.025373 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | -0.10284 | 42 | 42 |  |  |  |  | 0.10284 | 4.3193 |  |  |  |  | 0 | 4.3193
48512 | LPE_GT2_8075 | 2 | Houston | YES | 0.025373 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | -0.10284 | 42 | 42 |  |  |  |  | 0.10284 | 4.3193 |  |  |  |  | 0 | 4.3193
48500 | APD_GT1_8005 | 1 | Houston | YES | 0.025482 | 137.6 | 54.6 | 137.6 | 0 | 1.0362 | Cogen | -1 | -0.10295 | 0 | 0 |  |  |  |  | 0.10295 | 0 |  |  |  |  | 0 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | 0.025943 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | -0.10341 | 0 | 0 |  |  |  |  | 0.10341 | 0 |  |  |  |  | 0 | 0
48821 | SHELLG2 | 2 | Houston | YES | 0.025943 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | -0.10341 | 0 | 0 |  |  |  |  | 0.10341 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | 0.025943 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | -0.10341 | 0 | 0 |  |  |  |  | 0.10341 | 0 |  |  |  |  | 0 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | 0.025943 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | -0.10341 | 0 | 0 |  |  |  |  | 0.10341 | 0 |  |  |  |  | 0 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | 0.026278 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | -0.10375 | 0 | 0 |  |  |  |  | 0.10375 | 0 |  |  |  |  | 0 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | 0.026278 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | -0.10375 | 0 | 0 |  |  |  |  | 0.10375 | 0 |  |  |  |  | 0 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | 0.026278 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | -0.10375 | 0 | 0 |  |  |  |  | 0.10375 | 0 |  |  |  |  | 0 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | 0.026279 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | -0.10375 | 228 | 228 |  |  |  |  | 0.10375 | 23.6544 |  |  |  |  | 0 | 23.6544
48611 | DIB_GT1_8080 | 1 | Houston | YES | 0.026285 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | -0.10375 | 0 | 0 |  |  |  |  | 0.10375 | 0 |  |  |  |  | 0 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | 0.026285 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | -0.10375 | 0 | 0 |  |  |  |  | 0.10375 | 0 |  |  |  |  | 0 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | 0.026285 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | -0.10375 | 0 | 0 |  |  |  |  | 0.10375 | 0 |  |  |  |  | 0 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | 0.026285 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | -0.10375 | 0 | 0 |  |  |  |  | 0.10375 | 0 |  |  |  |  | 0 | 0
48845 | SOL_GT1 | 1 | Houston | YES | 0.026288 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | -0.10376 | 16.2 | 16.2 |  |  |  |  | 0.10376 | 1.6809 |  |  |  |  | 0 | 1.6809
48853 | SRB_GN3_3 | 3 | Houston | YES | 0.026292 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | -0.10376 | 213 | 213 |  |  |  |  | 0.10376 | 22.101 |  |  |  |  | 0 | 22.101
48551 | CAL_GT1_8045 | 1 | Houston | YES | 0.02635 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | -0.10382 | 0 | 0 |  |  |  |  | 0.10382 | 0 |  |  |  |  | 0 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | 0.02635 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | -0.10382 | 0 | 0 |  |  |  |  | 0.10382 | 0 |  |  |  |  | 0 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | 0.026355 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | -0.10382 | 165 | 165 |  |  |  |  | 0.10382 | 17.1309 |  |  |  |  | 0 | 17.1309
48852 | SRB_GN2_2 | 2 | Houston | YES | 0.026374 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | -0.10384 | 176 | 176 |  |  |  |  | 0.10384 | 18.2763 |  |  |  |  | 0 | 18.2763
48855 | SRB_GT211035 | B2 | Houston | YES | 0.026387 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | -0.10386 | 12 | 12 |  |  |  |  | 0.10386 | 1.2463 |  |  |  |  | 0 | 1.2463
48855 | SRB_GT211035 | B1 | Houston | YES | 0.026387 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | -0.10386 | 18 | 18 |  |  |  |  | 0.10386 | 1.8694 |  |  |  |  | 0 | 1.8694
48761 | PR_GT1__9040 | 1 | Houston | YES | 0.026627 | 26 | 0 | 35 |  | 1 | Cogen | -1 | -0.1041 | 0 | 0 |  |  |  |  | 0.1041 | 0 |  |  |  |  | 0 | 0
48644 | DPEC_GT45070 | 4 | Houston | YES | 0.026862 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | -0.10433 | 157 | 157 |  |  |  |  | 0.10433 | 16.3799 |  |  |  |  | 0 | 16.3799
48642 | DPEC_GT25025 | 2 | Houston | YES | 0.026862 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | -0.10433 | 157.1 | 157.1 |  |  |  |  | 0.10433 | 16.3903 |  |  |  |  | 0 | 16.3903
48643 | DPEC_GT35010 | 3 | Houston | YES | 0.026862 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | -0.10433 | 157.5 | 157.5 |  |  |  |  | 0.10433 | 16.432 |  |  |  |  | 0 | 16.432
48641 | DPEC_GT15040 | 1 | Houston | YES | 0.026862 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | -0.10433 | 163.2 | 163.2 |  |  |  |  | 0.10433 | 17.0267 |  |  |  |  | 0 | 17.0267
48645 | DPEC_ST55065 | 5 | Houston | YES | 0.026862 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | -0.10433 | 282 | 282 |  |  |  |  | 0.10433 | 29.4212 |  |  |  |  | 0 | 29.4212
48841 | SJS_GT1_GT1 | 1 | Houston | YES | 0.027111 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | -0.10458 | 0 | 0 |  |  |  |  | 0.10458 | 0 |  |  |  |  | 0 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | 0.027111 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | -0.10458 | 0 | 0 |  |  |  |  | 0.10458 | 0 |  |  |  |  | 0 | 0
48691 | GBY_73741085 | B | Houston | YES | 0.02743 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | -0.1049 | 47 | 47 |  |  |  |  | 0.1049 | 4.9302 |  |  |  |  | 0 | 4.9302
48691 | GBY_73741085 | A | Houston | YES | 0.02743 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | -0.1049 | 47 | 47 |  |  |  |  | 0.1049 | 4.9302 |  |  |  |  | 0 | 4.9302
48692 | GBY_81821075 | C | Houston | YES | 0.02743 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | -0.1049 | 47 | 47 |  |  |  |  | 0.1049 | 4.9302 |  |  |  |  | 0 | 4.9302
48693 | GBY_83841065 | F | Houston | YES | 0.02743 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | -0.1049 | 54 | 54 |  |  |  |  | 0.1049 | 5.6645 |  |  |  |  | 0 | 5.6645
48692 | GBY_81821075 | D | Houston | YES | 0.02743 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | -0.1049 | 55 | 55 |  |  |  |  | 0.1049 | 5.7694 |  |  |  |  | 0 | 5.7694
48693 | GBY_83841065 | E | Houston | YES | 0.02743 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | -0.1049 | 57 | 57 |  |  |  |  | 0.1049 | 5.9792 |  |  |  |  | 0 | 5.9792
48531 | BYU_GT1_8075 | 1 | Houston | YES | 0.028073 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | -0.10554 | 0 | 0 |  |  |  |  | 0.10554 | 0 |  |  |  |  | 0 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | 0.028073 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | -0.10554 | 0 | 0 |  |  |  |  | 0.10554 | 0 |  |  |  |  | 0 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | 0.028073 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | -0.10554 | 0 | 0 |  |  |  |  | 0.10554 | 0 |  |  |  |  | 0 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | 0.028073 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | -0.10554 | 0 | 0 |  |  |  |  | 0.10554 | 0 |  |  |  |  | 0 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | 0.028585 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | -0.10605 | 0 | 0 |  |  |  |  | 0.10605 | 0 |  |  |  |  | 0 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | 0.028585 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | -0.10605 | 0 | 0 |  |  |  |  | 0.10605 | 0 |  |  |  |  | 0 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | 0.028585 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | -0.10605 | 0 | 0 |  |  |  |  | 0.10605 | 0 |  |  |  |  | 0 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | 0.028585 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | -0.10605 | 0 | 0 |  |  |  |  | 0.10605 | 0 |  |  |  |  | 0 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | 0.028585 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | -0.10605 | 0 | 0 |  |  |  |  | 0.10605 | 0 |  |  |  |  | 0 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | 0.029921 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | -0.10739 | 0 | 0 |  |  |  |  | 0.10739 | 0 |  |  |  |  | 0 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | 0.031835 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | 0.031835 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | 0.031835 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | 0.031835 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | 0.031835 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | 0.031835 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | 0.031835 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | 0.031835 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | 0.031835 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | 0.031835 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | 0.031835 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | 0.031835 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | 0.031835 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | 0.031835 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | 0.031835 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | -0.1093 | 0 | 0 |  |  |  |  | 0.1093 | 0 |  |  |  |  | 0 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | 0.036348 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | -0.11382 | 13 | 13 |  |  |  |  | 0.11382 | 1.4796 |  |  |  |  | 0 | 1.4796
48921 | WAP_GN1_1 | 1 | Houston | YES | 0.036348 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | -0.11382 | 166 | 166 |  |  |  |  | 0.11382 | 18.8935 |  |  |  |  | 0 | 18.8935
48922 | WAP_GN2_2 | 2 | Houston | YES | 0.036348 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | -0.11382 | 166 | 166 |  |  |  |  | 0.11382 | 18.8935 |  |  |  |  | 0 | 18.8935
48923 | WAP_GN3_3 | 3 | Houston | YES | 0.036348 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | -0.11382 | 248 | 248 |  |  |  |  | 0.11382 | 28.2265 |  |  |  |  | 0 | 28.2265
48924 | WAP_GN4_4 | 4 | Houston | YES | 0.036348 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | -0.11382 | 546 | 546 |  |  |  |  | 0.11382 | 62.1437 |  |  |  |  | 0 | 62.1437
48925 | WAP_GN5_5 | 5 | Houston | YES | 0.036348 | 579.1 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | -0.11382 | 0 | 654 |  |  |  |  | 0.11382 | 0 |  |  |  |  | 0 | 0
48510 | AK_GT1__8040 | 1 | Houston | YES | 0.036461 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | -0.11393 | 0 | 0 |  |  |  |  | 0.11393 | 0 |  |  |  |  | 0 | 0
48522 | BVE_GT2_5035 | 2 | Houston | YES | 0.037466 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | -0.11493 | 166.4 | 166.4 |  |  |  |  | 0.11493 | 19.1251 |  |  |  |  | 0 | 19.1251
48521 | BVE_GT1_GT1 | 1 | Houston | YES | 0.037466 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | -0.11493 | 167.7 | 167.7 |  |  |  |  | 0.11493 | 19.2745 |  |  |  |  | 0 | 19.2745
48523 | BVE_ST1_GN1 | 3 | Houston | YES | 0.037466 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | -0.11493 | 252.4 | 252.4 |  |  |  |  | 0.11493 | 29.0094 |  |  |  |  | 0 | 29.0094
48730 | MNS_GT | 1 | Houston | YES | 0.037502 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | -0.11497 | 0 | 0 |  |  |  |  | 0.11497 | 0 |  |  |  |  | 0 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | 0.037524 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | -0.11499 | 0 | 564 |  |  |  |  | 0.11499 | 0 |  |  |  |  | 0 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | 0.037524 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | -0.11499 | 0 | 603 |  |  |  |  | 0.11499 | 0 |  |  |  |  | 0 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | 0.037524 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | -0.11499 | 0 | 651 |  |  |  |  | 0.11499 | 0 |  |  |  |  | 0 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | 0.044401 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | -0.12187 | 0 | 0 |  |  |  |  | 0.12187 | 0 |  |  |  |  | 0 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | 0.044401 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | -0.12187 | 0 | 0 |  |  |  |  | 0.12187 | 0 |  |  |  |  | 0 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | 0.044401 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | -0.12187 | 0 | 0 |  |  |  |  | 0.12187 | 0 |  |  |  |  | 0 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | 0.044401 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | -0.12187 | 0 | 0 |  |  |  |  | 0.12187 | 0 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | 0.046345 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | -0.12381 | 0 | 0 |  |  |  |  | 0.12381 | 0 |  |  |  |  | 0 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | 0.046345 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | -0.12381 | 0 | 0 |  |  |  |  | 0.12381 | 0 |  |  |  |  | 0 | 0
49851 | DOW17000 | 37 | Houston | YES | 0.048801 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49858 | DOW38100 | 31 | Houston | YES | 0.048801 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49859 | DOW38200 | 33 | Houston | YES | 0.048801 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49860 | DOW38300 | 32 | Houston | YES | 0.048801 | 63 | 0 | 101 |  | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49862 | DOW39100 | 36 | Houston | YES | 0.048801 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49863 | DOW39200 | 35 | Houston | YES | 0.048801 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49865 | DOW41000 | 41 | Houston | YES | 0.048801 | 31 | 0 | 50 |  | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49866 | DOW42000 | 42 | Houston | YES | 0.048801 | 11 | 0 | 18 |  | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49869 | DOW49000 | 45 | Houston | YES | 0.048801 | 59 | 0 | 94 |  | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49870 | DOW61000 | 61 | Houston | YES | 0.048801 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49871 | DOW62000 | 62 | Houston | YES | 0.048801 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49872 | DOW63000 | 63 | Houston | YES | 0.048801 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49873 | DOW64000 | 64 | Houston | YES | 0.048801 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49876 | DOW65000 | 65 | Houston | YES | 0.048801 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49877 | DOW66000 | 66 | Houston | YES | 0.048801 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49878 | DOW67000 | 67 | Houston | YES | 0.048801 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49882 | DOW81000 | 81 | Houston | YES | 0.048801 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49884 | DOW82000 | 82 | Houston | YES | 0.048801 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49885 | DOW83000 | 83 | Houston | YES | 0.048801 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
49886 | DOW84000 | 84 | Houston | YES | 0.048801 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | -0.12627 | 0 | 0 |  |  |  |  | 0.12627 | 0 |  |  |  |  | 0 | 0
8032 | AMISTADHYD1 | 1 | South | YES | 0.049694 | 33 | 13 | 33 | 0 | 1.03 | Hydro | -1 | -0.12716 | 0 | 0 |  |  | 0 | 0 | 0.12716 | 0 |  |  |  |  | 0 | 0
8033 | AMISTADHYD2 | 2 | South | YES | 0.049694 | 25 | 13 | 25 | 0 | 1.03 | Hydro | -1 | -0.12716 | 0 | 0 |  |  | 0 | 0 | 0.12716 | 0 |  |  |  |  | 0 | 0
88253 | HAMILTON | F | South | YES | 0.049694 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | -0.12716 | 0 | 0 |  |  | 0 | 0 | 0.12716 | 0 |  |  |  |  | 0 | 0
32892 | BRYN_DNSBY14 | 1 | North | YES | -0.015824 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | -0.12877 | 105 | 105 | -1.6615 | 105 |  |  | -0.12877 | -13.5211 |  |  |  |  | -13.5211 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | -0.015824 | 0 | 2 | 48 |  | 1.015 | GST | 1 | -0.12877 | 48 | 48 | -0.75955 | 48 |  |  | -0.12877 | -6.1811 |  |  |  |  | -6.1811 | 0
32884 | BRYN_DNSBY13 | 1 | North | YES | -0.015824 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | -0.12877 | 46 | 46 | -0.7279 | 46 |  |  | -0.12877 | -5.9235 |  |  |  |  | -5.9235 | 0
48674 | FTR_CN4_5095 | 4 | North | YES | -0.016497 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | -0.12945 | 380 | 380 | -6.2689 | 380 |  |  | -0.12945 | -49.1893 |  |  |  |  | -49.1893 | 0
48672 | FTR_GT2_5110 | 2 | North | YES | -0.016497 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | -0.12945 | 159 | 159 | -2.623 | 159 |  |  | -0.12945 | -20.5818 |  |  |  |  | -20.5818 | 0
48673 | FTR_GT3_5085 | 3 | North | YES | -0.016497 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | -0.12945 | 158 | 158 | -2.6065 | 158 |  |  | -0.12945 | -20.4524 |  |  |  |  | -20.4524 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | -0.016497 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | -0.12945 | 154.2 | 154.2 | -2.5438 | 154.2 |  |  | -0.12945 | -19.9605 |  |  |  |  | -19.9605 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | -0.018261 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | -0.13121 | 17 | 17 | -0.31044 | 17 |  |  | -0.13121 | -2.2306 |  |  |  |  | -2.2306 | 0
32886 | BRYN_ATKINS3 | MB | North | YES | -0.018261 | 0 | 5 | 12 |  | 1 | GST | 1 | -0.13121 | 0 | 0 | 0 | 0 |  |  | -0.13121 | 0 |  |  |  |  | 0 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | -0.018261 | 0 | 12 | 51 |  | 1.028 | GST | 1 | -0.13121 | 0 | 0 | 0 | 0 |  |  | -0.13121 | 0 |  |  |  |  | 0 | 0
32890 | BRYN_ATKINS4 | MB | North | YES | -0.018261 | 0 | 5 | 22 |  | 1.031 | GST | 1 | -0.13121 | 0 | 0 | 0 | 0 |  |  | -0.13121 | 0 |  |  |  |  | 0 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | -0.018261 | 0 | 5 | 25 |  | 1.031 | GST | 1 | -0.13121 | 0 | 0 | 0 | 0 |  |  | -0.13121 | 0 |  |  |  |  | 0 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | -0.018452 | 32 | 0 | 32 |  | 1.02 | GST | 1 | -0.1314 | 32 | 32 | -0.59046 | 32 |  |  | -0.1314 | -4.2048 |  |  |  |  | -4.2048 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | 0.058202 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | -0.13567 | 0 | 0 |  |  |  |  | 0.13567 | 0 |  |  |  |  | 0 | 0
990 | GIBN_CREK_G1 | 1 | North | YES | -0.023129 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | -0.13608 | 0 | 463 | -10.7087 | 463 |  |  | -0.13608 | -63.0039 |  |  |  |  | -63.0039 | 0
48731 | CBE_GT1 | 1 | Houston | YES | 0.061389 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | -0.13886 | 76 | 76 |  |  |  |  | 0.13886 | 10.5532 |  |  |  |  | 0 | 10.5532
48732 | CBE_GT2 | 1 | Houston | YES | 0.061389 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | -0.13886 | 76 | 76 |  |  |  |  | 0.13886 | 10.5532 |  |  |  |  | 0 | 10.5532
48734 | CBE_GT3 | 1 | Houston | YES | 0.061389 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | -0.13886 | 76 | 76 |  |  |  |  | 0.13886 | 10.5532 |  |  |  |  | 0 | 10.5532
48735 | CBE_GT4 | 1 | Houston | YES | 0.061389 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | -0.13886 | 76 | 76 |  |  |  |  | 0.13886 | 10.5532 |  |  |  |  | 0 | 10.5532
48733 | CBE_ST12 | 1 | Houston | YES | 0.061389 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | -0.13886 | 105 | 105 |  |  |  |  | 0.13886 | 14.58 |  |  |  |  | 0 | 14.58
48736 | CBE_ST34 | 1 | Houston | YES | 0.061389 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | -0.13886 | 105 | 105 |  |  |  |  | 0.13886 | 14.58 |  |  |  |  | 0 | 14.58
5911 | STP_GN1___1 | 1 | Houston | YES | 0.062009 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | -0.13948 | 0 | 0 |  |  |  |  | 0.13948 | 0 |  |  |  |  | 0 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | 0.062009 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | -0.13948 | 0 | 0 |  |  |  |  | 0.13948 | 0 |  |  |  |  | 0 | 0
8262 | ELPS | 1 | South | YES | 0.064073 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | -0.14154 | 0 | 0 |  |  | 0 | 0 | 0.14154 | 0 |  |  |  |  | 0 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | 0.071689 | 0 | 0 | 18 |  | 1 | Hydro | -1 | -0.14916 | 0 | 0 |  |  | 0 | 0 | 0.14916 | 0 |  |  |  |  | 0 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | 0.071689 | 0 | 0 | 18 |  | 1 | Hydro | -1 | -0.14916 | 0 | 0 |  |  | 0 | 0 | 0.14916 | 0 |  |  |  |  | 0 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | 0.071689 | 0 | 0 | 15 |  | 1 | Hydro | -1 | -0.14916 | 0 | 0 |  |  | 0 | 0 | 0.14916 | 0 |  |  |  |  | 0 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | 0.07245 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | -0.14992 | 0 | 0 |  |  | 0 | 0 | 0.14992 | 0 |  |  |  |  | 0 | 0
39960 | TNTNPONE_18 | 1 | North | YES | -0.045587 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | -0.15854 | 0 | 152.3 | -6.9429 | 152.3 |  |  | -0.15854 | -24.145 |  |  |  |  | -24.145 | 0
39970 | TNTNPONE_28 | 1 | North | YES | -0.045587 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | -0.15854 | 0 | 153 | -6.9748 | 153 |  |  | -0.15854 | -24.2559 |  |  |  |  | -24.2559 | 0
60202 | FRNDDRCS | F | West | YES | -0.04836 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | -0.16131 | 0 | 0 |  |  |  |  | -0.16131 | 0 |  |  |  |  | 0 | 0
8134 | FOR #1 | 1 | South | YES | 0.086112 | 54.1 | 45 | 79 | 0 | 1 | Cogen | -1 | -0.16358 | 0 | 0 |  |  | 0 | 0 | 0.16358 | 0 |  |  |  |  | 0 | 0
8138 | FOR #2 | 2 | South | YES | 0.086112 | 63.1 | 45 | 81 | 0 | 1 | Cogen | -1 | -0.16358 | 0 | 0 |  |  | 0 | 0 | 0.16358 | 0 |  |  |  |  | 0 | 0
8153 | FOR #3 | 3 | South | YES | 0.086112 | 63.1 | 45 | 79.9 | 0 | 1 | Cogen | -1 | -0.16358 | 0 | 0 |  |  | 0 | 0 | 0.16358 | 0 |  |  |  |  | 0 | 0
8154 | FOR #4 | 4 | South | YES | 0.086112 | 63.1 | 60 | 80 | 0 | 1 | Cogen | -1 | -0.16358 | 0 | 0 |  |  | 0 | 0 | 0.16358 | 0 |  |  |  |  | 0 | 0
8155 | FOR #5 | 5 | South | YES | 0.086112 | 63.1 | 60 | 78.4 | 0 | 1 | Cogen | -1 | -0.16358 | 0 | 0 |  |  | 0 | 0 | 0.16358 | 0 |  |  |  |  | 0 | 0
8156 | FOR #6 | 6 | South | YES | 0.086112 | 24.9 | 5 | 25 | 0 | 1 | Cogen | -1 | -0.16358 | 0 | 0 |  |  | 0 | 0 | 0.16358 | 0 |  |  |  |  | 0 | 0
8157 | FOR #7 | 7 | South | YES | 0.086112 | 28.8 | 5 | 46 | 0 | 1 | Cogen | -1 | -0.16358 | 0 | 0 |  |  | 0 | 0 | 0.16358 | 0 |  |  |  |  | 0 | 0
80051 | FOR #8 | 8 | South | YES | 0.086112 | 28 | 28 | 28 |  | 1 | Cogen | -1 | -0.16358 | 0 | 0 |  |  | 0 | 0 | 0.16358 | 0 |  |  |  |  | 0 | 0
80052 | FOR #9 | 9 | South | YES | 0.086112 | 29.7 | 5 | 43.6 | 0 | 1 | Cogen | -1 | -0.16358 | 0 | 0 |  |  | 0 | 0 | 0.16358 | 0 |  |  |  |  | 0 | 0
80053 | FOR #10 | 10 | South | YES | 0.086112 | 68.4 | 45 | 75 | 0 | 1 | Cogen | -1 | -0.16358 | 0 | 0 |  |  | 0 | 0 | 0.16358 | 0 |  |  |  |  | 0 | 0
80226 | ALCOA G | 1 | South | YES | 0.086785 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | -0.16425 | 0 | 0 |  |  | 0 | 0 | 0.16425 | 0 |  |  |  |  | 0 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | 0.086882 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | -0.16435 | 423.3 | 423.3 |  |  | 36.7772 | 423.3 | 0.16435 | 69.5695 |  |  |  |  | 0 | 69.5695
7035 | L_WIRTZ_1G1Y | 1 | South | YES | 0.087159 | 0 | 0 | 29 |  | 1 | Hydro | -1 | -0.16463 | 0 | 0 |  |  | 0 | 0 | 0.16463 | 0 |  |  |  |  | 0 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | 0.087159 | 0 | 0 | 29.7 |  | 1 | Hydro | -1 | -0.16463 | 0 | 0 |  |  | 0 | 0 | 0.16463 | 0 |  |  |  |  | 0 | 0
8147 | UCAR #2 | 10 | South | YES | 0.088972 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | -0.16644 | 0 | 0 |  |  | 0 | 0 | 0.16644 | 0 |  |  |  |  | 0 | 0
8148 | UCAR #1 | 2 | South | YES | 0.088972 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | -0.16644 | 0 | 0 |  |  | 0 | 0 | 0.16644 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 9 | South | YES | 0.088972 | 15 | 0 | 15 | 0 | 1.003 | DCTie | -1 | -0.16644 | 0 | 0 |  |  | 0 | 0 | 0.16644 | 0 |  |  |  |  | 0 | 0
80137 | CSDR89 | 8 | South | YES | 0.088972 | 33.9 | 0 | 39 | 0 | 1.003 | DCTie | -1 | -0.16644 | 0 | 0 |  |  | 0 | 0 | 0.16644 | 0 |  |  |  |  | 0 | 0
80138 | CSDR7 | 7 | South | YES | 0.088972 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | -0.16644 | 0 | 0 |  |  | 0 | 0 | 0.16644 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 6 | South | YES | 0.088972 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | -0.16644 | 0 | 0 |  |  | 0 | 0 | 0.16644 | 0 |  |  |  |  | 0 | 0
80139 | CSDR56 | 5 | South | YES | 0.088972 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | -0.16644 | 0 | 0 |  |  | 0 | 0 | 0.16644 | 0 |  |  |  |  | 0 | 0
80140 | CSDR11 | 11 | South | YES | 0.088972 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | -0.16644 | 0 | 0 |  |  | 0 | 0 | 0.16644 | 0 |  |  |  |  | 0 | 0
80227 | AIRCO G | 1 | South | YES | 0.089286 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | -0.16675 | 0 | 0 |  |  | 0 | 0 | 0.16675 | 0 |  |  |  |  | 0 | 0
80224 | VISTRONG1 | 1 | South | YES | 0.089885 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | -0.16735 | 0 | 0 |  |  | 0 | 0 | 0.16735 | 0 |  |  |  |  | 0 | 0
80225 | VISTRONG2 | 2 | South | YES | 0.089885 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | -0.16735 | 0 | 0 |  |  | 0 | 0 | 0.16735 | 0 |  |  |  |  | 0 | 0
48721 | LEG_1___1 | 1 | North | YES | -0.055103 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | -0.16805 | 0 | 827 | -45.5702 | 827 |  |  | -0.16805 | -138.9786 |  |  |  |  | -138.9786 | 0
48722 | LEG_2___2 | 2 | North | YES | -0.055103 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | -0.16805 | 0 | 819 | -45.1294 | 819 |  |  | -0.16805 | -137.6342 |  |  |  |  | -137.6342 | 0
5505 | RAYBURNGEN1 | 1 | South | YES | 0.090712 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | -0.16818 | 11 | 11 |  |  | 0.99783 | 11 | 0.16818 | 1.85 |  |  |  |  | 0 | 1.85
5506 | RAYBURNGEN2 | 1 | South | YES | 0.090712 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | -0.16818 | 11 | 11 |  |  | 0.99783 | 11 | 0.16818 | 1.85 |  |  |  |  | 0 | 1.85
5503 | RAYBURNGEN3 | 1 | South | YES | 0.090712 | 17.6 | 6 | 22 | 0 | 1.0224 | GST | -1 | -0.16818 | 22 | 22 |  |  | 1.9957 | 22 | 0.16818 | 3.7 |  |  |  |  | 0 | 3.7
80012 | LAR | F | South | YES | 0.091061 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | -0.16853 | 0 | 0 |  |  | 0 | 0 | 0.16853 | 0 |  |  |  |  | 0 | 0
80265 | LARECU40A | 4 | South | YES | 0.091061 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | -0.16853 | 100 | 100 |  |  | 9.1061 | 100 | 0.16853 | 16.8529 |  |  |  |  | 0 | 16.8529
80266 | LARECU50A | 5 | South | YES | 0.091061 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | -0.16853 | 100 | 100 |  |  | 9.1061 | 100 | 0.16853 | 16.8529 |  |  |  |  | 0 | 16.8529
5509 | RAYBURNCC10 | 1 | South | YES | 0.091471 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | -0.16894 | 37.3 | 37.3 |  |  | 3.4119 | 37.3 | 0.16894 | 6.3014 |  |  |  |  | 0 | 6.3014
5511 | RAYBURNCC7 | 1 | South | YES | 0.091471 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | -0.16894 | 47.5 | 47.5 |  |  | 4.3449 | 47.5 | 0.16894 | 8.0246 |  |  |  |  | 0 | 8.0246
5508 | RAYBURNCC9 | 1 | South | YES | 0.091471 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | -0.16894 | 47.7 | 47.7 |  |  | 4.3632 | 47.7 | 0.16894 | 8.0584 |  |  |  |  | 0 | 8.0584
5512 | RAYBURNCC8 | 1 | South | YES | 0.091471 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | -0.16894 | 49.3 | 49.3 |  |  | 4.5095 | 49.3 | 0.16894 | 8.3287 |  |  |  |  | 0 | 8.3287
8066 | DUP1V#1 | 1 | South | YES | 0.091512 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | -0.16898 | 0 | 0 |  |  | 0 | 0 | 0.16898 | 0 |  |  |  |  | 0 | 0
8926 | LGE_GT10A | 1 | South | YES | 0.09179 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | -0.16926 | 0 | 0 |  |  | 0 | 0 | 0.16926 | 0 |  |  |  |  | 0 | 0
8927 | LGE_GT20A | 2 | South | YES | 0.09179 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | -0.16926 | 0 | 0 |  |  | 0 | 0 | 0.16926 | 0 |  |  |  |  | 0 | 0
8928 | LGE_STG0A | 3 | South | YES | 0.09179 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | -0.16926 | 0 | 0 |  |  | 0 | 0 | 0.16926 | 0 |  |  |  |  | 0 | 0
8930 | ICPGN10A | 1 | South | YES | 0.09179 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | -0.16926 | 0 | 0 |  |  | 0 | 0 | 0.16926 | 0 |  |  |  |  | 0 | 0
8931 | ICPGN20A | 2 | South | YES | 0.09179 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | -0.16926 | 0 | 0 |  |  | 0 | 0 | 0.16926 | 0 |  |  |  |  | 0 | 0
8932 | ICPGN30A | 3 | South | YES | 0.09179 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | -0.16926 | 0 | 0 |  |  | 0 | 0 | 0.16926 | 0 |  |  |  |  | 0 | 0
80223 | REYSHR G | 1 | South | YES | 0.09179 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | -0.16926 | 0 | 0 |  |  | 0 | 0 | 0.16926 | 0 |  |  |  |  | 0 | 0
88299 | ZAPATA | F | South | YES | 0.091925 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | -0.16939 | 0 | 0 |  |  | 0 | 0 | 0.16939 | 0 |  |  |  |  | 0 | 0
8173 | VICEC51A | 5 | South | YES | 0.092439 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | -0.16991 | 144 | 144 |  |  | 13.3112 | 144 | 0.16991 | 24.4667 |  |  |  |  | 0 | 24.4667
8174 | VICEC61A | 6 | South | YES | 0.092439 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | -0.16991 | 188 | 188 |  |  | 17.3785 | 188 | 0.16991 | 31.9426 |  |  |  |  | 0 | 31.9426
5728 | FALCONHYDRO2 | 2 | South | YES | 0.092509 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | -0.16998 | 0 | 0 |  |  | 0 | 0 | 0.16998 | 0 |  |  |  |  | 0 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | 0.092509 | 11 | 0 | 11 | 0 | 1.0234 | Hydro | -1 | -0.16998 | 0 | 0 |  |  | 0 | 0 | 0.16998 | 0 |  |  |  |  | 0 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | 0.092509 | 12 | 0 | 12 | 0 | 1.0234 | Hydro | -1 | -0.16998 | 0 | 0 |  |  | 0 | 0 | 0.16998 | 0 |  |  |  |  | 0 | 0
88508 | FALFURRI | F | South | YES | 0.092514 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | -0.16998 | 0 | 0 |  |  | 0 | 0 | 0.16998 | 0 |  |  |  |  | 0 | 0
8442 | NBEC7 | MB | South | YES | 0.09258 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | -0.17005 | 0 | 0 |  |  | 0 | 0 | 0.17005 | 0 |  |  |  |  | 0 | 0
8442 | NBEC7 | 7 | South | YES | 0.09258 | 0 | 81 | 367 |  | 1.0298 | GST | -1 | -0.17005 | 367 | 367 |  |  | 33.9769 | 367 | 0.17005 | 62.4078 |  |  |  |  | 0 | 62.4078
8560 | CNOPGT1 | 1 | South | YES | 0.092589 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | -0.17006 | 0 | 0 |  |  | 0 | 0 | 0.17006 | 0 |  |  |  |  | 0 | 0
8561 | CNOPGT2 | 2 | South | YES | 0.092589 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | -0.17006 | 0 | 0 |  |  | 0 | 0 | 0.17006 | 0 |  |  |  |  | 0 | 0
8562 | CNOPST1 | 3 | South | YES | 0.092589 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | -0.17006 | 0 | 0 |  |  | 0 | 0 | 0.17006 | 0 |  |  |  |  | 0 | 0
8456 | COSW#1 | 1 | South | YES | 0.092634 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | -0.1701 | 0 | 0 |  |  | 0 | 0 | 0.1701 | 0 |  |  |  |  | 0 | 0
8457 | COSW#2 | 2 | South | YES | 0.092634 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | -0.1701 | 0 | 0 |  |  | 0 | 0 | 0.1701 | 0 |  |  |  |  | 0 | 0
8459 | B_DAVIS0B | MB | South | YES | 0.092744 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | -0.17021 | 0 | 0 |  |  | 0 | 0 | 0.17021 | 0 |  |  |  |  | 0 | 0
8460 | B_DAVIS0A | MB | South | YES | 0.092744 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | -0.17021 | 0 | 0 |  |  | 0 | 0 | 0.17021 | 0 |  |  |  |  | 0 | 0
80263 | B_DAVIS31A | 3 | South | YES | 0.092744 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | -0.17021 | 180 | 180 |  |  | 16.6939 | 180 | 0.17021 | 30.6382 |  |  |  |  | 0 | 30.6382
80264 | B_DAVIS41A | 4 | South | YES | 0.092744 | 0 | 0 | 180 |  | 1.0366 | CC | -1 | -0.17021 | 180 | 180 |  |  | 16.6939 | 180 | 0.17021 | 30.6382 |  |  |  |  | 0 | 30.6382
8506 | VAL #1 | 1 | South | YES | 0.092781 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | -0.17025 | 0 | 0 |  |  | 0 | 0 | 0.17025 | 0 |  |  |  |  | 0 | 0
8507 | VAL #2 | 2 | South | YES | 0.092781 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | -0.17025 | 0 | 0 |  |  | 0 | 0 | 0.17025 | 0 |  |  |  |  | 0 | 0
8461 | KOCH_UP0A | 1 | South | YES | 0.092861 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | -0.17033 | 0 | 0 |  |  | 0 | 0 | 0.17033 | 0 |  |  |  |  | 0 | 0
8511 | OXY_CC0A | 1 | South | YES | 0.092868 | 30.3 | 0 | 38 | 0 | 1.027 | Cogen | -1 | -0.17034 | 0 | 0 |  |  | 0 | 0 | 0.17034 | 0 |  |  |  |  | 0 | 0
8933 | FGNTS001 | 1 | South | YES | 0.093119 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | -0.17059 | 146.5 | 146.5 |  |  | 13.6419 | 146.5 | 0.17059 | 24.9911 |  |  |  |  | 0 | 24.9911
8934 | FGNTS101 | 2 | South | YES | 0.093119 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | -0.17059 | 147.9 | 147.9 |  |  | 13.7723 | 147.9 | 0.17059 | 25.2299 |  |  |  |  | 0 | 25.2299
8935 | FGNTS201 | 3 | South | YES | 0.093119 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | -0.17059 | 173 | 173 |  |  | 16.1096 | 173 | 0.17059 | 29.5116 |  |  |  |  | 0 | 29.5116
8517 | CELANEBI0A | 1 | South | YES | 0.093183 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | -0.17065 | 0 | 0 |  |  | 0 | 0 | 0.17065 | 0 |  |  |  |  | 0 | 0
8982 | HECN2 | 2 | South | YES | 0.093223 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | -0.17069 | 144.1 | 144.1 |  |  | 13.4334 | 144.1 | 0.17069 | 24.5966 |  |  |  |  | 0 | 24.5966
8981 | HECN1 | 1 | South | YES | 0.093223 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | -0.17069 | 144.8 | 144.8 |  |  | 13.4987 | 144.8 | 0.17069 | 24.7161 |  |  |  |  | 0 | 24.7161
8983 | HECN3 | 3 | South | YES | 0.093223 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | -0.17069 | 171.9 | 171.9 |  |  | 16.025 | 171.9 | 0.17069 | 29.3418 |  |  |  |  | 0 | 29.3418
8936 | MVGN#1 | 1 | South | YES | 0.093223 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | -0.17069 | 216.6 | 216.6 |  |  | 20.1921 | 216.6 | 0.17069 | 36.9718 |  |  |  |  | 0 | 36.9718
8937 | MVGN#2 | 2 | South | YES | 0.093223 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | -0.17069 | 216.7 | 216.7 |  |  | 20.2014 | 216.7 | 0.17069 | 36.9888 |  |  |  |  | 0 | 36.9888
8938 | MVGN#3 | 3 | South | YES | 0.093223 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | -0.17069 | 250.9 | 250.9 |  |  | 23.3897 | 250.9 | 0.17069 | 42.8265 |  |  |  |  | 0 | 42.8265
80003 | MILHWYS | F | South | YES | 0.093259 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | -0.17073 | 0 | 0 |  |  | 0 | 0 | 0.17073 | 0 |  |  |  |  | 0 | 0
5933 | SI_RAY6 | 6 | South | YES | 0.093259 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | -0.17073 | 19.3 | 19.3 |  |  | 1.7999 | 19.3 | 0.17073 | 3.295 |  |  |  |  | 0 | 3.295
5932 | SI_RAY9 | 9 | South | YES | 0.093259 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | -0.17073 | 38 | 38 |  |  | 3.5438 | 38 | 0.17073 | 6.4876 |  |  |  |  | 0 | 6.4876
5935 | SI_RAY10 | 10 | South | YES | 0.093259 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | -0.17073 | 47 | 47 |  |  | 4.3832 | 47 | 0.17073 | 8.0242 |  |  |  |  | 0 | 8.0242
80080 | GWINDT11A | 4 | South | YES | 0.093283 | 3.8 | 0 | 19 | 0 | 1.025 | Wind | -1 | -0.17075 | 0 | 19 |  |  | 0 | 0 | 0.17075 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 4 | South | YES | 0.093283 | 4.4 | 0 | 22 | 0 | 1.025 | Wind | -1 | -0.17075 | 0 | 22 |  |  | 0 | 0 | 0.17075 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 2 | South | YES | 0.093283 | 7.2 | 0 | 36 | 0 | 1.025 | Wind | -1 | -0.17075 | 0 | 36 |  |  | 0 | 0 | 0.17075 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 3 | South | YES | 0.093283 | 0 | 0 | 38 | 0 | 1.025 | Wind | -1 | -0.17075 | 0 | 38 |  |  | 0 | 0 | 0.17075 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 2 | South | YES | 0.093283 | 0 | 0 | 41 | 0 | 1.025 | Wind | -1 | -0.17075 | 0 | 41 |  |  | 0 | 0 | 0.17075 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 3 | South | YES | 0.093283 | 8.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | -0.17075 | 0 | 43 |  |  | 0 | 0 | 0.17075 | 0 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 2 | South | YES | 0.093283 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | -0.17075 | 0 | 50 |  |  | 0 | 0 | 0.17075 | 0 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 2 | South | YES | 0.093283 | 10 | 0 | 50 | 0 | 1.025 | Wind | -1 | -0.17075 | 0 | 50 |  |  | 0 | 0 | 0.17075 | 0 |  |  |  |  | 0 | 0
80181 | PNSCALT21A | 1 | South | YES | 0.093283 | 16.5 | 0 | 55 | 0 | 1.025 | Wind | -1 | -0.17075 | 0 | 55 |  |  | 0 | 0 | 0.17075 | 0 |  |  |  |  | 0 | 0
80080 | GWINDT11A | 1 | South | YES | 0.093283 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | -0.17075 | 0 | 94 |  |  | 0 | 0 | 0.17075 | 0 |  |  |  |  | 0 | 0
80081 | GWINDT21A | 1 | South | YES | 0.093283 | 28.2 | 0 | 94 | 0 | 1.025 | Wind | -1 | -0.17075 | 0 | 94 |  |  | 0 | 0 | 0.17075 | 0 |  |  |  |  | 0 | 0
80180 | PNSCALT11A | 1 | South | YES | 0.093283 | 43.8 | 0 | 148 | 0 | 1.025 | Wind | -1 | -0.17075 | 0 | 148 |  |  | 0 | 0 | 0.17075 | 0 |  |  |  |  | 0 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | 0.095069 | 0 | 0 | 18 |  | 1 | Hydro | -1 | -0.17254 | 0 | 0 |  |  | 0 | 0 | 0.17254 | 0 |  |  |  |  | 0 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | 0.095069 | 0 | 0 | 18 |  | 1 | Hydro | -1 | -0.17254 | 0 | 0 |  |  | 0 | 0 | 0.17254 | 0 |  |  |  |  | 0 | 0
60018 | DSKY1 | 1 | West | YES | -0.060196 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | -0.17314 | 0 | 84 |  |  |  |  | -0.17314 | -14.5441 |  |  |  |  | -14.5441 | 0
60000 | DSKY2 | 1 | West | YES | -0.060397 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | -0.17335 | 0 | 76.5 |  |  |  |  | -0.17335 | -13.2609 |  |  |  |  | -13.2609 | 0
60017 | ORNNWP1 | 1 | West | YES | -0.060961 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | -0.17391 | 0 | 80 |  |  |  |  | -0.17391 | -13.9128 |  |  |  |  | -13.9128 | 0
8161 | COLETO0A | 1 | South | YES | 0.096606 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | -0.17407 | 0 | 633 |  |  | 0 | 0 | 0.17407 | 0 |  |  |  |  | 0 | 0
58909 | PEARSALLSCG1 | 3 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58909 | PEARSALLSCG1 | 4 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58909 | PEARSALLSCG1 | 6 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58909 | PEARSALLSCG1 | 5 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58909 | PEARSALLSCG1 | 1 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58909 | PEARSALLSCG1 | 2 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58919 | PEARSALLSCG2 | 5 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58919 | PEARSALLSCG2 | 6 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58919 | PEARSALLSCG2 | 1 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58919 | PEARSALLSCG2 | 2 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58919 | PEARSALLSCG2 | 4 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58919 | PEARSALLSCG2 | 3 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58929 | PEARSALLSCG3 | 4 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58929 | PEARSALLSCG3 | 6 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58929 | PEARSALLSCG3 | 2 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58929 | PEARSALLSCG3 | 5 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58929 | PEARSALLSCG3 | 1 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58929 | PEARSALLSCG3 | 3 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58949 | PEARSALLSCG4 | 3 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58949 | PEARSALLSCG4 | 2 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58949 | PEARSALLSCG4 | 1 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58949 | PEARSALLSCG4 | 4 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58949 | PEARSALLSCG4 | 6 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
58949 | PEARSALLSCG4 | 5 | South | YES | 0.096761 | 0 | 0 | 8.4 |  | 1.027 | Diesel | -1 | -0.17423 | 8.4 | 8.4 |  |  | 0.81279 | 8.4 | 0.17423 | 1.4635 |  |  |  |  | 0 | 1.4635
88198 | BEEVILLE | F | South | YES | 0.097427 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | -0.1749 | 0 | 0 |  |  | 0 | 0 | 0.1749 | 0 |  |  |  |  | 0 | 0
38437 | TNSRBNMESA9 | 1 | West | YES | -0.063226 | 37.5 | 0 | 150 | 0 | 1.02 | Wind | 1 | -0.17617 | 0 | 150 |  |  |  |  | -0.17617 | -26.4262 |  |  |  |  | -26.4262 | 0
38332 | TNWDWRDU2_8 | 1 | West | YES | -0.063291 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | -0.17624 | 0 | 80 |  |  |  |  | -0.17624 | -14.0992 |  |  |  |  | -14.0992 | 0
60016 | WOODWRD11A | 1 | West | YES | -0.063306 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | -0.17625 | 0 | 80 |  |  |  |  | -0.17625 | -14.1004 |  |  |  |  | -14.1004 | 0
6016 | SWMESA | 1 | West | YES | -0.063386 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | -0.17633 | 0 | 75 |  |  |  |  | -0.17633 | -13.2251 |  |  |  |  | -13.2251 | 0
60003 | KING_NE1A | 1 | West | YES | -0.063386 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | -0.17633 | 0 | 80 |  |  |  |  | -0.17633 | -14.1068 |  |  |  |  | -14.1068 | 0
60005 | KING_SE1A | 1 | West | YES | -0.063386 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | -0.17633 | 0 | 40 |  |  |  |  | -0.17633 | -7.0534 |  |  |  |  | -7.0534 | 0
5892 | PEARSALLGEN3 | 1 | South | YES | 0.09868 | 19.1 | 6 | 23.9 | 0 | 1.0226 | GST | -1 | -0.17615 | 23.9 | 23.9 |  |  | 2.3585 | 23.9 | 0.17615 | 4.2099 |  |  |  |  | 0 | 4.2099
5890 | PEARSALLGEN1 | 1 | South | YES | 0.09868 | 19.2 | 6 | 24 | 0 | 1.0226 | GST | -1 | -0.17615 | 24 | 24 |  |  | 2.3683 | 24 | 0.17615 | 4.2276 |  |  |  |  | 0 | 4.2276
5891 | PEARSALLGEN2 | 1 | South | YES | 0.09868 | 19.4 | 6 | 24.3 | 0 | 1.0226 | GST | -1 | -0.17615 | 24.3 | 24.3 |  |  | 2.3979 | 24.3 | 0.17615 | 4.2804 |  |  |  |  | 0 | 4.2804
60201 | RIO DRCS | F | West | YES | -0.063507 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | -0.17646 | 0 | 0 |  |  |  |  | -0.17646 | 0 |  |  |  |  | 0 | 0
60007 | KING_SW1A | 1 | West | YES | -0.063813 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | -0.17676 | 0 | 80 |  |  |  |  | -0.17676 | -14.1409 |  |  |  |  | -14.1409 | 0
60019 | KING_NW1A | 1 | West | YES | -0.063813 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | -0.17676 | 0 | 80 |  |  |  |  | -0.17676 | -14.1409 |  |  |  |  | -14.1409 | 0
3381 | BBRN_1G | 1 | North | YES | -0.068671 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | -0.18162 | 0 | 618 | -42.4387 | 618 |  |  | -0.18162 | -112.2408 |  |  |  |  | -112.2408 | 0
3382 | BBRN_2G | 2 | North | YES | -0.068671 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | -0.18162 | 0 | 589 | -40.4472 | 589 |  |  | -0.18162 | -106.9739 |  |  |  |  | -106.9739 | 0
13133 | CALFREST_3G | 3 | North | YES | -0.069651 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | -0.1826 | 177.4 | 177.4 | -12.3561 | 177.4 |  |  | -0.1826 | -32.3931 |  |  |  |  | -32.3931 | 0
13132 | CALFREST_2G | 2 | North | YES | -0.069651 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | -0.1826 | 151 | 151 | -10.5173 | 151 |  |  | -0.1826 | -27.5725 |  |  |  |  | -27.5725 | 0
13131 | CALFREST_1G | 1 | North | YES | -0.069651 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | -0.1826 | 150.7 | 150.7 | -10.4964 | 150.7 |  |  | -0.1826 | -27.5177 |  |  |  |  | -27.5177 | 0
13136 | CALFREST_6G | 6 | North | YES | -0.069854 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | -0.1828 | 177.5 | 177.5 | -12.3991 | 177.5 |  |  | -0.1828 | -32.4474 |  |  |  |  | -32.4474 | 0
13135 | CALFREST_5G | 5 | North | YES | -0.069854 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | -0.1828 | 152.3 | 152.3 | -10.6388 | 152.3 |  |  | -0.1828 | -27.8408 |  |  |  |  | -27.8408 | 0
13134 | CALFREST_4G | 4 | North | YES | -0.069854 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | -0.1828 | 151.5 | 151.5 | -10.5829 | 151.5 |  |  | -0.1828 | -27.6946 |  |  |  |  | -27.6946 | 0
1349 | WESTXWIN_1G | 1 | West | YES | -0.070161 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | -0.18311 | 0 | 6.6 |  |  |  |  | -0.18311 | -1.2085 |  |  |  |  | -1.2085 | 0
1350 | NWPWRG1_1G | 1 | West | YES | -0.070161 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | -0.18311 | 0 | 34.3 |  |  |  |  | -0.18311 | -6.2807 |  |  |  |  | -6.2807 | 0
1008 | PB6GEN_7G | 6 | West | YES | -0.070386 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | -0.18333 | 515 | 515 |  |  |  |  | -0.18333 | -94.4173 |  |  |  |  | -94.4173 | 0
1007 | PB5GEN_6G | 5 | West | YES | -0.070386 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | -0.18333 | 114 | 114 |  |  |  |  | -0.18333 | -20.9001 |  |  |  |  | -20.9001 | 0
1005 | PBCTDGE_4G | D | West | YES | -0.070386 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | -0.18333 | 68 | 68 |  |  |  |  | -0.18333 | -12.4667 |  |  |  |  | -12.4667 | 0
1004 | PBCTCGE_3G | C | West | YES | -0.070386 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | -0.18333 | 67 | 67 |  |  |  |  | -0.18333 | -12.2834 |  |  |  |  | -12.2834 | 0
1006 | PBCTEGE_5G | E | West | YES | -0.070386 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | -0.18333 | 67 | 67 |  |  |  |  | -0.18333 | -12.2834 |  |  |  |  | -12.2834 | 0
1002 | PBCTAGE_1G | A | West | YES | -0.070386 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | -0.18333 | 66 | 66 |  |  |  |  | -0.18333 | -12.1001 |  |  |  |  | -12.1001 | 0
1003 | PBCTBGE_2G | B | West | YES | -0.070386 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | -0.18333 | 66 | 66 |  |  |  |  | -0.18333 | -12.1001 |  |  |  |  | -12.1001 | 0
7038 | L_DELAWA1_1Y | 1 | West | YES | -0.070457 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | -0.18341 | 0 | 35 |  |  |  |  | -0.18341 | -6.4192 |  |  |  |  | -6.4192 | 0
7038 | L_DELAWA1_1Y | 2 | West | YES | -0.070457 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | -0.18341 | 0 | 30 |  |  |  |  | -0.18341 | -5.5022 |  |  |  |  | -5.5022 | 0
11147 | NOTREES_1G | 1 | West | YES | -0.070592 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | -0.18354 | 0 | 149 |  |  |  |  | -0.18354 | -27.3475 |  |  |  |  | -27.3475 | 0
5903 | SANMIGUELGEN | 1 | South | YES | 0.10582 | 396.3 | 180 | 396.3 | 0 | 1.0336 | LIGCO | -1 | -0.18329 | 0 | 396.3 |  |  | 0 | 0 | 0.18329 | 0 |  |  |  |  | 0 | 0
76091 | L_DIVIDE1_1N | W1 | West | YES | -0.070857 | 22.5 | 0 | 112.5 |  | 1.02 | Wind | 1 | -0.18381 | 0 | 112.5 |  |  |  |  | -0.18381 | -20.6781 |  |  |  |  | -20.6781 | 0
76095 | L_CAPRSI1_1N | W1 | West | YES | -0.070857 | 29.9 | 0 | 149.5 | 0 | 1.02 | Wind | 1 | -0.18381 | 0 | 149.5 |  |  |  |  | -0.18381 | -27.4789 |  |  |  |  | -27.4789 | 0
76096 | L_CAPRSI1_2N | W1 | West | YES | -0.070857 | 37.2 | 0 | 186 | 0 | 1.02 | Wind | 1 | -0.18381 | 0 | 186 |  |  |  |  | -0.18381 | -34.1878 |  |  |  |  | -34.1878 | 0
76097 | L_CAPRGE1_1N | W1 | West | YES | -0.070857 | 42.9 | 0 | 214.5 | 0 | 1.02 | Wind | 1 | -0.18381 | 0 | 214.5 |  |  |  |  | -0.18381 | -39.4263 |  |  |  |  | -39.4263 | 0
76031 | L_GASCCR1_1N | W1 | West | YES | -0.071152 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | -0.1841 | 0 | 150 |  |  |  |  | -0.1841 | -27.6151 |  |  |  |  | -27.6151 | 0
1320 | BSP 1 | 1 | West | YES | -0.071338 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | -0.18429 | 0 | 0 |  |  |  |  | -0.18429 | 0 |  |  |  |  | 0 | 0
1326 | STANTONW_8 | 1 | West | YES | -0.07137 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | -0.18432 | 0 | 100.5 |  |  |  |  | -0.18432 | -18.524 |  |  |  |  | -18.524 | 0
11025 | TIEHVSG_2G | 1 | West | YES | -0.071371 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | -0.18432 | 213.2 | 213.2 |  |  |  |  | -0.18432 | -39.2969 |  |  |  |  | -39.2969 | 0
11020 | TIEHVSG_1G | 1 | West | YES | -0.071371 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | -0.18432 | 208.2 | 208.2 |  |  |  |  | -0.18432 | -38.3753 |  |  |  |  | -38.3753 | 0
11024 | TIEHVCG_4G | 1 | West | YES | -0.071371 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | -0.18432 | 147 | 147 |  |  |  |  | -0.18432 | -27.095 |  |  |  |  | -27.095 | 0
11021 | TIEHVCG_1G | 1 | West | YES | -0.071371 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | -0.18432 | 142.1 | 142.1 |  |  |  |  | -0.18432 | -26.1918 |  |  |  |  | -26.1918 | 0
11023 | TIEHVCG_3G | 1 | West | YES | -0.071371 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | -0.18432 | 137.4 | 137.4 |  |  |  |  | -0.18432 | -25.3255 |  |  |  |  | -25.3255 | 0
11022 | TIEHVCG_2G | 1 | West | YES | -0.071371 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | -0.18432 | 132.4 | 132.4 |  |  |  |  | -0.18432 | -24.4039 |  |  |  |  | -24.4039 | 0
11014 | NAV6ST | 1 | West | YES | -0.071382 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | -0.18433 | 115 | 115 |  |  |  |  | -0.18433 | -21.198 |  |  |  |  | -21.198 | 0
11011 | NAV3ST | 1 | West | YES | -0.071382 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | -0.18433 | 92.8 | 92.8 |  |  |  |  | -0.18433 | -17.1059 |  |  |  |  | -17.1059 | 0
11012 | NAV4CT | 1 | West | YES | -0.071382 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | -0.18433 | 80 | 80 |  |  |  |  | -0.18433 | -14.7464 |  |  |  |  | -14.7464 | 0
11013 | NAV5CT | 1 | West | YES | -0.071382 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | -0.18433 | 80 | 80 |  |  |  |  | -0.18433 | -14.7464 |  |  |  |  | -14.7464 | 0
11009 | NAV2CT | 1 | West | YES | -0.071382 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | -0.18433 | 71.4 | 71.4 |  |  |  |  | -0.18433 | -13.1612 |  |  |  |  | -13.1612 | 0
11001 | NAV1CT | 1 | West | YES | -0.071382 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | -0.18433 | 70.4 | 70.4 |  |  |  |  | -0.18433 | -12.9769 |  |  |  |  | -12.9769 | 0
60057 | CALLAHAN1A | 1 | West | YES | -0.071504 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | -0.18445 | 0 | 114 |  |  |  |  | -0.18445 | -21.0276 |  |  |  |  | -21.0276 | 0
1328 | OCOTILLO_1G | 1 | West | YES | -0.071505 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | -0.18445 | 0 | 58 |  |  |  |  | -0.18445 | -10.6983 |  |  |  |  | -10.6983 | 0
1333 | MCDDONAL_8 | 1 | West | YES | -0.071684 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | -0.18463 | 0 | 214.2 |  |  |  |  | -0.18463 | -39.5483 |  |  |  |  | -39.5483 | 0
1327 | WILDHRSE_1G | 1 | West | YES | -0.071918 | 0 | 0 | 120 |  | 1 | Wind | 1 | -0.18487 | 0 | 120 |  |  |  |  | -0.18487 | -22.184 |  |  |  |  | -22.184 | 0
1360 | GUNSIGHT_8 | 1 | West | YES | -0.07196 | 0 | 0 | 120 |  | 1.01 | Wind | 1 | -0.18491 | 0 | 120 |  |  |  |  | -0.18491 | -22.189 |  |  |  |  | -22.189 | 0
1045 | CALENG1G_1G | 1 | West | YES | -0.072204 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | -0.18515 | 0 | 0 |  |  |  |  | -0.18515 | 0 |  |  |  |  | 0 | 0
1046 | CALENG2G_2G | 2 | West | YES | -0.072204 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | -0.18515 | 0 | 0 |  |  |  |  | -0.18515 | 0 |  |  |  |  | 0 | 0
1047 | CALENG3G_3G | 3 | West | YES | -0.072204 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | -0.18515 | 0 | 0 |  |  |  |  | -0.18515 | 0 |  |  |  |  | 0 | 0
11320 | COYOTE_1G | 1 | West | YES | -0.072223 | 22.5 | 0 | 225 |  | 1 | Wind | 1 | -0.18517 | 0 | 225 |  |  |  |  | -0.18517 | -41.6636 |  |  |  |  | -41.6636 | 0
11309 | BULLCREK_2G | 1 | West | YES | -0.072289 | 20.9 | 0 | 180 |  | 1 | Wind | 1 | -0.18524 | 0 | 180 |  |  |  |  | -0.18524 | -33.3427 |  |  |  |  | -33.3427 | 0
11310 | BULLCREK_1G | 1 | West | YES | -0.072289 | 15.1 | 0 | 180 |  | 1 | Wind | 1 | -0.18524 | 0 | 180 |  |  |  |  | -0.18524 | -33.3427 |  |  |  |  | -33.3427 | 0
1058 | LONGSHORE_5 | 1 | West | YES | -0.072395 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | -0.18534 | 0 | 150 |  |  |  |  | -0.18534 | -27.8015 |  |  |  |  | -27.8015 | 0
1058 | LONGSHORE_5 | 2 | West | YES | -0.072395 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | -0.18534 | 0 | 220 |  |  |  |  | -0.18534 | -40.7756 |  |  |  |  | -40.7756 | 0
11065 | ELBOWCK_1G | 1 | West | YES | -0.072395 | 23.4 | 0 | 121.9 | 0 | 1 | Wind | 1 | -0.18534 | 0 | 121.9 |  |  |  |  | -0.18534 | -22.5934 |  |  |  |  | -22.5934 | 0
1037 | MORGAN5G_5G | 5 | West | YES | -0.072588 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | -0.18554 | 137 | 137 |  |  |  |  | -0.18554 | -25.4185 |  |  |  |  | -25.4185 | 0
1040 | MRGNBG_2G | B | West | YES | -0.072588 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | -0.18554 | 71 | 71 |  |  |  |  | -0.18554 | -13.1731 |  |  |  |  | -13.1731 | 0
1041 | MRGNCG_3G | C | West | YES | -0.072588 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | -0.18554 | 70 | 70 |  |  |  |  | -0.18554 | -12.9876 |  |  |  |  | -12.9876 | 0
1043 | MRGNEG_5G | E | West | YES | -0.072588 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | -0.18554 | 70 | 70 |  |  |  |  | -0.18554 | -12.9876 |  |  |  |  | -12.9876 | 0
1039 | MRGNAG_1G | A | West | YES | -0.072588 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | -0.18554 | 69 | 69 |  |  |  |  | -0.18554 | -12.802 |  |  |  |  | -12.802 | 0
1042 | MRGNDG_4G | D | West | YES | -0.072588 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | -0.18554 | 68 | 68 |  |  |  |  | -0.18554 | -12.6165 |  |  |  |  | -12.6165 | 0
1044 | MRGNFG_6G | F | West | YES | -0.072588 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | -0.18554 | 66 | 66 |  |  |  |  | -0.18554 | -12.2454 |  |  |  |  | -12.2454 | 0
60058 | BUFF_GAP1A | 1 | West | YES | -0.072677 | 24 | 0 | 120 |  | 1 | Wind | 1 | -0.18563 | 0 | 120 |  |  |  |  | -0.18563 | -22.2751 |  |  |  |  | -22.2751 | 0
60060 | CIRELLO | 1 | West | YES | -0.072677 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | -0.18563 | 0 | 233 |  |  |  |  | -0.18563 | -43.2507 |  |  |  |  | -43.2507 | 0
60063 | BUFF_GAP1B | 1 | West | YES | -0.072677 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | -0.18563 | 0 | 170.2 |  |  |  |  | -0.18563 | -31.5935 |  |  |  |  | -31.5935 | 0
60066 | H_HOLLOW1A | 1 | West | YES | -0.072677 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | -0.18563 | 0 | 222 |  |  |  |  | -0.18563 | -41.2089 |  |  |  |  | -41.2089 | 0
60068 | HHOLLOW21A | 1 | West | YES | -0.072677 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | -0.18563 | 0 | 184 |  |  |  |  | -0.18563 | -34.1551 |  |  |  |  | -34.1551 | 0
60070 | HHOLLOW31A | 1 | West | YES | -0.072677 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | -0.18563 | 0 | 224 |  |  |  |  | -0.18563 | -41.5801 |  |  |  |  | -41.5801 | 0
60072 | HHOLLOW41A | 1 | West | YES | -0.072677 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | -0.18563 | 0 | 115 |  |  |  |  | -0.18563 | -21.3469 |  |  |  |  | -21.3469 | 0
6637 | SNYDERW1A | 1 | West | YES | -0.072681 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | -0.18563 | 0 | 63 |  |  |  |  | -0.18563 | -11.6947 |  |  |  |  | -11.6947 | 0
1068 | SCURRYCW_1G | 1 | West | YES | -0.072746 | 28.2 | 1.3 | 141 | 0 | 1.0217 | Wind | 1 | -0.18569 | 0 | 141 |  |  |  |  | -0.18569 | -26.1829 |  |  |  |  | -26.1829 | 0
1073 | SCURRYCW_2G | 2 | West | YES | -0.072746 | 24 | 0 | 120 | 0 | 1.0217 | Wind | 1 | -0.18569 | 0 | 120 |  |  |  |  | -0.18569 | -22.2833 |  |  |  |  | -22.2833 | 0
1061 | CIELOGEN_1G | 1 | West | YES | -0.072757 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | -0.18571 | 0 | 99 |  |  |  |  | -0.18571 | -18.3848 |  |  |  |  | -18.3848 | 0
1062 | CIELOGEN_2G | 1 | West | YES | -0.072757 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | -0.18571 | 0 | 61 |  |  |  |  | -0.18571 | -11.328 |  |  |  |  | -11.328 | 0
1069 | KINDERMG_1G | 1 | West | YES | -0.072757 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | -0.18571 | 0 | 0 |  |  |  |  | -0.18571 | 0 |  |  |  |  | 0 | 0
1070 | KINDERMG_2G | 1 | West | YES | -0.072757 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | -0.18571 | 0 | 0 |  |  |  |  | -0.18571 | 0 |  |  |  |  | 0 | 0
1071 | KINDERMG_3G | 1 | West | YES | -0.072757 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | -0.18571 | 0 | 0 |  |  |  |  | -0.18571 | 0 |  |  |  |  | 0 | 0
8189 | CUECPL2A | 1 | South | YES | 0.10813 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | -0.1856 | 0 | 0 |  |  | 0 | 0 | 0.1856 | 0 |  |  |  |  | 0 | 0
36998 | RDCNYNG1 | 1 | West | YES | -0.072957 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | -0.18591 | 0 | 84 |  |  |  |  | -0.18591 | -15.6161 |  |  |  |  | -15.6161 | 0
11056 | ROSCOE_1G | 1 | West | YES | -0.073449 | 41.8 | 0 | 209 |  | 1 | Wind | 1 | -0.1864 | 0 | 209 |  |  |  |  | -0.1864 | -38.9571 |  |  |  |  | -38.9571 | 0
11057 | CHAMPION_1G | 1 | West | YES | -0.073449 | 25.3 | 0 | 126.5 |  | 1 | Wind | 1 | -0.1864 | 0 | 126.5 |  |  |  |  | -0.1864 | -23.5793 |  |  |  |  | -23.5793 | 0
11058 | PYRON_1G | 1 | West | YES | -0.073449 | 49.8 | 0 | 249 |  | 1 | Wind | 1 | -0.1864 | 0 | 249 |  |  |  |  | -0.1864 | -46.413 |  |  |  |  | -46.413 | 0
11059 | INADALE_1G | 1 | West | YES | -0.073449 | 39.4 | 0 | 197 |  | 1 | Wind | 1 | -0.1864 | 0 | 197 |  |  |  |  | -0.1864 | -36.7203 |  |  |  |  | -36.7203 | 0
71051 | L_BITTCR1_1N | W1 | West | YES | -0.073488 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | -0.18644 | 0 | 37.5 |  |  |  |  | -0.18644 | -6.9914 |  |  |  |  | -6.9914 | 0
71054 | L_SWEETW1_1N | W1 | West | YES | -0.073488 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | -0.18644 | 0 | 107.5 |  |  |  |  | -0.18644 | -20.0419 |  |  |  |  | -20.0419 | 0
71057 | L_SWEETW1_2N | W1 | West | YES | -0.073488 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | -0.18644 | 0 | 135 |  |  |  |  | -0.18644 | -25.1689 |  |  |  |  | -25.1689 | 0
71059 | L_SWEETW1_3N | W1 | West | YES | -0.073488 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | -0.18644 | 0 | 119 |  |  |  |  | -0.18644 | -22.1859 |  |  |  |  | -22.1859 | 0
71060 | L_SWEETW1_4N | W1 | West | YES | -0.073488 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | -0.18644 | 0 | 105 |  |  |  |  | -0.18644 | -19.5758 |  |  |  |  | -19.5758 | 0
71061 | L_SWEETW1_5N | W1 | West | YES | -0.073488 | 16.1 | 0 | 80.5 | 0 | 1.02 | Wind | 1 | -0.18644 | 0 | 80.5 |  |  |  |  | -0.18644 | -15.0081 |  |  |  |  | -15.0081 | 0
1343 | TRENTIPP_8 | 1 | West | YES | -0.073554 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | -0.1865 | 0 | 150 |  |  |  |  | -0.1865 | -27.9754 |  |  |  |  | -27.9754 | 0
1354 | AEPWIND_8 | 1 | West | YES | -0.073554 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | -0.1865 | 0 | 101 |  |  |  |  | -0.1865 | -18.8368 |  |  |  |  | -18.8368 | 0
3108 | STRYKER_2G | 2 | North | YES | -0.073578 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | -0.18653 | 484 | 484 | -35.6118 | 484 |  |  | -0.18653 | -90.2788 |  |  |  |  | -90.2788 | 0
3107 | STRYKER_1G | 1 | North | YES | -0.073578 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | -0.18653 | 182 | 182 | -13.3912 | 182 |  |  | -0.18653 | -33.9478 |  |  |  |  | -33.9478 | 0
6144 | MCADOO1A | 1 | West | YES | -0.073835 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | -0.18678 | 0 | 150 |  |  |  |  | -0.18678 | -28.0175 |  |  |  |  | -28.0175 | 0
3309 | ASPN_G | 1 | North | YES | -0.073872 | 50 | 0 | 50 |  | 1 | Bio | 1 | -0.18682 | 50 | 50 | -3.6936 | 50 |  |  | -0.18682 | -9.341 |  |  |  |  | -9.341 | 0
1417 | SWETWATR_2G | 2 | West | YES | -0.073874 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | -0.18682 | 72 | 72 |  |  |  |  | -0.18682 | -13.4512 |  |  |  |  | -13.4512 | 0
1418 | SWETWATR_3G | 3 | West | YES | -0.073874 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | -0.18682 | 68 | 68 |  |  |  |  | -0.18682 | -12.7039 |  |  |  |  | -12.7039 | 0
1419 | SWETWATR_4G | 4 | West | YES | -0.073874 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | -0.18682 | 61 | 61 |  |  |  |  | -0.18682 | -11.3962 |  |  |  |  | -11.3962 | 0
1416 | SWETWATR_1G | 1 | West | YES | -0.073874 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | -0.18682 | 30 | 30 |  |  |  |  | -0.18682 | -5.6047 |  |  |  |  | -5.6047 | 0
3348 | CHAMPION_1G | MB | North | YES | -0.073911 | 0 | 42 | 42 |  | 1 | Cogen | 1 | -0.18686 | 0 | 0 | 0 | 0 |  |  | -0.18686 | 0 |  |  |  |  | 0 | 0
6407 | TURKTRAK1A | 1 | West | YES | -0.074181 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | -0.18713 | 0 | 169.5 |  |  |  |  | -0.18713 | -31.7184 |  |  |  |  | -31.7184 | 0
13119 | TGATEWAY_4G | 4 | North | YES | -0.074396 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | -0.18734 | 399 | 399 | -29.684 | 399 |  |  | -0.18734 | -74.7504 |  |  |  |  | -74.7504 | 0
13116 | TGATEWAY_1G | 1 | North | YES | -0.074396 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | -0.18734 | 151 | 151 | -11.2338 | 151 |  |  | -0.18734 | -28.289 |  |  |  |  | -28.289 | 0
13118 | TGATEWAY_3G | 3 | North | YES | -0.074396 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | -0.18734 | 148 | 148 | -11.0106 | 148 |  |  | -0.18734 | -27.727 |  |  |  |  | -27.727 | 0
13117 | TGATEWAY_2G | 2 | North | YES | -0.074396 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | -0.18734 | 130 | 130 | -9.6715 | 130 |  |  | -0.18734 | -24.3548 |  |  |  |  | -24.3548 | 0
60081 | WHRLWIND1A | 1 | West | YES | -0.074799 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | -0.18775 | 0 | 60 |  |  |  |  | -0.18775 | -11.2648 |  |  |  |  | -11.2648 | 0
3097 | MARTLAKE_1G | 1 | North | YES | -0.074802 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | -0.18775 | 0 | 790 | -59.0936 | 790 |  |  | -0.18775 | -148.3229 |  |  |  |  | -148.3229 | 0
3098 | MARTLAKE_2G | 2 | North | YES | -0.074802 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | -0.18775 | 0 | 795 | -59.4676 | 795 |  |  | -0.18775 | -149.2616 |  |  |  |  | -149.2616 | 0
3099 | MARTLAKE_3G | 3 | North | YES | -0.074802 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | -0.18775 | 0 | 804 | -60.1408 | 804 |  |  | -0.18775 | -150.9514 |  |  |  |  | -150.9514 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | 0.11031 | 562 | 100 | 562 | 0 | 1.026 | LIGCO | -1 | -0.18778 | 0 | 562 |  |  | 0 | 0 | 0.18778 | 0 |  |  |  |  | 0 | 0
5268 | LEON_LCPCT3 | 3 | South | YES | 0.11045 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | -0.18791 | 43 | 43 |  |  | 4.7491 | 43 | 0.18791 | 8.0803 |  |  |  |  | 0 | 8.0803
5266 | LEON_LCPCT1 | 1 | South | YES | 0.11045 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | -0.18791 | 44 | 44 |  |  | 4.8596 | 44 | 0.18791 | 8.2682 |  |  |  |  | 0 | 8.2682
5267 | LEON_LCPCT2 | 2 | South | YES | 0.11045 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | -0.18791 | 44 | 44 |  |  | 4.8596 | 44 | 0.18791 | 8.2682 |  |  |  |  | 0 | 8.2682
5269 | LEON_LCPCT4 | 4 | South | YES | 0.11045 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | -0.18791 | 45 | 45 |  |  | 4.97 | 45 | 0.18791 | 8.4561 |  |  |  |  | 0 | 8.4561
5264 | LEON_LCP3G3 | 3 | South | YES | 0.11045 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | -0.18791 | 58 | 58 |  |  | 6.4058 | 58 | 0.18791 | 10.899 |  |  |  |  | 0 | 10.899
5265 | LEON_LCP4G4 | 4 | South | YES | 0.11045 | 89 | 25 | 89 | 0 | 1.0197 | GST | -1 | -0.18791 | 89 | 89 |  |  | 9.8296 | 89 | 0.18791 | 16.7243 |  |  |  |  | 0 | 16.7243
5476 | BRA_AVR1_CT1 | 1 | South | YES | 0.11081 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | -0.18828 | 155 | 155 |  |  | 17.1762 | 155 | 0.18828 | 29.1838 |  |  |  |  | 0 | 29.1838
5478 | BRA_AVR1_CT2 | 1 | South | YES | 0.11081 | 155 | 90 | 155 | 0 | 1.025 | CC | -1 | -0.18828 | 155 | 155 |  |  | 17.1762 | 155 | 0.18828 | 29.1838 |  |  |  |  | 0 | 29.1838
5477 | BRA_AVR1_ST | 1 | South | YES | 0.11081 | 174 | 138 | 174 | 0 | 1.025 | CC | -1 | -0.18828 | 174 | 174 |  |  | 19.2816 | 174 | 0.18828 | 32.7611 |  |  |  |  | 0 | 32.7611
1437 | MESQUITW_1G | 1 | North | YES | -0.075751 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | -0.1887 | 0 | 400 | -30.3004 | 400 |  |  | -0.1887 | -75.4798 |  |  |  |  | -75.4798 | 0
1438 | MESQUITW_2G | 1 | North | YES | -0.075754 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | -0.1887 | 0 | 236 | -17.8779 | 236 |  |  | -0.1887 | -44.5338 |  |  |  |  | -44.5338 | 0
5028 | BRAUNIG_VHB3 | 3 | South | YES | 0.11119 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | -0.18866 | 407 | 407 |  |  | 45.2547 | 407 | 0.18866 | 76.7844 |  |  |  |  | 0 | 76.7844
5026 | BRAUNIG_VHB1 | 1 | South | YES | 0.11124 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | -0.18871 | 215 | 215 |  |  | 23.916 | 215 | 0.18871 | 40.5717 |  |  |  |  | 0 | 40.5717
5027 | BRAUNIG_VHB2 | 2 | South | YES | 0.11124 | 216 | 40 | 216 | 0 | 1.0192 | GST | -1 | -0.18871 | 216 | 216 |  |  | 24.0272 | 216 | 0.18871 | 40.7604 |  |  |  |  | 0 | 40.7604
5397 | CALAVER_OWS2 | 2 | South | YES | 0.11138 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | -0.18885 | 400 | 400 |  |  | 44.5516 | 400 | 0.18885 | 75.539 |  |  |  |  | 0 | 75.539
5396 | CALAVER_OWS1 | 1 | South | YES | 0.11138 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | -0.18885 | 418 | 418 |  |  | 46.5564 | 418 | 0.18885 | 78.9382 |  |  |  |  | 0 | 78.9382
5111 | CALAVER_JTD1 | 1 | South | YES | 0.11154 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | -0.189 | 0 | 430 |  |  | 0 | 0 | 0.189 | 0 |  |  |  |  | 0 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | 0.11154 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | -0.189 | 0 | 430 |  |  | 0 | 0 | 0.189 | 0 |  |  |  |  | 0 | 0
1442 | COKFIELD_5 | 1 | North | YES | -0.076455 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | -0.1894 | 0 | 165 | -12.6151 | 165 |  |  | -0.1894 | -31.2516 |  |  |  |  | -31.2516 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | 0.112 | 0 | 0 | 36 |  | 1 | Hydro | -1 | -0.18947 | 0 | 0 |  |  | 0 | 0 | 0.18947 | 0 |  |  |  |  | 0 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | 0.112 | 0 | 0 | 35 |  | 1 | Hydro | -1 | -0.18947 | 0 | 0 |  |  | 0 | 0 | 0.18947 | 0 |  |  |  |  | 0 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | 0.112 | 0 | 0 | 36 |  | 1 | Hydro | -1 | -0.18947 | 0 | 0 |  |  | 0 | 0 | 0.18947 | 0 |  |  |  |  | 0 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | 0.11202 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | -0.18948 | 61 | 61 |  |  | 6.8329 | 61 | 0.18948 | 11.5585 |  |  |  |  | 0 | 11.5585
5438 | TUTTL_WBT3G3 | 3 | South | YES | 0.11202 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | -0.18948 | 95 | 95 |  |  | 10.6414 | 95 | 0.18948 | 18.0009 |  |  |  |  | 0 | 18.0009
5439 | TUTTL_WBT4G4 | 4 | South | YES | 0.11202 | 151 | 40 | 151 | 0 | 1.012 | GST | -1 | -0.18948 | 151 | 151 |  |  | 16.9143 | 151 | 0.18948 | 28.612 |  |  |  |  | 0 | 28.612
6100 | OKLA7A | EQ | West | YES | -0.077014 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | -0.18996 | 0 | 0 |  |  |  |  | -0.18996 | 0 |  |  |  |  | 0 | 0
6752 | OKLA0A | 1 | West | YES | -0.077014 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | -0.18996 | 0 | 649.7 |  |  |  |  | -0.18996 | -123.4186 |  |  |  |  | -123.4186 | 0
12424 | FPLEFR2S_G | 4 | North | YES | -0.077899 | 415 | 191 | 415 | 0 | 1 | CC | 1 | -0.19085 | 415 | 415 | -32.3281 | 415 |  |  | -0.19085 | -79.2017 |  |  |  |  | -79.2017 | 0
12414 | FPLEFR1S_G | 4 | North | YES | -0.077899 | 414 | 191 | 414 | 0 | 1 | CC | 1 | -0.19085 | 414 | 414 | -32.2502 | 414 |  |  | -0.19085 | -79.0109 |  |  |  |  | -79.0109 | 0
12412 | FPLEFR1B_G | 2 | North | YES | -0.077899 | 164 | 72 | 164 | 0 | 1 | CC | 1 | -0.19085 | 164 | 164 | -12.7754 | 164 |  |  | -0.19085 | -31.299 |  |  |  |  | -31.299 | 0
12413 | FPLEFR1C_G | 3 | North | YES | -0.077899 | 164 | 72 | 164 | 0 | 1 | CC | 1 | -0.19085 | 164 | 164 | -12.7754 | 164 |  |  | -0.19085 | -31.299 |  |  |  |  | -31.299 | 0
12423 | FPLEFR2C_G | 3 | North | YES | -0.077899 | 163 | 72 | 163 | 0 | 1 | CC | 1 | -0.19085 | 163 | 163 | -12.6975 | 163 |  |  | -0.19085 | -31.1081 |  |  |  |  | -31.1081 | 0
12421 | FPLEFR2A_G | 1 | North | YES | -0.077899 | 162 | 72 | 162 | 0 | 1 | CC | 1 | -0.19085 | 162 | 162 | -12.6196 | 162 |  |  | -0.19085 | -30.9173 |  |  |  |  | -30.9173 | 0
12411 | FPLEFR1A_G | 1 | North | YES | -0.077899 | 161 | 72 | 161 | 0 | 1 | CC | 1 | -0.19085 | 161 | 161 | -12.5417 | 161 |  |  | -0.19085 | -30.7264 |  |  |  |  | -30.7264 | 0
12422 | FPLEFR2B_G | 2 | North | YES | -0.077899 | 161 | 72 | 161 | 0 | 1 | CC | 1 | -0.19085 | 161 | 161 | -12.5417 | 161 |  |  | -0.19085 | -30.7264 |  |  |  |  | -30.7264 | 0
3126 | TRINIDAD_6G | 1 | North | YES | -0.078229 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | -0.19118 | 224 | 224 | -17.5233 | 224 |  |  | -0.19118 | -42.8238 |  |  |  |  | -42.8238 | 0
2452 | LKHB2_G | 2 | North | YES | -0.078519 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | -0.19147 | 516 | 516 | -40.5158 | 516 |  |  | -0.19147 | -98.7972 |  |  |  |  | -98.7972 | 0
2451 | LKHB1_G | 1 | North | YES | -0.078519 | 0 | 80 | 391 |  | 1.022 | GST | 1 | -0.19147 | 391 | 391 | -30.7009 | 391 |  |  | -0.19147 | -74.8638 |  |  |  |  | -74.8638 | 0
12440 | PARKD_1SVC8 | 1 | North | YES | -0.078652 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | -0.1916 | 0 | 0 | 0 | 0 |  |  | -0.1916 | 0 |  |  |  |  | 0 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | -0.078652 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | -0.1916 | 0 | 0 | 0 | 0 |  |  | -0.1916 | 0 |  |  |  |  | 0 | 0
1432 | GRHAMSES_2G | 2 | North | YES | -0.078676 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | -0.19162 | 366 | 366 | -28.7954 | 366 |  |  | -0.19162 | -70.1346 |  |  |  |  | -70.1346 | 0
950 | STEAM3 | 1 | North | YES | -0.078698 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | -0.19165 | 42 | 42 | -3.3053 | 42 |  |  | -0.19165 | -8.0492 |  |  |  |  | -8.0492 | 0
949 | STEAM2 | 1 | North | YES | -0.078698 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | -0.19165 | 26 | 26 | -2.0461 | 26 |  |  | -0.19165 | -4.9828 |  |  |  |  | -4.9828 | 0
948 | STEAM1 | 1 | North | YES | -0.078698 | 0 | 12 | 20 |  | 1.02 | GST | 1 | -0.19165 | 20 | 20 | -1.574 | 20 |  |  | -0.19165 | -3.8329 |  |  |  |  | -3.8329 | 0
1479 | WFCOGEN_1G | 1 | North | YES | -0.078793 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | -0.19174 | 0 | 0 | 0 | 0 |  |  | -0.19174 | 0 |  |  |  |  | 0 | 0
1479 | WFCOGEN_1G | 2 | North | YES | -0.078793 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | -0.19174 | 0 | 0 | 0 | 0 |  |  | -0.19174 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 2 | North | YES | -0.078793 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | -0.19174 | 0 | 0 | 0 | 0 |  |  | -0.19174 | 0 |  |  |  |  | 0 | 0
1482 | WFCOGEN_2G | 1 | North | YES | -0.078793 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | -0.19174 | 0 | 0 | 0 | 0 |  |  | -0.19174 | 0 |  |  |  |  | 0 | 0
844 | OLINGER_G3 | 1 | North | YES | -0.078831 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | -0.19178 | 150 | 150 | -11.8247 | 150 |  |  | -0.19178 | -28.7669 |  |  |  |  | -28.7669 | 0
843 | OLINGER_G2 | 1 | North | YES | -0.078831 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | -0.19178 | 110 | 110 | -8.6714 | 110 |  |  | -0.19178 | -21.0957 |  |  |  |  | -21.0957 | 0
842 | OLINGER_G1 | 1 | North | YES | -0.078831 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | -0.19178 | 79 | 79 | -6.2276 | 79 |  |  | -0.19178 | -15.1506 |  |  |  |  | -15.1506 | 0
845 | OLINGER_G4 | 1 | North | YES | -0.078831 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | -0.19178 | 76 | 76 | -5.9912 | 76 |  |  | -0.19178 | -14.5752 |  |  |  |  | -14.5752 | 0
837 | NEWMAN_G5 | 1 | North | YES | -0.078834 | 0 | 15 | 40 |  | 1.01 | GST | 1 | -0.19178 | 40 | 40 | -3.1534 | 40 |  |  | -0.19178 | -7.6713 |  |  |  |  | -7.6713 | 0
1701 | MOSES_1G | 1 | North | YES | -0.078932 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | -0.19188 | 0 | 558 | -44.0441 | 558 |  |  | -0.19188 | -107.0693 |  |  |  |  | -107.0693 | 0
1702 | MOSES_2G | 2 | North | YES | -0.078932 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | -0.19188 | 0 | 579 | -45.7016 | 579 |  |  | -0.19188 | -111.0988 |  |  |  |  | -111.0988 | 0
1703 | MOSES_3G | 3 | North | YES | -0.078932 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | -0.19188 | 0 | 808 | -63.7771 | 808 |  |  | -0.19188 | -155.0394 |  |  |  |  | -155.0394 | 0
5925 | DCEAST | EQ | North | YES | -0.078932 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | -0.19188 | 0 | 0 | 0 | 0 |  |  | -0.19188 | 0 |  |  |  |  | 0 | 0
1675 | PEC_1G | 1 | North | YES | -0.078997 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | -0.19195 | 0 | 0 | 0 | 0 |  |  | -0.19195 | 0 |  |  |  |  | 0 | 0
1676 | PEC_2G | 2 | North | YES | -0.078997 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | -0.19195 | 0 | 0 | 0 | 0 |  |  | -0.19195 | 0 |  |  |  |  | 0 | 0
1677 | PEC_3G | 3 | North | YES | -0.078997 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | -0.19195 | 0 | 0 | 0 | 0 |  |  | -0.19195 | 0 |  |  |  |  | 0 | 0
1433 | GRHAMSES_1G | 1 | North | YES | -0.079015 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | -0.19196 | 242 | 242 | -19.1216 | 242 |  |  | -0.19196 | -46.4552 |  |  |  |  | -46.4552 | 0
1683 | LAMARPWR_6G | 6 | North | YES | -0.079067 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | -0.19202 | 198 | 198 | -15.6553 | 198 |  |  | -0.19202 | -38.0191 |  |  |  |  | -38.0191 | 0
1680 | LAMARPWR_3G | 3 | North | YES | -0.079067 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | -0.19202 | 196 | 196 | -15.4971 | 196 |  |  | -0.19202 | -37.635 |  |  |  |  | -37.635 | 0
1678 | LAMARPWR_1G | 1 | North | YES | -0.079067 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | -0.19202 | 160 | 160 | -12.6507 | 160 |  |  | -0.19202 | -30.7225 |  |  |  |  | -30.7225 | 0
1682 | LAMARPWR_5G | 5 | North | YES | -0.079067 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | -0.19202 | 157 | 157 | -12.4135 | 157 |  |  | -0.19202 | -30.1464 |  |  |  |  | -30.1464 | 0
1679 | LAMARPWR_2G | 2 | North | YES | -0.079067 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | -0.19202 | 156 | 156 | -12.3345 | 156 |  |  | -0.19202 | -29.9544 |  |  |  |  | -29.9544 | 0
1681 | LAMARPWR_4G | 4 | North | YES | -0.079067 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | -0.19202 | 156 | 156 | -12.3345 | 156 |  |  | -0.19202 | -29.9544 |  |  |  |  | -29.9544 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | 0.11428 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | -0.19175 | 0 | 0 |  |  | 0 | 0 | 0.19175 | 0 |  |  |  |  | 0 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | 0.11428 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | -0.19175 | 0 | 0 |  |  | 0 | 0 | 0.19175 | 0 |  |  |  |  | 0 | 0
1689 | VALLEY_3G | 3 | North | YES | -0.079149 | 0 | 25 | 375 |  | 1.003 | GST | 1 | -0.1921 | 375 | 375 | -29.6809 | 375 |  |  | -0.1921 | -72.0366 |  |  |  |  | -72.0366 | 0
11693 | KMICHIST3_G | 3 | North | YES | -0.079149 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | -0.1921 | 312 | 312 | -24.6945 | 312 |  |  | -0.1921 | -59.9344 |  |  |  |  | -59.9344 | 0
11696 | KMICHIST6_G | 6 | North | YES | -0.079149 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | -0.1921 | 310 | 310 | -24.5362 | 310 |  |  | -0.1921 | -59.5502 |  |  |  |  | -59.5502 | 0
11695 | KMICHICT5_G | 5 | North | YES | -0.079149 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | -0.1921 | 148 | 148 | -11.7141 | 148 |  |  | -0.1921 | -28.4304 |  |  |  |  | -28.4304 | 0
11692 | KMICHICT2_G | 2 | North | YES | -0.079149 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | -0.1921 | 146 | 146 | -11.5558 | 146 |  |  | -0.1921 | -28.0462 |  |  |  |  | -28.0462 | 0
11691 | KMICHICT1_G | 1 | North | YES | -0.079149 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | -0.1921 | 144 | 144 | -11.3975 | 144 |  |  | -0.1921 | -27.662 |  |  |  |  | -27.662 | 0
11694 | KMICHICT4_G | 4 | North | YES | -0.079149 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | -0.1921 | 144 | 144 | -11.3975 | 144 |  |  | -0.1921 | -27.662 |  |  |  |  | -27.662 | 0
1688 | VALLEY_2G | 2 | North | YES | -0.079274 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | -0.19222 | 527 | 527 | -41.7774 | 527 |  |  | -0.19222 | -101.3012 |  |  |  |  | -101.3012 | 0
1687 | VALLEY_1G | 1 | North | YES | -0.079274 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | -0.19222 | 170 | 170 | -13.4766 | 170 |  |  | -0.19222 | -32.6778 |  |  |  |  | -32.6778 | 0
6948 | DENISNDM | 1 | North | YES | -0.079384 | 40 | 5 | 40 |  | 1.015 | Hydro | 1 | -0.19233 | 0 | 0 | 0 | 0 |  |  | -0.19233 | 0 |  |  |  |  | 0 | 0
6948 | DENISNDM | 2 | North | YES | -0.079384 | 31 | 5 | 40 |  | 1.015 | Hydro | 1 | -0.19233 | 0 | 0 | 0 | 0 |  |  | -0.19233 | 0 |  |  |  |  | 0 | 0
2371 | COLLIN_1G | MB | North | YES | -0.079895 | 0 | 40 | 138 |  | 1.022 | GST | 1 | -0.19284 | 0 | 0 | 0 | 0 |  |  | -0.19284 | 0 |  |  |  |  | 0 | 0
2417 | MTCK8_G | 8 | North | YES | -0.080047 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | -0.193 | 556 | 556 | -44.5061 | 556 |  |  | -0.193 | -107.3055 |  |  |  |  | -107.3055 | 0
2413 | MTCK6_G | 6 | North | YES | -0.080047 | 0 | 30 | 118 |  | 1.022 | GST | 1 | -0.193 | 118 | 118 | -9.4455 | 118 |  |  | -0.193 | -22.7735 |  |  |  |  | -22.7735 | 0
2414 | MTCK7_G | 7 | North | YES | -0.080047 | 0 | 30 | 115 |  | 1.022 | GST | 1 | -0.193 | 115 | 115 | -9.2054 | 115 |  |  | -0.193 | -22.1945 |  |  |  |  | -22.1945 | 0
7801 | L_GUADGE1_2Y | 2 | South | YES | 0.11532 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | -0.19279 | 138 | 138 |  |  | 15.9148 | 138 | 0.19279 | 26.6055 |  |  |  |  | 0 | 26.6055
7802 | L_GUADGE1_3Y | 3 | South | YES | 0.11532 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | -0.19279 | 146 | 146 |  |  | 16.8375 | 146 | 0.19279 | 28.1478 |  |  |  |  | 0 | 28.1478
7800 | L_GUADGE1_1Y | 1 | South | YES | 0.11532 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | -0.19279 | 147 | 147 |  |  | 16.9528 | 147 | 0.19279 | 28.3406 |  |  |  |  | 0 | 28.3406
7803 | L_GUADGE1_4Y | 4 | South | YES | 0.11532 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | -0.19279 | 149 | 149 |  |  | 17.1834 | 149 | 0.19279 | 28.7262 |  |  |  |  | 0 | 28.7262
7804 | L_GUADGE1_5Y | 5 | South | YES | 0.11532 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | -0.19279 | 182 | 182 |  |  | 20.9891 | 182 | 0.19279 | 35.0884 |  |  |  |  | 0 | 35.0884
7805 | L_GUADGE1_6Y | 6 | South | YES | 0.11532 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | -0.19279 | 203 | 203 |  |  | 23.411 | 203 | 0.19279 | 39.1371 |  |  |  |  | 0 | 39.1371
2383 | NTHLK3_G | 3 | North | YES | -0.080447 | 0 | 50 | 329 |  | 1.022 | GST | 1 | -0.1934 | 329 | 329 | -26.4671 | 329 |  |  | -0.1934 | -63.6271 |  |  |  |  | -63.6271 | 0
2382 | NTHLK2_G | 2 | North | YES | -0.080447 | 0 | 35 | 181 |  | 1.022 | GST | 1 | -0.1934 | 181 | 181 | -14.5609 | 181 |  |  | -0.1934 | -35.0046 |  |  |  |  | -35.0046 | 0
2381 | NTHLK1_G | 1 | North | YES | -0.080447 | 0 | 35 | 156 |  | 1.022 | GST | 1 | -0.1934 | 156 | 156 | -12.5497 | 156 |  |  | -0.1934 | -30.1697 |  |  |  |  | -30.1697 | 0
1455 | WCPWRCO_3G | 3 | North | YES | -0.080514 | 242 | 50 | 242 |  | 1.02 | CC | 1 | -0.19346 | 242 | 242 | -19.4844 | 242 |  |  | -0.19346 | -46.8179 |  |  |  |  | -46.8179 | 0
1453 | WCPWRCO_1G | 1 | North | YES | -0.080514 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | -0.19346 | 204 | 204 | -16.4249 | 204 |  |  | -0.19346 | -39.4663 |  |  |  |  | -39.4663 | 0
1454 | WCPWRCO_2G | 2 | North | YES | -0.080514 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | -0.19346 | 204 | 204 | -16.4249 | 204 |  |  | -0.19346 | -39.4663 |  |  |  |  | -39.4663 | 0
924 | SPENCER_G5 | 1 | North | YES | -0.080587 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | -0.19354 | 66 | 66 | -5.3187 | 66 |  |  | -0.19354 | -12.7733 |  |  |  |  | -12.7733 | 0
923 | SPENCER_G4 | 1 | North | YES | -0.080587 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | -0.19354 | 61 | 61 | -4.9158 | 61 |  |  | -0.19354 | -11.8057 |  |  |  |  | -11.8057 | 0
728 | WOLFRIDGE801 | 1 | North | YES | -0.080609 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | -0.19356 | 0 | 112.5 | -9.0685 | 112.5 |  |  | -0.19356 | -21.7752 |  |  |  |  | -21.7752 | 0
344 | MRSSHPRD | 1 | North | YES | -0.080876 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | -0.19382 | 0 | 0 | 0 | 0 |  |  | -0.19382 | 0 |  |  |  |  | 0 | 0
345 | MRSSHPRD01 | 2 | North | YES | -0.080876 | 0 | 0 | 12 |  | 1.03 | Hydro | 1 | -0.19382 | 0 | 0 | 0 | 0 |  |  | -0.19382 | 0 |  |  |  |  | 0 | 0
1600 | BARTNWND_1G | 1 | North | YES | -0.080879 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | -0.19383 | 0 | 120 | -9.7055 | 120 |  |  | -0.19383 | -23.2593 |  |  |  |  | -23.2593 | 0
580 | JCKCNTY801 | 1 | North | YES | -0.081465 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | -0.19441 | 288 | 288 | -23.4619 | 288 |  |  | -0.19441 | -55.9911 |  |  |  |  | -55.9911 | 0
581 | JCKCNTY802 | 2 | North | YES | -0.081465 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | -0.19441 | 147 | 147 | -11.9754 | 147 |  |  | -0.19441 | -28.5788 |  |  |  |  | -28.5788 | 0
582 | JCKCNTY803 | 3 | North | YES | -0.081465 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | -0.19441 | 147 | 147 | -11.9754 | 147 |  |  | -0.19441 | -28.5788 |  |  |  |  | -28.5788 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | 0.11669 | 0 | 0 | 4 |  | 1 | Hydro | -1 | -0.19416 | 0 | 0 |  |  | 0 | 0 | 0.19416 | 0 |  |  |  |  | 0 | 0
12322 | ENNSTRAC_1G | 1 | North | YES | -0.081523 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | -0.19447 | 196 | 196 | -15.9785 | 196 |  |  | -0.19447 | -38.1164 |  |  |  |  | -38.1164 | 0
12323 | ENNSTRAC_2G | 2 | North | YES | -0.081523 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | -0.19447 | 116 | 116 | -9.4567 | 116 |  |  | -0.19447 | -22.5587 |  |  |  |  | -22.5587 | 0
1861 | EAGLEMNT_1G | MB | North | YES | -0.082051 | 0 | 30 | 112 |  | 1.022 | GST | 1 | -0.195 | 0 | 0 | 0 | 0 |  |  | -0.195 | 0 |  |  |  |  | 0 | 0
1862 | EAGLEMNT_2G | MB | North | YES | -0.082051 | 0 | 40 | 100 |  | 1.022 | GST | 1 | -0.195 | 0 | 0 | 0 | 0 |  |  | -0.195 | 0 |  |  |  |  | 0 | 0
1863 | EAGLEMNT_3G | MB | North | YES | -0.082051 | 0 | 50 | 378 |  | 1.022 | GST | 1 | -0.195 | 0 | 0 | 0 | 0 |  |  | -0.195 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | 0.1173 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | -0.19477 | 0 | 0 |  |  | 0 | 0 | 0.19477 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | 0.1173 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | -0.19477 | 0 | 0 |  |  | 0 | 0 | 0.19477 | 0 |  |  |  |  | 0 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | 0.1173 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | -0.19477 | 0 | 0 |  |  | 0 | 0 | 0.19477 | 0 |  |  |  |  | 0 | 0
505 | NTHTEXAS03 | 3 | North | YES | -0.08264 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | -0.19559 | 38 | 38 | -3.1403 | 38 |  |  | -0.19559 | -7.4324 |  |  |  |  | -7.4324 | 0
503 | NTHTEXAS01 | 1 | North | YES | -0.08264 | 0 | 5 | 18 |  | 1.015 | GST | 1 | -0.19559 | 18 | 18 | -1.4875 | 18 |  |  | -0.19559 | -3.5206 |  |  |  |  | -3.5206 | 0
504 | NTHTEXAS02 | 2 | North | YES | -0.08264 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | -0.19559 | 18 | 18 | -1.4875 | 18 |  |  | -0.19559 | -3.5206 |  |  |  |  | -3.5206 | 0
1948 | HANDLEY_4G | 4 | North | YES | -0.083129 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | -0.19608 | 435 | 435 | -36.1611 | 435 |  |  | -0.19608 | -85.2937 |  |  |  |  | -85.2937 | 0
1898 | COMCHEPK_1G | 1 | North | YES | -0.083155 | 1217 | 1150 | 1217 | 0 | 1.032 | Nuc | 1 | -0.1961 | 0 | 0 | 0 | 0 |  |  | -0.1961 | 0 |  |  |  |  | 0 | 0
1899 | COMCHEPK_2G | 2 | North | YES | -0.083155 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | -0.1961 | 0 | 0 | 0 | 0 |  |  | -0.1961 | 0 |  |  |  |  | 0 | 0
1949 | HANDLEY_5G | 5 | North | YES | -0.08326 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | -0.19621 | 435 | 435 | -36.2181 | 435 |  |  | -0.19621 | -85.3507 |  |  |  |  | -85.3507 | 0
1947 | HANDLEY_3G | 3 | North | YES | -0.08326 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | -0.19621 | 395 | 395 | -32.8877 | 395 |  |  | -0.19621 | -77.5023 |  |  |  |  | -77.5023 | 0
1879 | WLFHOLW_3G | 3 | North | YES | -0.083279 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | -0.19623 | 272.4 | 272.4 | -22.6852 | 272.4 |  |  | -0.19623 | -53.4524 |  |  |  |  | -53.4524 | 0
1877 | WLFHOLW_1G | 1 | North | YES | -0.083279 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | -0.19623 | 217.3 | 217.3 | -18.0965 | 217.3 |  |  | -0.19623 | -42.6402 |  |  |  |  | -42.6402 | 0
1878 | WLFHOLW_2G | 2 | North | YES | -0.083279 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | -0.19623 | 215.7 | 215.7 | -17.9633 | 215.7 |  |  | -0.19623 | -42.3263 |  |  |  |  | -42.3263 | 0
1889 | DECRDOVA_1G | 1 | North | YES | -0.08342 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | -0.19637 | 779 | 779 | -64.9842 | 779 |  |  | -0.19637 | -152.971 |  |  |  |  | -152.971 | 0
334 | RWMILLER03 | 3 | North | YES | -0.083777 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | -0.19673 | 208 | 208 | -17.4256 | 208 |  |  | -0.19673 | -40.9189 |  |  |  |  | -40.9189 | 0
333 | RWMILLER02 | 2 | North | YES | -0.083777 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | -0.19673 | 119 | 119 | -9.9695 | 119 |  |  | -0.19673 | -23.4103 |  |  |  |  | -23.4103 | 0
335 | RWMILLER04 | 4 | North | YES | -0.083777 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | -0.19673 | 102 | 102 | -8.5453 | 102 |  |  | -0.19673 | -20.066 |  |  |  |  | -20.066 | 0
336 | RWMILLER05 | 5 | North | YES | -0.083777 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | -0.19673 | 101 | 101 | -8.4615 | 101 |  |  | -0.19673 | -19.8693 |  |  |  |  | -19.8693 | 0
332 | RWMILLER01 | 1 | North | YES | -0.083777 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | -0.19673 | 73 | 73 | -6.1157 | 73 |  |  | -0.19673 | -14.361 |  |  |  |  | -14.361 | 0
1643 | SLSTR1PP_1G | 1 | North | YES | -0.083839 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | -0.19679 | 0 | 60 | -5.0303 | 60 |  |  | -0.19679 | -11.8072 |  |  |  |  | -11.8072 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | 0.1196 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | -0.19707 | 148 | 148 |  |  | 17.7007 | 148 | 0.19707 | 29.166 |  |  |  |  | 0 | 29.166
7811 | L_RIONOG1G2Y | 2 | South | YES | 0.1196 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | -0.19707 | 148 | 148 |  |  | 17.7007 | 148 | 0.19707 | 29.166 |  |  |  |  | 0 | 29.166
7812 | L_RIONOG1G3Y | 3 | South | YES | 0.1196 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | -0.19707 | 154 | 154 |  |  | 18.4182 | 154 | 0.19707 | 30.3484 |  |  |  |  | 0 | 30.3484
7813 | L_RIONOG1S1Y | 4 | South | YES | 0.1196 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | -0.19707 | 293 | 293 |  |  | 35.0425 | 293 | 0.19707 | 57.7407 |  |  |  |  | 0 | 57.7407
1892 | DECRDOVA_2G | A | North | YES | -0.084646 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | -0.19759 | 70 | 70 | -5.9252 | 70 |  |  | -0.19759 | -13.8316 |  |  |  |  | -13.8316 | 0
1893 | DECRDOVA_3G | B | North | YES | -0.084646 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | -0.19759 | 69 | 69 | -5.8406 | 69 |  |  | -0.19759 | -13.634 |  |  |  |  | -13.634 | 0
1894 | DECRDOVA_4G | C | North | YES | -0.084646 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | -0.19759 | 69 | 69 | -5.8406 | 69 |  |  | -0.19759 | -13.634 |  |  |  |  | -13.634 | 0
1895 | DECRDOVA_5G | D | North | YES | -0.084646 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | -0.19759 | 68 | 68 | -5.7559 | 68 |  |  | -0.19759 | -13.4364 |  |  |  |  | -13.4364 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | 0.12024 | 0 | 0 | 6 |  | 1 | Hydro | -1 | -0.19771 | 0 | 0 |  |  | 0 | 0 | 0.19771 | 0 |  |  |  |  | 0 | 0
1941 | MDLTHELP_1G | 1 | North | YES | -0.086038 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | -0.19899 | 216.4 | 216.4 | -18.6186 | 216.4 |  |  | -0.19899 | -43.0607 |  |  |  |  | -43.0607 | 0
1942 | MDLTHELP_2G | 2 | North | YES | -0.086038 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | -0.19899 | 216.1 | 216.1 | -18.5928 | 216.1 |  |  | -0.19899 | -43.001 |  |  |  |  | -43.001 | 0
1938 | MDLTHELP_6G | 6 | North | YES | -0.08652 | 226 | 74 | 226 | 0 | 1 | CC | 1 | -0.19947 | 226 | 226 | -19.5535 | 226 |  |  | -0.19947 | -45.0799 |  |  |  |  | -45.0799 | 0
1937 | MDLTHELP_5G | 5 | North | YES | -0.08652 | 224 | 74 | 224 | 0 | 1 | CC | 1 | -0.19947 | 224 | 224 | -19.3805 | 224 |  |  | -0.19947 | -44.6809 |  |  |  |  | -44.6809 | 0
1943 | MDLTHELP_3G | 3 | North | YES | -0.08652 | 212 | 74 | 212 | 0 | 1 | CC | 1 | -0.19947 | 212 | 212 | -18.3422 | 212 |  |  | -0.19947 | -42.2873 |  |  |  |  | -42.2873 | 0
1944 | MDLTHELP_4G | 4 | North | YES | -0.08652 | 211 | 74 | 211 | 0 | 1 | CC | 1 | -0.19947 | 211 | 211 | -18.2557 | 211 |  |  | -0.19947 | -42.0878 |  |  |  |  | -42.0878 | 0
366 | JNSNCNTY802 | 1 | North | YES | -0.08714 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | -0.20009 | 0 | 0 | 0 | 0 |  |  | -0.20009 | 0 |  |  |  |  | 0 | 0
367 | JNSNCNTY802 | 2 | North | YES | -0.08714 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | -0.20009 | 0 | 0 | 0 | 0 |  |  | -0.20009 | 0 |  |  |  |  | 0 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | 0.12312 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | -0.20059 | 50 | 50 |  |  | 6.1559 | 50 | 0.20059 | 10.0293 |  |  |  |  | 0 | 10.0293
7303 | L_WPPGS12_1Y | 2 | South | YES | 0.12312 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | -0.20059 | 50 | 50 |  |  | 6.1559 | 50 | 0.20059 | 10.0293 |  |  |  |  | 0 | 10.0293
7305 | L_WPPGS34_1Y | 3 | South | YES | 0.12312 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | -0.20059 | 50 | 50 |  |  | 6.1559 | 50 | 0.20059 | 10.0293 |  |  |  |  | 0 | 10.0293
7305 | L_WPPGS34_1Y | 4 | South | YES | 0.12312 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | -0.20059 | 50 | 50 |  |  | 6.1559 | 50 | 0.20059 | 10.0293 |  |  |  |  | 0 | 10.0293
7014 | L_HAYSEN1_1Y | 1 | South | YES | 0.12425 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | -0.20172 | 223.9 | 223.9 |  |  | 27.8194 | 223.9 | 0.20172 | 45.1645 |  |  |  |  | 0 | 45.1645
7016 | L_HAYSEN1_3Y | 3 | South | YES | 0.12425 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | -0.20172 | 224.6 | 224.6 |  |  | 27.9063 | 224.6 | 0.20172 | 45.3057 |  |  |  |  | 0 | 45.3057
7015 | L_HAYSEN1_2Y | 2 | South | YES | 0.12425 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | -0.20172 | 225 | 225 |  |  | 27.956 | 225 | 0.20172 | 45.3864 |  |  |  |  | 0 | 45.3864
7017 | L_HAYSEN1_4Y | 4 | South | YES | 0.12425 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | -0.20172 | 226.7 | 226.7 |  |  | 28.1672 | 226.7 | 0.20172 | 45.7293 |  |  |  |  | 0 | 45.7293
7020 | L_AUSTPL1_1Y | 1 | South | YES | 0.12447 | 0 | 0 | 8 |  | 1 | Hydro | -1 | -0.20194 | 0 | 0 |  |  | 0 | 0 | 0.20194 | 0 |  |  |  |  | 0 | 0
7020 | L_AUSTPL1_1Y | 2 | South | YES | 0.12447 | 0 | 0 | 8 |  | 1 | Hydro | -1 | -0.20194 | 0 | 0 |  |  | 0 | 0 | 0.20194 | 0 |  |  |  |  | 0 | 0
9000 | DECKR_G1 | 1 | South | YES | 0.12759 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | -0.20506 | 321 | 321 |  |  | 40.9574 | 321 | 0.20506 | 65.8247 |  |  |  |  | 0 | 65.8247
9001 | DECKR_G2 | 2 | South | YES | 0.12759 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | -0.20506 | 426 | 426 |  |  | 54.3546 | 426 | 0.20506 | 87.3561 |  |  |  |  | 0 | 87.3561
7004 | L_SIMGID1_1Y | 1 | South | YES | 0.12828 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | -0.20575 | 132 | 132 |  |  | 16.9332 | 132 | 0.20575 | 27.159 |  |  |  |  | 0 | 27.159
7005 | L_SIMGID1_2Y | 2 | South | YES | 0.12828 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | -0.20575 | 139 | 139 |  |  | 17.8312 | 139 | 0.20575 | 28.5993 |  |  |  |  | 0 | 28.5993
7006 | L_SIMGID1_3Y | 3 | South | YES | 0.12828 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | -0.20575 | 329 | 329 |  |  | 42.2048 | 329 | 0.20575 | 67.6919 |  |  |  |  | 0 | 67.6919
9017 | SANDH_G2 | 2 | South | YES | 0.12871 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | -0.20618 | 46 | 46 |  |  | 5.9207 | 46 | 0.20618 | 9.4842 |  |  |  |  | 0 | 9.4842
9018 | SANDH_G3 | 3 | South | YES | 0.12871 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | -0.20618 | 46 | 46 |  |  | 5.9207 | 46 | 0.20618 | 9.4842 |  |  |  |  | 0 | 9.4842
9019 | SANDH_G4 | 4 | South | YES | 0.12871 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | -0.20618 | 47 | 47 |  |  | 6.0494 | 47 | 0.20618 | 9.6904 |  |  |  |  | 0 | 9.6904
9016 | SANDH_G1 | 1 | South | YES | 0.12871 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | -0.20618 | 49 | 49 |  |  | 6.3068 | 49 | 0.20618 | 10.1027 |  |  |  |  | 0 | 10.1027
9021 | SANDHG5C | 5C | South | YES | 0.12871 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | -0.20618 | 148 | 148 |  |  | 19.0491 | 148 | 0.20618 | 30.5144 |  |  |  |  | 0 | 30.5144
9020 | SANDHG5A | 5A | South | YES | 0.12871 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | -0.20618 | 155 | 155 |  |  | 19.9501 | 155 | 0.20618 | 31.9576 |  |  |  |  | 0 | 31.9576
9002 | DECKR_G3 | 3 | South | YES | 0.12965 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | -0.20712 | 42 | 42 |  |  | 5.4455 | 42 | 0.20712 | 8.6992 |  |  |  |  | 0 | 8.6992
9003 | DECKR_G4 | 4 | South | YES | 0.12965 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | -0.20712 | 44 | 44 |  |  | 5.7048 | 44 | 0.20712 | 9.1134 |  |  |  |  | 0 | 9.1134
9004 | DECKR_G5 | 5 | South | YES | 0.12965 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | -0.20712 | 44 | 44 |  |  | 5.7048 | 44 | 0.20712 | 9.1134 |  |  |  |  | 0 | 9.1134
9005 | DECKR_G6 | 6 | South | YES | 0.12965 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | -0.20712 | 47 | 47 |  |  | 6.0938 | 47 | 0.20712 | 9.7348 |  |  |  |  | 0 | 9.7348
7012 | L_FPPYD21_3Y | 3 | South | YES | 0.1304 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | -0.20787 | 0 | 436 |  |  | 0 | 0 | 0.20787 | 0 |  |  |  |  | 0 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | 0.13054 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | -0.20801 | 0 | 598 |  |  | 0 | 0 | 0.20801 | 0 |  |  |  |  | 0 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | 0.13054 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | -0.20801 | 0 | 606 |  |  | 0 | 0 | 0.20801 | 0 |  |  |  |  | 0 | 0
244 | WHITNYDM01 | 1 | North | YES | -0.10688 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | -0.21983 | 0 | 0 | 0 | 0 |  |  | -0.21983 | 0 |  |  |  |  | 0 | 0
245 | WHITNYDM02 | 2 | North | YES | -0.10688 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | -0.21983 | 0 | 0 | 0 | 0 |  |  | -0.21983 | 0 |  |  |  |  | 0 | 0
7808 | L_BASTEN1_2Y | 1 | South | YES | 0.14743 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | -0.2249 | 149.5 | 149.5 |  |  | 22.0412 | 149.5 | 0.2249 | 33.6228 |  |  |  |  | 0 | 33.6228
7807 | L_BASTEN1_1Y | 1 | South | YES | 0.14743 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | -0.2249 | 152.5 | 152.5 |  |  | 22.4835 | 152.5 | 0.2249 | 34.2975 |  |  |  |  | 0 | 34.2975
7809 | L_BASTEN1_3Y | 1 | South | YES | 0.14743 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | -0.2249 | 232.6 | 232.6 |  |  | 34.2929 | 232.6 | 0.2249 | 52.3121 |  |  |  |  | 0 | 52.3121
251 | BOSQUESW803 | 2 | North | YES | -0.11226 | 150 | 0 | 150 | 0 | 1.032 | CC | 1 | -0.22521 | 150 | 150 | -16.8392 | 150 |  |  | -0.22521 | -33.7814 |  |  |  |  | -33.7814 | 0
253 | BOSQUESW804 | 2 | North | YES | -0.11226 | 80 | 0 | 80 | 0 | 1.032 | CC | 1 | -0.22521 | 80 | 80 | -8.9809 | 80 |  |  | -0.22521 | -18.0168 |  |  |  |  | -18.0168 | 0
3432 | SANDOW_4G | 4 | South | YES | 0.14861 | 580 | 225 | 580 | 0 | 1.029 | LIGCO | -1 | -0.22608 | 0 | 580 |  |  | 0 | 0 | 0.22608 | 0 |  |  |  |  | 0 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | 0.14926 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | -0.22673 | 158 | 158 |  |  | 23.5828 | 158 | 0.22673 | 35.8228 |  |  |  |  | 0 | 35.8228
7008 | L_LOSTPI1_2Y | 2 | South | YES | 0.14926 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | -0.22673 | 160 | 160 |  |  | 23.8813 | 160 | 0.22673 | 36.2762 |  |  |  |  | 0 | 36.2762
7009 | L_LOSTPI1_3Y | 3 | South | YES | 0.14926 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | -0.22673 | 175 | 175 |  |  | 26.1201 | 175 | 0.22673 | 39.6771 |  |  |  |  | 0 | 39.6771
238 | BOSQUESW505 | 1 | North | YES | -0.12069 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | -0.23364 | 255 | 255 | -30.7767 | 255 |  |  | -0.23364 | -59.5786 |  |  |  |  | -59.5786 | 0
247 | BOSQUESW501 | 2 | North | YES | -0.12069 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | -0.23364 | 156 | 156 | -18.8281 | 156 |  |  | -0.23364 | -36.4481 |  |  |  |  | -36.4481 | 0
239 | BOSQUESW502 | 1 | North | YES | -0.12069 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | -0.23364 | 149 | 149 | -17.9833 | 149 |  |  | -0.23364 | -34.8126 |  |  |  |  | -34.8126 | 0
3417 | LAKE_CRK2_G | 2 | North | YES | -0.12298 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | -0.23593 | 222 | 222 | -27.3009 | 222 |  |  | -0.23593 | -52.3755 |  |  |  |  | -52.3755 | 0
3416 | LAKE_CRK1_G | 1 | North | YES | -0.12298 | 60 | 33 | 75 |  | 1.029 | GST | 1 | -0.23593 | 75 | 75 | -9.2233 | 75 |  |  | -0.23593 | -17.6944 |  |  |  |  | -17.6944 | 0
3404 | THOUSE_2G | 2 | North | YES | -0.12657 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | -0.23952 | 807 | 807 | -102.1396 | 807 |  |  | -0.23952 | -193.289 |  |  |  |  | -193.289 | 0
3403 | THOUSE_1G | 1 | North | YES | -0.12657 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | -0.23952 | 563 | 563 | -71.2572 | 563 |  |  | -0.23952 | -134.8472 |  |  |  |  | -134.8472 | 0
13432 | SANDOW_5G | 5 | South | YES | 0.19604 | 581 | 225 | 581 |  | 1.029 | LIGCO | -1 | -0.27351 | 0 | 581 |  |  | 0 | 0 | 0.27351 | 0 |  |  |  |  | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0
[26 empty] | 0 | 0

## Zones
Houston | -1
North | 1
South | -1
West | 1
SET UP AREA, copy & paste values to cell B1
Source | North |  | N to H | N to W | N to S | W to N | S to N | W to S
Sink | South | Houston | -1 | 1 | -1 | -1 | 1 | -1
|  | North | 1 | 1 | 1 | -1 | -1 | -1
|  | South | -1 | 1 | -1 | -1 | 1 | -1
|  | West | 1 | -1 | 1 | 1 | -1 | 1
|  | Source | North | North | North | West | South | West
|  | Sink | Houston | West | South | North | North | South

## Tech
Number of Bus | Name of Bus | Tech Type
238 | BOSQUESW505 | CC
239 | BOSQUESW502 | GGT
244 | WHITNYDM01 | Hydro
245 | WHITNYDM02 | Hydro
247 | BOSQUESW501 | GGT
251 | BOSQUESW803 | CC
253 | BOSQUESW804 | CC
332 | RWMILLER01 | GST
333 | RWMILLER02 | GST
334 | RWMILLER03 | GST
335 | RWMILLER04 | GST
336 | RWMILLER05 | GST
344 | MRSSHPRD | Hydro
345 | MRSSHPRD01 | Hydro
366 | JNSNCNTY802 | Cogen
367 | JNSNCNTY802 | Cogen
503 | NTHTEXAS01 | GST
504 | NTHTEXAS02 | GST
505 | NTHTEXAS03 | GST
580 | JCKCNTY801 | CC
581 | JCKCNTY802 | CC
582 | JCKCNTY803 | CC
728 | WOLFRIDGE801 | Wind
837 | NEWMAN_G5 | GST
842 | OLINGER_G1 | GST
843 | OLINGER_G2 | GST
844 | OLINGER_G3 | GST
845 | OLINGER_G4 | GGT
923 | SPENCER_G4 | GST
924 | SPENCER_G5 | GST
948 | STEAM1 | GST
949 | STEAM2 | GST
950 | STEAM3 | GST
990 | GIBN_CREK_G1 | LIGCO
1002 | PBCTAGE_1G | GGT
1003 | PBCTBGE_2G | GGT
1004 | PBCTCGE_3G | GGT
1005 | PBCTDGE_4G | GGT
1006 | PBCTEGE_5G | GGT
1007 | PB5GEN_6G | GST
1008 | PB6GEN_7G | GST
1037 | MORGAN5G_5G | GST
1039 | MRGNAG_1G | GGT
1040 | MRGNBG_2G | GGT
1041 | MRGNCG_3G | GGT
1042 | MRGNDG_4G | GGT
1043 | MRGNEG_5G | GGT
1044 | MRGNFG_6G | GGT
1045 | CALENG1G_1G | Cogen
1046 | CALENG2G_2G | Cogen
1047 | CALENG3G_3G | Cogen
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1061 | CIELOGEN_1G | Wind
1062 | CIELOGEN_2G | Wind
1068 | SCURRYCW_1G | Wind
1069 | KINDERMG_1G | Cogen
1070 | KINDERMG_2G | Cogen
1071 | KINDERMG_3G | Cogen
1073 | SCURRYCW_2G | Wind
1320 | BSP 1 | Cogen
1326 | STANTONW_8 | Wind
1327 | WILDHRSE_1G | Wind
1328 | OCOTILLO_1G | Wind
1333 | MCDDONAL_8 | Wind
1343 | TRENTIPP_8 | Wind
1349 | WESTXWIN_1G | Wind
1350 | NWPWRG1_1G | Wind
1354 | AEPWIND_8 | Wind
1360 | GUNSIGHT_8 | Wind
1416 | SWETWATR_1G | CC
1417 | SWETWATR_2G | CC
1418 | SWETWATR_3G | CC
1419 | SWETWATR_4G | CC
1432 | GRHAMSES_2G | GST
1433 | GRHAMSES_1G | GST
1437 | MESQUITW_1G | Wind
1438 | MESQUITW_2G | Wind
1442 | COKFIELD_5 | Wind
1453 | WCPWRCO_1G | CC
1454 | WCPWRCO_2G | CC
1455 | WCPWRCO_3G | CC
1479 | WFCOGEN_1G | Cogen
1479 | WFCOGEN_1G | Cogen
1482 | WFCOGEN_2G | Cogen
1482 | WFCOGEN_2G | Cogen
1600 | BARTNWND_1G | Wind
1643 | SLSTR1PP_1G | Wind
1675 | PEC_1G | Cogen
1676 | PEC_2G | Cogen
1677 | PEC_3G | Cogen
1678 | LAMARPWR_1G | CC
1679 | LAMARPWR_2G | CC
1680 | LAMARPWR_3G | CC
1681 | LAMARPWR_4G | CC
1682 | LAMARPWR_5G | CC
1683 | LAMARPWR_6G | CC
1687 | VALLEY_1G | GST
1688 | VALLEY_2G | GSC
1689 | VALLEY_3G | GST
1701 | MOSES_1G | LIGCO
1702 | MOSES_2G | LIGCO
1703 | MOSES_3G | LIGCO
1861 | EAGLEMNT_1G | GST
1862 | EAGLEMNT_2G | GST
1863 | EAGLEMNT_3G | GST
1877 | WLFHOLW_1G | CC
1878 | WLFHOLW_2G | CC
1879 | WLFHOLW_3G | CC
1889 | DECRDOVA_1G | GSC
1892 | DECRDOVA_2G | GGT
1893 | DECRDOVA_3G | GGT
1894 | DECRDOVA_4G | GGT
1895 | DECRDOVA_5G | GGT
1898 | COMCHEPK_1G | Nuc
1899 | COMCHEPK_2G | Nuc
1937 | MDLTHELP_5G | CC
1938 | MDLTHELP_6G | CC
1941 | MDLTHELP_1G | CC
1942 | MDLTHELP_2G | CC
1943 | MDLTHELP_3G | CC
1944 | MDLTHELP_4G | CC
1947 | HANDLEY_3G | GST
1948 | HANDLEY_4G | GST
1949 | HANDLEY_5G | GST
2371 | COLLIN_1G | GST
2381 | NTHLK1_G | GST
2382 | NTHLK2_G | GST
2383 | NTHLK3_G | GST
2413 | MTCK6_G | GST
2414 | MTCK7_G | GST
2417 | MTCK8_G | GSC
2451 | LKHB1_G | GST
2452 | LKHB2_G | GST
3097 | MARTLAKE_1G | LIGCO
3098 | MARTLAKE_2G | LIGCO
3099 | MARTLAKE_3G | LIGCO
3107 | STRYKER_1G | GST
3108 | STRYKER_2G | GST
3126 | TRINIDAD_6G | GST
3309 | ASPN_G | Bio
3348 | CHAMPION_1G | Cogen
3381 | BBRN_1G | LIGCO
3382 | BBRN_2G | LIGCO
3403 | THOUSE_1G | GSC
3404 | THOUSE_2G | GSC
3416 | LAKE_CRK1_G | GST
3417 | LAKE_CRK2_G | GST
3432 | SANDOW_4G | LIGCO
5026 | BRAUNIG_VHB1 | GST
5027 | BRAUNIG_VHB2 | GST
5028 | BRAUNIG_VHB3 | GST
5111 | CALAVER_JTD1 | LIGCO
5112 | CALAVER_JTD2 | LIGCO
5264 | LEON_LCP3G3 | GST
5265 | LEON_LCP4G4 | GST
5266 | LEON_LCPCT1 | GGT
5267 | LEON_LCPCT2 | GGT
5268 | LEON_LCPCT3 | GGT
5269 | LEON_LCPCT4 | GGT
5396 | CALAVER_OWS1 | GST
5397 | CALAVER_OWS2 | GST
5401 | CALAVER_JKS1 | LIGCO
5436 | TUTTL_WBT1G1 | GST
5438 | TUTTL_WBT3G3 | GST
5439 | TUTTL_WBT4G4 | GST
5476 | BRA_AVR1_CT1 | CC
5477 | BRA_AVR1_ST | CC
5478 | BRA_AVR1_CT2 | CC
5503 | RAYBURNGEN3 | GST
5505 | RAYBURNGEN1 | GGT
5506 | RAYBURNGEN2 | GGT
5508 | RAYBURNCC9 | CC
5509 | RAYBURNCC10 | CC
5511 | RAYBURNCC7 | CC
5512 | RAYBURNCC8 | CC
5728 | FALCONHYDRO2 | Hydro
5729 | FALCONHYDRO3 | Hydro
5890 | PEARSALLGEN1 | GST
5891 | PEARSALLGEN2 | GST
5892 | PEARSALLGEN3 | GST
5903 | SANMIGUELGEN | LIGCO
5911 | STP_GN1___1 | Nuc
5912 | STP_GN2___2 | Nuc
5920 | WELSHDC1 | DCTie
5925 | DCEAST | DCTie
5932 | SI_RAY9 | CC
5933 | SI_RAY6 | GST
5934 | SI_RAY5 | GST
5935 | SI_RAY10 | CC
6016 | SWMESA | Wind
6096 | NORTHDC7 | DCTie
6100 | OKLA7A | DCTie
6144 | MCADOO1A | Wind
6407 | TURKTRAK1A | Wind
6637 | SNYDERW1A | Wind
6752 | OKLA0A | LIGCO
6948 | DENISNDM | Hydro
6948 | DENISNDM | Hydro
7000 | L_FERGUS1_1Y | GSC
7004 | L_SIMGID1_1Y | GST
7005 | L_SIMGID1_2Y | GST
7006 | L_SIMGID1_3Y | GST
7007 | L_LOSTPI1_1Y | CC
7008 | L_LOSTPI1_2Y | CC
7009 | L_LOSTPI1_3Y | CC
7010 | L_FPPYD11_1Y | LIGCO
7011 | L_FPPYD11_2Y | LIGCO
7012 | L_FPPYD21_3Y | LIGCO
7014 | L_HAYSEN1_1Y | CC
7015 | L_HAYSEN1_2Y | CC
7016 | L_HAYSEN1_3Y | CC
7017 | L_HAYSEN1_4Y | CC
7020 | L_AUSTPL1_1Y | Hydro
7020 | L_AUSTPL1_1Y | Hydro
7022 | L_BUCHAN1_1Y | Hydro
7023 | L_BUCHAN1_2Y | Hydro
7024 | L_BUCHAN1_3Y | Hydro
7026 | L_INKSDA1_1Y | Hydro
7028 | L_MARBFA1_1Y | Hydro
7029 | L_MARBFA1_2Y | Hydro
7031 | L_MARSFO1G1Y | Hydro
7032 | L_MARSFO1G2Y | Hydro
7033 | L_MARSFO1G3Y | Hydro
7035 | L_WIRTZ_1G1Y | Hydro
7036 | L_WIRTZ_1G2Y | Hydro
7038 | L_DELAWA1_1Y | Wind
7038 | L_DELAWA1_1Y | Wind
7303 | L_WPPGS12_1Y | GGT
7303 | L_WPPGS12_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7487 | L_CANYHY8_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7609 | L_SCHUMA8_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7800 | L_GUADGE1_1Y | CC
7801 | L_GUADGE1_2Y | CC
7802 | L_GUADGE1_3Y | CC
7803 | L_GUADGE1_4Y | CC
7804 | L_GUADGE1_5Y | CC
7805 | L_GUADGE1_6Y | CC
7807 | L_BASTEN1_1Y | CC
7808 | L_BASTEN1_2Y | CC
7809 | L_BASTEN1_3Y | CC
7810 | L_RIONOG1G1Y | CC
7811 | L_RIONOG1G2Y | CC
7812 | L_RIONOG1G3Y | CC
7813 | L_RIONOG1S1Y | CC
8032 | AMISTADHYD1 | Hydro
8033 | AMISTADHYD2 | Hydro
8048 | FALCONHYDRO1 | Hydro
8066 | DUP1V#1 | Cogen
8134 | FOR #1 | Cogen
8138 | FOR #2 | Cogen
8139 | JOS #1 | GST
8147 | UCAR #2 | Cogen
8148 | UCAR #1 | Cogen
8153 | FOR #3 | Cogen
8154 | FOR #4 | Cogen
8155 | FOR #5 | Cogen
8156 | FOR #6 | Cogen
8157 | FOR #7 | Cogen
8161 | COLETO0A | LIGCO
8173 | VICEC51A | CC
8174 | VICEC61A | CC
8189 | CUECPL2A | Cogen
8262 | ELPS | Hydro
8285 | LAR #1 | GST
8287 | LAR #2 | GST
8288 | LAR #3 | GST
8388 | BATES0A | GST
8393 | BATES0B | GST
8437 | NUECES_B0C | GST
8438 | NUECES_B0B | GST
8442 | NBEC7 | GST
8442 | NBEC7 | GST
8456 | COSW#1 | Cogen
8457 | COSW#2 | Cogen
8459 | B_DAVIS0B | GSC
8460 | B_DAVIS0A | GSC
8461 | KOCH_UP0A | Cogen
8506 | VAL #1 | Cogen
8507 | VAL #2 | Cogen
8511 | OXY_CC0A | Cogen
8517 | CELANEBI0A | Cogen
8560 | CNOPGT1 | Cogen
8561 | CNOPGT2 | Cogen
8562 | CNOPST1 | Cogen
8926 | LGE_GT10A | Cogen
8927 | LGE_GT20A | Cogen
8928 | LGE_STG0A | Cogen
8930 | ICPGN10A | Cogen
8931 | ICPGN20A | Cogen
8932 | ICPGN30A | Cogen
8933 | FGNTS001 | CC
8934 | FGNTS101 | CC
8935 | FGNTS201 | CC
8936 | MVGN#1 | CC
8937 | MVGN#2 | CC
8938 | MVGN#3 | CC
8981 | HECN1 | CC
8982 | HECN2 | CC
8983 | HECN3 | CC
9000 | DECKR_G1 | GST
9001 | DECKR_G2 | GST
9002 | DECKR_G3 | GGT
9003 | DECKR_G4 | GGT
9004 | DECKR_G5 | GGT
9005 | DECKR_G6 | GGT
9016 | SANDH_G1 | GGT
9017 | SANDH_G2 | GGT
9018 | SANDH_G3 | GGT
9019 | SANDH_G4 | GGT
9020 | SANDHG5A | CC
9021 | SANDHG5C | CC
11001 | NAV1CT | CC
11009 | NAV2CT | CC
11011 | NAV3ST | CC
11012 | NAV4CT | CC
11013 | NAV5CT | CC
11014 | NAV6ST | CC
11020 | TIEHVSG_1G | CC
11021 | TIEHVCG_1G | CC
11022 | TIEHVCG_2G | CC
11023 | TIEHVCG_3G | CC
11024 | TIEHVCG_4G | CC
11025 | TIEHVSG_2G | CC
11056 | ROSCOE_1G | Wind
11057 | CHAMPION_1G | Wind
11058 | PYRON_1G | Wind
11059 | INADALE_1G | Wind
11065 | ELBOWCK_1G | Wind
11147 | NOTREES_1G | Wind
11309 | BULLCREK_2G | Wind
11310 | BULLCREK_1G | Wind
11320 | COYOTE_1G | Wind
11691 | KMICHICT1_G | CC
11692 | KMICHICT2_G | CC
11693 | KMICHIST3_G | CC
11694 | KMICHICT4_G | CC
11695 | KMICHICT5_G | CC
11696 | KMICHIST6_G | CC
12322 | ENNSTRAC_1G | CC
12323 | ENNSTRAC_2G | CC
12411 | FPLEFR1A_G | CC
12412 | FPLEFR1B_G | CC
12413 | FPLEFR1C_G | CC
12414 | FPLEFR1S_G | CC
12421 | FPLEFR2A_G | CC
12422 | FPLEFR2B_G | CC
12423 | FPLEFR2C_G | CC
12424 | FPLEFR2S_G | CC
12440 | PARKD_1SVC8 | GST
12449 | PARKD_2SVC8 | GST
13116 | TGATEWAY_1G | CC
13117 | TGATEWAY_2G | CC
13118 | TGATEWAY_3G | CC
13119 | TGATEWAY_4G | CC
13131 | CALFREST_1G | CC
13132 | CALFREST_2G | CC
13133 | CALFREST_3G | CC
13134 | CALFREST_4G | CC
13135 | CALFREST_5G | CC
13136 | CALFREST_6G | CC
13432 | SANDOW_5G | LIGCO
32798 | BRYN_TAMUGEN | GST
32883 | BRYN_DNSBY3 | GST
32884 | BRYN_DNSBY13 | GST
32886 | BRYN_ATKINS3 | GST
32887 | BRYN_ATKINS6 | GST
32888 | BRYN_ATKINS7 | GGT
32890 | BRYN_ATKINS4 | GST
32891 | BRYN_ATKINS5 | GST
32892 | BRYN_DNSBY14 | GST
36998 | RDCNYNG1 | Wind
38332 | TNWDWRDU2_8 | Wind
38437 | TNSRBNMESA9 | Wind
38580 | TNBP_CGN1_8 | Cogen
38590 | TNBP_CGN2_8 | Cogen
38600 | TNBP_CGN3_8 | Cogen
38611 | TNBPAMCG1_8 | Cogen
38612 | TNBPAMCG2_8 | Cogen
38613 | TNBPAMCG3_8 | Cogen
38614 | TNBPAMCG4_8 | Cogen
38615 | TNBPAMCG5_8 | Cogen
38690 | TNBP_CGN4_8 | Cogen
38711 | TNTXCTY1CG8 | Cogen
38712 | TNTXCTY2CG8 | Cogen
38713 | TNTXCTY3CG8 | Cogen
38714 | TNTXCTY4CG8 | Cogen
39190 | TNSLCGN1__8 | Cogen
39470 | TNDOWCGNSG8 | Cogen
39480 | TNDOWCGNGG8 | Cogen
39760 | TNSCLP1___8 | Cogen
39770 | TNSCLP2___8 | Cogen
39775 | TNSCLP4___8 | Cogen
39790 | TNSCLP3___8 | Cogen
39960 | TNTNPONE_18 | LIGCO
39970 | TNTNPONE_28 | LIGCO
48500 | APD_GT1_8005 | Cogen
48510 | AK_GT1__8040 | Cogen
48511 | LPE_GT1_8070 | GGT
48512 | LPE_GT2_8075 | GGT
48513 | LPE_GT3_8080 | GGT
48514 | LPE_GT4_8085 | GGT
48520 | BSF_GT1_8070 | Cogen
48520 | BSF_GT1_8070 | Cogen
48521 | BVE_GT1_GT1 | CC
48522 | BVE_GT2_5035 | CC
48523 | BVE_ST1_GN1 | CC
48531 | BYU_GT1_8075 | Cogen
48532 | BYU_GT2_8055 | Cogen
48533 | BYU_GT3_8060 | Cogen
48534 | BYU_GT4_8065 | Cogen
48551 | CAL_GT1_8045 | Cogen
48552 | CAL_ST1_8000 | Cogen
48561 | CTL_GT2_8130 | Cogen
48562 | CTL_GT3_8135 | Cogen
48563 | CTL_GT4_8140 | Cogen
48564 | CTL_GN1_8145 | Cogen
48565 | CTL_GN2_8155 | Cogen
48581 | CBY_GN1_1 | GSC
48582 | CBY_GN2_2 | GSC
48583 | CBY_GT4_1 | GSC
48584 | CBY_GT4_2 | CC
48585 | CBY_ST4_1 | CC
48591 | CHE_GT2_5030 | Cogen
48593 | CHE_GT1_8015 | Cogen
48594 | CHE_GN4_8025 | Cogen
48595 | BTE_GT2_8075 | CC
48596 | BTE_GT3_8045 | CC
48597 | BTE_GT4_8055 | CC
48598 | BTE_ST1_8070 | CC
48611 | DIB_GT1_8080 | Cogen
48612 | DIB_GT2_8075 | Cogen
48613 | DIB_ST1_8085 | Cogen
48614 | DIB_GT3_8090 | Cogen
48641 | DPEC_GT15040 | CC
48642 | DPEC_GT25025 | CC
48643 | DPEC_GT35010 | CC
48644 | DPEC_GT45070 | CC
48645 | DPEC_ST55065 | CC
48651 | EP_1_2 | Cogen
48651 | EP_1_2 | Cogen
48671 | FTR_GT1_5105 | CC
48672 | FTR_GT2_5110 | CC
48673 | FTR_GT3_5085 | CC
48674 | FTR_CN4_5095 | CC
48690 | GBY_GN5_5 | GSC
48691 | GBY_73741085 | GGT
48691 | GBY_73741085 | GGT
48692 | GBY_81821075 | GGT
48692 | GBY_81821075 | GGT
48693 | GBY_83841065 | GGT
48693 | GBY_83841065 | GGT
48721 | LEG_1___1 | LIGCO
48722 | LEG_2___2 | LIGCO
48730 | MNS_GT | Cogen
48731 | CBE_GT1 | CC
48732 | CBE_GT2 | CC
48733 | CBE_ST12 | CC
48734 | CBE_GT3 | CC
48735 | CBE_GT4 | CC
48736 | CBE_ST34 | CC
48740 | PSG_GN2_8050 | Cogen
48741 | PSG_GT2_8040 | Cogen
48742 | PSG_GT3_8060 | Cogen
48761 | PR_GT1__9040 | Cogen
48772 | PHR_GN2_2 | GSC
48791 | PSA_GT1_8160 | Cogen
48792 | PSA_GT2_8155 | Cogen
48793 | PSA_GT3_8150 | Cogen
48794 | PSA_GT4_8145 | Cogen
48795 | PSA_GT5_8140 | Cogen
48796 | PSA_GN1_8165 | Cogen
48797 | PSA_GT6_8135 | Cogen
48811 | CVC_GT3_5045 | Cogen
48812 | CVC_GT2_5020 | Cogen
48813 | CVC_GT1_5035 | Cogen
48814 | CVC_ST5_5040 | Cogen
48815 | CVC_GT4_8005 | Cogen
48820 | SHELLG1_3015 | Cogen
48821 | SHELLG2 | Cogen
48822 | SHELLG3_3020 | Cogen
48822 | SHELLG3_3020 | Cogen
48841 | SJS_GT1_GT1 | Cogen
48842 | SJS_GT2_GT2 | Cogen
48845 | SOL_GT1 | Solar
48851 | SRB_GN1_1 | GST
48852 | SRB_GN2_2 | GST
48853 | SRB_GN3_3 | GST
48854 | SRB_GN4_4 | GST
48855 | SRB_GT211035 | GGT
48855 | SRB_GT211035 | GGT
48873 | THW_ST3_ST_3 | CC
48874 | THW_ST4_ST_4 | CC
48875 | THW_3132 | CC
48875 | THW_3132 | CC
48877 | THW_3334 | CC
48877 | THW_3334 | CC
48879 | THW_4142 | CC
48879 | THW_4142 | CC
48881 | THW_4344 | CC
48881 | THW_4344 | CC
48883 | THW_GT1_GT_1 | GGT
48885 | THW_5152 | GGT
48885 | THW_5152 | GGT
48886 | THW_5354 | GGT
48886 | THW_5354 | GGT
48887 | THW_5556 | GGT
48887 | THW_5556 | GGT
48911 | TGF_GT1_8000 | Cogen
48921 | WAP_GN1_1 | GST
48922 | WAP_GN2_2 | GST
48923 | WAP_GN3_3 | GST
48924 | WAP_GN4_4 | GSC
48925 | WAP_GN5_5 | LIGCO
48926 | WAP_GN6_6 | LIGCO
48927 | WAP_GN7_7 | LIGCO
48928 | WAP_GN8_8 | LIGCO
48929 | WAPGT21_GT1 | GGT
48940 | WARVUE_GT1 | Cogen
49803 | EXN_15GT | Cogen
49804 | EXN_16GT | Cogen
49805 | EXN_17GT | Cogen
49826 | EXN938GT | Cogen
49828 | EXN941GT | Cogen
49829 | EXN942GT | Cogen
49830 | EXN943GT | Cogen
49831 | EXN944GT | Cogen
49832 | EXN945GT | Cogen
49837 | EXN_GT | Cogen
49838 | EXN_14GT | Cogen
49851 | DOW17000 | Cogen
49858 | DOW38100 | Cogen
49859 | DOW38200 | Cogen
49860 | DOW38300 | Cogen
49862 | DOW39100 | Cogen
49863 | DOW39200 | Cogen
49865 | DOW41000 | Cogen
49866 | DOW42000 | Cogen
49869 | DOW49000 | Cogen
49870 | DOW61000 | Cogen
49871 | DOW62000 | Cogen
49872 | DOW63000 | Cogen
49873 | DOW64000 | Cogen
49876 | DOW65000 | Cogen
49877 | DOW66000 | Cogen
49878 | DOW67000 | Cogen
49882 | DOW81000 | Cogen
49884 | DOW82000 | Cogen
49885 | DOW83000 | Cogen
49886 | DOW84000 | Cogen
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58909 | PEARSALLSCG1 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58919 | PEARSALLSCG2 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58929 | PEARSALLSCG3 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
58949 | PEARSALLSCG4 | Diesel
60000 | DSKY2 | Wind
60003 | KING_NE1A | Wind
60005 | KING_SE1A | Wind
60007 | KING_SW1A | Wind
60016 | WOODWRD11A | Wind
60017 | ORNNWP1 | Wind
60018 | DSKY1 | Wind
60019 | KING_NW1A | Wind
60057 | CALLAHAN1A | Wind
60058 | BUFF_GAP1A | Wind
60060 | CIRELLO | Wind
60063 | BUFF_GAP1B | Wind
60066 | H_HOLLOW1A | Wind
60068 | HHOLLOW21A | Wind
60070 | HHOLLOW31A | Wind
60072 | HHOLLOW41A | Wind
60081 | WHRLWIND1A | Wind
60201 | RIO DRCS | AVR
60202 | FRNDDRCS | AVR
71051 | L_BITTCR1_1N | Wind
71054 | L_SWEETW1_1N | Wind
71057 | L_SWEETW1_2N | Wind
71059 | L_SWEETW1_3N | Wind
71060 | L_SWEETW1_4N | Wind
71061 | L_SWEETW1_5N | Wind
76031 | L_GASCCR1_1N | Wind
76091 | L_DIVIDE1_1N | Wind
76095 | L_CAPRSI1_1N | Wind
76096 | L_CAPRSI1_2N | Wind
76097 | L_CAPRGE1_1N | Wind
80003 | MILHWYS | AVR
80012 | LAR | DCTie
80051 | FOR #8 | Cogen
80052 | FOR #9 | Cogen
80053 | FOR #10 | Cogen
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80137 | CSDR89 | DCTie
80137 | CSDR89 | DCTie
80138 | CSDR7 | DCTie
80139 | CSDR56 | DCTie
80139 | CSDR56 | DCTie
80140 | CSDR11 | DCTie
80180 | PNSCALT11A | Wind
80180 | PNSCALT11A | Wind
80181 | PNSCALT21A | Wind
80181 | PNSCALT21A | Wind
80223 | REYSHR G | Cogen
80224 | VISTRONG1 | Cogen
80225 | VISTRONG2 | Cogen
80226 | ALCOA G | Cogen
80227 | AIRCO G | Cogen
80263 | B_DAVIS31A | CC
80264 | B_DAVIS41A | CC
80265 | LARECU40A | GGT
80266 | LARECU50A | GGT
86104 | CID-138 | DCTie
86105 | CID-230 | DCTie
86106 | CUF-230 | DCTie
86107 | CUF-138 | DCTie
88198 | BEEVILLE | AVR
88253 | HAMILTON | BLT
88299 | ZAPATA | BLT
88508 | FALFURRI | AVR