## Set up
Step 1 | Go to the Zones worksheet in this workbook. Make sure that the source and sink zones are set correctly and the "1"s and "-1"s are correct |  |  |  | Summary of Key Data points | Value
[5 empty] | File Description: Cont_ Lake to Tradinghouse and TemplePEC to Tradinghouse OL_ TempleSS to LakeCreek | Cont_ Lake to Tradinghouse and TemplePEC to Tradinghouse OL_ TempleSS to LakeCreek
Step 2 | Open Dennis' file that needs to have the data transferred, same file that is listed in cell K29 |  |  |  | Number of units | 624
[5 empty] | Dec Concentrated Generation | 2227
Step 3 | Copy columns J:X from an old Dennis' Sheet to the new sheet (if first round of a new alaysis) |  |  |  | Dec Line weighted impact | 940.5633
[5 empty] | Dec PTDF | 0.42235
Step 4 | Mark the contingencies and monitored element set by a "y" in column K of Dennis' sheet, if there are a match on the filename use something to make unique |  |  |  | Dec Concentration | 1.4046
[5 empty] | Inc Concentrated Generation | 2294.6
Step 5 | Enter Dennis' file name into cell K29 |  |  |  | Inc Line weighted impact | 768.9243
[5 empty] | Inc PTDF | 0.3351
Step 6 | click the step one button |  |  |  | Inc Concentartion | 1.1145
[5 empty] | Source Zonal weighted AWGSF | 0.13196
Step 7 | Enter the line ratings in Dennis' workbook, the Input worksheet, in the cells |  |  |  | Sink Zonal weighted AWGSF | -0.16872
| X6:X30, or to the end of the selected list. |  |  |  | Source - Sink PTDF | 0.30068
[5 empty] | OL Line Rating (MW) | 1072
Step 8 | Check to see that the number of generators in Dennis' file matches the length |  |  |  | Source Zone (diagnostic) | North
| of the formulas in columns L:X (Distributed Slack - Dec) have been copied through to the apporpriate number of rows |  |  |  | Sink Zone (diagnostic) | South
If Dennis' sheet data is less than this file then clear any old unit data in columns A:K of this workbook to match the correct length
Clear any old data that will be below the new data iin the "Distributed Slack - Inc" worksheet, as well
Step 9 | Click the step 2 button
The last file saved will still be open, you will need to close this file.
This Template sheet will no longer be open.
|  | Current Source Zone | North
|  | Current Sink Zone | South | NS_062609automation.xls
The file listed in cell K29 needs to be in the same folder as this template file
Copy Dennis' data step 1
Copy Dennis' Data Step 2

## Distributed Slack - Dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Concentrated Capacity | Cumulative Concentrated Impact | Cont_ Lake to Tradinghouse and TemplePEC to Tradinghouse OL_ TempleSS to LakeCreek
3403 | THOUSE_1G | 1 | North | YES | 0.27281 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.44153 | 563 | 563 | 153.5948 | 563 |  |  | 0.44153 | 248.5826 | 563 | 248.5826
3404 | THOUSE_2G | 2 | North | YES | 0.27281 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.44153 | 807 | 807 | 220.1617 | 807 |  |  | 0.44153 | 356.3164 | 1370 | 604.899 |  |  |  | 624
238 | BOSQUESW505 | 1 | North | YES | 0.22303 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.39175 | 255 | 255 | 56.8721 | 255 |  |  | 0.39175 | 99.895 | 1625 | 704.794
239 | BOSQUESW502 | 1 | North | YES | 0.22303 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.39175 | 149 | 149 | 33.2312 | 149 |  |  | 0.39175 | 58.37 | 1774 | 763.164 | Weighted Shift Factors |  | chk
247 | BOSQUESW501 | 2 | North | YES | 0.22303 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.39175 | 156 | 156 | 34.7924 | 156 |  |  | 0.39175 | 61.1122 | 1930 | 824.2762 | North | 0.13196 | 0.13196
3416 | LAKE_CRK1_G | 1 | North | YES | 0.22282 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.39154 | 75 | 75 | 16.7116 | 75 |  |  | 0.39154 | 29.3654 | 2005 | 853.6416 | South | -0.16872 | -0.16872
3417 | LAKE_CRK2_G | 2 | North | YES | 0.22282 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.39154 | 222 | 222 | 49.4665 | 222 |  |  | 0.39154 | 86.9217 | 2227 | 940.5633 |  | 0.30068 | 0.30068
251 | BOSQUESW803 | 2 | North | YES | 0.18858 | 150 | 0 | 150 |  | 1.032 | CC | 1 | 0.3573 | 150 | 150 | 28.2873 | 150 |  |  | 0.3573 | 53.5949
253 | BOSQUESW804 | 2 | North | YES | 0.18858 | 80 | 0 | 80 |  | 1.032 | CC | 1 | 0.3573 | 80 | 80 | 15.0866 | 80 |  |  | 0.3573 | 28.5839 |  |  | Line Cap | 1072
244 | WHITNYDM01 | 1 | North | YES | 0.17974 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.34846 | 0 | 0 | 0 | 0 |  |  | 0.34846 | 0 |  |  | Conc Gen | 2227
245 | WHITNYDM02 | 2 | North | YES | 0.17974 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.34846 | 0 | 0 | 0 | 0 |  |  | 0.34846 | 0 |  |  | Weighted Imp. | 940.5633
1937 | MDLTHELP_5G | 5 | North | YES | 0.15473 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.32344 | 224 | 224 | 34.6584 | 224 |  |  | 0.32344 | 72.451 |  |  | PTDF | 0.42235
1938 | MDLTHELP_6G | 6 | North | YES | 0.15473 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.32344 | 226 | 226 | 34.9678 | 226 |  |  | 0.32344 | 73.0979
1943 | MDLTHELP_3G | 3 | North | YES | 0.15473 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.32344 | 212 | 212 | 32.8017 | 212 |  |  | 0.32344 | 68.5697 |  |  | Concentration | 1.4046
1944 | MDLTHELP_4G | 4 | North | YES | 0.15473 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.32344 | 211 | 211 | 32.647 | 211 |  |  | 0.32344 | 68.2463
1941 | MDLTHELP_1G | 1 | North | YES | 0.15413 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.32284 | 216.4 | 216.4 | 33.3531 | 216.4 |  |  | 0.32284 | 69.8635 |  |  |  | Pass
1942 | MDLTHELP_2G | 2 | North | YES | 0.15413 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.32284 | 216.1 | 216.1 | 33.3068 | 216.1 |  |  | 0.32284 | 69.7666
366 | JNSNCNTY802 | 1 | North | YES | 0.151 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.31972 | 0 | 0 | 0 | 0 |  |  | 0.31972 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.151 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.31972 | 0 | 0 | 0 | 0 |  |  | 0.31972 | 0
1892 | DECRDOVA_2G | A | North | YES | 0.14558 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.3143 | 70 | 70 | 10.191 | 70 |  |  | 0.3143 | 22.0011
1893 | DECRDOVA_3G | B | North | YES | 0.14558 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.3143 | 69 | 69 | 10.0454 | 69 |  |  | 0.3143 | 21.6868
1894 | DECRDOVA_4G | C | North | YES | 0.14558 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.3143 | 69 | 69 | 10.0454 | 69 |  |  | 0.3143 | 21.6868
1895 | DECRDOVA_5G | D | North | YES | 0.14558 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.3143 | 68 | 68 | 9.8998 | 68 |  |  | 0.3143 | 21.3725
1947 | HANDLEY_3G | 3 | North | YES | 0.14541 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.31413 | 395 | 395 | 57.4366 | 395 |  |  | 0.31413 | 124.0798
1949 | HANDLEY_5G | 5 | North | YES | 0.14541 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.31413 | 435 | 435 | 63.2529 | 435 |  |  | 0.31413 | 136.6448
1948 | HANDLEY_4G | 4 | North | YES | 0.14502 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.31374 | 435 | 435 | 63.0828 | 435 |  |  | 0.31374 | 136.4748
1945 | HANDLEY_1G | MB | North | YES | 0.1448 | 0 | 25 | 36 |  | 0.986 | GST | 1 | 0.31352 | 0 | 0 | 0 | 0 |  |  | 0.31352 | 0
1946 | HANDLEY_2G | MB | North | YES | 0.1448 | 0 | 30 | 68 |  | 0.986 | GST | 1 | 0.31352 | 0 | 0 | 0 | 0 |  |  | 0.31352 | 0
1889 | DECRDOVA_1G | 1 | North | YES | 0.14452 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.31324 | 779 | 779 | 112.5842 | 779 |  |  | 0.31324 | 244.0148
1877 | WLFHOLW_1G | 1 | North | YES | 0.14409 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.3128 | 217.3 | 217.3 | 31.3101 | 217.3 |  |  | 0.3128 | 67.9723
1878 | WLFHOLW_2G | 2 | North | YES | 0.14409 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.3128 | 215.7 | 215.7 | 31.0796 | 215.7 |  |  | 0.3128 | 67.4718
1879 | WLFHOLW_3G | 3 | North | YES | 0.14409 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.3128 | 272.4 | 272.4 | 39.2493 | 272.4 |  |  | 0.3128 | 85.2078
1898 | COMCHEPK_1G | 1 | North | YES | 0.14351 | 1159 | 1150 | 1159 | 0 | 1.032 | Nuc | 1 | 0.31223 | 0 | 0 | 0 | 0 |  |  | 0.31223 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.14351 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.31223 | 0 | 0 | 0 | 0 |  |  | 0.31223 | 0
1861 | EAGLEMNT_1G | MB | North | YES | 0.14196 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.31068 | 0 | 0 | 0 | 0 |  |  | 0.31068 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.14196 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.31068 | 0 | 0 | 0 | 0 |  |  | 0.31068 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.14196 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.31068 | 0 | 0 | 0 | 0 |  |  | 0.31068 | 0
332 | RWMILLER01 | 1 | North | YES | 0.14145 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.31017 | 73 | 73 | 10.3262 | 73 |  |  | 0.31017 | 22.6426
333 | RWMILLER02 | 2 | North | YES | 0.14145 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.31017 | 119 | 119 | 16.8331 | 119 |  |  | 0.31017 | 36.9105
334 | RWMILLER03 | 3 | North | YES | 0.14145 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.31017 | 208 | 208 | 29.4226 | 208 |  |  | 0.31017 | 64.5158
335 | RWMILLER04 | 4 | North | YES | 0.14145 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.31017 | 102 | 102 | 14.4284 | 102 |  |  | 0.31017 | 31.6376
336 | RWMILLER05 | 5 | North | YES | 0.14145 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.31017 | 101 | 101 | 14.287 | 101 |  |  | 0.31017 | 31.3274
503 | NTHTEXAS01 | 1 | North | YES | 0.14047 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.30918 | 18 | 18 | 2.5284 | 18 |  |  | 0.30918 | 5.5653
504 | NTHTEXAS02 | 2 | North | YES | 0.14047 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.30918 | 18 | 18 | 2.5284 | 18 |  |  | 0.30918 | 5.5653
505 | NTHTEXAS03 | 3 | North | YES | 0.14047 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.30918 | 38 | 38 | 5.3377 | 38 |  |  | 0.30918 | 11.749
580 | JCKCNTY801 | 1 | North | YES | 0.13977 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.30849 | 288 | 288 | 40.2538 | 288 |  |  | 0.30849 | 88.8443
581 | JCKCNTY802 | 2 | North | YES | 0.13977 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.30849 | 147 | 147 | 20.5462 | 147 |  |  | 0.30849 | 45.3476
582 | JCKCNTY803 | 3 | North | YES | 0.13977 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.30849 | 147 | 147 | 20.5462 | 147 |  |  | 0.30849 | 45.3476
12322 | ENNSTRAC_1G | 1 | North | YES | 0.13873 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.30745 | 196 | 196 | 27.1911 | 196 |  |  | 0.30745 | 60.2596
12323 | ENNSTRAC_2G | 2 | North | YES | 0.13873 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.30745 | 116 | 116 | 16.0927 | 116 |  |  | 0.30745 | 35.6639
2418 | MTCK2_G | 2 | North | YES | 0.1386 | 0 | 10 | 23 |  | 0.971 | GSC | 1 | 0.30731 | 23 | 23 | 3.1877 | 23 |  |  | 0.30731 | 7.0682
2419 | MTCK3_G | MB | North | YES | 0.1386 | 0 | 10 | 63 |  | 0.971 | GSC | 1 | 0.30731 | 0 | 0 | 0 | 0 |  |  | 0.30731 | 0
923 | SPENCER_G4 | 1 | North | YES | 0.13832 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.30704 | 61 | 61 | 8.4375 | 61 |  |  | 0.30704 | 18.7292
924 | SPENCER_G5 | 1 | North | YES | 0.13832 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.30704 | 66 | 66 | 9.1291 | 66 |  |  | 0.30704 | 20.2644
1453 | WCPWRCO_1G | 1 | North | YES | 0.13828 | 204 | 50 | 204 |  | 1.02 | CC | 1 | 0.307 | 204 | 204 | 28.2095 | 204 |  |  | 0.307 | 62.6278
1454 | WCPWRCO_2G | 2 | North | YES | 0.13828 | 204 | 50 | 204 |  | 1.02 | CC | 1 | 0.307 | 204 | 204 | 28.2095 | 204 |  |  | 0.307 | 62.6278
1455 | WCPWRCO_3G | 3 | North | YES | 0.13828 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.307 | 242 | 242 | 33.4642 | 242 |  |  | 0.307 | 74.2938
728 | WOLFRIDGE801 | 1 | North | YES | 0.13811 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.30683 | 0 | 112.5 | 15.5379 | 112.5 |  |  | 0.30683 | 34.5186
2381 | NTHLK1_G | 1 | North | YES | 0.13807 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.30679 | 156 | 156 | 21.5388 | 156 |  |  | 0.30679 | 47.8586
2382 | NTHLK2_G | 2 | North | YES | 0.13807 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.30679 | 181 | 181 | 24.9905 | 181 |  |  | 0.30679 | 55.5283
2383 | NTHLK3_G | 3 | North | YES | 0.13807 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.30679 | 329 | 329 | 45.4247 | 329 |  |  | 0.30679 | 100.9326
344 | MRSSHPRD | 1 | North | YES | 0.13733 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.30604 | 0 | 0 | 0 | 0 |  |  | 0.30604 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.13733 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.30604 | 0 | 0 | 0 | 0 |  |  | 0.30604 | 0
2413 | MTCK6_G | 6 | North | YES | 0.13695 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.30567 | 118 | 118 | 16.1607 | 118 |  |  | 0.30567 | 36.0693
2414 | MTCK7_G | 7 | North | YES | 0.13695 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.30567 | 115 | 115 | 15.7498 | 115 |  |  | 0.30567 | 35.1523
2417 | MTCK8_G | 8 | North | YES | 0.13695 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.30567 | 556 | 556 | 76.147 | 556 |  |  | 0.30567 | 169.9537
1600 | BARTNWND_1G | 1 | North | YES | 0.13695 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.30567 | 0 | 120 | 16.4342 | 120 |  |  | 0.30567 | 36.6803
2371 | COLLIN_1G | MB | North | YES | 0.1365 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.30522 | 0 | 0 | 0 | 0 |  |  | 0.30522 | 0
1643 | SLSTR1PP_1G | 1 | North | YES | 0.13599 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.3047 | 0 | 60 | 8.1592 | 60 |  |  | 0.3047 | 18.2822
6948 | DENISNDM | 1 | North | YES | 0.1351 | 40 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.30382 | 0 | 0 | 0 | 0 |  |  | 0.30382 | 0
6948 | DENISNDM | 2 | North | YES | 0.1351 | 31 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.30382 | 0 | 0 | 0 | 0 |  |  | 0.30382 | 0
1687 | VALLEY_1G | 1 | North | YES | 0.13481 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.30352 | 170 | 170 | 22.9169 | 170 |  |  | 0.30352 | 51.5988
1688 | VALLEY_2G | 2 | North | YES | 0.13481 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.30352 | 527 | 527 | 71.0422 | 527 |  |  | 0.30352 | 159.9561
1689 | VALLEY_3G | 3 | North | YES | 0.13447 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.30319 | 375 | 375 | 50.4266 | 375 |  |  | 0.30319 | 113.6955
11691 | KMICHICT1_G | 1 | North | YES | 0.13447 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.30319 | 144 | 144 | 19.3638 | 144 |  |  | 0.30319 | 43.6591
11692 | KMICHICT2_G | 2 | North | YES | 0.13447 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.30319 | 146 | 146 | 19.6328 | 146 |  |  | 0.30319 | 44.2655
11693 | KMICHIST3_G | 3 | North | YES | 0.13447 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.30319 | 312 | 312 | 41.955 | 312 |  |  | 0.30319 | 94.5947
11694 | KMICHICT4_G | 4 | North | YES | 0.13447 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.30319 | 144 | 144 | 19.3638 | 144 |  |  | 0.30319 | 43.6591
11695 | KMICHICT5_G | 5 | North | YES | 0.13447 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.30319 | 148 | 148 | 19.9017 | 148 |  |  | 0.30319 | 44.8718
11696 | KMICHIST6_G | 6 | North | YES | 0.13447 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.30319 | 310 | 310 | 41.686 | 310 |  |  | 0.30319 | 93.9883
1678 | LAMARPWR_1G | 1 | North | YES | 0.13425 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.30296 | 160 | 160 | 21.4792 | 160 |  |  | 0.30296 | 48.4739
1679 | LAMARPWR_2G | 2 | North | YES | 0.13425 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.30296 | 156 | 156 | 20.9422 | 156 |  |  | 0.30296 | 47.2621
1680 | LAMARPWR_3G | 3 | North | YES | 0.13425 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.30296 | 196 | 196 | 26.312 | 196 |  |  | 0.30296 | 59.3806
1681 | LAMARPWR_4G | 4 | North | YES | 0.13425 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.30296 | 156 | 156 | 20.9422 | 156 |  |  | 0.30296 | 47.2621
1682 | LAMARPWR_5G | 5 | North | YES | 0.13425 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.30296 | 157 | 157 | 21.0765 | 157 |  |  | 0.30296 | 47.565
1683 | LAMARPWR_6G | 6 | North | YES | 0.13425 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.30296 | 198 | 198 | 26.5805 | 198 |  |  | 0.30296 | 59.9865
1432 | GRHAMSES_2G | 2 | North | YES | 0.13417 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.30288 | 366 | 366 | 49.1051 | 366 |  |  | 0.30288 | 110.8556
1479 | WFCOGEN_1G | 1 | North | YES | 0.13413 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30285 | 0 | 0 | 0 | 0 |  |  | 0.30285 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.13413 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30285 | 0 | 0 | 0 | 0 |  |  | 0.30285 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.13413 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.30285 | 0 | 0 | 0 | 0 |  |  | 0.30285 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.13413 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30285 | 0 | 0 | 0 | 0 |  |  | 0.30285 | 0
1675 | PEC_1G | 1 | North | YES | 0.13405 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.30276 | 0 | 0 | 0 | 0 |  |  | 0.30276 | 0
1676 | PEC_2G | 2 | North | YES | 0.13405 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.30276 | 0 | 0 | 0 | 0 |  |  | 0.30276 | 0
1677 | PEC_3G | 3 | North | YES | 0.13405 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.30276 | 0 | 0 | 0 | 0 |  |  | 0.30276 | 0
1701 | MOSES_1G | 1 | North | YES | 0.13388 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.30259 | 0 | 558 | 74.7028 | 558 |  |  | 0.30259 | 168.8469
1702 | MOSES_2G | 2 | North | YES | 0.13388 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.30259 | 0 | 579 | 77.5142 | 579 |  |  | 0.30259 | 175.2014
1703 | MOSES_3G | 3 | North | YES | 0.13388 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.30259 | 0 | 808 | 108.1718 | 808 |  |  | 0.30259 | 244.4952
5925 | DCEAST | EQ | North | YES | 0.13388 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.30259 | 0 | 0 | 0 | 0 |  |  | 0.30259 | 0
1433 | GRHAMSES_1G | 1 | North | YES | 0.13378 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.3025 | 242 | 242 | 32.3745 | 242 |  |  | 0.3025 | 73.2041
842 | OLINGER_G1 | 1 | North | YES | 0.13353 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.30225 | 79 | 79 | 10.5487 | 79 |  |  | 0.30225 | 23.8774
843 | OLINGER_G2 | 1 | North | YES | 0.13353 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.30225 | 110 | 110 | 14.6881 | 110 |  |  | 0.30225 | 33.247
844 | OLINGER_G3 | 1 | North | YES | 0.13353 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.30225 | 150 | 150 | 20.0292 | 150 |  |  | 0.30225 | 45.3368
845 | OLINGER_G4 | 1 | North | YES | 0.13353 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.30225 | 76 | 76 | 10.1481 | 76 |  |  | 0.30225 | 22.9706
837 | NEWMAN_G5 | 1 | North | YES | 0.13348 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.3022 | 40 | 40 | 5.3394 | 40 |  |  | 0.3022 | 12.0881
12440 | PARKD_1SVC8 | 1 | North | YES | 0.1332 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.30192 | 0 | 0 | 0 | 0 |  |  | 0.30192 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.1332 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.30192 | 0 | 0 | 0 | 0 |  |  | 0.30192 | 0
948 | STEAM1 | 1 | North | YES | 0.13318 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.30189 | 20 | 20 | 2.6635 | 20 |  |  | 0.30189 | 6.0379
949 | STEAM2 | 1 | North | YES | 0.13318 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.30189 | 26 | 26 | 3.4626 | 26 |  |  | 0.30189 | 7.8492
950 | STEAM3 | 1 | North | YES | 0.13318 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.30189 | 42 | 42 | 5.5934 | 42 |  |  | 0.30189 | 12.6796
2451 | LKHB1_G | 1 | North | YES | 0.13279 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.30151 | 391 | 391 | 51.9225 | 391 |  |  | 0.30151 | 117.8908
2452 | LKHB2_G | 2 | North | YES | 0.13279 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.30151 | 516 | 516 | 68.5217 | 516 |  |  | 0.30151 | 155.5797
12411 | FPLEFR1A_G | 1 | North | YES | 0.13109 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.29981 | 161 | 161 | 21.1055 | 161 |  |  | 0.29981 | 48.2689
12412 | FPLEFR1B_G | 2 | North | YES | 0.13109 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.29981 | 164 | 164 | 21.4988 | 164 |  |  | 0.29981 | 49.1684
12413 | FPLEFR1C_G | 3 | North | YES | 0.13109 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.29981 | 164 | 164 | 21.4988 | 164 |  |  | 0.29981 | 49.1684
12414 | FPLEFR1S_G | 4 | North | YES | 0.13109 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.29981 | 414 | 414 | 54.2713 | 414 |  |  | 0.29981 | 124.1201
12421 | FPLEFR2A_G | 1 | North | YES | 0.13109 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.29981 | 162 | 162 | 21.2366 | 162 |  |  | 0.29981 | 48.5687
12422 | FPLEFR2B_G | 2 | North | YES | 0.13109 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.29981 | 161 | 161 | 21.1055 | 161 |  |  | 0.29981 | 48.2689
12423 | FPLEFR2C_G | 3 | North | YES | 0.13109 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.29981 | 163 | 163 | 21.3677 | 163 |  |  | 0.29981 | 48.8686
12424 | FPLEFR2S_G | 4 | North | YES | 0.13109 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.29981 | 415 | 415 | 54.4023 | 415 |  |  | 0.29981 | 124.4199
6100 | OKLA7A | EQ | West | YES | 0.13037 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.29909 | 0 | 0 |  |  |  |  | 0.29909 | 0
6752 | OKLA0A | 1 | West | YES | 0.13037 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.29909 | 0 | 649.7 |  |  |  |  | 0.29909 | 194.3188
3126 | TRINIDAD_6G | 1 | North | YES | 0.12975 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.29847 | 224 | 224 | 29.0642 | 224 |  |  | 0.29847 | 66.8569
1442 | COKFIELD_5 | 1 | North | YES | 0.12935 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.29807 | 0 | 165 | 21.3436 | 165 |  |  | 0.29807 | 49.1819
1438 | MESQUITW_2G | 1 | North | YES | 0.12784 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.29655 | 0 | 236 | 30.1691 | 236 |  |  | 0.29655 | 69.9863
1437 | MESQUITW_1G | 1 | North | YES | 0.12783 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.29654 | 0 | 400 | 51.1308 | 400 |  |  | 0.29654 | 118.6176
60052 | WILDHRS11A | 1 | West | YES | 0.12617 | 25.3 | 0 | 126.5 | 0 | 1.005 | Wind | 1 | 0.29489 | 0 | 126.5 |  |  |  |  | 0.29489 | 37.3035
60053 | WILDHRS21A | 1 | West | YES | 0.12617 | 7.8 | 0 | 39 | 0 | 1.025 | Wind | 1 | 0.29489 | 0 | 39 |  |  |  |  | 0.29489 | 11.5007
60081 | WHRLWIND1A | 1 | West | YES | 0.12504 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.29375 | 0 | 60 |  |  |  |  | 0.29375 | 17.6251
1416 | SWETWATR_1G | 1 | West | YES | 0.12405 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.29277 | 30 | 30 |  |  |  |  | 0.29277 | 8.7832
1417 | SWETWATR_2G | 2 | West | YES | 0.12405 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.29277 | 72 | 72 |  |  |  |  | 0.29277 | 21.0796
1418 | SWETWATR_3G | 3 | West | YES | 0.12405 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.29277 | 68 | 68 |  |  |  |  | 0.29277 | 19.9085
1419 | SWETWATR_4G | 4 | West | YES | 0.12405 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.29277 | 61 | 61 |  |  |  |  | 0.29277 | 17.8591
6144 | MCADOO1A | 1 | West | YES | 0.12327 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.29199 | 0 | 150 |  |  |  |  | 0.29199 | 43.7987
1049 | ROSCOEWI_5 | 1 | West | YES | 0.12326 | 41.8 | 0 | 209 |  | 1.01 | Wind | 1 | 0.29198 | 0 | 209 |  |  |  |  | 0.29198 | 61.0228
1057 | ROSCOEWI_5 | 2 | West | YES | 0.12326 | 25.3 | 0 | 126.5 |  | 1.01 | Wind | 1 | 0.29198 | 0 | 126.5 |  |  |  |  | 0.29198 | 36.9348
1060 | ROSCOEWI_5 | 3 | West | YES | 0.12326 | 39.4 | 0 | 197 | 0 | 1.01 | Wind | 1 | 0.29198 | 0 | 197 |  |  |  |  | 0.29198 | 57.5191
1072 | ROSCOEWI_5 | 4 | West | YES | 0.12326 | 63.6 | 0 | 318 | 0 | 1.01 | Wind | 1 | 0.29198 | 0 | 318 |  |  |  |  | 0.29198 | 92.8481
71051 | L_BITTCR1_1N | W1 | West | YES | 0.12311 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.29183 | 0 | 37.5 |  |  |  |  | 0.29183 | 10.9435
71054 | L_SWEETW1_1N | W1 | West | YES | 0.12311 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.29183 | 0 | 107.5 |  |  |  |  | 0.29183 | 31.3713
71057 | L_SWEETW1_2N | W1 | West | YES | 0.12311 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.29183 | 0 | 135 |  |  |  |  | 0.29183 | 39.3965
71059 | L_SWEETW1_3N | W1 | West | YES | 0.12311 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.29183 | 0 | 119 |  |  |  |  | 0.29183 | 34.7273
71060 | L_SWEETW1_4N | W1 | West | YES | 0.12311 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.29183 | 0 | 105 |  |  |  |  | 0.29183 | 30.6417
3097 | MARTLAKE_1G | 1 | North | YES | 0.12275 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.29147 | 0 | 790 | 96.9717 | 790 |  |  | 0.29147 | 230.2582
3098 | MARTLAKE_2G | 2 | North | YES | 0.12275 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.29147 | 0 | 795 | 97.5855 | 795 |  |  | 0.29147 | 231.7155
3099 | MARTLAKE_3G | 3 | North | YES | 0.12275 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.29147 | 0 | 804 | 98.6902 | 804 |  |  | 0.29147 | 234.3387
36998 | RDCNYNG1 | 1 | West | YES | 0.12193 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.29065 | 0 | 84 |  |  |  |  | 0.29065 | 24.4147
1343 | TRENTIPP_8 | 1 | West | YES | 0.12168 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.2904 | 0 | 150 |  |  |  |  | 0.2904 | 43.56
1354 | AEPWIND_8 | 1 | West | YES | 0.12168 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.2904 | 0 | 101 |  |  |  |  | 0.2904 | 29.3304
1061 | CIELOGEN_1G | 1 | West | YES | 0.12163 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.29035 | 0 | 99 |  |  |  |  | 0.29035 | 28.7443
1062 | CIELOGEN_2G | 1 | West | YES | 0.12163 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.29035 | 0 | 61 |  |  |  |  | 0.29035 | 17.7111
1069 | KINDERMG_1G | 1 | West | YES | 0.12163 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.29035 | 0 | 0 |  |  |  |  | 0.29035 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.12163 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.29035 | 0 | 0 |  |  |  |  | 0.29035 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.12163 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.29035 | 0 | 0 |  |  |  |  | 0.29035 | 0
1068 | SCURRYCW_1G | 1 | West | YES | 0.12161 | 28.2 | 1.3 | 141 |  | 1.01 | Wind | 1 | 0.29033 | 0 | 141 |  |  |  |  | 0.29033 | 40.9364
1073 | SCURRYCW_2G | 2 | West | YES | 0.12161 | 24 | 0 | 120 | 0 | 1.017 | Wind | 1 | 0.29033 | 0 | 120 |  |  |  |  | 0.29033 | 34.8395
13116 | TGATEWAY_1G | 1 | North | YES | 0.12156 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.29028 | 151 | 151 | 18.3556 | 151 |  |  | 0.29028 | 43.8318
13117 | TGATEWAY_2G | 2 | North | YES | 0.12156 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.29028 | 130 | 130 | 15.8028 | 130 |  |  | 0.29028 | 37.736
13118 | TGATEWAY_3G | 3 | North | YES | 0.12156 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.29028 | 148 | 148 | 17.9909 | 148 |  |  | 0.29028 | 42.961
13119 | TGATEWAY_4G | 4 | North | YES | 0.12156 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.29028 | 399 | 399 | 48.5024 | 399 |  |  | 0.29028 | 115.8206
6637 | SNYDERW1A | 1 | West | YES | 0.12149 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.29021 | 0 | 63 |  |  |  |  | 0.29021 | 18.2833
1037 | MORGAN5G_5G | 5 | West | YES | 0.12138 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.2901 | 137 | 137 |  |  |  |  | 0.2901 | 39.7438
1039 | MRGNAG_1G | A | West | YES | 0.12138 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.2901 | 69 | 69 |  |  |  |  | 0.2901 | 20.017
1040 | MRGNBG_2G | B | West | YES | 0.12138 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.2901 | 71 | 71 |  |  |  |  | 0.2901 | 20.5972
1041 | MRGNCG_3G | C | West | YES | 0.12138 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.2901 | 70 | 70 |  |  |  |  | 0.2901 | 20.3071
1042 | MRGNDG_4G | D | West | YES | 0.12138 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.2901 | 68 | 68 |  |  |  |  | 0.2901 | 19.7269
1043 | MRGNEG_5G | E | West | YES | 0.12138 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.2901 | 70 | 70 |  |  |  |  | 0.2901 | 20.3071
1044 | MRGNFG_6G | F | West | YES | 0.12138 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.2901 | 66 | 66 |  |  |  |  | 0.2901 | 19.1467
1301 | BULLCREK_8 | 1 | West | YES | 0.12122 | 36 | 0 | 180 | 0 | 1.017 | Wind | 1 | 0.28993 | 0 | 180 |  |  |  |  | 0.28993 | 52.188
1058 | LONGSHORE_5 | 1 | West | YES | 0.12118 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.2899 | 0 | 150 |  |  |  |  | 0.2899 | 43.4844
1058 | LONGSHORE_5 | 2 | West | YES | 0.12118 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.2899 | 0 | 220 |  |  |  |  | 0.2899 | 63.7771
1058 | LONGSHORE_5 | 3 | West | YES | 0.12118 | 23.4 | 0 | 117 |  | 1.01 | Wind | 1 | 0.2899 | 0 | 117 |  |  |  |  | 0.2899 | 33.9178
60058 | BUFF_GAP1A | 1 | West | YES | 0.12102 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.28974 | 0 | 120 |  |  |  |  | 0.28974 | 34.7685
60060 | CIRELLO | 1 | West | YES | 0.12102 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.28974 | 0 | 233 |  |  |  |  | 0.28974 | 67.5087
60063 | BUFF_GAP1B | 1 | West | YES | 0.12102 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.28974 | 0 | 170.2 |  |  |  |  | 0.28974 | 49.3133
60066 | H_HOLLOW1A | 1 | West | YES | 0.12102 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.28974 | 0 | 222 |  |  |  |  | 0.28974 | 64.3216
60068 | HHOLLOW21A | 1 | West | YES | 0.12102 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.28974 | 0 | 184 |  |  |  |  | 0.28974 | 53.3116
60070 | HHOLLOW31A | 1 | West | YES | 0.12102 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.28974 | 0 | 224 |  |  |  |  | 0.28974 | 64.9011
60072 | HHOLLOW41A | 1 | West | YES | 0.12102 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.28974 | 0 | 115 |  |  |  |  | 0.28974 | 33.3198
1045 | CALENG1G_1G | 1 | West | YES | 0.12087 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.28958 | 0 | 0 |  |  |  |  | 0.28958 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.12087 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.28958 | 0 | 0 |  |  |  |  | 0.28958 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.12087 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.28958 | 0 | 0 |  |  |  |  | 0.28958 | 0
1302 | COYOTEWG_8 | 1 | West | YES | 0.12075 | 45 | 0 | 225 |  | 1.01 | Wind | 1 | 0.28947 | 0 | 225 |  |  |  |  | 0.28947 | 65.1305
1360 | GUNSIGHT_8 | 1 | West | YES | 0.12047 | 24 | 0 | 120 | 0 | 1.01 | Wind | 1 | 0.28918 | 0 | 120 |  |  |  |  | 0.28918 | 34.7019
1327 | WILDHRSE_1G | 1 | West | YES | 0.12043 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.28914 | 0 | 120 |  |  |  |  | 0.28914 | 34.6973
3348 | CHAMPION_1G | MB | North | YES | 0.12036 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.28907 | 0 | 0 | 0 | 0 |  |  | 0.28907 | 0
3113 | LUFKINWB_1G | 1 | North | YES | 0.12024 | 0 | 0 | 50 |  | 1.01 | Trash | 1 | 0.28896 | 50 | 50 | 6.0121 | 50 |  |  | 0.28896 | 14.4479
1170 | AIRLAMESA_1G | 1 | West | YES | 0.1201 | 0 | 0 | 180 |  | 1 | Wind | 1 | 0.28882 | 0 | 180 |  |  |  |  | 0.28882 | 51.9878
1333 | MCDDONAL_8 | 1 | West | YES | 0.11974 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.28846 | 0 | 214.2 |  |  |  |  | 0.28846 | 61.7882
3107 | STRYKER_1G | 1 | North | YES | 0.11974 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.28846 | 182 | 182 | 21.7927 | 182 |  |  | 0.28846 | 52.4992
3108 | STRYKER_2G | 2 | North | YES | 0.11974 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.28846 | 484 | 484 | 57.9542 | 484 |  |  | 0.28846 | 139.6132
1320 | BSP 1 | 1 | West | YES | 0.11954 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.28826 | 0 | 0 |  |  |  |  | 0.28826 | 0
1326 | STANTONW_8 | 1 | West | YES | 0.11953 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.28824 | 0 | 100.5 |  |  |  |  | 0.28824 | 28.9685
11001 | NAV1CT | 1 | West | YES | 0.11952 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.28823 | 70.4 | 70.4 |  |  |  |  | 0.28823 | 20.2916
11009 | NAV2CT | 1 | West | YES | 0.11952 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.28823 | 71.4 | 71.4 |  |  |  |  | 0.28823 | 20.5798
11011 | NAV3ST | 1 | West | YES | 0.11952 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.28823 | 92.8 | 92.8 |  |  |  |  | 0.28823 | 26.748
11012 | NAV4CT | 1 | West | YES | 0.11952 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.28823 | 80 | 80 |  |  |  |  | 0.28823 | 23.0586
11013 | NAV5CT | 1 | West | YES | 0.11952 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.28823 | 80 | 80 |  |  |  |  | 0.28823 | 23.0586
11014 | NAV6ST | 1 | West | YES | 0.11952 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.28823 | 115 | 115 |  |  |  |  | 0.28823 | 33.1468
11020 | TIEHVSG_1G | 1 | West | YES | 0.1195 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.28821 | 208.2 | 208.2 |  |  |  |  | 0.28821 | 60.0058
11021 | TIEHVCG_1G | 1 | West | YES | 0.1195 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.28821 | 142.1 | 142.1 |  |  |  |  | 0.28821 | 40.9549
11022 | TIEHVCG_2G | 1 | West | YES | 0.1195 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.28821 | 132.4 | 132.4 |  |  |  |  | 0.28821 | 38.1593
11023 | TIEHVCG_3G | 1 | West | YES | 0.1195 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.28821 | 137.4 | 137.4 |  |  |  |  | 0.28821 | 39.6003
11024 | TIEHVCG_4G | 1 | West | YES | 0.1195 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.28821 | 147 | 147 |  |  |  |  | 0.28821 | 42.3672
11025 | TIEHVSG_2G | 1 | West | YES | 0.1195 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.28821 | 213.2 | 213.2 |  |  |  |  | 0.28821 | 61.4468
1328 | OCOTILLO_1G | 1 | West | YES | 0.11948 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.28819 | 0 | 58 |  |  |  |  | 0.28819 | 16.7152
60057 | CALLAHAN1A | 1 | West | YES | 0.1192 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.28792 | 0 | 114 |  |  |  |  | 0.28792 | 32.823
76031 | L_GASCCR1_1N | W1 | West | YES | 0.1183 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.28702 | 0 | 150 |  |  |  |  | 0.28702 | 43.0526
1146 | NOTREES_1G | 1 | West | YES | 0.11817 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.28689 | 0 | 149 |  |  |  |  | 0.28689 | 42.7468
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.11795 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.28667 | 0 | 35 |  |  |  |  | 0.28667 | 10.0334
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.11795 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.28667 | 0 | 30 |  |  |  |  | 0.28667 | 8.6001
1002 | PBCTAGE_1G | A | West | YES | 0.11784 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.28655 | 66 | 66 |  |  |  |  | 0.28655 | 18.9125
1003 | PBCTBGE_2G | B | West | YES | 0.11784 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.28655 | 66 | 66 |  |  |  |  | 0.28655 | 18.9125
1004 | PBCTCGE_3G | C | West | YES | 0.11784 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.28655 | 67 | 67 |  |  |  |  | 0.28655 | 19.1991
1005 | PBCTDGE_4G | D | West | YES | 0.11784 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.28655 | 68 | 68 |  |  |  |  | 0.28655 | 19.4856
1006 | PBCTEGE_5G | E | West | YES | 0.11784 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.28655 | 67 | 67 |  |  |  |  | 0.28655 | 19.1991
1007 | PB5GEN_6G | 5 | West | YES | 0.11784 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.28655 | 114 | 114 |  |  |  |  | 0.28655 | 32.6671
1008 | PB6GEN_7G | 6 | West | YES | 0.11784 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.28655 | 515 | 515 |  |  |  |  | 0.28655 | 147.5748
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.11765 | 110 | 0 | 550 | 0 | 1.02 | Wind | 1 | 0.28637 | 0 | 550 |  |  |  |  | 0.28637 | 157.503
1349 | WESTXWIN_1G | 1 | West | YES | 0.11739 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.28611 | 0 | 6.6 |  |  |  |  | 0.28611 | 1.8883
1350 | NWPWRG1_1G | 1 | West | YES | 0.11739 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.28611 | 0 | 34.3 |  |  |  |  | 0.28611 | 9.8135
6407 | TURKTRAK1A | 1 | West | YES | 0.11491 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.28363 | 0 | 169.5 |  |  |  |  | 0.28363 | 48.075
13134 | CALFREST_4G | 4 | North | YES | 0.10837 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.27709 | 151.5 | 151.5 | 16.4182 | 151.5 |  |  | 0.27709 | 41.9788
13135 | CALFREST_5G | 5 | North | YES | 0.10837 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.27709 | 152.3 | 152.3 | 16.5049 | 152.3 |  |  | 0.27709 | 42.2005
13136 | CALFREST_6G | 6 | North | YES | 0.10837 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.27709 | 177.5 | 177.5 | 19.2359 | 177.5 |  |  | 0.27709 | 49.1831
13131 | CALFREST_1G | 1 | North | YES | 0.10786 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.27657 | 150.7 | 150.7 | 16.2537 | 150.7 |  |  | 0.27657 | 41.6794
13132 | CALFREST_2G | 2 | North | YES | 0.10786 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.27657 | 151 | 151 | 16.2861 | 151 |  |  | 0.27657 | 41.7624
13133 | CALFREST_3G | 3 | North | YES | 0.10786 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.27657 | 177.4 | 177.4 | 19.1335 | 177.4 |  |  | 0.27657 | 49.0639
60007 | KING_SW1A | 1 | West | YES | 0.10683 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27555 | 0 | 80 |  |  |  |  | 0.27555 | 22.0437
60019 | KING_NW1A | 1 | West | YES | 0.10683 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27555 | 0 | 80 |  |  |  |  | 0.27555 | 22.0437
60201 | RIO DRCS | F | West | YES | 0.10594 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.27466 | 0 | 0 |  |  |  |  | 0.27466 | 0
60016 | WOODWRD11A | 1 | West | YES | 0.10586 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.27458 | 0 | 80 |  |  |  |  | 0.27458 | 21.9662
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.10584 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.27455 | 0 | 80 |  |  |  |  | 0.27455 | 21.9642
38437 | TNSRBNMESA9 | 1 | West | YES | 0.10576 | 37.5 | 0 | 150 |  | 1.02 | Wind | 1 | 0.27447 | 0 | 150 |  |  |  |  | 0.27447 | 41.171
6016 | SWMESA | 1 | West | YES | 0.10537 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.27408 | 0 | 75 |  |  |  |  | 0.27408 | 20.5563
60003 | KING_NE1A | 1 | West | YES | 0.10537 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27408 | 0 | 80 |  |  |  |  | 0.27408 | 21.9267
60005 | KING_SE1A | 1 | West | YES | 0.10537 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.27408 | 0 | 40 |  |  |  |  | 0.27408 | 10.9634
3381 | BBRN_1G | 1 | North | YES | 0.10503 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.27375 | 0 | 618 | 64.9098 | 618 |  |  | 0.27375 | 169.1769
3382 | BBRN_2G | 2 | North | YES | 0.10503 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.27375 | 0 | 589 | 61.8638 | 589 |  |  | 0.27375 | 161.2382
60000 | DSKY2 | 1 | West | YES | 0.10393 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.27265 | 0 | 76.5 |  |  |  |  | 0.27265 | 20.8574
60017 | ORNNWP1 | 1 | West | YES | 0.10314 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.27186 | 0 | 80 |  |  |  |  | 0.27186 | 21.7486
60018 | DSKY1 | 1 | West | YES | 0.10227 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.27099 | 0 | 84 |  |  |  |  | 0.27099 | 22.7627
60202 | FRNDDRCS | F | West | YES | 0.084629 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.25335 | 0 | 0 |  |  |  |  | 0.25335 | 0
48721 | LEG_1___1 | 1 | North | YES | 0.072347 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.24106 | 0 | 827 | 59.831 | 827 |  |  | 0.24106 | 199.36
48722 | LEG_2___2 | 2 | North | YES | 0.072347 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.24106 | 0 | 819 | 59.2522 | 819 |  |  | 0.24106 | 197.4315
39960 | TNTNPONE_18 | 1 | North | YES | 0.059377 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.22809 | 0 | 152.3 | 9.0431 | 152.3 |  |  | 0.22809 | 34.7387
39970 | TNTNPONE_28 | 1 | North | YES | 0.059377 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.22809 | 0 | 153 | 9.0847 | 153 |  |  | 0.22809 | 34.8984
990 | GIBN_CREK_G1 | 1 | North | YES | 0.026875 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.19559 | 0 | 463 | 12.4431 | 463 |  |  | 0.19559 | 90.5591
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.019931 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.18865 | 32 | 32 | 0.63779 | 32 |  |  | 0.18865 | 6.0367
32886 | BRYN_ATKINS3 | MB | North | YES | 0.019144 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.18786 | 0 | 0 | 0 | 0 |  |  | 0.18786 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.019144 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.18786 | 0 | 0 | 0 | 0 |  |  | 0.18786 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.019144 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.18786 | 17 | 17 | 0.32545 | 17 |  |  | 0.18786 | 3.1936
32890 | BRYN_ATKINS4 | MB | North | YES | 0.019144 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.18786 | 0 | 0 | 0 | 0 |  |  | 0.18786 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.019144 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.18786 | 0 | 0 | 0 | 0 |  |  | 0.18786 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | 0.01743 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.18615 | 154.2 | 154.2 | 2.6877 | 154.2 |  |  | 0.18615 | 28.7039
48672 | FTR_GT2_5110 | 2 | North | YES | 0.01743 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.18615 | 159 | 159 | 2.7714 | 159 |  |  | 0.18615 | 29.5974
48673 | FTR_GT3_5085 | 3 | North | YES | 0.01743 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.18615 | 158 | 158 | 2.7539 | 158 |  |  | 0.18615 | 29.4112
48674 | FTR_CN4_5095 | 4 | North | YES | 0.01743 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.18615 | 380 | 380 | 6.6234 | 380 |  |  | 0.18615 | 70.7359
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.016483 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.1852 | 48 | 48 | 0.79118 | 48 |  |  | 0.1852 | 8.8896
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.016483 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.1852 | 46 | 46 | 0.75822 | 46 |  |  | 0.1852 | 8.5192
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.016483 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.1852 | 105 | 105 | 1.7307 | 105 |  |  | 0.1852 | 19.446
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.13196 | 15 | 15 |  |  | 0 | 15 | -0.13196 | -1.9794
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8442 | NUECES_B0A | MB | South | YES | 0 | 0 | 81 | 367 |  | 1.03 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.13196 | 0 | 0 |  |  |  |  | -0.13196 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.030326 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.16229 | 0 | 0 |  |  |  |  | -0.16229 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.030326 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.16229 | 0 | 0 |  |  |  |  | -0.16229 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.030326 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.16229 | 0 | 0 |  |  |  |  | -0.16229 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.030326 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.16229 | 0 | 0 |  |  |  |  | -0.16229 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.030326 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.16229 | 0 | 0 |  |  |  |  | -0.16229 | 0
48885 | THW_5152 | A | Houston | YES | -0.035609 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.16757 | 58 | 58 |  |  |  |  | -0.16757 | -9.7191
48885 | THW_5152 | B | Houston | YES | -0.035609 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.16757 | 59 | 59 |  |  |  |  | -0.16757 | -9.8867
48886 | THW_5354 | C | Houston | YES | -0.035609 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.16757 | 57 | 57 |  |  |  |  | -0.16757 | -9.5516
48886 | THW_5354 | D | Houston | YES | -0.035609 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.16757 | 58 | 58 |  |  |  |  | -0.16757 | -9.7191
48887 | THW_5556 | E | Houston | YES | -0.035609 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.16757 | 59 | 59 |  |  |  |  | -0.16757 | -9.8867
48887 | THW_5556 | F | Houston | YES | -0.035609 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.16757 | 57 | 57 |  |  |  |  | -0.16757 | -9.5516
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.035987 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.16795 | 398 | 398 |  |  |  |  | -0.16795 | -66.8438
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.036246 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.16821 | 162.8 | 162.8 |  |  |  |  | -0.16821 | -27.3843
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.036246 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.16821 | 161.4 | 161.4 |  |  |  |  | -0.16821 | -27.1488
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.036246 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.16821 | 158.9 | 158.9 |  |  |  |  | -0.16821 | -26.7283
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.036246 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.16821 | 269.2 | 269.2 |  |  |  |  | -0.16821 | -45.2817
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.037111 | 172 | 0 | 172 | 0 | 1.026 | GSC | -1 | 0.16907 | 172 | 172 |  |  |  |  | -0.16907 | -29.0806
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.037111 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.16907 | 172 | 172 |  |  |  |  | -0.16907 | -29.0806
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.037111 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.16907 | 172 | 172 |  |  |  |  | -0.16907 | -29.0806
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.037276 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.16924 | 0 | 0 |  |  |  |  | -0.16924 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.037497 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.16946 | 744 | 744 |  |  |  |  | -0.16946 | -126.0777
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.037551 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.037551 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.037551 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.037551 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.037551 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.037551 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.037551 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48651 | EP_1_2 | 2 | Houston | YES | -0.037563 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.16953 | 0 | 0 |  |  |  |  | -0.16953 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.037563 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.16953 | 0 | 0 |  |  |  |  | -0.16953 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.038238 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.1702 | 12 | 12 |  |  |  |  | -0.1702 | -2.0424
49803 | EXN_15GT | 1 | Houston | YES | -0.038381 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.038381 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.038381 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.038381 | 43 | 9.2 | 45.9 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.038381 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.038381 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.038381 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.038381 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.038381 | 18.5 | 9.2 | 18.5 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.038381 | 81 | 21.3 | 85.4 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.038381 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.038681 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.17064 | 746 | 746 |  |  |  |  | -0.17064 | -127.2999
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.039389 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.17135 | 107 | 107 |  |  |  |  | -0.17135 | -18.3346
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.039389 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.17135 | 108 | 108 |  |  |  |  | -0.17135 | -18.5059
48875 | THW_3132 | B | Houston | YES | -0.039389 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.17135 | 53 | 53 |  |  |  |  | -0.17135 | -9.0816
48875 | THW_3132 | A | Houston | YES | -0.039389 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.17135 | 55 | 55 |  |  |  |  | -0.17135 | -9.4243
48877 | THW_3334 | C | Houston | YES | -0.039389 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.17135 | 55 | 55 |  |  |  |  | -0.17135 | -9.4243
48877 | THW_3334 | D | Houston | YES | -0.039389 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.17135 | 57 | 57 |  |  |  |  | -0.17135 | -9.767
48879 | THW_4142 | F | Houston | YES | -0.039389 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.17135 | 55 | 55 |  |  |  |  | -0.17135 | -9.4243
48879 | THW_4142 | E | Houston | YES | -0.039389 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.17135 | 56 | 56 |  |  |  |  | -0.17135 | -9.5957
48881 | THW_4344 | G | Houston | YES | -0.039389 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.17135 | 58 | 58 |  |  |  |  | -0.17135 | -9.9384
48881 | THW_4344 | H | Houston | YES | -0.039389 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.17135 | 58 | 58 |  |  |  |  | -0.17135 | -9.9384
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.040331 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.17229 | 0 | 0 |  |  |  |  | -0.17229 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.040331 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.17229 | 0 | 0 |  |  |  |  | -0.17229 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.040458 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.17242 | 42 | 42 |  |  |  |  | -0.17242 | -7.2417
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.040458 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.17242 | 42 | 42 |  |  |  |  | -0.17242 | -7.2417
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.040458 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.17242 | 39 | 39 |  |  |  |  | -0.17242 | -6.7244
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.040458 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.17242 | 39 | 39 |  |  |  |  | -0.17242 | -6.7244
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.040575 | 137.6 | 54.6 | 137.6 |  | 1.0362 | Cogen | -1 | 0.17254 | 0 | 0 |  |  |  |  | -0.17254 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.041232 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.17319 | 0 | 0 |  |  |  |  | -0.17319 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.041232 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.17319 | 0 | 0 |  |  |  |  | -0.17319 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.041232 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.17319 | 0 | 0 |  |  |  |  | -0.17319 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.041232 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.17319 | 0 | 0 |  |  |  |  | -0.17319 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.041685 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.17365 | 0 | 0 |  |  |  |  | -0.17365 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.041685 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.17365 | 0 | 0 |  |  |  |  | -0.17365 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.041685 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.17365 | 0 | 0 |  |  |  |  | -0.17365 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.04169 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.17365 | 228 | 228 |  |  |  |  | -0.17365 | -39.5927
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.0417 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.17366 | 0 | 0 |  |  |  |  | -0.17366 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.0417 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.17366 | 0 | 0 |  |  |  |  | -0.17366 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.0417 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.17366 | 0 | 0 |  |  |  |  | -0.17366 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.0417 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.17366 | 0 | 0 |  |  |  |  | -0.17366 | 0
48845 | SOL_GT1 | 1 | Houston | YES | -0.041704 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.17367 | 16.2 | 16.2 |  |  |  |  | -0.17367 | -2.8134
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.041711 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.17367 | 213 | 213 |  |  |  |  | -0.17367 | -36.9924
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.041785 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.17375 | 0 | 0 |  |  |  |  | -0.17375 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.041785 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.17375 | 0 | 0 |  |  |  |  | -0.17375 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.041797 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.17376 | 165 | 165 |  |  |  |  | -0.17376 | -28.6703
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.041822 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.17378 | 176 | 176 |  |  |  |  | -0.17378 | -30.586
48855 | SRB_GT211035 | B1 | Houston | YES | -0.04184 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.1738 | 18 | 18 |  |  |  |  | -0.1738 | -3.1284
48855 | SRB_GT211035 | B2 | Houston | YES | -0.04184 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.1738 | 12 | 12 |  |  |  |  | -0.1738 | -2.0856
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.042166 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.17413 | 0 | 0 |  |  |  |  | -0.17413 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.042472 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.17443 | 163.2 | 163.2 |  |  |  |  | -0.17443 | -28.4677
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.042472 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.17443 | 157.1 | 157.1 |  |  |  |  | -0.17443 | -27.4036
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.042472 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.17443 | 157.5 | 157.5 |  |  |  |  | -0.17443 | -27.4734
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.042472 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.17443 | 157 | 157 |  |  |  |  | -0.17443 | -27.3862
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.042472 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.17443 | 282 | 282 |  |  |  |  | -0.17443 | -49.1905
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.042829 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.17479 | 0 | 0 |  |  |  |  | -0.17479 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.042829 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.17479 | 0 | 0 |  |  |  |  | -0.17479 | 0
48691 | GBY_73741085 | A | Houston | YES | -0.043266 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.17523 | 47 | 47 |  |  |  |  | -0.17523 | -8.2357
48691 | GBY_73741085 | B | Houston | YES | -0.043266 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.17523 | 47 | 47 |  |  |  |  | -0.17523 | -8.2357
48692 | GBY_81821075 | D | Houston | YES | -0.043266 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.17523 | 55 | 55 |  |  |  |  | -0.17523 | -9.6376
48692 | GBY_81821075 | C | Houston | YES | -0.043266 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.17523 | 47 | 47 |  |  |  |  | -0.17523 | -8.2357
48693 | GBY_83841065 | E | Houston | YES | -0.043266 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.17523 | 57 | 57 |  |  |  |  | -0.17523 | -9.988
48693 | GBY_83841065 | F | Houston | YES | -0.043266 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.17523 | 54 | 54 |  |  |  |  | -0.17523 | -9.4623
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.044156 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.17612 | 0 | 0 |  |  |  |  | -0.17612 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.044156 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.17612 | 0 | 0 |  |  |  |  | -0.17612 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.044156 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.17612 | 0 | 0 |  |  |  |  | -0.17612 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.044156 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.17612 | 0 | 0 |  |  |  |  | -0.17612 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.044862 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.17682 | 0 | 0 |  |  |  |  | -0.17682 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.044862 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.17682 | 0 | 0 |  |  |  |  | -0.17682 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.044862 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.17682 | 0 | 0 |  |  |  |  | -0.17682 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.044862 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.17682 | 0 | 0 |  |  |  |  | -0.17682 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.044862 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.17682 | 0 | 0 |  |  |  |  | -0.17682 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.046708 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.17867 | 0 | 0 |  |  |  |  | -0.17867 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.049353 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.049353 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.049353 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.049353 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.049353 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.049353 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.049353 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.049353 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.049353 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.049353 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.049353 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.049353 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.049353 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.049353 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.049353 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.055639 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.1876 | 166 | 166 |  |  |  |  | -0.1876 | -31.1418
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.055639 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.1876 | 166 | 166 |  |  |  |  | -0.1876 | -31.1418
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.055639 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.1876 | 248 | 248 |  |  |  |  | -0.1876 | -46.5251
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.055639 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.1876 | 546 | 546 |  |  |  |  | -0.1876 | -102.4303
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.055639 | 598.9 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.1876 | 0 | 654 |  |  |  |  | -0.1876 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.055639 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.1876 | 13 | 13 |  |  |  |  | -0.1876 | -2.4388
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.055772 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.18773 | 0 | 0 |  |  |  |  | -0.18773 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.057123 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.18909 | 167.7 | 167.7 |  |  |  |  | -0.18909 | -31.7096
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.057123 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.18909 | 166.4 | 166.4 |  |  |  |  | -0.18909 | -31.4638
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.057123 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.18909 | 252.4 | 252.4 |  |  |  |  | -0.18909 | -47.7251
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.057203 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.18917 | 0 | 651 |  |  |  |  | -0.18917 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.057203 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.18917 | 0 | 564 |  |  |  |  | -0.18917 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.057203 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.18917 | 0 | 603 |  |  |  |  | -0.18917 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.057221 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.18918 | 0 | 0 |  |  |  |  | -0.18918 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.066829 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.19879 | 0 | 0 |  |  |  |  | -0.19879 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.066829 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.19879 | 0 | 0 |  |  |  |  | -0.19879 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.066829 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.19879 | 0 | 0 |  |  |  |  | -0.19879 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.066829 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.19879 | 0 | 0 |  |  |  |  | -0.19879 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.067939 | 33 | 13 | 33 | 0 | 1.0375 | Hydro | -1 | 0.1999 | 0 | 0 |  |  | 0 | 0 | -0.1999 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.067939 | 25 | 13 | 25 | 0 | 1.0375 | Hydro | -1 | 0.1999 | 0 | 0 |  |  | 0 | 0 | -0.1999 | 0
88253 | HAMILTON | F | South | YES | -0.067939 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.1999 | 0 | 0 |  |  | 0 | 0 | -0.1999 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.06949 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.20145 | 0 | 0 |  |  |  |  | -0.20145 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.06949 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.20145 | 0 | 0 |  |  |  |  | -0.20145 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.072855 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.072855 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.072855 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.072855 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.072855 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.072855 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.072855 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.072855 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.072855 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.072855 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.072855 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.072855 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.072855 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.072855 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.072855 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.072855 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.072855 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.072855 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.072855 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.072855 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.086106 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.21807 | 0 | 0 |  |  |  |  | -0.21807 | 0
8262 | ELPS | 1 | South | YES | -0.090039 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.222 | 0 | 0 |  |  | 0 | 0 | -0.222 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.0905 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22246 | 76 | 76 |  |  |  |  | -0.22246 | -16.9071
48732 | CBE_GT2 | 1 | Houston | YES | -0.0905 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22246 | 76 | 76 |  |  |  |  | -0.22246 | -16.9071
48733 | CBE_ST12 | 1 | Houston | YES | -0.0905 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.22246 | 105 | 105 |  |  |  |  | -0.22246 | -23.3585
48734 | CBE_GT3 | 1 | Houston | YES | -0.0905 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22246 | 76 | 76 |  |  |  |  | -0.22246 | -16.9071
48735 | CBE_GT4 | 1 | Houston | YES | -0.0905 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22246 | 76 | 76 |  |  |  |  | -0.22246 | -16.9071
48736 | CBE_ST34 | 1 | Houston | YES | -0.0905 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.22246 | 105 | 105 |  |  |  |  | -0.22246 | -23.3585
5911 | STP_GN1___1 | 1 | Houston | YES | -0.091154 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.22312 | 0 | 0 |  |  |  |  | -0.22312 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.091154 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.22312 | 0 | 0 |  |  |  |  | -0.22312 | 0
80010 | EPLVT1 | F | South | YES | -0.095179 | 0 | 0 | 0 |  | 1.0376 | AVR | -1 | 0.22714 | 0 | 0 |  |  | 0 | 0 | -0.22714 | 0
8134 | FOR #1 | 1 | South | YES | -0.12574 | 54.1 | 45 | 79 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
8138 | FOR #2 | 2 | South | YES | -0.12574 | 63.1 | 45 | 81 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
8153 | FOR #3 | 3 | South | YES | -0.12574 | 63.1 | 45 | 79.9 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
8154 | FOR #4 | 4 | South | YES | -0.12574 | 63.1 | 60 | 80 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
8155 | FOR #5 | 5 | South | YES | -0.12574 | 63.1 | 60 | 78.4 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
8156 | FOR #6 | 6 | South | YES | -0.12574 | 24.9 | 5 | 25 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
8157 | FOR #7 | 7 | South | YES | -0.12574 | 28.8 | 5 | 46 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
80051 | FOR #8 | 8 | South | YES | -0.12574 | 28 | 28 | 28 | 0 | 1.016 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
80052 | FOR #9 | 9 | South | YES | -0.12574 | 29.7 | 5 | 43.6 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
80053 | FOR #10 | 10 | South | YES | -0.12574 | 68.4 | 45 | 75 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
80226 | ALCOA G | 1 | South | YES | -0.12671 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.25867 | 0 | 0 |  |  | 0 | 0 | -0.25867 | 0
8147 | UCAR #2 | 10 | South | YES | -0.12993 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
8148 | UCAR #1 | 2 | South | YES | -0.12993 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80137 | CSDR89 | 9 | South | YES | -0.12993 | 0 | 0 | 15 |  | 1.003 | DCTie | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80137 | CSDR89 | 8 | South | YES | -0.12993 | 33.9 | 0 | 39 |  | 1.003 | DCTie | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80138 | CSDR7 | 7 | South | YES | -0.12993 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80139 | CSDR56 | 6 | South | YES | -0.12993 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80139 | CSDR56 | 5 | South | YES | -0.12993 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80140 | CSDR11 | 11 | South | YES | -0.12993 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80227 | AIRCO G | 1 | South | YES | -0.1303 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.26226 | 0 | 0 |  |  | 0 | 0 | -0.26226 | 0
80224 | VISTRONG1 | 1 | South | YES | -0.13116 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.26312 | 0 | 0 |  |  | 0 | 0 | -0.26312 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.13116 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.26312 | 0 | 0 |  |  | 0 | 0 | -0.26312 | 0
80012 | LAR | F | South | YES | -0.13196 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.26393 | 0 | 0 |  |  | 0 | 0 | -0.26393 | 0
80265 | LARECU40A | 4 | South | YES | -0.13196 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.26393 | 100 | 100 |  |  | -13.1963 | 100 | -0.26393 | -26.3925
80266 | LARECU50A | 5 | South | YES | -0.13196 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.26393 | 100 | 100 |  |  | -13.1963 | 100 | -0.26393 | -26.3925
5503 | RAYBURNGEN3 | 1 | South | YES | -0.13225 | 17.6 | 6 | 22 | 0 | 1.0223 | GST | -1 | 0.26421 | 22 | 22 |  |  | -2.9095 | 22 | -0.26421 | -5.8127
5505 | RAYBURNGEN1 | 1 | South | YES | -0.13225 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.26421 | 11 | 11 |  |  | -1.4547 | 11 | -0.26421 | -2.9063
5506 | RAYBURNGEN2 | 1 | South | YES | -0.13225 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.26421 | 11 | 11 |  |  | -1.4547 | 11 | -0.26421 | -2.9063
88299 | ZAPATA | F | South | YES | -0.13332 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.26528 | 0 | 0 |  |  | 0 | 0 | -0.26528 | 0
5508 | RAYBURNCC9 | 1 | South | YES | -0.13335 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.26531 | 47.7 | 47.7 |  |  | -6.3606 | 47.7 | -0.26531 | -12.6552
5509 | RAYBURNCC10 | 1 | South | YES | -0.13335 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.26531 | 37.3 | 37.3 |  |  | -4.9738 | 37.3 | -0.26531 | -9.896
5511 | RAYBURNCC7 | 1 | South | YES | -0.13335 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.26531 | 47.5 | 47.5 |  |  | -6.3339 | 47.5 | -0.26531 | -12.6021
5512 | RAYBURNCC8 | 1 | South | YES | -0.13335 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.26531 | 49.3 | 49.3 |  |  | -6.574 | 49.3 | -0.26531 | -13.0797
8066 | DUP1V#1 | 1 | South | YES | -0.13347 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.26543 | 0 | 0 |  |  | 0 | 0 | -0.26543 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.13362 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.13362 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.13362 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
8930 | ICPGN10A | 1 | South | YES | -0.13362 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
8931 | ICPGN20A | 2 | South | YES | -0.13362 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
8932 | ICPGN30A | 3 | South | YES | -0.13362 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
80223 | REYSHR G | 1 | South | YES | -0.13362 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | -0.13426 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.26622 | 0 | 0 |  |  | 0 | 0 | -0.26622 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.13426 | 11 | 0 | 11 | 0 | 1.0227 | Hydro | -1 | 0.26622 | 0 | 0 |  |  | 0 | 0 | -0.26622 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.13426 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.26622 | 0 | 0 |  |  | 0 | 0 | -0.26622 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.13473 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.2667 | 0 | 0 |  |  | 0 | 0 | -0.2667 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.13473 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.2667 | 0 | 0 |  |  | 0 | 0 | -0.2667 | 0
8562 | CNOPST1 | 3 | South | YES | -0.13473 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.2667 | 0 | 0 |  |  | 0 | 0 | -0.2667 | 0
88508 | FALFURRI | F | South | YES | -0.13477 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.26673 | 0 | 0 |  |  | 0 | 0 | -0.26673 | 0
8173 | VICEC51A | 5 | South | YES | -0.13479 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.26675 | 144 | 144 |  |  | -19.4095 | 144 | -0.26675 | -38.412
8174 | VICEC61A | 6 | South | YES | -0.13479 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.26675 | 188 | 188 |  |  | -25.3401 | 188 | -0.26675 | -50.1491
8456 | COSW#1 | 1 | South | YES | -0.1348 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.26676 | 0 | 0 |  |  | 0 | 0 | -0.26676 | 0
8457 | COSW#2 | 2 | South | YES | -0.1348 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.26676 | 0 | 0 |  |  | 0 | 0 | -0.26676 | 0
8459 | B_DAVIS0B | MB | South | YES | -0.13494 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.2669 | 0 | 0 |  |  | 0 | 0 | -0.2669 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.13494 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.2669 | 0 | 0 |  |  | 0 | 0 | -0.2669 | 0
8506 | VAL #1 | 1 | South | YES | -0.13501 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.26697 | 0 | 0 |  |  | 0 | 0 | -0.26697 | 0
8507 | VAL #2 | 2 | South | YES | -0.13501 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.26697 | 0 | 0 |  |  | 0 | 0 | -0.26697 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.13513 | 30.3 | 0 | 38 |  | 1.027 | Cogen | -1 | 0.26709 | 0 | 0 |  |  | 0 | 0 | -0.26709 | 0
8461 | KOCH_UP0A | 1 | South | YES | -0.13513 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.26709 | 0 | 0 |  |  | 0 | 0 | -0.26709 | 0
8933 | FGNTS001 | 1 | South | YES | -0.13523 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.2672 | 146.5 | 146.5 |  |  | -19.8118 | 146.5 | -0.2672 | -39.1443
8934 | FGNTS101 | 2 | South | YES | -0.13523 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.2672 | 147.9 | 147.9 |  |  | -20.0011 | 147.9 | -0.2672 | -39.5183
8935 | FGNTS201 | 3 | South | YES | -0.13523 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.2672 | 173 | 173 |  |  | -23.3955 | 173 | -0.2672 | -46.225
8936 | MVGN#1 | 1 | South | YES | -0.13539 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.26736 | 216.6 | 216.6 |  |  | -29.3263 | 216.6 | -0.26736 | -57.9094
8937 | MVGN#2 | 2 | South | YES | -0.13539 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.26736 | 216.7 | 216.7 |  |  | -29.3399 | 216.7 | -0.26736 | -57.9361
8938 | MVGN#3 | 3 | South | YES | -0.13539 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.26736 | 250.9 | 250.9 |  |  | -33.9704 | 250.9 | -0.26736 | -67.0797
8981 | HECN1 | 1 | South | YES | -0.13539 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.26736 | 144.8 | 144.8 |  |  | -19.6052 | 144.8 | -0.26736 | -38.7133
8982 | HECN2 | 2 | South | YES | -0.13539 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.26736 | 144.1 | 144.1 |  |  | -19.5104 | 144.1 | -0.26736 | -38.5262
8983 | HECN3 | 3 | South | YES | -0.13539 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.26736 | 171.9 | 171.9 |  |  | -23.2744 | 171.9 | -0.26736 | -45.9587
5932 | SI_RAY9 | 9 | South | YES | -0.13551 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.26748 | 38 | 38 |  |  | -5.1495 | 38 | -0.26748 | -10.1641
5933 | SI_RAY6 | 6 | South | YES | -0.13551 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.26748 | 19.3 | 19.3 |  |  | -2.6154 | 19.3 | -0.26748 | -5.1623
5935 | SI_RAY10 | 10 | South | YES | -0.13551 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.26748 | 47 | 47 |  |  | -6.3691 | 47 | -0.26748 | -12.5713
80003 | MILHWYS | F | South | YES | -0.13551 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.26748 | 0 | 0 |  |  | 0 | 0 | -0.26748 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.13552 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.26748 | 0 | 0 |  |  | 0 | 0 | -0.26748 | 0
80080 | GWINDT11A | 2 | South | YES | -0.13558 | 17.7 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 41 |  |  | 0 | 0 | -0.26754 | 0
80080 | GWINDT11A | 3 | South | YES | -0.13558 | 16.4 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 38 |  |  | 0 | 0 | -0.26754 | 0
80080 | GWINDT11A | 1 | South | YES | -0.13558 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 94 |  |  | 0 | 0 | -0.26754 | 0
80080 | GWINDT11A | 4 | South | YES | -0.13558 | 8.2 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 19 |  |  | 0 | 0 | -0.26754 | 0
80081 | GWINDT21A | 4 | South | YES | -0.13558 | 9.5 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 22 |  |  | 0 | 0 | -0.26754 | 0
80081 | GWINDT21A | 1 | South | YES | -0.13558 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 94 |  |  | 0 | 0 | -0.26754 | 0
80081 | GWINDT21A | 3 | South | YES | -0.13558 | 18.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 43 |  |  | 0 | 0 | -0.26754 | 0
80081 | GWINDT21A | 2 | South | YES | -0.13558 | 15.5 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 36 |  |  | 0 | 0 | -0.26754 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.13558 | 63 | 0 | 146 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 146 |  |  | 0 | 0 | -0.26754 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.13558 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 50 |  |  | 0 | 0 | -0.26754 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.13558 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 50 |  |  | 0 | 0 | -0.26754 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.13558 | 23.7 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 55 |  |  | 0 | 0 | -0.26754 | 0
8161 | COLETO0A | 1 | South | YES | -0.14053 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.27249 | 0 | 633 |  |  | 0 | 0 | -0.27249 | 0
88198 | BEEVILLE | F | South | YES | -0.14195 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.27391 | 0 | 0 |  |  | 0 | 0 | -0.27391 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.14291 | 19.2 | 6 | 24 | 0 | 1.0161 | GST | -1 | 0.27487 | 24 | 24 |  |  | -3.4298 | 24 | -0.27487 | -6.5969
5891 | PEARSALLGEN2 | 1 | South | YES | -0.14291 | 19.4 | 6 | 24.3 | 0 | 1.0161 | GST | -1 | 0.27487 | 24.3 | 24.3 |  |  | -3.4726 | 24.3 | -0.27487 | -6.6793
5892 | PEARSALLGEN3 | 1 | South | YES | -0.14291 | 19.1 | 6 | 23.9 | 0 | 1.0161 | GST | -1 | 0.27487 | 23.9 | 23.9 |  |  | -3.4155 | 23.9 | -0.27487 | -6.5694
5903 | SANMIGUELGEN | 1 | South | YES | -0.15279 | 396.3 | 180 | 396.3 | 0 | 1.0331 | LIGCO | -1 | 0.28475 | 0 | 396.3 |  |  | 0 | 0 | -0.28475 | 0
8189 | CUECPL2A | 1 | South | YES | -0.1587 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.29066 | 0 | 0 |  |  | 0 | 0 | -0.29066 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.16004 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.292 | 58 | 58 |  |  | -9.2821 | 58 | -0.292 | -16.9359
5265 | LEON_LCP4G4 | 4 | South | YES | -0.16004 | 71.2 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.292 | 89 | 89 |  |  | -14.2432 | 89 | -0.292 | -25.9879
5266 | LEON_LCPCT1 | 1 | South | YES | -0.16004 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.292 | 44 | 44 |  |  | -7.0416 | 44 | -0.292 | -12.8479
5267 | LEON_LCPCT2 | 2 | South | YES | -0.16004 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.292 | 44 | 44 |  |  | -7.0416 | 44 | -0.292 | -12.8479
5268 | LEON_LCPCT3 | 3 | South | YES | -0.16004 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.292 | 43 | 43 |  |  | -6.8815 | 43 | -0.292 | -12.5559
5269 | LEON_LCPCT4 | 4 | South | YES | -0.16004 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.292 | 45 | 45 |  |  | -7.2016 | 45 | -0.292 | -13.1399
5401 | CALAVER_JKS1 | 1 | South | YES | -0.16034 | 562 | 100 | 562 | 0 | 1.018 | LIGCO | -1 | 0.29231 | 0 | 562 |  |  | 0 | 0 | -0.29231 | 0
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.16101 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.29297 | 155 | 155 |  |  | -24.9567 | 155 | -0.29297 | -45.4109
5477 | BRA_AVR1_ST1 | 1 | South | YES | -0.16101 | 174 | 138 | 174 | 0 | 1.017 | CC | -1 | 0.29297 | 174 | 174 |  |  | -28.0159 | 174 | -0.29297 | -50.9774
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.16101 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.29297 | 155 | 155 |  |  | -24.9567 | 155 | -0.29297 | -45.4109
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.16102 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.29298 | 407 | 407 |  |  | -65.5339 | 407 | -0.29298 | -119.2426
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.1611 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.29306 | 215 | 215 |  |  | -34.6361 | 215 | -0.29306 | -63.008
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.1611 | 172.8 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.29306 | 216 | 216 |  |  | -34.7972 | 216 | -0.29306 | -63.301
5031 | BRA_VHBCT1 | 1 | South | YES | -0.1611 | 44 | 24 | 44 | 0 | 1.0192 | GST | -1 | 0.29306 | 44 | 44 |  |  | -7.0883 | 44 | -0.29306 | -12.8947
5032 | BRA_VHBCT2 | 2 | South | YES | -0.1611 | 44 | 24 | 44 | 0 | 1.0192 | GST | -1 | 0.29306 | 44 | 44 |  |  | -7.0883 | 44 | -0.29306 | -12.8947
5033 | BRA_VHBCT3 | 3 | South | YES | -0.1611 | 43 | 24 | 43 | 0 | 1.0192 | GST | -1 | 0.29306 | 43 | 43 |  |  | -6.9272 | 43 | -0.29306 | -12.6016
5034 | BRA_VHBCT4 | 4 | South | YES | -0.1611 | 45 | 24 | 45 | 0 | 1.0192 | GST | -1 | 0.29306 | 45 | 45 |  |  | -7.2494 | 45 | -0.29306 | -13.1877
5396 | CALAVER_OWS1 | 1 | South | YES | -0.16129 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.29325 | 418 | 418 |  |  | -67.4192 | 418 | -0.29325 | -122.5795
5397 | CALAVER_OWS2 | 2 | South | YES | -0.16129 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.29325 | 400 | 400 |  |  | -64.516 | 400 | -0.29325 | -117.3009
5111 | CALAVER_JTD1 | 1 | South | YES | -0.16145 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.29341 | 0 | 430 |  |  | 0 | 0 | -0.29341 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.16145 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.29341 | 0 | 430 |  |  | 0 | 0 | -0.29341 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.16202 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.29398 | 61 | 61 |  |  | -9.883 | 61 | -0.29398 | -17.9327
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.16202 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.29398 | 95 | 95 |  |  | -15.3916 | 95 | -0.29398 | -27.928
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.16202 | 120.8 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.29398 | 151 | 151 |  |  | -24.4646 | 151 | -0.29398 | -44.3909
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.1653 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.29726 | 0 | 0 |  |  | 0 | 0 | -0.29726 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.16582 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.29778 | 147 | 147 |  |  | -24.3751 | 147 | -0.29778 | -43.7736
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.16582 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.29778 | 138 | 138 |  |  | -22.8827 | 138 | -0.29778 | -41.0935
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.16582 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.29778 | 146 | 146 |  |  | -24.2093 | 146 | -0.29778 | -43.4758
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.16582 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.29778 | 149 | 149 |  |  | -24.7067 | 149 | -0.29778 | -44.3691
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.16582 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.29778 | 182 | 182 |  |  | -30.1787 | 182 | -0.29778 | -54.1958
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.16582 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.29778 | 203 | 203 |  |  | -33.6609 | 203 | -0.29778 | -60.4492
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.16804 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.30001 | 0 | 0 |  |  | 0 | 0 | -0.30001 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.16804 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.30001 | 0 | 0 |  |  | 0 | 0 | -0.30001 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.16914 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.30111 | 0 | 0 |  |  | 0 | 0 | -0.30111 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.17097 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.30294 | 0 | 0 |  |  | 0 | 0 | -0.30294 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.17097 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.30294 | 0 | 0 |  |  | 0 | 0 | -0.30294 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.17097 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.30294 | 0 | 0 |  |  | 0 | 0 | -0.30294 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.17152 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.30349 | 148 | 148 |  |  | -25.3854 | 148 | -0.30349 | -44.9158
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.17152 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.30349 | 148 | 148 |  |  | -25.3854 | 148 | -0.30349 | -44.9158
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.17152 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.30349 | 154 | 154 |  |  | -26.4145 | 154 | -0.30349 | -46.7367
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.17152 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.30349 | 293 | 293 |  |  | -50.2562 | 293 | -0.30349 | -88.9212
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.17161 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.30357 | 0 | 0 |  |  | 0 | 0 | -0.30357 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.17161 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.30357 | 0 | 0 |  |  | 0 | 0 | -0.30357 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.17161 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.30357 | 0 | 0 |  |  | 0 | 0 | -0.30357 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.17207 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.30403 | 423.3 | 423.3 |  |  | -72.8372 | 423.3 | -0.30403 | -128.6969
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.17343 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.30539 | 0 | 0 |  |  | 0 | 0 | -0.30539 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.17343 | 23 | 0 | 29.8 |  | 1 | Hydro | -1 | 0.30539 | 0 | 0 |  |  | 0 | 0 | -0.30539 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.1776 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.30956 | 223.9 | 223.9 |  |  | -39.7635 | 223.9 | -0.30956 | -69.3099
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.1776 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.30956 | 225 | 225 |  |  | -39.9589 | 225 | -0.30956 | -69.6504
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.1776 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.30956 | 224.6 | 224.6 |  |  | -39.8878 | 224.6 | -0.30956 | -69.5266
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.1776 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.30956 | 226.7 | 226.7 |  |  | -40.2608 | 226.7 | -0.30956 | -70.1766
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.17833 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.31029 | 0 | 0 |  |  | 0 | 0 | -0.31029 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.17833 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.31029 | 0 | 0 |  |  | 0 | 0 | -0.31029 | 0
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.17897 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.31093 | 0 | 0 |  |  | 0 | 0 | -0.31093 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.18111 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.31307 | 50 | 50 |  |  | -9.0555 | 50 | -0.31307 | -15.6536
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.18111 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.31307 | 50 | 50 |  |  | -9.0555 | 50 | -0.31307 | -15.6536
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.18111 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.31307 | 50 | 50 |  |  | -9.0555 | 50 | -0.31307 | -15.6536
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.18111 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.31307 | 50 | 50 |  |  | -9.0555 | 50 | -0.31307 | -15.6536
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.18267 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.31463 | 0 | 436 |  |  | 0 | 0 | -0.31463 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.18284 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.3148 | 0 | 606 |  |  | 0 | 0 | -0.3148 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.18284 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.3148 | 0 | 598 |  |  | 0 | 0 | -0.3148 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.19251 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.32448 | 0 | 0 |  |  | 0 | 0 | -0.32448 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.19251 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.32448 | 0 | 0 |  |  | 0 | 0 | -0.32448 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.19251 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.32448 | 0 | 0 |  |  | 0 | 0 | -0.32448 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.19516 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.32712 | 132 | 132 |  |  | -25.7613 | 132 | -0.32712 | -43.1803
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.19516 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.32712 | 139 | 139 |  |  | -27.1274 | 139 | -0.32712 | -45.4701
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.19516 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.32712 | 329 | 329 |  |  | -64.208 | 329 | -0.32712 | -107.6236
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.19989 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.33185 | 0 | 0 |  |  | 0 | 0 | -0.33185 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.19989 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.33185 | 0 | 0 |  |  | 0 | 0 | -0.33185 | 0
9016 | SANDH_G1 | 1 | South | YES | -0.20054 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.3325 | 49 | 49 |  |  | -9.8264 | 49 | -0.3325 | -16.2925
9017 | SANDH_G2 | 2 | South | YES | -0.20054 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.3325 | 46 | 46 |  |  | -9.2247 | 46 | -0.3325 | -15.295
9018 | SANDH_G3 | 3 | South | YES | -0.20054 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.3325 | 46 | 46 |  |  | -9.2247 | 46 | -0.3325 | -15.295
9019 | SANDH_G4 | 4 | South | YES | -0.20054 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.3325 | 47 | 47 |  |  | -9.4253 | 47 | -0.3325 | -15.6275
9020 | SANDHG5A | 5A | South | YES | -0.20054 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.3325 | 155 | 155 |  |  | -31.0834 | 155 | -0.3325 | -51.5376
9021 | SANDHG5C | 5C | South | YES | -0.20054 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.3325 | 148 | 148 |  |  | -29.6796 | 148 | -0.3325 | -49.21
9000 | DECKR_G1 | 1 | South | YES | -0.20155 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.33352 | 321 | 321 |  |  | -64.6988 | 321 | -0.33352 | -107.0587
9001 | DECKR_G2 | 2 | South | YES | -0.20155 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.33352 | 426 | 426 |  |  | -85.862 | 426 | -0.33352 | -142.078
9002 | DECKR_G3 | 3 | South | YES | -0.20355 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.33551 | 42 | 42 |  |  | -8.5489 | 42 | -0.33551 | -14.0913
9003 | DECKR_G4 | 4 | South | YES | -0.20355 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.33551 | 44 | 44 |  |  | -8.956 | 44 | -0.33551 | -14.7623
9004 | DECKR_G5 | 5 | South | YES | -0.20355 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.33551 | 44 | 44 |  |  | -8.956 | 44 | -0.33551 | -14.7623
9005 | DECKR_G6 | 6 | South | YES | -0.20355 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.33551 | 47 | 47 |  |  | -9.5666 | 47 | -0.33551 | -15.7688
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.20492 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.33688 | 158 | 158 |  |  | -32.377 | 158 | -0.33688 | -53.2271
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.20492 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.33688 | 160 | 160 |  |  | -32.7869 | 160 | -0.33688 | -53.9009
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.20492 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.33688 | 175 | 175 |  |  | -35.8606 | 175 | -0.33688 | -58.9541
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.20525 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.33721 | 152.5 | 152.5 |  |  | -31.3005 | 152.5 | -0.33721 | -51.4247
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.20525 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.33721 | 149.5 | 149.5 |  |  | -30.6847 | 149.5 | -0.33721 | -50.4131
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.20525 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.33721 | 232.6 | 232.6 |  |  | -47.7409 | 232.6 | -0.33721 | -78.4354
3432 | SANDOW_4G | 4 | South | YES | -0.24826 | 580 | 225 | 580 | 0 | 1.029 | LIGCO | -1 | 0.38022 | 0 | 580 |  |  | 0 | 0 | -0.38022 | 0
13432 | SANDOW_5G | 5 | South | YES | -0.24826 | 581 | 225 | 581 | 0 | 1.029 | LIGCO | -1 | 0.38022 | 0 | 581 |  |  | 0 | 0 | -0.38022 | 0
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Concentrated Capacity | Cumulative Concentrated Impact | Cont_ Lake to Tradinghouse and TemplePEC to Tradinghouse OL_ TempleSS to LakeCreek
3432 | SANDOW_4G | 4 | South | YES | -0.24826 | 580 | 225 | 580 | 0 | 1.029 | LIGCO | -1 | 0.38022 | 0 | 580 |  |  | 0 | 0 | -0.38022 | 0 | 0 | 0
13432 | SANDOW_5G | 5 | South | YES | -0.24826 | 581 | 225 | 581 | 0 | 1.029 | LIGCO | -1 | 0.38022 | 0 | 581 |  |  | 0 | 0 | -0.38022 | 0 | 0 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.20525 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.33721 | 152.5 | 152.5 |  |  | -31.3005 | 152.5 | -0.33721 | -51.4247 | 152.5 | 51.4247
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.20525 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.33721 | 149.5 | 149.5 |  |  | -30.6847 | 149.5 | -0.33721 | -50.4131 | 302 | 101.8378 | Weighted Shift Factors
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.20525 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.33721 | 232.6 | 232.6 |  |  | -47.7409 | 232.6 | -0.33721 | -78.4354 | 534.6 | 180.2732 | North | 0.13196
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.20492 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.33688 | 158 | 158 |  |  | -32.377 | 158 | -0.33688 | -53.2271 | 692.6 | 233.5003 | South | -0.16872
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.20492 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.33688 | 160 | 160 |  |  | -32.7869 | 160 | -0.33688 | -53.9009 | 852.6 | 287.4011 |  | 0.30068
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.20492 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.33688 | 175 | 175 |  |  | -35.8606 | 175 | -0.33688 | -58.9541 | 1027.6 | 346.3552
9002 | DECKR_G3 | 3 | South | YES | -0.20355 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.33551 | 42 | 42 |  |  | -8.5489 | 42 | -0.33551 | -14.0913 | 1069.6 | 360.4465 | Line Cap | 1072
9003 | DECKR_G4 | 4 | South | YES | -0.20355 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.33551 | 44 | 44 |  |  | -8.956 | 44 | -0.33551 | -14.7623 | 1113.6 | 375.2088 | Conc Gen | 2294.6
9004 | DECKR_G5 | 5 | South | YES | -0.20355 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.33551 | 44 | 44 |  |  | -8.956 | 44 | -0.33551 | -14.7623 | 1157.6 | 389.9711 | Weighted Imp. | 768.9243
9005 | DECKR_G6 | 6 | South | YES | -0.20355 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.33551 | 47 | 47 |  |  | -9.5666 | 47 | -0.33551 | -15.7688 | 1204.6 | 405.74 | PTDF | 0.3351
9000 | DECKR_G1 | 1 | South | YES | -0.20155 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.33352 | 321 | 321 |  |  | -64.6988 | 321 | -0.33352 | -107.0587 | 1525.6 | 512.7987
9001 | DECKR_G2 | 2 | South | YES | -0.20155 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.33352 | 426 | 426 |  |  | -85.862 | 426 | -0.33352 | -142.078 | 1951.6 | 654.8767 | Concentration | 1.1145
9016 | SANDH_G1 | 1 | South | YES | -0.20054 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.3325 | 49 | 49 |  |  | -9.8264 | 49 | -0.3325 | -16.2925 | 2000.6 | 671.1692
9017 | SANDH_G2 | 2 | South | YES | -0.20054 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.3325 | 46 | 46 |  |  | -9.2247 | 46 | -0.3325 | -15.295 | 2046.6 | 686.4642 |  | Pass
9018 | SANDH_G3 | 3 | South | YES | -0.20054 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.3325 | 46 | 46 |  |  | -9.2247 | 46 | -0.3325 | -15.295 | 2092.6 | 701.7592
9019 | SANDH_G4 | 4 | South | YES | -0.20054 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.3325 | 47 | 47 |  |  | -9.4253 | 47 | -0.3325 | -15.6275 | 2139.6 | 717.3867
9020 | SANDHG5A | 5A | South | YES | -0.20054 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.3325 | 155 | 155 |  |  | -31.0834 | 155 | -0.3325 | -51.5376 | 2294.6 | 768.9243
9021 | SANDHG5C | 5C | South | YES | -0.20054 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.3325 | 148 | 148 |  |  | -29.6796 | 148 | -0.3325 | -49.21
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.19989 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.33185 | 0 | 0 |  |  | 0 | 0 | -0.33185 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.19989 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.33185 | 0 | 0 |  |  | 0 | 0 | -0.33185 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.19516 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.32712 | 132 | 132 |  |  | -25.7613 | 132 | -0.32712 | -43.1803
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.19516 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.32712 | 139 | 139 |  |  | -27.1274 | 139 | -0.32712 | -45.4701
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.19516 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.32712 | 329 | 329 |  |  | -64.208 | 329 | -0.32712 | -107.6236
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.19251 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.32448 | 0 | 0 |  |  | 0 | 0 | -0.32448 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.19251 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.32448 | 0 | 0 |  |  | 0 | 0 | -0.32448 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.19251 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.32448 | 0 | 0 |  |  | 0 | 0 | -0.32448 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.18284 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.3148 | 0 | 606 |  |  | 0 | 0 | -0.3148 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.18284 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.3148 | 0 | 598 |  |  | 0 | 0 | -0.3148 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.18267 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.31463 | 0 | 436 |  |  | 0 | 0 | -0.31463 | 0
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.18111 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.31307 | 50 | 50 |  |  | -9.0555 | 50 | -0.31307 | -15.6536
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.18111 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.31307 | 50 | 50 |  |  | -9.0555 | 50 | -0.31307 | -15.6536
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.18111 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.31307 | 50 | 50 |  |  | -9.0555 | 50 | -0.31307 | -15.6536
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.18111 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.31307 | 50 | 50 |  |  | -9.0555 | 50 | -0.31307 | -15.6536
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.17897 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.31093 | 0 | 0 |  |  | 0 | 0 | -0.31093 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.17833 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.31029 | 0 | 0 |  |  | 0 | 0 | -0.31029 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.17833 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.31029 | 0 | 0 |  |  | 0 | 0 | -0.31029 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.1776 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.30956 | 223.9 | 223.9 |  |  | -39.7635 | 223.9 | -0.30956 | -69.3099
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.1776 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.30956 | 225 | 225 |  |  | -39.9589 | 225 | -0.30956 | -69.6504
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.1776 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.30956 | 224.6 | 224.6 |  |  | -39.8878 | 224.6 | -0.30956 | -69.5266
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.1776 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.30956 | 226.7 | 226.7 |  |  | -40.2608 | 226.7 | -0.30956 | -70.1766
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.17343 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.30539 | 0 | 0 |  |  | 0 | 0 | -0.30539 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.17343 | 23 | 0 | 29.8 |  | 1 | Hydro | -1 | 0.30539 | 0 | 0 |  |  | 0 | 0 | -0.30539 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.17207 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.30403 | 423.3 | 423.3 |  |  | -72.8372 | 423.3 | -0.30403 | -128.6969
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.17161 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.30357 | 0 | 0 |  |  | 0 | 0 | -0.30357 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.17161 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.30357 | 0 | 0 |  |  | 0 | 0 | -0.30357 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.17161 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.30357 | 0 | 0 |  |  | 0 | 0 | -0.30357 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.17152 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.30349 | 148 | 148 |  |  | -25.3854 | 148 | -0.30349 | -44.9158
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.17152 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.30349 | 148 | 148 |  |  | -25.3854 | 148 | -0.30349 | -44.9158
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.17152 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.30349 | 154 | 154 |  |  | -26.4145 | 154 | -0.30349 | -46.7367
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.17152 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.30349 | 293 | 293 |  |  | -50.2562 | 293 | -0.30349 | -88.9212
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.17097 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.30294 | 0 | 0 |  |  | 0 | 0 | -0.30294 | 0
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.17097 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.30294 | 0 | 0 |  |  | 0 | 0 | -0.30294 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.17097 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.30294 | 0 | 0 |  |  | 0 | 0 | -0.30294 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.16914 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.30111 | 0 | 0 |  |  | 0 | 0 | -0.30111 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.16804 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.30001 | 0 | 0 |  |  | 0 | 0 | -0.30001 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.16804 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.30001 | 0 | 0 |  |  | 0 | 0 | -0.30001 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.16582 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.29778 | 147 | 147 |  |  | -24.3751 | 147 | -0.29778 | -43.7736
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.16582 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.29778 | 138 | 138 |  |  | -22.8827 | 138 | -0.29778 | -41.0935
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.16582 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.29778 | 146 | 146 |  |  | -24.2093 | 146 | -0.29778 | -43.4758
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.16582 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.29778 | 149 | 149 |  |  | -24.7067 | 149 | -0.29778 | -44.3691
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.16582 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.29778 | 182 | 182 |  |  | -30.1787 | 182 | -0.29778 | -54.1958
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.16582 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.29778 | 203 | 203 |  |  | -33.6609 | 203 | -0.29778 | -60.4492
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.1653 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.29726 | 0 | 0 |  |  | 0 | 0 | -0.29726 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.16202 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.29398 | 61 | 61 |  |  | -9.883 | 61 | -0.29398 | -17.9327
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.16202 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.29398 | 95 | 95 |  |  | -15.3916 | 95 | -0.29398 | -27.928
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.16202 | 120.8 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.29398 | 151 | 151 |  |  | -24.4646 | 151 | -0.29398 | -44.3909
5111 | CALAVER_JTD1 | 1 | South | YES | -0.16145 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.29341 | 0 | 430 |  |  | 0 | 0 | -0.29341 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.16145 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.29341 | 0 | 430 |  |  | 0 | 0 | -0.29341 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | -0.16129 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.29325 | 418 | 418 |  |  | -67.4192 | 418 | -0.29325 | -122.5795
5397 | CALAVER_OWS2 | 2 | South | YES | -0.16129 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.29325 | 400 | 400 |  |  | -64.516 | 400 | -0.29325 | -117.3009
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.1611 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.29306 | 215 | 215 |  |  | -34.6361 | 215 | -0.29306 | -63.008
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.1611 | 172.8 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.29306 | 216 | 216 |  |  | -34.7972 | 216 | -0.29306 | -63.301
5031 | BRA_VHBCT1 | 1 | South | YES | -0.1611 | 44 | 24 | 44 | 0 | 1.0192 | GST | -1 | 0.29306 | 44 | 44 |  |  | -7.0883 | 44 | -0.29306 | -12.8947
5032 | BRA_VHBCT2 | 2 | South | YES | -0.1611 | 44 | 24 | 44 | 0 | 1.0192 | GST | -1 | 0.29306 | 44 | 44 |  |  | -7.0883 | 44 | -0.29306 | -12.8947
5033 | BRA_VHBCT3 | 3 | South | YES | -0.1611 | 43 | 24 | 43 | 0 | 1.0192 | GST | -1 | 0.29306 | 43 | 43 |  |  | -6.9272 | 43 | -0.29306 | -12.6016
5034 | BRA_VHBCT4 | 4 | South | YES | -0.1611 | 45 | 24 | 45 | 0 | 1.0192 | GST | -1 | 0.29306 | 45 | 45 |  |  | -7.2494 | 45 | -0.29306 | -13.1877
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.16102 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.29298 | 407 | 407 |  |  | -65.5339 | 407 | -0.29298 | -119.2426
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.16101 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.29297 | 155 | 155 |  |  | -24.9567 | 155 | -0.29297 | -45.4109
5477 | BRA_AVR1_ST1 | 1 | South | YES | -0.16101 | 174 | 138 | 174 | 0 | 1.017 | CC | -1 | 0.29297 | 174 | 174 |  |  | -28.0159 | 174 | -0.29297 | -50.9774
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.16101 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.29297 | 155 | 155 |  |  | -24.9567 | 155 | -0.29297 | -45.4109
5401 | CALAVER_JKS1 | 1 | South | YES | -0.16034 | 562 | 100 | 562 | 0 | 1.018 | LIGCO | -1 | 0.29231 | 0 | 562 |  |  | 0 | 0 | -0.29231 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.16004 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.292 | 58 | 58 |  |  | -9.2821 | 58 | -0.292 | -16.9359
5265 | LEON_LCP4G4 | 4 | South | YES | -0.16004 | 71.2 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.292 | 89 | 89 |  |  | -14.2432 | 89 | -0.292 | -25.9879
5266 | LEON_LCPCT1 | 1 | South | YES | -0.16004 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.292 | 44 | 44 |  |  | -7.0416 | 44 | -0.292 | -12.8479
5267 | LEON_LCPCT2 | 2 | South | YES | -0.16004 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.292 | 44 | 44 |  |  | -7.0416 | 44 | -0.292 | -12.8479
5268 | LEON_LCPCT3 | 3 | South | YES | -0.16004 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.292 | 43 | 43 |  |  | -6.8815 | 43 | -0.292 | -12.5559
5269 | LEON_LCPCT4 | 4 | South | YES | -0.16004 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.292 | 45 | 45 |  |  | -7.2016 | 45 | -0.292 | -13.1399
8189 | CUECPL2A | 1 | South | YES | -0.1587 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.29066 | 0 | 0 |  |  | 0 | 0 | -0.29066 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.15279 | 396.3 | 180 | 396.3 | 0 | 1.0331 | LIGCO | -1 | 0.28475 | 0 | 396.3 |  |  | 0 | 0 | -0.28475 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.14291 | 19.2 | 6 | 24 | 0 | 1.0161 | GST | -1 | 0.27487 | 24 | 24 |  |  | -3.4298 | 24 | -0.27487 | -6.5969
5891 | PEARSALLGEN2 | 1 | South | YES | -0.14291 | 19.4 | 6 | 24.3 | 0 | 1.0161 | GST | -1 | 0.27487 | 24.3 | 24.3 |  |  | -3.4726 | 24.3 | -0.27487 | -6.6793
5892 | PEARSALLGEN3 | 1 | South | YES | -0.14291 | 19.1 | 6 | 23.9 | 0 | 1.0161 | GST | -1 | 0.27487 | 23.9 | 23.9 |  |  | -3.4155 | 23.9 | -0.27487 | -6.5694
88198 | BEEVILLE | F | South | YES | -0.14195 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.27391 | 0 | 0 |  |  | 0 | 0 | -0.27391 | 0
8161 | COLETO0A | 1 | South | YES | -0.14053 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.27249 | 0 | 633 |  |  | 0 | 0 | -0.27249 | 0
80080 | GWINDT11A | 2 | South | YES | -0.13558 | 17.7 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 41 |  |  | 0 | 0 | -0.26754 | 0
80080 | GWINDT11A | 3 | South | YES | -0.13558 | 16.4 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 38 |  |  | 0 | 0 | -0.26754 | 0
80080 | GWINDT11A | 1 | South | YES | -0.13558 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 94 |  |  | 0 | 0 | -0.26754 | 0
80080 | GWINDT11A | 4 | South | YES | -0.13558 | 8.2 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 19 |  |  | 0 | 0 | -0.26754 | 0
80081 | GWINDT21A | 4 | South | YES | -0.13558 | 9.5 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 22 |  |  | 0 | 0 | -0.26754 | 0
80081 | GWINDT21A | 1 | South | YES | -0.13558 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 94 |  |  | 0 | 0 | -0.26754 | 0
80081 | GWINDT21A | 3 | South | YES | -0.13558 | 18.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 43 |  |  | 0 | 0 | -0.26754 | 0
80081 | GWINDT21A | 2 | South | YES | -0.13558 | 15.5 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 36 |  |  | 0 | 0 | -0.26754 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.13558 | 63 | 0 | 146 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 146 |  |  | 0 | 0 | -0.26754 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.13558 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 50 |  |  | 0 | 0 | -0.26754 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.13558 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 50 |  |  | 0 | 0 | -0.26754 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.13558 | 23.7 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.26754 | 0 | 55 |  |  | 0 | 0 | -0.26754 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.13552 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.26748 | 0 | 0 |  |  | 0 | 0 | -0.26748 | 0
5932 | SI_RAY9 | 9 | South | YES | -0.13551 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.26748 | 38 | 38 |  |  | -5.1495 | 38 | -0.26748 | -10.1641
5933 | SI_RAY6 | 6 | South | YES | -0.13551 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.26748 | 19.3 | 19.3 |  |  | -2.6154 | 19.3 | -0.26748 | -5.1623
5935 | SI_RAY10 | 10 | South | YES | -0.13551 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.26748 | 47 | 47 |  |  | -6.3691 | 47 | -0.26748 | -12.5713
80003 | MILHWYS | F | South | YES | -0.13551 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.26748 | 0 | 0 |  |  | 0 | 0 | -0.26748 | 0
8981 | HECN1 | 1 | South | YES | -0.13539 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.26736 | 144.8 | 144.8 |  |  | -19.6052 | 144.8 | -0.26736 | -38.7133
8982 | HECN2 | 2 | South | YES | -0.13539 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.26736 | 144.1 | 144.1 |  |  | -19.5104 | 144.1 | -0.26736 | -38.5262
8983 | HECN3 | 3 | South | YES | -0.13539 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.26736 | 171.9 | 171.9 |  |  | -23.2744 | 171.9 | -0.26736 | -45.9587
8936 | MVGN#1 | 1 | South | YES | -0.13539 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.26736 | 216.6 | 216.6 |  |  | -29.3263 | 216.6 | -0.26736 | -57.9094
8937 | MVGN#2 | 2 | South | YES | -0.13539 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.26736 | 216.7 | 216.7 |  |  | -29.3399 | 216.7 | -0.26736 | -57.9361
8938 | MVGN#3 | 3 | South | YES | -0.13539 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.26736 | 250.9 | 250.9 |  |  | -33.9704 | 250.9 | -0.26736 | -67.0797
8933 | FGNTS001 | 1 | South | YES | -0.13523 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.2672 | 146.5 | 146.5 |  |  | -19.8118 | 146.5 | -0.2672 | -39.1443
8934 | FGNTS101 | 2 | South | YES | -0.13523 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.2672 | 147.9 | 147.9 |  |  | -20.0011 | 147.9 | -0.2672 | -39.5183
8935 | FGNTS201 | 3 | South | YES | -0.13523 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.2672 | 173 | 173 |  |  | -23.3955 | 173 | -0.2672 | -46.225
8461 | KOCH_UP0A | 1 | South | YES | -0.13513 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.26709 | 0 | 0 |  |  | 0 | 0 | -0.26709 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.13513 | 30.3 | 0 | 38 |  | 1.027 | Cogen | -1 | 0.26709 | 0 | 0 |  |  | 0 | 0 | -0.26709 | 0
8506 | VAL #1 | 1 | South | YES | -0.13501 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.26697 | 0 | 0 |  |  | 0 | 0 | -0.26697 | 0
8507 | VAL #2 | 2 | South | YES | -0.13501 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.26697 | 0 | 0 |  |  | 0 | 0 | -0.26697 | 0
8459 | B_DAVIS0B | MB | South | YES | -0.13494 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.2669 | 0 | 0 |  |  | 0 | 0 | -0.2669 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.13494 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.2669 | 0 | 0 |  |  | 0 | 0 | -0.2669 | 0
8456 | COSW#1 | 1 | South | YES | -0.1348 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.26676 | 0 | 0 |  |  | 0 | 0 | -0.26676 | 0
8457 | COSW#2 | 2 | South | YES | -0.1348 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.26676 | 0 | 0 |  |  | 0 | 0 | -0.26676 | 0
8173 | VICEC51A | 5 | South | YES | -0.13479 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.26675 | 144 | 144 |  |  | -19.4095 | 144 | -0.26675 | -38.412
8174 | VICEC61A | 6 | South | YES | -0.13479 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.26675 | 188 | 188 |  |  | -25.3401 | 188 | -0.26675 | -50.1491
88508 | FALFURRI | F | South | YES | -0.13477 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.26673 | 0 | 0 |  |  | 0 | 0 | -0.26673 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.13473 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.2667 | 0 | 0 |  |  | 0 | 0 | -0.2667 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.13473 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.2667 | 0 | 0 |  |  | 0 | 0 | -0.2667 | 0
8562 | CNOPST1 | 3 | South | YES | -0.13473 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.2667 | 0 | 0 |  |  | 0 | 0 | -0.2667 | 0
5728 | FALCONHYDRO2 | 2 | South | YES | -0.13426 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.26622 | 0 | 0 |  |  | 0 | 0 | -0.26622 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.13426 | 11 | 0 | 11 | 0 | 1.0227 | Hydro | -1 | 0.26622 | 0 | 0 |  |  | 0 | 0 | -0.26622 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.13426 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.26622 | 0 | 0 |  |  | 0 | 0 | -0.26622 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.13362 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.13362 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.13362 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
8930 | ICPGN10A | 1 | South | YES | -0.13362 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
8931 | ICPGN20A | 2 | South | YES | -0.13362 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
8932 | ICPGN30A | 3 | South | YES | -0.13362 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
80223 | REYSHR G | 1 | South | YES | -0.13362 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.26558 | 0 | 0 |  |  | 0 | 0 | -0.26558 | 0
8066 | DUP1V#1 | 1 | South | YES | -0.13347 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.26543 | 0 | 0 |  |  | 0 | 0 | -0.26543 | 0
5508 | RAYBURNCC9 | 1 | South | YES | -0.13335 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.26531 | 47.7 | 47.7 |  |  | -6.3606 | 47.7 | -0.26531 | -12.6552
5509 | RAYBURNCC10 | 1 | South | YES | -0.13335 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.26531 | 37.3 | 37.3 |  |  | -4.9738 | 37.3 | -0.26531 | -9.896
5511 | RAYBURNCC7 | 1 | South | YES | -0.13335 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.26531 | 47.5 | 47.5 |  |  | -6.3339 | 47.5 | -0.26531 | -12.6021
5512 | RAYBURNCC8 | 1 | South | YES | -0.13335 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.26531 | 49.3 | 49.3 |  |  | -6.574 | 49.3 | -0.26531 | -13.0797
88299 | ZAPATA | F | South | YES | -0.13332 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.26528 | 0 | 0 |  |  | 0 | 0 | -0.26528 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.13225 | 17.6 | 6 | 22 | 0 | 1.0223 | GST | -1 | 0.26421 | 22 | 22 |  |  | -2.9095 | 22 | -0.26421 | -5.8127
5505 | RAYBURNGEN1 | 1 | South | YES | -0.13225 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.26421 | 11 | 11 |  |  | -1.4547 | 11 | -0.26421 | -2.9063
5506 | RAYBURNGEN2 | 1 | South | YES | -0.13225 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.26421 | 11 | 11 |  |  | -1.4547 | 11 | -0.26421 | -2.9063
80012 | LAR | F | South | YES | -0.13196 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.26393 | 0 | 0 |  |  | 0 | 0 | -0.26393 | 0
80265 | LARECU40A | 4 | South | YES | -0.13196 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.26393 | 100 | 100 |  |  | -13.1963 | 100 | -0.26393 | -26.3925
80266 | LARECU50A | 5 | South | YES | -0.13196 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.26393 | 100 | 100 |  |  | -13.1963 | 100 | -0.26393 | -26.3925
80224 | VISTRONG1 | 1 | South | YES | -0.13116 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.26312 | 0 | 0 |  |  | 0 | 0 | -0.26312 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.13116 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.26312 | 0 | 0 |  |  | 0 | 0 | -0.26312 | 0
80227 | AIRCO G | 1 | South | YES | -0.1303 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.26226 | 0 | 0 |  |  | 0 | 0 | -0.26226 | 0
8147 | UCAR #2 | 10 | South | YES | -0.12993 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
8148 | UCAR #1 | 2 | South | YES | -0.12993 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80137 | CSDR89 | 9 | South | YES | -0.12993 | 0 | 0 | 15 |  | 1.003 | DCTie | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80137 | CSDR89 | 8 | South | YES | -0.12993 | 33.9 | 0 | 39 |  | 1.003 | DCTie | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80138 | CSDR7 | 7 | South | YES | -0.12993 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80139 | CSDR56 | 6 | South | YES | -0.12993 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80139 | CSDR56 | 5 | South | YES | -0.12993 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80140 | CSDR11 | 11 | South | YES | -0.12993 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.26189 | 0 | 0 |  |  | 0 | 0 | -0.26189 | 0
80226 | ALCOA G | 1 | South | YES | -0.12671 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.25867 | 0 | 0 |  |  | 0 | 0 | -0.25867 | 0
8134 | FOR #1 | 1 | South | YES | -0.12574 | 54.1 | 45 | 79 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
8138 | FOR #2 | 2 | South | YES | -0.12574 | 63.1 | 45 | 81 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
8153 | FOR #3 | 3 | South | YES | -0.12574 | 63.1 | 45 | 79.9 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
8154 | FOR #4 | 4 | South | YES | -0.12574 | 63.1 | 60 | 80 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
8155 | FOR #5 | 5 | South | YES | -0.12574 | 63.1 | 60 | 78.4 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
8156 | FOR #6 | 6 | South | YES | -0.12574 | 24.9 | 5 | 25 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
8157 | FOR #7 | 7 | South | YES | -0.12574 | 28.8 | 5 | 46 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
80051 | FOR #8 | 8 | South | YES | -0.12574 | 28 | 28 | 28 | 0 | 1.016 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
80052 | FOR #9 | 9 | South | YES | -0.12574 | 29.7 | 5 | 43.6 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
80053 | FOR #10 | 10 | South | YES | -0.12574 | 68.4 | 45 | 75 | 0 | 1.03 | Cogen | -1 | 0.25771 | 0 | 0 |  |  | 0 | 0 | -0.25771 | 0
80010 | EPLVT1 | F | South | YES | -0.095179 | 0 | 0 | 0 |  | 1.0376 | AVR | -1 | 0.22714 | 0 | 0 |  |  | 0 | 0 | -0.22714 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | -0.091154 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.22312 | 0 | 0 |  |  |  |  | -0.22312 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.091154 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.22312 | 0 | 0 |  |  |  |  | -0.22312 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.0905 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22246 | 76 | 76 |  |  |  |  | -0.22246 | -16.9071
48732 | CBE_GT2 | 1 | Houston | YES | -0.0905 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22246 | 76 | 76 |  |  |  |  | -0.22246 | -16.9071
48733 | CBE_ST12 | 1 | Houston | YES | -0.0905 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.22246 | 105 | 105 |  |  |  |  | -0.22246 | -23.3585
48734 | CBE_GT3 | 1 | Houston | YES | -0.0905 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22246 | 76 | 76 |  |  |  |  | -0.22246 | -16.9071
48735 | CBE_GT4 | 1 | Houston | YES | -0.0905 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.22246 | 76 | 76 |  |  |  |  | -0.22246 | -16.9071
48736 | CBE_ST34 | 1 | Houston | YES | -0.0905 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.22246 | 105 | 105 |  |  |  |  | -0.22246 | -23.3585
8262 | ELPS | 1 | South | YES | -0.090039 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.222 | 0 | 0 |  |  | 0 | 0 | -0.222 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.086106 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.21807 | 0 | 0 |  |  |  |  | -0.21807 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.072855 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.072855 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.072855 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.072855 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.072855 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.072855 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.072855 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.072855 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.072855 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.072855 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.072855 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.072855 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.072855 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.072855 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.072855 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.072855 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.072855 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.072855 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.072855 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.072855 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.20482 | 0 | 0 |  |  |  |  | -0.20482 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.06949 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.20145 | 0 | 0 |  |  |  |  | -0.20145 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.06949 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.20145 | 0 | 0 |  |  |  |  | -0.20145 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.067939 | 33 | 13 | 33 | 0 | 1.0375 | Hydro | -1 | 0.1999 | 0 | 0 |  |  | 0 | 0 | -0.1999 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.067939 | 25 | 13 | 25 | 0 | 1.0375 | Hydro | -1 | 0.1999 | 0 | 0 |  |  | 0 | 0 | -0.1999 | 0
88253 | HAMILTON | F | South | YES | -0.067939 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.1999 | 0 | 0 |  |  | 0 | 0 | -0.1999 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.066829 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.19879 | 0 | 0 |  |  |  |  | -0.19879 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.066829 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.19879 | 0 | 0 |  |  |  |  | -0.19879 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.066829 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.19879 | 0 | 0 |  |  |  |  | -0.19879 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.066829 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.19879 | 0 | 0 |  |  |  |  | -0.19879 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.057221 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.18918 | 0 | 0 |  |  |  |  | -0.18918 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.057203 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.18917 | 0 | 651 |  |  |  |  | -0.18917 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.057203 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.18917 | 0 | 564 |  |  |  |  | -0.18917 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.057203 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.18917 | 0 | 603 |  |  |  |  | -0.18917 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.057123 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.18909 | 167.7 | 167.7 |  |  |  |  | -0.18909 | -31.7096
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.057123 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.18909 | 166.4 | 166.4 |  |  |  |  | -0.18909 | -31.4638
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.057123 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.18909 | 252.4 | 252.4 |  |  |  |  | -0.18909 | -47.7251
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.055772 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.18773 | 0 | 0 |  |  |  |  | -0.18773 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.055639 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.1876 | 166 | 166 |  |  |  |  | -0.1876 | -31.1418
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.055639 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.1876 | 166 | 166 |  |  |  |  | -0.1876 | -31.1418
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.055639 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.1876 | 248 | 248 |  |  |  |  | -0.1876 | -46.5251
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.055639 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.1876 | 546 | 546 |  |  |  |  | -0.1876 | -102.4303
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.055639 | 598.9 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.1876 | 0 | 654 |  |  |  |  | -0.1876 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.055639 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.1876 | 13 | 13 |  |  |  |  | -0.1876 | -2.4388
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.049353 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.049353 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.049353 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.049353 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.049353 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.049353 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.049353 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.049353 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.049353 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.049353 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.049353 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.049353 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.049353 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.049353 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.049353 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.18132 | 0 | 0 |  |  |  |  | -0.18132 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.046708 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.17867 | 0 | 0 |  |  |  |  | -0.17867 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.044862 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.17682 | 0 | 0 |  |  |  |  | -0.17682 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.044862 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.17682 | 0 | 0 |  |  |  |  | -0.17682 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.044862 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.17682 | 0 | 0 |  |  |  |  | -0.17682 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.044862 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.17682 | 0 | 0 |  |  |  |  | -0.17682 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.044862 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.17682 | 0 | 0 |  |  |  |  | -0.17682 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.044156 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.17612 | 0 | 0 |  |  |  |  | -0.17612 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.044156 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.17612 | 0 | 0 |  |  |  |  | -0.17612 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.044156 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.17612 | 0 | 0 |  |  |  |  | -0.17612 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.044156 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.17612 | 0 | 0 |  |  |  |  | -0.17612 | 0
48691 | GBY_73741085 | A | Houston | YES | -0.043266 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.17523 | 47 | 47 |  |  |  |  | -0.17523 | -8.2357
48691 | GBY_73741085 | B | Houston | YES | -0.043266 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.17523 | 47 | 47 |  |  |  |  | -0.17523 | -8.2357
48692 | GBY_81821075 | D | Houston | YES | -0.043266 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.17523 | 55 | 55 |  |  |  |  | -0.17523 | -9.6376
48692 | GBY_81821075 | C | Houston | YES | -0.043266 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.17523 | 47 | 47 |  |  |  |  | -0.17523 | -8.2357
48693 | GBY_83841065 | E | Houston | YES | -0.043266 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.17523 | 57 | 57 |  |  |  |  | -0.17523 | -9.988
48693 | GBY_83841065 | F | Houston | YES | -0.043266 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.17523 | 54 | 54 |  |  |  |  | -0.17523 | -9.4623
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.042829 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.17479 | 0 | 0 |  |  |  |  | -0.17479 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.042829 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.17479 | 0 | 0 |  |  |  |  | -0.17479 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.042472 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.17443 | 163.2 | 163.2 |  |  |  |  | -0.17443 | -28.4677
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.042472 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.17443 | 157.1 | 157.1 |  |  |  |  | -0.17443 | -27.4036
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.042472 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.17443 | 157.5 | 157.5 |  |  |  |  | -0.17443 | -27.4734
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.042472 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.17443 | 157 | 157 |  |  |  |  | -0.17443 | -27.3862
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.042472 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.17443 | 282 | 282 |  |  |  |  | -0.17443 | -49.1905
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.042166 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.17413 | 0 | 0 |  |  |  |  | -0.17413 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | -0.04184 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.1738 | 18 | 18 |  |  |  |  | -0.1738 | -3.1284
48855 | SRB_GT211035 | B2 | Houston | YES | -0.04184 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.1738 | 12 | 12 |  |  |  |  | -0.1738 | -2.0856
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.041822 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.17378 | 176 | 176 |  |  |  |  | -0.17378 | -30.586
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.041797 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.17376 | 165 | 165 |  |  |  |  | -0.17376 | -28.6703
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.041785 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.17375 | 0 | 0 |  |  |  |  | -0.17375 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.041785 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.17375 | 0 | 0 |  |  |  |  | -0.17375 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.041711 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.17367 | 213 | 213 |  |  |  |  | -0.17367 | -36.9924
48845 | SOL_GT1 | 1 | Houston | YES | -0.041704 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.17367 | 16.2 | 16.2 |  |  |  |  | -0.17367 | -2.8134
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.0417 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.17366 | 0 | 0 |  |  |  |  | -0.17366 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.0417 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.17366 | 0 | 0 |  |  |  |  | -0.17366 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.0417 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.17366 | 0 | 0 |  |  |  |  | -0.17366 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.0417 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.17366 | 0 | 0 |  |  |  |  | -0.17366 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.04169 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.17365 | 228 | 228 |  |  |  |  | -0.17365 | -39.5927
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.041685 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.17365 | 0 | 0 |  |  |  |  | -0.17365 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.041685 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.17365 | 0 | 0 |  |  |  |  | -0.17365 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.041685 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.17365 | 0 | 0 |  |  |  |  | -0.17365 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.041232 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.17319 | 0 | 0 |  |  |  |  | -0.17319 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.041232 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.17319 | 0 | 0 |  |  |  |  | -0.17319 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.041232 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.17319 | 0 | 0 |  |  |  |  | -0.17319 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.041232 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.17319 | 0 | 0 |  |  |  |  | -0.17319 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.040575 | 137.6 | 54.6 | 137.6 |  | 1.0362 | Cogen | -1 | 0.17254 | 0 | 0 |  |  |  |  | -0.17254 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.040458 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.17242 | 42 | 42 |  |  |  |  | -0.17242 | -7.2417
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.040458 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.17242 | 42 | 42 |  |  |  |  | -0.17242 | -7.2417
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.040458 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.17242 | 39 | 39 |  |  |  |  | -0.17242 | -6.7244
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.040458 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.17242 | 39 | 39 |  |  |  |  | -0.17242 | -6.7244
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.040331 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.17229 | 0 | 0 |  |  |  |  | -0.17229 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.040331 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.17229 | 0 | 0 |  |  |  |  | -0.17229 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.039389 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.17135 | 107 | 107 |  |  |  |  | -0.17135 | -18.3346
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.039389 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.17135 | 108 | 108 |  |  |  |  | -0.17135 | -18.5059
48875 | THW_3132 | B | Houston | YES | -0.039389 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.17135 | 53 | 53 |  |  |  |  | -0.17135 | -9.0816
48875 | THW_3132 | A | Houston | YES | -0.039389 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.17135 | 55 | 55 |  |  |  |  | -0.17135 | -9.4243
48877 | THW_3334 | C | Houston | YES | -0.039389 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.17135 | 55 | 55 |  |  |  |  | -0.17135 | -9.4243
48877 | THW_3334 | D | Houston | YES | -0.039389 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.17135 | 57 | 57 |  |  |  |  | -0.17135 | -9.767
48879 | THW_4142 | F | Houston | YES | -0.039389 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.17135 | 55 | 55 |  |  |  |  | -0.17135 | -9.4243
48879 | THW_4142 | E | Houston | YES | -0.039389 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.17135 | 56 | 56 |  |  |  |  | -0.17135 | -9.5957
48881 | THW_4344 | G | Houston | YES | -0.039389 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.17135 | 58 | 58 |  |  |  |  | -0.17135 | -9.9384
48881 | THW_4344 | H | Houston | YES | -0.039389 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.17135 | 58 | 58 |  |  |  |  | -0.17135 | -9.9384
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.038681 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.17064 | 746 | 746 |  |  |  |  | -0.17064 | -127.2999
49803 | EXN_15GT | 1 | Houston | YES | -0.038381 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.038381 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.038381 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.038381 | 43 | 9.2 | 45.9 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.038381 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.038381 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.038381 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.038381 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.038381 | 18.5 | 9.2 | 18.5 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.038381 | 81 | 21.3 | 85.4 | 0 | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.038381 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.17034 | 0 | 0 |  |  |  |  | -0.17034 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.038238 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.1702 | 12 | 12 |  |  |  |  | -0.1702 | -2.0424
48651 | EP_1_2 | 2 | Houston | YES | -0.037563 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.16953 | 0 | 0 |  |  |  |  | -0.16953 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.037563 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.16953 | 0 | 0 |  |  |  |  | -0.16953 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.037551 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.037551 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.037551 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.037551 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.037551 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.037551 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.037551 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.16951 | 0 | 0 |  |  |  |  | -0.16951 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.037497 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.16946 | 744 | 744 |  |  |  |  | -0.16946 | -126.0777
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.037276 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.16924 | 0 | 0 |  |  |  |  | -0.16924 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.037111 | 172 | 0 | 172 | 0 | 1.026 | GSC | -1 | 0.16907 | 172 | 172 |  |  |  |  | -0.16907 | -29.0806
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.037111 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.16907 | 172 | 172 |  |  |  |  | -0.16907 | -29.0806
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.037111 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.16907 | 172 | 172 |  |  |  |  | -0.16907 | -29.0806
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.036246 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.16821 | 162.8 | 162.8 |  |  |  |  | -0.16821 | -27.3843
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.036246 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.16821 | 161.4 | 161.4 |  |  |  |  | -0.16821 | -27.1488
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.036246 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.16821 | 158.9 | 158.9 |  |  |  |  | -0.16821 | -26.7283
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.036246 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.16821 | 269.2 | 269.2 |  |  |  |  | -0.16821 | -45.2817
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.035987 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.16795 | 398 | 398 |  |  |  |  | -0.16795 | -66.8438
48885 | THW_5152 | A | Houston | YES | -0.035609 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.16757 | 58 | 58 |  |  |  |  | -0.16757 | -9.7191
48885 | THW_5152 | B | Houston | YES | -0.035609 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.16757 | 59 | 59 |  |  |  |  | -0.16757 | -9.8867
48886 | THW_5354 | C | Houston | YES | -0.035609 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.16757 | 57 | 57 |  |  |  |  | -0.16757 | -9.5516
48886 | THW_5354 | D | Houston | YES | -0.035609 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.16757 | 58 | 58 |  |  |  |  | -0.16757 | -9.7191
48887 | THW_5556 | E | Houston | YES | -0.035609 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.16757 | 59 | 59 |  |  |  |  | -0.16757 | -9.8867
48887 | THW_5556 | F | Houston | YES | -0.035609 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.16757 | 57 | 57 |  |  |  |  | -0.16757 | -9.5516
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.030326 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.16229 | 0 | 0 |  |  |  |  | -0.16229 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.030326 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.16229 | 0 | 0 |  |  |  |  | -0.16229 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.030326 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.16229 | 0 | 0 |  |  |  |  | -0.16229 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.030326 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.16229 | 0 | 0 |  |  |  |  | -0.16229 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.030326 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.16229 | 0 | 0 |  |  |  |  | -0.16229 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.13196 | 15 | 15 |  |  | 0 | 15 | -0.13196 | -1.9794
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
8442 | NUECES_B0A | MB | South | YES | 0 | 0 | 81 | 367 |  | 1.03 | GST | -1 | 0.13196 | 0 | 0 |  |  | 0 | 0 | -0.13196 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.13196 | 0 | 0 |  |  |  |  | -0.13196 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.016483 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.1852 | 48 | 48 | 0.79118 | 48 |  |  | 0.1852 | 8.8896
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.016483 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.1852 | 46 | 46 | 0.75822 | 46 |  |  | 0.1852 | 8.5192
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.016483 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.1852 | 105 | 105 | 1.7307 | 105 |  |  | 0.1852 | 19.446
48671 | FTR_GT1_5105 | 1 | North | YES | 0.01743 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.18615 | 154.2 | 154.2 | 2.6877 | 154.2 |  |  | 0.18615 | 28.7039
48672 | FTR_GT2_5110 | 2 | North | YES | 0.01743 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.18615 | 159 | 159 | 2.7714 | 159 |  |  | 0.18615 | 29.5974
48673 | FTR_GT3_5085 | 3 | North | YES | 0.01743 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.18615 | 158 | 158 | 2.7539 | 158 |  |  | 0.18615 | 29.4112
48674 | FTR_CN4_5095 | 4 | North | YES | 0.01743 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.18615 | 380 | 380 | 6.6234 | 380 |  |  | 0.18615 | 70.7359
32886 | BRYN_ATKINS3 | MB | North | YES | 0.019144 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.18786 | 0 | 0 | 0 | 0 |  |  | 0.18786 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.019144 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.18786 | 0 | 0 | 0 | 0 |  |  | 0.18786 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.019144 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.18786 | 17 | 17 | 0.32545 | 17 |  |  | 0.18786 | 3.1936
32890 | BRYN_ATKINS4 | MB | North | YES | 0.019144 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.18786 | 0 | 0 | 0 | 0 |  |  | 0.18786 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.019144 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.18786 | 0 | 0 | 0 | 0 |  |  | 0.18786 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.019931 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.18865 | 32 | 32 | 0.63779 | 32 |  |  | 0.18865 | 6.0367
990 | GIBN_CREK_G1 | 1 | North | YES | 0.026875 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.19559 | 0 | 463 | 12.4431 | 463 |  |  | 0.19559 | 90.5591
39960 | TNTNPONE_18 | 1 | North | YES | 0.059377 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.22809 | 0 | 152.3 | 9.0431 | 152.3 |  |  | 0.22809 | 34.7387
39970 | TNTNPONE_28 | 1 | North | YES | 0.059377 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.22809 | 0 | 153 | 9.0847 | 153 |  |  | 0.22809 | 34.8984
48721 | LEG_1___1 | 1 | North | YES | 0.072347 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.24106 | 0 | 827 | 59.831 | 827 |  |  | 0.24106 | 199.36
48722 | LEG_2___2 | 2 | North | YES | 0.072347 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.24106 | 0 | 819 | 59.2522 | 819 |  |  | 0.24106 | 197.4315
60202 | FRNDDRCS | F | West | YES | 0.084629 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.25335 | 0 | 0 |  |  |  |  | 0.25335 | 0
60018 | DSKY1 | 1 | West | YES | 0.10227 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.27099 | 0 | 84 |  |  |  |  | 0.27099 | 22.7627
60017 | ORNNWP1 | 1 | West | YES | 0.10314 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.27186 | 0 | 80 |  |  |  |  | 0.27186 | 21.7486
60000 | DSKY2 | 1 | West | YES | 0.10393 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.27265 | 0 | 76.5 |  |  |  |  | 0.27265 | 20.8574
3381 | BBRN_1G | 1 | North | YES | 0.10503 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.27375 | 0 | 618 | 64.9098 | 618 |  |  | 0.27375 | 169.1769
3382 | BBRN_2G | 2 | North | YES | 0.10503 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.27375 | 0 | 589 | 61.8638 | 589 |  |  | 0.27375 | 161.2382
6016 | SWMESA | 1 | West | YES | 0.10537 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.27408 | 0 | 75 |  |  |  |  | 0.27408 | 20.5563
60003 | KING_NE1A | 1 | West | YES | 0.10537 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27408 | 0 | 80 |  |  |  |  | 0.27408 | 21.9267
60005 | KING_SE1A | 1 | West | YES | 0.10537 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.27408 | 0 | 40 |  |  |  |  | 0.27408 | 10.9634
38437 | TNSRBNMESA9 | 1 | West | YES | 0.10576 | 37.5 | 0 | 150 |  | 1.02 | Wind | 1 | 0.27447 | 0 | 150 |  |  |  |  | 0.27447 | 41.171
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.10584 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.27455 | 0 | 80 |  |  |  |  | 0.27455 | 21.9642
60016 | WOODWRD11A | 1 | West | YES | 0.10586 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.27458 | 0 | 80 |  |  |  |  | 0.27458 | 21.9662
60201 | RIO DRCS | F | West | YES | 0.10594 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.27466 | 0 | 0 |  |  |  |  | 0.27466 | 0
60007 | KING_SW1A | 1 | West | YES | 0.10683 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27555 | 0 | 80 |  |  |  |  | 0.27555 | 22.0437
60019 | KING_NW1A | 1 | West | YES | 0.10683 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.27555 | 0 | 80 |  |  |  |  | 0.27555 | 22.0437
13131 | CALFREST_1G | 1 | North | YES | 0.10786 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.27657 | 150.7 | 150.7 | 16.2537 | 150.7 |  |  | 0.27657 | 41.6794
13132 | CALFREST_2G | 2 | North | YES | 0.10786 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.27657 | 151 | 151 | 16.2861 | 151 |  |  | 0.27657 | 41.7624
13133 | CALFREST_3G | 3 | North | YES | 0.10786 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.27657 | 177.4 | 177.4 | 19.1335 | 177.4 |  |  | 0.27657 | 49.0639
13134 | CALFREST_4G | 4 | North | YES | 0.10837 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.27709 | 151.5 | 151.5 | 16.4182 | 151.5 |  |  | 0.27709 | 41.9788
13135 | CALFREST_5G | 5 | North | YES | 0.10837 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.27709 | 152.3 | 152.3 | 16.5049 | 152.3 |  |  | 0.27709 | 42.2005
13136 | CALFREST_6G | 6 | North | YES | 0.10837 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.27709 | 177.5 | 177.5 | 19.2359 | 177.5 |  |  | 0.27709 | 49.1831
6407 | TURKTRAK1A | 1 | West | YES | 0.11491 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.28363 | 0 | 169.5 |  |  |  |  | 0.28363 | 48.075
1349 | WESTXWIN_1G | 1 | West | YES | 0.11739 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.28611 | 0 | 6.6 |  |  |  |  | 0.28611 | 1.8883
1350 | NWPWRG1_1G | 1 | West | YES | 0.11739 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.28611 | 0 | 34.3 |  |  |  |  | 0.28611 | 9.8135
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.11765 | 110 | 0 | 550 | 0 | 1.02 | Wind | 1 | 0.28637 | 0 | 550 |  |  |  |  | 0.28637 | 157.503
1002 | PBCTAGE_1G | A | West | YES | 0.11784 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.28655 | 66 | 66 |  |  |  |  | 0.28655 | 18.9125
1003 | PBCTBGE_2G | B | West | YES | 0.11784 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.28655 | 66 | 66 |  |  |  |  | 0.28655 | 18.9125
1004 | PBCTCGE_3G | C | West | YES | 0.11784 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.28655 | 67 | 67 |  |  |  |  | 0.28655 | 19.1991
1005 | PBCTDGE_4G | D | West | YES | 0.11784 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.28655 | 68 | 68 |  |  |  |  | 0.28655 | 19.4856
1006 | PBCTEGE_5G | E | West | YES | 0.11784 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.28655 | 67 | 67 |  |  |  |  | 0.28655 | 19.1991
1007 | PB5GEN_6G | 5 | West | YES | 0.11784 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.28655 | 114 | 114 |  |  |  |  | 0.28655 | 32.6671
1008 | PB6GEN_7G | 6 | West | YES | 0.11784 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.28655 | 515 | 515 |  |  |  |  | 0.28655 | 147.5748
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.11795 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.28667 | 0 | 35 |  |  |  |  | 0.28667 | 10.0334
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.11795 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.28667 | 0 | 30 |  |  |  |  | 0.28667 | 8.6001
1146 | NOTREES_1G | 1 | West | YES | 0.11817 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.28689 | 0 | 149 |  |  |  |  | 0.28689 | 42.7468
76031 | L_GASCCR1_1N | W1 | West | YES | 0.1183 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.28702 | 0 | 150 |  |  |  |  | 0.28702 | 43.0526
60057 | CALLAHAN1A | 1 | West | YES | 0.1192 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.28792 | 0 | 114 |  |  |  |  | 0.28792 | 32.823
1328 | OCOTILLO_1G | 1 | West | YES | 0.11948 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.28819 | 0 | 58 |  |  |  |  | 0.28819 | 16.7152
11020 | TIEHVSG_1G | 1 | West | YES | 0.1195 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.28821 | 208.2 | 208.2 |  |  |  |  | 0.28821 | 60.0058
11021 | TIEHVCG_1G | 1 | West | YES | 0.1195 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.28821 | 142.1 | 142.1 |  |  |  |  | 0.28821 | 40.9549
11022 | TIEHVCG_2G | 1 | West | YES | 0.1195 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.28821 | 132.4 | 132.4 |  |  |  |  | 0.28821 | 38.1593
11023 | TIEHVCG_3G | 1 | West | YES | 0.1195 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.28821 | 137.4 | 137.4 |  |  |  |  | 0.28821 | 39.6003
11024 | TIEHVCG_4G | 1 | West | YES | 0.1195 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.28821 | 147 | 147 |  |  |  |  | 0.28821 | 42.3672
11025 | TIEHVSG_2G | 1 | West | YES | 0.1195 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.28821 | 213.2 | 213.2 |  |  |  |  | 0.28821 | 61.4468
11001 | NAV1CT | 1 | West | YES | 0.11952 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.28823 | 70.4 | 70.4 |  |  |  |  | 0.28823 | 20.2916
11009 | NAV2CT | 1 | West | YES | 0.11952 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.28823 | 71.4 | 71.4 |  |  |  |  | 0.28823 | 20.5798
11011 | NAV3ST | 1 | West | YES | 0.11952 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.28823 | 92.8 | 92.8 |  |  |  |  | 0.28823 | 26.748
11012 | NAV4CT | 1 | West | YES | 0.11952 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.28823 | 80 | 80 |  |  |  |  | 0.28823 | 23.0586
11013 | NAV5CT | 1 | West | YES | 0.11952 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.28823 | 80 | 80 |  |  |  |  | 0.28823 | 23.0586
11014 | NAV6ST | 1 | West | YES | 0.11952 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.28823 | 115 | 115 |  |  |  |  | 0.28823 | 33.1468
1326 | STANTONW_8 | 1 | West | YES | 0.11953 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.28824 | 0 | 100.5 |  |  |  |  | 0.28824 | 28.9685
1320 | BSP 1 | 1 | West | YES | 0.11954 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.28826 | 0 | 0 |  |  |  |  | 0.28826 | 0
3107 | STRYKER_1G | 1 | North | YES | 0.11974 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.28846 | 182 | 182 | 21.7927 | 182 |  |  | 0.28846 | 52.4992
3108 | STRYKER_2G | 2 | North | YES | 0.11974 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.28846 | 484 | 484 | 57.9542 | 484 |  |  | 0.28846 | 139.6132
1333 | MCDDONAL_8 | 1 | West | YES | 0.11974 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.28846 | 0 | 214.2 |  |  |  |  | 0.28846 | 61.7882
1170 | AIRLAMESA_1G | 1 | West | YES | 0.1201 | 0 | 0 | 180 |  | 1 | Wind | 1 | 0.28882 | 0 | 180 |  |  |  |  | 0.28882 | 51.9878
3113 | LUFKINWB_1G | 1 | North | YES | 0.12024 | 0 | 0 | 50 |  | 1.01 | Trash | 1 | 0.28896 | 50 | 50 | 6.0121 | 50 |  |  | 0.28896 | 14.4479
3348 | CHAMPION_1G | MB | North | YES | 0.12036 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.28907 | 0 | 0 | 0 | 0 |  |  | 0.28907 | 0
1327 | WILDHRSE_1G | 1 | West | YES | 0.12043 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.28914 | 0 | 120 |  |  |  |  | 0.28914 | 34.6973
1360 | GUNSIGHT_8 | 1 | West | YES | 0.12047 | 24 | 0 | 120 | 0 | 1.01 | Wind | 1 | 0.28918 | 0 | 120 |  |  |  |  | 0.28918 | 34.7019
1302 | COYOTEWG_8 | 1 | West | YES | 0.12075 | 45 | 0 | 225 |  | 1.01 | Wind | 1 | 0.28947 | 0 | 225 |  |  |  |  | 0.28947 | 65.1305
1045 | CALENG1G_1G | 1 | West | YES | 0.12087 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.28958 | 0 | 0 |  |  |  |  | 0.28958 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.12087 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.28958 | 0 | 0 |  |  |  |  | 0.28958 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.12087 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.28958 | 0 | 0 |  |  |  |  | 0.28958 | 0
60058 | BUFF_GAP1A | 1 | West | YES | 0.12102 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.28974 | 0 | 120 |  |  |  |  | 0.28974 | 34.7685
60060 | CIRELLO | 1 | West | YES | 0.12102 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.28974 | 0 | 233 |  |  |  |  | 0.28974 | 67.5087
60063 | BUFF_GAP1B | 1 | West | YES | 0.12102 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.28974 | 0 | 170.2 |  |  |  |  | 0.28974 | 49.3133
60066 | H_HOLLOW1A | 1 | West | YES | 0.12102 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.28974 | 0 | 222 |  |  |  |  | 0.28974 | 64.3216
60068 | HHOLLOW21A | 1 | West | YES | 0.12102 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.28974 | 0 | 184 |  |  |  |  | 0.28974 | 53.3116
60070 | HHOLLOW31A | 1 | West | YES | 0.12102 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.28974 | 0 | 224 |  |  |  |  | 0.28974 | 64.9011
60072 | HHOLLOW41A | 1 | West | YES | 0.12102 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.28974 | 0 | 115 |  |  |  |  | 0.28974 | 33.3198
1058 | LONGSHORE_5 | 1 | West | YES | 0.12118 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.2899 | 0 | 150 |  |  |  |  | 0.2899 | 43.4844
1058 | LONGSHORE_5 | 2 | West | YES | 0.12118 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.2899 | 0 | 220 |  |  |  |  | 0.2899 | 63.7771
1058 | LONGSHORE_5 | 3 | West | YES | 0.12118 | 23.4 | 0 | 117 |  | 1.01 | Wind | 1 | 0.2899 | 0 | 117 |  |  |  |  | 0.2899 | 33.9178
1301 | BULLCREK_8 | 1 | West | YES | 0.12122 | 36 | 0 | 180 | 0 | 1.017 | Wind | 1 | 0.28993 | 0 | 180 |  |  |  |  | 0.28993 | 52.188
1037 | MORGAN5G_5G | 5 | West | YES | 0.12138 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.2901 | 137 | 137 |  |  |  |  | 0.2901 | 39.7438
1039 | MRGNAG_1G | A | West | YES | 0.12138 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.2901 | 69 | 69 |  |  |  |  | 0.2901 | 20.017
1040 | MRGNBG_2G | B | West | YES | 0.12138 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.2901 | 71 | 71 |  |  |  |  | 0.2901 | 20.5972
1041 | MRGNCG_3G | C | West | YES | 0.12138 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.2901 | 70 | 70 |  |  |  |  | 0.2901 | 20.3071
1042 | MRGNDG_4G | D | West | YES | 0.12138 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.2901 | 68 | 68 |  |  |  |  | 0.2901 | 19.7269
1043 | MRGNEG_5G | E | West | YES | 0.12138 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.2901 | 70 | 70 |  |  |  |  | 0.2901 | 20.3071
1044 | MRGNFG_6G | F | West | YES | 0.12138 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.2901 | 66 | 66 |  |  |  |  | 0.2901 | 19.1467
6637 | SNYDERW1A | 1 | West | YES | 0.12149 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.29021 | 0 | 63 |  |  |  |  | 0.29021 | 18.2833
13116 | TGATEWAY_1G | 1 | North | YES | 0.12156 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.29028 | 151 | 151 | 18.3556 | 151 |  |  | 0.29028 | 43.8318
13117 | TGATEWAY_2G | 2 | North | YES | 0.12156 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.29028 | 130 | 130 | 15.8028 | 130 |  |  | 0.29028 | 37.736
13118 | TGATEWAY_3G | 3 | North | YES | 0.12156 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.29028 | 148 | 148 | 17.9909 | 148 |  |  | 0.29028 | 42.961
13119 | TGATEWAY_4G | 4 | North | YES | 0.12156 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.29028 | 399 | 399 | 48.5024 | 399 |  |  | 0.29028 | 115.8206
1068 | SCURRYCW_1G | 1 | West | YES | 0.12161 | 28.2 | 1.3 | 141 |  | 1.01 | Wind | 1 | 0.29033 | 0 | 141 |  |  |  |  | 0.29033 | 40.9364
1073 | SCURRYCW_2G | 2 | West | YES | 0.12161 | 24 | 0 | 120 | 0 | 1.017 | Wind | 1 | 0.29033 | 0 | 120 |  |  |  |  | 0.29033 | 34.8395
1061 | CIELOGEN_1G | 1 | West | YES | 0.12163 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.29035 | 0 | 99 |  |  |  |  | 0.29035 | 28.7443
1062 | CIELOGEN_2G | 1 | West | YES | 0.12163 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.29035 | 0 | 61 |  |  |  |  | 0.29035 | 17.7111
1069 | KINDERMG_1G | 1 | West | YES | 0.12163 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.29035 | 0 | 0 |  |  |  |  | 0.29035 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.12163 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.29035 | 0 | 0 |  |  |  |  | 0.29035 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.12163 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.29035 | 0 | 0 |  |  |  |  | 0.29035 | 0
1343 | TRENTIPP_8 | 1 | West | YES | 0.12168 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.2904 | 0 | 150 |  |  |  |  | 0.2904 | 43.56
1354 | AEPWIND_8 | 1 | West | YES | 0.12168 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.2904 | 0 | 101 |  |  |  |  | 0.2904 | 29.3304
36998 | RDCNYNG1 | 1 | West | YES | 0.12193 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.29065 | 0 | 84 |  |  |  |  | 0.29065 | 24.4147
3097 | MARTLAKE_1G | 1 | North | YES | 0.12275 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.29147 | 0 | 790 | 96.9717 | 790 |  |  | 0.29147 | 230.2582
3098 | MARTLAKE_2G | 2 | North | YES | 0.12275 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.29147 | 0 | 795 | 97.5855 | 795 |  |  | 0.29147 | 231.7155
3099 | MARTLAKE_3G | 3 | North | YES | 0.12275 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.29147 | 0 | 804 | 98.6902 | 804 |  |  | 0.29147 | 234.3387
71051 | L_BITTCR1_1N | W1 | West | YES | 0.12311 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.29183 | 0 | 37.5 |  |  |  |  | 0.29183 | 10.9435
71054 | L_SWEETW1_1N | W1 | West | YES | 0.12311 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.29183 | 0 | 107.5 |  |  |  |  | 0.29183 | 31.3713
71057 | L_SWEETW1_2N | W1 | West | YES | 0.12311 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.29183 | 0 | 135 |  |  |  |  | 0.29183 | 39.3965
71059 | L_SWEETW1_3N | W1 | West | YES | 0.12311 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.29183 | 0 | 119 |  |  |  |  | 0.29183 | 34.7273
71060 | L_SWEETW1_4N | W1 | West | YES | 0.12311 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.29183 | 0 | 105 |  |  |  |  | 0.29183 | 30.6417
1049 | ROSCOEWI_5 | 1 | West | YES | 0.12326 | 41.8 | 0 | 209 |  | 1.01 | Wind | 1 | 0.29198 | 0 | 209 |  |  |  |  | 0.29198 | 61.0228
1057 | ROSCOEWI_5 | 2 | West | YES | 0.12326 | 25.3 | 0 | 126.5 |  | 1.01 | Wind | 1 | 0.29198 | 0 | 126.5 |  |  |  |  | 0.29198 | 36.9348
1060 | ROSCOEWI_5 | 3 | West | YES | 0.12326 | 39.4 | 0 | 197 | 0 | 1.01 | Wind | 1 | 0.29198 | 0 | 197 |  |  |  |  | 0.29198 | 57.5191
1072 | ROSCOEWI_5 | 4 | West | YES | 0.12326 | 63.6 | 0 | 318 | 0 | 1.01 | Wind | 1 | 0.29198 | 0 | 318 |  |  |  |  | 0.29198 | 92.8481
6144 | MCADOO1A | 1 | West | YES | 0.12327 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.29199 | 0 | 150 |  |  |  |  | 0.29199 | 43.7987
1416 | SWETWATR_1G | 1 | West | YES | 0.12405 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.29277 | 30 | 30 |  |  |  |  | 0.29277 | 8.7832
1417 | SWETWATR_2G | 2 | West | YES | 0.12405 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.29277 | 72 | 72 |  |  |  |  | 0.29277 | 21.0796
1418 | SWETWATR_3G | 3 | West | YES | 0.12405 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.29277 | 68 | 68 |  |  |  |  | 0.29277 | 19.9085
1419 | SWETWATR_4G | 4 | West | YES | 0.12405 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.29277 | 61 | 61 |  |  |  |  | 0.29277 | 17.8591
60081 | WHRLWIND1A | 1 | West | YES | 0.12504 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.29375 | 0 | 60 |  |  |  |  | 0.29375 | 17.6251
60052 | WILDHRS11A | 1 | West | YES | 0.12617 | 25.3 | 0 | 126.5 | 0 | 1.005 | Wind | 1 | 0.29489 | 0 | 126.5 |  |  |  |  | 0.29489 | 37.3035
60053 | WILDHRS21A | 1 | West | YES | 0.12617 | 7.8 | 0 | 39 | 0 | 1.025 | Wind | 1 | 0.29489 | 0 | 39 |  |  |  |  | 0.29489 | 11.5007
1437 | MESQUITW_1G | 1 | North | YES | 0.12783 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.29654 | 0 | 400 | 51.1308 | 400 |  |  | 0.29654 | 118.6176
1438 | MESQUITW_2G | 1 | North | YES | 0.12784 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.29655 | 0 | 236 | 30.1691 | 236 |  |  | 0.29655 | 69.9863
1442 | COKFIELD_5 | 1 | North | YES | 0.12935 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.29807 | 0 | 165 | 21.3436 | 165 |  |  | 0.29807 | 49.1819
3126 | TRINIDAD_6G | 1 | North | YES | 0.12975 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.29847 | 224 | 224 | 29.0642 | 224 |  |  | 0.29847 | 66.8569
6100 | OKLA7A | EQ | West | YES | 0.13037 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.29909 | 0 | 0 |  |  |  |  | 0.29909 | 0
6752 | OKLA0A | 1 | West | YES | 0.13037 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.29909 | 0 | 649.7 |  |  |  |  | 0.29909 | 194.3188
12411 | FPLEFR1A_G | 1 | North | YES | 0.13109 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.29981 | 161 | 161 | 21.1055 | 161 |  |  | 0.29981 | 48.2689
12412 | FPLEFR1B_G | 2 | North | YES | 0.13109 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.29981 | 164 | 164 | 21.4988 | 164 |  |  | 0.29981 | 49.1684
12413 | FPLEFR1C_G | 3 | North | YES | 0.13109 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.29981 | 164 | 164 | 21.4988 | 164 |  |  | 0.29981 | 49.1684
12414 | FPLEFR1S_G | 4 | North | YES | 0.13109 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.29981 | 414 | 414 | 54.2713 | 414 |  |  | 0.29981 | 124.1201
12421 | FPLEFR2A_G | 1 | North | YES | 0.13109 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.29981 | 162 | 162 | 21.2366 | 162 |  |  | 0.29981 | 48.5687
12422 | FPLEFR2B_G | 2 | North | YES | 0.13109 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.29981 | 161 | 161 | 21.1055 | 161 |  |  | 0.29981 | 48.2689
12423 | FPLEFR2C_G | 3 | North | YES | 0.13109 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.29981 | 163 | 163 | 21.3677 | 163 |  |  | 0.29981 | 48.8686
12424 | FPLEFR2S_G | 4 | North | YES | 0.13109 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.29981 | 415 | 415 | 54.4023 | 415 |  |  | 0.29981 | 124.4199
2451 | LKHB1_G | 1 | North | YES | 0.13279 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.30151 | 391 | 391 | 51.9225 | 391 |  |  | 0.30151 | 117.8908
2452 | LKHB2_G | 2 | North | YES | 0.13279 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.30151 | 516 | 516 | 68.5217 | 516 |  |  | 0.30151 | 155.5797
948 | STEAM1 | 1 | North | YES | 0.13318 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.30189 | 20 | 20 | 2.6635 | 20 |  |  | 0.30189 | 6.0379
949 | STEAM2 | 1 | North | YES | 0.13318 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.30189 | 26 | 26 | 3.4626 | 26 |  |  | 0.30189 | 7.8492
950 | STEAM3 | 1 | North | YES | 0.13318 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.30189 | 42 | 42 | 5.5934 | 42 |  |  | 0.30189 | 12.6796
12440 | PARKD_1SVC8 | 1 | North | YES | 0.1332 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.30192 | 0 | 0 | 0 | 0 |  |  | 0.30192 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.1332 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.30192 | 0 | 0 | 0 | 0 |  |  | 0.30192 | 0
837 | NEWMAN_G5 | 1 | North | YES | 0.13348 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.3022 | 40 | 40 | 5.3394 | 40 |  |  | 0.3022 | 12.0881
842 | OLINGER_G1 | 1 | North | YES | 0.13353 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.30225 | 79 | 79 | 10.5487 | 79 |  |  | 0.30225 | 23.8774
843 | OLINGER_G2 | 1 | North | YES | 0.13353 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.30225 | 110 | 110 | 14.6881 | 110 |  |  | 0.30225 | 33.247
844 | OLINGER_G3 | 1 | North | YES | 0.13353 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.30225 | 150 | 150 | 20.0292 | 150 |  |  | 0.30225 | 45.3368
845 | OLINGER_G4 | 1 | North | YES | 0.13353 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.30225 | 76 | 76 | 10.1481 | 76 |  |  | 0.30225 | 22.9706
1433 | GRHAMSES_1G | 1 | North | YES | 0.13378 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.3025 | 242 | 242 | 32.3745 | 242 |  |  | 0.3025 | 73.2041
1701 | MOSES_1G | 1 | North | YES | 0.13388 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.30259 | 0 | 558 | 74.7028 | 558 |  |  | 0.30259 | 168.8469
1702 | MOSES_2G | 2 | North | YES | 0.13388 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.30259 | 0 | 579 | 77.5142 | 579 |  |  | 0.30259 | 175.2014
1703 | MOSES_3G | 3 | North | YES | 0.13388 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.30259 | 0 | 808 | 108.1718 | 808 |  |  | 0.30259 | 244.4952
5925 | DCEAST | EQ | North | YES | 0.13388 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.30259 | 0 | 0 | 0 | 0 |  |  | 0.30259 | 0
1675 | PEC_1G | 1 | North | YES | 0.13405 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.30276 | 0 | 0 | 0 | 0 |  |  | 0.30276 | 0
1676 | PEC_2G | 2 | North | YES | 0.13405 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.30276 | 0 | 0 | 0 | 0 |  |  | 0.30276 | 0
1677 | PEC_3G | 3 | North | YES | 0.13405 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.30276 | 0 | 0 | 0 | 0 |  |  | 0.30276 | 0
1479 | WFCOGEN_1G | 1 | North | YES | 0.13413 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30285 | 0 | 0 | 0 | 0 |  |  | 0.30285 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.13413 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30285 | 0 | 0 | 0 | 0 |  |  | 0.30285 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.13413 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.30285 | 0 | 0 | 0 | 0 |  |  | 0.30285 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.13413 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.30285 | 0 | 0 | 0 | 0 |  |  | 0.30285 | 0
1432 | GRHAMSES_2G | 2 | North | YES | 0.13417 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.30288 | 366 | 366 | 49.1051 | 366 |  |  | 0.30288 | 110.8556
1678 | LAMARPWR_1G | 1 | North | YES | 0.13425 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.30296 | 160 | 160 | 21.4792 | 160 |  |  | 0.30296 | 48.4739
1679 | LAMARPWR_2G | 2 | North | YES | 0.13425 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.30296 | 156 | 156 | 20.9422 | 156 |  |  | 0.30296 | 47.2621
1680 | LAMARPWR_3G | 3 | North | YES | 0.13425 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.30296 | 196 | 196 | 26.312 | 196 |  |  | 0.30296 | 59.3806
1681 | LAMARPWR_4G | 4 | North | YES | 0.13425 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.30296 | 156 | 156 | 20.9422 | 156 |  |  | 0.30296 | 47.2621
1682 | LAMARPWR_5G | 5 | North | YES | 0.13425 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.30296 | 157 | 157 | 21.0765 | 157 |  |  | 0.30296 | 47.565
1683 | LAMARPWR_6G | 6 | North | YES | 0.13425 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.30296 | 198 | 198 | 26.5805 | 198 |  |  | 0.30296 | 59.9865
1689 | VALLEY_3G | 3 | North | YES | 0.13447 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.30319 | 375 | 375 | 50.4266 | 375 |  |  | 0.30319 | 113.6955
11691 | KMICHICT1_G | 1 | North | YES | 0.13447 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.30319 | 144 | 144 | 19.3638 | 144 |  |  | 0.30319 | 43.6591
11692 | KMICHICT2_G | 2 | North | YES | 0.13447 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.30319 | 146 | 146 | 19.6328 | 146 |  |  | 0.30319 | 44.2655
11693 | KMICHIST3_G | 3 | North | YES | 0.13447 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.30319 | 312 | 312 | 41.955 | 312 |  |  | 0.30319 | 94.5947
11694 | KMICHICT4_G | 4 | North | YES | 0.13447 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.30319 | 144 | 144 | 19.3638 | 144 |  |  | 0.30319 | 43.6591
11695 | KMICHICT5_G | 5 | North | YES | 0.13447 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.30319 | 148 | 148 | 19.9017 | 148 |  |  | 0.30319 | 44.8718
11696 | KMICHIST6_G | 6 | North | YES | 0.13447 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.30319 | 310 | 310 | 41.686 | 310 |  |  | 0.30319 | 93.9883
1687 | VALLEY_1G | 1 | North | YES | 0.13481 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.30352 | 170 | 170 | 22.9169 | 170 |  |  | 0.30352 | 51.5988
1688 | VALLEY_2G | 2 | North | YES | 0.13481 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.30352 | 527 | 527 | 71.0422 | 527 |  |  | 0.30352 | 159.9561
6948 | DENISNDM | 1 | North | YES | 0.1351 | 40 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.30382 | 0 | 0 | 0 | 0 |  |  | 0.30382 | 0
6948 | DENISNDM | 2 | North | YES | 0.1351 | 31 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.30382 | 0 | 0 | 0 | 0 |  |  | 0.30382 | 0
1643 | SLSTR1PP_1G | 1 | North | YES | 0.13599 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.3047 | 0 | 60 | 8.1592 | 60 |  |  | 0.3047 | 18.2822
2371 | COLLIN_1G | MB | North | YES | 0.1365 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.30522 | 0 | 0 | 0 | 0 |  |  | 0.30522 | 0
1600 | BARTNWND_1G | 1 | North | YES | 0.13695 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.30567 | 0 | 120 | 16.4342 | 120 |  |  | 0.30567 | 36.6803
2413 | MTCK6_G | 6 | North | YES | 0.13695 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.30567 | 118 | 118 | 16.1607 | 118 |  |  | 0.30567 | 36.0693
2414 | MTCK7_G | 7 | North | YES | 0.13695 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.30567 | 115 | 115 | 15.7498 | 115 |  |  | 0.30567 | 35.1523
2417 | MTCK8_G | 8 | North | YES | 0.13695 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.30567 | 556 | 556 | 76.147 | 556 |  |  | 0.30567 | 169.9537
344 | MRSSHPRD | 1 | North | YES | 0.13733 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.30604 | 0 | 0 | 0 | 0 |  |  | 0.30604 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.13733 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.30604 | 0 | 0 | 0 | 0 |  |  | 0.30604 | 0
2381 | NTHLK1_G | 1 | North | YES | 0.13807 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.30679 | 156 | 156 | 21.5388 | 156 |  |  | 0.30679 | 47.8586
2382 | NTHLK2_G | 2 | North | YES | 0.13807 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.30679 | 181 | 181 | 24.9905 | 181 |  |  | 0.30679 | 55.5283
2383 | NTHLK3_G | 3 | North | YES | 0.13807 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.30679 | 329 | 329 | 45.4247 | 329 |  |  | 0.30679 | 100.9326
728 | WOLFRIDGE801 | 1 | North | YES | 0.13811 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.30683 | 0 | 112.5 | 15.5379 | 112.5 |  |  | 0.30683 | 34.5186
1453 | WCPWRCO_1G | 1 | North | YES | 0.13828 | 204 | 50 | 204 |  | 1.02 | CC | 1 | 0.307 | 204 | 204 | 28.2095 | 204 |  |  | 0.307 | 62.6278
1454 | WCPWRCO_2G | 2 | North | YES | 0.13828 | 204 | 50 | 204 |  | 1.02 | CC | 1 | 0.307 | 204 | 204 | 28.2095 | 204 |  |  | 0.307 | 62.6278
1455 | WCPWRCO_3G | 3 | North | YES | 0.13828 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.307 | 242 | 242 | 33.4642 | 242 |  |  | 0.307 | 74.2938
923 | SPENCER_G4 | 1 | North | YES | 0.13832 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.30704 | 61 | 61 | 8.4375 | 61 |  |  | 0.30704 | 18.7292
924 | SPENCER_G5 | 1 | North | YES | 0.13832 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.30704 | 66 | 66 | 9.1291 | 66 |  |  | 0.30704 | 20.2644
2418 | MTCK2_G | 2 | North | YES | 0.1386 | 0 | 10 | 23 |  | 0.971 | GSC | 1 | 0.30731 | 23 | 23 | 3.1877 | 23 |  |  | 0.30731 | 7.0682
2419 | MTCK3_G | MB | North | YES | 0.1386 | 0 | 10 | 63 |  | 0.971 | GSC | 1 | 0.30731 | 0 | 0 | 0 | 0 |  |  | 0.30731 | 0
12322 | ENNSTRAC_1G | 1 | North | YES | 0.13873 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.30745 | 196 | 196 | 27.1911 | 196 |  |  | 0.30745 | 60.2596
12323 | ENNSTRAC_2G | 2 | North | YES | 0.13873 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.30745 | 116 | 116 | 16.0927 | 116 |  |  | 0.30745 | 35.6639
580 | JCKCNTY801 | 1 | North | YES | 0.13977 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.30849 | 288 | 288 | 40.2538 | 288 |  |  | 0.30849 | 88.8443
581 | JCKCNTY802 | 2 | North | YES | 0.13977 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.30849 | 147 | 147 | 20.5462 | 147 |  |  | 0.30849 | 45.3476
582 | JCKCNTY803 | 3 | North | YES | 0.13977 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.30849 | 147 | 147 | 20.5462 | 147 |  |  | 0.30849 | 45.3476
503 | NTHTEXAS01 | 1 | North | YES | 0.14047 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.30918 | 18 | 18 | 2.5284 | 18 |  |  | 0.30918 | 5.5653
504 | NTHTEXAS02 | 2 | North | YES | 0.14047 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.30918 | 18 | 18 | 2.5284 | 18 |  |  | 0.30918 | 5.5653
505 | NTHTEXAS03 | 3 | North | YES | 0.14047 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.30918 | 38 | 38 | 5.3377 | 38 |  |  | 0.30918 | 11.749
332 | RWMILLER01 | 1 | North | YES | 0.14145 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.31017 | 73 | 73 | 10.3262 | 73 |  |  | 0.31017 | 22.6426
333 | RWMILLER02 | 2 | North | YES | 0.14145 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.31017 | 119 | 119 | 16.8331 | 119 |  |  | 0.31017 | 36.9105
334 | RWMILLER03 | 3 | North | YES | 0.14145 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.31017 | 208 | 208 | 29.4226 | 208 |  |  | 0.31017 | 64.5158
335 | RWMILLER04 | 4 | North | YES | 0.14145 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.31017 | 102 | 102 | 14.4284 | 102 |  |  | 0.31017 | 31.6376
336 | RWMILLER05 | 5 | North | YES | 0.14145 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.31017 | 101 | 101 | 14.287 | 101 |  |  | 0.31017 | 31.3274
1861 | EAGLEMNT_1G | MB | North | YES | 0.14196 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.31068 | 0 | 0 | 0 | 0 |  |  | 0.31068 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.14196 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.31068 | 0 | 0 | 0 | 0 |  |  | 0.31068 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.14196 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.31068 | 0 | 0 | 0 | 0 |  |  | 0.31068 | 0
1898 | COMCHEPK_1G | 1 | North | YES | 0.14351 | 1159 | 1150 | 1159 | 0 | 1.032 | Nuc | 1 | 0.31223 | 0 | 0 | 0 | 0 |  |  | 0.31223 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.14351 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.31223 | 0 | 0 | 0 | 0 |  |  | 0.31223 | 0
1877 | WLFHOLW_1G | 1 | North | YES | 0.14409 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.3128 | 217.3 | 217.3 | 31.3101 | 217.3 |  |  | 0.3128 | 67.9723
1878 | WLFHOLW_2G | 2 | North | YES | 0.14409 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.3128 | 215.7 | 215.7 | 31.0796 | 215.7 |  |  | 0.3128 | 67.4718
1879 | WLFHOLW_3G | 3 | North | YES | 0.14409 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.3128 | 272.4 | 272.4 | 39.2493 | 272.4 |  |  | 0.3128 | 85.2078
1889 | DECRDOVA_1G | 1 | North | YES | 0.14452 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.31324 | 779 | 779 | 112.5842 | 779 |  |  | 0.31324 | 244.0148
1945 | HANDLEY_1G | MB | North | YES | 0.1448 | 0 | 25 | 36 |  | 0.986 | GST | 1 | 0.31352 | 0 | 0 | 0 | 0 |  |  | 0.31352 | 0
1946 | HANDLEY_2G | MB | North | YES | 0.1448 | 0 | 30 | 68 |  | 0.986 | GST | 1 | 0.31352 | 0 | 0 | 0 | 0 |  |  | 0.31352 | 0
1948 | HANDLEY_4G | 4 | North | YES | 0.14502 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.31374 | 435 | 435 | 63.0828 | 435 |  |  | 0.31374 | 136.4748
1947 | HANDLEY_3G | 3 | North | YES | 0.14541 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.31413 | 395 | 395 | 57.4366 | 395 |  |  | 0.31413 | 124.0798
1949 | HANDLEY_5G | 5 | North | YES | 0.14541 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.31413 | 435 | 435 | 63.2529 | 435 |  |  | 0.31413 | 136.6448
1892 | DECRDOVA_2G | A | North | YES | 0.14558 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.3143 | 70 | 70 | 10.191 | 70 |  |  | 0.3143 | 22.0011
1893 | DECRDOVA_3G | B | North | YES | 0.14558 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.3143 | 69 | 69 | 10.0454 | 69 |  |  | 0.3143 | 21.6868
1894 | DECRDOVA_4G | C | North | YES | 0.14558 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.3143 | 69 | 69 | 10.0454 | 69 |  |  | 0.3143 | 21.6868
1895 | DECRDOVA_5G | D | North | YES | 0.14558 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.3143 | 68 | 68 | 9.8998 | 68 |  |  | 0.3143 | 21.3725
366 | JNSNCNTY802 | 1 | North | YES | 0.151 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.31972 | 0 | 0 | 0 | 0 |  |  | 0.31972 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.151 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.31972 | 0 | 0 | 0 | 0 |  |  | 0.31972 | 0
1941 | MDLTHELP_1G | 1 | North | YES | 0.15413 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.32284 | 216.4 | 216.4 | 33.3531 | 216.4 |  |  | 0.32284 | 69.8635
1942 | MDLTHELP_2G | 2 | North | YES | 0.15413 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.32284 | 216.1 | 216.1 | 33.3068 | 216.1 |  |  | 0.32284 | 69.7666
1937 | MDLTHELP_5G | 5 | North | YES | 0.15473 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.32344 | 224 | 224 | 34.6584 | 224 |  |  | 0.32344 | 72.451
1938 | MDLTHELP_6G | 6 | North | YES | 0.15473 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.32344 | 226 | 226 | 34.9678 | 226 |  |  | 0.32344 | 73.0979
1943 | MDLTHELP_3G | 3 | North | YES | 0.15473 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.32344 | 212 | 212 | 32.8017 | 212 |  |  | 0.32344 | 68.5697
1944 | MDLTHELP_4G | 4 | North | YES | 0.15473 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.32344 | 211 | 211 | 32.647 | 211 |  |  | 0.32344 | 68.2463
244 | WHITNYDM01 | 1 | North | YES | 0.17974 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.34846 | 0 | 0 | 0 | 0 |  |  | 0.34846 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.17974 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.34846 | 0 | 0 | 0 | 0 |  |  | 0.34846 | 0
251 | BOSQUESW803 | 2 | North | YES | 0.18858 | 150 | 0 | 150 |  | 1.032 | CC | 1 | 0.3573 | 150 | 150 | 28.2873 | 150 |  |  | 0.3573 | 53.5949
253 | BOSQUESW804 | 2 | North | YES | 0.18858 | 80 | 0 | 80 |  | 1.032 | CC | 1 | 0.3573 | 80 | 80 | 15.0866 | 80 |  |  | 0.3573 | 28.5839
3416 | LAKE_CRK1_G | 1 | North | YES | 0.22282 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.39154 | 75 | 75 | 16.7116 | 75 |  |  | 0.39154 | 29.3654
3417 | LAKE_CRK2_G | 2 | North | YES | 0.22282 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.39154 | 222 | 222 | 49.4665 | 222 |  |  | 0.39154 | 86.9217
238 | BOSQUESW505 | 1 | North | YES | 0.22303 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.39175 | 255 | 255 | 56.8721 | 255 |  |  | 0.39175 | 99.895
239 | BOSQUESW502 | 1 | North | YES | 0.22303 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.39175 | 149 | 149 | 33.2312 | 149 |  |  | 0.39175 | 58.37
247 | BOSQUESW501 | 2 | North | YES | 0.22303 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.39175 | 156 | 156 | 34.7924 | 156 |  |  | 0.39175 | 61.1122
3403 | THOUSE_1G | 1 | North | YES | 0.27281 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.44153 | 563 | 563 | 153.5948 | 563 |  |  | 0.44153 | 248.5826
3404 | THOUSE_2G | 2 | North | YES | 0.27281 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.44153 | 807 | 807 | 220.1617 | 807 |  |  | 0.44153 | 356.3164

## Zones
Houston | -1
North | 1
South | -1
West | 1
SET UP AREA, copy & paste values to cell B1
Source | North |  | N to H | N to W | N to S | W to N | S to N | W to S
Sink | South | Houston | -1 | 1 | -1 | -1 | 1 | -1
|  | North | 1 | 1 | 1 | -1 | -1 | -1
|  | South | -1 | 1 | -1 | -1 | 1 | -1
|  | West | 1 | -1 | 1 | 1 | -1 | 1
|  | Source | North | North | North | West | South | West
|  | Sink | Houston | West | South | North | North | South

## Tech
Number of Bus | Name of Bus | Tech Type
238 | BOSQUESW505 | CC
239 | BOSQUESW502 | GGT
244 | WHITNYDM01 | Hydro
245 | WHITNYDM02 | Hydro
247 | BOSQUESW501 | GGT
251 | BOSQUESW803 | CC
253 | BOSQUESW804 | CC
332 | RWMILLER01 | GST
333 | RWMILLER02 | GST
334 | RWMILLER03 | GST
335 | RWMILLER04 | GST
336 | RWMILLER05 | GST
344 | MRSSHPRD | Hydro
345 | MRSSHPRD01 | Hydro
366 | JNSNCNTY802 | Cogen
367 | JNSNCNTY802 | Cogen
503 | NTHTEXAS01 | GST
504 | NTHTEXAS02 | GST
505 | NTHTEXAS03 | GST
580 | JCKCNTY801 | CC
581 | JCKCNTY802 | CC
582 | JCKCNTY803 | CC
728 | WOLFRIDGE801 | Wind
837 | NEWMAN_G5 | GST
842 | OLINGER_G1 | GST
843 | OLINGER_G2 | GST
844 | OLINGER_G3 | GST
845 | OLINGER_G4 | GGT
923 | SPENCER_G4 | GST
924 | SPENCER_G5 | GST
948 | STEAM1 | GST
949 | STEAM2 | GST
950 | STEAM3 | GST
990 | GIBN_CREK_G1 | LIGCO
1002 | PBCTAGE_1G | GGT
1003 | PBCTBGE_2G | GGT
1004 | PBCTCGE_3G | GGT
1005 | PBCTDGE_4G | GGT
1006 | PBCTEGE_5G | GGT
1007 | PB5GEN_6G | GST
1008 | PB6GEN_7G | GST
1037 | MORGAN5G_5G | GST
1039 | MRGNAG_1G | GGT
1040 | MRGNBG_2G | GGT
1041 | MRGNCG_3G | GGT
1042 | MRGNDG_4G | GGT
1043 | MRGNEG_5G | GGT
1044 | MRGNFG_6G | GGT
1045 | CALENG1G_1G | Cogen
1046 | CALENG2G_2G | Cogen
1047 | CALENG3G_3G | Cogen
1049 | ROSCOEWI_5 | Wind
1057 | ROSCOEWI_5 | Wind
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1060 | ROSCOEWI_5 | Wind
1061 | CIELOGEN_1G | Wind
1062 | CIELOGEN_2G | Wind
1068 | SCURRYCW_1G | Wind
1069 | KINDERMG_1G | Cogen
1070 | KINDERMG_2G | Cogen
1071 | KINDERMG_3G | Cogen
1072 | ROSCOEWI_5 | Wind
1073 | SCURRYCW_2G | Wind
1146 | NOTREES_1G | Wind
1170 | AIRLAMESA_1G | Wind
1301 | BULLCREK_8 | Wind
1302 | COYOTEWG_8 | Wind
1320 | BSP 1 | Cogen
1326 | STANTONW_8 | Wind
1327 | WILDHRSE_1G | Wind
1328 | OCOTILLO_1G | Wind
1333 | MCDDONAL_8 | Wind
1343 | TRENTIPP_8 | Wind
1349 | WESTXWIN_1G | Wind
1350 | NWPWRG1_1G | Wind
1354 | AEPWIND_8 | Wind
1360 | GUNSIGHT_8 | Wind
1416 | SWETWATR_1G | CC
1417 | SWETWATR_2G | CC
1418 | SWETWATR_3G | CC
1419 | SWETWATR_4G | CC
1432 | GRHAMSES_2G | GST
1433 | GRHAMSES_1G | GST
1437 | MESQUITW_1G | Wind
1438 | MESQUITW_2G | Wind
1442 | COKFIELD_5 | Wind
1453 | WCPWRCO_1G | CC
1454 | WCPWRCO_2G | CC
1455 | WCPWRCO_3G | CC
1479 | WFCOGEN_1G | Cogen
1479 | WFCOGEN_1G | Cogen
1482 | WFCOGEN_2G | Cogen
1482 | WFCOGEN_2G | Cogen
1600 | BARTNWND_1G | Wind
1643 | SLSTR1PP_1G | Wind
1675 | PEC_1G | Cogen
1676 | PEC_2G | Cogen
1677 | PEC_3G | Cogen
1678 | LAMARPWR_1G | CC
1679 | LAMARPWR_2G | CC
1680 | LAMARPWR_3G | CC
1681 | LAMARPWR_4G | CC
1682 | LAMARPWR_5G | CC
1683 | LAMARPWR_6G | CC
1687 | VALLEY_1G | GST
1688 | VALLEY_2G | GSC
1689 | VALLEY_3G | GST
1701 | MOSES_1G | LIGCO
1702 | MOSES_2G | LIGCO
1703 | MOSES_3G | LIGCO
1861 | EAGLEMNT_1G | GST
1862 | EAGLEMNT_2G | GST
1863 | EAGLEMNT_3G | GST
1877 | WLFHOLW_1G | CC
1878 | WLFHOLW_2G | CC
1879 | WLFHOLW_3G | CC
1889 | DECRDOVA_1G | GSC
1892 | DECRDOVA_2G | GGT
1893 | DECRDOVA_3G | GGT
1894 | DECRDOVA_4G | GGT
1895 | DECRDOVA_5G | GGT
1898 | COMCHEPK_1G | Nuc
1899 | COMCHEPK_2G | Nuc
1937 | MDLTHELP_5G | CC
1938 | MDLTHELP_6G | CC
1941 | MDLTHELP_1G | CC
1942 | MDLTHELP_2G | CC
1943 | MDLTHELP_3G | CC
1944 | MDLTHELP_4G | CC
1945 | HANDLEY_1G | GST
1946 | HANDLEY_2G | GST
1947 | HANDLEY_3G | GST
1948 | HANDLEY_4G | GST
1949 | HANDLEY_5G | GST
2371 | COLLIN_1G | GST
2381 | NTHLK1_G | GST
2382 | NTHLK2_G | GST
2383 | NTHLK3_G | GST
2413 | MTCK6_G | GST
2414 | MTCK7_G | GST
2417 | MTCK8_G | GSC
2418 | MTCK2_G | GSC
2419 | MTCK3_G | GSC
2451 | LKHB1_G | GST
2452 | LKHB2_G | GST
3097 | MARTLAKE_1G | LIGCO
3098 | MARTLAKE_2G | LIGCO
3099 | MARTLAKE_3G | LIGCO
3107 | STRYKER_1G | GST
3108 | STRYKER_2G | GST
3113 | LUFKINWB_1G | Trash
3126 | TRINIDAD_6G | GST
3348 | CHAMPION_1G | Cogen
3381 | BBRN_1G | LIGCO
3382 | BBRN_2G | LIGCO
3403 | THOUSE_1G | GSC
3404 | THOUSE_2G | GSC
3416 | LAKE_CRK1_G | GST
3417 | LAKE_CRK2_G | GST
3432 | SANDOW_4G | LIGCO
5026 | BRAUNIG_VHB1 | GST
5027 | BRAUNIG_VHB2 | GST
5028 | BRAUNIG_VHB3 | GST
5031 | BRA_VHBCT1 | GST
5032 | BRA_VHBCT2 | GST
5033 | BRA_VHBCT3 | GST
5034 | BRA_VHBCT4 | GST
5111 | CALAVER_JTD1 | LIGCO
5112 | CALAVER_JTD2 | LIGCO
5264 | LEON_LCP3G3 | GST
5265 | LEON_LCP4G4 | GST
5266 | LEON_LCPCT1 | GGT
5267 | LEON_LCPCT2 | GGT
5268 | LEON_LCPCT3 | GGT
5269 | LEON_LCPCT4 | GGT
5396 | CALAVER_OWS1 | GST
5397 | CALAVER_OWS2 | GST
5401 | CALAVER_JKS1 | LIGCO
5436 | TUTTL_WBT1G1 | GST
5438 | TUTTL_WBT3G3 | GST
5439 | TUTTL_WBT4G4 | GST
5476 | BRA_AVR1_CT1 | CC
5477 | BRA_AVR1_ST1 | CC
5478 | BRA_AVR1_CT2 | CC
5503 | RAYBURNGEN3 | GST
5505 | RAYBURNGEN1 | GGT
5506 | RAYBURNGEN2 | GGT
5508 | RAYBURNCC9 | CC
5509 | RAYBURNCC10 | CC
5511 | RAYBURNCC7 | CC
5512 | RAYBURNCC8 | CC
5728 | FALCONHYDRO2 | Hydro
5729 | FALCONHYDRO3 | Hydro
5890 | PEARSALLGEN1 | GST
5891 | PEARSALLGEN2 | GST
5892 | PEARSALLGEN3 | GST
5903 | SANMIGUELGEN | LIGCO
5911 | STP_GN1___1 | Nuc
5912 | STP_GN2___2 | Nuc
5925 | DCEAST | DCTie
5932 | SI_RAY9 | CC
5933 | SI_RAY6 | GST
5934 | SI_RAY5 | GST
5935 | SI_RAY10 | CC
6016 | SWMESA | Wind
6100 | OKLA7A | DCTie
6144 | MCADOO1A | Wind
6407 | TURKTRAK1A | Wind
6637 | SNYDERW1A | Wind
6752 | OKLA0A | LIGCO
6948 | DENISNDM | Hydro
6948 | DENISNDM | Hydro
7000 | L_FERGUS1_1Y | GSC
7004 | L_SIMGID1_1Y | GST
7005 | L_SIMGID1_2Y | GST
7006 | L_SIMGID1_3Y | GST
7007 | L_LOSTPI1_1Y | CC
7008 | L_LOSTPI1_2Y | CC
7009 | L_LOSTPI1_3Y | CC
7010 | L_FPPYD11_1Y | LIGCO
7011 | L_FPPYD11_2Y | LIGCO
7012 | L_FPPYD21_3Y | LIGCO
7014 | L_HAYSEN1_1Y | CC
7015 | L_HAYSEN1_2Y | CC
7016 | L_HAYSEN1_3Y | CC
7017 | L_HAYSEN1_4Y | CC
7020 | L_AUSTPL1_1Y | Hydro
7020 | L_AUSTPL1_1Y | Hydro
7022 | L_BUCHAN1_1Y | Hydro
7023 | L_BUCHAN1_2Y | Hydro
7024 | L_BUCHAN1_3Y | Hydro
7026 | L_INKSDA1_1Y | Hydro
7028 | L_MARBFA1_1Y | Hydro
7029 | L_MARBFA1_2Y | Hydro
7031 | L_MARSFO1G1Y | Hydro
7032 | L_MARSFO1G2Y | Hydro
7033 | L_MARSFO1G3Y | Hydro
7035 | L_WIRTZ_1G1Y | Hydro
7036 | L_WIRTZ_1G2Y | Hydro
7038 | L_DELAWA1_1Y | Wind
7038 | L_DELAWA1_1Y | Wind
7303 | L_WPPGS12_1Y | GGT
7303 | L_WPPGS12_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7487 | L_CANYHY8_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7609 | L_SCHUMA8_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7800 | L_GUADGE1_1Y | CC
7801 | L_GUADGE1_2Y | CC
7802 | L_GUADGE1_3Y | CC
7803 | L_GUADGE1_4Y | CC
7804 | L_GUADGE1_5Y | CC
7805 | L_GUADGE1_6Y | CC
7807 | L_BASTEN1_1Y | CC
7808 | L_BASTEN1_2Y | CC
7809 | L_BASTEN1_3Y | CC
7810 | L_RIONOG1G1Y | CC
7811 | L_RIONOG1G2Y | CC
7812 | L_RIONOG1G3Y | CC
7813 | L_RIONOG1S1Y | CC
8032 | AMISTADHYD1 | Hydro
8033 | AMISTADHYD2 | Hydro
8048 | FALCONHYDRO1 | Hydro
8066 | DUP1V#1 | Cogen
8134 | FOR #1 | Cogen
8138 | FOR #2 | Cogen
8139 | JOS #1 | GST
8147 | UCAR #2 | Cogen
8148 | UCAR #1 | Cogen
8153 | FOR #3 | Cogen
8154 | FOR #4 | Cogen
8155 | FOR #5 | Cogen
8156 | FOR #6 | Cogen
8157 | FOR #7 | Cogen
8161 | COLETO0A | LIGCO
8173 | VICEC51A | CC
8174 | VICEC61A | CC
8189 | CUECPL2A | Cogen
8262 | ELPS | Hydro
8285 | LAR #1 | GST
8287 | LAR #2 | GST
8288 | LAR #3 | GST
8388 | BATES0A | GST
8393 | BATES0B | GST
8437 | NUECES_B0C | GST
8438 | NUECES_B0B | GST
8442 | NUECES_B0A | GST
8456 | COSW#1 | Cogen
8457 | COSW#2 | Cogen
8459 | B_DAVIS0B | GSC
8460 | B_DAVIS0A | GSC
8461 | KOCH_UP0A | Cogen
8506 | VAL #1 | Cogen
8507 | VAL #2 | Cogen
8511 | OXY_CC0A | Cogen
8517 | CELANEBI0A | Cogen
8560 | CNOPGT1 | Cogen
8561 | CNOPGT2 | Cogen
8562 | CNOPST1 | Cogen
8926 | LGE_GT10A | Cogen
8927 | LGE_GT20A | Cogen
8928 | LGE_STG0A | Cogen
8930 | ICPGN10A | Cogen
8931 | ICPGN20A | Cogen
8932 | ICPGN30A | Cogen
8933 | FGNTS001 | CC
8934 | FGNTS101 | CC
8935 | FGNTS201 | CC
8936 | MVGN#1 | CC
8937 | MVGN#2 | CC
8938 | MVGN#3 | CC
8981 | HECN1 | CC
8982 | HECN2 | CC
8983 | HECN3 | CC
9000 | DECKR_G1 | GST
9001 | DECKR_G2 | GST
9002 | DECKR_G3 | GGT
9003 | DECKR_G4 | GGT
9004 | DECKR_G5 | GGT
9005 | DECKR_G6 | GGT
9016 | SANDH_G1 | GGT
9017 | SANDH_G2 | GGT
9018 | SANDH_G3 | GGT
9019 | SANDH_G4 | GGT
9020 | SANDHG5A | CC
9021 | SANDHG5C | CC
11001 | NAV1CT | CC
11009 | NAV2CT | CC
11011 | NAV3ST | CC
11012 | NAV4CT | CC
11013 | NAV5CT | CC
11014 | NAV6ST | CC
11020 | TIEHVSG_1G | CC
11021 | TIEHVCG_1G | CC
11022 | TIEHVCG_2G | CC
11023 | TIEHVCG_3G | CC
11024 | TIEHVCG_4G | CC
11025 | TIEHVSG_2G | CC
11691 | KMICHICT1_G | CC
11692 | KMICHICT2_G | CC
11693 | KMICHIST3_G | CC
11694 | KMICHICT4_G | CC
11695 | KMICHICT5_G | CC
11696 | KMICHIST6_G | CC
12322 | ENNSTRAC_1G | CC
12323 | ENNSTRAC_2G | CC
12411 | FPLEFR1A_G | CC
12412 | FPLEFR1B_G | CC
12413 | FPLEFR1C_G | CC
12414 | FPLEFR1S_G | CC
12421 | FPLEFR2A_G | CC
12422 | FPLEFR2B_G | CC
12423 | FPLEFR2C_G | CC
12424 | FPLEFR2S_G | CC
12440 | PARKD_1SVC8 | GST
12449 | PARKD_2SVC8 | GST
13116 | TGATEWAY_1G | CC
13117 | TGATEWAY_2G | CC
13118 | TGATEWAY_3G | CC
13119 | TGATEWAY_4G | CC
13131 | CALFREST_1G | CC
13132 | CALFREST_2G | CC
13133 | CALFREST_3G | CC
13134 | CALFREST_4G | CC
13135 | CALFREST_5G | CC
13136 | CALFREST_6G | CC
13432 | SANDOW_5G | LIGCO
32798 | BRYN_TAMUGEN | GST
32883 | BRYN_DNSBY3 | GST
32884 | BRYN_DNSBY13 | GST
32886 | BRYN_ATKINS3 | GST
32887 | BRYN_ATKINS6 | GST
32888 | BRYN_ATKINS7 | GGT
32890 | BRYN_ATKINS4 | GST
32891 | BRYN_ATKINS5 | GST
32892 | BRYN_DNSBY14 | GST
36998 | RDCNYNG1 | Wind
38332 | TNWDWRDU2_8 | Wind
38437 | TNSRBNMESA9 | Wind
38580 | TNBP_CGN1_8 | Cogen
38590 | TNBP_CGN2_8 | Cogen
38600 | TNBP_CGN3_8 | Cogen
38611 | TNBPAMCG1_8 | Cogen
38612 | TNBPAMCG2_8 | Cogen
38613 | TNBPAMCG3_8 | Cogen
38614 | TNBPAMCG4_8 | Cogen
38615 | TNBPAMCG5_8 | Cogen
38690 | TNBP_CGN4_8 | Cogen
38711 | TNTXCTY1CG8 | Cogen
38712 | TNTXCTY2CG8 | Cogen
38713 | TNTXCTY3CG8 | Cogen
38714 | TNTXCTY4CG8 | Cogen
39190 | TNSLCGN1__8 | Cogen
39470 | TNDOWCGNSG8 | Cogen
39480 | TNDOWCGNGG8 | Cogen
39760 | TNSCLP1___8 | Cogen
39770 | TNSCLP2___8 | Cogen
39775 | TNSCLP4___8 | Cogen
39790 | TNSCLP3___8 | Cogen
39960 | TNTNPONE_18 | LIGCO
39970 | TNTNPONE_28 | LIGCO
48500 | APD_GT1_8005 | Cogen
48510 | AK_GT1__8040 | Cogen
48511 | LPE_GT1_8070 | GGT
48512 | LPE_GT2_8075 | GGT
48513 | LPE_GT3_8080 | GGT
48514 | LPE_GT4_8085 | GGT
48520 | BSF_GT1_8070 | Cogen
48520 | BSF_GT1_8070 | Cogen
48521 | BVE_GT1_GT1 | CC
48522 | BVE_GT2_5035 | CC
48523 | BVE_ST1_GN1 | CC
48531 | BYU_GT1_8075 | Cogen
48532 | BYU_GT2_8055 | Cogen
48533 | BYU_GT3_8060 | Cogen
48534 | BYU_GT4_8065 | Cogen
48551 | CAL_GT1_8045 | Cogen
48552 | CAL_ST1_8000 | Cogen
48561 | CTL_GT2_8130 | Cogen
48562 | CTL_GT3_8135 | Cogen
48563 | CTL_GT4_8140 | Cogen
48564 | CTL_GN1_8145 | Cogen
48565 | CTL_GN2_8155 | Cogen
48581 | CBY_GN1_1 | GSC
48582 | CBY_GN2_2 | GSC
48583 | CBY_GT4_1 | GSC
48584 | CBY_GT4_2 | CC
48585 | CBY_ST4_1 | CC
48591 | CHE_GT2_5030 | Cogen
48593 | CHE_GT1_8015 | Cogen
48594 | CHE_GN4_8025 | Cogen
48595 | BTE_GT2_8075 | CC
48596 | BTE_GT3_8045 | CC
48597 | BTE_GT4_8055 | CC
48598 | BTE_ST1_8070 | CC
48611 | DIB_GT1_8080 | Cogen
48612 | DIB_GT2_8075 | Cogen
48613 | DIB_ST1_8085 | Cogen
48614 | DIB_GT3_8090 | Cogen
48641 | DPEC_GT15040 | CC
48642 | DPEC_GT25025 | CC
48643 | DPEC_GT35010 | CC
48644 | DPEC_GT45070 | CC
48645 | DPEC_ST55065 | CC
48651 | EP_1_2 | Cogen
48651 | EP_1_2 | Cogen
48671 | FTR_GT1_5105 | CC
48672 | FTR_GT2_5110 | CC
48673 | FTR_GT3_5085 | CC
48674 | FTR_CN4_5095 | CC
48690 | GBY_GN5_5 | GSC
48691 | GBY_73741085 | GGT
48691 | GBY_73741085 | GGT
48692 | GBY_81821075 | GGT
48692 | GBY_81821075 | GGT
48693 | GBY_83841065 | GGT
48693 | GBY_83841065 | GGT
48721 | LEG_1___1 | LIGCO
48722 | LEG_2___2 | LIGCO
48730 | MNS_GT | Cogen
48731 | CBE_GT1 | CC
48732 | CBE_GT2 | CC
48733 | CBE_ST12 | CC
48734 | CBE_GT3 | CC
48735 | CBE_GT4 | CC
48736 | CBE_ST34 | CC
48740 | PSG_GN2_8050 | Cogen
48741 | PSG_GT2_8040 | Cogen
48742 | PSG_GT3_8060 | Cogen
48761 | PR_GT1__9040 | Cogen
48772 | PHR_GN2_2 | GSC
48791 | PSA_GT1_8160 | Cogen
48792 | PSA_GT2_8155 | Cogen
48793 | PSA_GT3_8150 | Cogen
48794 | PSA_GT4_8145 | Cogen
48795 | PSA_GT5_8140 | Cogen
48796 | PSA_GN1_8165 | Cogen
48797 | PSA_GT6_8135 | Cogen
48811 | CVC_GT3_5045 | Cogen
48812 | CVC_GT2_5020 | Cogen
48813 | CVC_GT1_5035 | Cogen
48814 | CVC_ST5_5040 | Cogen
48815 | CVC_GT4_8005 | Cogen
48820 | SHELLG1_3015 | Cogen
48821 | SHELLG2 | Cogen
48822 | SHELLG3_3020 | Cogen
48822 | SHELLG3_3020 | Cogen
48841 | SJS_GT1_GT1 | Cogen
48842 | SJS_GT2_GT2 | Cogen
48845 | SOL_GT1 | Solar
48851 | SRB_GN1_1 | GST
48852 | SRB_GN2_2 | GST
48853 | SRB_GN3_3 | GST
48854 | SRB_GN4_4 | GST
48855 | SRB_GT211035 | GGT
48855 | SRB_GT211035 | GGT
48873 | THW_ST3_ST_3 | CC
48874 | THW_ST4_ST_4 | CC
48875 | THW_3132 | CC
48875 | THW_3132 | CC
48877 | THW_3334 | CC
48877 | THW_3334 | CC
48879 | THW_4142 | CC
48879 | THW_4142 | CC
48881 | THW_4344 | CC
48881 | THW_4344 | CC
48883 | THW_GT1_GT_1 | GGT
48885 | THW_5152 | GGT
48885 | THW_5152 | GGT
48886 | THW_5354 | GGT
48886 | THW_5354 | GGT
48887 | THW_5556 | GGT
48887 | THW_5556 | GGT
48911 | TGF_GT1_8000 | Cogen
48921 | WAP_GN1_1 | GST
48922 | WAP_GN2_2 | GST
48923 | WAP_GN3_3 | GST
48924 | WAP_GN4_4 | GSC
48925 | WAP_GN5_5 | LIGCO
48926 | WAP_GN6_6 | LIGCO
48927 | WAP_GN7_7 | LIGCO
48928 | WAP_GN8_8 | LIGCO
48929 | WAPGT21_GT1 | GGT
49803 | EXN_15GT | Cogen
49804 | EXN_16GT | Cogen
49805 | EXN_17GT | Cogen
49826 | EXN938GT | Cogen
49828 | EXN941GT | Cogen
49829 | EXN942GT | Cogen
49830 | EXN943GT | Cogen
49831 | EXN944GT | Cogen
49832 | EXN945GT | Cogen
49837 | EXN_GT | Cogen
49838 | EXN_14GT | Cogen
49851 | DOW17000 | Cogen
49858 | DOW38100 | Cogen
49859 | DOW38200 | Cogen
49860 | DOW38300 | Cogen
49862 | DOW39100 | Cogen
49863 | DOW39200 | Cogen
49865 | DOW41000 | Cogen
49866 | DOW42000 | Cogen
49869 | DOW49000 | Cogen
49870 | DOW61000 | Cogen
49871 | DOW62000 | Cogen
49872 | DOW63000 | Cogen
49873 | DOW64000 | Cogen
49876 | DOW65000 | Cogen
49877 | DOW66000 | Cogen
49878 | DOW67000 | Cogen
49882 | DOW81000 | Cogen
49884 | DOW82000 | Cogen
49885 | DOW83000 | Cogen
49886 | DOW84000 | Cogen
60000 | DSKY2 | Wind
60003 | KING_NE1A | Wind
60005 | KING_SE1A | Wind
60007 | KING_SW1A | Wind
60016 | WOODWRD11A | Wind
60017 | ORNNWP1 | Wind
60018 | DSKY1 | Wind
60019 | KING_NW1A | Wind
60052 | WILDHRS11A | Wind
60053 | WILDHRS21A | Wind
60057 | CALLAHAN1A | Wind
60058 | BUFF_GAP1A | Wind
60060 | CIRELLO | Wind
60063 | BUFF_GAP1B | Wind
60066 | H_HOLLOW1A | Wind
60068 | HHOLLOW21A | Wind
60070 | HHOLLOW31A | Wind
60072 | HHOLLOW41A | Wind
60081 | WHRLWIND1A | Wind
60201 | RIO DRCS | AVR
60202 | FRNDDRCS | AVR
71051 | L_BITTCR1_1N | Wind
71054 | L_SWEETW1_1N | Wind
71057 | L_SWEETW1_2N | Wind
71059 | L_SWEETW1_3N | Wind
71060 | L_SWEETW1_4N | Wind
76031 | L_GASCCR1_1N | Wind
76091 | L_DIVIDE1_1N | Wind
80003 | MILHWYS | AVR
80010 | EPLVT1 | AVR
80012 | LAR | DCTie
80051 | FOR #8 | Cogen
80052 | FOR #9 | Cogen
80053 | FOR #10 | Cogen
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80137 | CSDR89 | DCTie
80137 | CSDR89 | DCTie
80138 | CSDR7 | DCTie
80139 | CSDR56 | DCTie
80139 | CSDR56 | DCTie
80140 | CSDR11 | DCTie
80180 | PNSCALT11A | Wind
80180 | PNSCALT11A | Wind
80181 | PNSCALT21A | Wind
80181 | PNSCALT21A | Wind
80223 | REYSHR G | Cogen
80224 | VISTRONG1 | Cogen
80225 | VISTRONG2 | Cogen
80226 | ALCOA G | Cogen
80227 | AIRCO G | Cogen
80265 | LARECU40A | GGT
80266 | LARECU50A | GGT
88198 | BEEVILLE | AVR
88253 | HAMILTON | BLT
88299 | ZAPATA | BLT
88508 | FALFURRI | AVR