## Set up
Step 1 | Go to the Zones worksheet in this workbook. Make sure that the source and sink zones are set correctly and the "1"s and "-1"s are correct |  |  |  | Summary of Key Data points | Value
[5 empty] | File Description: Cont_ TempleSS to TemplePEC and TempleSS to LakeCreek OL_ Evant to Goldthwaite | Cont_ TempleSS to TemplePEC and TempleSS to LakeCreek OL_ Evant to Goldthwaite
Step 2 | Open Dennis' file that needs to have the data transferred, same file that is listed in cell K29 |  |  |  | Number of units | 624
[5 empty] | Dec Concentrated Generation | 283.5
Step 3 | Copy columns J:X from an old Dennis' Sheet to the new sheet (if first round of a new alaysis) |  |  |  | Dec Line weighted impact | 16.9698
[5 empty] | Dec PTDF | 0.059858
Step 4 | Mark the contingencies and monitored element set by a "y" in column K of Dennis' sheet, if there are a match on the filename use something to make unique |  |  |  | Dec Concentration | 1.6893
[5 empty] | Inc Concentrated Generation | 423.3
Step 5 | Enter Dennis' file name into cell K29 |  |  |  | Inc Line weighted impact | 31.582
[5 empty] | Inc PTDF | 0.074609
Step 6 | click the step one button |  |  |  | Inc Concentartion | 2.1056
[5 empty] | Source Zonal weighted AWGSF | 0.01396
Step 7 | Enter the line ratings in Dennis' workbook, the Input worksheet, in the cells |  |  |  | Sink Zonal weighted AWGSF | -0.021474
| X6:X30, or to the end of the selected list. |  |  |  | Source - Sink PTDF | 0.035434
[5 empty] | OL Line Rating (MW) | 128
Step 8 | Check to see that the number of generators in Dennis' file matches the length |  |  |  | Source Zone (diagnostic) | North
| of the formulas in columns L:X (Distributed Slack - Dec) have been copied through to the apporpriate number of rows |  |  |  | Sink Zone (diagnostic) | South
If Dennis' sheet data is less than this file then clear any old unit data in columns A:K of this workbook to match the correct length
Clear any old data that will be below the new data iin the "Distributed Slack - Inc" worksheet, as well
Step 9 | Click the step 2 button
The last file saved will still be open, you will need to close this file.
This Template sheet will no longer be open.
|  | Current Source Zone | North
|  | Current Sink Zone | South | NS_062609automation.xls
The file listed in cell K29 needs to be in the same folder as this template file
Copy Dennis' data step 1
Copy Dennis' Data Step 2

## Distributed Slack - Dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Concentrated Capacity | Cumulative Concentrated Impact | Cont_ TempleSS to TemplePEC and TempleSS to LakeCreek OL_ Evant to Goldthwaite
6407 | TURKTRAK1A | 1 | West | YES | 0.040325 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.061799 | 0 | 169.5 |  |  |  |  | 0.061799 | 10.475 | 169.5 | 10.475
60057 | CALLAHAN1A | 1 | West | YES | 0.035498 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.056972 | 0 | 114 |  |  |  |  | 0.056972 | 6.4948 | 283.5 | 16.9698 |  |  |  | 624
1643 | SLSTR1PP_1G | 1 | North | YES | 0.034716 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.05619 | 0 | 60 | 2.083 | 60 |  |  | 0.05619 | 3.3714
1343 | TRENTIPP_8 | 1 | West | YES | 0.031074 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.052548 | 0 | 150 |  |  |  |  | 0.052548 | 7.8822 |  |  | Weighted Shift Factors |  | chk
1354 | AEPWIND_8 | 1 | West | YES | 0.031074 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.052548 | 0 | 101 |  |  |  |  | 0.052548 | 5.3074 |  |  | North | 0.01396 | 0.01396
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.029418 | 110 | 0 | 550 | 0 | 1.02 | Wind | 1 | 0.050892 | 0 | 550 |  |  |  |  | 0.050892 | 27.9907 |  |  | South | -0.021474 | -0.021474
1349 | WESTXWIN_1G | 1 | West | YES | 0.029353 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.050827 | 0 | 6.6 |  |  |  |  | 0.050827 | 0.33546 |  |  |  | 0.035434 | 0.035434
1350 | NWPWRG1_1G | 1 | West | YES | 0.029353 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.050827 | 0 | 34.3 |  |  |  |  | 0.050827 | 1.7434
76031 | L_GASCCR1_1N | W1 | West | YES | 0.02916 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.050634 | 0 | 150 |  |  |  |  | 0.050634 | 7.5951 |  |  | Line Cap | 128
60058 | BUFF_GAP1A | 1 | West | YES | 0.029033 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.050507 | 0 | 120 |  |  |  |  | 0.050507 | 6.0609 |  |  | Conc Gen | 283.5
60060 | CIRELLO | 1 | West | YES | 0.029033 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.050507 | 0 | 233 |  |  |  |  | 0.050507 | 11.7682 |  |  | Weighted Imp. | 16.9698
60063 | BUFF_GAP1B | 1 | West | YES | 0.029033 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.050507 | 0 | 170.2 |  |  |  |  | 0.050507 | 8.5963 |  |  | PTDF | 0.059858
60066 | H_HOLLOW1A | 1 | West | YES | 0.029033 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.050507 | 0 | 222 |  |  |  |  | 0.050507 | 11.2126
60068 | HHOLLOW21A | 1 | West | YES | 0.029033 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.050507 | 0 | 184 |  |  |  |  | 0.050507 | 9.2933 |  |  | Concentration | 1.6893
60070 | HHOLLOW31A | 1 | West | YES | 0.029033 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.050507 | 0 | 224 |  |  |  |  | 0.050507 | 11.3136
60072 | HHOLLOW41A | 1 | West | YES | 0.029033 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.050507 | 0 | 115 |  |  |  |  | 0.050507 | 5.8083 |  |  |  | Pass
6144 | MCADOO1A | 1 | West | YES | 0.028867 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.050341 | 0 | 150 |  |  |  |  | 0.050341 | 7.5512
60081 | WHRLWIND1A | 1 | West | YES | 0.028603 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.050077 | 0 | 60 |  |  |  |  | 0.050077 | 3.0046
1320 | BSP 1 | 1 | West | YES | 0.028582 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.050056 | 0 | 0 |  |  |  |  | 0.050056 | 0
60052 | WILDHRS11A | 1 | West | YES | 0.02847 | 25.3 | 0 | 126.5 | 0 | 1.005 | Wind | 1 | 0.049944 | 0 | 126.5 |  |  |  |  | 0.049944 | 6.3179
60053 | WILDHRS21A | 1 | West | YES | 0.02847 | 7.8 | 0 | 39 | 0 | 1.025 | Wind | 1 | 0.049944 | 0 | 39 |  |  |  |  | 0.049944 | 1.9478
36998 | RDCNYNG1 | 1 | West | YES | 0.028468 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.049942 | 0 | 84 |  |  |  |  | 0.049942 | 4.1951
6637 | SNYDERW1A | 1 | West | YES | 0.028402 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.049876 | 0 | 63 |  |  |  |  | 0.049876 | 3.1422
1061 | CIELOGEN_1G | 1 | West | YES | 0.028377 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.049851 | 0 | 99 |  |  |  |  | 0.049851 | 4.9353
1062 | CIELOGEN_2G | 1 | West | YES | 0.028377 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.049851 | 0 | 61 |  |  |  |  | 0.049851 | 3.0409
1069 | KINDERMG_1G | 1 | West | YES | 0.028377 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.049851 | 0 | 0 |  |  |  |  | 0.049851 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.028377 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.049851 | 0 | 0 |  |  |  |  | 0.049851 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.028377 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.049851 | 0 | 0 |  |  |  |  | 0.049851 | 0
1068 | SCURRYCW_1G | 1 | West | YES | 0.028375 | 28.2 | 1.3 | 141 |  | 1.01 | Wind | 1 | 0.049849 | 0 | 141 |  |  |  |  | 0.049849 | 7.0287
1073 | SCURRYCW_2G | 2 | West | YES | 0.028375 | 24 | 0 | 120 | 0 | 1.017 | Wind | 1 | 0.049849 | 0 | 120 |  |  |  |  | 0.049849 | 5.9819
1360 | GUNSIGHT_8 | 1 | West | YES | 0.028329 | 24 | 0 | 120 | 0 | 1.01 | Wind | 1 | 0.049803 | 0 | 120 |  |  |  |  | 0.049803 | 5.9764
1327 | WILDHRSE_1G | 1 | West | YES | 0.028315 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.049789 | 0 | 120 |  |  |  |  | 0.049789 | 5.9747
1301 | BULLCREK_8 | 1 | West | YES | 0.028304 | 36 | 0 | 180 | 0 | 1.017 | Wind | 1 | 0.049778 | 0 | 180 |  |  |  |  | 0.049778 | 8.9601
1302 | COYOTEWG_8 | 1 | West | YES | 0.028227 | 45 | 0 | 225 |  | 1.01 | Wind | 1 | 0.049701 | 0 | 225 |  |  |  |  | 0.049701 | 11.1828
1037 | MORGAN5G_5G | 5 | West | YES | 0.028179 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.049653 | 137 | 137 |  |  |  |  | 0.049653 | 6.8025
1039 | MRGNAG_1G | A | West | YES | 0.028179 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.049653 | 69 | 69 |  |  |  |  | 0.049653 | 3.4261
1040 | MRGNBG_2G | B | West | YES | 0.028179 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.049653 | 71 | 71 |  |  |  |  | 0.049653 | 3.5254
1041 | MRGNCG_3G | C | West | YES | 0.028179 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.049653 | 70 | 70 |  |  |  |  | 0.049653 | 3.4757
1042 | MRGNDG_4G | D | West | YES | 0.028179 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.049653 | 68 | 68 |  |  |  |  | 0.049653 | 3.3764
1043 | MRGNEG_5G | E | West | YES | 0.028179 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.049653 | 70 | 70 |  |  |  |  | 0.049653 | 3.4757
1044 | MRGNFG_6G | F | West | YES | 0.028179 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.049653 | 66 | 66 |  |  |  |  | 0.049653 | 3.2771
1170 | AIRLAMESA_1G | 1 | West | YES | 0.028119 | 0 | 0 | 180 |  | 1 | Wind | 1 | 0.049593 | 0 | 180 |  |  |  |  | 0.049593 | 8.9268
1326 | STANTONW_8 | 1 | West | YES | 0.028015 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.049489 | 0 | 100.5 |  |  |  |  | 0.049489 | 4.9737
1333 | MCDDONAL_8 | 1 | West | YES | 0.028002 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.049476 | 0 | 214.2 |  |  |  |  | 0.049476 | 10.5978
1328 | OCOTILLO_1G | 1 | West | YES | 0.027973 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.049447 | 0 | 58 |  |  |  |  | 0.049447 | 2.8679
1058 | LONGSHORE_5 | 1 | West | YES | 0.027816 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.04929 | 0 | 150 |  |  |  |  | 0.04929 | 7.3935
1058 | LONGSHORE_5 | 2 | West | YES | 0.027816 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.04929 | 0 | 220 |  |  |  |  | 0.04929 | 10.8438
1058 | LONGSHORE_5 | 3 | West | YES | 0.027816 | 23.4 | 0 | 117 |  | 1.01 | Wind | 1 | 0.04929 | 0 | 117 |  |  |  |  | 0.04929 | 5.7669
1045 | CALENG1G_1G | 1 | West | YES | 0.027812 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.049286 | 0 | 0 |  |  |  |  | 0.049286 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.027812 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.049286 | 0 | 0 |  |  |  |  | 0.049286 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.027812 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.049286 | 0 | 0 |  |  |  |  | 0.049286 | 0
11001 | NAV1CT | 1 | West | YES | 0.02775 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.049224 | 70.4 | 70.4 |  |  |  |  | 0.049224 | 3.4654
11009 | NAV2CT | 1 | West | YES | 0.02775 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.049224 | 71.4 | 71.4 |  |  |  |  | 0.049224 | 3.5146
11011 | NAV3ST | 1 | West | YES | 0.02775 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.049224 | 92.8 | 92.8 |  |  |  |  | 0.049224 | 4.568
11012 | NAV4CT | 1 | West | YES | 0.02775 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.049224 | 80 | 80 |  |  |  |  | 0.049224 | 3.9379
11013 | NAV5CT | 1 | West | YES | 0.02775 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.049224 | 80 | 80 |  |  |  |  | 0.049224 | 3.9379
11014 | NAV6ST | 1 | West | YES | 0.02775 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.049224 | 115 | 115 |  |  |  |  | 0.049224 | 5.6608
11020 | TIEHVSG_1G | 1 | West | YES | 0.027749 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.049223 | 208.2 | 208.2 |  |  |  |  | 0.049223 | 10.2483
11021 | TIEHVCG_1G | 1 | West | YES | 0.027749 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.049223 | 142.1 | 142.1 |  |  |  |  | 0.049223 | 6.9946
11022 | TIEHVCG_2G | 1 | West | YES | 0.027749 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.049223 | 132.4 | 132.4 |  |  |  |  | 0.049223 | 6.5171
11023 | TIEHVCG_3G | 1 | West | YES | 0.027749 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.049223 | 137.4 | 137.4 |  |  |  |  | 0.049223 | 6.7633
11024 | TIEHVCG_4G | 1 | West | YES | 0.027749 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.049223 | 147 | 147 |  |  |  |  | 0.049223 | 7.2358
11025 | TIEHVSG_2G | 1 | West | YES | 0.027749 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.049223 | 213.2 | 213.2 |  |  |  |  | 0.049223 | 10.4944
1146 | NOTREES_1G | 1 | West | YES | 0.027716 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.04919 | 0 | 149 |  |  |  |  | 0.04919 | 7.3293
71051 | L_BITTCR1_1N | W1 | West | YES | 0.027686 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.04916 | 0 | 37.5 |  |  |  |  | 0.04916 | 1.8435
71054 | L_SWEETW1_1N | W1 | West | YES | 0.027686 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.04916 | 0 | 107.5 |  |  |  |  | 0.04916 | 5.2847
71057 | L_SWEETW1_2N | W1 | West | YES | 0.027686 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.04916 | 0 | 135 |  |  |  |  | 0.04916 | 6.6366
71059 | L_SWEETW1_3N | W1 | West | YES | 0.027686 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.04916 | 0 | 119 |  |  |  |  | 0.04916 | 5.8501
71060 | L_SWEETW1_4N | W1 | West | YES | 0.027686 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.04916 | 0 | 105 |  |  |  |  | 0.04916 | 5.1618
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.027682 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.049156 | 0 | 30 |  |  |  |  | 0.049156 | 1.4747
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.027682 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.049156 | 0 | 35 |  |  |  |  | 0.049156 | 1.7205
1002 | PBCTAGE_1G | A | West | YES | 0.027665 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.049139 | 66 | 66 |  |  |  |  | 0.049139 | 3.2432
1003 | PBCTBGE_2G | B | West | YES | 0.027665 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.049139 | 66 | 66 |  |  |  |  | 0.049139 | 3.2432
1004 | PBCTCGE_3G | C | West | YES | 0.027665 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.049139 | 67 | 67 |  |  |  |  | 0.049139 | 3.2923
1005 | PBCTDGE_4G | D | West | YES | 0.027665 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.049139 | 68 | 68 |  |  |  |  | 0.049139 | 3.3415
1006 | PBCTEGE_5G | E | West | YES | 0.027665 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.049139 | 67 | 67 |  |  |  |  | 0.049139 | 3.2923
1007 | PB5GEN_6G | 5 | West | YES | 0.027665 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.049139 | 114 | 114 |  |  |  |  | 0.049139 | 5.6019
1008 | PB6GEN_7G | 6 | West | YES | 0.027665 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.049139 | 515 | 515 |  |  |  |  | 0.049139 | 25.3067
1049 | ROSCOEWI_5 | 1 | West | YES | 0.027205 | 41.8 | 0 | 209 |  | 1.01 | Wind | 1 | 0.048679 | 0 | 209 |  |  |  |  | 0.048679 | 10.1739
1057 | ROSCOEWI_5 | 2 | West | YES | 0.027205 | 25.3 | 0 | 126.5 |  | 1.01 | Wind | 1 | 0.048679 | 0 | 126.5 |  |  |  |  | 0.048679 | 6.1579
1060 | ROSCOEWI_5 | 3 | West | YES | 0.027205 | 39.4 | 0 | 197 | 0 | 1.01 | Wind | 1 | 0.048679 | 0 | 197 |  |  |  |  | 0.048679 | 9.5898
1072 | ROSCOEWI_5 | 4 | West | YES | 0.027205 | 63.6 | 0 | 318 | 0 | 1.01 | Wind | 1 | 0.048679 | 0 | 318 |  |  |  |  | 0.048679 | 15.48
1416 | SWETWATR_1G | 1 | West | YES | 0.027065 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.048539 | 30 | 30 |  |  |  |  | 0.048539 | 1.4562
1417 | SWETWATR_2G | 2 | West | YES | 0.027065 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.048539 | 72 | 72 |  |  |  |  | 0.048539 | 3.4948
1418 | SWETWATR_3G | 3 | West | YES | 0.027065 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.048539 | 68 | 68 |  |  |  |  | 0.048539 | 3.3007
1419 | SWETWATR_4G | 4 | West | YES | 0.027065 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.048539 | 61 | 61 |  |  |  |  | 0.048539 | 2.9609
60007 | KING_SW1A | 1 | West | YES | 0.026805 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.048279 | 0 | 80 |  |  |  |  | 0.048279 | 3.8623
60019 | KING_NW1A | 1 | West | YES | 0.026805 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.048279 | 0 | 80 |  |  |  |  | 0.048279 | 3.8623
332 | RWMILLER01 | 1 | North | YES | 0.026747 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.048221 | 73 | 73 | 1.9525 | 73 |  |  | 0.048221 | 3.5201
333 | RWMILLER02 | 2 | North | YES | 0.026747 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.048221 | 119 | 119 | 3.1829 | 119 |  |  | 0.048221 | 5.7383
334 | RWMILLER03 | 3 | North | YES | 0.026747 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.048221 | 208 | 208 | 5.5634 | 208 |  |  | 0.048221 | 10.03
335 | RWMILLER04 | 4 | North | YES | 0.026747 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.048221 | 102 | 102 | 2.7282 | 102 |  |  | 0.048221 | 4.9186
336 | RWMILLER05 | 5 | North | YES | 0.026747 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.048221 | 101 | 101 | 2.7014 | 101 |  |  | 0.048221 | 4.8703
60201 | RIO DRCS | F | West | YES | 0.026713 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.048187 | 0 | 0 |  |  |  |  | 0.048187 | 0
60016 | WOODWRD11A | 1 | West | YES | 0.026707 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.048181 | 0 | 80 |  |  |  |  | 0.048181 | 3.8545
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.026705 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.048179 | 0 | 80 |  |  |  |  | 0.048179 | 3.8543
38437 | TNSRBNMESA9 | 1 | West | YES | 0.026698 | 37.5 | 0 | 150 |  | 1.02 | Wind | 1 | 0.048172 | 0 | 150 |  |  |  |  | 0.048172 | 7.2258
6016 | SWMESA | 1 | West | YES | 0.026683 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.048157 | 0 | 75 |  |  |  |  | 0.048157 | 3.6118
60003 | KING_NE1A | 1 | West | YES | 0.026683 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.048157 | 0 | 80 |  |  |  |  | 0.048157 | 3.8526
60005 | KING_SE1A | 1 | West | YES | 0.026683 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.048157 | 0 | 40 |  |  |  |  | 0.048157 | 1.9263
60000 | DSKY2 | 1 | West | YES | 0.026518 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.047992 | 0 | 76.5 |  |  |  |  | 0.047992 | 3.6714
60017 | ORNNWP1 | 1 | West | YES | 0.026415 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.047889 | 0 | 80 |  |  |  |  | 0.047889 | 3.8311
60018 | DSKY1 | 1 | West | YES | 0.026321 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.047795 | 0 | 84 |  |  |  |  | 0.047795 | 4.0148
1437 | MESQUITW_1G | 1 | North | YES | 0.025874 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.047348 | 0 | 400 | 10.3496 | 400 |  |  | 0.047348 | 18.9393
1438 | MESQUITW_2G | 1 | North | YES | 0.025869 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.047343 | 0 | 236 | 6.1051 | 236 |  |  | 0.047343 | 11.173
1442 | COKFIELD_5 | 1 | North | YES | 0.025181 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.046655 | 0 | 165 | 4.1549 | 165 |  |  | 0.046655 | 7.6981
6100 | OKLA7A | EQ | West | YES | 0.024929 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.046403 | 0 | 0 |  |  |  |  | 0.046403 | 0
6752 | OKLA0A | 1 | West | YES | 0.024929 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.046403 | 0 | 649.7 |  |  |  |  | 0.046403 | 30.1481
1433 | GRHAMSES_1G | 1 | North | YES | 0.024583 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.046057 | 242 | 242 | 5.9491 | 242 |  |  | 0.046057 | 11.1458
60202 | FRNDDRCS | F | West | YES | 0.024527 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.046001 | 0 | 0 |  |  |  |  | 0.046001 | 0
1479 | WFCOGEN_1G | 1 | North | YES | 0.023186 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.04466 | 0 | 0 | 0 | 0 |  |  | 0.04466 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.023186 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.04466 | 0 | 0 | 0 | 0 |  |  | 0.04466 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.023186 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.04466 | 0 | 0 | 0 | 0 |  |  | 0.04466 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.023186 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.04466 | 0 | 0 | 0 | 0 |  |  | 0.04466 | 0
1600 | BARTNWND_1G | 1 | North | YES | 0.023107 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.044581 | 0 | 120 | 2.7728 | 120 |  |  | 0.044581 | 5.3497
1432 | GRHAMSES_2G | 2 | North | YES | 0.023002 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.044476 | 366 | 366 | 8.4187 | 366 |  |  | 0.044476 | 16.2783
344 | MRSSHPRD | 1 | North | YES | 0.022829 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.044303 | 0 | 0 | 0 | 0 |  |  | 0.044303 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.022829 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.044303 | 0 | 0 | 0 | 0 |  |  | 0.044303 | 0
1898 | COMCHEPK_1G | 1 | North | YES | 0.022157 | 1159 | 1150 | 1159 | 0 | 1.032 | Nuc | 1 | 0.043631 | 0 | 0 | 0 | 0 |  |  | 0.043631 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.022157 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.043631 | 0 | 0 | 0 | 0 |  |  | 0.043631 | 0
1877 | WLFHOLW_1G | 1 | North | YES | 0.021423 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.042897 | 217.3 | 217.3 | 4.6552 | 217.3 |  |  | 0.042897 | 9.3215
1878 | WLFHOLW_2G | 2 | North | YES | 0.021423 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.042897 | 215.7 | 215.7 | 4.6209 | 215.7 |  |  | 0.042897 | 9.2529
1879 | WLFHOLW_3G | 3 | North | YES | 0.021423 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.042897 | 272.4 | 272.4 | 5.8356 | 272.4 |  |  | 0.042897 | 11.6852
503 | NTHTEXAS01 | 1 | North | YES | 0.021393 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.042867 | 18 | 18 | 0.38507 | 18 |  |  | 0.042867 | 0.77161
504 | NTHTEXAS02 | 2 | North | YES | 0.021393 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.042867 | 18 | 18 | 0.38507 | 18 |  |  | 0.042867 | 0.77161
505 | NTHTEXAS03 | 3 | North | YES | 0.021393 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.042867 | 38 | 38 | 0.81293 | 38 |  |  | 0.042867 | 1.629
1892 | DECRDOVA_2G | A | North | YES | 0.021062 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.042536 | 70 | 70 | 1.4743 | 70 |  |  | 0.042536 | 2.9775
1893 | DECRDOVA_3G | B | North | YES | 0.021062 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.042536 | 69 | 69 | 1.4533 | 69 |  |  | 0.042536 | 2.935
1894 | DECRDOVA_4G | C | North | YES | 0.021062 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.042536 | 69 | 69 | 1.4533 | 69 |  |  | 0.042536 | 2.935
1895 | DECRDOVA_5G | D | North | YES | 0.021062 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.042536 | 68 | 68 | 1.4322 | 68 |  |  | 0.042536 | 2.8925
1453 | WCPWRCO_1G | 1 | North | YES | 0.02083 | 204 | 50 | 204 |  | 1.02 | CC | 1 | 0.042304 | 204 | 204 | 4.2493 | 204 |  |  | 0.042304 | 8.63
1454 | WCPWRCO_2G | 2 | North | YES | 0.02083 | 204 | 50 | 204 |  | 1.02 | CC | 1 | 0.042304 | 204 | 204 | 4.2493 | 204 |  |  | 0.042304 | 8.63
1455 | WCPWRCO_3G | 3 | North | YES | 0.02083 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.042304 | 242 | 242 | 5.0409 | 242 |  |  | 0.042304 | 10.2376
1889 | DECRDOVA_1G | 1 | North | YES | 0.020422 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.041896 | 779 | 779 | 15.9087 | 779 |  |  | 0.041896 | 32.6371
580 | JCKCNTY801 | 1 | North | YES | 0.020204 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.041678 | 288 | 288 | 5.8188 | 288 |  |  | 0.041678 | 12.0033
581 | JCKCNTY802 | 2 | North | YES | 0.020204 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.041678 | 147 | 147 | 2.97 | 147 |  |  | 0.041678 | 6.1267
582 | JCKCNTY803 | 3 | North | YES | 0.020204 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.041678 | 147 | 147 | 2.97 | 147 |  |  | 0.041678 | 6.1267
728 | WOLFRIDGE801 | 1 | North | YES | 0.018745 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.040219 | 0 | 112.5 | 2.1088 | 112.5 |  |  | 0.040219 | 4.5247
366 | JNSNCNTY802 | 1 | North | YES | 0.018579 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.040053 | 0 | 0 | 0 | 0 |  |  | 0.040053 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.018579 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.040053 | 0 | 0 | 0 | 0 |  |  | 0.040053 | 0
1861 | EAGLEMNT_1G | MB | North | YES | 0.018408 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.039882 | 0 | 0 | 0 | 0 |  |  | 0.039882 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.018408 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.039882 | 0 | 0 | 0 | 0 |  |  | 0.039882 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.018408 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.039882 | 0 | 0 | 0 | 0 |  |  | 0.039882 | 0
923 | SPENCER_G4 | 1 | North | YES | 0.017537 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.039011 | 61 | 61 | 1.0698 | 61 |  |  | 0.039011 | 2.3797
924 | SPENCER_G5 | 1 | North | YES | 0.017537 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.039011 | 66 | 66 | 1.1574 | 66 |  |  | 0.039011 | 2.5747
1945 | HANDLEY_1G | MB | North | YES | 0.017122 | 0 | 25 | 36 |  | 0.986 | GST | 1 | 0.038596 | 0 | 0 | 0 | 0 |  |  | 0.038596 | 0
1946 | HANDLEY_2G | MB | North | YES | 0.017122 | 0 | 30 | 68 |  | 0.986 | GST | 1 | 0.038596 | 0 | 0 | 0 | 0 |  |  | 0.038596 | 0
1947 | HANDLEY_3G | 3 | North | YES | 0.017026 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.0385 | 395 | 395 | 6.7253 | 395 |  |  | 0.0385 | 15.2076
1949 | HANDLEY_5G | 5 | North | YES | 0.017026 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.0385 | 435 | 435 | 7.4063 | 435 |  |  | 0.0385 | 16.7476
1948 | HANDLEY_4G | 4 | North | YES | 0.016873 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.038347 | 435 | 435 | 7.3398 | 435 |  |  | 0.038347 | 16.681
1937 | MDLTHELP_5G | 5 | North | YES | 0.015717 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.037191 | 224 | 224 | 3.5206 | 224 |  |  | 0.037191 | 8.3308
1938 | MDLTHELP_6G | 6 | North | YES | 0.015717 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.037191 | 226 | 226 | 3.552 | 226 |  |  | 0.037191 | 8.4052
1943 | MDLTHELP_3G | 3 | North | YES | 0.015717 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.037191 | 212 | 212 | 3.332 | 212 |  |  | 0.037191 | 7.8845
1944 | MDLTHELP_4G | 4 | North | YES | 0.015717 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.037191 | 211 | 211 | 3.3163 | 211 |  |  | 0.037191 | 7.8473
2371 | COLLIN_1G | MB | North | YES | 0.015701 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.037175 | 0 | 0 | 0 | 0 |  |  | 0.037175 | 0
2381 | NTHLK1_G | 1 | North | YES | 0.015554 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.037028 | 156 | 156 | 2.4264 | 156 |  |  | 0.037028 | 5.7764
2382 | NTHLK2_G | 2 | North | YES | 0.015554 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.037028 | 181 | 181 | 2.8153 | 181 |  |  | 0.037028 | 6.7021
2383 | NTHLK3_G | 3 | North | YES | 0.015554 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.037028 | 329 | 329 | 5.1173 | 329 |  |  | 0.037028 | 12.1823
6948 | DENISNDM | 1 | North | YES | 0.015442 | 40 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.036916 | 0 | 0 | 0 | 0 |  |  | 0.036916 | 0
6948 | DENISNDM | 2 | North | YES | 0.015442 | 31 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.036916 | 0 | 0 | 0 | 0 |  |  | 0.036916 | 0
1687 | VALLEY_1G | 1 | North | YES | 0.01531 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.036784 | 170 | 170 | 2.6027 | 170 |  |  | 0.036784 | 6.2533
1688 | VALLEY_2G | 2 | North | YES | 0.01531 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.036784 | 527 | 527 | 8.0684 | 527 |  |  | 0.036784 | 19.3852
1689 | VALLEY_3G | 3 | North | YES | 0.015131 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.036605 | 375 | 375 | 5.6741 | 375 |  |  | 0.036605 | 13.7269
11691 | KMICHICT1_G | 1 | North | YES | 0.015131 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.036605 | 144 | 144 | 2.1789 | 144 |  |  | 0.036605 | 5.2711
11692 | KMICHICT2_G | 2 | North | YES | 0.015131 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.036605 | 146 | 146 | 2.2091 | 146 |  |  | 0.036605 | 5.3443
11693 | KMICHIST3_G | 3 | North | YES | 0.015131 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.036605 | 312 | 312 | 4.7209 | 312 |  |  | 0.036605 | 11.4208
11694 | KMICHICT4_G | 4 | North | YES | 0.015131 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.036605 | 144 | 144 | 2.1789 | 144 |  |  | 0.036605 | 5.2711
11695 | KMICHICT5_G | 5 | North | YES | 0.015131 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.036605 | 148 | 148 | 2.2394 | 148 |  |  | 0.036605 | 5.4176
11696 | KMICHIST6_G | 6 | North | YES | 0.015131 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.036605 | 310 | 310 | 4.6906 | 310 |  |  | 0.036605 | 11.3476
1678 | LAMARPWR_1G | 1 | North | YES | 0.015072 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.036546 | 160 | 160 | 2.4115 | 160 |  |  | 0.036546 | 5.8474
1679 | LAMARPWR_2G | 2 | North | YES | 0.015072 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.036546 | 156 | 156 | 2.3512 | 156 |  |  | 0.036546 | 5.7012
1680 | LAMARPWR_3G | 3 | North | YES | 0.015072 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.036546 | 196 | 196 | 2.9541 | 196 |  |  | 0.036546 | 7.163
1681 | LAMARPWR_4G | 4 | North | YES | 0.015072 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.036546 | 156 | 156 | 2.3512 | 156 |  |  | 0.036546 | 5.7012
1682 | LAMARPWR_5G | 5 | North | YES | 0.015072 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.036546 | 157 | 157 | 2.3663 | 157 |  |  | 0.036546 | 5.7377
1683 | LAMARPWR_6G | 6 | North | YES | 0.015072 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.036546 | 198 | 198 | 2.9843 | 198 |  |  | 0.036546 | 7.2361
2418 | MTCK2_G | 2 | North | YES | 0.015058 | 0 | 10 | 23 |  | 0.971 | GSC | 1 | 0.036532 | 23 | 23 | 0.34633 | 23 |  |  | 0.036532 | 0.84024
2419 | MTCK3_G | MB | North | YES | 0.015058 | 0 | 10 | 63 |  | 0.971 | GSC | 1 | 0.036532 | 0 | 0 | 0 | 0 |  |  | 0.036532 | 0
1675 | PEC_1G | 1 | North | YES | 0.01504 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.036514 | 0 | 0 | 0 | 0 |  |  | 0.036514 | 0
1676 | PEC_2G | 2 | North | YES | 0.01504 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.036514 | 0 | 0 | 0 | 0 |  |  | 0.036514 | 0
1677 | PEC_3G | 3 | North | YES | 0.01504 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.036514 | 0 | 0 | 0 | 0 |  |  | 0.036514 | 0
1701 | MOSES_1G | 1 | North | YES | 0.014959 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.036433 | 0 | 558 | 8.3471 | 558 |  |  | 0.036433 | 20.3297
1702 | MOSES_2G | 2 | North | YES | 0.014959 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.036433 | 0 | 579 | 8.6613 | 579 |  |  | 0.036433 | 21.0948
1703 | MOSES_3G | 3 | North | YES | 0.014959 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.036433 | 0 | 808 | 12.0869 | 808 |  |  | 0.036433 | 29.438
5925 | DCEAST | EQ | North | YES | 0.014959 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.036433 | 0 | 0 | 0 | 0 |  |  | 0.036433 | 0
2413 | MTCK6_G | 6 | North | YES | 0.014804 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.036278 | 118 | 118 | 1.7469 | 118 |  |  | 0.036278 | 4.2808
2414 | MTCK7_G | 7 | North | YES | 0.014804 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.036278 | 115 | 115 | 1.7025 | 115 |  |  | 0.036278 | 4.172
2417 | MTCK8_G | 8 | North | YES | 0.014804 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.036278 | 556 | 556 | 8.231 | 556 |  |  | 0.036278 | 20.1706
842 | OLINGER_G1 | 1 | North | YES | 0.014764 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.036238 | 79 | 79 | 1.1664 | 79 |  |  | 0.036238 | 2.8628
843 | OLINGER_G2 | 1 | North | YES | 0.014764 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.036238 | 110 | 110 | 1.624 | 110 |  |  | 0.036238 | 3.9862
844 | OLINGER_G3 | 1 | North | YES | 0.014764 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.036238 | 150 | 150 | 2.2146 | 150 |  |  | 0.036238 | 5.4357
845 | OLINGER_G4 | 1 | North | YES | 0.014764 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.036238 | 76 | 76 | 1.1221 | 76 |  |  | 0.036238 | 2.7541
837 | NEWMAN_G5 | 1 | North | YES | 0.014718 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.036192 | 40 | 40 | 0.58872 | 40 |  |  | 0.036192 | 1.4477
948 | STEAM1 | 1 | North | YES | 0.014692 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.036166 | 20 | 20 | 0.29384 | 20 |  |  | 0.036166 | 0.72332
949 | STEAM2 | 1 | North | YES | 0.014692 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.036166 | 26 | 26 | 0.38199 | 26 |  |  | 0.036166 | 0.94032
950 | STEAM3 | 1 | North | YES | 0.014692 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.036166 | 42 | 42 | 0.61706 | 42 |  |  | 0.036166 | 1.519
1941 | MDLTHELP_1G | 1 | North | YES | 0.014503 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.035977 | 216.4 | 216.4 | 3.1384 | 216.4 |  |  | 0.035977 | 7.7855
1942 | MDLTHELP_2G | 2 | North | YES | 0.014503 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.035977 | 216.1 | 216.1 | 3.1341 | 216.1 |  |  | 0.035977 | 7.7747
2451 | LKHB1_G | 1 | North | YES | 0.014493 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.035967 | 391 | 391 | 5.6668 | 391 |  |  | 0.035967 | 14.0631
2452 | LKHB2_G | 2 | North | YES | 0.014493 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.035967 | 516 | 516 | 7.4784 | 516 |  |  | 0.035967 | 18.559
12440 | PARKD_1SVC8 | 1 | North | YES | 0.014481 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.035955 | 0 | 0 | 0 | 0 |  |  | 0.035955 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.014481 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.035955 | 0 | 0 | 0 | 0 |  |  | 0.035955 | 0
12411 | FPLEFR1A_G | 1 | North | YES | 0.014284 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.035758 | 161 | 161 | 2.2997 | 161 |  |  | 0.035758 | 5.7571
12412 | FPLEFR1B_G | 2 | North | YES | 0.014284 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.035758 | 164 | 164 | 2.3426 | 164 |  |  | 0.035758 | 5.8643
12413 | FPLEFR1C_G | 3 | North | YES | 0.014284 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.035758 | 164 | 164 | 2.3426 | 164 |  |  | 0.035758 | 5.8643
12414 | FPLEFR1S_G | 4 | North | YES | 0.014284 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.035758 | 414 | 414 | 5.9136 | 414 |  |  | 0.035758 | 14.8039
12421 | FPLEFR2A_G | 1 | North | YES | 0.014284 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.035758 | 162 | 162 | 2.314 | 162 |  |  | 0.035758 | 5.7928
12422 | FPLEFR2B_G | 2 | North | YES | 0.014284 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.035758 | 161 | 161 | 2.2997 | 161 |  |  | 0.035758 | 5.7571
12423 | FPLEFR2C_G | 3 | North | YES | 0.014284 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.035758 | 163 | 163 | 2.3283 | 163 |  |  | 0.035758 | 5.8286
12424 | FPLEFR2S_G | 4 | North | YES | 0.014284 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.035758 | 415 | 415 | 5.9279 | 415 |  |  | 0.035758 | 14.8396
12322 | ENNSTRAC_1G | 1 | North | YES | 0.014109 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.035583 | 196 | 196 | 2.7654 | 196 |  |  | 0.035583 | 6.9743
12323 | ENNSTRAC_2G | 2 | North | YES | 0.014109 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.035583 | 116 | 116 | 1.6366 | 116 |  |  | 0.035583 | 4.1276
3097 | MARTLAKE_1G | 1 | North | YES | 0.012918 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.034392 | 0 | 790 | 10.2052 | 790 |  |  | 0.034392 | 27.1698
3098 | MARTLAKE_2G | 2 | North | YES | 0.012918 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.034392 | 0 | 795 | 10.2698 | 795 |  |  | 0.034392 | 27.3417
3099 | MARTLAKE_3G | 3 | North | YES | 0.012918 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.034392 | 0 | 804 | 10.3861 | 804 |  |  | 0.034392 | 27.6513
13116 | TGATEWAY_1G | 1 | North | YES | 0.012732 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.034206 | 151 | 151 | 1.9225 | 151 |  |  | 0.034206 | 5.1651
13117 | TGATEWAY_2G | 2 | North | YES | 0.012732 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.034206 | 130 | 130 | 1.6552 | 130 |  |  | 0.034206 | 4.4468
13118 | TGATEWAY_3G | 3 | North | YES | 0.012732 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.034206 | 148 | 148 | 1.8843 | 148 |  |  | 0.034206 | 5.0625
13119 | TGATEWAY_4G | 4 | North | YES | 0.012732 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.034206 | 399 | 399 | 5.0801 | 399 |  |  | 0.034206 | 13.6482
3126 | TRINIDAD_6G | 1 | North | YES | 0.012616 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.03409 | 224 | 224 | 2.826 | 224 |  |  | 0.03409 | 7.6362
3348 | CHAMPION_1G | MB | North | YES | 0.012543 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.034017 | 0 | 0 | 0 | 0 |  |  | 0.034017 | 0
3113 | LUFKINWB_1G | 1 | North | YES | 0.012527 | 0 | 0 | 50 |  | 1.01 | Trash | 1 | 0.034001 | 50 | 50 | 0.62635 | 50 |  |  | 0.034001 | 1.7001
3107 | STRYKER_1G | 1 | North | YES | 0.012431 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.033905 | 182 | 182 | 2.2624 | 182 |  |  | 0.033905 | 6.1707
3108 | STRYKER_2G | 2 | North | YES | 0.012431 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.033905 | 484 | 484 | 6.0166 | 484 |  |  | 0.033905 | 16.4101
244 | WHITNYDM01 | 1 | North | YES | 0.011589 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.033063 | 0 | 0 | 0 | 0 |  |  | 0.033063 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.011589 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.033063 | 0 | 0 | 0 | 0 |  |  | 0.033063 | 0
13134 | CALFREST_4G | 4 | North | YES | 0.010838 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.032312 | 151.5 | 151.5 | 1.642 | 151.5 |  |  | 0.032312 | 4.8953
13135 | CALFREST_5G | 5 | North | YES | 0.010838 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.032312 | 152.3 | 152.3 | 1.6506 | 152.3 |  |  | 0.032312 | 4.9211
13136 | CALFREST_6G | 6 | North | YES | 0.010838 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.032312 | 177.5 | 177.5 | 1.9237 | 177.5 |  |  | 0.032312 | 5.7354
13131 | CALFREST_1G | 1 | North | YES | 0.010773 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.032247 | 150.7 | 150.7 | 1.6235 | 150.7 |  |  | 0.032247 | 4.8596
13132 | CALFREST_2G | 2 | North | YES | 0.010773 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.032247 | 151 | 151 | 1.6267 | 151 |  |  | 0.032247 | 4.8693
13133 | CALFREST_3G | 3 | North | YES | 0.010773 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.032247 | 177.4 | 177.4 | 1.9111 | 177.4 |  |  | 0.032247 | 5.7206
3381 | BBRN_1G | 1 | North | YES | 0.010388 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.031862 | 0 | 618 | 6.4198 | 618 |  |  | 0.031862 | 19.6908
3382 | BBRN_2G | 2 | North | YES | 0.010388 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.031862 | 0 | 589 | 6.1185 | 589 |  |  | 0.031862 | 18.7668
251 | BOSQUESW803 | 2 | North | YES | 0.009728 | 150 | 0 | 150 |  | 1.032 | CC | 1 | 0.031202 | 150 | 150 | 1.4592 | 150 |  |  | 0.031202 | 4.6803
253 | BOSQUESW804 | 2 | North | YES | 0.009728 | 80 | 0 | 80 |  | 1.032 | CC | 1 | 0.031202 | 80 | 80 | 0.77824 | 80 |  |  | 0.031202 | 2.4962
238 | BOSQUESW505 | 1 | North | YES | 0.008562 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.030036 | 255 | 255 | 2.1833 | 255 |  |  | 0.030036 | 7.6592
239 | BOSQUESW502 | 1 | North | YES | 0.008562 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.030036 | 149 | 149 | 1.2757 | 149 |  |  | 0.030036 | 4.4754
247 | BOSQUESW501 | 2 | North | YES | 0.008562 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.030036 | 156 | 156 | 1.3357 | 156 |  |  | 0.030036 | 4.6856
3403 | THOUSE_1G | 1 | North | YES | 0.007395 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.028869 | 563 | 563 | 4.1634 | 563 |  |  | 0.028869 | 16.2533
3404 | THOUSE_2G | 2 | North | YES | 0.007395 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.028869 | 807 | 807 | 5.9678 | 807 |  |  | 0.028869 | 23.2974
48721 | LEG_1___1 | 1 | North | YES | 0.00684 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.028314 | 0 | 827 | 5.6567 | 827 |  |  | 0.028314 | 23.4158
48722 | LEG_2___2 | 2 | North | YES | 0.00684 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.028314 | 0 | 819 | 5.602 | 819 |  |  | 0.028314 | 23.1893
39960 | TNTNPONE_18 | 1 | North | YES | 0.005426 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.0269 | 0 | 152.3 | 0.82638 | 152.3 |  |  | 0.0269 | 4.0969
39970 | TNTNPONE_28 | 1 | North | YES | 0.005426 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.0269 | 0 | 153 | 0.83018 | 153 |  |  | 0.0269 | 4.1157
3416 | LAKE_CRK1_G | 1 | North | YES | 0.00504 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.026514 | 75 | 75 | 0.378 | 75 |  |  | 0.026514 | 1.9886
3417 | LAKE_CRK2_G | 2 | North | YES | 0.00504 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.026514 | 222 | 222 | 1.1189 | 222 |  |  | 0.026514 | 5.8861
990 | GIBN_CREK_G1 | 1 | North | YES | 0.001955 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.023429 | 0 | 463 | 0.90516 | 463 |  |  | 0.023429 | 10.8477
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.001433 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.022907 | 32 | 32 | 0.045856 | 32 |  |  | 0.022907 | 0.73303
32886 | BRYN_ATKINS3 | MB | North | YES | 0.001355 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.022829 | 0 | 0 | 0 | 0 |  |  | 0.022829 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.001355 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.022829 | 0 | 0 | 0 | 0 |  |  | 0.022829 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.001355 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.022829 | 17 | 17 | 0.023035 | 17 |  |  | 0.022829 | 0.3881
32890 | BRYN_ATKINS4 | MB | North | YES | 0.001355 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.022829 | 0 | 0 | 0 | 0 |  |  | 0.022829 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.001355 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.022829 | 0 | 0 | 0 | 0 |  |  | 0.022829 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.00119 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.022664 | 48 | 48 | 0.05712 | 48 |  |  | 0.022664 | 1.0879
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.00119 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.022664 | 46 | 46 | 0.05474 | 46 |  |  | 0.022664 | 1.0426
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.00119 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.022664 | 105 | 105 | 0.12495 | 105 |  |  | 0.022664 | 2.3797
48671 | FTR_GT1_5105 | 1 | North | YES | 0.000927 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.022401 | 154.2 | 154.2 | 0.14294 | 154.2 |  |  | 0.022401 | 3.4543
48672 | FTR_GT2_5110 | 2 | North | YES | 0.000927 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.022401 | 159 | 159 | 0.14739 | 159 |  |  | 0.022401 | 3.5618
48673 | FTR_GT3_5085 | 3 | North | YES | 0.000927 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.022401 | 158 | 158 | 0.14647 | 158 |  |  | 0.022401 | 3.5394
48674 | FTR_CN4_5095 | 4 | North | YES | 0.000927 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.022401 | 380 | 380 | 0.35226 | 380 |  |  | 0.022401 | 8.5124
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.01396 | 15 | 15 |  |  | 0 | 15 | -0.01396 | -0.2094
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8442 | NUECES_B0A | MB | South | YES | 0 | 0 | 81 | 367 |  | 1.03 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.01396 | 0 | 0 |  |  |  |  | -0.01396 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.002851 | 33 | 13 | 33 | 0 | 1.0375 | Hydro | -1 | 0.016811 | 0 | 0 |  |  | 0 | 0 | -0.016811 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.002851 | 25 | 13 | 25 | 0 | 1.0375 | Hydro | -1 | 0.016811 | 0 | 0 |  |  | 0 | 0 | -0.016811 | 0
88253 | HAMILTON | F | South | YES | -0.002851 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.016811 | 0 | 0 |  |  | 0 | 0 | -0.016811 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.004214 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.018174 | 0 | 0 |  |  |  |  | -0.018174 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.004214 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.018174 | 0 | 0 |  |  |  |  | -0.018174 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.004214 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.018174 | 0 | 0 |  |  |  |  | -0.018174 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.004214 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.018174 | 0 | 0 |  |  |  |  | -0.018174 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.004214 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.018174 | 0 | 0 |  |  |  |  | -0.018174 | 0
48885 | THW_5152 | B | Houston | YES | -0.004783 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.018743 | 59 | 59 |  |  |  |  | -0.018743 | -1.1058
48885 | THW_5152 | A | Houston | YES | -0.004783 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.018743 | 58 | 58 |  |  |  |  | -0.018743 | -1.0871
48886 | THW_5354 | D | Houston | YES | -0.004783 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.018743 | 58 | 58 |  |  |  |  | -0.018743 | -1.0871
48886 | THW_5354 | C | Houston | YES | -0.004783 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.018743 | 57 | 57 |  |  |  |  | -0.018743 | -1.0683
48887 | THW_5556 | E | Houston | YES | -0.004783 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.018743 | 59 | 59 |  |  |  |  | -0.018743 | -1.1058
48887 | THW_5556 | F | Houston | YES | -0.004783 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.018743 | 57 | 57 |  |  |  |  | -0.018743 | -1.0683
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.004825 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.018785 | 398 | 398 |  |  |  |  | -0.018785 | -7.4764
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.004855 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.018815 | 162.8 | 162.8 |  |  |  |  | -0.018815 | -3.0631
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.004855 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.018815 | 161.4 | 161.4 |  |  |  |  | -0.018815 | -3.0367
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.004855 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.018815 | 158.9 | 158.9 |  |  |  |  | -0.018815 | -2.9897
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.004855 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.018815 | 269.2 | 269.2 |  |  |  |  | -0.018815 | -5.065
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.004949 | 172 | 0 | 172 | 0 | 1.026 | GSC | -1 | 0.018909 | 172 | 172 |  |  |  |  | -0.018909 | -3.2523
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.004949 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.018909 | 172 | 172 |  |  |  |  | -0.018909 | -3.2523
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.004949 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.018909 | 172 | 172 |  |  |  |  | -0.018909 | -3.2523
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.004965 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.018925 | 0 | 0 |  |  |  |  | -0.018925 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.00499 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.01895 | 744 | 744 |  |  |  |  | -0.01895 | -14.0987
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.004995 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.004995 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.004995 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.004995 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.004995 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.004995 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.004995 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48651 | EP_1_2 | 2 | Houston | YES | -0.004997 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.018957 | 0 | 0 |  |  |  |  | -0.018957 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.004997 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.018957 | 0 | 0 |  |  |  |  | -0.018957 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.005066 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.019026 | 12 | 12 |  |  |  |  | -0.019026 | -0.22831
49803 | EXN_15GT | 1 | Houston | YES | -0.005085 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.005085 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.005085 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.005085 | 43 | 9.2 | 45.9 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.005085 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.005085 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.005085 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.005085 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.005085 | 18.5 | 9.2 | 18.5 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.005085 | 81 | 21.3 | 85.4 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.005085 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.005118 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.019078 | 746 | 746 |  |  |  |  | -0.019078 | -14.2321
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.005189 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.019149 | 107 | 107 |  |  |  |  | -0.019149 | -2.0489
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.005189 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.019149 | 108 | 108 |  |  |  |  | -0.019149 | -2.0681
48875 | THW_3132 | A | Houston | YES | -0.005189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.019149 | 55 | 55 |  |  |  |  | -0.019149 | -1.0532
48875 | THW_3132 | B | Houston | YES | -0.005189 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.019149 | 53 | 53 |  |  |  |  | -0.019149 | -1.0149
48877 | THW_3334 | D | Houston | YES | -0.005189 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.019149 | 57 | 57 |  |  |  |  | -0.019149 | -1.0915
48877 | THW_3334 | C | Houston | YES | -0.005189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.019149 | 55 | 55 |  |  |  |  | -0.019149 | -1.0532
48879 | THW_4142 | E | Houston | YES | -0.005189 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.019149 | 56 | 56 |  |  |  |  | -0.019149 | -1.0723
48879 | THW_4142 | F | Houston | YES | -0.005189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.019149 | 55 | 55 |  |  |  |  | -0.019149 | -1.0532
48881 | THW_4344 | G | Houston | YES | -0.005189 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.019149 | 58 | 58 |  |  |  |  | -0.019149 | -1.1106
48881 | THW_4344 | H | Houston | YES | -0.005189 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.019149 | 58 | 58 |  |  |  |  | -0.019149 | -1.1106
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.005295 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.019255 | 0 | 0 |  |  |  |  | -0.019255 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.005295 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.019255 | 0 | 0 |  |  |  |  | -0.019255 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.00531 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.01927 | 42 | 42 |  |  |  |  | -0.01927 | -0.80934
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.00531 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.01927 | 42 | 42 |  |  |  |  | -0.01927 | -0.80934
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.00531 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.01927 | 39 | 39 |  |  |  |  | -0.01927 | -0.75153
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.00531 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.01927 | 39 | 39 |  |  |  |  | -0.01927 | -0.75153
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.005321 | 137.6 | 54.6 | 137.6 |  | 1.0362 | Cogen | -1 | 0.019281 | 0 | 0 |  |  |  |  | -0.019281 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.005394 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.019354 | 0 | 0 |  |  |  |  | -0.019354 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.005394 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.019354 | 0 | 0 |  |  |  |  | -0.019354 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.005394 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.019354 | 0 | 0 |  |  |  |  | -0.019354 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.005394 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.019354 | 0 | 0 |  |  |  |  | -0.019354 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.005443 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.019403 | 0 | 0 |  |  |  |  | -0.019403 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.005443 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.019403 | 0 | 0 |  |  |  |  | -0.019403 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.005443 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.019403 | 0 | 0 |  |  |  |  | -0.019403 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.005444 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.019404 | 228 | 228 |  |  |  |  | -0.019404 | -4.4241
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.005445 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.019405 | 0 | 0 |  |  |  |  | -0.019405 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.005445 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.019405 | 0 | 0 |  |  |  |  | -0.019405 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.005445 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.019405 | 0 | 0 |  |  |  |  | -0.019405 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.005445 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.019405 | 0 | 0 |  |  |  |  | -0.019405 | 0
48845 | SOL_GT1 | 1 | Houston | YES | -0.005445 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.019405 | 16.2 | 16.2 |  |  |  |  | -0.019405 | -0.31436
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.005446 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.019406 | 213 | 213 |  |  |  |  | -0.019406 | -4.1335
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.005454 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.019414 | 0 | 0 |  |  |  |  | -0.019414 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.005454 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.019414 | 0 | 0 |  |  |  |  | -0.019414 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.005455 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.019415 | 165 | 165 |  |  |  |  | -0.019415 | -3.2035
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.005458 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.019418 | 176 | 176 |  |  |  |  | -0.019418 | -3.4176
48855 | SRB_GT211035 | B2 | Houston | YES | -0.00546 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.01942 | 12 | 12 |  |  |  |  | -0.01942 | -0.23304
48855 | SRB_GT211035 | B1 | Houston | YES | -0.00546 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.01942 | 18 | 18 |  |  |  |  | -0.01942 | -0.34956
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.005495 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.019455 | 0 | 0 |  |  |  |  | -0.019455 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.00553 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.01949 | 163.2 | 163.2 |  |  |  |  | -0.01949 | -3.1808
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.00553 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.01949 | 157.1 | 157.1 |  |  |  |  | -0.01949 | -3.0619
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.00553 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.01949 | 157.5 | 157.5 |  |  |  |  | -0.01949 | -3.0697
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.00553 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.01949 | 157 | 157 |  |  |  |  | -0.01949 | -3.0599
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.00553 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.01949 | 282 | 282 |  |  |  |  | -0.01949 | -5.4962
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.005567 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.019527 | 0 | 0 |  |  |  |  | -0.019527 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.005567 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.019527 | 0 | 0 |  |  |  |  | -0.019527 | 0
48691 | GBY_73741085 | A | Houston | YES | -0.00561 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.01957 | 47 | 47 |  |  |  |  | -0.01957 | -0.91979
48691 | GBY_73741085 | B | Houston | YES | -0.00561 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.01957 | 47 | 47 |  |  |  |  | -0.01957 | -0.91979
48692 | GBY_81821075 | D | Houston | YES | -0.00561 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.01957 | 55 | 55 |  |  |  |  | -0.01957 | -1.0763
48692 | GBY_81821075 | C | Houston | YES | -0.00561 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.01957 | 47 | 47 |  |  |  |  | -0.01957 | -0.91979
48693 | GBY_83841065 | F | Houston | YES | -0.00561 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.01957 | 54 | 54 |  |  |  |  | -0.01957 | -1.0568
48693 | GBY_83841065 | E | Houston | YES | -0.00561 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.01957 | 57 | 57 |  |  |  |  | -0.01957 | -1.1155
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.005711 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.019671 | 0 | 0 |  |  |  |  | -0.019671 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.005711 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.019671 | 0 | 0 |  |  |  |  | -0.019671 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.005711 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.019671 | 0 | 0 |  |  |  |  | -0.019671 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.005711 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.019671 | 0 | 0 |  |  |  |  | -0.019671 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.005788 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.019748 | 0 | 0 |  |  |  |  | -0.019748 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.005788 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.019748 | 0 | 0 |  |  |  |  | -0.019748 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.005788 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.019748 | 0 | 0 |  |  |  |  | -0.019748 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.005788 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.019748 | 0 | 0 |  |  |  |  | -0.019748 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.005788 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.019748 | 0 | 0 |  |  |  |  | -0.019748 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.005989 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.019949 | 0 | 0 |  |  |  |  | -0.019949 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.006276 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.006276 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.006276 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.006276 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.006276 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.006276 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.006276 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.006276 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.006276 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.006276 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.006276 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.006276 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.006276 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.006276 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.006276 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.006941 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.020901 | 166 | 166 |  |  |  |  | -0.020901 | -3.4696
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.006941 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.020901 | 166 | 166 |  |  |  |  | -0.020901 | -3.4696
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.006941 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.020901 | 248 | 248 |  |  |  |  | -0.020901 | -5.1834
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.006941 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.020901 | 546 | 546 |  |  |  |  | -0.020901 | -11.4119
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.006941 | 598 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.020901 | 0 | 654 |  |  |  |  | -0.020901 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.006941 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.020901 | 13 | 13 |  |  |  |  | -0.020901 | -0.27171
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.006976 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.020936 | 0 | 0 |  |  |  |  | -0.020936 | 0
8262 | ELPS | 1 | South | YES | -0.006986 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.020946 | 0 | 0 |  |  | 0 | 0 | -0.020946 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.007109 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.021069 | 167.7 | 167.7 |  |  |  |  | -0.021069 | -3.5333
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.007109 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.021069 | 166.4 | 166.4 |  |  |  |  | -0.021069 | -3.5059
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.007109 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.021069 | 252.4 | 252.4 |  |  |  |  | -0.021069 | -5.3178
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.007118 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.021078 | 0 | 651 |  |  |  |  | -0.021078 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.007118 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.021078 | 0 | 564 |  |  |  |  | -0.021078 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.007118 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.021078 | 0 | 603 |  |  |  |  | -0.021078 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.007135 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.021095 | 0 | 0 |  |  |  |  | -0.021095 | 0
80010 | EPLVT1 | F | South | YES | -0.007948 | 0 | 0 | 0 |  | 1.0376 | AVR | -1 | 0.021908 | 0 | 0 |  |  | 0 | 0 | -0.021908 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.008183 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.022143 | 0 | 0 |  |  |  |  | -0.022143 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.008183 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.022143 | 0 | 0 |  |  |  |  | -0.022143 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.008183 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.022143 | 0 | 0 |  |  |  |  | -0.022143 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.008183 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.022143 | 0 | 0 |  |  |  |  | -0.022143 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.008483 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.022443 | 0 | 0 |  |  |  |  | -0.022443 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.008483 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.022443 | 0 | 0 |  |  |  |  | -0.022443 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.008856 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.008856 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.008856 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.008856 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.008856 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.008856 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.008856 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.008856 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.008856 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.008856 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.008856 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.008856 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.008856 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.008856 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.008856 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.008856 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.008856 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.008856 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.008856 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.008856 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.010314 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.024274 | 0 | 0 |  |  |  |  | -0.024274 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.010748 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.024708 | 76 | 76 |  |  |  |  | -0.024708 | -1.8778
48732 | CBE_GT2 | 1 | Houston | YES | -0.010748 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.024708 | 76 | 76 |  |  |  |  | -0.024708 | -1.8778
48733 | CBE_ST12 | 1 | Houston | YES | -0.010748 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.024708 | 105 | 105 |  |  |  |  | -0.024708 | -2.5943
48734 | CBE_GT3 | 1 | Houston | YES | -0.010748 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.024708 | 76 | 76 |  |  |  |  | -0.024708 | -1.8778
48735 | CBE_GT4 | 1 | Houston | YES | -0.010748 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.024708 | 76 | 76 |  |  |  |  | -0.024708 | -1.8778
48736 | CBE_ST34 | 1 | Houston | YES | -0.010748 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.024708 | 105 | 105 |  |  |  |  | -0.024708 | -2.5943
5911 | STP_GN1___1 | 1 | Houston | YES | -0.01088 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.02484 | 0 | 0 |  |  |  |  | -0.02484 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.01088 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.02484 | 0 | 0 |  |  |  |  | -0.02484 | 0
8134 | FOR #1 | 1 | South | YES | -0.015045 | 54.1 | 45 | 79 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
8138 | FOR #2 | 2 | South | YES | -0.015045 | 63.1 | 45 | 81 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
8153 | FOR #3 | 3 | South | YES | -0.015045 | 63.1 | 45 | 79.9 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
8154 | FOR #4 | 4 | South | YES | -0.015045 | 63.1 | 60 | 80 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
8155 | FOR #5 | 5 | South | YES | -0.015045 | 63.1 | 60 | 78.4 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
8156 | FOR #6 | 6 | South | YES | -0.015045 | 24.9 | 5 | 25 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
8157 | FOR #7 | 7 | South | YES | -0.015045 | 28.8 | 5 | 46 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
80051 | FOR #8 | 8 | South | YES | -0.015045 | 28 | 28 | 28 | 0 | 1.016 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
80052 | FOR #9 | 9 | South | YES | -0.015045 | 29.7 | 5 | 43.6 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
80053 | FOR #10 | 10 | South | YES | -0.015045 | 68.4 | 45 | 75 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
80012 | LAR | F | South | YES | -0.01513 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.02909 | 0 | 0 |  |  | 0 | 0 | -0.02909 | 0
80265 | LARECU40A | 4 | South | YES | -0.01513 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.02909 | 100 | 100 |  |  | -1.513 | 100 | -0.02909 | -2.909
80266 | LARECU50A | 5 | South | YES | -0.01513 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.02909 | 100 | 100 |  |  | -1.513 | 100 | -0.02909 | -2.909
80226 | ALCOA G | 1 | South | YES | -0.015162 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.029122 | 0 | 0 |  |  | 0 | 0 | -0.029122 | 0
88299 | ZAPATA | F | South | YES | -0.015535 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.029495 | 0 | 0 |  |  | 0 | 0 | -0.029495 | 0
8147 | UCAR #2 | 10 | South | YES | -0.015548 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
8148 | UCAR #1 | 2 | South | YES | -0.015548 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
80137 | CSDR89 | 9 | South | YES | -0.015548 | 0 | 0 | 15 |  | 1.003 | DCTie | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
80137 | CSDR89 | 8 | South | YES | -0.015548 | 33.9 | 0 | 39 |  | 1.003 | DCTie | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
80138 | CSDR7 | 7 | South | YES | -0.015548 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
80139 | CSDR56 | 6 | South | YES | -0.015548 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
80139 | CSDR56 | 5 | South | YES | -0.015548 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
80140 | CSDR11 | 11 | South | YES | -0.015548 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
80227 | AIRCO G | 1 | South | YES | -0.015595 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.029555 | 0 | 0 |  |  | 0 | 0 | -0.029555 | 0
80224 | VISTRONG1 | 1 | South | YES | -0.015701 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.029661 | 0 | 0 |  |  | 0 | 0 | -0.029661 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.015701 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.029661 | 0 | 0 |  |  | 0 | 0 | -0.029661 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.01581 | 17.6 | 6 | 22 | 0 | 1.0223 | GST | -1 | 0.02977 | 22 | 22 |  |  | -0.34782 | 22 | -0.02977 | -0.65494
5505 | RAYBURNGEN1 | 1 | South | YES | -0.01581 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.02977 | 11 | 11 |  |  | -0.17391 | 11 | -0.02977 | -0.32747
5506 | RAYBURNGEN2 | 1 | South | YES | -0.01581 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.02977 | 11 | 11 |  |  | -0.17391 | 11 | -0.02977 | -0.32747
5728 | FALCONHYDRO2 | 2 | South | YES | -0.015814 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.029774 | 0 | 0 |  |  | 0 | 0 | -0.029774 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.015814 | 11 | 0 | 11 | 0 | 1.0227 | Hydro | -1 | 0.029774 | 0 | 0 |  |  | 0 | 0 | -0.029774 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.015814 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.029774 | 0 | 0 |  |  | 0 | 0 | -0.029774 | 0
5508 | RAYBURNCC9 | 1 | South | YES | -0.015963 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.029923 | 47.7 | 47.7 |  |  | -0.76144 | 47.7 | -0.029923 | -1.4273
5509 | RAYBURNCC10 | 1 | South | YES | -0.015963 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.029923 | 37.3 | 37.3 |  |  | -0.59542 | 37.3 | -0.029923 | -1.1161
5511 | RAYBURNCC7 | 1 | South | YES | -0.015963 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.029923 | 47.5 | 47.5 |  |  | -0.75824 | 47.5 | -0.029923 | -1.4213
5512 | RAYBURNCC8 | 1 | South | YES | -0.015963 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.029923 | 49.3 | 49.3 |  |  | -0.78698 | 49.3 | -0.029923 | -1.4752
88508 | FALFURRI | F | South | YES | -0.015971 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.029931 | 0 | 0 |  |  | 0 | 0 | -0.029931 | 0
8066 | DUP1V#1 | 1 | South | YES | -0.015984 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.029944 | 0 | 0 |  |  | 0 | 0 | -0.029944 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.015991 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.015991 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.015991 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
8930 | ICPGN10A | 1 | South | YES | -0.015991 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
8931 | ICPGN20A | 2 | South | YES | -0.015991 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
8932 | ICPGN30A | 3 | South | YES | -0.015991 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
80223 | REYSHR G | 1 | South | YES | -0.015991 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
8933 | FGNTS001 | 1 | South | YES | -0.016106 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.030066 | 146.5 | 146.5 |  |  | -2.3595 | 146.5 | -0.030066 | -4.4047
8934 | FGNTS101 | 2 | South | YES | -0.016106 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.030066 | 147.9 | 147.9 |  |  | -2.3821 | 147.9 | -0.030066 | -4.4468
8935 | FGNTS201 | 3 | South | YES | -0.016106 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.030066 | 173 | 173 |  |  | -2.7863 | 173 | -0.030066 | -5.2014
8560 | CNOPGT1 | 1 | South | YES | -0.016123 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.030083 | 0 | 0 |  |  | 0 | 0 | -0.030083 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.016123 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.030083 | 0 | 0 |  |  | 0 | 0 | -0.030083 | 0
8562 | CNOPST1 | 3 | South | YES | -0.016123 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.030083 | 0 | 0 |  |  | 0 | 0 | -0.030083 | 0
8456 | COSW#1 | 1 | South | YES | -0.01613 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.03009 | 0 | 0 |  |  | 0 | 0 | -0.03009 | 0
8457 | COSW#2 | 2 | South | YES | -0.01613 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.03009 | 0 | 0 |  |  | 0 | 0 | -0.03009 | 0
8173 | VICEC51A | 5 | South | YES | -0.016145 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.030105 | 144 | 144 |  |  | -2.3249 | 144 | -0.030105 | -4.3351
8174 | VICEC61A | 6 | South | YES | -0.016145 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.030105 | 188 | 188 |  |  | -3.0353 | 188 | -0.030105 | -5.6597
8459 | B_DAVIS0B | MB | South | YES | -0.016147 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.030107 | 0 | 0 |  |  | 0 | 0 | -0.030107 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.016147 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.030107 | 0 | 0 |  |  | 0 | 0 | -0.030107 | 0
8506 | VAL #1 | 1 | South | YES | -0.016154 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.030114 | 0 | 0 |  |  | 0 | 0 | -0.030114 | 0
8507 | VAL #2 | 2 | South | YES | -0.016154 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.030114 | 0 | 0 |  |  | 0 | 0 | -0.030114 | 0
8936 | MVGN#1 | 1 | South | YES | -0.016154 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.030114 | 216.6 | 216.6 |  |  | -3.499 | 216.6 | -0.030114 | -6.5227
8937 | MVGN#2 | 2 | South | YES | -0.016154 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.030114 | 216.7 | 216.7 |  |  | -3.5006 | 216.7 | -0.030114 | -6.5257
8938 | MVGN#3 | 3 | South | YES | -0.016154 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.030114 | 250.9 | 250.9 |  |  | -4.053 | 250.9 | -0.030114 | -7.5556
8981 | HECN1 | 1 | South | YES | -0.016154 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.030114 | 144.8 | 144.8 |  |  | -2.3391 | 144.8 | -0.030114 | -4.3605
8982 | HECN2 | 2 | South | YES | -0.016154 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.030114 | 144.1 | 144.1 |  |  | -2.3278 | 144.1 | -0.030114 | -4.3394
8983 | HECN3 | 3 | South | YES | -0.016154 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.030114 | 171.9 | 171.9 |  |  | -2.7769 | 171.9 | -0.030114 | -5.1766
8461 | KOCH_UP0A | 1 | South | YES | -0.016167 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.030127 | 0 | 0 |  |  | 0 | 0 | -0.030127 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.016169 | 30.3 | 0 | 38 |  | 1.027 | Cogen | -1 | 0.030129 | 0 | 0 |  |  | 0 | 0 | -0.030129 | 0
80003 | MILHWYS | F | South | YES | -0.016189 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.030149 | 0 | 0 |  |  | 0 | 0 | -0.030149 | 0
5932 | SI_RAY9 | 9 | South | YES | -0.01619 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.03015 | 38 | 38 |  |  | -0.61522 | 38 | -0.03015 | -1.1457
5933 | SI_RAY6 | 6 | South | YES | -0.01619 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.03015 | 19.3 | 19.3 |  |  | -0.31247 | 19.3 | -0.03015 | -0.58189
5935 | SI_RAY10 | 10 | South | YES | -0.01619 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.03015 | 47 | 47 |  |  | -0.76093 | 47 | -0.03015 | -1.417
8517 | CELANEBI0A | 1 | South | YES | -0.016208 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.030168 | 0 | 0 |  |  | 0 | 0 | -0.030168 | 0
80080 | GWINDT11A | 2 | South | YES | -0.016209 | 17.7 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 41 |  |  | 0 | 0 | -0.030169 | 0
80080 | GWINDT11A | 3 | South | YES | -0.016209 | 16.4 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 38 |  |  | 0 | 0 | -0.030169 | 0
80080 | GWINDT11A | 1 | South | YES | -0.016209 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 94 |  |  | 0 | 0 | -0.030169 | 0
80080 | GWINDT11A | 4 | South | YES | -0.016209 | 8.2 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 19 |  |  | 0 | 0 | -0.030169 | 0
80081 | GWINDT21A | 2 | South | YES | -0.016209 | 15.5 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 36 |  |  | 0 | 0 | -0.030169 | 0
80081 | GWINDT21A | 4 | South | YES | -0.016209 | 9.5 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 22 |  |  | 0 | 0 | -0.030169 | 0
80081 | GWINDT21A | 3 | South | YES | -0.016209 | 18.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 43 |  |  | 0 | 0 | -0.030169 | 0
80081 | GWINDT21A | 1 | South | YES | -0.016209 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 94 |  |  | 0 | 0 | -0.030169 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.016209 | 63 | 0 | 146 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 146 |  |  | 0 | 0 | -0.030169 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.016209 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 50 |  |  | 0 | 0 | -0.030169 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.016209 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 50 |  |  | 0 | 0 | -0.030169 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.016209 | 23.7 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 55 |  |  | 0 | 0 | -0.030169 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.016675 | 19.2 | 6 | 24 | 0 | 1.0161 | GST | -1 | 0.030635 | 24 | 24 |  |  | -0.4002 | 24 | -0.030635 | -0.73524
5891 | PEARSALLGEN2 | 1 | South | YES | -0.016675 | 19.4 | 6 | 24.3 | 0 | 1.0161 | GST | -1 | 0.030635 | 24.3 | 24.3 |  |  | -0.4052 | 24.3 | -0.030635 | -0.74443
5892 | PEARSALLGEN3 | 1 | South | YES | -0.016675 | 19.1 | 6 | 23.9 | 0 | 1.0161 | GST | -1 | 0.030635 | 23.9 | 23.9 |  |  | -0.39853 | 23.9 | -0.030635 | -0.73217
8161 | COLETO0A | 1 | South | YES | -0.016872 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.030832 | 0 | 633 |  |  | 0 | 0 | -0.030832 | 0
88198 | BEEVILLE | F | South | YES | -0.017006 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.030966 | 0 | 0 |  |  | 0 | 0 | -0.030966 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.018295 | 396.3 | 180 | 396.3 | 0 | 1.0331 | LIGCO | -1 | 0.032255 | 0 | 396.3 |  |  | 0 | 0 | -0.032255 | 0
8189 | CUECPL2A | 1 | South | YES | -0.019154 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.033114 | 0 | 0 |  |  | 0 | 0 | -0.033114 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.019265 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.033225 | 0 | 436 |  |  | 0 | 0 | -0.033225 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.019274 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.033234 | 0 | 606 |  |  | 0 | 0 | -0.033234 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.019274 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.033234 | 0 | 598 |  |  | 0 | 0 | -0.033234 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | -0.019547 | 562 | 100 | 562 | 0 | 1.018 | LIGCO | -1 | 0.033507 | 0 | 562 |  |  | 0 | 0 | -0.033507 | 0
3432 | SANDOW_4G | 4 | South | YES | -0.019561 | 580 | 225 | 580 | 0 | 1.029 | LIGCO | -1 | 0.033521 | 0 | 580 |  |  | 0 | 0 | -0.033521 | 0
13432 | SANDOW_5G | 5 | South | YES | -0.019561 | 581 | 225 | 581 | 0 | 1.029 | LIGCO | -1 | 0.033521 | 0 | 581 |  |  | 0 | 0 | -0.033521 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.019628 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.033588 | 58 | 58 |  |  | -1.1384 | 58 | -0.033588 | -1.9481
5265 | LEON_LCP4G4 | 4 | South | YES | -0.019628 | 71.2 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.033588 | 89 | 89 |  |  | -1.7469 | 89 | -0.033588 | -2.9893
5266 | LEON_LCPCT1 | 1 | South | YES | -0.019628 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.033588 | 44 | 44 |  |  | -0.86363 | 44 | -0.033588 | -1.4779
5267 | LEON_LCPCT2 | 2 | South | YES | -0.019628 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.033588 | 44 | 44 |  |  | -0.86363 | 44 | -0.033588 | -1.4779
5268 | LEON_LCPCT3 | 3 | South | YES | -0.019628 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.033588 | 43 | 43 |  |  | -0.844 | 43 | -0.033588 | -1.4443
5269 | LEON_LCPCT4 | 4 | South | YES | -0.019628 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.033588 | 45 | 45 |  |  | -0.88326 | 45 | -0.033588 | -1.5115
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.019723 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.033683 | 215 | 215 |  |  | -4.2404 | 215 | -0.033683 | -7.2418
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.019723 | 172.8 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.033683 | 216 | 216 |  |  | -4.2602 | 216 | -0.033683 | -7.2755
5031 | BRA_VHBCT1 | 1 | South | YES | -0.019723 | 44 | 24 | 44 | 0 | 1.0192 | GST | -1 | 0.033683 | 44 | 44 |  |  | -0.86781 | 44 | -0.033683 | -1.482
5032 | BRA_VHBCT2 | 2 | South | YES | -0.019723 | 44 | 24 | 44 | 0 | 1.0192 | GST | -1 | 0.033683 | 44 | 44 |  |  | -0.86781 | 44 | -0.033683 | -1.482
5033 | BRA_VHBCT3 | 3 | South | YES | -0.019723 | 43 | 24 | 43 | 0 | 1.0192 | GST | -1 | 0.033683 | 43 | 43 |  |  | -0.84809 | 43 | -0.033683 | -1.4484
5034 | BRA_VHBCT4 | 4 | South | YES | -0.019723 | 45 | 24 | 45 | 0 | 1.0192 | GST | -1 | 0.033683 | 45 | 45 |  |  | -0.88753 | 45 | -0.033683 | -1.5157
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.019753 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.033713 | 407 | 407 |  |  | -8.0395 | 407 | -0.033713 | -13.7212
5396 | CALAVER_OWS1 | 1 | South | YES | -0.019758 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.033718 | 418 | 418 |  |  | -8.2588 | 418 | -0.033718 | -14.0941
5397 | CALAVER_OWS2 | 2 | South | YES | -0.019758 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.033718 | 400 | 400 |  |  | -7.9032 | 400 | -0.033718 | -13.4872
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.019762 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.033722 | 155 | 155 |  |  | -3.0631 | 155 | -0.033722 | -5.2269
5477 | BRA_AVR1_ST1 | 1 | South | YES | -0.019762 | 174 | 138 | 174 | 0 | 1.017 | CC | -1 | 0.033722 | 174 | 174 |  |  | -3.4386 | 174 | -0.033722 | -5.8676
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.019762 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.033722 | 155 | 155 |  |  | -3.0631 | 155 | -0.033722 | -5.2269
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.019769 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.033729 | 147 | 147 |  |  | -2.906 | 147 | -0.033729 | -4.9582
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.019769 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.033729 | 138 | 138 |  |  | -2.7281 | 138 | -0.033729 | -4.6546
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.019769 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.033729 | 146 | 146 |  |  | -2.8863 | 146 | -0.033729 | -4.9244
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.019769 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.033729 | 149 | 149 |  |  | -2.9456 | 149 | -0.033729 | -5.0256
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.019769 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.033729 | 182 | 182 |  |  | -3.598 | 182 | -0.033729 | -6.1387
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.019769 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.033729 | 203 | 203 |  |  | -4.0131 | 203 | -0.033729 | -6.847
5111 | CALAVER_JTD1 | 1 | South | YES | -0.01979 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.03375 | 0 | 430 |  |  | 0 | 0 | -0.03375 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.01979 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.03375 | 0 | 430 |  |  | 0 | 0 | -0.03375 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.019807 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.033767 | 61 | 61 |  |  | -1.2082 | 61 | -0.033767 | -2.0598
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.019807 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.033767 | 95 | 95 |  |  | -1.8817 | 95 | -0.033767 | -3.2079
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.019807 | 120.8 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.033767 | 151 | 151 |  |  | -2.9909 | 151 | -0.033767 | -5.0988
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.020241 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.034201 | 148 | 148 |  |  | -2.9957 | 148 | -0.034201 | -5.0617
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.020241 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.034201 | 148 | 148 |  |  | -2.9957 | 148 | -0.034201 | -5.0617
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.020241 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.034201 | 154 | 154 |  |  | -3.1171 | 154 | -0.034201 | -5.2669
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.020241 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.034201 | 293 | 293 |  |  | -5.9306 | 293 | -0.034201 | -10.0209
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.020479 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.034439 | 50 | 50 |  |  | -1.0239 | 50 | -0.034439 | -1.7219
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.020479 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.034439 | 50 | 50 |  |  | -1.0239 | 50 | -0.034439 | -1.7219
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.020479 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.034439 | 50 | 50 |  |  | -1.0239 | 50 | -0.034439 | -1.7219
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.020479 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.034439 | 50 | 50 |  |  | -1.0239 | 50 | -0.034439 | -1.7219
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.020483 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.034443 | 0 | 0 |  |  | 0 | 0 | -0.034443 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.020483 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.034443 | 0 | 0 |  |  | 0 | 0 | -0.034443 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.020543 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.034503 | 158 | 158 |  |  | -3.2458 | 158 | -0.034503 | -5.4515
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.020543 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.034503 | 160 | 160 |  |  | -3.2869 | 160 | -0.034503 | -5.5205
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.020543 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.034503 | 175 | 175 |  |  | -3.595 | 175 | -0.034503 | -6.038
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.020595 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.034555 | 0 | 0 |  |  | 0 | 0 | -0.034555 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.020726 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.034686 | 223.9 | 223.9 |  |  | -4.6406 | 223.9 | -0.034686 | -7.7662
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.020726 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.034686 | 225 | 225 |  |  | -4.6634 | 225 | -0.034686 | -7.8043
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.020726 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.034686 | 224.6 | 224.6 |  |  | -4.6551 | 224.6 | -0.034686 | -7.7905
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.020726 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.034686 | 226.7 | 226.7 |  |  | -4.6986 | 226.7 | -0.034686 | -7.8633
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.02086 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.03482 | 0 | 0 |  |  | 0 | 0 | -0.03482 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.02086 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.03482 | 0 | 0 |  |  | 0 | 0 | -0.03482 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.02086 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.03482 | 0 | 0 |  |  | 0 | 0 | -0.03482 | 0
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.021402 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.035362 | 152.5 | 152.5 |  |  | -3.2638 | 152.5 | -0.035362 | -5.3927
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.021402 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.035362 | 149.5 | 149.5 |  |  | -3.1996 | 149.5 | -0.035362 | -5.2866
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.021402 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.035362 | 232.6 | 232.6 |  |  | -4.9781 | 232.6 | -0.035362 | -8.2252
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.022856 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.036816 | 132 | 132 |  |  | -3.017 | 132 | -0.036816 | -4.8597
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.022856 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.036816 | 139 | 139 |  |  | -3.177 | 139 | -0.036816 | -5.1174
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.022856 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.036816 | 329 | 329 |  |  | -7.5196 | 329 | -0.036816 | -12.1124
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.023403 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.037363 | 0 | 0 |  |  | 0 | 0 | -0.037363 | 0
9002 | DECKR_G3 | 3 | South | YES | -0.025346 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.039306 | 42 | 42 |  |  | -1.0645 | 42 | -0.039306 | -1.6508
9003 | DECKR_G4 | 4 | South | YES | -0.025346 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.039306 | 44 | 44 |  |  | -1.1152 | 44 | -0.039306 | -1.7295
9004 | DECKR_G5 | 5 | South | YES | -0.025346 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.039306 | 44 | 44 |  |  | -1.1152 | 44 | -0.039306 | -1.7295
9005 | DECKR_G6 | 6 | South | YES | -0.025346 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.039306 | 47 | 47 |  |  | -1.1913 | 47 | -0.039306 | -1.8474
9016 | SANDH_G1 | 1 | South | YES | -0.025395 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.039355 | 49 | 49 |  |  | -1.2444 | 49 | -0.039355 | -1.9284
9017 | SANDH_G2 | 2 | South | YES | -0.025395 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.039355 | 46 | 46 |  |  | -1.1682 | 46 | -0.039355 | -1.8103
9018 | SANDH_G3 | 3 | South | YES | -0.025395 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.039355 | 46 | 46 |  |  | -1.1682 | 46 | -0.039355 | -1.8103
9019 | SANDH_G4 | 4 | South | YES | -0.025395 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.039355 | 47 | 47 |  |  | -1.1936 | 47 | -0.039355 | -1.8497
9020 | SANDHG5A | 5A | South | YES | -0.025395 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.039355 | 155 | 155 |  |  | -3.9362 | 155 | -0.039355 | -6.1
9021 | SANDHG5C | 5C | South | YES | -0.025395 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.039355 | 148 | 148 |  |  | -3.7585 | 148 | -0.039355 | -5.8245
9000 | DECKR_G1 | 1 | South | YES | -0.025655 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.039615 | 321 | 321 |  |  | -8.2353 | 321 | -0.039615 | -12.7164
9001 | DECKR_G2 | 2 | South | YES | -0.025655 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.039615 | 426 | 426 |  |  | -10.929 | 426 | -0.039615 | -16.876
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.026428 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.040388 | 0 | 0 |  |  | 0 | 0 | -0.040388 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.026428 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.040388 | 0 | 0 |  |  | 0 | 0 | -0.040388 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.03567 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.04963 | 0 | 0 |  |  | 0 | 0 | -0.04963 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.03567 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.04963 | 0 | 0 |  |  | 0 | 0 | -0.04963 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.03567 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.04963 | 0 | 0 |  |  | 0 | 0 | -0.04963 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.053005 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.066965 | 0 | 0 |  |  | 0 | 0 | -0.066965 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.053005 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.066965 | 0 | 0 |  |  | 0 | 0 | -0.066965 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.060649 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.074609 | 423.3 | 423.3 |  |  | -25.6727 | 423.3 | -0.074609 | -31.582
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.061582 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.075542 | 0 | 0 |  |  | 0 | 0 | -0.075542 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.061582 | 23 | 0 | 29.8 |  | 1 | Hydro | -1 | 0.075542 | 0 | 0 |  |  | 0 | 0 | -0.075542 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.076867 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.090827 | 0 | 0 |  |  | 0 | 0 | -0.090827 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.08521 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.09917 | 0 | 0 |  |  | 0 | 0 | -0.09917 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.08521 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.09917 | 0 | 0 |  |  | 0 | 0 | -0.09917 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.08521 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.09917 | 0 | 0 |  |  | 0 | 0 | -0.09917 | 0
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Concentrated Capacity | Cumulative Concentrated Impact | Cont_ TempleSS to TemplePEC and TempleSS to LakeCreek OL_ Evant to Goldthwaite
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.08521 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.09917 | 0 | 0 |  |  | 0 | 0 | -0.09917 | 0 | 0 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.08521 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.09917 | 0 | 0 |  |  | 0 | 0 | -0.09917 | 0 | 0 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.08521 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.09917 | 0 | 0 |  |  | 0 | 0 | -0.09917 | 0 | 0 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.076867 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.090827 | 0 | 0 |  |  | 0 | 0 | -0.090827 | 0 | 0 | 0 | Weighted Shift Factors
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.061582 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.075542 | 0 | 0 |  |  | 0 | 0 | -0.075542 | 0 | 0 | 0 | North | 0.01396
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.061582 | 23 | 0 | 29.8 |  | 1 | Hydro | -1 | 0.075542 | 0 | 0 |  |  | 0 | 0 | -0.075542 | 0 | 0 | 0 | South | -0.021474
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.060649 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.074609 | 423.3 | 423.3 |  |  | -25.6727 | 423.3 | -0.074609 | -31.582 | 423.3 | 31.582 |  | 0.035434
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.053005 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.066965 | 0 | 0 |  |  | 0 | 0 | -0.066965 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.053005 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.066965 | 0 | 0 |  |  | 0 | 0 | -0.066965 | 0 |  |  | Line Cap | 128
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.03567 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.04963 | 0 | 0 |  |  | 0 | 0 | -0.04963 | 0 |  |  | Conc Gen | 423.3
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.03567 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.04963 | 0 | 0 |  |  | 0 | 0 | -0.04963 | 0 |  |  | Weighted Imp. | 31.582
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.03567 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.04963 | 0 | 0 |  |  | 0 | 0 | -0.04963 | 0 |  |  | PTDF | 0.074609
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.026428 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.040388 | 0 | 0 |  |  | 0 | 0 | -0.040388 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.026428 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.040388 | 0 | 0 |  |  | 0 | 0 | -0.040388 | 0 |  |  | Concentration | 2.1056
9000 | DECKR_G1 | 1 | South | YES | -0.025655 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.039615 | 321 | 321 |  |  | -8.2353 | 321 | -0.039615 | -12.7164
9001 | DECKR_G2 | 2 | South | YES | -0.025655 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.039615 | 426 | 426 |  |  | -10.929 | 426 | -0.039615 | -16.876 |  |  |  | Fail
9016 | SANDH_G1 | 1 | South | YES | -0.025395 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.039355 | 49 | 49 |  |  | -1.2444 | 49 | -0.039355 | -1.9284
9017 | SANDH_G2 | 2 | South | YES | -0.025395 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.039355 | 46 | 46 |  |  | -1.1682 | 46 | -0.039355 | -1.8103
9018 | SANDH_G3 | 3 | South | YES | -0.025395 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.039355 | 46 | 46 |  |  | -1.1682 | 46 | -0.039355 | -1.8103
9019 | SANDH_G4 | 4 | South | YES | -0.025395 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.039355 | 47 | 47 |  |  | -1.1936 | 47 | -0.039355 | -1.8497
9020 | SANDHG5A | 5A | South | YES | -0.025395 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.039355 | 155 | 155 |  |  | -3.9362 | 155 | -0.039355 | -6.1
9021 | SANDHG5C | 5C | South | YES | -0.025395 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.039355 | 148 | 148 |  |  | -3.7585 | 148 | -0.039355 | -5.8245
9002 | DECKR_G3 | 3 | South | YES | -0.025346 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.039306 | 42 | 42 |  |  | -1.0645 | 42 | -0.039306 | -1.6508
9003 | DECKR_G4 | 4 | South | YES | -0.025346 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.039306 | 44 | 44 |  |  | -1.1152 | 44 | -0.039306 | -1.7295
9004 | DECKR_G5 | 5 | South | YES | -0.025346 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.039306 | 44 | 44 |  |  | -1.1152 | 44 | -0.039306 | -1.7295
9005 | DECKR_G6 | 6 | South | YES | -0.025346 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.039306 | 47 | 47 |  |  | -1.1913 | 47 | -0.039306 | -1.8474
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.023403 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.037363 | 0 | 0 |  |  | 0 | 0 | -0.037363 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.022856 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.036816 | 132 | 132 |  |  | -3.017 | 132 | -0.036816 | -4.8597
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.022856 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.036816 | 139 | 139 |  |  | -3.177 | 139 | -0.036816 | -5.1174
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.022856 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.036816 | 329 | 329 |  |  | -7.5196 | 329 | -0.036816 | -12.1124
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.021402 | 152.5 | 83.5 | 152.5 | 0 | 1.004 | CC | -1 | 0.035362 | 152.5 | 152.5 |  |  | -3.2638 | 152.5 | -0.035362 | -5.3927
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.021402 | 149.5 | 83.5 | 149.5 | 0 | 1.004 | CC | -1 | 0.035362 | 149.5 | 149.5 |  |  | -3.1996 | 149.5 | -0.035362 | -5.2866
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.021402 | 232.6 | 42 | 232.6 | 0 | 1.004 | CC | -1 | 0.035362 | 232.6 | 232.6 |  |  | -4.9781 | 232.6 | -0.035362 | -8.2252
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.02086 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.03482 | 0 | 0 |  |  | 0 | 0 | -0.03482 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.02086 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.03482 | 0 | 0 |  |  | 0 | 0 | -0.03482 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.02086 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.03482 | 0 | 0 |  |  | 0 | 0 | -0.03482 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.020726 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.034686 | 223.9 | 223.9 |  |  | -4.6406 | 223.9 | -0.034686 | -7.7662
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.020726 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.034686 | 225 | 225 |  |  | -4.6634 | 225 | -0.034686 | -7.8043
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.020726 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.034686 | 224.6 | 224.6 |  |  | -4.6551 | 224.6 | -0.034686 | -7.7905
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.020726 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.034686 | 226.7 | 226.7 |  |  | -4.6986 | 226.7 | -0.034686 | -7.8633
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.020595 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.034555 | 0 | 0 |  |  | 0 | 0 | -0.034555 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.020543 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.034503 | 158 | 158 |  |  | -3.2458 | 158 | -0.034503 | -5.4515
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.020543 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.034503 | 160 | 160 |  |  | -3.2869 | 160 | -0.034503 | -5.5205
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.020543 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.034503 | 175 | 175 |  |  | -3.595 | 175 | -0.034503 | -6.038
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.020483 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.034443 | 0 | 0 |  |  | 0 | 0 | -0.034443 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.020483 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.034443 | 0 | 0 |  |  | 0 | 0 | -0.034443 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.020479 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.034439 | 50 | 50 |  |  | -1.0239 | 50 | -0.034439 | -1.7219
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.020479 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.034439 | 50 | 50 |  |  | -1.0239 | 50 | -0.034439 | -1.7219
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.020479 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.034439 | 50 | 50 |  |  | -1.0239 | 50 | -0.034439 | -1.7219
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.020479 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.034439 | 50 | 50 |  |  | -1.0239 | 50 | -0.034439 | -1.7219
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.020241 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.034201 | 148 | 148 |  |  | -2.9957 | 148 | -0.034201 | -5.0617
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.020241 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.034201 | 148 | 148 |  |  | -2.9957 | 148 | -0.034201 | -5.0617
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.020241 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.034201 | 154 | 154 |  |  | -3.1171 | 154 | -0.034201 | -5.2669
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.020241 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.034201 | 293 | 293 |  |  | -5.9306 | 293 | -0.034201 | -10.0209
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.019807 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.033767 | 61 | 61 |  |  | -1.2082 | 61 | -0.033767 | -2.0598
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.019807 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.033767 | 95 | 95 |  |  | -1.8817 | 95 | -0.033767 | -3.2079
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.019807 | 120.8 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.033767 | 151 | 151 |  |  | -2.9909 | 151 | -0.033767 | -5.0988
5111 | CALAVER_JTD1 | 1 | South | YES | -0.01979 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.03375 | 0 | 430 |  |  | 0 | 0 | -0.03375 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.01979 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.03375 | 0 | 430 |  |  | 0 | 0 | -0.03375 | 0
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.019769 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.033729 | 147 | 147 |  |  | -2.906 | 147 | -0.033729 | -4.9582
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.019769 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.033729 | 138 | 138 |  |  | -2.7281 | 138 | -0.033729 | -4.6546
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.019769 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.033729 | 146 | 146 |  |  | -2.8863 | 146 | -0.033729 | -4.9244
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.019769 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.033729 | 149 | 149 |  |  | -2.9456 | 149 | -0.033729 | -5.0256
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.019769 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.033729 | 182 | 182 |  |  | -3.598 | 182 | -0.033729 | -6.1387
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.019769 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.033729 | 203 | 203 |  |  | -4.0131 | 203 | -0.033729 | -6.847
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.019762 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.033722 | 155 | 155 |  |  | -3.0631 | 155 | -0.033722 | -5.2269
5477 | BRA_AVR1_ST1 | 1 | South | YES | -0.019762 | 174 | 138 | 174 | 0 | 1.017 | CC | -1 | 0.033722 | 174 | 174 |  |  | -3.4386 | 174 | -0.033722 | -5.8676
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.019762 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.033722 | 155 | 155 |  |  | -3.0631 | 155 | -0.033722 | -5.2269
5396 | CALAVER_OWS1 | 1 | South | YES | -0.019758 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.033718 | 418 | 418 |  |  | -8.2588 | 418 | -0.033718 | -14.0941
5397 | CALAVER_OWS2 | 2 | South | YES | -0.019758 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.033718 | 400 | 400 |  |  | -7.9032 | 400 | -0.033718 | -13.4872
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.019753 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.033713 | 407 | 407 |  |  | -8.0395 | 407 | -0.033713 | -13.7212
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.019723 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.033683 | 215 | 215 |  |  | -4.2404 | 215 | -0.033683 | -7.2418
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.019723 | 172.8 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.033683 | 216 | 216 |  |  | -4.2602 | 216 | -0.033683 | -7.2755
5031 | BRA_VHBCT1 | 1 | South | YES | -0.019723 | 44 | 24 | 44 | 0 | 1.0192 | GST | -1 | 0.033683 | 44 | 44 |  |  | -0.86781 | 44 | -0.033683 | -1.482
5032 | BRA_VHBCT2 | 2 | South | YES | -0.019723 | 44 | 24 | 44 | 0 | 1.0192 | GST | -1 | 0.033683 | 44 | 44 |  |  | -0.86781 | 44 | -0.033683 | -1.482
5033 | BRA_VHBCT3 | 3 | South | YES | -0.019723 | 43 | 24 | 43 | 0 | 1.0192 | GST | -1 | 0.033683 | 43 | 43 |  |  | -0.84809 | 43 | -0.033683 | -1.4484
5034 | BRA_VHBCT4 | 4 | South | YES | -0.019723 | 45 | 24 | 45 | 0 | 1.0192 | GST | -1 | 0.033683 | 45 | 45 |  |  | -0.88753 | 45 | -0.033683 | -1.5157
5264 | LEON_LCP3G3 | 3 | South | YES | -0.019628 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.033588 | 58 | 58 |  |  | -1.1384 | 58 | -0.033588 | -1.9481
5265 | LEON_LCP4G4 | 4 | South | YES | -0.019628 | 71.2 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.033588 | 89 | 89 |  |  | -1.7469 | 89 | -0.033588 | -2.9893
5266 | LEON_LCPCT1 | 1 | South | YES | -0.019628 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.033588 | 44 | 44 |  |  | -0.86363 | 44 | -0.033588 | -1.4779
5267 | LEON_LCPCT2 | 2 | South | YES | -0.019628 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.033588 | 44 | 44 |  |  | -0.86363 | 44 | -0.033588 | -1.4779
5268 | LEON_LCPCT3 | 3 | South | YES | -0.019628 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.033588 | 43 | 43 |  |  | -0.844 | 43 | -0.033588 | -1.4443
5269 | LEON_LCPCT4 | 4 | South | YES | -0.019628 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.033588 | 45 | 45 |  |  | -0.88326 | 45 | -0.033588 | -1.5115
3432 | SANDOW_4G | 4 | South | YES | -0.019561 | 580 | 225 | 580 | 0 | 1.029 | LIGCO | -1 | 0.033521 | 0 | 580 |  |  | 0 | 0 | -0.033521 | 0
13432 | SANDOW_5G | 5 | South | YES | -0.019561 | 581 | 225 | 581 | 0 | 1.029 | LIGCO | -1 | 0.033521 | 0 | 581 |  |  | 0 | 0 | -0.033521 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | -0.019547 | 562 | 100 | 562 | 0 | 1.018 | LIGCO | -1 | 0.033507 | 0 | 562 |  |  | 0 | 0 | -0.033507 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.019274 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.033234 | 0 | 606 |  |  | 0 | 0 | -0.033234 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.019274 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.033234 | 0 | 598 |  |  | 0 | 0 | -0.033234 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.019265 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.033225 | 0 | 436 |  |  | 0 | 0 | -0.033225 | 0
8189 | CUECPL2A | 1 | South | YES | -0.019154 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.033114 | 0 | 0 |  |  | 0 | 0 | -0.033114 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.018295 | 396.3 | 180 | 396.3 | 0 | 1.0331 | LIGCO | -1 | 0.032255 | 0 | 396.3 |  |  | 0 | 0 | -0.032255 | 0
88198 | BEEVILLE | F | South | YES | -0.017006 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.030966 | 0 | 0 |  |  | 0 | 0 | -0.030966 | 0
8161 | COLETO0A | 1 | South | YES | -0.016872 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.030832 | 0 | 633 |  |  | 0 | 0 | -0.030832 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.016675 | 19.2 | 6 | 24 | 0 | 1.0161 | GST | -1 | 0.030635 | 24 | 24 |  |  | -0.4002 | 24 | -0.030635 | -0.73524
5891 | PEARSALLGEN2 | 1 | South | YES | -0.016675 | 19.4 | 6 | 24.3 | 0 | 1.0161 | GST | -1 | 0.030635 | 24.3 | 24.3 |  |  | -0.4052 | 24.3 | -0.030635 | -0.74443
5892 | PEARSALLGEN3 | 1 | South | YES | -0.016675 | 19.1 | 6 | 23.9 | 0 | 1.0161 | GST | -1 | 0.030635 | 23.9 | 23.9 |  |  | -0.39853 | 23.9 | -0.030635 | -0.73217
80080 | GWINDT11A | 2 | South | YES | -0.016209 | 17.7 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 41 |  |  | 0 | 0 | -0.030169 | 0
80080 | GWINDT11A | 3 | South | YES | -0.016209 | 16.4 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 38 |  |  | 0 | 0 | -0.030169 | 0
80080 | GWINDT11A | 1 | South | YES | -0.016209 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 94 |  |  | 0 | 0 | -0.030169 | 0
80080 | GWINDT11A | 4 | South | YES | -0.016209 | 8.2 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 19 |  |  | 0 | 0 | -0.030169 | 0
80081 | GWINDT21A | 2 | South | YES | -0.016209 | 15.5 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 36 |  |  | 0 | 0 | -0.030169 | 0
80081 | GWINDT21A | 4 | South | YES | -0.016209 | 9.5 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 22 |  |  | 0 | 0 | -0.030169 | 0
80081 | GWINDT21A | 3 | South | YES | -0.016209 | 18.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 43 |  |  | 0 | 0 | -0.030169 | 0
80081 | GWINDT21A | 1 | South | YES | -0.016209 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 94 |  |  | 0 | 0 | -0.030169 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.016209 | 63 | 0 | 146 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 146 |  |  | 0 | 0 | -0.030169 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.016209 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 50 |  |  | 0 | 0 | -0.030169 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.016209 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 50 |  |  | 0 | 0 | -0.030169 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.016209 | 23.7 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.030169 | 0 | 55 |  |  | 0 | 0 | -0.030169 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.016208 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.030168 | 0 | 0 |  |  | 0 | 0 | -0.030168 | 0
5932 | SI_RAY9 | 9 | South | YES | -0.01619 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.03015 | 38 | 38 |  |  | -0.61522 | 38 | -0.03015 | -1.1457
5933 | SI_RAY6 | 6 | South | YES | -0.01619 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.03015 | 19.3 | 19.3 |  |  | -0.31247 | 19.3 | -0.03015 | -0.58189
5935 | SI_RAY10 | 10 | South | YES | -0.01619 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.03015 | 47 | 47 |  |  | -0.76093 | 47 | -0.03015 | -1.417
80003 | MILHWYS | F | South | YES | -0.016189 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.030149 | 0 | 0 |  |  | 0 | 0 | -0.030149 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.016169 | 30.3 | 0 | 38 |  | 1.027 | Cogen | -1 | 0.030129 | 0 | 0 |  |  | 0 | 0 | -0.030129 | 0
8461 | KOCH_UP0A | 1 | South | YES | -0.016167 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.030127 | 0 | 0 |  |  | 0 | 0 | -0.030127 | 0
8506 | VAL #1 | 1 | South | YES | -0.016154 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.030114 | 0 | 0 |  |  | 0 | 0 | -0.030114 | 0
8507 | VAL #2 | 2 | South | YES | -0.016154 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.030114 | 0 | 0 |  |  | 0 | 0 | -0.030114 | 0
8936 | MVGN#1 | 1 | South | YES | -0.016154 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.030114 | 216.6 | 216.6 |  |  | -3.499 | 216.6 | -0.030114 | -6.5227
8937 | MVGN#2 | 2 | South | YES | -0.016154 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.030114 | 216.7 | 216.7 |  |  | -3.5006 | 216.7 | -0.030114 | -6.5257
8938 | MVGN#3 | 3 | South | YES | -0.016154 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.030114 | 250.9 | 250.9 |  |  | -4.053 | 250.9 | -0.030114 | -7.5556
8981 | HECN1 | 1 | South | YES | -0.016154 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.030114 | 144.8 | 144.8 |  |  | -2.3391 | 144.8 | -0.030114 | -4.3605
8982 | HECN2 | 2 | South | YES | -0.016154 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.030114 | 144.1 | 144.1 |  |  | -2.3278 | 144.1 | -0.030114 | -4.3394
8983 | HECN3 | 3 | South | YES | -0.016154 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.030114 | 171.9 | 171.9 |  |  | -2.7769 | 171.9 | -0.030114 | -5.1766
8459 | B_DAVIS0B | MB | South | YES | -0.016147 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.030107 | 0 | 0 |  |  | 0 | 0 | -0.030107 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.016147 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.030107 | 0 | 0 |  |  | 0 | 0 | -0.030107 | 0
8173 | VICEC51A | 5 | South | YES | -0.016145 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.030105 | 144 | 144 |  |  | -2.3249 | 144 | -0.030105 | -4.3351
8174 | VICEC61A | 6 | South | YES | -0.016145 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.030105 | 188 | 188 |  |  | -3.0353 | 188 | -0.030105 | -5.6597
8456 | COSW#1 | 1 | South | YES | -0.01613 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.03009 | 0 | 0 |  |  | 0 | 0 | -0.03009 | 0
8457 | COSW#2 | 2 | South | YES | -0.01613 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.03009 | 0 | 0 |  |  | 0 | 0 | -0.03009 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.016123 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.030083 | 0 | 0 |  |  | 0 | 0 | -0.030083 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.016123 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.030083 | 0 | 0 |  |  | 0 | 0 | -0.030083 | 0
8562 | CNOPST1 | 3 | South | YES | -0.016123 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.030083 | 0 | 0 |  |  | 0 | 0 | -0.030083 | 0
8933 | FGNTS001 | 1 | South | YES | -0.016106 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.030066 | 146.5 | 146.5 |  |  | -2.3595 | 146.5 | -0.030066 | -4.4047
8934 | FGNTS101 | 2 | South | YES | -0.016106 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.030066 | 147.9 | 147.9 |  |  | -2.3821 | 147.9 | -0.030066 | -4.4468
8935 | FGNTS201 | 3 | South | YES | -0.016106 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.030066 | 173 | 173 |  |  | -2.7863 | 173 | -0.030066 | -5.2014
8926 | LGE_GT10A | 1 | South | YES | -0.015991 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.015991 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.015991 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
8930 | ICPGN10A | 1 | South | YES | -0.015991 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
8931 | ICPGN20A | 2 | South | YES | -0.015991 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
8932 | ICPGN30A | 3 | South | YES | -0.015991 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
80223 | REYSHR G | 1 | South | YES | -0.015991 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.029951 | 0 | 0 |  |  | 0 | 0 | -0.029951 | 0
8066 | DUP1V#1 | 1 | South | YES | -0.015984 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.029944 | 0 | 0 |  |  | 0 | 0 | -0.029944 | 0
88508 | FALFURRI | F | South | YES | -0.015971 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.029931 | 0 | 0 |  |  | 0 | 0 | -0.029931 | 0
5508 | RAYBURNCC9 | 1 | South | YES | -0.015963 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.029923 | 47.7 | 47.7 |  |  | -0.76144 | 47.7 | -0.029923 | -1.4273
5509 | RAYBURNCC10 | 1 | South | YES | -0.015963 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.029923 | 37.3 | 37.3 |  |  | -0.59542 | 37.3 | -0.029923 | -1.1161
5511 | RAYBURNCC7 | 1 | South | YES | -0.015963 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.029923 | 47.5 | 47.5 |  |  | -0.75824 | 47.5 | -0.029923 | -1.4213
5512 | RAYBURNCC8 | 1 | South | YES | -0.015963 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.029923 | 49.3 | 49.3 |  |  | -0.78698 | 49.3 | -0.029923 | -1.4752
5728 | FALCONHYDRO2 | 2 | South | YES | -0.015814 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.029774 | 0 | 0 |  |  | 0 | 0 | -0.029774 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.015814 | 11 | 0 | 11 | 0 | 1.0227 | Hydro | -1 | 0.029774 | 0 | 0 |  |  | 0 | 0 | -0.029774 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.015814 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.029774 | 0 | 0 |  |  | 0 | 0 | -0.029774 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.01581 | 17.6 | 6 | 22 | 0 | 1.0223 | GST | -1 | 0.02977 | 22 | 22 |  |  | -0.34782 | 22 | -0.02977 | -0.65494
5505 | RAYBURNGEN1 | 1 | South | YES | -0.01581 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.02977 | 11 | 11 |  |  | -0.17391 | 11 | -0.02977 | -0.32747
5506 | RAYBURNGEN2 | 1 | South | YES | -0.01581 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.02977 | 11 | 11 |  |  | -0.17391 | 11 | -0.02977 | -0.32747
80224 | VISTRONG1 | 1 | South | YES | -0.015701 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.029661 | 0 | 0 |  |  | 0 | 0 | -0.029661 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.015701 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.029661 | 0 | 0 |  |  | 0 | 0 | -0.029661 | 0
80227 | AIRCO G | 1 | South | YES | -0.015595 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.029555 | 0 | 0 |  |  | 0 | 0 | -0.029555 | 0
8147 | UCAR #2 | 10 | South | YES | -0.015548 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
8148 | UCAR #1 | 2 | South | YES | -0.015548 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
80137 | CSDR89 | 9 | South | YES | -0.015548 | 0 | 0 | 15 |  | 1.003 | DCTie | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
80137 | CSDR89 | 8 | South | YES | -0.015548 | 33.9 | 0 | 39 |  | 1.003 | DCTie | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
80138 | CSDR7 | 7 | South | YES | -0.015548 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
80139 | CSDR56 | 6 | South | YES | -0.015548 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
80139 | CSDR56 | 5 | South | YES | -0.015548 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
80140 | CSDR11 | 11 | South | YES | -0.015548 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.029508 | 0 | 0 |  |  | 0 | 0 | -0.029508 | 0
88299 | ZAPATA | F | South | YES | -0.015535 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.029495 | 0 | 0 |  |  | 0 | 0 | -0.029495 | 0
80226 | ALCOA G | 1 | South | YES | -0.015162 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.029122 | 0 | 0 |  |  | 0 | 0 | -0.029122 | 0
80012 | LAR | F | South | YES | -0.01513 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.02909 | 0 | 0 |  |  | 0 | 0 | -0.02909 | 0
80265 | LARECU40A | 4 | South | YES | -0.01513 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.02909 | 100 | 100 |  |  | -1.513 | 100 | -0.02909 | -2.909
80266 | LARECU50A | 5 | South | YES | -0.01513 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.02909 | 100 | 100 |  |  | -1.513 | 100 | -0.02909 | -2.909
8134 | FOR #1 | 1 | South | YES | -0.015045 | 54.1 | 45 | 79 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
8138 | FOR #2 | 2 | South | YES | -0.015045 | 63.1 | 45 | 81 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
8153 | FOR #3 | 3 | South | YES | -0.015045 | 63.1 | 45 | 79.9 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
8154 | FOR #4 | 4 | South | YES | -0.015045 | 63.1 | 60 | 80 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
8155 | FOR #5 | 5 | South | YES | -0.015045 | 63.1 | 60 | 78.4 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
8156 | FOR #6 | 6 | South | YES | -0.015045 | 24.9 | 5 | 25 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
8157 | FOR #7 | 7 | South | YES | -0.015045 | 28.8 | 5 | 46 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
80051 | FOR #8 | 8 | South | YES | -0.015045 | 28 | 28 | 28 | 0 | 1.016 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
80052 | FOR #9 | 9 | South | YES | -0.015045 | 29.7 | 5 | 43.6 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
80053 | FOR #10 | 10 | South | YES | -0.015045 | 68.4 | 45 | 75 | 0 | 1.03 | Cogen | -1 | 0.029005 | 0 | 0 |  |  | 0 | 0 | -0.029005 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | -0.01088 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.02484 | 0 | 0 |  |  |  |  | -0.02484 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.01088 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.02484 | 0 | 0 |  |  |  |  | -0.02484 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.010748 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.024708 | 76 | 76 |  |  |  |  | -0.024708 | -1.8778
48732 | CBE_GT2 | 1 | Houston | YES | -0.010748 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.024708 | 76 | 76 |  |  |  |  | -0.024708 | -1.8778
48733 | CBE_ST12 | 1 | Houston | YES | -0.010748 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.024708 | 105 | 105 |  |  |  |  | -0.024708 | -2.5943
48734 | CBE_GT3 | 1 | Houston | YES | -0.010748 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.024708 | 76 | 76 |  |  |  |  | -0.024708 | -1.8778
48735 | CBE_GT4 | 1 | Houston | YES | -0.010748 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.024708 | 76 | 76 |  |  |  |  | -0.024708 | -1.8778
48736 | CBE_ST34 | 1 | Houston | YES | -0.010748 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.024708 | 105 | 105 |  |  |  |  | -0.024708 | -2.5943
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.010314 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.024274 | 0 | 0 |  |  |  |  | -0.024274 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.008856 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.008856 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.008856 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.008856 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.008856 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.008856 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.008856 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.008856 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.008856 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.008856 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.008856 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.008856 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.008856 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.008856 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.008856 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.008856 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.008856 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.008856 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.008856 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.008856 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.022816 | 0 | 0 |  |  |  |  | -0.022816 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.008483 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.022443 | 0 | 0 |  |  |  |  | -0.022443 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.008483 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.022443 | 0 | 0 |  |  |  |  | -0.022443 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.008183 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.022143 | 0 | 0 |  |  |  |  | -0.022143 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.008183 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.022143 | 0 | 0 |  |  |  |  | -0.022143 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.008183 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.022143 | 0 | 0 |  |  |  |  | -0.022143 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.008183 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.022143 | 0 | 0 |  |  |  |  | -0.022143 | 0
80010 | EPLVT1 | F | South | YES | -0.007948 | 0 | 0 | 0 |  | 1.0376 | AVR | -1 | 0.021908 | 0 | 0 |  |  | 0 | 0 | -0.021908 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.007135 | 43 | 0 | 46.1 |  | 1.029 | Cogen | -1 | 0.021095 | 0 | 0 |  |  |  |  | -0.021095 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.007118 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.021078 | 0 | 651 |  |  |  |  | -0.021078 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.007118 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.021078 | 0 | 564 |  |  |  |  | -0.021078 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.007118 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.021078 | 0 | 603 |  |  |  |  | -0.021078 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.007109 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.021069 | 167.7 | 167.7 |  |  |  |  | -0.021069 | -3.5333
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.007109 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.021069 | 166.4 | 166.4 |  |  |  |  | -0.021069 | -3.5059
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.007109 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.021069 | 252.4 | 252.4 |  |  |  |  | -0.021069 | -5.3178
8262 | ELPS | 1 | South | YES | -0.006986 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.020946 | 0 | 0 |  |  | 0 | 0 | -0.020946 | 0
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.006976 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.020936 | 0 | 0 |  |  |  |  | -0.020936 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.006941 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.020901 | 166 | 166 |  |  |  |  | -0.020901 | -3.4696
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.006941 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.020901 | 166 | 166 |  |  |  |  | -0.020901 | -3.4696
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.006941 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.020901 | 248 | 248 |  |  |  |  | -0.020901 | -5.1834
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.006941 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.020901 | 546 | 546 |  |  |  |  | -0.020901 | -11.4119
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.006941 | 598 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.020901 | 0 | 654 |  |  |  |  | -0.020901 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.006941 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.020901 | 13 | 13 |  |  |  |  | -0.020901 | -0.27171
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.006276 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.006276 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.006276 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.006276 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.006276 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.006276 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.006276 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.006276 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.006276 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.006276 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.006276 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.006276 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.006276 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.006276 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.006276 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.020236 | 0 | 0 |  |  |  |  | -0.020236 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.005989 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.019949 | 0 | 0 |  |  |  |  | -0.019949 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.005788 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.019748 | 0 | 0 |  |  |  |  | -0.019748 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.005788 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.019748 | 0 | 0 |  |  |  |  | -0.019748 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.005788 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.019748 | 0 | 0 |  |  |  |  | -0.019748 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.005788 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.019748 | 0 | 0 |  |  |  |  | -0.019748 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.005788 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.019748 | 0 | 0 |  |  |  |  | -0.019748 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.005711 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.019671 | 0 | 0 |  |  |  |  | -0.019671 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.005711 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.019671 | 0 | 0 |  |  |  |  | -0.019671 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.005711 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.019671 | 0 | 0 |  |  |  |  | -0.019671 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.005711 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.019671 | 0 | 0 |  |  |  |  | -0.019671 | 0
48691 | GBY_73741085 | A | Houston | YES | -0.00561 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.01957 | 47 | 47 |  |  |  |  | -0.01957 | -0.91979
48691 | GBY_73741085 | B | Houston | YES | -0.00561 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.01957 | 47 | 47 |  |  |  |  | -0.01957 | -0.91979
48692 | GBY_81821075 | D | Houston | YES | -0.00561 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.01957 | 55 | 55 |  |  |  |  | -0.01957 | -1.0763
48692 | GBY_81821075 | C | Houston | YES | -0.00561 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.01957 | 47 | 47 |  |  |  |  | -0.01957 | -0.91979
48693 | GBY_83841065 | F | Houston | YES | -0.00561 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.01957 | 54 | 54 |  |  |  |  | -0.01957 | -1.0568
48693 | GBY_83841065 | E | Houston | YES | -0.00561 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.01957 | 57 | 57 |  |  |  |  | -0.01957 | -1.1155
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.005567 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.019527 | 0 | 0 |  |  |  |  | -0.019527 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.005567 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.019527 | 0 | 0 |  |  |  |  | -0.019527 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.00553 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.01949 | 163.2 | 163.2 |  |  |  |  | -0.01949 | -3.1808
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.00553 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.01949 | 157.1 | 157.1 |  |  |  |  | -0.01949 | -3.0619
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.00553 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.01949 | 157.5 | 157.5 |  |  |  |  | -0.01949 | -3.0697
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.00553 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.01949 | 157 | 157 |  |  |  |  | -0.01949 | -3.0599
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.00553 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.01949 | 282 | 282 |  |  |  |  | -0.01949 | -5.4962
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.005495 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.019455 | 0 | 0 |  |  |  |  | -0.019455 | 0
48855 | SRB_GT211035 | B2 | Houston | YES | -0.00546 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.01942 | 12 | 12 |  |  |  |  | -0.01942 | -0.23304
48855 | SRB_GT211035 | B1 | Houston | YES | -0.00546 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.01942 | 18 | 18 |  |  |  |  | -0.01942 | -0.34956
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.005458 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.019418 | 176 | 176 |  |  |  |  | -0.019418 | -3.4176
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.005455 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.019415 | 165 | 165 |  |  |  |  | -0.019415 | -3.2035
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.005454 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.019414 | 0 | 0 |  |  |  |  | -0.019414 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.005454 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.019414 | 0 | 0 |  |  |  |  | -0.019414 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.005446 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.019406 | 213 | 213 |  |  |  |  | -0.019406 | -4.1335
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.005445 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.019405 | 0 | 0 |  |  |  |  | -0.019405 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.005445 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.019405 | 0 | 0 |  |  |  |  | -0.019405 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.005445 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.019405 | 0 | 0 |  |  |  |  | -0.019405 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.005445 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.019405 | 0 | 0 |  |  |  |  | -0.019405 | 0
48845 | SOL_GT1 | 1 | Houston | YES | -0.005445 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.019405 | 16.2 | 16.2 |  |  |  |  | -0.019405 | -0.31436
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.005444 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.019404 | 228 | 228 |  |  |  |  | -0.019404 | -4.4241
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.005443 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.019403 | 0 | 0 |  |  |  |  | -0.019403 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.005443 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.019403 | 0 | 0 |  |  |  |  | -0.019403 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.005443 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.019403 | 0 | 0 |  |  |  |  | -0.019403 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.005394 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.019354 | 0 | 0 |  |  |  |  | -0.019354 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.005394 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.019354 | 0 | 0 |  |  |  |  | -0.019354 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.005394 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.019354 | 0 | 0 |  |  |  |  | -0.019354 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.005394 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.019354 | 0 | 0 |  |  |  |  | -0.019354 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.005321 | 137.6 | 54.6 | 137.6 |  | 1.0362 | Cogen | -1 | 0.019281 | 0 | 0 |  |  |  |  | -0.019281 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.00531 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.01927 | 42 | 42 |  |  |  |  | -0.01927 | -0.80934
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.00531 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.01927 | 42 | 42 |  |  |  |  | -0.01927 | -0.80934
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.00531 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.01927 | 39 | 39 |  |  |  |  | -0.01927 | -0.75153
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.00531 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.01927 | 39 | 39 |  |  |  |  | -0.01927 | -0.75153
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.005295 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.019255 | 0 | 0 |  |  |  |  | -0.019255 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.005295 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.019255 | 0 | 0 |  |  |  |  | -0.019255 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.005189 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.019149 | 107 | 107 |  |  |  |  | -0.019149 | -2.0489
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.005189 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.019149 | 108 | 108 |  |  |  |  | -0.019149 | -2.0681
48875 | THW_3132 | A | Houston | YES | -0.005189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.019149 | 55 | 55 |  |  |  |  | -0.019149 | -1.0532
48875 | THW_3132 | B | Houston | YES | -0.005189 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.019149 | 53 | 53 |  |  |  |  | -0.019149 | -1.0149
48877 | THW_3334 | D | Houston | YES | -0.005189 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.019149 | 57 | 57 |  |  |  |  | -0.019149 | -1.0915
48877 | THW_3334 | C | Houston | YES | -0.005189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.019149 | 55 | 55 |  |  |  |  | -0.019149 | -1.0532
48879 | THW_4142 | E | Houston | YES | -0.005189 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.019149 | 56 | 56 |  |  |  |  | -0.019149 | -1.0723
48879 | THW_4142 | F | Houston | YES | -0.005189 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.019149 | 55 | 55 |  |  |  |  | -0.019149 | -1.0532
48881 | THW_4344 | G | Houston | YES | -0.005189 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.019149 | 58 | 58 |  |  |  |  | -0.019149 | -1.1106
48881 | THW_4344 | H | Houston | YES | -0.005189 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.019149 | 58 | 58 |  |  |  |  | -0.019149 | -1.1106
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.005118 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.019078 | 746 | 746 |  |  |  |  | -0.019078 | -14.2321
49803 | EXN_15GT | 1 | Houston | YES | -0.005085 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.005085 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.005085 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.005085 | 43 | 9.2 | 45.9 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.005085 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.005085 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.005085 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.005085 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.005085 | 18.5 | 9.2 | 18.5 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.005085 | 81 | 21.3 | 85.4 | 0 | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.005085 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.019045 | 0 | 0 |  |  |  |  | -0.019045 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.005066 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.019026 | 12 | 12 |  |  |  |  | -0.019026 | -0.22831
48651 | EP_1_2 | 2 | Houston | YES | -0.004997 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.018957 | 0 | 0 |  |  |  |  | -0.018957 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.004997 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.018957 | 0 | 0 |  |  |  |  | -0.018957 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.004995 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.004995 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.004995 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.004995 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.004995 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.004995 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.004995 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.018955 | 0 | 0 |  |  |  |  | -0.018955 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.00499 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.01895 | 744 | 744 |  |  |  |  | -0.01895 | -14.0987
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.004965 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.018925 | 0 | 0 |  |  |  |  | -0.018925 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.004949 | 172 | 0 | 172 | 0 | 1.026 | GSC | -1 | 0.018909 | 172 | 172 |  |  |  |  | -0.018909 | -3.2523
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.004949 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.018909 | 172 | 172 |  |  |  |  | -0.018909 | -3.2523
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.004949 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.018909 | 172 | 172 |  |  |  |  | -0.018909 | -3.2523
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.004855 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.018815 | 162.8 | 162.8 |  |  |  |  | -0.018815 | -3.0631
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.004855 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.018815 | 161.4 | 161.4 |  |  |  |  | -0.018815 | -3.0367
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.004855 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.018815 | 158.9 | 158.9 |  |  |  |  | -0.018815 | -2.9897
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.004855 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.018815 | 269.2 | 269.2 |  |  |  |  | -0.018815 | -5.065
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.004825 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.018785 | 398 | 398 |  |  |  |  | -0.018785 | -7.4764
48885 | THW_5152 | B | Houston | YES | -0.004783 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.018743 | 59 | 59 |  |  |  |  | -0.018743 | -1.1058
48885 | THW_5152 | A | Houston | YES | -0.004783 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.018743 | 58 | 58 |  |  |  |  | -0.018743 | -1.0871
48886 | THW_5354 | D | Houston | YES | -0.004783 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.018743 | 58 | 58 |  |  |  |  | -0.018743 | -1.0871
48886 | THW_5354 | C | Houston | YES | -0.004783 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.018743 | 57 | 57 |  |  |  |  | -0.018743 | -1.0683
48887 | THW_5556 | E | Houston | YES | -0.004783 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.018743 | 59 | 59 |  |  |  |  | -0.018743 | -1.1058
48887 | THW_5556 | F | Houston | YES | -0.004783 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.018743 | 57 | 57 |  |  |  |  | -0.018743 | -1.0683
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.004214 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.018174 | 0 | 0 |  |  |  |  | -0.018174 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.004214 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.018174 | 0 | 0 |  |  |  |  | -0.018174 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.004214 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.018174 | 0 | 0 |  |  |  |  | -0.018174 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.004214 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.018174 | 0 | 0 |  |  |  |  | -0.018174 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.004214 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.018174 | 0 | 0 |  |  |  |  | -0.018174 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.002851 | 33 | 13 | 33 | 0 | 1.0375 | Hydro | -1 | 0.016811 | 0 | 0 |  |  | 0 | 0 | -0.016811 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.002851 | 25 | 13 | 25 | 0 | 1.0375 | Hydro | -1 | 0.016811 | 0 | 0 |  |  | 0 | 0 | -0.016811 | 0
88253 | HAMILTON | F | South | YES | -0.002851 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.016811 | 0 | 0 |  |  | 0 | 0 | -0.016811 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.01396 | 15 | 15 |  |  | 0 | 15 | -0.01396 | -0.2094
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
8442 | NUECES_B0A | MB | South | YES | 0 | 0 | 81 | 367 |  | 1.03 | GST | -1 | 0.01396 | 0 | 0 |  |  | 0 | 0 | -0.01396 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.01396 | 0 | 0 |  |  |  |  | -0.01396 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | 0.000927 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.022401 | 154.2 | 154.2 | 0.14294 | 154.2 |  |  | 0.022401 | 3.4543
48672 | FTR_GT2_5110 | 2 | North | YES | 0.000927 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.022401 | 159 | 159 | 0.14739 | 159 |  |  | 0.022401 | 3.5618
48673 | FTR_GT3_5085 | 3 | North | YES | 0.000927 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.022401 | 158 | 158 | 0.14647 | 158 |  |  | 0.022401 | 3.5394
48674 | FTR_CN4_5095 | 4 | North | YES | 0.000927 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.022401 | 380 | 380 | 0.35226 | 380 |  |  | 0.022401 | 8.5124
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.00119 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.022664 | 48 | 48 | 0.05712 | 48 |  |  | 0.022664 | 1.0879
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.00119 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.022664 | 46 | 46 | 0.05474 | 46 |  |  | 0.022664 | 1.0426
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.00119 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.022664 | 105 | 105 | 0.12495 | 105 |  |  | 0.022664 | 2.3797
32886 | BRYN_ATKINS3 | MB | North | YES | 0.001355 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.022829 | 0 | 0 | 0 | 0 |  |  | 0.022829 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.001355 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.022829 | 0 | 0 | 0 | 0 |  |  | 0.022829 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.001355 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.022829 | 17 | 17 | 0.023035 | 17 |  |  | 0.022829 | 0.3881
32890 | BRYN_ATKINS4 | MB | North | YES | 0.001355 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.022829 | 0 | 0 | 0 | 0 |  |  | 0.022829 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.001355 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.022829 | 0 | 0 | 0 | 0 |  |  | 0.022829 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.001433 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.022907 | 32 | 32 | 0.045856 | 32 |  |  | 0.022907 | 0.73303
990 | GIBN_CREK_G1 | 1 | North | YES | 0.001955 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.023429 | 0 | 463 | 0.90516 | 463 |  |  | 0.023429 | 10.8477
3416 | LAKE_CRK1_G | 1 | North | YES | 0.00504 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.026514 | 75 | 75 | 0.378 | 75 |  |  | 0.026514 | 1.9886
3417 | LAKE_CRK2_G | 2 | North | YES | 0.00504 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.026514 | 222 | 222 | 1.1189 | 222 |  |  | 0.026514 | 5.8861
39960 | TNTNPONE_18 | 1 | North | YES | 0.005426 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.0269 | 0 | 152.3 | 0.82638 | 152.3 |  |  | 0.0269 | 4.0969
39970 | TNTNPONE_28 | 1 | North | YES | 0.005426 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.0269 | 0 | 153 | 0.83018 | 153 |  |  | 0.0269 | 4.1157
48721 | LEG_1___1 | 1 | North | YES | 0.00684 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.028314 | 0 | 827 | 5.6567 | 827 |  |  | 0.028314 | 23.4158
48722 | LEG_2___2 | 2 | North | YES | 0.00684 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.028314 | 0 | 819 | 5.602 | 819 |  |  | 0.028314 | 23.1893
3403 | THOUSE_1G | 1 | North | YES | 0.007395 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.028869 | 563 | 563 | 4.1634 | 563 |  |  | 0.028869 | 16.2533
3404 | THOUSE_2G | 2 | North | YES | 0.007395 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.028869 | 807 | 807 | 5.9678 | 807 |  |  | 0.028869 | 23.2974
238 | BOSQUESW505 | 1 | North | YES | 0.008562 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.030036 | 255 | 255 | 2.1833 | 255 |  |  | 0.030036 | 7.6592
239 | BOSQUESW502 | 1 | North | YES | 0.008562 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.030036 | 149 | 149 | 1.2757 | 149 |  |  | 0.030036 | 4.4754
247 | BOSQUESW501 | 2 | North | YES | 0.008562 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.030036 | 156 | 156 | 1.3357 | 156 |  |  | 0.030036 | 4.6856
251 | BOSQUESW803 | 2 | North | YES | 0.009728 | 150 | 0 | 150 |  | 1.032 | CC | 1 | 0.031202 | 150 | 150 | 1.4592 | 150 |  |  | 0.031202 | 4.6803
253 | BOSQUESW804 | 2 | North | YES | 0.009728 | 80 | 0 | 80 |  | 1.032 | CC | 1 | 0.031202 | 80 | 80 | 0.77824 | 80 |  |  | 0.031202 | 2.4962
3381 | BBRN_1G | 1 | North | YES | 0.010388 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.031862 | 0 | 618 | 6.4198 | 618 |  |  | 0.031862 | 19.6908
3382 | BBRN_2G | 2 | North | YES | 0.010388 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.031862 | 0 | 589 | 6.1185 | 589 |  |  | 0.031862 | 18.7668
13131 | CALFREST_1G | 1 | North | YES | 0.010773 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.032247 | 150.7 | 150.7 | 1.6235 | 150.7 |  |  | 0.032247 | 4.8596
13132 | CALFREST_2G | 2 | North | YES | 0.010773 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.032247 | 151 | 151 | 1.6267 | 151 |  |  | 0.032247 | 4.8693
13133 | CALFREST_3G | 3 | North | YES | 0.010773 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.032247 | 177.4 | 177.4 | 1.9111 | 177.4 |  |  | 0.032247 | 5.7206
13134 | CALFREST_4G | 4 | North | YES | 0.010838 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.032312 | 151.5 | 151.5 | 1.642 | 151.5 |  |  | 0.032312 | 4.8953
13135 | CALFREST_5G | 5 | North | YES | 0.010838 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.032312 | 152.3 | 152.3 | 1.6506 | 152.3 |  |  | 0.032312 | 4.9211
13136 | CALFREST_6G | 6 | North | YES | 0.010838 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.032312 | 177.5 | 177.5 | 1.9237 | 177.5 |  |  | 0.032312 | 5.7354
244 | WHITNYDM01 | 1 | North | YES | 0.011589 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.033063 | 0 | 0 | 0 | 0 |  |  | 0.033063 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.011589 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.033063 | 0 | 0 | 0 | 0 |  |  | 0.033063 | 0
3107 | STRYKER_1G | 1 | North | YES | 0.012431 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.033905 | 182 | 182 | 2.2624 | 182 |  |  | 0.033905 | 6.1707
3108 | STRYKER_2G | 2 | North | YES | 0.012431 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.033905 | 484 | 484 | 6.0166 | 484 |  |  | 0.033905 | 16.4101
3113 | LUFKINWB_1G | 1 | North | YES | 0.012527 | 0 | 0 | 50 |  | 1.01 | Trash | 1 | 0.034001 | 50 | 50 | 0.62635 | 50 |  |  | 0.034001 | 1.7001
3348 | CHAMPION_1G | MB | North | YES | 0.012543 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.034017 | 0 | 0 | 0 | 0 |  |  | 0.034017 | 0
3126 | TRINIDAD_6G | 1 | North | YES | 0.012616 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.03409 | 224 | 224 | 2.826 | 224 |  |  | 0.03409 | 7.6362
13116 | TGATEWAY_1G | 1 | North | YES | 0.012732 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.034206 | 151 | 151 | 1.9225 | 151 |  |  | 0.034206 | 5.1651
13117 | TGATEWAY_2G | 2 | North | YES | 0.012732 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.034206 | 130 | 130 | 1.6552 | 130 |  |  | 0.034206 | 4.4468
13118 | TGATEWAY_3G | 3 | North | YES | 0.012732 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.034206 | 148 | 148 | 1.8843 | 148 |  |  | 0.034206 | 5.0625
13119 | TGATEWAY_4G | 4 | North | YES | 0.012732 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.034206 | 399 | 399 | 5.0801 | 399 |  |  | 0.034206 | 13.6482
3097 | MARTLAKE_1G | 1 | North | YES | 0.012918 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.034392 | 0 | 790 | 10.2052 | 790 |  |  | 0.034392 | 27.1698
3098 | MARTLAKE_2G | 2 | North | YES | 0.012918 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.034392 | 0 | 795 | 10.2698 | 795 |  |  | 0.034392 | 27.3417
3099 | MARTLAKE_3G | 3 | North | YES | 0.012918 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.034392 | 0 | 804 | 10.3861 | 804 |  |  | 0.034392 | 27.6513
12322 | ENNSTRAC_1G | 1 | North | YES | 0.014109 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.035583 | 196 | 196 | 2.7654 | 196 |  |  | 0.035583 | 6.9743
12323 | ENNSTRAC_2G | 2 | North | YES | 0.014109 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.035583 | 116 | 116 | 1.6366 | 116 |  |  | 0.035583 | 4.1276
12411 | FPLEFR1A_G | 1 | North | YES | 0.014284 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.035758 | 161 | 161 | 2.2997 | 161 |  |  | 0.035758 | 5.7571
12412 | FPLEFR1B_G | 2 | North | YES | 0.014284 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.035758 | 164 | 164 | 2.3426 | 164 |  |  | 0.035758 | 5.8643
12413 | FPLEFR1C_G | 3 | North | YES | 0.014284 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.035758 | 164 | 164 | 2.3426 | 164 |  |  | 0.035758 | 5.8643
12414 | FPLEFR1S_G | 4 | North | YES | 0.014284 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.035758 | 414 | 414 | 5.9136 | 414 |  |  | 0.035758 | 14.8039
12421 | FPLEFR2A_G | 1 | North | YES | 0.014284 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.035758 | 162 | 162 | 2.314 | 162 |  |  | 0.035758 | 5.7928
12422 | FPLEFR2B_G | 2 | North | YES | 0.014284 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.035758 | 161 | 161 | 2.2997 | 161 |  |  | 0.035758 | 5.7571
12423 | FPLEFR2C_G | 3 | North | YES | 0.014284 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.035758 | 163 | 163 | 2.3283 | 163 |  |  | 0.035758 | 5.8286
12424 | FPLEFR2S_G | 4 | North | YES | 0.014284 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.035758 | 415 | 415 | 5.9279 | 415 |  |  | 0.035758 | 14.8396
12440 | PARKD_1SVC8 | 1 | North | YES | 0.014481 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.035955 | 0 | 0 | 0 | 0 |  |  | 0.035955 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.014481 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.035955 | 0 | 0 | 0 | 0 |  |  | 0.035955 | 0
2451 | LKHB1_G | 1 | North | YES | 0.014493 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.035967 | 391 | 391 | 5.6668 | 391 |  |  | 0.035967 | 14.0631
2452 | LKHB2_G | 2 | North | YES | 0.014493 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.035967 | 516 | 516 | 7.4784 | 516 |  |  | 0.035967 | 18.559
1941 | MDLTHELP_1G | 1 | North | YES | 0.014503 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.035977 | 216.4 | 216.4 | 3.1384 | 216.4 |  |  | 0.035977 | 7.7855
1942 | MDLTHELP_2G | 2 | North | YES | 0.014503 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.035977 | 216.1 | 216.1 | 3.1341 | 216.1 |  |  | 0.035977 | 7.7747
948 | STEAM1 | 1 | North | YES | 0.014692 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.036166 | 20 | 20 | 0.29384 | 20 |  |  | 0.036166 | 0.72332
949 | STEAM2 | 1 | North | YES | 0.014692 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.036166 | 26 | 26 | 0.38199 | 26 |  |  | 0.036166 | 0.94032
950 | STEAM3 | 1 | North | YES | 0.014692 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.036166 | 42 | 42 | 0.61706 | 42 |  |  | 0.036166 | 1.519
837 | NEWMAN_G5 | 1 | North | YES | 0.014718 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.036192 | 40 | 40 | 0.58872 | 40 |  |  | 0.036192 | 1.4477
842 | OLINGER_G1 | 1 | North | YES | 0.014764 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.036238 | 79 | 79 | 1.1664 | 79 |  |  | 0.036238 | 2.8628
843 | OLINGER_G2 | 1 | North | YES | 0.014764 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.036238 | 110 | 110 | 1.624 | 110 |  |  | 0.036238 | 3.9862
844 | OLINGER_G3 | 1 | North | YES | 0.014764 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.036238 | 150 | 150 | 2.2146 | 150 |  |  | 0.036238 | 5.4357
845 | OLINGER_G4 | 1 | North | YES | 0.014764 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.036238 | 76 | 76 | 1.1221 | 76 |  |  | 0.036238 | 2.7541
2413 | MTCK6_G | 6 | North | YES | 0.014804 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.036278 | 118 | 118 | 1.7469 | 118 |  |  | 0.036278 | 4.2808
2414 | MTCK7_G | 7 | North | YES | 0.014804 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.036278 | 115 | 115 | 1.7025 | 115 |  |  | 0.036278 | 4.172
2417 | MTCK8_G | 8 | North | YES | 0.014804 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.036278 | 556 | 556 | 8.231 | 556 |  |  | 0.036278 | 20.1706
1701 | MOSES_1G | 1 | North | YES | 0.014959 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.036433 | 0 | 558 | 8.3471 | 558 |  |  | 0.036433 | 20.3297
1702 | MOSES_2G | 2 | North | YES | 0.014959 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.036433 | 0 | 579 | 8.6613 | 579 |  |  | 0.036433 | 21.0948
1703 | MOSES_3G | 3 | North | YES | 0.014959 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.036433 | 0 | 808 | 12.0869 | 808 |  |  | 0.036433 | 29.438
5925 | DCEAST | EQ | North | YES | 0.014959 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.036433 | 0 | 0 | 0 | 0 |  |  | 0.036433 | 0
1675 | PEC_1G | 1 | North | YES | 0.01504 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.036514 | 0 | 0 | 0 | 0 |  |  | 0.036514 | 0
1676 | PEC_2G | 2 | North | YES | 0.01504 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.036514 | 0 | 0 | 0 | 0 |  |  | 0.036514 | 0
1677 | PEC_3G | 3 | North | YES | 0.01504 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.036514 | 0 | 0 | 0 | 0 |  |  | 0.036514 | 0
2418 | MTCK2_G | 2 | North | YES | 0.015058 | 0 | 10 | 23 |  | 0.971 | GSC | 1 | 0.036532 | 23 | 23 | 0.34633 | 23 |  |  | 0.036532 | 0.84024
2419 | MTCK3_G | MB | North | YES | 0.015058 | 0 | 10 | 63 |  | 0.971 | GSC | 1 | 0.036532 | 0 | 0 | 0 | 0 |  |  | 0.036532 | 0
1678 | LAMARPWR_1G | 1 | North | YES | 0.015072 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.036546 | 160 | 160 | 2.4115 | 160 |  |  | 0.036546 | 5.8474
1679 | LAMARPWR_2G | 2 | North | YES | 0.015072 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.036546 | 156 | 156 | 2.3512 | 156 |  |  | 0.036546 | 5.7012
1680 | LAMARPWR_3G | 3 | North | YES | 0.015072 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.036546 | 196 | 196 | 2.9541 | 196 |  |  | 0.036546 | 7.163
1681 | LAMARPWR_4G | 4 | North | YES | 0.015072 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.036546 | 156 | 156 | 2.3512 | 156 |  |  | 0.036546 | 5.7012
1682 | LAMARPWR_5G | 5 | North | YES | 0.015072 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.036546 | 157 | 157 | 2.3663 | 157 |  |  | 0.036546 | 5.7377
1683 | LAMARPWR_6G | 6 | North | YES | 0.015072 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.036546 | 198 | 198 | 2.9843 | 198 |  |  | 0.036546 | 7.2361
1689 | VALLEY_3G | 3 | North | YES | 0.015131 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.036605 | 375 | 375 | 5.6741 | 375 |  |  | 0.036605 | 13.7269
11691 | KMICHICT1_G | 1 | North | YES | 0.015131 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.036605 | 144 | 144 | 2.1789 | 144 |  |  | 0.036605 | 5.2711
11692 | KMICHICT2_G | 2 | North | YES | 0.015131 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.036605 | 146 | 146 | 2.2091 | 146 |  |  | 0.036605 | 5.3443
11693 | KMICHIST3_G | 3 | North | YES | 0.015131 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.036605 | 312 | 312 | 4.7209 | 312 |  |  | 0.036605 | 11.4208
11694 | KMICHICT4_G | 4 | North | YES | 0.015131 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.036605 | 144 | 144 | 2.1789 | 144 |  |  | 0.036605 | 5.2711
11695 | KMICHICT5_G | 5 | North | YES | 0.015131 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.036605 | 148 | 148 | 2.2394 | 148 |  |  | 0.036605 | 5.4176
11696 | KMICHIST6_G | 6 | North | YES | 0.015131 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.036605 | 310 | 310 | 4.6906 | 310 |  |  | 0.036605 | 11.3476
1687 | VALLEY_1G | 1 | North | YES | 0.01531 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.036784 | 170 | 170 | 2.6027 | 170 |  |  | 0.036784 | 6.2533
1688 | VALLEY_2G | 2 | North | YES | 0.01531 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.036784 | 527 | 527 | 8.0684 | 527 |  |  | 0.036784 | 19.3852
6948 | DENISNDM | 1 | North | YES | 0.015442 | 40 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.036916 | 0 | 0 | 0 | 0 |  |  | 0.036916 | 0
6948 | DENISNDM | 2 | North | YES | 0.015442 | 31 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.036916 | 0 | 0 | 0 | 0 |  |  | 0.036916 | 0
2381 | NTHLK1_G | 1 | North | YES | 0.015554 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.037028 | 156 | 156 | 2.4264 | 156 |  |  | 0.037028 | 5.7764
2382 | NTHLK2_G | 2 | North | YES | 0.015554 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.037028 | 181 | 181 | 2.8153 | 181 |  |  | 0.037028 | 6.7021
2383 | NTHLK3_G | 3 | North | YES | 0.015554 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.037028 | 329 | 329 | 5.1173 | 329 |  |  | 0.037028 | 12.1823
2371 | COLLIN_1G | MB | North | YES | 0.015701 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.037175 | 0 | 0 | 0 | 0 |  |  | 0.037175 | 0
1937 | MDLTHELP_5G | 5 | North | YES | 0.015717 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.037191 | 224 | 224 | 3.5206 | 224 |  |  | 0.037191 | 8.3308
1938 | MDLTHELP_6G | 6 | North | YES | 0.015717 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.037191 | 226 | 226 | 3.552 | 226 |  |  | 0.037191 | 8.4052
1943 | MDLTHELP_3G | 3 | North | YES | 0.015717 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.037191 | 212 | 212 | 3.332 | 212 |  |  | 0.037191 | 7.8845
1944 | MDLTHELP_4G | 4 | North | YES | 0.015717 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.037191 | 211 | 211 | 3.3163 | 211 |  |  | 0.037191 | 7.8473
1948 | HANDLEY_4G | 4 | North | YES | 0.016873 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.038347 | 435 | 435 | 7.3398 | 435 |  |  | 0.038347 | 16.681
1947 | HANDLEY_3G | 3 | North | YES | 0.017026 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.0385 | 395 | 395 | 6.7253 | 395 |  |  | 0.0385 | 15.2076
1949 | HANDLEY_5G | 5 | North | YES | 0.017026 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.0385 | 435 | 435 | 7.4063 | 435 |  |  | 0.0385 | 16.7476
1945 | HANDLEY_1G | MB | North | YES | 0.017122 | 0 | 25 | 36 |  | 0.986 | GST | 1 | 0.038596 | 0 | 0 | 0 | 0 |  |  | 0.038596 | 0
1946 | HANDLEY_2G | MB | North | YES | 0.017122 | 0 | 30 | 68 |  | 0.986 | GST | 1 | 0.038596 | 0 | 0 | 0 | 0 |  |  | 0.038596 | 0
923 | SPENCER_G4 | 1 | North | YES | 0.017537 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.039011 | 61 | 61 | 1.0698 | 61 |  |  | 0.039011 | 2.3797
924 | SPENCER_G5 | 1 | North | YES | 0.017537 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.039011 | 66 | 66 | 1.1574 | 66 |  |  | 0.039011 | 2.5747
1861 | EAGLEMNT_1G | MB | North | YES | 0.018408 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.039882 | 0 | 0 | 0 | 0 |  |  | 0.039882 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.018408 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.039882 | 0 | 0 | 0 | 0 |  |  | 0.039882 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.018408 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.039882 | 0 | 0 | 0 | 0 |  |  | 0.039882 | 0
366 | JNSNCNTY802 | 1 | North | YES | 0.018579 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.040053 | 0 | 0 | 0 | 0 |  |  | 0.040053 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.018579 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.040053 | 0 | 0 | 0 | 0 |  |  | 0.040053 | 0
728 | WOLFRIDGE801 | 1 | North | YES | 0.018745 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.040219 | 0 | 112.5 | 2.1088 | 112.5 |  |  | 0.040219 | 4.5247
580 | JCKCNTY801 | 1 | North | YES | 0.020204 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.041678 | 288 | 288 | 5.8188 | 288 |  |  | 0.041678 | 12.0033
581 | JCKCNTY802 | 2 | North | YES | 0.020204 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.041678 | 147 | 147 | 2.97 | 147 |  |  | 0.041678 | 6.1267
582 | JCKCNTY803 | 3 | North | YES | 0.020204 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.041678 | 147 | 147 | 2.97 | 147 |  |  | 0.041678 | 6.1267
1889 | DECRDOVA_1G | 1 | North | YES | 0.020422 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.041896 | 779 | 779 | 15.9087 | 779 |  |  | 0.041896 | 32.6371
1453 | WCPWRCO_1G | 1 | North | YES | 0.02083 | 204 | 50 | 204 |  | 1.02 | CC | 1 | 0.042304 | 204 | 204 | 4.2493 | 204 |  |  | 0.042304 | 8.63
1454 | WCPWRCO_2G | 2 | North | YES | 0.02083 | 204 | 50 | 204 |  | 1.02 | CC | 1 | 0.042304 | 204 | 204 | 4.2493 | 204 |  |  | 0.042304 | 8.63
1455 | WCPWRCO_3G | 3 | North | YES | 0.02083 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.042304 | 242 | 242 | 5.0409 | 242 |  |  | 0.042304 | 10.2376
1892 | DECRDOVA_2G | A | North | YES | 0.021062 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.042536 | 70 | 70 | 1.4743 | 70 |  |  | 0.042536 | 2.9775
1893 | DECRDOVA_3G | B | North | YES | 0.021062 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.042536 | 69 | 69 | 1.4533 | 69 |  |  | 0.042536 | 2.935
1894 | DECRDOVA_4G | C | North | YES | 0.021062 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.042536 | 69 | 69 | 1.4533 | 69 |  |  | 0.042536 | 2.935
1895 | DECRDOVA_5G | D | North | YES | 0.021062 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.042536 | 68 | 68 | 1.4322 | 68 |  |  | 0.042536 | 2.8925
503 | NTHTEXAS01 | 1 | North | YES | 0.021393 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.042867 | 18 | 18 | 0.38507 | 18 |  |  | 0.042867 | 0.77161
504 | NTHTEXAS02 | 2 | North | YES | 0.021393 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.042867 | 18 | 18 | 0.38507 | 18 |  |  | 0.042867 | 0.77161
505 | NTHTEXAS03 | 3 | North | YES | 0.021393 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.042867 | 38 | 38 | 0.81293 | 38 |  |  | 0.042867 | 1.629
1877 | WLFHOLW_1G | 1 | North | YES | 0.021423 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.042897 | 217.3 | 217.3 | 4.6552 | 217.3 |  |  | 0.042897 | 9.3215
1878 | WLFHOLW_2G | 2 | North | YES | 0.021423 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.042897 | 215.7 | 215.7 | 4.6209 | 215.7 |  |  | 0.042897 | 9.2529
1879 | WLFHOLW_3G | 3 | North | YES | 0.021423 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.042897 | 272.4 | 272.4 | 5.8356 | 272.4 |  |  | 0.042897 | 11.6852
1898 | COMCHEPK_1G | 1 | North | YES | 0.022157 | 1159 | 1150 | 1159 | 0 | 1.032 | Nuc | 1 | 0.043631 | 0 | 0 | 0 | 0 |  |  | 0.043631 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.022157 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.043631 | 0 | 0 | 0 | 0 |  |  | 0.043631 | 0
344 | MRSSHPRD | 1 | North | YES | 0.022829 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.044303 | 0 | 0 | 0 | 0 |  |  | 0.044303 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.022829 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.044303 | 0 | 0 | 0 | 0 |  |  | 0.044303 | 0
1432 | GRHAMSES_2G | 2 | North | YES | 0.023002 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.044476 | 366 | 366 | 8.4187 | 366 |  |  | 0.044476 | 16.2783
1600 | BARTNWND_1G | 1 | North | YES | 0.023107 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.044581 | 0 | 120 | 2.7728 | 120 |  |  | 0.044581 | 5.3497
1479 | WFCOGEN_1G | 1 | North | YES | 0.023186 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.04466 | 0 | 0 | 0 | 0 |  |  | 0.04466 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.023186 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.04466 | 0 | 0 | 0 | 0 |  |  | 0.04466 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.023186 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.04466 | 0 | 0 | 0 | 0 |  |  | 0.04466 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.023186 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.04466 | 0 | 0 | 0 | 0 |  |  | 0.04466 | 0
60202 | FRNDDRCS | F | West | YES | 0.024527 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.046001 | 0 | 0 |  |  |  |  | 0.046001 | 0
1433 | GRHAMSES_1G | 1 | North | YES | 0.024583 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.046057 | 242 | 242 | 5.9491 | 242 |  |  | 0.046057 | 11.1458
6100 | OKLA7A | EQ | West | YES | 0.024929 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.046403 | 0 | 0 |  |  |  |  | 0.046403 | 0
6752 | OKLA0A | 1 | West | YES | 0.024929 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.046403 | 0 | 649.7 |  |  |  |  | 0.046403 | 30.1481
1442 | COKFIELD_5 | 1 | North | YES | 0.025181 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.046655 | 0 | 165 | 4.1549 | 165 |  |  | 0.046655 | 7.6981
1438 | MESQUITW_2G | 1 | North | YES | 0.025869 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.047343 | 0 | 236 | 6.1051 | 236 |  |  | 0.047343 | 11.173
1437 | MESQUITW_1G | 1 | North | YES | 0.025874 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.047348 | 0 | 400 | 10.3496 | 400 |  |  | 0.047348 | 18.9393
60018 | DSKY1 | 1 | West | YES | 0.026321 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.047795 | 0 | 84 |  |  |  |  | 0.047795 | 4.0148
60017 | ORNNWP1 | 1 | West | YES | 0.026415 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.047889 | 0 | 80 |  |  |  |  | 0.047889 | 3.8311
60000 | DSKY2 | 1 | West | YES | 0.026518 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.047992 | 0 | 76.5 |  |  |  |  | 0.047992 | 3.6714
6016 | SWMESA | 1 | West | YES | 0.026683 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.048157 | 0 | 75 |  |  |  |  | 0.048157 | 3.6118
60003 | KING_NE1A | 1 | West | YES | 0.026683 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.048157 | 0 | 80 |  |  |  |  | 0.048157 | 3.8526
60005 | KING_SE1A | 1 | West | YES | 0.026683 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.048157 | 0 | 40 |  |  |  |  | 0.048157 | 1.9263
38437 | TNSRBNMESA9 | 1 | West | YES | 0.026698 | 37.5 | 0 | 150 |  | 1.02 | Wind | 1 | 0.048172 | 0 | 150 |  |  |  |  | 0.048172 | 7.2258
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.026705 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.048179 | 0 | 80 |  |  |  |  | 0.048179 | 3.8543
60016 | WOODWRD11A | 1 | West | YES | 0.026707 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.048181 | 0 | 80 |  |  |  |  | 0.048181 | 3.8545
60201 | RIO DRCS | F | West | YES | 0.026713 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.048187 | 0 | 0 |  |  |  |  | 0.048187 | 0
332 | RWMILLER01 | 1 | North | YES | 0.026747 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.048221 | 73 | 73 | 1.9525 | 73 |  |  | 0.048221 | 3.5201
333 | RWMILLER02 | 2 | North | YES | 0.026747 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.048221 | 119 | 119 | 3.1829 | 119 |  |  | 0.048221 | 5.7383
334 | RWMILLER03 | 3 | North | YES | 0.026747 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.048221 | 208 | 208 | 5.5634 | 208 |  |  | 0.048221 | 10.03
335 | RWMILLER04 | 4 | North | YES | 0.026747 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.048221 | 102 | 102 | 2.7282 | 102 |  |  | 0.048221 | 4.9186
336 | RWMILLER05 | 5 | North | YES | 0.026747 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.048221 | 101 | 101 | 2.7014 | 101 |  |  | 0.048221 | 4.8703
60007 | KING_SW1A | 1 | West | YES | 0.026805 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.048279 | 0 | 80 |  |  |  |  | 0.048279 | 3.8623
60019 | KING_NW1A | 1 | West | YES | 0.026805 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.048279 | 0 | 80 |  |  |  |  | 0.048279 | 3.8623
1416 | SWETWATR_1G | 1 | West | YES | 0.027065 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.048539 | 30 | 30 |  |  |  |  | 0.048539 | 1.4562
1417 | SWETWATR_2G | 2 | West | YES | 0.027065 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.048539 | 72 | 72 |  |  |  |  | 0.048539 | 3.4948
1418 | SWETWATR_3G | 3 | West | YES | 0.027065 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.048539 | 68 | 68 |  |  |  |  | 0.048539 | 3.3007
1419 | SWETWATR_4G | 4 | West | YES | 0.027065 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.048539 | 61 | 61 |  |  |  |  | 0.048539 | 2.9609
1049 | ROSCOEWI_5 | 1 | West | YES | 0.027205 | 41.8 | 0 | 209 |  | 1.01 | Wind | 1 | 0.048679 | 0 | 209 |  |  |  |  | 0.048679 | 10.1739
1057 | ROSCOEWI_5 | 2 | West | YES | 0.027205 | 25.3 | 0 | 126.5 |  | 1.01 | Wind | 1 | 0.048679 | 0 | 126.5 |  |  |  |  | 0.048679 | 6.1579
1060 | ROSCOEWI_5 | 3 | West | YES | 0.027205 | 39.4 | 0 | 197 | 0 | 1.01 | Wind | 1 | 0.048679 | 0 | 197 |  |  |  |  | 0.048679 | 9.5898
1072 | ROSCOEWI_5 | 4 | West | YES | 0.027205 | 63.6 | 0 | 318 | 0 | 1.01 | Wind | 1 | 0.048679 | 0 | 318 |  |  |  |  | 0.048679 | 15.48
1002 | PBCTAGE_1G | A | West | YES | 0.027665 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.049139 | 66 | 66 |  |  |  |  | 0.049139 | 3.2432
1003 | PBCTBGE_2G | B | West | YES | 0.027665 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.049139 | 66 | 66 |  |  |  |  | 0.049139 | 3.2432
1004 | PBCTCGE_3G | C | West | YES | 0.027665 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.049139 | 67 | 67 |  |  |  |  | 0.049139 | 3.2923
1005 | PBCTDGE_4G | D | West | YES | 0.027665 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.049139 | 68 | 68 |  |  |  |  | 0.049139 | 3.3415
1006 | PBCTEGE_5G | E | West | YES | 0.027665 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.049139 | 67 | 67 |  |  |  |  | 0.049139 | 3.2923
1007 | PB5GEN_6G | 5 | West | YES | 0.027665 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.049139 | 114 | 114 |  |  |  |  | 0.049139 | 5.6019
1008 | PB6GEN_7G | 6 | West | YES | 0.027665 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.049139 | 515 | 515 |  |  |  |  | 0.049139 | 25.3067
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.027682 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.049156 | 0 | 30 |  |  |  |  | 0.049156 | 1.4747
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.027682 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.049156 | 0 | 35 |  |  |  |  | 0.049156 | 1.7205
71051 | L_BITTCR1_1N | W1 | West | YES | 0.027686 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.04916 | 0 | 37.5 |  |  |  |  | 0.04916 | 1.8435
71054 | L_SWEETW1_1N | W1 | West | YES | 0.027686 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.04916 | 0 | 107.5 |  |  |  |  | 0.04916 | 5.2847
71057 | L_SWEETW1_2N | W1 | West | YES | 0.027686 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.04916 | 0 | 135 |  |  |  |  | 0.04916 | 6.6366
71059 | L_SWEETW1_3N | W1 | West | YES | 0.027686 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.04916 | 0 | 119 |  |  |  |  | 0.04916 | 5.8501
71060 | L_SWEETW1_4N | W1 | West | YES | 0.027686 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.04916 | 0 | 105 |  |  |  |  | 0.04916 | 5.1618
1146 | NOTREES_1G | 1 | West | YES | 0.027716 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.04919 | 0 | 149 |  |  |  |  | 0.04919 | 7.3293
11020 | TIEHVSG_1G | 1 | West | YES | 0.027749 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.049223 | 208.2 | 208.2 |  |  |  |  | 0.049223 | 10.2483
11021 | TIEHVCG_1G | 1 | West | YES | 0.027749 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.049223 | 142.1 | 142.1 |  |  |  |  | 0.049223 | 6.9946
11022 | TIEHVCG_2G | 1 | West | YES | 0.027749 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.049223 | 132.4 | 132.4 |  |  |  |  | 0.049223 | 6.5171
11023 | TIEHVCG_3G | 1 | West | YES | 0.027749 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.049223 | 137.4 | 137.4 |  |  |  |  | 0.049223 | 6.7633
11024 | TIEHVCG_4G | 1 | West | YES | 0.027749 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.049223 | 147 | 147 |  |  |  |  | 0.049223 | 7.2358
11025 | TIEHVSG_2G | 1 | West | YES | 0.027749 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.049223 | 213.2 | 213.2 |  |  |  |  | 0.049223 | 10.4944
11001 | NAV1CT | 1 | West | YES | 0.02775 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.049224 | 70.4 | 70.4 |  |  |  |  | 0.049224 | 3.4654
11009 | NAV2CT | 1 | West | YES | 0.02775 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.049224 | 71.4 | 71.4 |  |  |  |  | 0.049224 | 3.5146
11011 | NAV3ST | 1 | West | YES | 0.02775 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.049224 | 92.8 | 92.8 |  |  |  |  | 0.049224 | 4.568
11012 | NAV4CT | 1 | West | YES | 0.02775 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.049224 | 80 | 80 |  |  |  |  | 0.049224 | 3.9379
11013 | NAV5CT | 1 | West | YES | 0.02775 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.049224 | 80 | 80 |  |  |  |  | 0.049224 | 3.9379
11014 | NAV6ST | 1 | West | YES | 0.02775 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.049224 | 115 | 115 |  |  |  |  | 0.049224 | 5.6608
1045 | CALENG1G_1G | 1 | West | YES | 0.027812 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.049286 | 0 | 0 |  |  |  |  | 0.049286 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.027812 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.049286 | 0 | 0 |  |  |  |  | 0.049286 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.027812 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.049286 | 0 | 0 |  |  |  |  | 0.049286 | 0
1058 | LONGSHORE_5 | 1 | West | YES | 0.027816 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.04929 | 0 | 150 |  |  |  |  | 0.04929 | 7.3935
1058 | LONGSHORE_5 | 2 | West | YES | 0.027816 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.04929 | 0 | 220 |  |  |  |  | 0.04929 | 10.8438
1058 | LONGSHORE_5 | 3 | West | YES | 0.027816 | 23.4 | 0 | 117 |  | 1.01 | Wind | 1 | 0.04929 | 0 | 117 |  |  |  |  | 0.04929 | 5.7669
1328 | OCOTILLO_1G | 1 | West | YES | 0.027973 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.049447 | 0 | 58 |  |  |  |  | 0.049447 | 2.8679
1333 | MCDDONAL_8 | 1 | West | YES | 0.028002 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.049476 | 0 | 214.2 |  |  |  |  | 0.049476 | 10.5978
1326 | STANTONW_8 | 1 | West | YES | 0.028015 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.049489 | 0 | 100.5 |  |  |  |  | 0.049489 | 4.9737
1170 | AIRLAMESA_1G | 1 | West | YES | 0.028119 | 0 | 0 | 180 |  | 1 | Wind | 1 | 0.049593 | 0 | 180 |  |  |  |  | 0.049593 | 8.9268
1037 | MORGAN5G_5G | 5 | West | YES | 0.028179 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.049653 | 137 | 137 |  |  |  |  | 0.049653 | 6.8025
1039 | MRGNAG_1G | A | West | YES | 0.028179 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.049653 | 69 | 69 |  |  |  |  | 0.049653 | 3.4261
1040 | MRGNBG_2G | B | West | YES | 0.028179 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.049653 | 71 | 71 |  |  |  |  | 0.049653 | 3.5254
1041 | MRGNCG_3G | C | West | YES | 0.028179 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.049653 | 70 | 70 |  |  |  |  | 0.049653 | 3.4757
1042 | MRGNDG_4G | D | West | YES | 0.028179 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.049653 | 68 | 68 |  |  |  |  | 0.049653 | 3.3764
1043 | MRGNEG_5G | E | West | YES | 0.028179 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.049653 | 70 | 70 |  |  |  |  | 0.049653 | 3.4757
1044 | MRGNFG_6G | F | West | YES | 0.028179 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.049653 | 66 | 66 |  |  |  |  | 0.049653 | 3.2771
1302 | COYOTEWG_8 | 1 | West | YES | 0.028227 | 45 | 0 | 225 |  | 1.01 | Wind | 1 | 0.049701 | 0 | 225 |  |  |  |  | 0.049701 | 11.1828
1301 | BULLCREK_8 | 1 | West | YES | 0.028304 | 36 | 0 | 180 | 0 | 1.017 | Wind | 1 | 0.049778 | 0 | 180 |  |  |  |  | 0.049778 | 8.9601
1327 | WILDHRSE_1G | 1 | West | YES | 0.028315 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.049789 | 0 | 120 |  |  |  |  | 0.049789 | 5.9747
1360 | GUNSIGHT_8 | 1 | West | YES | 0.028329 | 24 | 0 | 120 | 0 | 1.01 | Wind | 1 | 0.049803 | 0 | 120 |  |  |  |  | 0.049803 | 5.9764
1068 | SCURRYCW_1G | 1 | West | YES | 0.028375 | 28.2 | 1.3 | 141 |  | 1.01 | Wind | 1 | 0.049849 | 0 | 141 |  |  |  |  | 0.049849 | 7.0287
1073 | SCURRYCW_2G | 2 | West | YES | 0.028375 | 24 | 0 | 120 | 0 | 1.017 | Wind | 1 | 0.049849 | 0 | 120 |  |  |  |  | 0.049849 | 5.9819
1061 | CIELOGEN_1G | 1 | West | YES | 0.028377 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.049851 | 0 | 99 |  |  |  |  | 0.049851 | 4.9353
1062 | CIELOGEN_2G | 1 | West | YES | 0.028377 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.049851 | 0 | 61 |  |  |  |  | 0.049851 | 3.0409
1069 | KINDERMG_1G | 1 | West | YES | 0.028377 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.049851 | 0 | 0 |  |  |  |  | 0.049851 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.028377 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.049851 | 0 | 0 |  |  |  |  | 0.049851 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.028377 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.049851 | 0 | 0 |  |  |  |  | 0.049851 | 0
6637 | SNYDERW1A | 1 | West | YES | 0.028402 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.049876 | 0 | 63 |  |  |  |  | 0.049876 | 3.1422
36998 | RDCNYNG1 | 1 | West | YES | 0.028468 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.049942 | 0 | 84 |  |  |  |  | 0.049942 | 4.1951
60052 | WILDHRS11A | 1 | West | YES | 0.02847 | 25.3 | 0 | 126.5 | 0 | 1.005 | Wind | 1 | 0.049944 | 0 | 126.5 |  |  |  |  | 0.049944 | 6.3179
60053 | WILDHRS21A | 1 | West | YES | 0.02847 | 7.8 | 0 | 39 | 0 | 1.025 | Wind | 1 | 0.049944 | 0 | 39 |  |  |  |  | 0.049944 | 1.9478
1320 | BSP 1 | 1 | West | YES | 0.028582 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.050056 | 0 | 0 |  |  |  |  | 0.050056 | 0
60081 | WHRLWIND1A | 1 | West | YES | 0.028603 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.050077 | 0 | 60 |  |  |  |  | 0.050077 | 3.0046
6144 | MCADOO1A | 1 | West | YES | 0.028867 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.050341 | 0 | 150 |  |  |  |  | 0.050341 | 7.5512
60058 | BUFF_GAP1A | 1 | West | YES | 0.029033 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.050507 | 0 | 120 |  |  |  |  | 0.050507 | 6.0609
60060 | CIRELLO | 1 | West | YES | 0.029033 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.050507 | 0 | 233 |  |  |  |  | 0.050507 | 11.7682
60063 | BUFF_GAP1B | 1 | West | YES | 0.029033 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.050507 | 0 | 170.2 |  |  |  |  | 0.050507 | 8.5963
60066 | H_HOLLOW1A | 1 | West | YES | 0.029033 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.050507 | 0 | 222 |  |  |  |  | 0.050507 | 11.2126
60068 | HHOLLOW21A | 1 | West | YES | 0.029033 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.050507 | 0 | 184 |  |  |  |  | 0.050507 | 9.2933
60070 | HHOLLOW31A | 1 | West | YES | 0.029033 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.050507 | 0 | 224 |  |  |  |  | 0.050507 | 11.3136
60072 | HHOLLOW41A | 1 | West | YES | 0.029033 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.050507 | 0 | 115 |  |  |  |  | 0.050507 | 5.8083
76031 | L_GASCCR1_1N | W1 | West | YES | 0.02916 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.050634 | 0 | 150 |  |  |  |  | 0.050634 | 7.5951
1349 | WESTXWIN_1G | 1 | West | YES | 0.029353 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.050827 | 0 | 6.6 |  |  |  |  | 0.050827 | 0.33546
1350 | NWPWRG1_1G | 1 | West | YES | 0.029353 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.050827 | 0 | 34.3 |  |  |  |  | 0.050827 | 1.7434
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.029418 | 110 | 0 | 550 | 0 | 1.02 | Wind | 1 | 0.050892 | 0 | 550 |  |  |  |  | 0.050892 | 27.9907
1343 | TRENTIPP_8 | 1 | West | YES | 0.031074 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.052548 | 0 | 150 |  |  |  |  | 0.052548 | 7.8822
1354 | AEPWIND_8 | 1 | West | YES | 0.031074 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.052548 | 0 | 101 |  |  |  |  | 0.052548 | 5.3074
1643 | SLSTR1PP_1G | 1 | North | YES | 0.034716 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.05619 | 0 | 60 | 2.083 | 60 |  |  | 0.05619 | 3.3714
60057 | CALLAHAN1A | 1 | West | YES | 0.035498 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.056972 | 0 | 114 |  |  |  |  | 0.056972 | 6.4948
6407 | TURKTRAK1A | 1 | West | YES | 0.040325 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.061799 | 0 | 169.5 |  |  |  |  | 0.061799 | 10.475

## Zones
Houston | -1
North | 1
South | -1
West | 1
SET UP AREA, copy & paste values to cell B1
Source | North |  | N to H | N to W | N to S | W to N | S to N | W to S
Sink | South | Houston | -1 | 1 | -1 | -1 | 1 | -1
|  | North | 1 | 1 | 1 | -1 | -1 | -1
|  | South | -1 | 1 | -1 | -1 | 1 | -1
|  | West | 1 | -1 | 1 | 1 | -1 | 1
|  | Source | North | North | North | West | South | West
|  | Sink | Houston | West | South | North | North | South

## Tech
Number of Bus | Name of Bus | Tech Type
238 | BOSQUESW505 | CC
239 | BOSQUESW502 | GGT
244 | WHITNYDM01 | Hydro
245 | WHITNYDM02 | Hydro
247 | BOSQUESW501 | GGT
251 | BOSQUESW803 | CC
253 | BOSQUESW804 | CC
332 | RWMILLER01 | GST
333 | RWMILLER02 | GST
334 | RWMILLER03 | GST
335 | RWMILLER04 | GST
336 | RWMILLER05 | GST
344 | MRSSHPRD | Hydro
345 | MRSSHPRD01 | Hydro
366 | JNSNCNTY802 | Cogen
367 | JNSNCNTY802 | Cogen
503 | NTHTEXAS01 | GST
504 | NTHTEXAS02 | GST
505 | NTHTEXAS03 | GST
580 | JCKCNTY801 | CC
581 | JCKCNTY802 | CC
582 | JCKCNTY803 | CC
728 | WOLFRIDGE801 | Wind
837 | NEWMAN_G5 | GST
842 | OLINGER_G1 | GST
843 | OLINGER_G2 | GST
844 | OLINGER_G3 | GST
845 | OLINGER_G4 | GGT
923 | SPENCER_G4 | GST
924 | SPENCER_G5 | GST
948 | STEAM1 | GST
949 | STEAM2 | GST
950 | STEAM3 | GST
990 | GIBN_CREK_G1 | LIGCO
1002 | PBCTAGE_1G | GGT
1003 | PBCTBGE_2G | GGT
1004 | PBCTCGE_3G | GGT
1005 | PBCTDGE_4G | GGT
1006 | PBCTEGE_5G | GGT
1007 | PB5GEN_6G | GST
1008 | PB6GEN_7G | GST
1037 | MORGAN5G_5G | GST
1039 | MRGNAG_1G | GGT
1040 | MRGNBG_2G | GGT
1041 | MRGNCG_3G | GGT
1042 | MRGNDG_4G | GGT
1043 | MRGNEG_5G | GGT
1044 | MRGNFG_6G | GGT
1045 | CALENG1G_1G | Cogen
1046 | CALENG2G_2G | Cogen
1047 | CALENG3G_3G | Cogen
1049 | ROSCOEWI_5 | Wind
1057 | ROSCOEWI_5 | Wind
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1060 | ROSCOEWI_5 | Wind
1061 | CIELOGEN_1G | Wind
1062 | CIELOGEN_2G | Wind
1068 | SCURRYCW_1G | Wind
1069 | KINDERMG_1G | Cogen
1070 | KINDERMG_2G | Cogen
1071 | KINDERMG_3G | Cogen
1072 | ROSCOEWI_5 | Wind
1073 | SCURRYCW_2G | Wind
1146 | NOTREES_1G | Wind
1170 | AIRLAMESA_1G | Wind
1301 | BULLCREK_8 | Wind
1302 | COYOTEWG_8 | Wind
1320 | BSP 1 | Cogen
1326 | STANTONW_8 | Wind
1327 | WILDHRSE_1G | Wind
1328 | OCOTILLO_1G | Wind
1333 | MCDDONAL_8 | Wind
1343 | TRENTIPP_8 | Wind
1349 | WESTXWIN_1G | Wind
1350 | NWPWRG1_1G | Wind
1354 | AEPWIND_8 | Wind
1360 | GUNSIGHT_8 | Wind
1416 | SWETWATR_1G | CC
1417 | SWETWATR_2G | CC
1418 | SWETWATR_3G | CC
1419 | SWETWATR_4G | CC
1432 | GRHAMSES_2G | GST
1433 | GRHAMSES_1G | GST
1437 | MESQUITW_1G | Wind
1438 | MESQUITW_2G | Wind
1442 | COKFIELD_5 | Wind
1453 | WCPWRCO_1G | CC
1454 | WCPWRCO_2G | CC
1455 | WCPWRCO_3G | CC
1479 | WFCOGEN_1G | Cogen
1479 | WFCOGEN_1G | Cogen
1482 | WFCOGEN_2G | Cogen
1482 | WFCOGEN_2G | Cogen
1600 | BARTNWND_1G | Wind
1643 | SLSTR1PP_1G | Wind
1675 | PEC_1G | Cogen
1676 | PEC_2G | Cogen
1677 | PEC_3G | Cogen
1678 | LAMARPWR_1G | CC
1679 | LAMARPWR_2G | CC
1680 | LAMARPWR_3G | CC
1681 | LAMARPWR_4G | CC
1682 | LAMARPWR_5G | CC
1683 | LAMARPWR_6G | CC
1687 | VALLEY_1G | GST
1688 | VALLEY_2G | GSC
1689 | VALLEY_3G | GST
1701 | MOSES_1G | LIGCO
1702 | MOSES_2G | LIGCO
1703 | MOSES_3G | LIGCO
1861 | EAGLEMNT_1G | GST
1862 | EAGLEMNT_2G | GST
1863 | EAGLEMNT_3G | GST
1877 | WLFHOLW_1G | CC
1878 | WLFHOLW_2G | CC
1879 | WLFHOLW_3G | CC
1889 | DECRDOVA_1G | GSC
1892 | DECRDOVA_2G | GGT
1893 | DECRDOVA_3G | GGT
1894 | DECRDOVA_4G | GGT
1895 | DECRDOVA_5G | GGT
1898 | COMCHEPK_1G | Nuc
1899 | COMCHEPK_2G | Nuc
1937 | MDLTHELP_5G | CC
1938 | MDLTHELP_6G | CC
1941 | MDLTHELP_1G | CC
1942 | MDLTHELP_2G | CC
1943 | MDLTHELP_3G | CC
1944 | MDLTHELP_4G | CC
1945 | HANDLEY_1G | GST
1946 | HANDLEY_2G | GST
1947 | HANDLEY_3G | GST
1948 | HANDLEY_4G | GST
1949 | HANDLEY_5G | GST
2371 | COLLIN_1G | GST
2381 | NTHLK1_G | GST
2382 | NTHLK2_G | GST
2383 | NTHLK3_G | GST
2413 | MTCK6_G | GST
2414 | MTCK7_G | GST
2417 | MTCK8_G | GSC
2418 | MTCK2_G | GSC
2419 | MTCK3_G | GSC
2451 | LKHB1_G | GST
2452 | LKHB2_G | GST
3097 | MARTLAKE_1G | LIGCO
3098 | MARTLAKE_2G | LIGCO
3099 | MARTLAKE_3G | LIGCO
3107 | STRYKER_1G | GST
3108 | STRYKER_2G | GST
3113 | LUFKINWB_1G | Trash
3126 | TRINIDAD_6G | GST
3348 | CHAMPION_1G | Cogen
3381 | BBRN_1G | LIGCO
3382 | BBRN_2G | LIGCO
3403 | THOUSE_1G | GSC
3404 | THOUSE_2G | GSC
3416 | LAKE_CRK1_G | GST
3417 | LAKE_CRK2_G | GST
3432 | SANDOW_4G | LIGCO
5026 | BRAUNIG_VHB1 | GST
5027 | BRAUNIG_VHB2 | GST
5028 | BRAUNIG_VHB3 | GST
5031 | BRA_VHBCT1 | GST
5032 | BRA_VHBCT2 | GST
5033 | BRA_VHBCT3 | GST
5034 | BRA_VHBCT4 | GST
5111 | CALAVER_JTD1 | LIGCO
5112 | CALAVER_JTD2 | LIGCO
5264 | LEON_LCP3G3 | GST
5265 | LEON_LCP4G4 | GST
5266 | LEON_LCPCT1 | GGT
5267 | LEON_LCPCT2 | GGT
5268 | LEON_LCPCT3 | GGT
5269 | LEON_LCPCT4 | GGT
5396 | CALAVER_OWS1 | GST
5397 | CALAVER_OWS2 | GST
5401 | CALAVER_JKS1 | LIGCO
5436 | TUTTL_WBT1G1 | GST
5438 | TUTTL_WBT3G3 | GST
5439 | TUTTL_WBT4G4 | GST
5476 | BRA_AVR1_CT1 | CC
5477 | BRA_AVR1_ST1 | CC
5478 | BRA_AVR1_CT2 | CC
5503 | RAYBURNGEN3 | GST
5505 | RAYBURNGEN1 | GGT
5506 | RAYBURNGEN2 | GGT
5508 | RAYBURNCC9 | CC
5509 | RAYBURNCC10 | CC
5511 | RAYBURNCC7 | CC
5512 | RAYBURNCC8 | CC
5728 | FALCONHYDRO2 | Hydro
5729 | FALCONHYDRO3 | Hydro
5890 | PEARSALLGEN1 | GST
5891 | PEARSALLGEN2 | GST
5892 | PEARSALLGEN3 | GST
5903 | SANMIGUELGEN | LIGCO
5911 | STP_GN1___1 | Nuc
5912 | STP_GN2___2 | Nuc
5925 | DCEAST | DCTie
5932 | SI_RAY9 | CC
5933 | SI_RAY6 | GST
5934 | SI_RAY5 | GST
5935 | SI_RAY10 | CC
6016 | SWMESA | Wind
6100 | OKLA7A | DCTie
6144 | MCADOO1A | Wind
6407 | TURKTRAK1A | Wind
6637 | SNYDERW1A | Wind
6752 | OKLA0A | LIGCO
6948 | DENISNDM | Hydro
6948 | DENISNDM | Hydro
7000 | L_FERGUS1_1Y | GSC
7004 | L_SIMGID1_1Y | GST
7005 | L_SIMGID1_2Y | GST
7006 | L_SIMGID1_3Y | GST
7007 | L_LOSTPI1_1Y | CC
7008 | L_LOSTPI1_2Y | CC
7009 | L_LOSTPI1_3Y | CC
7010 | L_FPPYD11_1Y | LIGCO
7011 | L_FPPYD11_2Y | LIGCO
7012 | L_FPPYD21_3Y | LIGCO
7014 | L_HAYSEN1_1Y | CC
7015 | L_HAYSEN1_2Y | CC
7016 | L_HAYSEN1_3Y | CC
7017 | L_HAYSEN1_4Y | CC
7020 | L_AUSTPL1_1Y | Hydro
7020 | L_AUSTPL1_1Y | Hydro
7022 | L_BUCHAN1_1Y | Hydro
7023 | L_BUCHAN1_2Y | Hydro
7024 | L_BUCHAN1_3Y | Hydro
7026 | L_INKSDA1_1Y | Hydro
7028 | L_MARBFA1_1Y | Hydro
7029 | L_MARBFA1_2Y | Hydro
7031 | L_MARSFO1G1Y | Hydro
7032 | L_MARSFO1G2Y | Hydro
7033 | L_MARSFO1G3Y | Hydro
7035 | L_WIRTZ_1G1Y | Hydro
7036 | L_WIRTZ_1G2Y | Hydro
7038 | L_DELAWA1_1Y | Wind
7038 | L_DELAWA1_1Y | Wind
7303 | L_WPPGS12_1Y | GGT
7303 | L_WPPGS12_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7487 | L_CANYHY8_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7609 | L_SCHUMA8_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7800 | L_GUADGE1_1Y | CC
7801 | L_GUADGE1_2Y | CC
7802 | L_GUADGE1_3Y | CC
7803 | L_GUADGE1_4Y | CC
7804 | L_GUADGE1_5Y | CC
7805 | L_GUADGE1_6Y | CC
7807 | L_BASTEN1_1Y | CC
7808 | L_BASTEN1_2Y | CC
7809 | L_BASTEN1_3Y | CC
7810 | L_RIONOG1G1Y | CC
7811 | L_RIONOG1G2Y | CC
7812 | L_RIONOG1G3Y | CC
7813 | L_RIONOG1S1Y | CC
8032 | AMISTADHYD1 | Hydro
8033 | AMISTADHYD2 | Hydro
8048 | FALCONHYDRO1 | Hydro
8066 | DUP1V#1 | Cogen
8134 | FOR #1 | Cogen
8138 | FOR #2 | Cogen
8139 | JOS #1 | GST
8147 | UCAR #2 | Cogen
8148 | UCAR #1 | Cogen
8153 | FOR #3 | Cogen
8154 | FOR #4 | Cogen
8155 | FOR #5 | Cogen
8156 | FOR #6 | Cogen
8157 | FOR #7 | Cogen
8161 | COLETO0A | LIGCO
8173 | VICEC51A | CC
8174 | VICEC61A | CC
8189 | CUECPL2A | Cogen
8262 | ELPS | Hydro
8285 | LAR #1 | GST
8287 | LAR #2 | GST
8288 | LAR #3 | GST
8388 | BATES0A | GST
8393 | BATES0B | GST
8437 | NUECES_B0C | GST
8438 | NUECES_B0B | GST
8442 | NUECES_B0A | GST
8456 | COSW#1 | Cogen
8457 | COSW#2 | Cogen
8459 | B_DAVIS0B | GSC
8460 | B_DAVIS0A | GSC
8461 | KOCH_UP0A | Cogen
8506 | VAL #1 | Cogen
8507 | VAL #2 | Cogen
8511 | OXY_CC0A | Cogen
8517 | CELANEBI0A | Cogen
8560 | CNOPGT1 | Cogen
8561 | CNOPGT2 | Cogen
8562 | CNOPST1 | Cogen
8926 | LGE_GT10A | Cogen
8927 | LGE_GT20A | Cogen
8928 | LGE_STG0A | Cogen
8930 | ICPGN10A | Cogen
8931 | ICPGN20A | Cogen
8932 | ICPGN30A | Cogen
8933 | FGNTS001 | CC
8934 | FGNTS101 | CC
8935 | FGNTS201 | CC
8936 | MVGN#1 | CC
8937 | MVGN#2 | CC
8938 | MVGN#3 | CC
8981 | HECN1 | CC
8982 | HECN2 | CC
8983 | HECN3 | CC
9000 | DECKR_G1 | GST
9001 | DECKR_G2 | GST
9002 | DECKR_G3 | GGT
9003 | DECKR_G4 | GGT
9004 | DECKR_G5 | GGT
9005 | DECKR_G6 | GGT
9016 | SANDH_G1 | GGT
9017 | SANDH_G2 | GGT
9018 | SANDH_G3 | GGT
9019 | SANDH_G4 | GGT
9020 | SANDHG5A | CC
9021 | SANDHG5C | CC
11001 | NAV1CT | CC
11009 | NAV2CT | CC
11011 | NAV3ST | CC
11012 | NAV4CT | CC
11013 | NAV5CT | CC
11014 | NAV6ST | CC
11020 | TIEHVSG_1G | CC
11021 | TIEHVCG_1G | CC
11022 | TIEHVCG_2G | CC
11023 | TIEHVCG_3G | CC
11024 | TIEHVCG_4G | CC
11025 | TIEHVSG_2G | CC
11691 | KMICHICT1_G | CC
11692 | KMICHICT2_G | CC
11693 | KMICHIST3_G | CC
11694 | KMICHICT4_G | CC
11695 | KMICHICT5_G | CC
11696 | KMICHIST6_G | CC
12322 | ENNSTRAC_1G | CC
12323 | ENNSTRAC_2G | CC
12411 | FPLEFR1A_G | CC
12412 | FPLEFR1B_G | CC
12413 | FPLEFR1C_G | CC
12414 | FPLEFR1S_G | CC
12421 | FPLEFR2A_G | CC
12422 | FPLEFR2B_G | CC
12423 | FPLEFR2C_G | CC
12424 | FPLEFR2S_G | CC
12440 | PARKD_1SVC8 | GST
12449 | PARKD_2SVC8 | GST
13116 | TGATEWAY_1G | CC
13117 | TGATEWAY_2G | CC
13118 | TGATEWAY_3G | CC
13119 | TGATEWAY_4G | CC
13131 | CALFREST_1G | CC
13132 | CALFREST_2G | CC
13133 | CALFREST_3G | CC
13134 | CALFREST_4G | CC
13135 | CALFREST_5G | CC
13136 | CALFREST_6G | CC
13432 | SANDOW_5G | LIGCO
32798 | BRYN_TAMUGEN | GST
32883 | BRYN_DNSBY3 | GST
32884 | BRYN_DNSBY13 | GST
32886 | BRYN_ATKINS3 | GST
32887 | BRYN_ATKINS6 | GST
32888 | BRYN_ATKINS7 | GGT
32890 | BRYN_ATKINS4 | GST
32891 | BRYN_ATKINS5 | GST
32892 | BRYN_DNSBY14 | GST
36998 | RDCNYNG1 | Wind
38332 | TNWDWRDU2_8 | Wind
38437 | TNSRBNMESA9 | Wind
38580 | TNBP_CGN1_8 | Cogen
38590 | TNBP_CGN2_8 | Cogen
38600 | TNBP_CGN3_8 | Cogen
38611 | TNBPAMCG1_8 | Cogen
38612 | TNBPAMCG2_8 | Cogen
38613 | TNBPAMCG3_8 | Cogen
38614 | TNBPAMCG4_8 | Cogen
38615 | TNBPAMCG5_8 | Cogen
38690 | TNBP_CGN4_8 | Cogen
38711 | TNTXCTY1CG8 | Cogen
38712 | TNTXCTY2CG8 | Cogen
38713 | TNTXCTY3CG8 | Cogen
38714 | TNTXCTY4CG8 | Cogen
39190 | TNSLCGN1__8 | Cogen
39470 | TNDOWCGNSG8 | Cogen
39480 | TNDOWCGNGG8 | Cogen
39760 | TNSCLP1___8 | Cogen
39770 | TNSCLP2___8 | Cogen
39775 | TNSCLP4___8 | Cogen
39790 | TNSCLP3___8 | Cogen
39960 | TNTNPONE_18 | LIGCO
39970 | TNTNPONE_28 | LIGCO
48500 | APD_GT1_8005 | Cogen
48510 | AK_GT1__8040 | Cogen
48511 | LPE_GT1_8070 | GGT
48512 | LPE_GT2_8075 | GGT
48513 | LPE_GT3_8080 | GGT
48514 | LPE_GT4_8085 | GGT
48520 | BSF_GT1_8070 | Cogen
48520 | BSF_GT1_8070 | Cogen
48521 | BVE_GT1_GT1 | CC
48522 | BVE_GT2_5035 | CC
48523 | BVE_ST1_GN1 | CC
48531 | BYU_GT1_8075 | Cogen
48532 | BYU_GT2_8055 | Cogen
48533 | BYU_GT3_8060 | Cogen
48534 | BYU_GT4_8065 | Cogen
48551 | CAL_GT1_8045 | Cogen
48552 | CAL_ST1_8000 | Cogen
48561 | CTL_GT2_8130 | Cogen
48562 | CTL_GT3_8135 | Cogen
48563 | CTL_GT4_8140 | Cogen
48564 | CTL_GN1_8145 | Cogen
48565 | CTL_GN2_8155 | Cogen
48581 | CBY_GN1_1 | GSC
48582 | CBY_GN2_2 | GSC
48583 | CBY_GT4_1 | GSC
48584 | CBY_GT4_2 | CC
48585 | CBY_ST4_1 | CC
48591 | CHE_GT2_5030 | Cogen
48593 | CHE_GT1_8015 | Cogen
48594 | CHE_GN4_8025 | Cogen
48595 | BTE_GT2_8075 | CC
48596 | BTE_GT3_8045 | CC
48597 | BTE_GT4_8055 | CC
48598 | BTE_ST1_8070 | CC
48611 | DIB_GT1_8080 | Cogen
48612 | DIB_GT2_8075 | Cogen
48613 | DIB_ST1_8085 | Cogen
48614 | DIB_GT3_8090 | Cogen
48641 | DPEC_GT15040 | CC
48642 | DPEC_GT25025 | CC
48643 | DPEC_GT35010 | CC
48644 | DPEC_GT45070 | CC
48645 | DPEC_ST55065 | CC
48651 | EP_1_2 | Cogen
48651 | EP_1_2 | Cogen
48671 | FTR_GT1_5105 | CC
48672 | FTR_GT2_5110 | CC
48673 | FTR_GT3_5085 | CC
48674 | FTR_CN4_5095 | CC
48690 | GBY_GN5_5 | GSC
48691 | GBY_73741085 | GGT
48691 | GBY_73741085 | GGT
48692 | GBY_81821075 | GGT
48692 | GBY_81821075 | GGT
48693 | GBY_83841065 | GGT
48693 | GBY_83841065 | GGT
48721 | LEG_1___1 | LIGCO
48722 | LEG_2___2 | LIGCO
48730 | MNS_GT | Cogen
48731 | CBE_GT1 | CC
48732 | CBE_GT2 | CC
48733 | CBE_ST12 | CC
48734 | CBE_GT3 | CC
48735 | CBE_GT4 | CC
48736 | CBE_ST34 | CC
48740 | PSG_GN2_8050 | Cogen
48741 | PSG_GT2_8040 | Cogen
48742 | PSG_GT3_8060 | Cogen
48761 | PR_GT1__9040 | Cogen
48772 | PHR_GN2_2 | GSC
48791 | PSA_GT1_8160 | Cogen
48792 | PSA_GT2_8155 | Cogen
48793 | PSA_GT3_8150 | Cogen
48794 | PSA_GT4_8145 | Cogen
48795 | PSA_GT5_8140 | Cogen
48796 | PSA_GN1_8165 | Cogen
48797 | PSA_GT6_8135 | Cogen
48811 | CVC_GT3_5045 | Cogen
48812 | CVC_GT2_5020 | Cogen
48813 | CVC_GT1_5035 | Cogen
48814 | CVC_ST5_5040 | Cogen
48815 | CVC_GT4_8005 | Cogen
48820 | SHELLG1_3015 | Cogen
48821 | SHELLG2 | Cogen
48822 | SHELLG3_3020 | Cogen
48822 | SHELLG3_3020 | Cogen
48841 | SJS_GT1_GT1 | Cogen
48842 | SJS_GT2_GT2 | Cogen
48845 | SOL_GT1 | Solar
48851 | SRB_GN1_1 | GST
48852 | SRB_GN2_2 | GST
48853 | SRB_GN3_3 | GST
48854 | SRB_GN4_4 | GST
48855 | SRB_GT211035 | GGT
48855 | SRB_GT211035 | GGT
48873 | THW_ST3_ST_3 | CC
48874 | THW_ST4_ST_4 | CC
48875 | THW_3132 | CC
48875 | THW_3132 | CC
48877 | THW_3334 | CC
48877 | THW_3334 | CC
48879 | THW_4142 | CC
48879 | THW_4142 | CC
48881 | THW_4344 | CC
48881 | THW_4344 | CC
48883 | THW_GT1_GT_1 | GGT
48885 | THW_5152 | GGT
48885 | THW_5152 | GGT
48886 | THW_5354 | GGT
48886 | THW_5354 | GGT
48887 | THW_5556 | GGT
48887 | THW_5556 | GGT
48911 | TGF_GT1_8000 | Cogen
48921 | WAP_GN1_1 | GST
48922 | WAP_GN2_2 | GST
48923 | WAP_GN3_3 | GST
48924 | WAP_GN4_4 | GSC
48925 | WAP_GN5_5 | LIGCO
48926 | WAP_GN6_6 | LIGCO
48927 | WAP_GN7_7 | LIGCO
48928 | WAP_GN8_8 | LIGCO
48929 | WAPGT21_GT1 | GGT
49803 | EXN_15GT | Cogen
49804 | EXN_16GT | Cogen
49805 | EXN_17GT | Cogen
49826 | EXN938GT | Cogen
49828 | EXN941GT | Cogen
49829 | EXN942GT | Cogen
49830 | EXN943GT | Cogen
49831 | EXN944GT | Cogen
49832 | EXN945GT | Cogen
49837 | EXN_GT | Cogen
49838 | EXN_14GT | Cogen
49851 | DOW17000 | Cogen
49858 | DOW38100 | Cogen
49859 | DOW38200 | Cogen
49860 | DOW38300 | Cogen
49862 | DOW39100 | Cogen
49863 | DOW39200 | Cogen
49865 | DOW41000 | Cogen
49866 | DOW42000 | Cogen
49869 | DOW49000 | Cogen
49870 | DOW61000 | Cogen
49871 | DOW62000 | Cogen
49872 | DOW63000 | Cogen
49873 | DOW64000 | Cogen
49876 | DOW65000 | Cogen
49877 | DOW66000 | Cogen
49878 | DOW67000 | Cogen
49882 | DOW81000 | Cogen
49884 | DOW82000 | Cogen
49885 | DOW83000 | Cogen
49886 | DOW84000 | Cogen
60000 | DSKY2 | Wind
60003 | KING_NE1A | Wind
60005 | KING_SE1A | Wind
60007 | KING_SW1A | Wind
60016 | WOODWRD11A | Wind
60017 | ORNNWP1 | Wind
60018 | DSKY1 | Wind
60019 | KING_NW1A | Wind
60052 | WILDHRS11A | Wind
60053 | WILDHRS21A | Wind
60057 | CALLAHAN1A | Wind
60058 | BUFF_GAP1A | Wind
60060 | CIRELLO | Wind
60063 | BUFF_GAP1B | Wind
60066 | H_HOLLOW1A | Wind
60068 | HHOLLOW21A | Wind
60070 | HHOLLOW31A | Wind
60072 | HHOLLOW41A | Wind
60081 | WHRLWIND1A | Wind
60201 | RIO DRCS | AVR
60202 | FRNDDRCS | AVR
71051 | L_BITTCR1_1N | Wind
71054 | L_SWEETW1_1N | Wind
71057 | L_SWEETW1_2N | Wind
71059 | L_SWEETW1_3N | Wind
71060 | L_SWEETW1_4N | Wind
76031 | L_GASCCR1_1N | Wind
76091 | L_DIVIDE1_1N | Wind
80003 | MILHWYS | AVR
80010 | EPLVT1 | AVR
80012 | LAR | DCTie
80051 | FOR #8 | Cogen
80052 | FOR #9 | Cogen
80053 | FOR #10 | Cogen
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80137 | CSDR89 | DCTie
80137 | CSDR89 | DCTie
80138 | CSDR7 | DCTie
80139 | CSDR56 | DCTie
80139 | CSDR56 | DCTie
80140 | CSDR11 | DCTie
80180 | PNSCALT11A | Wind
80180 | PNSCALT11A | Wind
80181 | PNSCALT21A | Wind
80181 | PNSCALT21A | Wind
80223 | REYSHR G | Cogen
80224 | VISTRONG1 | Cogen
80225 | VISTRONG2 | Cogen
80226 | ALCOA G | Cogen
80227 | AIRCO G | Cogen
80265 | LARECU40A | GGT
80266 | LARECU50A | GGT
88198 | BEEVILLE | AVR
88253 | HAMILTON | BLT
88299 | ZAPATA | BLT
88508 | FALFURRI | AVR