## Set up
Step 1 | Go to the Zones worksheet in this workbook. Make sure that the source and sink zones are set correctly and the "1"s and "-1"s are correct |  |  |  | Summary of Key Data points | Value
[5 empty] | File Description: Cont_ TempleSS to LakeCreek and TemplePEC to Tradinghouse OL_ Evant to Goldthwaite | Cont_ TempleSS to LakeCreek and TemplePEC to Tradinghouse OL_ Evant to Goldthwaite
Step 2 | Open Dennis' file that needs to have the data transferred, same file that is listed in cell K29 |  |  |  | Number of units | 624
[5 empty] | Dec Concentrated Generation | 283.5
Step 3 | Copy columns J:X from an old Dennis' Sheet to the new sheet (if first round of a new alaysis) |  |  |  | Dec Line weighted impact | 18.102
[5 empty] | Dec PTDF | 0.063852
Step 4 | Mark the contingencies and monitored element set by a "y" in column K of Dennis' sheet, if there are a match on the filename use something to make unique |  |  |  | Dec Concentration | 1.6095
[5 empty] | Inc Concentrated Generation | 423.3
Step 5 | Enter Dennis' file name into cell K29 |  |  |  | Inc Line weighted impact | 33.5289
[5 empty] | Inc PTDF | 0.079208
Step 6 | click the step one button |  |  |  | Inc Concentartion | 1.9966
[5 empty] | Source Zonal weighted AWGSF | 0.015906
Step 7 | Enter the line ratings in Dennis' workbook, the Input worksheet, in the cells |  |  |  | Sink Zonal weighted AWGSF | -0.023766
| X6:X30, or to the end of the selected list. |  |  |  | Source - Sink PTDF | 0.039673
[5 empty] | OL Line Rating (MW) | 128
Step 8 | Check to see that the number of generators in Dennis' file matches the length |  |  |  | Source Zone (diagnostic) | North
| of the formulas in columns L:X (Distributed Slack - Dec) have been copied through to the apporpriate number of rows |  |  |  | Sink Zone (diagnostic) | South
If Dennis' sheet data is less than this file then clear any old unit data in columns A:K of this workbook to match the correct length
Clear any old data that will be below the new data iin the "Distributed Slack - Inc" worksheet, as well
Step 9 | Click the step 2 button
The last file saved will still be open, you will need to close this file.
This Template sheet will no longer be open.
|  | Current Source Zone | North
|  | Current Sink Zone | South | NS_062609automation.xls
The file listed in cell K29 needs to be in the same folder as this template file
Copy Dennis' data step 1
Copy Dennis' Data Step 2

## Distributed Slack - Dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Concentrated Capacity | Cumulative Concentrated Impact | Cont_ TempleSS to LakeCreek and TemplePEC to Tradinghouse OL_ Evant to Goldthwaite
6407 | TURKTRAK1A | 1 | West | YES | 0.041999 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.065765 | 0 | 169.5 |  |  |  |  | 0.065765 | 11.1472 | 169.5 | 11.1472
60057 | CALLAHAN1A | 1 | West | YES | 0.037241 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.061007 | 0 | 114 |  |  |  |  | 0.061007 | 6.9548 | 283.5 | 18.102 |  |  |  | 624
1643 | SLSTR1PP_1G | 1 | North | YES | 0.036615 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.060381 | 0 | 60 | 2.1969 | 60 |  |  | 0.060381 | 3.6229
1343 | TRENTIPP_8 | 1 | West | YES | 0.032859 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.056625 | 0 | 150 |  |  |  |  | 0.056625 | 8.4938 |  |  | Weighted Shift Factors |  | chk
1354 | AEPWIND_8 | 1 | West | YES | 0.032859 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.056625 | 0 | 101 |  |  |  |  | 0.056625 | 5.7191 |  |  | North | 0.015906 | 0.015906
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.031149 | 110 | 0 | 550 | 0 | 1.02 | Wind | 1 | 0.054915 | 0 | 550 |  |  |  |  | 0.054915 | 30.2034 |  |  | South | -0.023766 | -0.023766
1349 | WESTXWIN_1G | 1 | West | YES | 0.031081 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.054847 | 0 | 6.6 |  |  |  |  | 0.054847 | 0.36199 |  |  |  | 0.039673 | 0.039673
1350 | NWPWRG1_1G | 1 | West | YES | 0.031081 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.054847 | 0 | 34.3 |  |  |  |  | 0.054847 | 1.8813
76031 | L_GASCCR1_1N | W1 | West | YES | 0.030901 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.054667 | 0 | 150 |  |  |  |  | 0.054667 | 8.2001 |  |  | Line Cap | 128
60058 | BUFF_GAP1A | 1 | West | YES | 0.030814 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.05458 | 0 | 120 |  |  |  |  | 0.05458 | 6.5496 |  |  | Conc Gen | 283.5
60060 | CIRELLO | 1 | West | YES | 0.030814 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.05458 | 0 | 233 |  |  |  |  | 0.05458 | 12.7172 |  |  | Weighted Imp. | 18.102
60063 | BUFF_GAP1B | 1 | West | YES | 0.030814 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.05458 | 0 | 170.2 |  |  |  |  | 0.05458 | 9.2896 |  |  | PTDF | 0.063852
60066 | H_HOLLOW1A | 1 | West | YES | 0.030814 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.05458 | 0 | 222 |  |  |  |  | 0.05458 | 12.1168
60068 | HHOLLOW21A | 1 | West | YES | 0.030814 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.05458 | 0 | 184 |  |  |  |  | 0.05458 | 10.0428 |  |  | Concentration | 1.6095
60070 | HHOLLOW31A | 1 | West | YES | 0.030814 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.05458 | 0 | 224 |  |  |  |  | 0.05458 | 12.226
60072 | HHOLLOW41A | 1 | West | YES | 0.030814 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.05458 | 0 | 115 |  |  |  |  | 0.05458 | 6.2767 |  |  |  | Pass
6144 | MCADOO1A | 1 | West | YES | 0.03068 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.054446 | 0 | 150 |  |  |  |  | 0.054446 | 8.1669
60081 | WHRLWIND1A | 1 | West | YES | 0.030442 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.054208 | 0 | 60 |  |  |  |  | 0.054208 | 3.2525
1320 | BSP 1 | 1 | West | YES | 0.030343 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.054109 | 0 | 0 |  |  |  |  | 0.054109 | 0
60052 | WILDHRS11A | 1 | West | YES | 0.030325 | 25.3 | 0 | 126.5 | 0 | 1.005 | Wind | 1 | 0.054091 | 0 | 126.5 |  |  |  |  | 0.054091 | 6.8425
60053 | WILDHRS21A | 1 | West | YES | 0.030325 | 7.8 | 0 | 39 | 0 | 1.025 | Wind | 1 | 0.054091 | 0 | 39 |  |  |  |  | 0.054091 | 2.1096
36998 | RDCNYNG1 | 1 | West | YES | 0.030263 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.054029 | 0 | 84 |  |  |  |  | 0.054029 | 4.5385
6637 | SNYDERW1A | 1 | West | YES | 0.030191 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.053957 | 0 | 63 |  |  |  |  | 0.053957 | 3.3993
1061 | CIELOGEN_1G | 1 | West | YES | 0.030168 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.053934 | 0 | 99 |  |  |  |  | 0.053934 | 5.3395
1062 | CIELOGEN_2G | 1 | West | YES | 0.030168 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.053934 | 0 | 61 |  |  |  |  | 0.053934 | 3.29
1069 | KINDERMG_1G | 1 | West | YES | 0.030168 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.053934 | 0 | 0 |  |  |  |  | 0.053934 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.030168 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.053934 | 0 | 0 |  |  |  |  | 0.053934 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.030168 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.053934 | 0 | 0 |  |  |  |  | 0.053934 | 0
1068 | SCURRYCW_1G | 1 | West | YES | 0.030165 | 28.2 | 1.3 | 141 |  | 1.01 | Wind | 1 | 0.053931 | 0 | 141 |  |  |  |  | 0.053931 | 7.6043
1073 | SCURRYCW_2G | 2 | West | YES | 0.030165 | 24 | 0 | 120 | 0 | 1.017 | Wind | 1 | 0.053931 | 0 | 120 |  |  |  |  | 0.053931 | 6.4717
1360 | GUNSIGHT_8 | 1 | West | YES | 0.030103 | 24 | 0 | 120 | 0 | 1.01 | Wind | 1 | 0.053869 | 0 | 120 |  |  |  |  | 0.053869 | 6.4643
1301 | BULLCREK_8 | 1 | West | YES | 0.030089 | 36 | 0 | 180 | 0 | 1.017 | Wind | 1 | 0.053855 | 0 | 180 |  |  |  |  | 0.053855 | 9.6939
1327 | WILDHRSE_1G | 1 | West | YES | 0.030089 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.053855 | 0 | 120 |  |  |  |  | 0.053855 | 6.4626
1302 | COYOTEWG_8 | 1 | West | YES | 0.030005 | 45 | 0 | 225 |  | 1.01 | Wind | 1 | 0.053771 | 0 | 225 |  |  |  |  | 0.053771 | 12.0985
1037 | MORGAN5G_5G | 5 | West | YES | 0.029967 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.053733 | 137 | 137 |  |  |  |  | 0.053733 | 7.3614
1039 | MRGNAG_1G | A | West | YES | 0.029967 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.053733 | 69 | 69 |  |  |  |  | 0.053733 | 3.7076
1040 | MRGNBG_2G | B | West | YES | 0.029967 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.053733 | 71 | 71 |  |  |  |  | 0.053733 | 3.8151
1041 | MRGNCG_3G | C | West | YES | 0.029967 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.053733 | 70 | 70 |  |  |  |  | 0.053733 | 3.7613
1042 | MRGNDG_4G | D | West | YES | 0.029967 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.053733 | 68 | 68 |  |  |  |  | 0.053733 | 3.6539
1043 | MRGNEG_5G | E | West | YES | 0.029967 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.053733 | 70 | 70 |  |  |  |  | 0.053733 | 3.7613
1044 | MRGNFG_6G | F | West | YES | 0.029967 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.053733 | 66 | 66 |  |  |  |  | 0.053733 | 3.5464
1170 | AIRLAMESA_1G | 1 | West | YES | 0.029888 | 0 | 0 | 180 |  | 1 | Wind | 1 | 0.053654 | 0 | 180 |  |  |  |  | 0.053654 | 9.6578
1326 | STANTONW_8 | 1 | West | YES | 0.029776 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.053542 | 0 | 100.5 |  |  |  |  | 0.053542 | 5.381
1333 | MCDDONAL_8 | 1 | West | YES | 0.029767 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.053533 | 0 | 214.2 |  |  |  |  | 0.053533 | 11.4668
1328 | OCOTILLO_1G | 1 | West | YES | 0.029734 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.0535 | 0 | 58 |  |  |  |  | 0.0535 | 3.103
1058 | LONGSHORE_5 | 3 | West | YES | 0.029602 | 23.4 | 0 | 117 |  | 1.01 | Wind | 1 | 0.053368 | 0 | 117 |  |  |  |  | 0.053368 | 6.2441
1058 | LONGSHORE_5 | 2 | West | YES | 0.029602 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.053368 | 0 | 220 |  |  |  |  | 0.053368 | 11.741
1058 | LONGSHORE_5 | 1 | West | YES | 0.029602 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.053368 | 0 | 150 |  |  |  |  | 0.053368 | 8.0052
1045 | CALENG1G_1G | 1 | West | YES | 0.029594 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.05336 | 0 | 0 |  |  |  |  | 0.05336 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.029594 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.05336 | 0 | 0 |  |  |  |  | 0.05336 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.029594 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.05336 | 0 | 0 |  |  |  |  | 0.05336 | 0
11001 | NAV1CT | 1 | West | YES | 0.029512 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.053278 | 70.4 | 70.4 |  |  |  |  | 0.053278 | 3.7508
11009 | NAV2CT | 1 | West | YES | 0.029512 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.053278 | 71.4 | 71.4 |  |  |  |  | 0.053278 | 3.8041
11011 | NAV3ST | 1 | West | YES | 0.029512 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.053278 | 92.8 | 92.8 |  |  |  |  | 0.053278 | 4.9442
11012 | NAV4CT | 1 | West | YES | 0.029512 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.053278 | 80 | 80 |  |  |  |  | 0.053278 | 4.2623
11013 | NAV5CT | 1 | West | YES | 0.029512 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.053278 | 80 | 80 |  |  |  |  | 0.053278 | 4.2623
11014 | NAV6ST | 1 | West | YES | 0.029512 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.053278 | 115 | 115 |  |  |  |  | 0.053278 | 6.127
11020 | TIEHVSG_1G | 1 | West | YES | 0.029511 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.053277 | 208.2 | 208.2 |  |  |  |  | 0.053277 | 11.0923
11021 | TIEHVCG_1G | 1 | West | YES | 0.029511 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.053277 | 142.1 | 142.1 |  |  |  |  | 0.053277 | 7.5707
11022 | TIEHVCG_2G | 1 | West | YES | 0.029511 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.053277 | 132.4 | 132.4 |  |  |  |  | 0.053277 | 7.0539
11023 | TIEHVCG_3G | 1 | West | YES | 0.029511 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.053277 | 137.4 | 137.4 |  |  |  |  | 0.053277 | 7.3203
11024 | TIEHVCG_4G | 1 | West | YES | 0.029511 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.053277 | 147 | 147 |  |  |  |  | 0.053277 | 7.8317
11025 | TIEHVSG_2G | 1 | West | YES | 0.029511 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.053277 | 213.2 | 213.2 |  |  |  |  | 0.053277 | 11.3587
71051 | L_BITTCR1_1N | W1 | West | YES | 0.029501 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.053267 | 0 | 37.5 |  |  |  |  | 0.053267 | 1.9975
71054 | L_SWEETW1_1N | W1 | West | YES | 0.029501 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.053267 | 0 | 107.5 |  |  |  |  | 0.053267 | 5.7262
71057 | L_SWEETW1_2N | W1 | West | YES | 0.029501 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.053267 | 0 | 135 |  |  |  |  | 0.053267 | 7.1911
71059 | L_SWEETW1_3N | W1 | West | YES | 0.029501 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.053267 | 0 | 119 |  |  |  |  | 0.053267 | 6.3388
71060 | L_SWEETW1_4N | W1 | West | YES | 0.029501 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.053267 | 0 | 105 |  |  |  |  | 0.053267 | 5.5931
1146 | NOTREES_1G | 1 | West | YES | 0.029459 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.053225 | 0 | 149 |  |  |  |  | 0.053225 | 7.9306
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.029421 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.053187 | 0 | 35 |  |  |  |  | 0.053187 | 1.8616
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.029421 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.053187 | 0 | 30 |  |  |  |  | 0.053187 | 1.5956
1002 | PBCTAGE_1G | A | West | YES | 0.029403 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.053169 | 66 | 66 |  |  |  |  | 0.053169 | 3.5092
1003 | PBCTBGE_2G | B | West | YES | 0.029403 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.053169 | 66 | 66 |  |  |  |  | 0.053169 | 3.5092
1004 | PBCTCGE_3G | C | West | YES | 0.029403 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.053169 | 67 | 67 |  |  |  |  | 0.053169 | 3.5623
1005 | PBCTDGE_4G | D | West | YES | 0.029403 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.053169 | 68 | 68 |  |  |  |  | 0.053169 | 3.6155
1006 | PBCTEGE_5G | E | West | YES | 0.029403 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.053169 | 67 | 67 |  |  |  |  | 0.053169 | 3.5623
1007 | PB5GEN_6G | 5 | West | YES | 0.029403 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.053169 | 114 | 114 |  |  |  |  | 0.053169 | 6.0613
1008 | PB6GEN_7G | 6 | West | YES | 0.029403 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.053169 | 515 | 515 |  |  |  |  | 0.053169 | 27.3821
1049 | ROSCOEWI_5 | 1 | West | YES | 0.029023 | 41.8 | 0 | 209 |  | 1.01 | Wind | 1 | 0.052789 | 0 | 209 |  |  |  |  | 0.052789 | 11.0329
1057 | ROSCOEWI_5 | 2 | West | YES | 0.029023 | 25.3 | 0 | 126.5 |  | 1.01 | Wind | 1 | 0.052789 | 0 | 126.5 |  |  |  |  | 0.052789 | 6.6778
1060 | ROSCOEWI_5 | 3 | West | YES | 0.029023 | 39.4 | 0 | 197 | 0 | 1.01 | Wind | 1 | 0.052789 | 0 | 197 |  |  |  |  | 0.052789 | 10.3995
1072 | ROSCOEWI_5 | 4 | West | YES | 0.029023 | 63.6 | 0 | 318 | 0 | 1.01 | Wind | 1 | 0.052789 | 0 | 318 |  |  |  |  | 0.052789 | 16.787
1416 | SWETWATR_1G | 1 | West | YES | 0.028895 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.052661 | 30 | 30 |  |  |  |  | 0.052661 | 1.5798
1417 | SWETWATR_2G | 2 | West | YES | 0.028895 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.052661 | 72 | 72 |  |  |  |  | 0.052661 | 3.7916
1418 | SWETWATR_3G | 3 | West | YES | 0.028895 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.052661 | 68 | 68 |  |  |  |  | 0.052661 | 3.581
1419 | SWETWATR_4G | 4 | West | YES | 0.028895 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.052661 | 61 | 61 |  |  |  |  | 0.052661 | 3.2123
332 | RWMILLER01 | 1 | North | YES | 0.028771 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.052537 | 73 | 73 | 2.1003 | 73 |  |  | 0.052537 | 3.8352
333 | RWMILLER02 | 2 | North | YES | 0.028771 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.052537 | 119 | 119 | 3.4237 | 119 |  |  | 0.052537 | 6.2519
334 | RWMILLER03 | 3 | North | YES | 0.028771 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.052537 | 208 | 208 | 5.9844 | 208 |  |  | 0.052537 | 10.9277
335 | RWMILLER04 | 4 | North | YES | 0.028771 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.052537 | 102 | 102 | 2.9346 | 102 |  |  | 0.052537 | 5.3588
336 | RWMILLER05 | 5 | North | YES | 0.028771 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.052537 | 101 | 101 | 2.9059 | 101 |  |  | 0.052537 | 5.3063
60007 | KING_SW1A | 1 | West | YES | 0.028385 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.052151 | 0 | 80 |  |  |  |  | 0.052151 | 4.1721
60019 | KING_NW1A | 1 | West | YES | 0.028385 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.052151 | 0 | 80 |  |  |  |  | 0.052151 | 4.1721
60201 | RIO DRCS | F | West | YES | 0.028281 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.052047 | 0 | 0 |  |  |  |  | 0.052047 | 0
60016 | WOODWRD11A | 1 | West | YES | 0.028273 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.052039 | 0 | 80 |  |  |  |  | 0.052039 | 4.1631
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.028271 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.052037 | 0 | 80 |  |  |  |  | 0.052037 | 4.163
38437 | TNSRBNMESA9 | 1 | West | YES | 0.028263 | 37.5 | 0 | 150 |  | 1.02 | Wind | 1 | 0.052029 | 0 | 150 |  |  |  |  | 0.052029 | 7.8044
6016 | SWMESA | 1 | West | YES | 0.028242 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.052008 | 0 | 75 |  |  |  |  | 0.052008 | 3.9006
60003 | KING_NE1A | 1 | West | YES | 0.028242 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.052008 | 0 | 80 |  |  |  |  | 0.052008 | 4.1607
60005 | KING_SE1A | 1 | West | YES | 0.028242 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.052008 | 0 | 40 |  |  |  |  | 0.052008 | 2.0803
60000 | DSKY2 | 1 | West | YES | 0.028056 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.051822 | 0 | 76.5 |  |  |  |  | 0.051822 | 3.9644
60017 | ORNNWP1 | 1 | West | YES | 0.027943 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.051709 | 0 | 80 |  |  |  |  | 0.051709 | 4.1367
60018 | DSKY1 | 1 | West | YES | 0.027836 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.051602 | 0 | 84 |  |  |  |  | 0.051602 | 4.3346
1437 | MESQUITW_1G | 1 | North | YES | 0.027761 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.051527 | 0 | 400 | 11.1044 | 400 |  |  | 0.051527 | 20.6109
1438 | MESQUITW_2G | 1 | North | YES | 0.027756 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.051522 | 0 | 236 | 6.5504 | 236 |  |  | 0.051522 | 12.1592
1442 | COKFIELD_5 | 1 | North | YES | 0.027092 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.050858 | 0 | 165 | 4.4702 | 165 |  |  | 0.050858 | 8.3916
6100 | OKLA7A | EQ | West | YES | 0.026854 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.05062 | 0 | 0 |  |  |  |  | 0.05062 | 0
6752 | OKLA0A | 1 | West | YES | 0.026854 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.05062 | 0 | 649.7 |  |  |  |  | 0.05062 | 32.888
1433 | GRHAMSES_1G | 1 | North | YES | 0.026551 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.050317 | 242 | 242 | 6.4253 | 242 |  |  | 0.050317 | 12.1768
60202 | FRNDDRCS | F | West | YES | 0.025791 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.049557 | 0 | 0 |  |  |  |  | 0.049557 | 0
1479 | WFCOGEN_1G | 1 | North | YES | 0.025169 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.048935 | 0 | 0 | 0 | 0 |  |  | 0.048935 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.025169 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.048935 | 0 | 0 | 0 | 0 |  |  | 0.048935 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.025169 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.048935 | 0 | 0 | 0 | 0 |  |  | 0.048935 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.025169 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.048935 | 0 | 0 | 0 | 0 |  |  | 0.048935 | 0
1600 | BARTNWND_1G | 1 | North | YES | 0.02512 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.048886 | 0 | 120 | 3.0144 | 120 |  |  | 0.048886 | 5.8663
1432 | GRHAMSES_2G | 2 | North | YES | 0.024988 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.048754 | 366 | 366 | 9.1456 | 366 |  |  | 0.048754 | 17.844
344 | MRSSHPRD | 1 | North | YES | 0.024847 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.048613 | 0 | 0 | 0 | 0 |  |  | 0.048613 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.024847 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.048613 | 0 | 0 | 0 | 0 |  |  | 0.048613 | 0
1898 | COMCHEPK_1G | 1 | North | YES | 0.024284 | 1159 | 1150 | 1159 | 0 | 1.032 | Nuc | 1 | 0.04805 | 0 | 0 | 0 | 0 |  |  | 0.04805 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.024284 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.04805 | 0 | 0 | 0 | 0 |  |  | 0.04805 | 0
1877 | WLFHOLW_1G | 1 | North | YES | 0.023562 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.047328 | 217.3 | 217.3 | 5.12 | 217.3 |  |  | 0.047328 | 10.2844
1878 | WLFHOLW_2G | 2 | North | YES | 0.023562 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.047328 | 215.7 | 215.7 | 5.0823 | 215.7 |  |  | 0.047328 | 10.2087
1879 | WLFHOLW_3G | 3 | North | YES | 0.023562 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.047328 | 272.4 | 272.4 | 6.4183 | 272.4 |  |  | 0.047328 | 12.8922
503 | NTHTEXAS01 | 1 | North | YES | 0.023454 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.04722 | 18 | 18 | 0.42217 | 18 |  |  | 0.04722 | 0.84996
504 | NTHTEXAS02 | 2 | North | YES | 0.023454 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.04722 | 18 | 18 | 0.42217 | 18 |  |  | 0.04722 | 0.84996
505 | NTHTEXAS03 | 3 | North | YES | 0.023454 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.04722 | 38 | 38 | 0.89125 | 38 |  |  | 0.04722 | 1.7944
1892 | DECRDOVA_2G | A | North | YES | 0.023192 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.046958 | 70 | 70 | 1.6234 | 70 |  |  | 0.046958 | 3.2871
1893 | DECRDOVA_3G | B | North | YES | 0.023192 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.046958 | 69 | 69 | 1.6002 | 69 |  |  | 0.046958 | 3.2401
1894 | DECRDOVA_4G | C | North | YES | 0.023192 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.046958 | 69 | 69 | 1.6002 | 69 |  |  | 0.046958 | 3.2401
1895 | DECRDOVA_5G | D | North | YES | 0.023192 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.046958 | 68 | 68 | 1.5771 | 68 |  |  | 0.046958 | 3.1932
1453 | WCPWRCO_1G | 1 | North | YES | 0.022882 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.046648 | 204 | 204 | 4.6679 | 204 |  |  | 0.046648 | 9.5162
1454 | WCPWRCO_2G | 2 | North | YES | 0.022882 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.046648 | 204 | 204 | 4.6679 | 204 |  |  | 0.046648 | 9.5162
1455 | WCPWRCO_3G | 3 | North | YES | 0.022882 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.046648 | 242 | 242 | 5.5374 | 242 |  |  | 0.046648 | 11.2889
1889 | DECRDOVA_1G | 1 | North | YES | 0.022566 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.046332 | 779 | 779 | 17.5789 | 779 |  |  | 0.046332 | 36.0928
580 | JCKCNTY801 | 1 | North | YES | 0.022268 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.046034 | 288 | 288 | 6.4132 | 288 |  |  | 0.046034 | 13.2579
581 | JCKCNTY802 | 2 | North | YES | 0.022268 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.046034 | 147 | 147 | 3.2734 | 147 |  |  | 0.046034 | 6.767
582 | JCKCNTY803 | 3 | North | YES | 0.022268 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.046034 | 147 | 147 | 3.2734 | 147 |  |  | 0.046034 | 6.767
728 | WOLFRIDGE801 | 1 | North | YES | 0.020793 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.044559 | 0 | 112.5 | 2.3392 | 112.5 |  |  | 0.044559 | 5.0129
366 | JNSNCNTY802 | 1 | North | YES | 0.02077 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.044536 | 0 | 0 | 0 | 0 |  |  | 0.044536 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.02077 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.044536 | 0 | 0 | 0 | 0 |  |  | 0.044536 | 0
1861 | EAGLEMNT_1G | MB | North | YES | 0.02052 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.044286 | 0 | 0 | 0 | 0 |  |  | 0.044286 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.02052 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.044286 | 0 | 0 | 0 | 0 |  |  | 0.044286 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.02052 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.044286 | 0 | 0 | 0 | 0 |  |  | 0.044286 | 0
923 | SPENCER_G4 | 1 | North | YES | 0.019594 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.04336 | 61 | 61 | 1.1952 | 61 |  |  | 0.04336 | 2.645
924 | SPENCER_G5 | 1 | North | YES | 0.019594 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.04336 | 66 | 66 | 1.2932 | 66 |  |  | 0.04336 | 2.8618
1945 | HANDLEY_1G | MB | North | YES | 0.019282 | 0 | 25 | 36 |  | 0.986 | GST | 1 | 0.043048 | 0 | 0 | 0 | 0 |  |  | 0.043048 | 0
1946 | HANDLEY_2G | MB | North | YES | 0.019282 | 0 | 30 | 68 |  | 0.986 | GST | 1 | 0.043048 | 0 | 0 | 0 | 0 |  |  | 0.043048 | 0
1947 | HANDLEY_3G | 3 | North | YES | 0.019197 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.042963 | 395 | 395 | 7.5828 | 395 |  |  | 0.042963 | 16.9705
1949 | HANDLEY_5G | 5 | North | YES | 0.019197 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.042963 | 435 | 435 | 8.3507 | 435 |  |  | 0.042963 | 18.689
1948 | HANDLEY_4G | 4 | North | YES | 0.019037 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.042803 | 435 | 435 | 8.2811 | 435 |  |  | 0.042803 | 18.6194
1937 | MDLTHELP_5G | 5 | North | YES | 0.018043 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.041809 | 224 | 224 | 4.0416 | 224 |  |  | 0.041809 | 9.3653
1938 | MDLTHELP_6G | 6 | North | YES | 0.018043 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.041809 | 226 | 226 | 4.0777 | 226 |  |  | 0.041809 | 9.4489
1943 | MDLTHELP_3G | 3 | North | YES | 0.018043 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.041809 | 212 | 212 | 3.8251 | 212 |  |  | 0.041809 | 8.8636
1944 | MDLTHELP_4G | 4 | North | YES | 0.018043 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.041809 | 211 | 211 | 3.8071 | 211 |  |  | 0.041809 | 8.8217
2371 | COLLIN_1G | MB | North | YES | 0.017734 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.0415 | 0 | 0 | 0 | 0 |  |  | 0.0415 | 0
2381 | NTHLK1_G | 1 | North | YES | 0.017613 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.041379 | 156 | 156 | 2.7476 | 156 |  |  | 0.041379 | 6.4552
2382 | NTHLK2_G | 2 | North | YES | 0.017613 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.041379 | 181 | 181 | 3.188 | 181 |  |  | 0.041379 | 7.4896
2383 | NTHLK3_G | 3 | North | YES | 0.017613 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.041379 | 329 | 329 | 5.7947 | 329 |  |  | 0.041379 | 13.6138
6948 | DENISNDM | 1 | North | YES | 0.017452 | 40 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.041218 | 0 | 0 | 0 | 0 |  |  | 0.041218 | 0
6948 | DENISNDM | 2 | North | YES | 0.017452 | 31 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.041218 | 0 | 0 | 0 | 0 |  |  | 0.041218 | 0
1687 | VALLEY_1G | 1 | North | YES | 0.017315 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.041081 | 170 | 170 | 2.9436 | 170 |  |  | 0.041081 | 6.9838
1688 | VALLEY_2G | 2 | North | YES | 0.017315 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.041081 | 527 | 527 | 9.125 | 527 |  |  | 0.041081 | 21.6498
1689 | VALLEY_3G | 3 | North | YES | 0.017132 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.040898 | 375 | 375 | 6.4245 | 375 |  |  | 0.040898 | 15.3368
11691 | KMICHICT1_G | 1 | North | YES | 0.017132 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.040898 | 144 | 144 | 2.467 | 144 |  |  | 0.040898 | 5.8893
11692 | KMICHICT2_G | 2 | North | YES | 0.017132 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.040898 | 146 | 146 | 2.5013 | 146 |  |  | 0.040898 | 5.9711
11693 | KMICHIST3_G | 3 | North | YES | 0.017132 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.040898 | 312 | 312 | 5.3452 | 312 |  |  | 0.040898 | 12.7602
11694 | KMICHICT4_G | 4 | North | YES | 0.017132 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.040898 | 144 | 144 | 2.467 | 144 |  |  | 0.040898 | 5.8893
11695 | KMICHICT5_G | 5 | North | YES | 0.017132 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.040898 | 148 | 148 | 2.5355 | 148 |  |  | 0.040898 | 6.0529
11696 | KMICHIST6_G | 6 | North | YES | 0.017132 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.040898 | 310 | 310 | 5.3109 | 310 |  |  | 0.040898 | 12.6784
2418 | MTCK2_G | 2 | North | YES | 0.017124 | 0 | 10 | 23 |  | 0.971 | GSC | 1 | 0.04089 | 23 | 23 | 0.39385 | 23 |  |  | 0.04089 | 0.94047
2419 | MTCK3_G | MB | North | YES | 0.017124 | 0 | 10 | 63 |  | 0.971 | GSC | 1 | 0.04089 | 0 | 0 | 0 | 0 |  |  | 0.04089 | 0
1678 | LAMARPWR_1G | 1 | North | YES | 0.017069 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.040835 | 160 | 160 | 2.731 | 160 |  |  | 0.040835 | 6.5336
1679 | LAMARPWR_2G | 2 | North | YES | 0.017069 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.040835 | 156 | 156 | 2.6628 | 156 |  |  | 0.040835 | 6.3703
1680 | LAMARPWR_3G | 3 | North | YES | 0.017069 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.040835 | 196 | 196 | 3.3455 | 196 |  |  | 0.040835 | 8.0037
1681 | LAMARPWR_4G | 4 | North | YES | 0.017069 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.040835 | 156 | 156 | 2.6628 | 156 |  |  | 0.040835 | 6.3703
1682 | LAMARPWR_5G | 5 | North | YES | 0.017069 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.040835 | 157 | 157 | 2.6798 | 157 |  |  | 0.040835 | 6.4111
1683 | LAMARPWR_6G | 6 | North | YES | 0.017069 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.040835 | 198 | 198 | 3.3797 | 198 |  |  | 0.040835 | 8.0854
1675 | PEC_1G | 1 | North | YES | 0.017033 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.040799 | 0 | 0 | 0 | 0 |  |  | 0.040799 | 0
1676 | PEC_2G | 2 | North | YES | 0.017033 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.040799 | 0 | 0 | 0 | 0 |  |  | 0.040799 | 0
1677 | PEC_3G | 3 | North | YES | 0.017033 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.040799 | 0 | 0 | 0 | 0 |  |  | 0.040799 | 0
1701 | MOSES_1G | 1 | North | YES | 0.01695 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.040716 | 0 | 558 | 9.4581 | 558 |  |  | 0.040716 | 22.7196
1702 | MOSES_2G | 2 | North | YES | 0.01695 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.040716 | 0 | 579 | 9.814 | 579 |  |  | 0.040716 | 23.5747
1703 | MOSES_3G | 3 | North | YES | 0.01695 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.040716 | 0 | 808 | 13.6956 | 808 |  |  | 0.040716 | 32.8987
5925 | DCEAST | EQ | North | YES | 0.01695 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.040716 | 0 | 0 | 0 | 0 |  |  | 0.040716 | 0
2413 | MTCK6_G | 6 | North | YES | 0.016845 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.040611 | 118 | 118 | 1.9877 | 118 |  |  | 0.040611 | 4.7921
2414 | MTCK7_G | 7 | North | YES | 0.016845 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.040611 | 115 | 115 | 1.9372 | 115 |  |  | 0.040611 | 4.6703
2417 | MTCK8_G | 8 | North | YES | 0.016845 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.040611 | 556 | 556 | 9.3658 | 556 |  |  | 0.040611 | 22.5798
1941 | MDLTHELP_1G | 1 | North | YES | 0.01683 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.040596 | 216.4 | 216.4 | 3.642 | 216.4 |  |  | 0.040596 | 8.785
1942 | MDLTHELP_2G | 2 | North | YES | 0.01683 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.040596 | 216.1 | 216.1 | 3.637 | 216.1 |  |  | 0.040596 | 8.7728
842 | OLINGER_G1 | 1 | North | YES | 0.016749 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.040515 | 79 | 79 | 1.3232 | 79 |  |  | 0.040515 | 3.2007
843 | OLINGER_G2 | 1 | North | YES | 0.016749 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.040515 | 110 | 110 | 1.8424 | 110 |  |  | 0.040515 | 4.4567
844 | OLINGER_G3 | 1 | North | YES | 0.016749 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.040515 | 150 | 150 | 2.5124 | 150 |  |  | 0.040515 | 6.0773
845 | OLINGER_G4 | 1 | North | YES | 0.016749 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.040515 | 76 | 76 | 1.2729 | 76 |  |  | 0.040515 | 3.0792
837 | NEWMAN_G5 | 1 | North | YES | 0.016701 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.040467 | 40 | 40 | 0.66804 | 40 |  |  | 0.040467 | 1.6187
948 | STEAM1 | 1 | North | YES | 0.016671 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.040437 | 20 | 20 | 0.33342 | 20 |  |  | 0.040437 | 0.80874
949 | STEAM2 | 1 | North | YES | 0.016671 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.040437 | 26 | 26 | 0.43345 | 26 |  |  | 0.040437 | 1.0514
950 | STEAM3 | 1 | North | YES | 0.016671 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.040437 | 42 | 42 | 0.70018 | 42 |  |  | 0.040437 | 1.6984
2451 | LKHB1_G | 1 | North | YES | 0.016468 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.040234 | 391 | 391 | 6.439 | 391 |  |  | 0.040234 | 15.7316
2452 | LKHB2_G | 2 | North | YES | 0.016468 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.040234 | 516 | 516 | 8.4975 | 516 |  |  | 0.040234 | 20.7609
12440 | PARKD_1SVC8 | 1 | North | YES | 0.016463 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.040229 | 0 | 0 | 0 | 0 |  |  | 0.040229 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.016463 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.040229 | 0 | 0 | 0 | 0 |  |  | 0.040229 | 0
12411 | FPLEFR1A_G | 1 | North | YES | 0.016233 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.039999 | 161 | 161 | 2.6135 | 161 |  |  | 0.039999 | 6.4399
12412 | FPLEFR1B_G | 2 | North | YES | 0.016233 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.039999 | 164 | 164 | 2.6622 | 164 |  |  | 0.039999 | 6.5599
12413 | FPLEFR1C_G | 3 | North | YES | 0.016233 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.039999 | 164 | 164 | 2.6622 | 164 |  |  | 0.039999 | 6.5599
12414 | FPLEFR1S_G | 4 | North | YES | 0.016233 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.039999 | 414 | 414 | 6.7205 | 414 |  |  | 0.039999 | 16.5597
12421 | FPLEFR2A_G | 1 | North | YES | 0.016233 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.039999 | 162 | 162 | 2.6297 | 162 |  |  | 0.039999 | 6.4799
12422 | FPLEFR2B_G | 2 | North | YES | 0.016233 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.039999 | 161 | 161 | 2.6135 | 161 |  |  | 0.039999 | 6.4399
12423 | FPLEFR2C_G | 3 | North | YES | 0.016233 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.039999 | 163 | 163 | 2.646 | 163 |  |  | 0.039999 | 6.5199
12424 | FPLEFR2S_G | 4 | North | YES | 0.016233 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.039999 | 415 | 415 | 6.7367 | 415 |  |  | 0.039999 | 16.5997
12322 | ENNSTRAC_1G | 1 | North | YES | 0.016124 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.03989 | 196 | 196 | 3.1603 | 196 |  |  | 0.03989 | 7.8185
12323 | ENNSTRAC_2G | 2 | North | YES | 0.016124 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.03989 | 116 | 116 | 1.8704 | 116 |  |  | 0.03989 | 4.6273
3097 | MARTLAKE_1G | 1 | North | YES | 0.014738 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.038504 | 0 | 790 | 11.643 | 790 |  |  | 0.038504 | 30.4183
3098 | MARTLAKE_2G | 2 | North | YES | 0.014738 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.038504 | 0 | 795 | 11.7167 | 795 |  |  | 0.038504 | 30.6108
3099 | MARTLAKE_3G | 3 | North | YES | 0.014738 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.038504 | 0 | 804 | 11.8494 | 804 |  |  | 0.038504 | 30.9574
13116 | TGATEWAY_1G | 1 | North | YES | 0.014534 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.0383 | 151 | 151 | 2.1946 | 151 |  |  | 0.0383 | 5.7833
13117 | TGATEWAY_2G | 2 | North | YES | 0.014534 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.0383 | 130 | 130 | 1.8894 | 130 |  |  | 0.0383 | 4.979
13118 | TGATEWAY_3G | 3 | North | YES | 0.014534 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.0383 | 148 | 148 | 2.151 | 148 |  |  | 0.0383 | 5.6684
13119 | TGATEWAY_4G | 4 | North | YES | 0.014534 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.0383 | 399 | 399 | 5.7991 | 399 |  |  | 0.0383 | 15.2818
3126 | TRINIDAD_6G | 1 | North | YES | 0.014468 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.038234 | 224 | 224 | 3.2408 | 224 |  |  | 0.038234 | 8.5645
3348 | CHAMPION_1G | MB | North | YES | 0.014325 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.038091 | 0 | 0 | 0 | 0 |  |  | 0.038091 | 0
3113 | LUFKINWB_1G | 1 | North | YES | 0.014307 | 0 | 0 | 50 |  | 1.01 | Trash | 1 | 0.038073 | 50 | 50 | 0.71535 | 50 |  |  | 0.038073 | 1.9037
3107 | STRYKER_1G | 1 | North | YES | 0.014198 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.037964 | 182 | 182 | 2.584 | 182 |  |  | 0.037964 | 6.9095
3108 | STRYKER_2G | 2 | North | YES | 0.014198 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.037964 | 484 | 484 | 6.8718 | 484 |  |  | 0.037964 | 18.3747
244 | WHITNYDM01 | 1 | North | YES | 0.013833 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.037599 | 0 | 0 | 0 | 0 |  |  | 0.037599 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.013833 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.037599 | 0 | 0 | 0 | 0 |  |  | 0.037599 | 0
13134 | CALFREST_4G | 4 | North | YES | 0.01245 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.036216 | 151.5 | 151.5 | 1.8862 | 151.5 |  |  | 0.036216 | 5.4868
13135 | CALFREST_5G | 5 | North | YES | 0.01245 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.036216 | 152.3 | 152.3 | 1.8961 | 152.3 |  |  | 0.036216 | 5.5157
13136 | CALFREST_6G | 6 | North | YES | 0.01245 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.036216 | 177.5 | 177.5 | 2.2099 | 177.5 |  |  | 0.036216 | 6.4284
13131 | CALFREST_1G | 1 | North | YES | 0.012379 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.036145 | 150.7 | 150.7 | 1.8655 | 150.7 |  |  | 0.036145 | 5.4471
13132 | CALFREST_2G | 2 | North | YES | 0.012379 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.036145 | 151 | 151 | 1.8692 | 151 |  |  | 0.036145 | 5.4579
13133 | CALFREST_3G | 3 | North | YES | 0.012379 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.036145 | 177.4 | 177.4 | 2.196 | 177.4 |  |  | 0.036145 | 6.4122
251 | BOSQUESW803 | 2 | North | YES | 0.012027 | 150 | 0 | 150 |  | 1.032 | CC | 1 | 0.035793 | 150 | 150 | 1.804 | 150 |  |  | 0.035793 | 5.369
253 | BOSQUESW804 | 2 | North | YES | 0.012027 | 80 | 0 | 80 |  | 1.032 | CC | 1 | 0.035793 | 80 | 80 | 0.96216 | 80 |  |  | 0.035793 | 2.8635
3381 | BBRN_1G | 1 | North | YES | 0.011953 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.035719 | 0 | 618 | 7.387 | 618 |  |  | 0.035719 | 22.0745
3382 | BBRN_2G | 2 | North | YES | 0.011953 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.035719 | 0 | 589 | 7.0403 | 589 |  |  | 0.035719 | 21.0386
3403 | THOUSE_1G | 1 | North | YES | 0.011689 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.035455 | 563 | 563 | 6.5809 | 563 |  |  | 0.035455 | 19.9613
3404 | THOUSE_2G | 2 | North | YES | 0.011689 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.035455 | 807 | 807 | 9.433 | 807 |  |  | 0.035455 | 28.6124
238 | BOSQUESW505 | 1 | North | YES | 0.011625 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.035391 | 255 | 255 | 2.9644 | 255 |  |  | 0.035391 | 9.0248
239 | BOSQUESW502 | 1 | North | YES | 0.011625 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.035391 | 149 | 149 | 1.7321 | 149 |  |  | 0.035391 | 5.2733
247 | BOSQUESW501 | 2 | North | YES | 0.011625 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.035391 | 156 | 156 | 1.8135 | 156 |  |  | 0.035391 | 5.521
48721 | LEG_1___1 | 1 | North | YES | 0.007916 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.031682 | 0 | 827 | 6.5465 | 827 |  |  | 0.031682 | 26.2012
48722 | LEG_2___2 | 2 | North | YES | 0.007916 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.031682 | 0 | 819 | 6.4832 | 819 |  |  | 0.031682 | 25.9477
3416 | LAKE_CRK1_G | 1 | North | YES | 0.006707 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.030473 | 75 | 75 | 0.50303 | 75 |  |  | 0.030473 | 2.2855
3417 | LAKE_CRK2_G | 2 | North | YES | 0.006707 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.030473 | 222 | 222 | 1.489 | 222 |  |  | 0.030473 | 6.7651
39960 | TNTNPONE_18 | 1 | North | YES | 0.006313 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.030079 | 0 | 152.3 | 0.96147 | 152.3 |  |  | 0.030079 | 4.5811
39970 | TNTNPONE_28 | 1 | North | YES | 0.006313 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.030079 | 0 | 153 | 0.96589 | 153 |  |  | 0.030079 | 4.6021
990 | GIBN_CREK_G1 | 1 | North | YES | 0.002383 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.026149 | 0 | 463 | 1.1033 | 463 |  |  | 0.026149 | 12.1071
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.001704 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.02547 | 32 | 32 | 0.054528 | 32 |  |  | 0.02547 | 0.81505
32886 | BRYN_ATKINS3 | MB | North | YES | 0.001585 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.025351 | 0 | 0 | 0 | 0 |  |  | 0.025351 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.001585 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.025351 | 0 | 0 | 0 | 0 |  |  | 0.025351 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.001585 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.025351 | 17 | 17 | 0.026945 | 17 |  |  | 0.025351 | 0.43097
32890 | BRYN_ATKINS4 | MB | North | YES | 0.001585 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.025351 | 0 | 0 | 0 | 0 |  |  | 0.025351 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.001585 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.025351 | 0 | 0 | 0 | 0 |  |  | 0.025351 | 0
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.001393 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.025159 | 48 | 48 | 0.066864 | 48 |  |  | 0.025159 | 1.2076
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.001393 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.025159 | 46 | 46 | 0.064078 | 46 |  |  | 0.025159 | 1.1573
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.001393 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.025159 | 105 | 105 | 0.14627 | 105 |  |  | 0.025159 | 2.6417
48671 | FTR_GT1_5105 | 1 | North | YES | 0.001229 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.024995 | 154.2 | 154.2 | 0.18951 | 154.2 |  |  | 0.024995 | 3.8543
48672 | FTR_GT2_5110 | 2 | North | YES | 0.001229 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.024995 | 159 | 159 | 0.19541 | 159 |  |  | 0.024995 | 3.9742
48673 | FTR_GT3_5085 | 3 | North | YES | 0.001229 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.024995 | 158 | 158 | 0.19418 | 158 |  |  | 0.024995 | 3.9492
48674 | FTR_CN4_5095 | 4 | North | YES | 0.001229 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.024995 | 380 | 380 | 0.46702 | 380 |  |  | 0.024995 | 9.4982
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.015906 | 15 | 15 |  |  | 0 | 15 | -0.015906 | -0.2386
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8442 | NUECES_B0A | MB | South | YES | 0 | 0 | 81 | 367 |  | 1.03 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.015906 | 0 | 0 |  |  |  |  | -0.015906 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.003715 | 33 | 13 | 33 | 0 | 1.0375 | Hydro | -1 | 0.019621 | 0 | 0 |  |  | 0 | 0 | -0.019621 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.003715 | 25 | 13 | 25 | 0 | 1.0375 | Hydro | -1 | 0.019621 | 0 | 0 |  |  | 0 | 0 | -0.019621 | 0
88253 | HAMILTON | F | South | YES | -0.003715 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.019621 | 0 | 0 |  |  | 0 | 0 | -0.019621 | 0
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.004565 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.020471 | 0 | 0 |  |  |  |  | -0.020471 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.004565 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.020471 | 0 | 0 |  |  |  |  | -0.020471 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.004565 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.020471 | 0 | 0 |  |  |  |  | -0.020471 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.004565 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.020471 | 0 | 0 |  |  |  |  | -0.020471 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.004565 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.020471 | 0 | 0 |  |  |  |  | -0.020471 | 0
48885 | THW_5152 | B | Houston | YES | -0.005207 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.021113 | 59 | 59 |  |  |  |  | -0.021113 | -1.2457
48885 | THW_5152 | A | Houston | YES | -0.005207 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.021113 | 58 | 58 |  |  |  |  | -0.021113 | -1.2246
48886 | THW_5354 | C | Houston | YES | -0.005207 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.021113 | 57 | 57 |  |  |  |  | -0.021113 | -1.2035
48886 | THW_5354 | D | Houston | YES | -0.005207 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.021113 | 58 | 58 |  |  |  |  | -0.021113 | -1.2246
48887 | THW_5556 | F | Houston | YES | -0.005207 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.021113 | 57 | 57 |  |  |  |  | -0.021113 | -1.2035
48887 | THW_5556 | E | Houston | YES | -0.005207 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.021113 | 59 | 59 |  |  |  |  | -0.021113 | -1.2457
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.005254 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.02116 | 398 | 398 |  |  |  |  | -0.02116 | -8.4219
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.005287 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.021193 | 162.8 | 162.8 |  |  |  |  | -0.021193 | -3.4503
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.005287 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.021193 | 161.4 | 161.4 |  |  |  |  | -0.021193 | -3.4206
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.005287 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.021193 | 158.9 | 158.9 |  |  |  |  | -0.021193 | -3.3676
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.005287 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.021193 | 269.2 | 269.2 |  |  |  |  | -0.021193 | -5.7053
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.005393 | 172 | 0 | 172 | 0 | 1.026 | GSC | -1 | 0.021299 | 172 | 172 |  |  |  |  | -0.021299 | -3.6635
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.005393 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.021299 | 172 | 172 |  |  |  |  | -0.021299 | -3.6635
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.005393 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.021299 | 172 | 172 |  |  |  |  | -0.021299 | -3.6635
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.005411 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.021317 | 0 | 0 |  |  |  |  | -0.021317 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.005439 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.021345 | 744 | 744 |  |  |  |  | -0.021345 | -15.881
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.005445 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.005445 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.005445 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.005445 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.005445 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.005445 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.005445 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48651 | EP_1_2 | 2 | Houston | YES | -0.005447 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.021353 | 0 | 0 |  |  |  |  | -0.021353 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.005447 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.021353 | 0 | 0 |  |  |  |  | -0.021353 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.005525 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.021431 | 12 | 12 |  |  |  |  | -0.021431 | -0.25718
49803 | EXN_15GT | 1 | Houston | YES | -0.005547 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.005547 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.005547 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.005547 | 43 | 9.2 | 45.9 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.005547 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.005547 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.005547 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.005547 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.005547 | 18.5 | 9.2 | 18.5 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.005547 | 81 | 21.3 | 85.4 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.005547 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.005584 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.02149 | 746 | 746 |  |  |  |  | -0.02149 | -16.0319
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.005665 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.021571 | 107 | 107 |  |  |  |  | -0.021571 | -2.3081
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.005665 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.021571 | 108 | 108 |  |  |  |  | -0.021571 | -2.3297
48875 | THW_3132 | A | Houston | YES | -0.005665 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.021571 | 55 | 55 |  |  |  |  | -0.021571 | -1.1864
48875 | THW_3132 | B | Houston | YES | -0.005665 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.021571 | 53 | 53 |  |  |  |  | -0.021571 | -1.1433
48877 | THW_3334 | D | Houston | YES | -0.005665 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.021571 | 57 | 57 |  |  |  |  | -0.021571 | -1.2296
48877 | THW_3334 | C | Houston | YES | -0.005665 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.021571 | 55 | 55 |  |  |  |  | -0.021571 | -1.1864
48879 | THW_4142 | F | Houston | YES | -0.005665 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.021571 | 55 | 55 |  |  |  |  | -0.021571 | -1.1864
48879 | THW_4142 | E | Houston | YES | -0.005665 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.021571 | 56 | 56 |  |  |  |  | -0.021571 | -1.208
48881 | THW_4344 | H | Houston | YES | -0.005665 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.021571 | 58 | 58 |  |  |  |  | -0.021571 | -1.2511
48881 | THW_4344 | G | Houston | YES | -0.005665 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.021571 | 58 | 58 |  |  |  |  | -0.021571 | -1.2511
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.005783 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.021689 | 0 | 0 |  |  |  |  | -0.021689 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.005783 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.021689 | 0 | 0 |  |  |  |  | -0.021689 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.0058 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.021706 | 42 | 42 |  |  |  |  | -0.021706 | -0.91167
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.0058 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.021706 | 42 | 42 |  |  |  |  | -0.021706 | -0.91167
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.0058 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.021706 | 39 | 39 |  |  |  |  | -0.021706 | -0.84655
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.0058 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.021706 | 39 | 39 |  |  |  |  | -0.021706 | -0.84655
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.005812 | 137.6 | 54.6 | 137.6 |  | 1.0362 | Cogen | -1 | 0.021718 | 0 | 0 |  |  |  |  | -0.021718 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.005894 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.0218 | 0 | 0 |  |  |  |  | -0.0218 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.005894 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.0218 | 0 | 0 |  |  |  |  | -0.0218 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.005894 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.0218 | 0 | 0 |  |  |  |  | -0.0218 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.005894 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.0218 | 0 | 0 |  |  |  |  | -0.0218 | 0
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.005949 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.021855 | 0 | 0 |  |  |  |  | -0.021855 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.005949 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.021855 | 0 | 0 |  |  |  |  | -0.021855 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.005949 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.021855 | 0 | 0 |  |  |  |  | -0.021855 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.00595 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.021856 | 228 | 228 |  |  |  |  | -0.021856 | -4.9833
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.005951 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.021857 | 0 | 0 |  |  |  |  | -0.021857 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.005951 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.021857 | 0 | 0 |  |  |  |  | -0.021857 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.005951 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.021857 | 0 | 0 |  |  |  |  | -0.021857 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.005951 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.021857 | 0 | 0 |  |  |  |  | -0.021857 | 0
48845 | SOL_GT1 | 1 | Houston | YES | -0.005952 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.021858 | 16.2 | 16.2 |  |  |  |  | -0.021858 | -0.35411
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.005953 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.021859 | 213 | 213 |  |  |  |  | -0.021859 | -4.6561
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.005962 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.021868 | 0 | 0 |  |  |  |  | -0.021868 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.005962 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.021868 | 0 | 0 |  |  |  |  | -0.021868 | 0
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.005963 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.021869 | 165 | 165 |  |  |  |  | -0.021869 | -3.6085
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.005966 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.021872 | 176 | 176 |  |  |  |  | -0.021872 | -3.8495
48855 | SRB_GT211035 | B1 | Houston | YES | -0.005969 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.021875 | 18 | 18 |  |  |  |  | -0.021875 | -0.39376
48855 | SRB_GT211035 | B2 | Houston | YES | -0.005969 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.021875 | 12 | 12 |  |  |  |  | -0.021875 | -0.26251
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.006008 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.021914 | 0 | 0 |  |  |  |  | -0.021914 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.006048 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.021954 | 163.2 | 163.2 |  |  |  |  | -0.021954 | -3.583
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.006048 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.021954 | 157.1 | 157.1 |  |  |  |  | -0.021954 | -3.449
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.006048 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.021954 | 157.5 | 157.5 |  |  |  |  | -0.021954 | -3.4578
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.006048 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.021954 | 157 | 157 |  |  |  |  | -0.021954 | -3.4468
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.006048 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.021954 | 282 | 282 |  |  |  |  | -0.021954 | -6.1911
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.00609 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.021996 | 0 | 0 |  |  |  |  | -0.021996 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.00609 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.021996 | 0 | 0 |  |  |  |  | -0.021996 | 0
48691 | GBY_73741085 | A | Houston | YES | -0.006138 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.022044 | 47 | 47 |  |  |  |  | -0.022044 | -1.0361
48691 | GBY_73741085 | B | Houston | YES | -0.006138 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.022044 | 47 | 47 |  |  |  |  | -0.022044 | -1.0361
48692 | GBY_81821075 | D | Houston | YES | -0.006138 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.022044 | 55 | 55 |  |  |  |  | -0.022044 | -1.2124
48692 | GBY_81821075 | C | Houston | YES | -0.006138 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.022044 | 47 | 47 |  |  |  |  | -0.022044 | -1.0361
48693 | GBY_83841065 | E | Houston | YES | -0.006138 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.022044 | 57 | 57 |  |  |  |  | -0.022044 | -1.2565
48693 | GBY_83841065 | F | Houston | YES | -0.006138 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.022044 | 54 | 54 |  |  |  |  | -0.022044 | -1.1904
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.006252 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.022158 | 0 | 0 |  |  |  |  | -0.022158 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.006252 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.022158 | 0 | 0 |  |  |  |  | -0.022158 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.006252 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.022158 | 0 | 0 |  |  |  |  | -0.022158 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.006252 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.022158 | 0 | 0 |  |  |  |  | -0.022158 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.006338 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.022244 | 0 | 0 |  |  |  |  | -0.022244 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.006338 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.022244 | 0 | 0 |  |  |  |  | -0.022244 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.006338 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.022244 | 0 | 0 |  |  |  |  | -0.022244 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.006338 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.022244 | 0 | 0 |  |  |  |  | -0.022244 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.006338 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.022244 | 0 | 0 |  |  |  |  | -0.022244 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.006564 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.02247 | 0 | 0 |  |  |  |  | -0.02247 | 0
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.006887 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.006887 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.006887 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.006887 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.006887 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.006887 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.006887 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.006887 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.006887 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.006887 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.006887 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.006887 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.006887 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.006887 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.006887 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.007638 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.023544 | 166 | 166 |  |  |  |  | -0.023544 | -3.9084
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.007638 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.023544 | 166 | 166 |  |  |  |  | -0.023544 | -3.9084
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.007638 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.023544 | 248 | 248 |  |  |  |  | -0.023544 | -5.839
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.007638 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.023544 | 546 | 546 |  |  |  |  | -0.023544 | -12.8553
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.007638 | 625.7 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.023544 | 0 | 654 |  |  |  |  | -0.023544 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.007638 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.023544 | 13 | 13 |  |  |  |  | -0.023544 | -0.30608
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.007676 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.023582 | 0 | 0 |  |  |  |  | -0.023582 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.007827 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.023733 | 167.7 | 167.7 |  |  |  |  | -0.023733 | -3.9801
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.007827 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.023733 | 166.4 | 166.4 |  |  |  |  | -0.023733 | -3.9492
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.007827 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.023733 | 252.4 | 252.4 |  |  |  |  | -0.023733 | -5.9903
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.007836 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.023742 | 0 | 651 |  |  |  |  | -0.023742 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.007836 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.023742 | 0 | 564 |  |  |  |  | -0.023742 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.007836 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.023742 | 0 | 603 |  |  |  |  | -0.023742 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.007854 | 43 | 0 | 46.1 | 0 | 1.029 | Cogen | -1 | 0.02376 | 0 | 0 |  |  |  |  | -0.02376 | 0
8262 | ELPS | 1 | South | YES | -0.008156 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.024062 | 0 | 0 |  |  | 0 | 0 | -0.024062 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.009035 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.024941 | 0 | 0 |  |  |  |  | -0.024941 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.009035 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.024941 | 0 | 0 |  |  |  |  | -0.024941 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.009035 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.024941 | 0 | 0 |  |  |  |  | -0.024941 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.009035 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.024941 | 0 | 0 |  |  |  |  | -0.024941 | 0
80010 | EPLVT1 | F | South | YES | -0.009189 | 0 | 0 | 0 |  | 1.0376 | AVR | -1 | 0.025095 | 0 | 0 |  |  | 0 | 0 | -0.025095 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.00937 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.025276 | 0 | 0 |  |  |  |  | -0.025276 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.00937 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.025276 | 0 | 0 |  |  |  |  | -0.025276 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.00979 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.00979 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.00979 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.00979 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.00979 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.00979 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.00979 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.00979 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.00979 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.00979 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.00979 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.00979 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.00979 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.00979 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.00979 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.00979 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.00979 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.00979 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.00979 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.00979 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.011431 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.027337 | 0 | 0 |  |  |  |  | -0.027337 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.011925 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.027831 | 76 | 76 |  |  |  |  | -0.027831 | -2.1152
48732 | CBE_GT2 | 1 | Houston | YES | -0.011925 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.027831 | 76 | 76 |  |  |  |  | -0.027831 | -2.1152
48733 | CBE_ST12 | 1 | Houston | YES | -0.011925 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.027831 | 105 | 105 |  |  |  |  | -0.027831 | -2.9223
48734 | CBE_GT3 | 1 | Houston | YES | -0.011925 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.027831 | 76 | 76 |  |  |  |  | -0.027831 | -2.1152
48735 | CBE_GT4 | 1 | Houston | YES | -0.011925 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.027831 | 76 | 76 |  |  |  |  | -0.027831 | -2.1152
48736 | CBE_ST34 | 1 | Houston | YES | -0.011925 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.027831 | 105 | 105 |  |  |  |  | -0.027831 | -2.9223
5911 | STP_GN1___1 | 1 | Houston | YES | -0.012064 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.02797 | 0 | 0 |  |  |  |  | -0.02797 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.012064 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.02797 | 0 | 0 |  |  |  |  | -0.02797 | 0
8134 | FOR #1 | 1 | South | YES | -0.016713 | 54.1 | 45 | 79 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
8138 | FOR #2 | 2 | South | YES | -0.016713 | 63.1 | 45 | 81 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
8153 | FOR #3 | 3 | South | YES | -0.016713 | 63.1 | 45 | 79.9 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
8154 | FOR #4 | 4 | South | YES | -0.016713 | 63.1 | 60 | 80 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
8155 | FOR #5 | 5 | South | YES | -0.016713 | 63.1 | 60 | 78.4 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
8156 | FOR #6 | 6 | South | YES | -0.016713 | 24.9 | 5 | 25 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
8157 | FOR #7 | 7 | South | YES | -0.016713 | 28.8 | 5 | 46 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
80051 | FOR #8 | 8 | South | YES | -0.016713 | 28 | 28 | 28 | 0 | 1.016 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
80052 | FOR #9 | 9 | South | YES | -0.016713 | 29.7 | 5 | 43.6 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
80053 | FOR #10 | 10 | South | YES | -0.016713 | 68.4 | 45 | 75 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
80226 | ALCOA G | 1 | South | YES | -0.016843 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.032749 | 0 | 0 |  |  | 0 | 0 | -0.032749 | 0
80265 | LARECU40A | 4 | South | YES | -0.016882 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.032788 | 100 | 100 |  |  | -1.6882 | 100 | -0.032788 | -3.2788
80266 | LARECU50A | 5 | South | YES | -0.016882 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.032788 | 100 | 100 |  |  | -1.6882 | 100 | -0.032788 | -3.2788
80012 | LAR | F | South | YES | -0.016883 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.032789 | 0 | 0 |  |  | 0 | 0 | -0.032789 | 0
8147 | UCAR #2 | 10 | South | YES | -0.017275 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
8148 | UCAR #1 | 2 | South | YES | -0.017275 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
80137 | CSDR89 | 8 | South | YES | -0.017275 | 33.9 | 0 | 39 |  | 1.003 | DCTie | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
80137 | CSDR89 | 9 | South | YES | -0.017275 | 0 | 0 | 15 |  | 1.003 | DCTie | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
80138 | CSDR7 | 7 | South | YES | -0.017275 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
80139 | CSDR56 | 5 | South | YES | -0.017275 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
80139 | CSDR56 | 6 | South | YES | -0.017275 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
80140 | CSDR11 | 11 | South | YES | -0.017275 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
88299 | ZAPATA | F | South | YES | -0.017306 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.033212 | 0 | 0 |  |  | 0 | 0 | -0.033212 | 0
80227 | AIRCO G | 1 | South | YES | -0.017327 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.033233 | 0 | 0 |  |  | 0 | 0 | -0.033233 | 0
80224 | VISTRONG1 | 1 | South | YES | -0.017444 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.03335 | 0 | 0 |  |  | 0 | 0 | -0.03335 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.017444 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.03335 | 0 | 0 |  |  | 0 | 0 | -0.03335 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.017568 | 17.6 | 6 | 22 | 0 | 1.0223 | GST | -1 | 0.033474 | 22 | 22 |  |  | -0.3865 | 22 | -0.033474 | -0.73644
5505 | RAYBURNGEN1 | 1 | South | YES | -0.017568 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.033474 | 11 | 11 |  |  | -0.19325 | 11 | -0.033474 | -0.36822
5506 | RAYBURNGEN2 | 1 | South | YES | -0.017568 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.033474 | 11 | 11 |  |  | -0.19325 | 11 | -0.033474 | -0.36822
5728 | FALCONHYDRO2 | 2 | South | YES | -0.017599 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.033505 | 0 | 0 |  |  | 0 | 0 | -0.033505 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.017599 | 11 | 0 | 11 | 0 | 1.0227 | Hydro | -1 | 0.033505 | 0 | 0 |  |  | 0 | 0 | -0.033505 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.017599 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.033505 | 0 | 0 |  |  | 0 | 0 | -0.033505 | 0
5508 | RAYBURNCC9 | 1 | South | YES | -0.017736 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.033642 | 47.7 | 47.7 |  |  | -0.84601 | 47.7 | -0.033642 | -1.6047
5509 | RAYBURNCC10 | 1 | South | YES | -0.017736 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.033642 | 37.3 | 37.3 |  |  | -0.66155 | 37.3 | -0.033642 | -1.2549
5511 | RAYBURNCC7 | 1 | South | YES | -0.017736 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.033642 | 47.5 | 47.5 |  |  | -0.84246 | 47.5 | -0.033642 | -1.598
5512 | RAYBURNCC8 | 1 | South | YES | -0.017736 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.033642 | 49.3 | 49.3 |  |  | -0.87438 | 49.3 | -0.033642 | -1.6586
8066 | DUP1V#1 | 1 | South | YES | -0.01776 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.033666 | 0 | 0 |  |  | 0 | 0 | -0.033666 | 0
88508 | FALFURRI | F | South | YES | -0.017762 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.033668 | 0 | 0 |  |  | 0 | 0 | -0.033668 | 0
8926 | LGE_GT10A | 1 | South | YES | -0.017767 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.017767 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.017767 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
8930 | ICPGN10A | 1 | South | YES | -0.017767 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
8931 | ICPGN20A | 2 | South | YES | -0.017767 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
8932 | ICPGN30A | 3 | South | YES | -0.017767 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
80223 | REYSHR G | 1 | South | YES | -0.017767 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
8933 | FGNTS001 | 1 | South | YES | -0.017904 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.03381 | 146.5 | 146.5 |  |  | -2.6229 | 146.5 | -0.03381 | -4.9532
8934 | FGNTS101 | 2 | South | YES | -0.017904 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.03381 | 147.9 | 147.9 |  |  | -2.648 | 147.9 | -0.03381 | -5.0006
8935 | FGNTS201 | 3 | South | YES | -0.017904 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.03381 | 173 | 173 |  |  | -3.0974 | 173 | -0.03381 | -5.8492
8560 | CNOPGT1 | 1 | South | YES | -0.017914 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.03382 | 0 | 0 |  |  | 0 | 0 | -0.03382 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.017914 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.03382 | 0 | 0 |  |  | 0 | 0 | -0.03382 | 0
8562 | CNOPST1 | 3 | South | YES | -0.017914 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.03382 | 0 | 0 |  |  | 0 | 0 | -0.03382 | 0
8456 | COSW#1 | 1 | South | YES | -0.017922 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.033828 | 0 | 0 |  |  | 0 | 0 | -0.033828 | 0
8457 | COSW#2 | 2 | South | YES | -0.017922 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.033828 | 0 | 0 |  |  | 0 | 0 | -0.033828 | 0
8173 | VICEC51A | 5 | South | YES | -0.01794 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.033846 | 144 | 144 |  |  | -2.5834 | 144 | -0.033846 | -4.8739
8174 | VICEC61A | 6 | South | YES | -0.01794 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.033846 | 188 | 188 |  |  | -3.3727 | 188 | -0.033846 | -6.3631
8459 | B_DAVIS0B | MB | South | YES | -0.017941 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.033847 | 0 | 0 |  |  | 0 | 0 | -0.033847 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.017941 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.033847 | 0 | 0 |  |  | 0 | 0 | -0.033847 | 0
8506 | VAL #1 | 1 | South | YES | -0.017949 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.033855 | 0 | 0 |  |  | 0 | 0 | -0.033855 | 0
8507 | VAL #2 | 2 | South | YES | -0.017949 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.033855 | 0 | 0 |  |  | 0 | 0 | -0.033855 | 0
8936 | MVGN#1 | 1 | South | YES | -0.017954 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.03386 | 216.6 | 216.6 |  |  | -3.8888 | 216.6 | -0.03386 | -7.3342
8937 | MVGN#2 | 2 | South | YES | -0.017954 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.03386 | 216.7 | 216.7 |  |  | -3.8906 | 216.7 | -0.03386 | -7.3376
8938 | MVGN#3 | 3 | South | YES | -0.017954 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.03386 | 250.9 | 250.9 |  |  | -4.5047 | 250.9 | -0.03386 | -8.4956
8981 | HECN1 | 1 | South | YES | -0.017954 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.03386 | 144.8 | 144.8 |  |  | -2.5997 | 144.8 | -0.03386 | -4.903
8982 | HECN2 | 2 | South | YES | -0.017954 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.03386 | 144.1 | 144.1 |  |  | -2.5872 | 144.1 | -0.03386 | -4.8793
8983 | HECN3 | 3 | South | YES | -0.017954 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.03386 | 171.9 | 171.9 |  |  | -3.0863 | 171.9 | -0.03386 | -5.8206
8461 | KOCH_UP0A | 1 | South | YES | -0.017963 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.033869 | 0 | 0 |  |  | 0 | 0 | -0.033869 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.017965 | 30.3 | 0 | 38 |  | 1.027 | Cogen | -1 | 0.033871 | 0 | 0 |  |  | 0 | 0 | -0.033871 | 0
5932 | SI_RAY9 | 9 | South | YES | -0.017991 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.033897 | 38 | 38 |  |  | -0.68366 | 38 | -0.033897 | -1.2881
5933 | SI_RAY6 | 6 | South | YES | -0.017991 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.033897 | 19.3 | 19.3 |  |  | -0.34723 | 19.3 | -0.033897 | -0.65422
5935 | SI_RAY10 | 10 | South | YES | -0.017991 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.033897 | 47 | 47 |  |  | -0.84558 | 47 | -0.033897 | -1.5932
80003 | MILHWYS | F | South | YES | -0.017991 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.033897 | 0 | 0 |  |  | 0 | 0 | -0.033897 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.01801 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.033916 | 0 | 0 |  |  | 0 | 0 | -0.033916 | 0
80080 | GWINDT11A | 1 | South | YES | -0.018012 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 94 |  |  | 0 | 0 | -0.033918 | 0
80080 | GWINDT11A | 4 | South | YES | -0.018012 | 8.2 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 19 |  |  | 0 | 0 | -0.033918 | 0
80080 | GWINDT11A | 2 | South | YES | -0.018012 | 17.7 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 41 |  |  | 0 | 0 | -0.033918 | 0
80080 | GWINDT11A | 3 | South | YES | -0.018012 | 16.4 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 38 |  |  | 0 | 0 | -0.033918 | 0
80081 | GWINDT21A | 3 | South | YES | -0.018012 | 18.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 43 |  |  | 0 | 0 | -0.033918 | 0
80081 | GWINDT21A | 1 | South | YES | -0.018012 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 94 |  |  | 0 | 0 | -0.033918 | 0
80081 | GWINDT21A | 4 | South | YES | -0.018012 | 9.5 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 22 |  |  | 0 | 0 | -0.033918 | 0
80081 | GWINDT21A | 2 | South | YES | -0.018012 | 15.5 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 36 |  |  | 0 | 0 | -0.033918 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.018012 | 63 | 0 | 146 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 146 |  |  | 0 | 0 | -0.033918 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.018012 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 50 |  |  | 0 | 0 | -0.033918 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.018012 | 23.7 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 55 |  |  | 0 | 0 | -0.033918 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.018012 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 50 |  |  | 0 | 0 | -0.033918 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.01858 | 19.2 | 6 | 24 | 0 | 1.0161 | GST | -1 | 0.034486 | 24 | 24 |  |  | -0.44592 | 24 | -0.034486 | -0.82767
5891 | PEARSALLGEN2 | 1 | South | YES | -0.01858 | 19.4 | 6 | 24.3 | 0 | 1.0161 | GST | -1 | 0.034486 | 24.3 | 24.3 |  |  | -0.45149 | 24.3 | -0.034486 | -0.83802
5892 | PEARSALLGEN3 | 1 | South | YES | -0.01858 | 19.1 | 6 | 23.9 | 0 | 1.0161 | GST | -1 | 0.034486 | 23.9 | 23.9 |  |  | -0.44406 | 23.9 | -0.034486 | -0.82423
8161 | COLETO0A | 1 | South | YES | -0.018745 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.034651 | 0 | 633 |  |  | 0 | 0 | -0.034651 | 0
88198 | BEEVILLE | F | South | YES | -0.018899 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.034805 | 0 | 0 |  |  | 0 | 0 | -0.034805 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.020334 | 396.3 | 180 | 396.3 | 0 | 1.0331 | LIGCO | -1 | 0.03624 | 0 | 396.3 |  |  | 0 | 0 | -0.03624 | 0
8189 | CUECPL2A | 1 | South | YES | -0.021299 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.037205 | 0 | 0 |  |  | 0 | 0 | -0.037205 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.021672 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.037578 | 0 | 436 |  |  | 0 | 0 | -0.037578 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.021684 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.03759 | 0 | 606 |  |  | 0 | 0 | -0.03759 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.021684 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.03759 | 0 | 598 |  |  | 0 | 0 | -0.03759 | 0
5401 | CALAVER_JKS1 | 1 | South | YES | -0.021692 | 562 | 100 | 562 | 0 | 1.018 | LIGCO | -1 | 0.037598 | 0 | 562 |  |  | 0 | 0 | -0.037598 | 0
5264 | LEON_LCP3G3 | 3 | South | YES | -0.021772 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.037678 | 58 | 58 |  |  | -1.2628 | 58 | -0.037678 | -2.1853
5265 | LEON_LCP4G4 | 4 | South | YES | -0.021772 | 71.2 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.037678 | 89 | 89 |  |  | -1.9377 | 89 | -0.037678 | -3.3534
5266 | LEON_LCPCT1 | 1 | South | YES | -0.021772 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.037678 | 44 | 44 |  |  | -0.95797 | 44 | -0.037678 | -1.6579
5267 | LEON_LCPCT2 | 2 | South | YES | -0.021772 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.037678 | 44 | 44 |  |  | -0.95797 | 44 | -0.037678 | -1.6579
5268 | LEON_LCPCT3 | 3 | South | YES | -0.021772 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.037678 | 43 | 43 |  |  | -0.9362 | 43 | -0.037678 | -1.6202
5269 | LEON_LCPCT4 | 4 | South | YES | -0.021772 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.037678 | 45 | 45 |  |  | -0.97974 | 45 | -0.037678 | -1.6955
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.021882 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.037788 | 215 | 215 |  |  | -4.7046 | 215 | -0.037788 | -8.1245
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.021882 | 172.8 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.037788 | 216 | 216 |  |  | -4.7265 | 216 | -0.037788 | -8.1623
5031 | BRA_VHBCT1 | 1 | South | YES | -0.021882 | 44 | 24 | 44 | 0 | 1.0192 | GST | -1 | 0.037788 | 44 | 44 |  |  | -0.96281 | 44 | -0.037788 | -1.6627
5032 | BRA_VHBCT2 | 2 | South | YES | -0.021882 | 44 | 24 | 44 | 0 | 1.0192 | GST | -1 | 0.037788 | 44 | 44 |  |  | -0.96281 | 44 | -0.037788 | -1.6627
5033 | BRA_VHBCT3 | 3 | South | YES | -0.021882 | 43 | 24 | 43 | 0 | 1.0192 | GST | -1 | 0.037788 | 43 | 43 |  |  | -0.94093 | 43 | -0.037788 | -1.6249
5034 | BRA_VHBCT4 | 4 | South | YES | -0.021882 | 45 | 24 | 45 | 0 | 1.0192 | GST | -1 | 0.037788 | 45 | 45 |  |  | -0.98469 | 45 | -0.037788 | -1.7005
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.02191 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.037816 | 407 | 407 |  |  | -8.9174 | 407 | -0.037816 | -15.3913
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.021918 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.037824 | 155 | 155 |  |  | -3.3973 | 155 | -0.037824 | -5.8628
5477 | BRA_AVR1_ST1 | 1 | South | YES | -0.021918 | 174 | 138 | 174 | 0 | 1.017 | CC | -1 | 0.037824 | 174 | 174 |  |  | -3.8137 | 174 | -0.037824 | -6.5815
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.021918 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.037824 | 155 | 155 |  |  | -3.3973 | 155 | -0.037824 | -5.8628
5396 | CALAVER_OWS1 | 1 | South | YES | -0.021919 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.037825 | 418 | 418 |  |  | -9.1621 | 418 | -0.037825 | -15.811
5397 | CALAVER_OWS2 | 2 | South | YES | -0.021919 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.037825 | 400 | 400 |  |  | -8.7676 | 400 | -0.037825 | -15.1302
5111 | CALAVER_JTD1 | 1 | South | YES | -0.021953 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.037859 | 0 | 430 |  |  | 0 | 0 | -0.037859 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.021953 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.037859 | 0 | 430 |  |  | 0 | 0 | -0.037859 | 0
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.021978 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.037884 | 61 | 61 |  |  | -1.3407 | 61 | -0.037884 | -2.311
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.021978 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.037884 | 95 | 95 |  |  | -2.0879 | 95 | -0.037884 | -3.599
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.021978 | 120.8 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.037884 | 151 | 151 |  |  | -3.3187 | 151 | -0.037884 | -5.7205
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.021984 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.03789 | 147 | 147 |  |  | -3.2316 | 147 | -0.03789 | -5.5699
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.021984 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.03789 | 138 | 138 |  |  | -3.0338 | 138 | -0.03789 | -5.2289
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.021984 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.03789 | 146 | 146 |  |  | -3.2097 | 146 | -0.03789 | -5.532
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.021984 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.03789 | 149 | 149 |  |  | -3.2756 | 149 | -0.03789 | -5.6457
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.021984 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.03789 | 182 | 182 |  |  | -4.0011 | 182 | -0.03789 | -6.8961
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.021984 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.03789 | 203 | 203 |  |  | -4.4628 | 203 | -0.03789 | -7.6918
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.022533 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.038439 | 148 | 148 |  |  | -3.3349 | 148 | -0.038439 | -5.689
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.022533 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.038439 | 148 | 148 |  |  | -3.3349 | 148 | -0.038439 | -5.689
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.022533 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.038439 | 154 | 154 |  |  | -3.4701 | 154 | -0.038439 | -5.9197
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.022533 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.038439 | 293 | 293 |  |  | -6.6022 | 293 | -0.038439 | -11.2628
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.022763 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.038669 | 0 | 0 |  |  | 0 | 0 | -0.038669 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.022763 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.038669 | 0 | 0 |  |  | 0 | 0 | -0.038669 | 0
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.022869 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.038775 | 0 | 0 |  |  | 0 | 0 | -0.038775 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.022946 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.038852 | 50 | 50 |  |  | -1.1473 | 50 | -0.038852 | -1.9426
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.022946 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.038852 | 50 | 50 |  |  | -1.1473 | 50 | -0.038852 | -1.9426
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.022946 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.038852 | 50 | 50 |  |  | -1.1473 | 50 | -0.038852 | -1.9426
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.022946 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.038852 | 50 | 50 |  |  | -1.1473 | 50 | -0.038852 | -1.9426
3432 | SANDOW_4G | 4 | South | YES | -0.023059 | 580 | 225 | 580 | 0 | 1.029 | LIGCO | -1 | 0.038965 | 0 | 580 |  |  | 0 | 0 | -0.038965 | 0
13432 | SANDOW_5G | 5 | South | YES | -0.023059 | 581 | 225 | 581 | 0 | 1.029 | LIGCO | -1 | 0.038965 | 0 | 581 |  |  | 0 | 0 | -0.038965 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.023096 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.039002 | 223.9 | 223.9 |  |  | -5.1712 | 223.9 | -0.039002 | -8.7326
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.023096 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.039002 | 225 | 225 |  |  | -5.1966 | 225 | -0.039002 | -8.7755
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.023096 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.039002 | 224.6 | 224.6 |  |  | -5.1874 | 224.6 | -0.039002 | -8.7599
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.023096 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.039002 | 226.7 | 226.7 |  |  | -5.2359 | 226.7 | -0.039002 | -8.8419
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.023168 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.039074 | 0 | 0 |  |  | 0 | 0 | -0.039074 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.023168 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.039074 | 0 | 0 |  |  | 0 | 0 | -0.039074 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.023168 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.039074 | 0 | 0 |  |  | 0 | 0 | -0.039074 | 0
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.023219 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.039125 | 158 | 158 |  |  | -3.6686 | 158 | -0.039125 | -6.1818
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.023219 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.039125 | 160 | 160 |  |  | -3.715 | 160 | -0.039125 | -6.2601
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.023219 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.039125 | 175 | 175 |  |  | -4.0633 | 175 | -0.039125 | -6.847
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.02411 | 152.5 | 83.5 | 152.5 |  | 1.004 | CC | -1 | 0.040016 | 152.5 | 152.5 |  |  | -3.6768 | 152.5 | -0.040016 | -6.1025
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.02411 | 149.5 | 83.5 | 149.5 |  | 1.004 | CC | -1 | 0.040016 | 149.5 | 149.5 |  |  | -3.6044 | 149.5 | -0.040016 | -5.9825
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.02411 | 232.6 | 42 | 232.6 |  | 1.004 | CC | -1 | 0.040016 | 232.6 | 232.6 |  |  | -5.608 | 232.6 | -0.040016 | -9.3078
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.025581 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.041487 | 132 | 132 |  |  | -3.3767 | 132 | -0.041487 | -5.4763
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.025581 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.041487 | 139 | 139 |  |  | -3.5558 | 139 | -0.041487 | -5.7668
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.025581 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.041487 | 329 | 329 |  |  | -8.4161 | 329 | -0.041487 | -13.6494
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.025857 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.041763 | 0 | 0 |  |  | 0 | 0 | -0.041763 | 0
9016 | SANDH_G1 | 1 | South | YES | -0.02825 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.044156 | 49 | 49 |  |  | -1.3842 | 49 | -0.044156 | -2.1637
9017 | SANDH_G2 | 2 | South | YES | -0.02825 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.044156 | 46 | 46 |  |  | -1.2995 | 46 | -0.044156 | -2.0312
9018 | SANDH_G3 | 3 | South | YES | -0.02825 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.044156 | 46 | 46 |  |  | -1.2995 | 46 | -0.044156 | -2.0312
9019 | SANDH_G4 | 4 | South | YES | -0.02825 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.044156 | 47 | 47 |  |  | -1.3277 | 47 | -0.044156 | -2.0754
9020 | SANDHG5A | 5A | South | YES | -0.02825 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.044156 | 155 | 155 |  |  | -4.3788 | 155 | -0.044156 | -6.8442
9021 | SANDHG5C | 5C | South | YES | -0.02825 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.044156 | 148 | 148 |  |  | -4.181 | 148 | -0.044156 | -6.5352
9002 | DECKR_G3 | 3 | South | YES | -0.028261 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.044167 | 42 | 42 |  |  | -1.187 | 42 | -0.044167 | -1.855
9003 | DECKR_G4 | 4 | South | YES | -0.028261 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.044167 | 44 | 44 |  |  | -1.2435 | 44 | -0.044167 | -1.9434
9004 | DECKR_G5 | 5 | South | YES | -0.028261 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.044167 | 44 | 44 |  |  | -1.2435 | 44 | -0.044167 | -1.9434
9005 | DECKR_G6 | 6 | South | YES | -0.028261 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.044167 | 47 | 47 |  |  | -1.3283 | 47 | -0.044167 | -2.0759
9000 | DECKR_G1 | 1 | South | YES | -0.028551 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.044457 | 321 | 321 |  |  | -9.1649 | 321 | -0.044457 | -14.2708
9001 | DECKR_G2 | 2 | South | YES | -0.028551 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.044457 | 426 | 426 |  |  | -12.1627 | 426 | -0.044457 | -18.9389
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.029327 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.045233 | 0 | 0 |  |  | 0 | 0 | -0.045233 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.029327 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.045233 | 0 | 0 |  |  | 0 | 0 | -0.045233 | 0
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.038541 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.054447 | 0 | 0 |  |  | 0 | 0 | -0.054447 | 0
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.038541 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.054447 | 0 | 0 |  |  | 0 | 0 | -0.054447 | 0
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.038541 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.054447 | 0 | 0 |  |  | 0 | 0 | -0.054447 | 0
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.055725 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.071631 | 0 | 0 |  |  | 0 | 0 | -0.071631 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.055725 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.071631 | 0 | 0 |  |  | 0 | 0 | -0.071631 | 0
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.063302 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.079208 | 423.3 | 423.3 |  |  | -26.7957 | 423.3 | -0.079208 | -33.5289
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.064261 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.080167 | 0 | 0 |  |  | 0 | 0 | -0.080167 | 0
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.064261 | 23 | 0 | 29.8 |  | 1 | Hydro | -1 | 0.080167 | 0 | 0 |  |  | 0 | 0 | -0.080167 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.079507 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.095413 | 0 | 0 |  |  | 0 | 0 | -0.095413 | 0
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.087986 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.10389 | 0 | 0 |  |  | 0 | 0 | -0.10389 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.087986 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.10389 | 0 | 0 |  |  | 0 | 0 | -0.10389 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.087986 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.10389 | 0 | 0 |  |  | 0 | 0 | -0.10389 | 0
Note on AL4: Zonal Cap - Zonal Impact

## Distributed Slack - Inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | P Sensitivity of Bus | Gen MW | Min MW | Max MW | V Sensitivity of Bus | Set Volt | Tech Type | Zone Impact | Zone Correlation | Inc Max | Dec Max | Souce S.F. Weighting | Souce Capacity | Sink S.F. Weighting | Sink Capacity | PTDF Calc | PTDF Weighting | Cumulative Concentrated Capacity | Cumulative Concentrated Impact | Cont_ TempleSS to LakeCreek and TemplePEC to Tradinghouse OL_ Evant to Goldthwaite
7022 | L_BUCHAN1_1Y | 1 | South | YES | -0.087986 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.10389 | 0 | 0 |  |  | 0 | 0 | -0.10389 | 0 | 0 | 0
7023 | L_BUCHAN1_2Y | 2 | South | YES | -0.087986 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.10389 | 0 | 0 |  |  | 0 | 0 | -0.10389 | 0 | 0 | 0
7024 | L_BUCHAN1_3Y | 3 | South | YES | -0.087986 | 0 | 0 | 15 |  | 1 | Hydro | -1 | 0.10389 | 0 | 0 |  |  | 0 | 0 | -0.10389 | 0 | 0 | 0
7026 | L_INKSDA1_1Y | 1 | South | YES | -0.079507 | 0 | 0 | 13.7 |  | 1 | Hydro | -1 | 0.095413 | 0 | 0 |  |  | 0 | 0 | -0.095413 | 0 | 0 | 0 | Weighted Shift Factors
7035 | L_WIRTZ_1G1Y | 1 | South | YES | -0.064261 | 0 | 0 | 29 |  | 1 | Hydro | -1 | 0.080167 | 0 | 0 |  |  | 0 | 0 | -0.080167 | 0 | 0 | 0 | North | 0.015906
7036 | L_WIRTZ_1G2Y | 2 | South | YES | -0.064261 | 23 | 0 | 29.8 |  | 1 | Hydro | -1 | 0.080167 | 0 | 0 |  |  | 0 | 0 | -0.080167 | 0 | 0 | 0 | South | -0.023766
7000 | L_FERGUS1_1Y | 1 | South | YES | -0.063302 | 400 | 65 | 423.3 | 0 | 1.015 | GSC | -1 | 0.079208 | 423.3 | 423.3 |  |  | -26.7957 | 423.3 | -0.079208 | -33.5289 | 423.3 | 33.5289 |  | 0.039673
7028 | L_MARBFA1_1Y | 1 | South | YES | -0.055725 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.071631 | 0 | 0 |  |  | 0 | 0 | -0.071631 | 0
7029 | L_MARBFA1_2Y | 2 | South | YES | -0.055725 | 0 | 0 | 18 |  | 1 | Hydro | -1 | 0.071631 | 0 | 0 |  |  | 0 | 0 | -0.071631 | 0 |  |  | Line Cap | 128
7031 | L_MARSFO1G1Y | 1 | South | YES | -0.038541 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.054447 | 0 | 0 |  |  | 0 | 0 | -0.054447 | 0 |  |  | Conc Gen | 423.3
7032 | L_MARSFO1G2Y | 2 | South | YES | -0.038541 | 0 | 0 | 35 |  | 1 | Hydro | -1 | 0.054447 | 0 | 0 |  |  | 0 | 0 | -0.054447 | 0 |  |  | Weighted Imp. | 33.5289
7033 | L_MARSFO1G3Y | 3 | South | YES | -0.038541 | 0 | 0 | 36 |  | 1 | Hydro | -1 | 0.054447 | 0 | 0 |  |  | 0 | 0 | -0.054447 | 0 |  |  | PTDF | 0.079208
7020 | L_AUSTPL1_1Y | 2 | South | YES | -0.029327 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.045233 | 0 | 0 |  |  | 0 | 0 | -0.045233 | 0
7020 | L_AUSTPL1_1Y | 1 | South | YES | -0.029327 | 0 | 0 | 8 |  | 1 | Hydro | -1 | 0.045233 | 0 | 0 |  |  | 0 | 0 | -0.045233 | 0 |  |  | Concentration | 1.9966
9000 | DECKR_G1 | 1 | South | YES | -0.028551 | 280 | 50 | 321 | 0 | 1.015 | GST | -1 | 0.044457 | 321 | 321 |  |  | -9.1649 | 321 | -0.044457 | -14.2708
9001 | DECKR_G2 | 2 | South | YES | -0.028551 | 400 | 50 | 426 | 0 | 1.015 | GST | -1 | 0.044457 | 426 | 426 |  |  | -12.1627 | 426 | -0.044457 | -18.9389 |  |  |  | Pass
9002 | DECKR_G3 | 3 | South | YES | -0.028261 | 0 | 24 | 42 |  | 1.015 | GGT | -1 | 0.044167 | 42 | 42 |  |  | -1.187 | 42 | -0.044167 | -1.855
9003 | DECKR_G4 | 4 | South | YES | -0.028261 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.044167 | 44 | 44 |  |  | -1.2435 | 44 | -0.044167 | -1.9434
9004 | DECKR_G5 | 5 | South | YES | -0.028261 | 44 | 24 | 44 | 0 | 1.015 | GGT | -1 | 0.044167 | 44 | 44 |  |  | -1.2435 | 44 | -0.044167 | -1.9434
9005 | DECKR_G6 | 6 | South | YES | -0.028261 | 44 | 24 | 47 | 0 | 1.015 | GGT | -1 | 0.044167 | 47 | 47 |  |  | -1.3283 | 47 | -0.044167 | -2.0759
9016 | SANDH_G1 | 1 | South | YES | -0.02825 | 45 | 2 | 49 | 0 | 1.0175 | GGT | -1 | 0.044156 | 49 | 49 |  |  | -1.3842 | 49 | -0.044156 | -2.1637
9017 | SANDH_G2 | 2 | South | YES | -0.02825 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.044156 | 46 | 46 |  |  | -1.2995 | 46 | -0.044156 | -2.0312
9018 | SANDH_G3 | 3 | South | YES | -0.02825 | 45 | 2 | 46 | 0 | 1.0175 | GGT | -1 | 0.044156 | 46 | 46 |  |  | -1.2995 | 46 | -0.044156 | -2.0312
9019 | SANDH_G4 | 4 | South | YES | -0.02825 | 0 | 2 | 47 |  | 1.0175 | GGT | -1 | 0.044156 | 47 | 47 |  |  | -1.3277 | 47 | -0.044156 | -2.0754
9020 | SANDHG5A | 5A | South | YES | -0.02825 | 150 | 84 | 155 | 0 | 1.0175 | CC | -1 | 0.044156 | 155 | 155 |  |  | -4.3788 | 155 | -0.044156 | -6.8442
9021 | SANDHG5C | 5C | South | YES | -0.02825 | 140 | 0 | 148 | 0 | 1.0175 | CC | -1 | 0.044156 | 148 | 148 |  |  | -4.181 | 148 | -0.044156 | -6.5352
7487 | L_CANYHY8_1Y | 1 | South | YES | -0.025857 | 0 | 0 | 6 |  | 1 | Hydro | -1 | 0.041763 | 0 | 0 |  |  | 0 | 0 | -0.041763 | 0
7004 | L_SIMGID1_1Y | 1 | South | YES | -0.025581 | 132 | 40 | 132 | 0 | 1.02 | GST | -1 | 0.041487 | 132 | 132 |  |  | -3.3767 | 132 | -0.041487 | -5.4763
7005 | L_SIMGID1_2Y | 2 | South | YES | -0.025581 | 133 | 32 | 139 | 0 | 1.02 | GST | -1 | 0.041487 | 139 | 139 |  |  | -3.5558 | 139 | -0.041487 | -5.7668
7006 | L_SIMGID1_3Y | 3 | South | YES | -0.025581 | 324.9 | 60 | 329 | 0 | 1.02 | GST | -1 | 0.041487 | 329 | 329 |  |  | -8.4161 | 329 | -0.041487 | -13.6494
7807 | L_BASTEN1_1Y | 1 | South | YES | -0.02411 | 152.5 | 83.5 | 152.5 |  | 1.004 | CC | -1 | 0.040016 | 152.5 | 152.5 |  |  | -3.6768 | 152.5 | -0.040016 | -6.1025
7808 | L_BASTEN1_2Y | 1 | South | YES | -0.02411 | 149.5 | 83.5 | 149.5 |  | 1.004 | CC | -1 | 0.040016 | 149.5 | 149.5 |  |  | -3.6044 | 149.5 | -0.040016 | -5.9825
7809 | L_BASTEN1_3Y | 1 | South | YES | -0.02411 | 232.6 | 42 | 232.6 |  | 1.004 | CC | -1 | 0.040016 | 232.6 | 232.6 |  |  | -5.608 | 232.6 | -0.040016 | -9.3078
7007 | L_LOSTPI1_1Y | 1 | South | YES | -0.023219 | 158.6 | 110 | 158 | 0 | 1 | CC | -1 | 0.039125 | 158 | 158 |  |  | -3.6686 | 158 | -0.039125 | -6.1818
7008 | L_LOSTPI1_2Y | 2 | South | YES | -0.023219 | 157.7 | 107 | 160 | 0 | 1 | CC | -1 | 0.039125 | 160 | 160 |  |  | -3.715 | 160 | -0.039125 | -6.2601
7009 | L_LOSTPI1_3Y | 3 | South | YES | -0.023219 | 173.9 | 72 | 175 | 0 | 1 | CC | -1 | 0.039125 | 175 | 175 |  |  | -4.0633 | 175 | -0.039125 | -6.847
7605 | L_MCQUEE9_1Y | 1 | South | YES | -0.023168 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.039074 | 0 | 0 |  |  | 0 | 0 | -0.039074 | 0
7605 | L_MCQUEE9_1Y | 3 | South | YES | -0.023168 | 0 | 0 | 2.8 |  | 1.025 | Hydro | -1 | 0.039074 | 0 | 0 |  |  | 0 | 0 | -0.039074 | 0
7605 | L_MCQUEE9_1Y | 2 | South | YES | -0.023168 | 0 | 0 | 2.4 |  | 1.025 | Hydro | -1 | 0.039074 | 0 | 0 |  |  | 0 | 0 | -0.039074 | 0
7014 | L_HAYSEN1_1Y | 1 | South | YES | -0.023096 | 223.9 | 74 | 223.9 | 0 | 1.008 | CC | -1 | 0.039002 | 223.9 | 223.9 |  |  | -5.1712 | 223.9 | -0.039002 | -8.7326
7015 | L_HAYSEN1_2Y | 2 | South | YES | -0.023096 | 225 | 74 | 225 | 0 | 1.008 | CC | -1 | 0.039002 | 225 | 225 |  |  | -5.1966 | 225 | -0.039002 | -8.7755
7016 | L_HAYSEN1_3Y | 3 | South | YES | -0.023096 | 224.6 | 74 | 224.6 | 0 | 1.008 | CC | -1 | 0.039002 | 224.6 | 224.6 |  |  | -5.1874 | 224.6 | -0.039002 | -8.7599
7017 | L_HAYSEN1_4Y | 4 | South | YES | -0.023096 | 226.7 | 74 | 226.7 | 0 | 1.008 | CC | -1 | 0.039002 | 226.7 | 226.7 |  |  | -5.2359 | 226.7 | -0.039002 | -8.8419
3432 | SANDOW_4G | 4 | South | YES | -0.023059 | 580 | 225 | 580 | 0 | 1.029 | LIGCO | -1 | 0.038965 | 0 | 580 |  |  | 0 | 0 | -0.038965 | 0
13432 | SANDOW_5G | 5 | South | YES | -0.023059 | 581 | 225 | 581 | 0 | 1.029 | LIGCO | -1 | 0.038965 | 0 | 581 |  |  | 0 | 0 | -0.038965 | 0
7303 | L_WPPGS12_1Y | 1 | South | YES | -0.022946 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.038852 | 50 | 50 |  |  | -1.1473 | 50 | -0.038852 | -1.9426
7303 | L_WPPGS12_1Y | 2 | South | YES | -0.022946 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.038852 | 50 | 50 |  |  | -1.1473 | 50 | -0.038852 | -1.9426
7305 | L_WPPGS34_1Y | 3 | South | YES | -0.022946 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.038852 | 50 | 50 |  |  | -1.1473 | 50 | -0.038852 | -1.9426
7305 | L_WPPGS34_1Y | 4 | South | YES | -0.022946 | 50 | 0 | 50 | 0 | 1.025 | GGT | -1 | 0.038852 | 50 | 50 |  |  | -1.1473 | 50 | -0.038852 | -1.9426
7609 | L_SCHUMA8_1Y | 1 | South | YES | -0.022869 | 0 | 0 | 4 |  | 1 | Hydro | -1 | 0.038775 | 0 | 0 |  |  | 0 | 0 | -0.038775 | 0
7624 | L_LAKEWO9_1Y | 2 | South | YES | -0.022763 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.038669 | 0 | 0 |  |  | 0 | 0 | -0.038669 | 0
7624 | L_LAKEWO9_1Y | 1 | South | YES | -0.022763 | 0 | 0 | 2.4 |  | 1 | Hydro | -1 | 0.038669 | 0 | 0 |  |  | 0 | 0 | -0.038669 | 0
7810 | L_RIONOG1G1Y | 1 | South | YES | -0.022533 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.038439 | 148 | 148 |  |  | -3.3349 | 148 | -0.038439 | -5.689
7811 | L_RIONOG1G2Y | 2 | South | YES | -0.022533 | 148 | 0 | 148 | 0 | 1.02 | CC | -1 | 0.038439 | 148 | 148 |  |  | -3.3349 | 148 | -0.038439 | -5.689
7812 | L_RIONOG1G3Y | 3 | South | YES | -0.022533 | 154 | 0 | 154 | 0 | 1.02 | CC | -1 | 0.038439 | 154 | 154 |  |  | -3.4701 | 154 | -0.038439 | -5.9197
7813 | L_RIONOG1S1Y | 4 | South | YES | -0.022533 | 293 | 0 | 293 | 0 | 1.02 | CC | -1 | 0.038439 | 293 | 293 |  |  | -6.6022 | 293 | -0.038439 | -11.2628
7800 | L_GUADGE1_1Y | 1 | South | YES | -0.021984 | 147 | 30 | 147 | 0 | 1.02 | CC | -1 | 0.03789 | 147 | 147 |  |  | -3.2316 | 147 | -0.03789 | -5.5699
7801 | L_GUADGE1_2Y | 2 | South | YES | -0.021984 | 138 | 30 | 138 | 0 | 1.02 | CC | -1 | 0.03789 | 138 | 138 |  |  | -3.0338 | 138 | -0.03789 | -5.2289
7802 | L_GUADGE1_3Y | 3 | South | YES | -0.021984 | 146 | 30 | 146 | 0 | 1.02 | CC | -1 | 0.03789 | 146 | 146 |  |  | -3.2097 | 146 | -0.03789 | -5.532
7803 | L_GUADGE1_4Y | 4 | South | YES | -0.021984 | 149 | 30 | 149 | 0 | 1.02 | CC | -1 | 0.03789 | 149 | 149 |  |  | -3.2756 | 149 | -0.03789 | -5.6457
7804 | L_GUADGE1_5Y | 5 | South | YES | -0.021984 | 182 | 30 | 182 | 0 | 1.02 | CC | -1 | 0.03789 | 182 | 182 |  |  | -4.0011 | 182 | -0.03789 | -6.8961
7805 | L_GUADGE1_6Y | 6 | South | YES | -0.021984 | 203 | 30 | 203 | 0 | 1.02 | CC | -1 | 0.03789 | 203 | 203 |  |  | -4.4628 | 203 | -0.03789 | -7.6918
5436 | TUTTL_WBT1G1 | 1 | South | YES | -0.021978 | 48.8 | 20 | 61 | 0 | 1.012 | GST | -1 | 0.037884 | 61 | 61 |  |  | -1.3407 | 61 | -0.037884 | -2.311
5438 | TUTTL_WBT3G3 | 3 | South | YES | -0.021978 | 95 | 25 | 95 | 0 | 1.012 | GST | -1 | 0.037884 | 95 | 95 |  |  | -2.0879 | 95 | -0.037884 | -3.599
5439 | TUTTL_WBT4G4 | 4 | South | YES | -0.021978 | 120.8 | 40 | 151 | 0 | 1.012 | GST | -1 | 0.037884 | 151 | 151 |  |  | -3.3187 | 151 | -0.037884 | -5.7205
5111 | CALAVER_JTD1 | 1 | South | YES | -0.021953 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.037859 | 0 | 430 |  |  | 0 | 0 | -0.037859 | 0
5112 | CALAVER_JTD2 | 2 | South | YES | -0.021953 | 430 | 80 | 430 | 0 | 1.0138 | LIGCO | -1 | 0.037859 | 0 | 430 |  |  | 0 | 0 | -0.037859 | 0
5396 | CALAVER_OWS1 | 1 | South | YES | -0.021919 | 418 | 80 | 418 | 0 | 1.0192 | GST | -1 | 0.037825 | 418 | 418 |  |  | -9.1621 | 418 | -0.037825 | -15.811
5397 | CALAVER_OWS2 | 2 | South | YES | -0.021919 | 400 | 80 | 400 | 0 | 1.0192 | GST | -1 | 0.037825 | 400 | 400 |  |  | -8.7676 | 400 | -0.037825 | -15.1302
5476 | BRA_AVR1_CT1 | 1 | South | YES | -0.021918 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.037824 | 155 | 155 |  |  | -3.3973 | 155 | -0.037824 | -5.8628
5477 | BRA_AVR1_ST1 | 1 | South | YES | -0.021918 | 174 | 138 | 174 | 0 | 1.017 | CC | -1 | 0.037824 | 174 | 174 |  |  | -3.8137 | 174 | -0.037824 | -6.5815
5478 | BRA_AVR1_CT2 | 1 | South | YES | -0.021918 | 155 | 90 | 155 | 0 | 1.017 | CC | -1 | 0.037824 | 155 | 155 |  |  | -3.3973 | 155 | -0.037824 | -5.8628
5028 | BRAUNIG_VHB3 | 3 | South | YES | -0.02191 | 407 | 60 | 407 | 0 | 1.0138 | GST | -1 | 0.037816 | 407 | 407 |  |  | -8.9174 | 407 | -0.037816 | -15.3913
5026 | BRAUNIG_VHB1 | 1 | South | YES | -0.021882 | 215 | 40 | 215 | 0 | 1.0192 | GST | -1 | 0.037788 | 215 | 215 |  |  | -4.7046 | 215 | -0.037788 | -8.1245
5027 | BRAUNIG_VHB2 | 2 | South | YES | -0.021882 | 172.8 | 40 | 216 | 0 | 1.0192 | GST | -1 | 0.037788 | 216 | 216 |  |  | -4.7265 | 216 | -0.037788 | -8.1623
5031 | BRA_VHBCT1 | 1 | South | YES | -0.021882 | 44 | 24 | 44 | 0 | 1.0192 | GST | -1 | 0.037788 | 44 | 44 |  |  | -0.96281 | 44 | -0.037788 | -1.6627
5032 | BRA_VHBCT2 | 2 | South | YES | -0.021882 | 44 | 24 | 44 | 0 | 1.0192 | GST | -1 | 0.037788 | 44 | 44 |  |  | -0.96281 | 44 | -0.037788 | -1.6627
5033 | BRA_VHBCT3 | 3 | South | YES | -0.021882 | 43 | 24 | 43 | 0 | 1.0192 | GST | -1 | 0.037788 | 43 | 43 |  |  | -0.94093 | 43 | -0.037788 | -1.6249
5034 | BRA_VHBCT4 | 4 | South | YES | -0.021882 | 45 | 24 | 45 | 0 | 1.0192 | GST | -1 | 0.037788 | 45 | 45 |  |  | -0.98469 | 45 | -0.037788 | -1.7005
5264 | LEON_LCP3G3 | 3 | South | YES | -0.021772 | 0 | 20 | 58 |  | 1.0197 | GST | -1 | 0.037678 | 58 | 58 |  |  | -1.2628 | 58 | -0.037678 | -2.1853
5265 | LEON_LCP4G4 | 4 | South | YES | -0.021772 | 71.2 | 25 | 89 | 0 | 1.0197 | GST | -1 | 0.037678 | 89 | 89 |  |  | -1.9377 | 89 | -0.037678 | -3.3534
5266 | LEON_LCPCT1 | 1 | South | YES | -0.021772 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.037678 | 44 | 44 |  |  | -0.95797 | 44 | -0.037678 | -1.6579
5267 | LEON_LCPCT2 | 2 | South | YES | -0.021772 | 44 | 24 | 44 | 0 | 1.0197 | GGT | -1 | 0.037678 | 44 | 44 |  |  | -0.95797 | 44 | -0.037678 | -1.6579
5268 | LEON_LCPCT3 | 3 | South | YES | -0.021772 | 43 | 24 | 43 | 0 | 1.0197 | GGT | -1 | 0.037678 | 43 | 43 |  |  | -0.9362 | 43 | -0.037678 | -1.6202
5269 | LEON_LCPCT4 | 4 | South | YES | -0.021772 | 45 | 24 | 45 | 0 | 1.0197 | GGT | -1 | 0.037678 | 45 | 45 |  |  | -0.97974 | 45 | -0.037678 | -1.6955
5401 | CALAVER_JKS1 | 1 | South | YES | -0.021692 | 562 | 100 | 562 | 0 | 1.018 | LIGCO | -1 | 0.037598 | 0 | 562 |  |  | 0 | 0 | -0.037598 | 0
7010 | L_FPPYD11_1Y | 1 | South | YES | -0.021684 | 547.4 | 200 | 606 | 0 | 1.02 | LIGCO | -1 | 0.03759 | 0 | 606 |  |  | 0 | 0 | -0.03759 | 0
7011 | L_FPPYD11_2Y | 2 | South | YES | -0.021684 | 552.2 | 200 | 598 | 0 | 1.02 | LIGCO | -1 | 0.03759 | 0 | 598 |  |  | 0 | 0 | -0.03759 | 0
7012 | L_FPPYD21_3Y | 3 | South | YES | -0.021672 | 427.5 | 200 | 436 | 0 | 1.02 | LIGCO | -1 | 0.037578 | 0 | 436 |  |  | 0 | 0 | -0.037578 | 0
8189 | CUECPL2A | 1 | South | YES | -0.021299 | 12 | 0 | 12 | 0 | 1.02 | Cogen | -1 | 0.037205 | 0 | 0 |  |  | 0 | 0 | -0.037205 | 0
5903 | SANMIGUELGEN | 1 | South | YES | -0.020334 | 396.3 | 180 | 396.3 | 0 | 1.0331 | LIGCO | -1 | 0.03624 | 0 | 396.3 |  |  | 0 | 0 | -0.03624 | 0
88198 | BEEVILLE | F | South | YES | -0.018899 | 0 | 0 | 0 | 0 | 1.02 | AVR | -1 | 0.034805 | 0 | 0 |  |  | 0 | 0 | -0.034805 | 0
8161 | COLETO0A | 1 | South | YES | -0.018745 | 633 | 200 | 633 | 0 | 1.03 | LIGCO | -1 | 0.034651 | 0 | 633 |  |  | 0 | 0 | -0.034651 | 0
5890 | PEARSALLGEN1 | 1 | South | YES | -0.01858 | 19.2 | 6 | 24 | 0 | 1.0161 | GST | -1 | 0.034486 | 24 | 24 |  |  | -0.44592 | 24 | -0.034486 | -0.82767
5891 | PEARSALLGEN2 | 1 | South | YES | -0.01858 | 19.4 | 6 | 24.3 | 0 | 1.0161 | GST | -1 | 0.034486 | 24.3 | 24.3 |  |  | -0.45149 | 24.3 | -0.034486 | -0.83802
5892 | PEARSALLGEN3 | 1 | South | YES | -0.01858 | 19.1 | 6 | 23.9 | 0 | 1.0161 | GST | -1 | 0.034486 | 23.9 | 23.9 |  |  | -0.44406 | 23.9 | -0.034486 | -0.82423
80080 | GWINDT11A | 1 | South | YES | -0.018012 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 94 |  |  | 0 | 0 | -0.033918 | 0
80080 | GWINDT11A | 4 | South | YES | -0.018012 | 8.2 | 0 | 19 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 19 |  |  | 0 | 0 | -0.033918 | 0
80080 | GWINDT11A | 2 | South | YES | -0.018012 | 17.7 | 0 | 41 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 41 |  |  | 0 | 0 | -0.033918 | 0
80080 | GWINDT11A | 3 | South | YES | -0.018012 | 16.4 | 0 | 38 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 38 |  |  | 0 | 0 | -0.033918 | 0
80081 | GWINDT21A | 3 | South | YES | -0.018012 | 18.6 | 0 | 43 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 43 |  |  | 0 | 0 | -0.033918 | 0
80081 | GWINDT21A | 1 | South | YES | -0.018012 | 40.6 | 0 | 94 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 94 |  |  | 0 | 0 | -0.033918 | 0
80081 | GWINDT21A | 4 | South | YES | -0.018012 | 9.5 | 0 | 22 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 22 |  |  | 0 | 0 | -0.033918 | 0
80081 | GWINDT21A | 2 | South | YES | -0.018012 | 15.5 | 0 | 36 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 36 |  |  | 0 | 0 | -0.033918 | 0
80180 | PNSCALT11A | 1 | South | YES | -0.018012 | 63 | 0 | 146 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 146 |  |  | 0 | 0 | -0.033918 | 0
80180 | PNSCALT11A | 2 | South | YES | -0.018012 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 50 |  |  | 0 | 0 | -0.033918 | 0
80181 | PNSCALT21A | 1 | South | YES | -0.018012 | 23.7 | 0 | 55 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 55 |  |  | 0 | 0 | -0.033918 | 0
80181 | PNSCALT21A | 2 | South | YES | -0.018012 | 21.6 | 0 | 50 | 0 | 1.025 | Wind | -1 | 0.033918 | 0 | 50 |  |  | 0 | 0 | -0.033918 | 0
8517 | CELANEBI0A | 1 | South | YES | -0.01801 | 29 | 0 | 29 | 0 | 1.02 | Cogen | -1 | 0.033916 | 0 | 0 |  |  | 0 | 0 | -0.033916 | 0
5932 | SI_RAY9 | 9 | South | YES | -0.017991 | 32 | 32 | 38 | 0 | 1.035 | CC | -1 | 0.033897 | 38 | 38 |  |  | -0.68366 | 38 | -0.033897 | -1.2881
5933 | SI_RAY6 | 6 | South | YES | -0.017991 | 15.4 | 10 | 19.3 | 0 | 1.035 | GST | -1 | 0.033897 | 19.3 | 19.3 |  |  | -0.34723 | 19.3 | -0.033897 | -0.65422
5935 | SI_RAY10 | 10 | South | YES | -0.017991 | 47 | 10 | 47 | 0 | 1.03 | CC | -1 | 0.033897 | 47 | 47 |  |  | -0.84558 | 47 | -0.033897 | -1.5932
80003 | MILHWYS | F | South | YES | -0.017991 | 0 | 0 | 0 | 0 | 1.0168 | AVR | -1 | 0.033897 | 0 | 0 |  |  | 0 | 0 | -0.033897 | 0
8511 | OXY_CC0A | 1 | South | YES | -0.017965 | 30.3 | 0 | 38 |  | 1.027 | Cogen | -1 | 0.033871 | 0 | 0 |  |  | 0 | 0 | -0.033871 | 0
8461 | KOCH_UP0A | 1 | South | YES | -0.017963 | 38 | 0 | 38 | 0 | 1.012 | Cogen | -1 | 0.033869 | 0 | 0 |  |  | 0 | 0 | -0.033869 | 0
8936 | MVGN#1 | 1 | South | YES | -0.017954 | 216.6 | 0 | 216.6 | 0 | 1.0304 | CC | -1 | 0.03386 | 216.6 | 216.6 |  |  | -3.8888 | 216.6 | -0.03386 | -7.3342
8937 | MVGN#2 | 2 | South | YES | -0.017954 | 216.7 | 0 | 216.7 | 0 | 1.0304 | CC | -1 | 0.03386 | 216.7 | 216.7 |  |  | -3.8906 | 216.7 | -0.03386 | -7.3376
8938 | MVGN#3 | 3 | South | YES | -0.017954 | 250.9 | 0 | 250.9 | 0 | 1.0304 | CC | -1 | 0.03386 | 250.9 | 250.9 |  |  | -4.5047 | 250.9 | -0.03386 | -8.4956
8981 | HECN1 | 1 | South | YES | -0.017954 | 144.8 | 0 | 144.8 | 0 | 1.0304 | CC | -1 | 0.03386 | 144.8 | 144.8 |  |  | -2.5997 | 144.8 | -0.03386 | -4.903
8982 | HECN2 | 2 | South | YES | -0.017954 | 144.1 | 0 | 144.1 | 0 | 1.0304 | CC | -1 | 0.03386 | 144.1 | 144.1 |  |  | -2.5872 | 144.1 | -0.03386 | -4.8793
8983 | HECN3 | 3 | South | YES | -0.017954 | 171.9 | 0 | 171.9 | 0 | 1.0304 | CC | -1 | 0.03386 | 171.9 | 171.9 |  |  | -3.0863 | 171.9 | -0.03386 | -5.8206
8506 | VAL #1 | 1 | South | YES | -0.017949 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.033855 | 0 | 0 |  |  | 0 | 0 | -0.033855 | 0
8507 | VAL #2 | 2 | South | YES | -0.017949 | 20.9 | 0 | 25 | 0 | 1.0055 | Cogen | -1 | 0.033855 | 0 | 0 |  |  | 0 | 0 | -0.033855 | 0
8459 | B_DAVIS0B | MB | South | YES | -0.017941 | 0 | 50 | 339 |  | 1.03 | GSC | -1 | 0.033847 | 0 | 0 |  |  | 0 | 0 | -0.033847 | 0
8460 | B_DAVIS0A | MB | South | YES | -0.017941 | 0 | 50 | 340 |  | 1.03 | GSC | -1 | 0.033847 | 0 | 0 |  |  | 0 | 0 | -0.033847 | 0
8173 | VICEC51A | 5 | South | YES | -0.01794 | 144 | 18 | 144 | 0 | 1.025 | CC | -1 | 0.033846 | 144 | 144 |  |  | -2.5834 | 144 | -0.033846 | -4.8739
8174 | VICEC61A | 6 | South | YES | -0.01794 | 188 | 42 | 188 | 0 | 1.025 | CC | -1 | 0.033846 | 188 | 188 |  |  | -3.3727 | 188 | -0.033846 | -6.3631
8456 | COSW#1 | 1 | South | YES | -0.017922 | 20 | 0 | 20 | 0 | 1.027 | Cogen | -1 | 0.033828 | 0 | 0 |  |  | 0 | 0 | -0.033828 | 0
8457 | COSW#2 | 2 | South | YES | -0.017922 | 14 | 0 | 14 | 0 | 1.027 | Cogen | -1 | 0.033828 | 0 | 0 |  |  | 0 | 0 | -0.033828 | 0
8560 | CNOPGT1 | 1 | South | YES | -0.017914 | 148.3 | 0 | 148.3 | 0 | 1.03 | Cogen | -1 | 0.03382 | 0 | 0 |  |  | 0 | 0 | -0.03382 | 0
8561 | CNOPGT2 | 2 | South | YES | -0.017914 | 148.6 | 0 | 148.6 | 0 | 1.03 | Cogen | -1 | 0.03382 | 0 | 0 |  |  | 0 | 0 | -0.03382 | 0
8562 | CNOPST1 | 3 | South | YES | -0.017914 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.03382 | 0 | 0 |  |  | 0 | 0 | -0.03382 | 0
8933 | FGNTS001 | 1 | South | YES | -0.017904 | 146.5 | 0 | 146.5 | 0 | 1.03 | CC | -1 | 0.03381 | 146.5 | 146.5 |  |  | -2.6229 | 146.5 | -0.03381 | -4.9532
8934 | FGNTS101 | 2 | South | YES | -0.017904 | 147.9 | 0 | 147.9 | 0 | 1.03 | CC | -1 | 0.03381 | 147.9 | 147.9 |  |  | -2.648 | 147.9 | -0.03381 | -5.0006
8935 | FGNTS201 | 3 | South | YES | -0.017904 | 173 | 0 | 173 | 0 | 1.03 | CC | -1 | 0.03381 | 173 | 173 |  |  | -3.0974 | 173 | -0.03381 | -5.8492
8926 | LGE_GT10A | 1 | South | YES | -0.017767 | 158 | 0 | 158 | 0 | 1.03 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
8927 | LGE_GT20A | 2 | South | YES | -0.017767 | 153 | 0 | 153 | 0 | 1.03 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
8928 | LGE_STG0A | 3 | South | YES | -0.017767 | 100 | 0 | 100 | 0 | 1.03 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
8930 | ICPGN10A | 1 | South | YES | -0.017767 | 149 | 0 | 149 | 0 | 1.03 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
8931 | ICPGN20A | 2 | South | YES | -0.017767 | 150 | 0 | 150 | 0 | 1.03 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
8932 | ICPGN30A | 3 | South | YES | -0.017767 | 127 | 0 | 127 | 0 | 1.03 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
80223 | REYSHR G | 1 | South | YES | -0.017767 | 12 | 0 | 12 | 0 | 1.032 | Cogen | -1 | 0.033673 | 0 | 0 |  |  | 0 | 0 | -0.033673 | 0
88508 | FALFURRI | F | South | YES | -0.017762 | 0 | 0 | 0 | 0 | 1 | AVR | -1 | 0.033668 | 0 | 0 |  |  | 0 | 0 | -0.033668 | 0
8066 | DUP1V#1 | 1 | South | YES | -0.01776 | 52.3 | 0 | 73 | 0 | 1.01 | Cogen | -1 | 0.033666 | 0 | 0 |  |  | 0 | 0 | -0.033666 | 0
5508 | RAYBURNCC9 | 1 | South | YES | -0.017736 | 47.7 | 18.2 | 47.7 | 0 | 1.0296 | CC | -1 | 0.033642 | 47.7 | 47.7 |  |  | -0.84601 | 47.7 | -0.033642 | -1.6047
5509 | RAYBURNCC10 | 1 | South | YES | -0.017736 | 37.3 | 5.2 | 37.3 | 0 | 1.0296 | CC | -1 | 0.033642 | 37.3 | 37.3 |  |  | -0.66155 | 37.3 | -0.033642 | -1.2549
5511 | RAYBURNCC7 | 1 | South | YES | -0.017736 | 47.5 | 18.2 | 47.5 | 0 | 1.0296 | CC | -1 | 0.033642 | 47.5 | 47.5 |  |  | -0.84246 | 47.5 | -0.033642 | -1.598
5512 | RAYBURNCC8 | 1 | South | YES | -0.017736 | 49.3 | 18.2 | 49.3 | 0 | 1.0296 | CC | -1 | 0.033642 | 49.3 | 49.3 |  |  | -0.87438 | 49.3 | -0.033642 | -1.6586
5728 | FALCONHYDRO2 | 2 | South | YES | -0.017599 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.033505 | 0 | 0 |  |  | 0 | 0 | -0.033505 | 0
5729 | FALCONHYDRO3 | 3 | South | YES | -0.017599 | 11 | 0 | 11 | 0 | 1.0227 | Hydro | -1 | 0.033505 | 0 | 0 |  |  | 0 | 0 | -0.033505 | 0
8048 | FALCONHYDRO1 | 1 | South | YES | -0.017599 | 12 | 0 | 12 | 0 | 1.0227 | Hydro | -1 | 0.033505 | 0 | 0 |  |  | 0 | 0 | -0.033505 | 0
5503 | RAYBURNGEN3 | 1 | South | YES | -0.017568 | 17.6 | 6 | 22 | 0 | 1.0223 | GST | -1 | 0.033474 | 22 | 22 |  |  | -0.3865 | 22 | -0.033474 | -0.73644
5505 | RAYBURNGEN1 | 1 | South | YES | -0.017568 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.033474 | 11 | 11 |  |  | -0.19325 | 11 | -0.033474 | -0.36822
5506 | RAYBURNGEN2 | 1 | South | YES | -0.017568 | 0 | 1 | 11 |  | 1.0223 | GGT | -1 | 0.033474 | 11 | 11 |  |  | -0.19325 | 11 | -0.033474 | -0.36822
80224 | VISTRONG1 | 1 | South | YES | -0.017444 | 13.1 | 0 | 15 | 0 | 1.01 | Cogen | -1 | 0.03335 | 0 | 0 |  |  | 0 | 0 | -0.03335 | 0
80225 | VISTRONG2 | 2 | South | YES | -0.017444 | 20.2 | 0 | 23 | 0 | 1.01 | Cogen | -1 | 0.03335 | 0 | 0 |  |  | 0 | 0 | -0.03335 | 0
80227 | AIRCO G | 1 | South | YES | -0.017327 | 7.2 | 0 | 8 | 0 | 1.0104 | Cogen | -1 | 0.033233 | 0 | 0 |  |  | 0 | 0 | -0.033233 | 0
88299 | ZAPATA | F | South | YES | -0.017306 | 0 | 0 | 0 | 0 | 1.02 | BLT | -1 | 0.033212 | 0 | 0 |  |  | 0 | 0 | -0.033212 | 0
8147 | UCAR #2 | 10 | South | YES | -0.017275 | 18.2 | 0 | 28 |  | 1 | Cogen | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
8148 | UCAR #1 | 2 | South | YES | -0.017275 | 6.1 | 0 | 7 | 0 | 1.009 | Cogen | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
80137 | CSDR89 | 8 | South | YES | -0.017275 | 33.9 | 0 | 39 |  | 1.003 | DCTie | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
80137 | CSDR89 | 9 | South | YES | -0.017275 | 0 | 0 | 15 |  | 1.003 | DCTie | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
80138 | CSDR7 | 7 | South | YES | -0.017275 | 6.1 | 0 | 7 | 0 | 1.014 | DCTie | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
80139 | CSDR56 | 5 | South | YES | -0.017275 | 15 | 0 | 15 |  | 1.0033 | DCTie | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
80139 | CSDR56 | 6 | South | YES | -0.017275 | 0 | 0 | 39 |  | 1.0033 | DCTie | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
80140 | CSDR11 | 11 | South | YES | -0.017275 | 33.9 | 0 | 39 | 0 | 1.03 | DCTie | -1 | 0.033181 | 0 | 0 |  |  | 0 | 0 | -0.033181 | 0
80012 | LAR | F | South | YES | -0.016883 | 0 | 0 | 0 | 0 | 1.04 | DCTie | -1 | 0.032789 | 0 | 0 |  |  | 0 | 0 | -0.032789 | 0
80265 | LARECU40A | 4 | South | YES | -0.016882 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.032788 | 100 | 100 |  |  | -1.6882 | 100 | -0.032788 | -3.2788
80266 | LARECU50A | 5 | South | YES | -0.016882 | 80 | 0 | 100 |  | 1.039 | GGT | -1 | 0.032788 | 100 | 100 |  |  | -1.6882 | 100 | -0.032788 | -3.2788
80226 | ALCOA G | 1 | South | YES | -0.016843 | 32.3 | 5 | 48 | 0 | 1.015 | Cogen | -1 | 0.032749 | 0 | 0 |  |  | 0 | 0 | -0.032749 | 0
8134 | FOR #1 | 1 | South | YES | -0.016713 | 54.1 | 45 | 79 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
8138 | FOR #2 | 2 | South | YES | -0.016713 | 63.1 | 45 | 81 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
8153 | FOR #3 | 3 | South | YES | -0.016713 | 63.1 | 45 | 79.9 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
8154 | FOR #4 | 4 | South | YES | -0.016713 | 63.1 | 60 | 80 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
8155 | FOR #5 | 5 | South | YES | -0.016713 | 63.1 | 60 | 78.4 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
8156 | FOR #6 | 6 | South | YES | -0.016713 | 24.9 | 5 | 25 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
8157 | FOR #7 | 7 | South | YES | -0.016713 | 28.8 | 5 | 46 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
80051 | FOR #8 | 8 | South | YES | -0.016713 | 28 | 28 | 28 | 0 | 1.016 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
80052 | FOR #9 | 9 | South | YES | -0.016713 | 29.7 | 5 | 43.6 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
80053 | FOR #10 | 10 | South | YES | -0.016713 | 68.4 | 45 | 75 | 0 | 1.03 | Cogen | -1 | 0.032619 | 0 | 0 |  |  | 0 | 0 | -0.032619 | 0
5911 | STP_GN1___1 | 1 | Houston | YES | -0.012064 | 1333 | 1249 | 1333 | 0 | 1.0406 | Nuc | -1 | 0.02797 | 0 | 0 |  |  |  |  | -0.02797 | 0
5912 | STP_GN2___2 | 2 | Houston | YES | -0.012064 | 1332 | 1249 | 1332 | 0 | 1.0406 | Nuc | -1 | 0.02797 | 0 | 0 |  |  |  |  | -0.02797 | 0
48731 | CBE_GT1 | 1 | Houston | YES | -0.011925 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.027831 | 76 | 76 |  |  |  |  | -0.027831 | -2.1152
48732 | CBE_GT2 | 1 | Houston | YES | -0.011925 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.027831 | 76 | 76 |  |  |  |  | -0.027831 | -2.1152
48733 | CBE_ST12 | 1 | Houston | YES | -0.011925 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.027831 | 105 | 105 |  |  |  |  | -0.027831 | -2.9223
48734 | CBE_GT3 | 1 | Houston | YES | -0.011925 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.027831 | 76 | 76 |  |  |  |  | -0.027831 | -2.1152
48735 | CBE_GT4 | 1 | Houston | YES | -0.011925 | 76 | 0 | 76 | 0 | 1.029 | CC | -1 | 0.027831 | 76 | 76 |  |  |  |  | -0.027831 | -2.1152
48736 | CBE_ST34 | 1 | Houston | YES | -0.011925 | 105 | 0 | 105 | 0 | 1.029 | CC | -1 | 0.027831 | 105 | 105 |  |  |  |  | -0.027831 | -2.9223
48911 | TGF_GT1_8000 | 1 | Houston | YES | -0.011431 | 69.2 | 0 | 69.2 |  | 1.029 | Cogen | -1 | 0.027337 | 0 | 0 |  |  |  |  | -0.027337 | 0
49851 | DOW17000 | 37 | Houston | YES | -0.00979 | 39 | 0 | 62 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49858 | DOW38100 | 31 | Houston | YES | -0.00979 | 45 | 0 | 71.4 |  | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49859 | DOW38200 | 33 | Houston | YES | -0.00979 | 28 | 0 | 45 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49860 | DOW38300 | 32 | Houston | YES | -0.00979 | 63 | 0 | 101 |  | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49862 | DOW39100 | 36 | Houston | YES | -0.00979 | 54 | 0 | 86 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49863 | DOW39200 | 35 | Houston | YES | -0.00979 | 55 | 0 | 88 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49865 | DOW41000 | 41 | Houston | YES | -0.00979 | 31 | 0 | 50 |  | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49866 | DOW42000 | 42 | Houston | YES | -0.00979 | 11 | 0 | 18 |  | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49869 | DOW49000 | 45 | Houston | YES | -0.00979 | 59 | 0 | 94 |  | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49870 | DOW61000 | 61 | Houston | YES | -0.00979 | 44 | 0 | 70 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49871 | DOW62000 | 62 | Houston | YES | -0.00979 | 40 | 0 | 63 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49872 | DOW63000 | 63 | Houston | YES | -0.00979 | 45 | 0 | 72 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49873 | DOW64000 | 64 | Houston | YES | -0.00979 | 41 | 0 | 64.8 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49876 | DOW65000 | 65 | Houston | YES | -0.00979 | 63 | 0 | 101 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49877 | DOW66000 | 66 | Houston | YES | -0.00979 | 61 | 0 | 97 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49878 | DOW67000 | 67 | Houston | YES | -0.00979 | 65 | 0 | 103 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49882 | DOW81000 | 81 | Houston | YES | -0.00979 | 47 | 0 | 76 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49884 | DOW82000 | 82 | Houston | YES | -0.00979 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49885 | DOW83000 | 83 | Houston | YES | -0.00979 | 51 | 0 | 80 | 0 | 1 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
49886 | DOW84000 | 84 | Houston | YES | -0.00979 | 107 | 0 | 171 | 0 | 0.98 | Cogen | -1 | 0.025696 | 0 | 0 |  |  |  |  | -0.025696 | 0
48520 | BSF_GT1_8070 | 1 | Houston | YES | -0.00937 | 72 | 0 | 72 | 0 | 1.0326 | Cogen | -1 | 0.025276 | 0 | 0 |  |  |  |  | -0.025276 | 0
48520 | BSF_GT1_8070 | 2 | Houston | YES | -0.00937 | 10 | 0 | 10 | 0 | 1.0326 | Cogen | -1 | 0.025276 | 0 | 0 |  |  |  |  | -0.025276 | 0
80010 | EPLVT1 | F | South | YES | -0.009189 | 0 | 0 | 0 |  | 1.0376 | AVR | -1 | 0.025095 | 0 | 0 |  |  | 0 | 0 | -0.025095 | 0
39760 | TNSCLP1___8 | 1 | Houston | YES | -0.009035 | 93.4 | 20 | 116.8 | 0 | 1.04 | Cogen | -1 | 0.024941 | 0 | 0 |  |  |  |  | -0.024941 | 0
39770 | TNSCLP2___8 | 1 | Houston | YES | -0.009035 | 91.6 | 20 | 114.5 | 0 | 1.04 | Cogen | -1 | 0.024941 | 0 | 0 |  |  |  |  | -0.024941 | 0
39775 | TNSCLP4___8 | 1 | Houston | YES | -0.009035 | 95.2 | 20 | 119 | 0 | 1.04 | Cogen | -1 | 0.024941 | 0 | 0 |  |  |  |  | -0.024941 | 0
39790 | TNSCLP3___8 | 1 | Houston | YES | -0.009035 | 87.6 | 20 | 109.5 | 0 | 1.027 | Cogen | -1 | 0.024941 | 0 | 0 |  |  |  |  | -0.024941 | 0
8262 | ELPS | 1 | South | YES | -0.008156 | 6 | 6 | 6 | 0 | 1.15 | Hydro | -1 | 0.024062 | 0 | 0 |  |  | 0 | 0 | -0.024062 | 0
48730 | MNS_GT | 1 | Houston | YES | -0.007854 | 43 | 0 | 46.1 | 0 | 1.029 | Cogen | -1 | 0.02376 | 0 | 0 |  |  |  |  | -0.02376 | 0
48926 | WAP_GN6_6 | 6 | Houston | YES | -0.007836 | 651 | 280 | 651 |  | 1.035 | LIGCO | -1 | 0.023742 | 0 | 651 |  |  |  |  | -0.023742 | 0
48927 | WAP_GN7_7 | 7 | Houston | YES | -0.007836 | 564 | 277 | 564 |  | 1.035 | LIGCO | -1 | 0.023742 | 0 | 564 |  |  |  |  | -0.023742 | 0
48928 | WAP_GN8_8 | 8 | Houston | YES | -0.007836 | 603 | 275 | 603 |  | 1.035 | LIGCO | -1 | 0.023742 | 0 | 603 |  |  |  |  | -0.023742 | 0
48521 | BVE_GT1_GT1 | 1 | Houston | YES | -0.007827 | 167.7 | 0 | 167.7 |  | 1.035 | CC | -1 | 0.023733 | 167.7 | 167.7 |  |  |  |  | -0.023733 | -3.9801
48522 | BVE_GT2_5035 | 2 | Houston | YES | -0.007827 | 166.4 | 0 | 166.4 |  | 1.035 | CC | -1 | 0.023733 | 166.4 | 166.4 |  |  |  |  | -0.023733 | -3.9492
48523 | BVE_ST1_GN1 | 3 | Houston | YES | -0.007827 | 252.4 | 0 | 252.4 |  | 1.035 | CC | -1 | 0.023733 | 252.4 | 252.4 |  |  |  |  | -0.023733 | -5.9903
48510 | AK_GT1__8040 | 1 | Houston | YES | -0.007676 | 33.4 | 8.1 | 34 |  | 1.029 | Cogen | -1 | 0.023582 | 0 | 0 |  |  |  |  | -0.023582 | 0
48921 | WAP_GN1_1 | 1 | Houston | YES | -0.007638 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.023544 | 166 | 166 |  |  |  |  | -0.023544 | -3.9084
48922 | WAP_GN2_2 | 2 | Houston | YES | -0.007638 | 132.8 | 37 | 166 | 0 | 1.0362 | GST | -1 | 0.023544 | 166 | 166 |  |  |  |  | -0.023544 | -3.9084
48923 | WAP_GN3_3 | 3 | Houston | YES | -0.007638 | 198.4 | 93 | 248 | 0 | 1.0362 | GST | -1 | 0.023544 | 248 | 248 |  |  |  |  | -0.023544 | -5.839
48924 | WAP_GN4_4 | 4 | Houston | YES | -0.007638 | 546 | 217 | 546 | 0 | 1.0362 | GSC | -1 | 0.023544 | 546 | 546 |  |  |  |  | -0.023544 | -12.8553
48925 | WAP_GN5_5 | 5 | Houston | YES | -0.007638 | 625.7 | 278 | 654 | 0 | 0.985 | LIGCO | -1 | 0.023544 | 0 | 654 |  |  |  |  | -0.023544 | 0
48929 | WAPGT21_GT1 | B1 | Houston | YES | -0.007638 | 0 | 0 | 13 |  | 1.05 | GGT | -1 | 0.023544 | 13 | 13 |  |  |  |  | -0.023544 | -0.30608
38580 | TNBP_CGN1_8 | 1 | Houston | YES | -0.006887 | 70.8 | 0 | 70.8 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38590 | TNBP_CGN2_8 | 2 | Houston | YES | -0.006887 | 66.7 | 0 | 66.7 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38600 | TNBP_CGN3_8 | 5 | Houston | YES | -0.006887 | 53 | 0 | 53 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38611 | TNBPAMCG1_8 | 1 | Houston | YES | -0.006887 | 153.2 | 0 | 153.2 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38612 | TNBPAMCG2_8 | 2 | Houston | YES | -0.006887 | 153.5 | 0 | 153.5 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38613 | TNBPAMCG3_8 | 3 | Houston | YES | -0.006887 | 152.3 | 0 | 152.3 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38614 | TNBPAMCG4_8 | 4 | Houston | YES | -0.006887 | 96 | 0 | 96 |  | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38615 | TNBPAMCG5_8 | 1 | Houston | YES | -0.006887 | 244 | 0 | 244 | 0 | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38690 | TNBP_CGN4_8 | 3 | Houston | YES | -0.006887 | 40 | 0 | 40 |  | 1.005 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38711 | TNTXCTY1CG8 | 1 | Houston | YES | -0.006887 | 100.3 | 59 | 100.3 | 0 | 1 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38712 | TNTXCTY2CG8 | 1 | Houston | YES | -0.006887 | 92.9 | 59 | 92.9 | 0 | 1 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38713 | TNTXCTY3CG8 | 1 | Houston | YES | -0.006887 | 102.7 | 59 | 102.7 | 0 | 1 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
38714 | TNTXCTY4CG8 | 1 | Houston | YES | -0.006887 | 103 | 59 | 103 | 0 | 1 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
39470 | TNDOWCGNSG8 | 1 | Houston | YES | -0.006887 | 32 | 10 | 32 | 0 | 0.985 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
39480 | TNDOWCGNGG8 | 1 | Houston | YES | -0.006887 | 30 | 10 | 30 | 0 | 0.985 | Cogen | -1 | 0.022793 | 0 | 0 |  |  |  |  | -0.022793 | 0
48772 | PHR_GN2_2 | MB | Houston | YES | -0.006564 | 0 | 72 | 459 |  | 1.0362 | GSC | -1 | 0.02247 | 0 | 0 |  |  |  |  | -0.02247 | 0
48561 | CTL_GT2_8130 | 1 | Houston | YES | -0.006338 | 73.5 | 30.3 | 91.9 |  | 1.0362 | Cogen | -1 | 0.022244 | 0 | 0 |  |  |  |  | -0.022244 | 0
48562 | CTL_GT3_8135 | 2 | Houston | YES | -0.006338 | 70.1 | 30.3 | 87.6 |  | 1.0362 | Cogen | -1 | 0.022244 | 0 | 0 |  |  |  |  | -0.022244 | 0
48563 | CTL_GT4_8140 | 3 | Houston | YES | -0.006338 | 69.6 | 30.3 | 87 |  | 1.0362 | Cogen | -1 | 0.022244 | 0 | 0 |  |  |  |  | -0.022244 | 0
48564 | CTL_GN1_8145 | 4 | Houston | YES | -0.006338 | 43.6 | 12.9 | 54.5 |  | 1.0362 | Cogen | -1 | 0.022244 | 0 | 0 |  |  |  |  | -0.022244 | 0
48565 | CTL_GN2_8155 | 5 | Houston | YES | -0.006338 | 9.8 | 3.4 | 12.2 |  | 1.0362 | Cogen | -1 | 0.022244 | 0 | 0 |  |  |  |  | -0.022244 | 0
48531 | BYU_GT1_8075 | 1 | Houston | YES | -0.006252 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.022158 | 0 | 0 |  |  |  |  | -0.022158 | 0
48532 | BYU_GT2_8055 | 2 | Houston | YES | -0.006252 | 62 | 0 | 62 |  | 1.0362 | Cogen | -1 | 0.022158 | 0 | 0 |  |  |  |  | -0.022158 | 0
48533 | BYU_GT3_8060 | 3 | Houston | YES | -0.006252 | 67 | 0 | 67 |  | 1.0362 | Cogen | -1 | 0.022158 | 0 | 0 |  |  |  |  | -0.022158 | 0
48534 | BYU_GT4_8065 | 4 | Houston | YES | -0.006252 | 65 | 0 | 65 |  | 1.0362 | Cogen | -1 | 0.022158 | 0 | 0 |  |  |  |  | -0.022158 | 0
48691 | GBY_73741085 | A | Houston | YES | -0.006138 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.022044 | 47 | 47 |  |  |  |  | -0.022044 | -1.0361
48691 | GBY_73741085 | B | Houston | YES | -0.006138 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.022044 | 47 | 47 |  |  |  |  | -0.022044 | -1.0361
48692 | GBY_81821075 | D | Houston | YES | -0.006138 | 44 | 20 | 55 | 0 | 1.0362 | GGT | -1 | 0.022044 | 55 | 55 |  |  |  |  | -0.022044 | -1.2124
48692 | GBY_81821075 | C | Houston | YES | -0.006138 | 37.6 | 20 | 47 | 0 | 1.0362 | GGT | -1 | 0.022044 | 47 | 47 |  |  |  |  | -0.022044 | -1.0361
48693 | GBY_83841065 | E | Houston | YES | -0.006138 | 45.6 | 20 | 57 | 0 | 1.0362 | GGT | -1 | 0.022044 | 57 | 57 |  |  |  |  | -0.022044 | -1.2565
48693 | GBY_83841065 | F | Houston | YES | -0.006138 | 43.2 | 20 | 54 | 0 | 1.0362 | GGT | -1 | 0.022044 | 54 | 54 |  |  |  |  | -0.022044 | -1.1904
48841 | SJS_GT1_GT1 | 1 | Houston | YES | -0.00609 | 62.4 | 49 | 78 | 0 | 1.0362 | Cogen | -1 | 0.021996 | 0 | 0 |  |  |  |  | -0.021996 | 0
48842 | SJS_GT2_GT2 | 2 | Houston | YES | -0.00609 | 64.8 | 49 | 81 | 0 | 1.0362 | Cogen | -1 | 0.021996 | 0 | 0 |  |  |  |  | -0.021996 | 0
48641 | DPEC_GT15040 | 1 | Houston | YES | -0.006048 | 163.2 | 98 | 163.2 | 0 | 1.0319 | CC | -1 | 0.021954 | 163.2 | 163.2 |  |  |  |  | -0.021954 | -3.583
48642 | DPEC_GT25025 | 2 | Houston | YES | -0.006048 | 157.1 | 98 | 157.1 | 0 | 1.0319 | CC | -1 | 0.021954 | 157.1 | 157.1 |  |  |  |  | -0.021954 | -3.449
48643 | DPEC_GT35010 | 3 | Houston | YES | -0.006048 | 157.5 | 98 | 157.5 | 0 | 1.0319 | CC | -1 | 0.021954 | 157.5 | 157.5 |  |  |  |  | -0.021954 | -3.4578
48644 | DPEC_GT45070 | 4 | Houston | YES | -0.006048 | 157 | 98 | 157 | 0 | 1.0319 | CC | -1 | 0.021954 | 157 | 157 |  |  |  |  | -0.021954 | -3.4468
48645 | DPEC_ST55065 | 5 | Houston | YES | -0.006048 | 282 | 0 | 282 | 0 | 1.0319 | CC | -1 | 0.021954 | 282 | 282 |  |  |  |  | -0.021954 | -6.1911
48761 | PR_GT1__9040 | 1 | Houston | YES | -0.006008 | 26 | 0 | 35 |  | 1 | Cogen | -1 | 0.021914 | 0 | 0 |  |  |  |  | -0.021914 | 0
48855 | SRB_GT211035 | B1 | Houston | YES | -0.005969 | 0 | 0 | 18 |  | 1.014 | GGT | -1 | 0.021875 | 18 | 18 |  |  |  |  | -0.021875 | -0.39376
48855 | SRB_GT211035 | B2 | Houston | YES | -0.005969 | 0 | 0 | 12 |  | 1.014 | GGT | -1 | 0.021875 | 12 | 12 |  |  |  |  | -0.021875 | -0.26251
48852 | SRB_GN2_2 | 2 | Houston | YES | -0.005966 | 140.8 | 26 | 176 | 0 | 1.0217 | GST | -1 | 0.021872 | 176 | 176 |  |  |  |  | -0.021872 | -3.8495
48851 | SRB_GN1_1 | 1 | Houston | YES | -0.005963 | 132 | 26 | 165 | 0 | 1.0217 | GST | -1 | 0.021869 | 165 | 165 |  |  |  |  | -0.021869 | -3.6085
48551 | CAL_GT1_8045 | 1 | Houston | YES | -0.005962 | 149 | 0 | 149 | 0 | 1.0326 | Cogen | -1 | 0.021868 | 0 | 0 |  |  |  |  | -0.021868 | 0
48552 | CAL_ST1_8000 | 2 | Houston | YES | -0.005962 | 65.1 | 0 | 65.1 | 0 | 1.0326 | Cogen | -1 | 0.021868 | 0 | 0 |  |  |  |  | -0.021868 | 0
48853 | SRB_GN3_3 | 3 | Houston | YES | -0.005953 | 170.4 | 35 | 213 |  | 1.0326 | GST | -1 | 0.021859 | 213 | 213 |  |  |  |  | -0.021859 | -4.6561
48845 | SOL_GT1 | 1 | Houston | YES | -0.005952 | 16.2 | 15.4 | 16.2 |  | 1.0326 | Solar | -1 | 0.021858 | 16.2 | 16.2 |  |  |  |  | -0.021858 | -0.35411
48611 | DIB_GT1_8080 | 1 | Houston | YES | -0.005951 | 64 | 0 | 64 | 0 | 1.0326 | Cogen | -1 | 0.021857 | 0 | 0 |  |  |  |  | -0.021857 | 0
48612 | DIB_GT2_8075 | 2 | Houston | YES | -0.005951 | 63.2 | 0 | 63.2 | 0 | 1.0326 | Cogen | -1 | 0.021857 | 0 | 0 |  |  |  |  | -0.021857 | 0
48613 | DIB_ST1_8085 | 3 | Houston | YES | -0.005951 | 67.9 | 30 | 82.6 | 0 | 1.0326 | Cogen | -1 | 0.021857 | 0 | 0 |  |  |  |  | -0.021857 | 0
48614 | DIB_GT3_8090 | 4 | Houston | YES | -0.005951 | 73.6 | 15 | 73.6 | 0 | 1.0326 | Cogen | -1 | 0.021857 | 0 | 0 |  |  |  |  | -0.021857 | 0
48854 | SRB_GN4_4 | 4 | Houston | YES | -0.00595 | 182.4 | 35 | 228 | 0 | 1.0326 | GST | -1 | 0.021856 | 228 | 228 |  |  |  |  | -0.021856 | -4.9833
48740 | PSG_GN2_8050 | 1 | Houston | YES | -0.005949 | 182 | 60 | 182 | 0 | 1.0326 | Cogen | -1 | 0.021855 | 0 | 0 |  |  |  |  | -0.021855 | 0
48741 | PSG_GT2_8040 | 1 | Houston | YES | -0.005949 | 158.6 | 50 | 158.6 | 0 | 1.0326 | Cogen | -1 | 0.021855 | 0 | 0 |  |  |  |  | -0.021855 | 0
48742 | PSG_GT3_8060 | 1 | Houston | YES | -0.005949 | 157 | 50 | 157 | 0 | 1.0326 | Cogen | -1 | 0.021855 | 0 | 0 |  |  |  |  | -0.021855 | 0
48820 | SHELLG1_3015 | 1 | Houston | YES | -0.005894 | 71 | 34.5 | 71 |  | 1.029 | Cogen | -1 | 0.0218 | 0 | 0 |  |  |  |  | -0.0218 | 0
48821 | SHELLG2 | 2 | Houston | YES | -0.005894 | 72 | 34.5 | 72 |  | 1.029 | Cogen | -1 | 0.0218 | 0 | 0 |  |  |  |  | -0.0218 | 0
48822 | SHELLG3_3020 | 1 | Houston | YES | -0.005894 | 39 | 0 | 39 |  | 1.029 | Cogen | -1 | 0.0218 | 0 | 0 |  |  |  |  | -0.0218 | 0
48822 | SHELLG3_3020 | 2 | Houston | YES | -0.005894 | 30 | 0 | 30 |  | 1.029 | Cogen | -1 | 0.0218 | 0 | 0 |  |  |  |  | -0.0218 | 0
48500 | APD_GT1_8005 | 1 | Houston | YES | -0.005812 | 137.6 | 54.6 | 137.6 |  | 1.0362 | Cogen | -1 | 0.021718 | 0 | 0 |  |  |  |  | -0.021718 | 0
48511 | LPE_GT1_8070 | 1 | Houston | YES | -0.0058 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.021706 | 42 | 42 |  |  |  |  | -0.021706 | -0.91167
48512 | LPE_GT2_8075 | 2 | Houston | YES | -0.0058 | 42 | 0 | 42 | 0 | 1.0362 | GGT | -1 | 0.021706 | 42 | 42 |  |  |  |  | -0.021706 | -0.91167
48513 | LPE_GT3_8080 | 3 | Houston | YES | -0.0058 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.021706 | 39 | 39 |  |  |  |  | -0.021706 | -0.84655
48514 | LPE_GT4_8085 | 4 | Houston | YES | -0.0058 | 39 | 0 | 39 | 0 | 1.0362 | GGT | -1 | 0.021706 | 39 | 39 |  |  |  |  | -0.021706 | -0.84655
48593 | CHE_GT1_8015 | 1 | Houston | YES | -0.005783 | 173 | 50 | 173 | 0 | 1.0362 | Cogen | -1 | 0.021689 | 0 | 0 |  |  |  |  | -0.021689 | 0
48594 | CHE_GN4_8025 | 4 | Houston | YES | -0.005783 | 142 | 60 | 142 | 0 | 1.0362 | Cogen | -1 | 0.021689 | 0 | 0 |  |  |  |  | -0.021689 | 0
48873 | THW_ST3_ST_3 | 3 | Houston | YES | -0.005665 | 107 | 19 | 107 | 0 | 1.0435 | CC | -1 | 0.021571 | 107 | 107 |  |  |  |  | -0.021571 | -2.3081
48874 | THW_ST4_ST_4 | 4 | Houston | YES | -0.005665 | 108 | 19 | 108 | 0 | 1.0435 | CC | -1 | 0.021571 | 108 | 108 |  |  |  |  | -0.021571 | -2.3297
48875 | THW_3132 | A | Houston | YES | -0.005665 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.021571 | 55 | 55 |  |  |  |  | -0.021571 | -1.1864
48875 | THW_3132 | B | Houston | YES | -0.005665 | 53 | 5 | 53 | 0 | 1.0435 | CC | -1 | 0.021571 | 53 | 53 |  |  |  |  | -0.021571 | -1.1433
48877 | THW_3334 | D | Houston | YES | -0.005665 | 57 | 5 | 57 | 0 | 1.0435 | CC | -1 | 0.021571 | 57 | 57 |  |  |  |  | -0.021571 | -1.2296
48877 | THW_3334 | C | Houston | YES | -0.005665 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.021571 | 55 | 55 |  |  |  |  | -0.021571 | -1.1864
48879 | THW_4142 | F | Houston | YES | -0.005665 | 55 | 5 | 55 | 0 | 1.0435 | CC | -1 | 0.021571 | 55 | 55 |  |  |  |  | -0.021571 | -1.1864
48879 | THW_4142 | E | Houston | YES | -0.005665 | 56 | 5 | 56 | 0 | 1.0435 | CC | -1 | 0.021571 | 56 | 56 |  |  |  |  | -0.021571 | -1.208
48881 | THW_4344 | H | Houston | YES | -0.005665 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.021571 | 58 | 58 |  |  |  |  | -0.021571 | -1.2511
48881 | THW_4344 | G | Houston | YES | -0.005665 | 58 | 5 | 58 | 0 | 1.0435 | CC | -1 | 0.021571 | 58 | 58 |  |  |  |  | -0.021571 | -1.2511
48582 | CBY_GN2_2 | 2 | Houston | YES | -0.005584 | 596.8 | 110 | 746 | 0 | 1.0435 | GSC | -1 | 0.02149 | 746 | 746 |  |  |  |  | -0.02149 | -16.0319
49803 | EXN_15GT | 1 | Houston | YES | -0.005547 | 33 | 8.3 | 34 |  | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49804 | EXN_16GT | 2 | Houston | YES | -0.005547 | 32 | 8.3 | 34.7 |  | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49805 | EXN_17GT | 3 | Houston | YES | -0.005547 | 31 | 8.3 | 32.7 |  | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49826 | EXN938GT | 5 | Houston | YES | -0.005547 | 43 | 9.2 | 45.9 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49828 | EXN941GT | 10 | Houston | YES | -0.005547 | 17.7 | 5.4 | 17.7 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49829 | EXN942GT | 11 | Houston | YES | -0.005547 | 20 | 5.4 | 20.4 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49830 | EXN943GT | 12 | Houston | YES | -0.005547 | 19 | 5.4 | 19.9 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49831 | EXN944GT | 13 | Houston | YES | -0.005547 | 33 | 5.4 | 35 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49832 | EXN945GT | 9 | Houston | YES | -0.005547 | 18.5 | 9.2 | 18.5 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49837 | EXN_GT | 4 | Houston | YES | -0.005547 | 81 | 21.3 | 85.4 | 0 | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
49838 | EXN_14GT | 14 | Houston | YES | -0.005547 | 140 | 0 | 148 |  | 1.0326 | Cogen | -1 | 0.021453 | 0 | 0 |  |  |  |  | -0.021453 | 0
48883 | THW_GT1_GT_1 | B2 | Houston | YES | -0.005525 | 0 | 0 | 12 |  | 1.043 | GGT | -1 | 0.021431 | 12 | 12 |  |  |  |  | -0.021431 | -0.25718
48651 | EP_1_2 | 2 | Houston | YES | -0.005447 | 17.7 | 10 | 21 | 0 | 1.0362 | Cogen | -1 | 0.021353 | 0 | 0 |  |  |  |  | -0.021353 | 0
48651 | EP_1_2 | 1 | Houston | YES | -0.005447 | 4 | 0 | 5 | 0 | 1.0362 | Cogen | -1 | 0.021353 | 0 | 0 |  |  |  |  | -0.021353 | 0
48791 | PSA_GT1_8160 | 1 | Houston | YES | -0.005445 | 52 | 20.8 | 65 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48792 | PSA_GT2_8155 | 2 | Houston | YES | -0.005445 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48793 | PSA_GT3_8150 | 3 | Houston | YES | -0.005445 | 56 | 20.3 | 70 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48794 | PSA_GT4_8145 | 4 | Houston | YES | -0.005445 | 52.8 | 20.3 | 66 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48795 | PSA_GT5_8140 | 5 | Houston | YES | -0.005445 | 51.2 | 20.3 | 64 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48796 | PSA_GN1_8165 | 1 | Houston | YES | -0.005445 | 83.2 | 43.1 | 104 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48797 | PSA_GT6_8135 | 6 | Houston | YES | -0.005445 | 47.2 | 34.5 | 59 | 0 | 1.0362 | Cogen | -1 | 0.021351 | 0 | 0 |  |  |  |  | -0.021351 | 0
48581 | CBY_GN1_1 | 1 | Houston | YES | -0.005439 | 595.2 | 108 | 744 | 0 | 1.0435 | GSC | -1 | 0.021345 | 744 | 744 |  |  |  |  | -0.021345 | -15.881
48815 | CVC_GT4_8005 | 4 | Houston | YES | -0.005411 | 165 | 91.8 | 165 |  | 1.0362 | Cogen | -1 | 0.021317 | 0 | 0 |  |  |  |  | -0.021317 | 0
48583 | CBY_GT4_1 | 1 | Houston | YES | -0.005393 | 172 | 0 | 172 | 0 | 1.026 | GSC | -1 | 0.021299 | 172 | 172 |  |  |  |  | -0.021299 | -3.6635
48584 | CBY_GT4_2 | 2 | Houston | YES | -0.005393 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.021299 | 172 | 172 |  |  |  |  | -0.021299 | -3.6635
48585 | CBY_ST4_1 | 3 | Houston | YES | -0.005393 | 172 | 0 | 172 | 0 | 1.026 | CC | -1 | 0.021299 | 172 | 172 |  |  |  |  | -0.021299 | -3.6635
48595 | BTE_GT2_8075 | 1 | Houston | YES | -0.005287 | 162.8 | 130 | 162.8 | 0 | 1.0261 | CC | -1 | 0.021193 | 162.8 | 162.8 |  |  |  |  | -0.021193 | -3.4503
48596 | BTE_GT3_8045 | 2 | Houston | YES | -0.005287 | 161.4 | 130 | 161.4 | 0 | 1.0261 | CC | -1 | 0.021193 | 161.4 | 161.4 |  |  |  |  | -0.021193 | -3.4206
48597 | BTE_GT4_8055 | 3 | Houston | YES | -0.005287 | 158.9 | 130 | 158.9 | 0 | 1.0261 | CC | -1 | 0.021193 | 158.9 | 158.9 |  |  |  |  | -0.021193 | -3.3676
48598 | BTE_ST1_8070 | 4 | Houston | YES | -0.005287 | 269.2 | 60 | 269.2 | 0 | 1.0261 | CC | -1 | 0.021193 | 269.2 | 269.2 |  |  |  |  | -0.021193 | -5.7053
48690 | GBY_GN5_5 | 5 | Houston | YES | -0.005254 | 318.4 | 81 | 398 |  | 1.0362 | GSC | -1 | 0.02116 | 398 | 398 |  |  |  |  | -0.02116 | -8.4219
48885 | THW_5152 | B | Houston | YES | -0.005207 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.021113 | 59 | 59 |  |  |  |  | -0.021113 | -1.2457
48885 | THW_5152 | A | Houston | YES | -0.005207 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.021113 | 58 | 58 |  |  |  |  | -0.021113 | -1.2246
48886 | THW_5354 | C | Houston | YES | -0.005207 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.021113 | 57 | 57 |  |  |  |  | -0.021113 | -1.2035
48886 | THW_5354 | D | Houston | YES | -0.005207 | 46.4 | 5 | 58 |  | 1.0319 | GGT | -1 | 0.021113 | 58 | 58 |  |  |  |  | -0.021113 | -1.2246
48887 | THW_5556 | F | Houston | YES | -0.005207 | 45.6 | 5 | 57 |  | 1.0319 | GGT | -1 | 0.021113 | 57 | 57 |  |  |  |  | -0.021113 | -1.2035
48887 | THW_5556 | E | Houston | YES | -0.005207 | 47.2 | 5 | 59 |  | 1.0319 | GGT | -1 | 0.021113 | 59 | 59 |  |  |  |  | -0.021113 | -1.2457
48591 | CHE_GT2_5030 | 2 | Houston | YES | -0.004565 | 173 | 50 | 173 | 0 | 1.029 | Cogen | -1 | 0.020471 | 0 | 0 |  |  |  |  | -0.020471 | 0
48811 | CVC_GT3_5045 | 3 | Houston | YES | -0.004565 | 156 | 91.8 | 156 | 0 | 1.029 | Cogen | -1 | 0.020471 | 0 | 0 |  |  |  |  | -0.020471 | 0
48812 | CVC_GT2_5020 | 2 | Houston | YES | -0.004565 | 158 | 91.8 | 158 | 0 | 1.029 | Cogen | -1 | 0.020471 | 0 | 0 |  |  |  |  | -0.020471 | 0
48813 | CVC_GT1_5035 | 1 | Houston | YES | -0.004565 | 160 | 91.8 | 160 | 0 | 1.029 | Cogen | -1 | 0.020471 | 0 | 0 |  |  |  |  | -0.020471 | 0
48814 | CVC_ST5_5040 | 1 | Houston | YES | -0.004565 | 162 | 91.8 | 162 | 0 | 1.029 | Cogen | -1 | 0.020471 | 0 | 0 |  |  |  |  | -0.020471 | 0
8032 | AMISTADHYD1 | 1 | South | YES | -0.003715 | 33 | 13 | 33 | 0 | 1.0375 | Hydro | -1 | 0.019621 | 0 | 0 |  |  | 0 | 0 | -0.019621 | 0
8033 | AMISTADHYD2 | 2 | South | YES | -0.003715 | 25 | 13 | 25 | 0 | 1.0375 | Hydro | -1 | 0.019621 | 0 | 0 |  |  | 0 | 0 | -0.019621 | 0
88253 | HAMILTON | F | South | YES | -0.003715 | 0 | 0 | 0 | 0 | 1.04 | BLT | -1 | 0.019621 | 0 | 0 |  |  | 0 | 0 | -0.019621 | 0
5934 | SI_RAY5 | 5 | South | YES | 0 | 0 | 10 | 15 |  | 1.035 | GST | -1 | 0.015906 | 15 | 15 |  |  | 0 | 15 | -0.015906 | -0.2386
8139 | JOS #1 | MB | South | YES | 0 | 0 | 45 | 255 |  | 1.02 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8285 | LAR #1 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.0497 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8287 | LAR #2 | MB | South | YES | 0 | 0 | 9 | 32 |  | 1.04 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8288 | LAR #3 | MB | South | YES | 0 | 0 | 25 | 105 |  | 1.04 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8388 | BATES0A | MB | South | YES | 0 | 0 | 21 | 71 |  | 1.033 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8393 | BATES0B | MB | South | YES | 0 | 0 | 25 | 110 |  | 1.03 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8437 | NUECES_B0C | MB | South | YES | 0 | 0 | 7 | 30 |  | 1.03 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8438 | NUECES_B0B | MB | South | YES | 0 | 0 | 26 | 169 |  | 1.03 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
8442 | NUECES_B0A | MB | South | YES | 0 | 0 | 81 | 367 |  | 1.03 | GST | -1 | 0.015906 | 0 | 0 |  |  | 0 | 0 | -0.015906 | 0
39190 | TNSLCGN1__8 | 1 | Houston | YES | 0 | 0 | 10 | 30 |  | 1.03 | Cogen | -1 | 0.015906 | 0 | 0 |  |  |  |  | -0.015906 | 0
48671 | FTR_GT1_5105 | 1 | North | YES | 0.001229 | 154.2 | 0 | 154.2 | 0 | 1.0319 | CC | 1 | 0.024995 | 154.2 | 154.2 | 0.18951 | 154.2 |  |  | 0.024995 | 3.8543
48672 | FTR_GT2_5110 | 2 | North | YES | 0.001229 | 159 | 0 | 159 | 0 | 1.0319 | CC | 1 | 0.024995 | 159 | 159 | 0.19541 | 159 |  |  | 0.024995 | 3.9742
48673 | FTR_GT3_5085 | 3 | North | YES | 0.001229 | 158 | 0 | 158 | 0 | 1.0319 | CC | 1 | 0.024995 | 158 | 158 | 0.19418 | 158 |  |  | 0.024995 | 3.9492
48674 | FTR_CN4_5095 | 4 | North | YES | 0.001229 | 380 | 0 | 380 | 0 | 1.0319 | CC | 1 | 0.024995 | 380 | 380 | 0.46702 | 380 |  |  | 0.024995 | 9.4982
32883 | BRYN_DNSBY3 | 1 | North | YES | 0.001393 | 0 | 2 | 48 |  | 1.015 | GST | 1 | 0.025159 | 48 | 48 | 0.066864 | 48 |  |  | 0.025159 | 1.2076
32884 | BRYN_DNSBY13 | 1 | North | YES | 0.001393 | 46 | 2 | 46 | 0 | 1.015 | GST | 1 | 0.025159 | 46 | 46 | 0.064078 | 46 |  |  | 0.025159 | 1.1573
32892 | BRYN_DNSBY14 | 1 | North | YES | 0.001393 | 84 | 25 | 105 | 0 | 1.035 | GST | 1 | 0.025159 | 105 | 105 | 0.14627 | 105 |  |  | 0.025159 | 2.6417
32886 | BRYN_ATKINS3 | MB | North | YES | 0.001585 | 0 | 5 | 12 |  | 1 | GST | 1 | 0.025351 | 0 | 0 | 0 | 0 |  |  | 0.025351 | 0
32887 | BRYN_ATKINS6 | MB | North | YES | 0.001585 | 0 | 12 | 51 |  | 1.028 | GST | 1 | 0.025351 | 0 | 0 | 0 | 0 |  |  | 0.025351 | 0
32888 | BRYN_ATKINS7 | 1 | North | YES | 0.001585 | 13.6 | 4 | 17 |  | 1.028 | GGT | 1 | 0.025351 | 17 | 17 | 0.026945 | 17 |  |  | 0.025351 | 0.43097
32890 | BRYN_ATKINS4 | MB | North | YES | 0.001585 | 0 | 5 | 22 |  | 1.031 | GST | 1 | 0.025351 | 0 | 0 | 0 | 0 |  |  | 0.025351 | 0
32891 | BRYN_ATKINS5 | MB | North | YES | 0.001585 | 0 | 5 | 25 |  | 1.031 | GST | 1 | 0.025351 | 0 | 0 | 0 | 0 |  |  | 0.025351 | 0
32798 | BRYN_TAMUGEN | 1 | North | YES | 0.001704 | 32 | 0 | 32 |  | 1.02 | GST | 1 | 0.02547 | 32 | 32 | 0.054528 | 32 |  |  | 0.02547 | 0.81505
990 | GIBN_CREK_G1 | 1 | North | YES | 0.002383 | 463 | 200 | 463 | 0 | 1.0275 | LIGCO | 1 | 0.026149 | 0 | 463 | 1.1033 | 463 |  |  | 0.026149 | 12.1071
39960 | TNTNPONE_18 | 1 | North | YES | 0.006313 | 152.3 | 30 | 152.3 |  | 1.04 | LIGCO | 1 | 0.030079 | 0 | 152.3 | 0.96147 | 152.3 |  |  | 0.030079 | 4.5811
39970 | TNTNPONE_28 | 1 | North | YES | 0.006313 | 153 | 30 | 153 |  | 1.04 | LIGCO | 1 | 0.030079 | 0 | 153 | 0.96589 | 153 |  |  | 0.030079 | 4.6021
3416 | LAKE_CRK1_G | 1 | North | YES | 0.006707 | 60 | 33 | 75 |  | 1.029 | GST | 1 | 0.030473 | 75 | 75 | 0.50303 | 75 |  |  | 0.030473 | 2.2855
3417 | LAKE_CRK2_G | 2 | North | YES | 0.006707 | 177.6 | 40 | 222 | 0 | 1.029 | GST | 1 | 0.030473 | 222 | 222 | 1.489 | 222 |  |  | 0.030473 | 6.7651
48721 | LEG_1___1 | 1 | North | YES | 0.007916 | 827 | 357 | 827 | 0 | 1.0348 | LIGCO | 1 | 0.031682 | 0 | 827 | 6.5465 | 827 |  |  | 0.031682 | 26.2012
48722 | LEG_2___2 | 2 | North | YES | 0.007916 | 819 | 357 | 819 | 0 | 1.0348 | LIGCO | 1 | 0.031682 | 0 | 819 | 6.4832 | 819 |  |  | 0.031682 | 25.9477
238 | BOSQUESW505 | 1 | North | YES | 0.011625 | 255 | 0 | 255 | 0 | 1.02 | CC | 1 | 0.035391 | 255 | 255 | 2.9644 | 255 |  |  | 0.035391 | 9.0248
239 | BOSQUESW502 | 1 | North | YES | 0.011625 | 119.2 | 0 | 149 | 0 | 1.02 | GGT | 1 | 0.035391 | 149 | 149 | 1.7321 | 149 |  |  | 0.035391 | 5.2733
247 | BOSQUESW501 | 2 | North | YES | 0.011625 | 124.8 | 0 | 156 | 0 | 1.02 | GGT | 1 | 0.035391 | 156 | 156 | 1.8135 | 156 |  |  | 0.035391 | 5.521
3403 | THOUSE_1G | 1 | North | YES | 0.011689 | 563 | 200 | 563 | 0 | 1.012 | GSC | 1 | 0.035455 | 563 | 563 | 6.5809 | 563 |  |  | 0.035455 | 19.9613
3404 | THOUSE_2G | 2 | North | YES | 0.011689 | 807 | 250 | 807 | 0 | 1.012 | GSC | 1 | 0.035455 | 807 | 807 | 9.433 | 807 |  |  | 0.035455 | 28.6124
3381 | BBRN_1G | 1 | North | YES | 0.011953 | 618 | 225 | 618 | 0 | 1.03 | LIGCO | 1 | 0.035719 | 0 | 618 | 7.387 | 618 |  |  | 0.035719 | 22.0745
3382 | BBRN_2G | 2 | North | YES | 0.011953 | 589 | 225 | 589 | 0 | 1.03 | LIGCO | 1 | 0.035719 | 0 | 589 | 7.0403 | 589 |  |  | 0.035719 | 21.0386
251 | BOSQUESW803 | 2 | North | YES | 0.012027 | 150 | 0 | 150 |  | 1.032 | CC | 1 | 0.035793 | 150 | 150 | 1.804 | 150 |  |  | 0.035793 | 5.369
253 | BOSQUESW804 | 2 | North | YES | 0.012027 | 80 | 0 | 80 |  | 1.032 | CC | 1 | 0.035793 | 80 | 80 | 0.96216 | 80 |  |  | 0.035793 | 2.8635
13131 | CALFREST_1G | 1 | North | YES | 0.012379 | 150.7 | 40 | 150.7 | 0 | 1.031 | CC | 1 | 0.036145 | 150.7 | 150.7 | 1.8655 | 150.7 |  |  | 0.036145 | 5.4471
13132 | CALFREST_2G | 2 | North | YES | 0.012379 | 151 | 57 | 151 | 0 | 1.031 | CC | 1 | 0.036145 | 151 | 151 | 1.8692 | 151 |  |  | 0.036145 | 5.4579
13133 | CALFREST_3G | 3 | North | YES | 0.012379 | 177.4 | 40 | 177.4 | 0 | 1.031 | CC | 1 | 0.036145 | 177.4 | 177.4 | 2.196 | 177.4 |  |  | 0.036145 | 6.4122
13134 | CALFREST_4G | 4 | North | YES | 0.01245 | 151.5 | 40 | 151.5 | 0 | 1.031 | CC | 1 | 0.036216 | 151.5 | 151.5 | 1.8862 | 151.5 |  |  | 0.036216 | 5.4868
13135 | CALFREST_5G | 5 | North | YES | 0.01245 | 152.3 | 57 | 152.3 | 0 | 1.031 | CC | 1 | 0.036216 | 152.3 | 152.3 | 1.8961 | 152.3 |  |  | 0.036216 | 5.5157
13136 | CALFREST_6G | 6 | North | YES | 0.01245 | 177.5 | 40 | 177.5 | 0 | 1.031 | CC | 1 | 0.036216 | 177.5 | 177.5 | 2.2099 | 177.5 |  |  | 0.036216 | 6.4284
244 | WHITNYDM01 | 1 | North | YES | 0.013833 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.037599 | 0 | 0 | 0 | 0 |  |  | 0.037599 | 0
245 | WHITNYDM02 | 2 | North | YES | 0.013833 | 15 | 0 | 15 | 0 | 1.035 | Hydro | 1 | 0.037599 | 0 | 0 | 0 | 0 |  |  | 0.037599 | 0
3107 | STRYKER_1G | 1 | North | YES | 0.014198 | 145.6 | 45 | 182 | 0 | 1.029 | GST | 1 | 0.037964 | 182 | 182 | 2.584 | 182 |  |  | 0.037964 | 6.9095
3108 | STRYKER_2G | 2 | North | YES | 0.014198 | 484 | 75 | 484 | 0 | 1.029 | GST | 1 | 0.037964 | 484 | 484 | 6.8718 | 484 |  |  | 0.037964 | 18.3747
3113 | LUFKINWB_1G | 1 | North | YES | 0.014307 | 0 | 0 | 50 |  | 1.01 | Trash | 1 | 0.038073 | 50 | 50 | 0.71535 | 50 |  |  | 0.038073 | 1.9037
3348 | CHAMPION_1G | MB | North | YES | 0.014325 | 0 | 42 | 42 |  | 1 | Cogen | 1 | 0.038091 | 0 | 0 | 0 | 0 |  |  | 0.038091 | 0
3126 | TRINIDAD_6G | 1 | North | YES | 0.014468 | 179.2 | 46 | 224 | 0 | 1 | GST | 1 | 0.038234 | 224 | 224 | 3.2408 | 224 |  |  | 0.038234 | 8.5645
13116 | TGATEWAY_1G | 1 | North | YES | 0.014534 | 151 | 30 | 151 | 0 | 1.0232 | CC | 1 | 0.0383 | 151 | 151 | 2.1946 | 151 |  |  | 0.0383 | 5.7833
13117 | TGATEWAY_2G | 2 | North | YES | 0.014534 | 130 | 30 | 130 | 0 | 1.0232 | CC | 1 | 0.0383 | 130 | 130 | 1.8894 | 130 |  |  | 0.0383 | 4.979
13118 | TGATEWAY_3G | 3 | North | YES | 0.014534 | 148 | 30 | 148 | 0 | 1.0232 | CC | 1 | 0.0383 | 148 | 148 | 2.151 | 148 |  |  | 0.0383 | 5.6684
13119 | TGATEWAY_4G | 4 | North | YES | 0.014534 | 399 | 65 | 399 | 0 | 1.0232 | CC | 1 | 0.0383 | 399 | 399 | 5.7991 | 399 |  |  | 0.0383 | 15.2818
3097 | MARTLAKE_1G | 1 | North | YES | 0.014738 | 790 | 500 | 790 | 0 | 1.017 | LIGCO | 1 | 0.038504 | 0 | 790 | 11.643 | 790 |  |  | 0.038504 | 30.4183
3098 | MARTLAKE_2G | 2 | North | YES | 0.014738 | 795 | 461 | 795 | 0 | 1.017 | LIGCO | 1 | 0.038504 | 0 | 795 | 11.7167 | 795 |  |  | 0.038504 | 30.6108
3099 | MARTLAKE_3G | 3 | North | YES | 0.014738 | 804 | 500 | 804 | 0 | 1.017 | LIGCO | 1 | 0.038504 | 0 | 804 | 11.8494 | 804 |  |  | 0.038504 | 30.9574
12322 | ENNSTRAC_1G | 1 | North | YES | 0.016124 | 196 | 130 | 196 | 0 | 1.036 | CC | 1 | 0.03989 | 196 | 196 | 3.1603 | 196 |  |  | 0.03989 | 7.8185
12323 | ENNSTRAC_2G | 2 | North | YES | 0.016124 | 116 | 100 | 116 | 0 | 1.036 | CC | 1 | 0.03989 | 116 | 116 | 1.8704 | 116 |  |  | 0.03989 | 4.6273
12411 | FPLEFR1A_G | 1 | North | YES | 0.016233 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.039999 | 161 | 161 | 2.6135 | 161 |  |  | 0.039999 | 6.4399
12412 | FPLEFR1B_G | 2 | North | YES | 0.016233 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.039999 | 164 | 164 | 2.6622 | 164 |  |  | 0.039999 | 6.5599
12413 | FPLEFR1C_G | 3 | North | YES | 0.016233 | 164 | 72 | 164 | 0 | 1 | CC | 1 | 0.039999 | 164 | 164 | 2.6622 | 164 |  |  | 0.039999 | 6.5599
12414 | FPLEFR1S_G | 4 | North | YES | 0.016233 | 414 | 191 | 414 | 0 | 1 | CC | 1 | 0.039999 | 414 | 414 | 6.7205 | 414 |  |  | 0.039999 | 16.5597
12421 | FPLEFR2A_G | 1 | North | YES | 0.016233 | 162 | 72 | 162 | 0 | 1 | CC | 1 | 0.039999 | 162 | 162 | 2.6297 | 162 |  |  | 0.039999 | 6.4799
12422 | FPLEFR2B_G | 2 | North | YES | 0.016233 | 161 | 72 | 161 | 0 | 1 | CC | 1 | 0.039999 | 161 | 161 | 2.6135 | 161 |  |  | 0.039999 | 6.4399
12423 | FPLEFR2C_G | 3 | North | YES | 0.016233 | 163 | 72 | 163 | 0 | 1 | CC | 1 | 0.039999 | 163 | 163 | 2.646 | 163 |  |  | 0.039999 | 6.5199
12424 | FPLEFR2S_G | 4 | North | YES | 0.016233 | 415 | 191 | 415 | 0 | 1 | CC | 1 | 0.039999 | 415 | 415 | 6.7367 | 415 |  |  | 0.039999 | 16.5997
12440 | PARKD_1SVC8 | 1 | North | YES | 0.016463 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.040229 | 0 | 0 | 0 | 0 |  |  | 0.040229 | 0
12449 | PARKD_2SVC8 | 1 | North | YES | 0.016463 | 0 | 0 | 0 | 0 | 1.007 | GST | 1 | 0.040229 | 0 | 0 | 0 | 0 |  |  | 0.040229 | 0
2451 | LKHB1_G | 1 | North | YES | 0.016468 | 0 | 80 | 391 |  | 1.022 | GST | 1 | 0.040234 | 391 | 391 | 6.439 | 391 |  |  | 0.040234 | 15.7316
2452 | LKHB2_G | 2 | North | YES | 0.016468 | 516 | 80 | 516 | 0 | 1.022 | GST | 1 | 0.040234 | 516 | 516 | 8.4975 | 516 |  |  | 0.040234 | 20.7609
948 | STEAM1 | 1 | North | YES | 0.016671 | 0 | 12 | 20 |  | 1.02 | GST | 1 | 0.040437 | 20 | 20 | 0.33342 | 20 |  |  | 0.040437 | 0.80874
949 | STEAM2 | 1 | North | YES | 0.016671 | 26 | 8 | 26 | 0 | 0.99 | GST | 1 | 0.040437 | 26 | 26 | 0.43345 | 26 |  |  | 0.040437 | 1.0514
950 | STEAM3 | 1 | North | YES | 0.016671 | 41 | 13 | 42 | 0 | 1.02 | GST | 1 | 0.040437 | 42 | 42 | 0.70018 | 42 |  |  | 0.040437 | 1.6984
837 | NEWMAN_G5 | 1 | North | YES | 0.016701 | 0 | 15 | 40 |  | 1.01 | GST | 1 | 0.040467 | 40 | 40 | 0.66804 | 40 |  |  | 0.040467 | 1.6187
842 | OLINGER_G1 | 1 | North | YES | 0.016749 | 55.4 | 20 | 79 | 0 | 1.03 | GST | 1 | 0.040515 | 79 | 79 | 1.3232 | 79 |  |  | 0.040515 | 3.2007
843 | OLINGER_G2 | 1 | North | YES | 0.016749 | 76.2 | 25 | 110 | 0 | 1.03 | GST | 1 | 0.040515 | 110 | 110 | 1.8424 | 110 |  |  | 0.040515 | 4.4567
844 | OLINGER_G3 | 1 | North | YES | 0.016749 | 103.9 | 45 | 150 | 0 | 1.03 | GST | 1 | 0.040515 | 150 | 150 | 2.5124 | 150 |  |  | 0.040515 | 6.0773
845 | OLINGER_G4 | 1 | North | YES | 0.016749 | 51.9 | 0 | 76 | 0 | 1.03 | GGT | 1 | 0.040515 | 76 | 76 | 1.2729 | 76 |  |  | 0.040515 | 3.0792
1941 | MDLTHELP_1G | 1 | North | YES | 0.01683 | 216.4 | 74 | 216.4 | 0 | 1 | CC | 1 | 0.040596 | 216.4 | 216.4 | 3.642 | 216.4 |  |  | 0.040596 | 8.785
1942 | MDLTHELP_2G | 2 | North | YES | 0.01683 | 216.1 | 74 | 216.1 | 0 | 1 | CC | 1 | 0.040596 | 216.1 | 216.1 | 3.637 | 216.1 |  |  | 0.040596 | 8.7728
2413 | MTCK6_G | 6 | North | YES | 0.016845 | 0 | 30 | 118 |  | 1.022 | GST | 1 | 0.040611 | 118 | 118 | 1.9877 | 118 |  |  | 0.040611 | 4.7921
2414 | MTCK7_G | 7 | North | YES | 0.016845 | 0 | 30 | 115 |  | 1.022 | GST | 1 | 0.040611 | 115 | 115 | 1.9372 | 115 |  |  | 0.040611 | 4.6703
2417 | MTCK8_G | 8 | North | YES | 0.016845 | 444.8 | 60 | 556 | 0 | 1.022 | GSC | 1 | 0.040611 | 556 | 556 | 9.3658 | 556 |  |  | 0.040611 | 22.5798
1701 | MOSES_1G | 1 | North | YES | 0.01695 | 558 | 175 | 558 | 0 | 1.023 | LIGCO | 1 | 0.040716 | 0 | 558 | 9.4581 | 558 |  |  | 0.040716 | 22.7196
1702 | MOSES_2G | 2 | North | YES | 0.01695 | 579 | 175 | 579 | 0 | 1.023 | LIGCO | 1 | 0.040716 | 0 | 579 | 9.814 | 579 |  |  | 0.040716 | 23.5747
1703 | MOSES_3G | 3 | North | YES | 0.01695 | 808 | 463 | 808 | 0 | 1.023 | LIGCO | 1 | 0.040716 | 0 | 808 | 13.6956 | 808 |  |  | 0.040716 | 32.8987
5925 | DCEAST | EQ | North | YES | 0.01695 | 400.3 | -600 | 600 | 0 | 1.025 | DCTie | 1 | 0.040716 | 0 | 0 | 0 | 0 |  |  | 0.040716 | 0
1675 | PEC_1G | 1 | North | YES | 0.017033 | 76.7 | 35 | 76.7 | 0 | 1.022 | Cogen | 1 | 0.040799 | 0 | 0 | 0 | 0 |  |  | 0.040799 | 0
1676 | PEC_2G | 2 | North | YES | 0.017033 | 79.6 | 35 | 79.6 | 0 | 1.022 | Cogen | 1 | 0.040799 | 0 | 0 | 0 | 0 |  |  | 0.040799 | 0
1677 | PEC_3G | 3 | North | YES | 0.017033 | 88.4 | 35 | 88.4 | 0 | 1.022 | Cogen | 1 | 0.040799 | 0 | 0 | 0 | 0 |  |  | 0.040799 | 0
1678 | LAMARPWR_1G | 1 | North | YES | 0.017069 | 160 | 67.7 | 160 | 0 | 1.038 | CC | 1 | 0.040835 | 160 | 160 | 2.731 | 160 |  |  | 0.040835 | 6.5336
1679 | LAMARPWR_2G | 2 | North | YES | 0.017069 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.040835 | 156 | 156 | 2.6628 | 156 |  |  | 0.040835 | 6.3703
1680 | LAMARPWR_3G | 3 | North | YES | 0.017069 | 196 | 129.1 | 196 | 0 | 1.038 | CC | 1 | 0.040835 | 196 | 196 | 3.3455 | 196 |  |  | 0.040835 | 8.0037
1681 | LAMARPWR_4G | 4 | North | YES | 0.017069 | 156 | 67.7 | 156 | 0 | 1.038 | CC | 1 | 0.040835 | 156 | 156 | 2.6628 | 156 |  |  | 0.040835 | 6.3703
1682 | LAMARPWR_5G | 5 | North | YES | 0.017069 | 157 | 67.7 | 157 | 0 | 1.038 | CC | 1 | 0.040835 | 157 | 157 | 2.6798 | 157 |  |  | 0.040835 | 6.4111
1683 | LAMARPWR_6G | 6 | North | YES | 0.017069 | 198 | 129.1 | 198 | 0 | 1.038 | CC | 1 | 0.040835 | 198 | 198 | 3.3797 | 198 |  |  | 0.040835 | 8.0854
2418 | MTCK2_G | 2 | North | YES | 0.017124 | 0 | 10 | 23 |  | 0.971 | GSC | 1 | 0.04089 | 23 | 23 | 0.39385 | 23 |  |  | 0.04089 | 0.94047
2419 | MTCK3_G | MB | North | YES | 0.017124 | 0 | 10 | 63 |  | 0.971 | GSC | 1 | 0.04089 | 0 | 0 | 0 | 0 |  |  | 0.04089 | 0
1689 | VALLEY_3G | 3 | North | YES | 0.017132 | 0 | 25 | 375 |  | 1.003 | GST | 1 | 0.040898 | 375 | 375 | 6.4245 | 375 |  |  | 0.040898 | 15.3368
11691 | KMICHICT1_G | 1 | North | YES | 0.017132 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.040898 | 144 | 144 | 2.467 | 144 |  |  | 0.040898 | 5.8893
11692 | KMICHICT2_G | 2 | North | YES | 0.017132 | 146 | 80 | 146 | 0 | 1.026 | CC | 1 | 0.040898 | 146 | 146 | 2.5013 | 146 |  |  | 0.040898 | 5.9711
11693 | KMICHIST3_G | 3 | North | YES | 0.017132 | 312 | 60 | 312 | 0 | 1.026 | CC | 1 | 0.040898 | 312 | 312 | 5.3452 | 312 |  |  | 0.040898 | 12.7602
11694 | KMICHICT4_G | 4 | North | YES | 0.017132 | 144 | 80 | 144 | 0 | 1.026 | CC | 1 | 0.040898 | 144 | 144 | 2.467 | 144 |  |  | 0.040898 | 5.8893
11695 | KMICHICT5_G | 5 | North | YES | 0.017132 | 148 | 80 | 148 | 0 | 1.026 | CC | 1 | 0.040898 | 148 | 148 | 2.5355 | 148 |  |  | 0.040898 | 6.0529
11696 | KMICHIST6_G | 6 | North | YES | 0.017132 | 310 | 60 | 310 | 0 | 1.026 | CC | 1 | 0.040898 | 310 | 310 | 5.3109 | 310 |  |  | 0.040898 | 12.6784
1687 | VALLEY_1G | 1 | North | YES | 0.017315 | 136 | 15 | 170 | 0 | 1.029 | GST | 1 | 0.041081 | 170 | 170 | 2.9436 | 170 |  |  | 0.041081 | 6.9838
1688 | VALLEY_2G | 2 | North | YES | 0.017315 | 527 | 90 | 527 | 0 | 1.029 | GSC | 1 | 0.041081 | 527 | 527 | 9.125 | 527 |  |  | 0.041081 | 21.6498
6948 | DENISNDM | 1 | North | YES | 0.017452 | 40 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.041218 | 0 | 0 | 0 | 0 |  |  | 0.041218 | 0
6948 | DENISNDM | 2 | North | YES | 0.017452 | 31 | 5 | 40 | 0 | 1.015 | Hydro | 1 | 0.041218 | 0 | 0 | 0 | 0 |  |  | 0.041218 | 0
2381 | NTHLK1_G | 1 | North | YES | 0.017613 | 0 | 35 | 156 |  | 1.022 | GST | 1 | 0.041379 | 156 | 156 | 2.7476 | 156 |  |  | 0.041379 | 6.4552
2382 | NTHLK2_G | 2 | North | YES | 0.017613 | 0 | 35 | 181 |  | 1.022 | GST | 1 | 0.041379 | 181 | 181 | 3.188 | 181 |  |  | 0.041379 | 7.4896
2383 | NTHLK3_G | 3 | North | YES | 0.017613 | 0 | 50 | 329 |  | 1.022 | GST | 1 | 0.041379 | 329 | 329 | 5.7947 | 329 |  |  | 0.041379 | 13.6138
2371 | COLLIN_1G | MB | North | YES | 0.017734 | 0 | 40 | 138 |  | 1.022 | GST | 1 | 0.0415 | 0 | 0 | 0 | 0 |  |  | 0.0415 | 0
1937 | MDLTHELP_5G | 5 | North | YES | 0.018043 | 224 | 74 | 224 | 0 | 1 | CC | 1 | 0.041809 | 224 | 224 | 4.0416 | 224 |  |  | 0.041809 | 9.3653
1938 | MDLTHELP_6G | 6 | North | YES | 0.018043 | 226 | 74 | 226 | 0 | 1 | CC | 1 | 0.041809 | 226 | 226 | 4.0777 | 226 |  |  | 0.041809 | 9.4489
1943 | MDLTHELP_3G | 3 | North | YES | 0.018043 | 212 | 74 | 212 | 0 | 1 | CC | 1 | 0.041809 | 212 | 212 | 3.8251 | 212 |  |  | 0.041809 | 8.8636
1944 | MDLTHELP_4G | 4 | North | YES | 0.018043 | 211 | 74 | 211 | 0 | 1 | CC | 1 | 0.041809 | 211 | 211 | 3.8071 | 211 |  |  | 0.041809 | 8.8217
1948 | HANDLEY_4G | 4 | North | YES | 0.019037 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.042803 | 435 | 435 | 8.2811 | 435 |  |  | 0.042803 | 18.6194
1947 | HANDLEY_3G | 3 | North | YES | 0.019197 | 316 | 100 | 395 | 0 | 1.022 | GST | 1 | 0.042963 | 395 | 395 | 7.5828 | 395 |  |  | 0.042963 | 16.9705
1949 | HANDLEY_5G | 5 | North | YES | 0.019197 | 348 | 150 | 435 | 0 | 1.022 | GST | 1 | 0.042963 | 435 | 435 | 8.3507 | 435 |  |  | 0.042963 | 18.689
1945 | HANDLEY_1G | MB | North | YES | 0.019282 | 0 | 25 | 36 |  | 0.986 | GST | 1 | 0.043048 | 0 | 0 | 0 | 0 |  |  | 0.043048 | 0
1946 | HANDLEY_2G | MB | North | YES | 0.019282 | 0 | 30 | 68 |  | 0.986 | GST | 1 | 0.043048 | 0 | 0 | 0 | 0 |  |  | 0.043048 | 0
923 | SPENCER_G4 | 1 | North | YES | 0.019594 | 48 | 20 | 61 | 0 | 1.03 | GST | 1 | 0.04336 | 61 | 61 | 1.1952 | 61 |  |  | 0.04336 | 2.645
924 | SPENCER_G5 | 1 | North | YES | 0.019594 | 52 | 20 | 66 | 0 | 1.03 | GST | 1 | 0.04336 | 66 | 66 | 1.2932 | 66 |  |  | 0.04336 | 2.8618
1861 | EAGLEMNT_1G | MB | North | YES | 0.02052 | 0 | 30 | 112 |  | 1.022 | GST | 1 | 0.044286 | 0 | 0 | 0 | 0 |  |  | 0.044286 | 0
1862 | EAGLEMNT_2G | MB | North | YES | 0.02052 | 0 | 40 | 100 |  | 1.022 | GST | 1 | 0.044286 | 0 | 0 | 0 | 0 |  |  | 0.044286 | 0
1863 | EAGLEMNT_3G | MB | North | YES | 0.02052 | 0 | 50 | 378 |  | 1.022 | GST | 1 | 0.044286 | 0 | 0 | 0 | 0 |  |  | 0.044286 | 0
366 | JNSNCNTY802 | 1 | North | YES | 0.02077 | 168 | 20 | 168 | 0 | 1.02 | Cogen | 1 | 0.044536 | 0 | 0 | 0 | 0 |  |  | 0.044536 | 0
367 | JNSNCNTY802 | 2 | North | YES | 0.02077 | 90 | 20 | 90 | 0 | 1.02 | Cogen | 1 | 0.044536 | 0 | 0 | 0 | 0 |  |  | 0.044536 | 0
728 | WOLFRIDGE801 | 1 | North | YES | 0.020793 | 11.2 | 0 | 112.5 | 0 | 0.99 | Wind | 1 | 0.044559 | 0 | 112.5 | 2.3392 | 112.5 |  |  | 0.044559 | 5.0129
580 | JCKCNTY801 | 1 | North | YES | 0.022268 | 288 | 0 | 288 | 0 | 1.022 | CC | 1 | 0.046034 | 288 | 288 | 6.4132 | 288 |  |  | 0.046034 | 13.2579
581 | JCKCNTY802 | 2 | North | YES | 0.022268 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.046034 | 147 | 147 | 3.2734 | 147 |  |  | 0.046034 | 6.767
582 | JCKCNTY803 | 3 | North | YES | 0.022268 | 147 | 0 | 147 | 0 | 1.022 | CC | 1 | 0.046034 | 147 | 147 | 3.2734 | 147 |  |  | 0.046034 | 6.767
1889 | DECRDOVA_1G | 1 | North | YES | 0.022566 | 779 | 255 | 779 | 0 | 1.02 | GSC | 1 | 0.046332 | 779 | 779 | 17.5789 | 779 |  |  | 0.046332 | 36.0928
1453 | WCPWRCO_1G | 1 | North | YES | 0.022882 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.046648 | 204 | 204 | 4.6679 | 204 |  |  | 0.046648 | 9.5162
1454 | WCPWRCO_2G | 2 | North | YES | 0.022882 | 204 | 50 | 204 | 0 | 1.02 | CC | 1 | 0.046648 | 204 | 204 | 4.6679 | 204 |  |  | 0.046648 | 9.5162
1455 | WCPWRCO_3G | 3 | North | YES | 0.022882 | 242 | 50 | 242 |  | 1.02 | CC | 1 | 0.046648 | 242 | 242 | 5.5374 | 242 |  |  | 0.046648 | 11.2889
1892 | DECRDOVA_2G | A | North | YES | 0.023192 | 65 | 65 | 70 | 0 | 1.025 | GGT | 1 | 0.046958 | 70 | 70 | 1.6234 | 70 |  |  | 0.046958 | 3.2871
1893 | DECRDOVA_3G | B | North | YES | 0.023192 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.046958 | 69 | 69 | 1.6002 | 69 |  |  | 0.046958 | 3.2401
1894 | DECRDOVA_4G | C | North | YES | 0.023192 | 65 | 65 | 69 | 0 | 1.025 | GGT | 1 | 0.046958 | 69 | 69 | 1.6002 | 69 |  |  | 0.046958 | 3.2401
1895 | DECRDOVA_5G | D | North | YES | 0.023192 | 65 | 65 | 68 | 0 | 1.025 | GGT | 1 | 0.046958 | 68 | 68 | 1.5771 | 68 |  |  | 0.046958 | 3.1932
503 | NTHTEXAS01 | 1 | North | YES | 0.023454 | 0 | 5 | 18 |  | 1.015 | GST | 1 | 0.04722 | 18 | 18 | 0.42217 | 18 |  |  | 0.04722 | 0.84996
504 | NTHTEXAS02 | 2 | North | YES | 0.023454 | 14.4 | 5 | 18 |  | 1.015 | GST | 1 | 0.04722 | 18 | 18 | 0.42217 | 18 |  |  | 0.04722 | 0.84996
505 | NTHTEXAS03 | 3 | North | YES | 0.023454 | 30.4 | 15 | 38 |  | 1.015 | GST | 1 | 0.04722 | 38 | 38 | 0.89125 | 38 |  |  | 0.04722 | 1.7944
1877 | WLFHOLW_1G | 1 | North | YES | 0.023562 | 217.3 | 89.2 | 217.3 | 0 | 1.032 | CC | 1 | 0.047328 | 217.3 | 217.3 | 5.12 | 217.3 |  |  | 0.047328 | 10.2844
1878 | WLFHOLW_2G | 2 | North | YES | 0.023562 | 215.7 | 105 | 215.7 | 0 | 1.032 | CC | 1 | 0.047328 | 215.7 | 215.7 | 5.0823 | 215.7 |  |  | 0.047328 | 10.2087
1879 | WLFHOLW_3G | 3 | North | YES | 0.023562 | 272.4 | 89.2 | 272.4 | 0 | 1.032 | CC | 1 | 0.047328 | 272.4 | 272.4 | 6.4183 | 272.4 |  |  | 0.047328 | 12.8922
1898 | COMCHEPK_1G | 1 | North | YES | 0.024284 | 1159 | 1150 | 1159 | 0 | 1.032 | Nuc | 1 | 0.04805 | 0 | 0 | 0 | 0 |  |  | 0.04805 | 0
1899 | COMCHEPK_2G | 2 | North | YES | 0.024284 | 1159 | 1128 | 1159 | 0 | 1.032 | Nuc | 1 | 0.04805 | 0 | 0 | 0 | 0 |  |  | 0.04805 | 0
344 | MRSSHPRD | 1 | North | YES | 0.024847 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.048613 | 0 | 0 | 0 | 0 |  |  | 0.048613 | 0
345 | MRSSHPRD01 | 2 | North | YES | 0.024847 | 12 | 0 | 12 |  | 1.03 | Hydro | 1 | 0.048613 | 0 | 0 | 0 | 0 |  |  | 0.048613 | 0
1432 | GRHAMSES_2G | 2 | North | YES | 0.024988 | 294.9 | 90 | 366 | 0 | 1.014 | GST | 1 | 0.048754 | 366 | 366 | 9.1456 | 366 |  |  | 0.048754 | 17.844
1600 | BARTNWND_1G | 1 | North | YES | 0.02512 | 12 | 0 | 120 | 0 | 1.022 | Wind | 1 | 0.048886 | 0 | 120 | 3.0144 | 120 |  |  | 0.048886 | 5.8663
1479 | WFCOGEN_1G | 1 | North | YES | 0.025169 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.048935 | 0 | 0 | 0 | 0 |  |  | 0.048935 | 0
1479 | WFCOGEN_1G | 2 | North | YES | 0.025169 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.048935 | 0 | 0 | 0 | 0 |  |  | 0.048935 | 0
1482 | WFCOGEN_2G | 2 | North | YES | 0.025169 | 13.6 | 12 | 17 | 0 | 1 | Cogen | 1 | 0.048935 | 0 | 0 | 0 | 0 |  |  | 0.048935 | 0
1482 | WFCOGEN_2G | 1 | North | YES | 0.025169 | 16 | 12 | 20 | 0 | 1 | Cogen | 1 | 0.048935 | 0 | 0 | 0 | 0 |  |  | 0.048935 | 0
60202 | FRNDDRCS | F | West | YES | 0.025791 | 0 | 0 | 0 | 0 | 0.9985 | AVR | 1 | 0.049557 | 0 | 0 |  |  |  |  | 0.049557 | 0
1433 | GRHAMSES_1G | 1 | North | YES | 0.026551 | 242 | 60 | 242 | 0 | 1.038 | GST | 1 | 0.050317 | 242 | 242 | 6.4253 | 242 |  |  | 0.050317 | 12.1768
6100 | OKLA7A | EQ | West | YES | 0.026854 | 50 | -220 | 220 | 0 | 1.035 | DCTie | 1 | 0.05062 | 0 | 0 |  |  |  |  | 0.05062 | 0
6752 | OKLA0A | 1 | West | YES | 0.026854 | 649.7 | 175 | 649.7 | 0 | 1.035 | LIGCO | 1 | 0.05062 | 0 | 649.7 |  |  |  |  | 0.05062 | 32.888
1442 | COKFIELD_5 | 1 | North | YES | 0.027092 | 16.5 | 0 | 165 |  | 1.029 | Wind | 1 | 0.050858 | 0 | 165 | 4.4702 | 165 |  |  | 0.050858 | 8.3916
1438 | MESQUITW_2G | 1 | North | YES | 0.027756 | 23.6 | 0 | 236 |  | 1.017 | Wind | 1 | 0.051522 | 0 | 236 | 6.5504 | 236 |  |  | 0.051522 | 12.1592
1437 | MESQUITW_1G | 1 | North | YES | 0.027761 | 40 | 0 | 400 | 0 | 1.023 | Wind | 1 | 0.051527 | 0 | 400 | 11.1044 | 400 |  |  | 0.051527 | 20.6109
60018 | DSKY1 | 1 | West | YES | 0.027836 | 21 | 0 | 84 | 0 | 1.023 | Wind | 1 | 0.051602 | 0 | 84 |  |  |  |  | 0.051602 | 4.3346
60017 | ORNNWP1 | 1 | West | YES | 0.027943 | 20 | 0 | 80 |  | 1.027 | Wind | 1 | 0.051709 | 0 | 80 |  |  |  |  | 0.051709 | 4.1367
60000 | DSKY2 | 1 | West | YES | 0.028056 | 19.1 | 0 | 76.5 |  | 1.039 | Wind | 1 | 0.051822 | 0 | 76.5 |  |  |  |  | 0.051822 | 3.9644
6016 | SWMESA | 1 | West | YES | 0.028242 | 18.8 | 0 | 75 |  | 1.03 | Wind | 1 | 0.052008 | 0 | 75 |  |  |  |  | 0.052008 | 3.9006
60003 | KING_NE1A | 1 | West | YES | 0.028242 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.052008 | 0 | 80 |  |  |  |  | 0.052008 | 4.1607
60005 | KING_SE1A | 1 | West | YES | 0.028242 | 10 | 0 | 40 |  | 1.035 | Wind | 1 | 0.052008 | 0 | 40 |  |  |  |  | 0.052008 | 2.0803
38437 | TNSRBNMESA9 | 1 | West | YES | 0.028263 | 37.5 | 0 | 150 |  | 1.02 | Wind | 1 | 0.052029 | 0 | 150 |  |  |  |  | 0.052029 | 7.8044
38332 | TNWDWRDU2_8 | 1 | West | YES | 0.028271 | 20 | 0 | 80 | 0 | 1.0232 | Wind | 1 | 0.052037 | 0 | 80 |  |  |  |  | 0.052037 | 4.163
60016 | WOODWRD11A | 1 | West | YES | 0.028273 | 20 | 0 | 80 |  | 1.033 | Wind | 1 | 0.052039 | 0 | 80 |  |  |  |  | 0.052039 | 4.1631
60201 | RIO DRCS | F | West | YES | 0.028281 | 0 | 0 | 0 | 0 | 1.025 | AVR | 1 | 0.052047 | 0 | 0 |  |  |  |  | 0.052047 | 0
60007 | KING_SW1A | 1 | West | YES | 0.028385 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.052151 | 0 | 80 |  |  |  |  | 0.052151 | 4.1721
60019 | KING_NW1A | 1 | West | YES | 0.028385 | 20 | 0 | 80 |  | 1.03 | Wind | 1 | 0.052151 | 0 | 80 |  |  |  |  | 0.052151 | 4.1721
332 | RWMILLER01 | 1 | North | YES | 0.028771 | 58.4 | 18.5 | 73 | 0 | 1.04 | GST | 1 | 0.052537 | 73 | 73 | 2.1003 | 73 |  |  | 0.052537 | 3.8352
333 | RWMILLER02 | 2 | North | YES | 0.028771 | 95.2 | 37 | 119 | 0 | 1.04 | GST | 1 | 0.052537 | 119 | 119 | 3.4237 | 119 |  |  | 0.052537 | 6.2519
334 | RWMILLER03 | 3 | North | YES | 0.028771 | 166.4 | 65 | 208 | 0 | 1.04 | GST | 1 | 0.052537 | 208 | 208 | 5.9844 | 208 |  |  | 0.052537 | 10.9277
335 | RWMILLER04 | 4 | North | YES | 0.028771 | 81.6 | 0 | 102 | 0 | 1.04 | GST | 1 | 0.052537 | 102 | 102 | 2.9346 | 102 |  |  | 0.052537 | 5.3588
336 | RWMILLER05 | 5 | North | YES | 0.028771 | 80.8 | 0 | 101 | 0 | 1.04 | GST | 1 | 0.052537 | 101 | 101 | 2.9059 | 101 |  |  | 0.052537 | 5.3063
1416 | SWETWATR_1G | 1 | West | YES | 0.028895 | 30 | 18 | 30 | 0 | 1.026 | CC | 1 | 0.052661 | 30 | 30 |  |  |  |  | 0.052661 | 1.5798
1417 | SWETWATR_2G | 2 | West | YES | 0.028895 | 72 | 36 | 72 | 0 | 1.026 | CC | 1 | 0.052661 | 72 | 72 |  |  |  |  | 0.052661 | 3.7916
1418 | SWETWATR_3G | 3 | West | YES | 0.028895 | 68 | 36 | 68 | 0 | 1.026 | CC | 1 | 0.052661 | 68 | 68 |  |  |  |  | 0.052661 | 3.581
1419 | SWETWATR_4G | 4 | West | YES | 0.028895 | 61 | 36 | 61 | 0 | 1.026 | CC | 1 | 0.052661 | 61 | 61 |  |  |  |  | 0.052661 | 3.2123
1049 | ROSCOEWI_5 | 1 | West | YES | 0.029023 | 41.8 | 0 | 209 |  | 1.01 | Wind | 1 | 0.052789 | 0 | 209 |  |  |  |  | 0.052789 | 11.0329
1057 | ROSCOEWI_5 | 2 | West | YES | 0.029023 | 25.3 | 0 | 126.5 |  | 1.01 | Wind | 1 | 0.052789 | 0 | 126.5 |  |  |  |  | 0.052789 | 6.6778
1060 | ROSCOEWI_5 | 3 | West | YES | 0.029023 | 39.4 | 0 | 197 | 0 | 1.01 | Wind | 1 | 0.052789 | 0 | 197 |  |  |  |  | 0.052789 | 10.3995
1072 | ROSCOEWI_5 | 4 | West | YES | 0.029023 | 63.6 | 0 | 318 | 0 | 1.01 | Wind | 1 | 0.052789 | 0 | 318 |  |  |  |  | 0.052789 | 16.787
1002 | PBCTAGE_1G | A | West | YES | 0.029403 | 64 | 64 | 66 | 0 | 1.036 | GGT | 1 | 0.053169 | 66 | 66 |  |  |  |  | 0.053169 | 3.5092
1003 | PBCTBGE_2G | B | West | YES | 0.029403 | 65 | 65 | 66 | 0 | 1.036 | GGT | 1 | 0.053169 | 66 | 66 |  |  |  |  | 0.053169 | 3.5092
1004 | PBCTCGE_3G | C | West | YES | 0.029403 | 62 | 62 | 67 | 0 | 1.036 | GGT | 1 | 0.053169 | 67 | 67 |  |  |  |  | 0.053169 | 3.5623
1005 | PBCTDGE_4G | D | West | YES | 0.029403 | 65 | 65 | 68 | 0 | 1.036 | GGT | 1 | 0.053169 | 68 | 68 |  |  |  |  | 0.053169 | 3.6155
1006 | PBCTEGE_5G | E | West | YES | 0.029403 | 65 | 65 | 67 | 0 | 1.036 | GGT | 1 | 0.053169 | 67 | 67 |  |  |  |  | 0.053169 | 3.5623
1007 | PB5GEN_6G | 5 | West | YES | 0.029403 | 91.2 | 40 | 114 | 0 | 1.036 | GST | 1 | 0.053169 | 114 | 114 |  |  |  |  | 0.053169 | 6.0613
1008 | PB6GEN_7G | 6 | West | YES | 0.029403 | 515 | 130 | 515 | 0 | 1.036 | GST | 1 | 0.053169 | 515 | 515 |  |  |  |  | 0.053169 | 27.3821
7038 | L_DELAWA1_1Y | 1 | West | YES | 0.029421 | 3.5 | 0 | 35 | 0 | 1 | Wind | 1 | 0.053187 | 0 | 35 |  |  |  |  | 0.053187 | 1.8616
7038 | L_DELAWA1_1Y | 2 | West | YES | 0.029421 | 3 | 0 | 30 | 0 | 1 | Wind | 1 | 0.053187 | 0 | 30 |  |  |  |  | 0.053187 | 1.5956
1146 | NOTREES_1G | 1 | West | YES | 0.029459 | 29.8 | 0 | 149 | 0 | 1.017 | Wind | 1 | 0.053225 | 0 | 149 |  |  |  |  | 0.053225 | 7.9306
71051 | L_BITTCR1_1N | W1 | West | YES | 0.029501 | 7.5 | 0 | 37.5 |  | 1.02 | Wind | 1 | 0.053267 | 0 | 37.5 |  |  |  |  | 0.053267 | 1.9975
71054 | L_SWEETW1_1N | W1 | West | YES | 0.029501 | 21.5 | 0 | 107.5 |  | 1.02 | Wind | 1 | 0.053267 | 0 | 107.5 |  |  |  |  | 0.053267 | 5.7262
71057 | L_SWEETW1_2N | W1 | West | YES | 0.029501 | 27 | 0 | 135 |  | 1.02 | Wind | 1 | 0.053267 | 0 | 135 |  |  |  |  | 0.053267 | 7.1911
71059 | L_SWEETW1_3N | W1 | West | YES | 0.029501 | 23.8 | 0 | 119 | 0 | 1.02 | Wind | 1 | 0.053267 | 0 | 119 |  |  |  |  | 0.053267 | 6.3388
71060 | L_SWEETW1_4N | W1 | West | YES | 0.029501 | 21 | 0 | 105 | 0 | 1.02 | Wind | 1 | 0.053267 | 0 | 105 |  |  |  |  | 0.053267 | 5.5931
11020 | TIEHVSG_1G | 1 | West | YES | 0.029511 | 208.2 | 63 | 208.2 | 0 | 1.012 | CC | 1 | 0.053277 | 208.2 | 208.2 |  |  |  |  | 0.053277 | 11.0923
11021 | TIEHVCG_1G | 1 | West | YES | 0.029511 | 142.1 | 103 | 142.1 | 0 | 1.012 | CC | 1 | 0.053277 | 142.1 | 142.1 |  |  |  |  | 0.053277 | 7.5707
11022 | TIEHVCG_2G | 1 | West | YES | 0.029511 | 132.4 | 103 | 132.4 | 0 | 1.012 | CC | 1 | 0.053277 | 132.4 | 132.4 |  |  |  |  | 0.053277 | 7.0539
11023 | TIEHVCG_3G | 1 | West | YES | 0.029511 | 137.4 | 103 | 137.4 | 0 | 1.012 | CC | 1 | 0.053277 | 137.4 | 137.4 |  |  |  |  | 0.053277 | 7.3203
11024 | TIEHVCG_4G | 1 | West | YES | 0.029511 | 147 | 103 | 147 | 0 | 1.012 | CC | 1 | 0.053277 | 147 | 147 |  |  |  |  | 0.053277 | 7.8317
11025 | TIEHVSG_2G | 1 | West | YES | 0.029511 | 213.2 | 63 | 213.2 | 0 | 1.012 | CC | 1 | 0.053277 | 213.2 | 213.2 |  |  |  |  | 0.053277 | 11.3587
11001 | NAV1CT | 1 | West | YES | 0.029512 | 70.4 | 18 | 70.4 | 0 | 1.029 | CC | 1 | 0.053278 | 70.4 | 70.4 |  |  |  |  | 0.053278 | 3.7508
11009 | NAV2CT | 1 | West | YES | 0.029512 | 71.4 | 18 | 71.4 | 0 | 1.029 | CC | 1 | 0.053278 | 71.4 | 71.4 |  |  |  |  | 0.053278 | 3.8041
11011 | NAV3ST | 1 | West | YES | 0.029512 | 92.8 | 40 | 92.8 | 0 | 1.029 | CC | 1 | 0.053278 | 92.8 | 92.8 |  |  |  |  | 0.053278 | 4.9442
11012 | NAV4CT | 1 | West | YES | 0.029512 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.053278 | 80 | 80 |  |  |  |  | 0.053278 | 4.2623
11013 | NAV5CT | 1 | West | YES | 0.029512 | 80 | 18 | 80 | 0 | 1.029 | CC | 1 | 0.053278 | 80 | 80 |  |  |  |  | 0.053278 | 4.2623
11014 | NAV6ST | 1 | West | YES | 0.029512 | 115 | 40 | 115 | 0 | 1.029 | CC | 1 | 0.053278 | 115 | 115 |  |  |  |  | 0.053278 | 6.127
1045 | CALENG1G_1G | 1 | West | YES | 0.029594 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.05336 | 0 | 0 |  |  |  |  | 0.05336 | 0
1046 | CALENG2G_2G | 2 | West | YES | 0.029594 | 73.4 | 27 | 73.4 | 0 | 1.014 | Cogen | 1 | 0.05336 | 0 | 0 |  |  |  |  | 0.05336 | 0
1047 | CALENG3G_3G | 3 | West | YES | 0.029594 | 70.4 | 27 | 70.4 | 0 | 1.014 | Cogen | 1 | 0.05336 | 0 | 0 |  |  |  |  | 0.05336 | 0
1058 | LONGSHORE_5 | 3 | West | YES | 0.029602 | 23.4 | 0 | 117 |  | 1.01 | Wind | 1 | 0.053368 | 0 | 117 |  |  |  |  | 0.053368 | 6.2441
1058 | LONGSHORE_5 | 2 | West | YES | 0.029602 | 44 | 0 | 220 |  | 1.01 | Wind | 1 | 0.053368 | 0 | 220 |  |  |  |  | 0.053368 | 11.741
1058 | LONGSHORE_5 | 1 | West | YES | 0.029602 | 30 | 0 | 150 |  | 1.01 | Wind | 1 | 0.053368 | 0 | 150 |  |  |  |  | 0.053368 | 8.0052
1328 | OCOTILLO_1G | 1 | West | YES | 0.029734 | 11.6 | 0 | 58 |  | 1.01 | Wind | 1 | 0.0535 | 0 | 58 |  |  |  |  | 0.0535 | 3.103
1333 | MCDDONAL_8 | 1 | West | YES | 0.029767 | 42.8 | 0 | 214.2 |  | 1.01 | Wind | 1 | 0.053533 | 0 | 214.2 |  |  |  |  | 0.053533 | 11.4668
1326 | STANTONW_8 | 1 | West | YES | 0.029776 | 20.1 | 0 | 100.5 |  | 1.01 | Wind | 1 | 0.053542 | 0 | 100.5 |  |  |  |  | 0.053542 | 5.381
1170 | AIRLAMESA_1G | 1 | West | YES | 0.029888 | 0 | 0 | 180 |  | 1 | Wind | 1 | 0.053654 | 0 | 180 |  |  |  |  | 0.053654 | 9.6578
1037 | MORGAN5G_5G | 5 | West | YES | 0.029967 | 109.6 | 40 | 137 | 0 | 1.029 | GST | 1 | 0.053733 | 137 | 137 |  |  |  |  | 0.053733 | 7.3614
1039 | MRGNAG_1G | A | West | YES | 0.029967 | 69 | 69 | 69 | 0 | 1.029 | GGT | 1 | 0.053733 | 69 | 69 |  |  |  |  | 0.053733 | 3.7076
1040 | MRGNBG_2G | B | West | YES | 0.029967 | 70 | 70 | 71 | 0 | 1.029 | GGT | 1 | 0.053733 | 71 | 71 |  |  |  |  | 0.053733 | 3.8151
1041 | MRGNCG_3G | C | West | YES | 0.029967 | 69 | 69 | 70 | 0 | 1.029 | GGT | 1 | 0.053733 | 70 | 70 |  |  |  |  | 0.053733 | 3.7613
1042 | MRGNDG_4G | D | West | YES | 0.029967 | 68 | 68 | 68 | 0 | 1.029 | GGT | 1 | 0.053733 | 68 | 68 |  |  |  |  | 0.053733 | 3.6539
1043 | MRGNEG_5G | E | West | YES | 0.029967 | 68 | 68 | 70 | 0 | 1.029 | GGT | 1 | 0.053733 | 70 | 70 |  |  |  |  | 0.053733 | 3.7613
1044 | MRGNFG_6G | F | West | YES | 0.029967 | 66 | 66 | 66 | 0 | 1.029 | GGT | 1 | 0.053733 | 66 | 66 |  |  |  |  | 0.053733 | 3.5464
1302 | COYOTEWG_8 | 1 | West | YES | 0.030005 | 45 | 0 | 225 |  | 1.01 | Wind | 1 | 0.053771 | 0 | 225 |  |  |  |  | 0.053771 | 12.0985
1301 | BULLCREK_8 | 1 | West | YES | 0.030089 | 36 | 0 | 180 | 0 | 1.017 | Wind | 1 | 0.053855 | 0 | 180 |  |  |  |  | 0.053855 | 9.6939
1327 | WILDHRSE_1G | 1 | West | YES | 0.030089 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.053855 | 0 | 120 |  |  |  |  | 0.053855 | 6.4626
1360 | GUNSIGHT_8 | 1 | West | YES | 0.030103 | 24 | 0 | 120 | 0 | 1.01 | Wind | 1 | 0.053869 | 0 | 120 |  |  |  |  | 0.053869 | 6.4643
1068 | SCURRYCW_1G | 1 | West | YES | 0.030165 | 28.2 | 1.3 | 141 |  | 1.01 | Wind | 1 | 0.053931 | 0 | 141 |  |  |  |  | 0.053931 | 7.6043
1073 | SCURRYCW_2G | 2 | West | YES | 0.030165 | 24 | 0 | 120 | 0 | 1.017 | Wind | 1 | 0.053931 | 0 | 120 |  |  |  |  | 0.053931 | 6.4717
1061 | CIELOGEN_1G | 1 | West | YES | 0.030168 | 19.8 | 0 | 99 |  | 1 | Wind | 1 | 0.053934 | 0 | 99 |  |  |  |  | 0.053934 | 5.3395
1062 | CIELOGEN_2G | 1 | West | YES | 0.030168 | 12.2 | 0 | 61 |  | 1 | Wind | 1 | 0.053934 | 0 | 61 |  |  |  |  | 0.053934 | 3.29
1069 | KINDERMG_1G | 1 | West | YES | 0.030168 | 25 | 5 | 25 | 0 | 1.017 | Cogen | 1 | 0.053934 | 0 | 0 |  |  |  |  | 0.053934 | 0
1070 | KINDERMG_2G | 1 | West | YES | 0.030168 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.053934 | 0 | 0 |  |  |  |  | 0.053934 | 0
1071 | KINDERMG_3G | 1 | West | YES | 0.030168 | 45.7 | 12 | 45.7 | 0 | 1.017 | Cogen | 1 | 0.053934 | 0 | 0 |  |  |  |  | 0.053934 | 0
6637 | SNYDERW1A | 1 | West | YES | 0.030191 | 12.6 | 0 | 63 | 0 | 1.025 | Wind | 1 | 0.053957 | 0 | 63 |  |  |  |  | 0.053957 | 3.3993
36998 | RDCNYNG1 | 1 | West | YES | 0.030263 | 16.8 | 0 | 84 |  | 1.01 | Wind | 1 | 0.054029 | 0 | 84 |  |  |  |  | 0.054029 | 4.5385
60052 | WILDHRS11A | 1 | West | YES | 0.030325 | 25.3 | 0 | 126.5 | 0 | 1.005 | Wind | 1 | 0.054091 | 0 | 126.5 |  |  |  |  | 0.054091 | 6.8425
60053 | WILDHRS21A | 1 | West | YES | 0.030325 | 7.8 | 0 | 39 | 0 | 1.025 | Wind | 1 | 0.054091 | 0 | 39 |  |  |  |  | 0.054091 | 2.1096
1320 | BSP 1 | 1 | West | YES | 0.030343 | 25.5 | 2.9 | 25.8 | 0 | 1 | Cogen | 1 | 0.054109 | 0 | 0 |  |  |  |  | 0.054109 | 0
60081 | WHRLWIND1A | 1 | West | YES | 0.030442 | 12 | 0 | 60 | 0 | 1.03 | Wind | 1 | 0.054208 | 0 | 60 |  |  |  |  | 0.054208 | 3.2525
6144 | MCADOO1A | 1 | West | YES | 0.03068 | 15 | 0 | 150 | 0 | 1.025 | Wind | 1 | 0.054446 | 0 | 150 |  |  |  |  | 0.054446 | 8.1669
60058 | BUFF_GAP1A | 1 | West | YES | 0.030814 | 24 | 0 | 120 |  | 1 | Wind | 1 | 0.05458 | 0 | 120 |  |  |  |  | 0.05458 | 6.5496
60060 | CIRELLO | 1 | West | YES | 0.030814 | 46.6 | 0 | 233 | 0 | 1 | Wind | 1 | 0.05458 | 0 | 233 |  |  |  |  | 0.05458 | 12.7172
60063 | BUFF_GAP1B | 1 | West | YES | 0.030814 | 34 | 0 | 170.2 | 0 | 1.02 | Wind | 1 | 0.05458 | 0 | 170.2 |  |  |  |  | 0.05458 | 9.2896
60066 | H_HOLLOW1A | 1 | West | YES | 0.030814 | 44.4 | 0 | 222 | 0 | 1.005 | Wind | 1 | 0.05458 | 0 | 222 |  |  |  |  | 0.05458 | 12.1168
60068 | HHOLLOW21A | 1 | West | YES | 0.030814 | 36.8 | 0 | 184 | 0 | 1.025 | Wind | 1 | 0.05458 | 0 | 184 |  |  |  |  | 0.05458 | 10.0428
60070 | HHOLLOW31A | 1 | West | YES | 0.030814 | 44.8 | 0 | 224 | 0 | 1.025 | Wind | 1 | 0.05458 | 0 | 224 |  |  |  |  | 0.05458 | 12.226
60072 | HHOLLOW41A | 1 | West | YES | 0.030814 | 23 | 0 | 115 | 0 | 1.025 | Wind | 1 | 0.05458 | 0 | 115 |  |  |  |  | 0.05458 | 6.2767
76031 | L_GASCCR1_1N | W1 | West | YES | 0.030901 | 30 | 0 | 150 | 0 | 1.02 | Wind | 1 | 0.054667 | 0 | 150 |  |  |  |  | 0.054667 | 8.2001
1349 | WESTXWIN_1G | 1 | West | YES | 0.031081 | 1.3 | 0 | 6.6 |  | 1.014 | Wind | 1 | 0.054847 | 0 | 6.6 |  |  |  |  | 0.054847 | 0.36199
1350 | NWPWRG1_1G | 1 | West | YES | 0.031081 | 6.9 | 1 | 34.3 |  | 1.014 | Wind | 1 | 0.054847 | 0 | 34.3 |  |  |  |  | 0.054847 | 1.8813
76091 | L_DIVIDE1_1N | W1 | West | YES | 0.031149 | 110 | 0 | 550 | 0 | 1.02 | Wind | 1 | 0.054915 | 0 | 550 |  |  |  |  | 0.054915 | 30.2034
1343 | TRENTIPP_8 | 1 | West | YES | 0.032859 | 30 | 0 | 150 |  | 1.014 | Wind | 1 | 0.056625 | 0 | 150 |  |  |  |  | 0.056625 | 8.4938
1354 | AEPWIND_8 | 1 | West | YES | 0.032859 | 20.2 | 0 | 101 |  | 1 | Wind | 1 | 0.056625 | 0 | 101 |  |  |  |  | 0.056625 | 5.7191
1643 | SLSTR1PP_1G | 1 | North | YES | 0.036615 | 6 | 0 | 60 | 0 | 1.022 | Wind | 1 | 0.060381 | 0 | 60 | 2.1969 | 60 |  |  | 0.060381 | 3.6229
60057 | CALLAHAN1A | 1 | West | YES | 0.037241 | 22.8 | 0 | 114 | 0 | 1.04 | Wind | 1 | 0.061007 | 0 | 114 |  |  |  |  | 0.061007 | 6.9548
6407 | TURKTRAK1A | 1 | West | YES | 0.041999 | 33.9 | 0 | 169.5 | 0 | 1.025 | Wind | 1 | 0.065765 | 0 | 169.5 |  |  |  |  | 0.065765 | 11.1472

## Zones
Houston | -1
North | 1
South | -1
West | 1
SET UP AREA, copy & paste values to cell B1
Source | North |  | N to H | N to W | N to S | W to N | S to N | W to S
Sink | South | Houston | -1 | 1 | -1 | -1 | 1 | -1
|  | North | 1 | 1 | 1 | -1 | -1 | -1
|  | South | -1 | 1 | -1 | -1 | 1 | -1
|  | West | 1 | -1 | 1 | 1 | -1 | 1
|  | Source | North | North | North | West | South | West
|  | Sink | Houston | West | South | North | North | South

## Tech
Number of Bus | Name of Bus | Tech Type
238 | BOSQUESW505 | CC
239 | BOSQUESW502 | GGT
244 | WHITNYDM01 | Hydro
245 | WHITNYDM02 | Hydro
247 | BOSQUESW501 | GGT
251 | BOSQUESW803 | CC
253 | BOSQUESW804 | CC
332 | RWMILLER01 | GST
333 | RWMILLER02 | GST
334 | RWMILLER03 | GST
335 | RWMILLER04 | GST
336 | RWMILLER05 | GST
344 | MRSSHPRD | Hydro
345 | MRSSHPRD01 | Hydro
366 | JNSNCNTY802 | Cogen
367 | JNSNCNTY802 | Cogen
503 | NTHTEXAS01 | GST
504 | NTHTEXAS02 | GST
505 | NTHTEXAS03 | GST
580 | JCKCNTY801 | CC
581 | JCKCNTY802 | CC
582 | JCKCNTY803 | CC
728 | WOLFRIDGE801 | Wind
837 | NEWMAN_G5 | GST
842 | OLINGER_G1 | GST
843 | OLINGER_G2 | GST
844 | OLINGER_G3 | GST
845 | OLINGER_G4 | GGT
923 | SPENCER_G4 | GST
924 | SPENCER_G5 | GST
948 | STEAM1 | GST
949 | STEAM2 | GST
950 | STEAM3 | GST
990 | GIBN_CREK_G1 | LIGCO
1002 | PBCTAGE_1G | GGT
1003 | PBCTBGE_2G | GGT
1004 | PBCTCGE_3G | GGT
1005 | PBCTDGE_4G | GGT
1006 | PBCTEGE_5G | GGT
1007 | PB5GEN_6G | GST
1008 | PB6GEN_7G | GST
1037 | MORGAN5G_5G | GST
1039 | MRGNAG_1G | GGT
1040 | MRGNBG_2G | GGT
1041 | MRGNCG_3G | GGT
1042 | MRGNDG_4G | GGT
1043 | MRGNEG_5G | GGT
1044 | MRGNFG_6G | GGT
1045 | CALENG1G_1G | Cogen
1046 | CALENG2G_2G | Cogen
1047 | CALENG3G_3G | Cogen
1049 | ROSCOEWI_5 | Wind
1057 | ROSCOEWI_5 | Wind
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1058 | LONGSHORE_5 | Wind
1060 | ROSCOEWI_5 | Wind
1061 | CIELOGEN_1G | Wind
1062 | CIELOGEN_2G | Wind
1068 | SCURRYCW_1G | Wind
1069 | KINDERMG_1G | Cogen
1070 | KINDERMG_2G | Cogen
1071 | KINDERMG_3G | Cogen
1072 | ROSCOEWI_5 | Wind
1073 | SCURRYCW_2G | Wind
1146 | NOTREES_1G | Wind
1170 | AIRLAMESA_1G | Wind
1301 | BULLCREK_8 | Wind
1302 | COYOTEWG_8 | Wind
1320 | BSP 1 | Cogen
1326 | STANTONW_8 | Wind
1327 | WILDHRSE_1G | Wind
1328 | OCOTILLO_1G | Wind
1333 | MCDDONAL_8 | Wind
1343 | TRENTIPP_8 | Wind
1349 | WESTXWIN_1G | Wind
1350 | NWPWRG1_1G | Wind
1354 | AEPWIND_8 | Wind
1360 | GUNSIGHT_8 | Wind
1416 | SWETWATR_1G | CC
1417 | SWETWATR_2G | CC
1418 | SWETWATR_3G | CC
1419 | SWETWATR_4G | CC
1432 | GRHAMSES_2G | GST
1433 | GRHAMSES_1G | GST
1437 | MESQUITW_1G | Wind
1438 | MESQUITW_2G | Wind
1442 | COKFIELD_5 | Wind
1453 | WCPWRCO_1G | CC
1454 | WCPWRCO_2G | CC
1455 | WCPWRCO_3G | CC
1479 | WFCOGEN_1G | Cogen
1479 | WFCOGEN_1G | Cogen
1482 | WFCOGEN_2G | Cogen
1482 | WFCOGEN_2G | Cogen
1600 | BARTNWND_1G | Wind
1643 | SLSTR1PP_1G | Wind
1675 | PEC_1G | Cogen
1676 | PEC_2G | Cogen
1677 | PEC_3G | Cogen
1678 | LAMARPWR_1G | CC
1679 | LAMARPWR_2G | CC
1680 | LAMARPWR_3G | CC
1681 | LAMARPWR_4G | CC
1682 | LAMARPWR_5G | CC
1683 | LAMARPWR_6G | CC
1687 | VALLEY_1G | GST
1688 | VALLEY_2G | GSC
1689 | VALLEY_3G | GST
1701 | MOSES_1G | LIGCO
1702 | MOSES_2G | LIGCO
1703 | MOSES_3G | LIGCO
1861 | EAGLEMNT_1G | GST
1862 | EAGLEMNT_2G | GST
1863 | EAGLEMNT_3G | GST
1877 | WLFHOLW_1G | CC
1878 | WLFHOLW_2G | CC
1879 | WLFHOLW_3G | CC
1889 | DECRDOVA_1G | GSC
1892 | DECRDOVA_2G | GGT
1893 | DECRDOVA_3G | GGT
1894 | DECRDOVA_4G | GGT
1895 | DECRDOVA_5G | GGT
1898 | COMCHEPK_1G | Nuc
1899 | COMCHEPK_2G | Nuc
1937 | MDLTHELP_5G | CC
1938 | MDLTHELP_6G | CC
1941 | MDLTHELP_1G | CC
1942 | MDLTHELP_2G | CC
1943 | MDLTHELP_3G | CC
1944 | MDLTHELP_4G | CC
1945 | HANDLEY_1G | GST
1946 | HANDLEY_2G | GST
1947 | HANDLEY_3G | GST
1948 | HANDLEY_4G | GST
1949 | HANDLEY_5G | GST
2371 | COLLIN_1G | GST
2381 | NTHLK1_G | GST
2382 | NTHLK2_G | GST
2383 | NTHLK3_G | GST
2413 | MTCK6_G | GST
2414 | MTCK7_G | GST
2417 | MTCK8_G | GSC
2418 | MTCK2_G | GSC
2419 | MTCK3_G | GSC
2451 | LKHB1_G | GST
2452 | LKHB2_G | GST
3097 | MARTLAKE_1G | LIGCO
3098 | MARTLAKE_2G | LIGCO
3099 | MARTLAKE_3G | LIGCO
3107 | STRYKER_1G | GST
3108 | STRYKER_2G | GST
3113 | LUFKINWB_1G | Trash
3126 | TRINIDAD_6G | GST
3348 | CHAMPION_1G | Cogen
3381 | BBRN_1G | LIGCO
3382 | BBRN_2G | LIGCO
3403 | THOUSE_1G | GSC
3404 | THOUSE_2G | GSC
3416 | LAKE_CRK1_G | GST
3417 | LAKE_CRK2_G | GST
3432 | SANDOW_4G | LIGCO
5026 | BRAUNIG_VHB1 | GST
5027 | BRAUNIG_VHB2 | GST
5028 | BRAUNIG_VHB3 | GST
5031 | BRA_VHBCT1 | GST
5032 | BRA_VHBCT2 | GST
5033 | BRA_VHBCT3 | GST
5034 | BRA_VHBCT4 | GST
5111 | CALAVER_JTD1 | LIGCO
5112 | CALAVER_JTD2 | LIGCO
5264 | LEON_LCP3G3 | GST
5265 | LEON_LCP4G4 | GST
5266 | LEON_LCPCT1 | GGT
5267 | LEON_LCPCT2 | GGT
5268 | LEON_LCPCT3 | GGT
5269 | LEON_LCPCT4 | GGT
5396 | CALAVER_OWS1 | GST
5397 | CALAVER_OWS2 | GST
5401 | CALAVER_JKS1 | LIGCO
5436 | TUTTL_WBT1G1 | GST
5438 | TUTTL_WBT3G3 | GST
5439 | TUTTL_WBT4G4 | GST
5476 | BRA_AVR1_CT1 | CC
5477 | BRA_AVR1_ST1 | CC
5478 | BRA_AVR1_CT2 | CC
5503 | RAYBURNGEN3 | GST
5505 | RAYBURNGEN1 | GGT
5506 | RAYBURNGEN2 | GGT
5508 | RAYBURNCC9 | CC
5509 | RAYBURNCC10 | CC
5511 | RAYBURNCC7 | CC
5512 | RAYBURNCC8 | CC
5728 | FALCONHYDRO2 | Hydro
5729 | FALCONHYDRO3 | Hydro
5890 | PEARSALLGEN1 | GST
5891 | PEARSALLGEN2 | GST
5892 | PEARSALLGEN3 | GST
5903 | SANMIGUELGEN | LIGCO
5911 | STP_GN1___1 | Nuc
5912 | STP_GN2___2 | Nuc
5925 | DCEAST | DCTie
5932 | SI_RAY9 | CC
5933 | SI_RAY6 | GST
5934 | SI_RAY5 | GST
5935 | SI_RAY10 | CC
6016 | SWMESA | Wind
6100 | OKLA7A | DCTie
6144 | MCADOO1A | Wind
6407 | TURKTRAK1A | Wind
6637 | SNYDERW1A | Wind
6752 | OKLA0A | LIGCO
6948 | DENISNDM | Hydro
6948 | DENISNDM | Hydro
7000 | L_FERGUS1_1Y | GSC
7004 | L_SIMGID1_1Y | GST
7005 | L_SIMGID1_2Y | GST
7006 | L_SIMGID1_3Y | GST
7007 | L_LOSTPI1_1Y | CC
7008 | L_LOSTPI1_2Y | CC
7009 | L_LOSTPI1_3Y | CC
7010 | L_FPPYD11_1Y | LIGCO
7011 | L_FPPYD11_2Y | LIGCO
7012 | L_FPPYD21_3Y | LIGCO
7014 | L_HAYSEN1_1Y | CC
7015 | L_HAYSEN1_2Y | CC
7016 | L_HAYSEN1_3Y | CC
7017 | L_HAYSEN1_4Y | CC
7020 | L_AUSTPL1_1Y | Hydro
7020 | L_AUSTPL1_1Y | Hydro
7022 | L_BUCHAN1_1Y | Hydro
7023 | L_BUCHAN1_2Y | Hydro
7024 | L_BUCHAN1_3Y | Hydro
7026 | L_INKSDA1_1Y | Hydro
7028 | L_MARBFA1_1Y | Hydro
7029 | L_MARBFA1_2Y | Hydro
7031 | L_MARSFO1G1Y | Hydro
7032 | L_MARSFO1G2Y | Hydro
7033 | L_MARSFO1G3Y | Hydro
7035 | L_WIRTZ_1G1Y | Hydro
7036 | L_WIRTZ_1G2Y | Hydro
7038 | L_DELAWA1_1Y | Wind
7038 | L_DELAWA1_1Y | Wind
7303 | L_WPPGS12_1Y | GGT
7303 | L_WPPGS12_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7305 | L_WPPGS34_1Y | GGT
7487 | L_CANYHY8_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7605 | L_MCQUEE9_1Y | Hydro
7609 | L_SCHUMA8_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7624 | L_LAKEWO9_1Y | Hydro
7800 | L_GUADGE1_1Y | CC
7801 | L_GUADGE1_2Y | CC
7802 | L_GUADGE1_3Y | CC
7803 | L_GUADGE1_4Y | CC
7804 | L_GUADGE1_5Y | CC
7805 | L_GUADGE1_6Y | CC
7807 | L_BASTEN1_1Y | CC
7808 | L_BASTEN1_2Y | CC
7809 | L_BASTEN1_3Y | CC
7810 | L_RIONOG1G1Y | CC
7811 | L_RIONOG1G2Y | CC
7812 | L_RIONOG1G3Y | CC
7813 | L_RIONOG1S1Y | CC
8032 | AMISTADHYD1 | Hydro
8033 | AMISTADHYD2 | Hydro
8048 | FALCONHYDRO1 | Hydro
8066 | DUP1V#1 | Cogen
8134 | FOR #1 | Cogen
8138 | FOR #2 | Cogen
8139 | JOS #1 | GST
8147 | UCAR #2 | Cogen
8148 | UCAR #1 | Cogen
8153 | FOR #3 | Cogen
8154 | FOR #4 | Cogen
8155 | FOR #5 | Cogen
8156 | FOR #6 | Cogen
8157 | FOR #7 | Cogen
8161 | COLETO0A | LIGCO
8173 | VICEC51A | CC
8174 | VICEC61A | CC
8189 | CUECPL2A | Cogen
8262 | ELPS | Hydro
8285 | LAR #1 | GST
8287 | LAR #2 | GST
8288 | LAR #3 | GST
8388 | BATES0A | GST
8393 | BATES0B | GST
8437 | NUECES_B0C | GST
8438 | NUECES_B0B | GST
8442 | NUECES_B0A | GST
8456 | COSW#1 | Cogen
8457 | COSW#2 | Cogen
8459 | B_DAVIS0B | GSC
8460 | B_DAVIS0A | GSC
8461 | KOCH_UP0A | Cogen
8506 | VAL #1 | Cogen
8507 | VAL #2 | Cogen
8511 | OXY_CC0A | Cogen
8517 | CELANEBI0A | Cogen
8560 | CNOPGT1 | Cogen
8561 | CNOPGT2 | Cogen
8562 | CNOPST1 | Cogen
8926 | LGE_GT10A | Cogen
8927 | LGE_GT20A | Cogen
8928 | LGE_STG0A | Cogen
8930 | ICPGN10A | Cogen
8931 | ICPGN20A | Cogen
8932 | ICPGN30A | Cogen
8933 | FGNTS001 | CC
8934 | FGNTS101 | CC
8935 | FGNTS201 | CC
8936 | MVGN#1 | CC
8937 | MVGN#2 | CC
8938 | MVGN#3 | CC
8981 | HECN1 | CC
8982 | HECN2 | CC
8983 | HECN3 | CC
9000 | DECKR_G1 | GST
9001 | DECKR_G2 | GST
9002 | DECKR_G3 | GGT
9003 | DECKR_G4 | GGT
9004 | DECKR_G5 | GGT
9005 | DECKR_G6 | GGT
9016 | SANDH_G1 | GGT
9017 | SANDH_G2 | GGT
9018 | SANDH_G3 | GGT
9019 | SANDH_G4 | GGT
9020 | SANDHG5A | CC
9021 | SANDHG5C | CC
11001 | NAV1CT | CC
11009 | NAV2CT | CC
11011 | NAV3ST | CC
11012 | NAV4CT | CC
11013 | NAV5CT | CC
11014 | NAV6ST | CC
11020 | TIEHVSG_1G | CC
11021 | TIEHVCG_1G | CC
11022 | TIEHVCG_2G | CC
11023 | TIEHVCG_3G | CC
11024 | TIEHVCG_4G | CC
11025 | TIEHVSG_2G | CC
11691 | KMICHICT1_G | CC
11692 | KMICHICT2_G | CC
11693 | KMICHIST3_G | CC
11694 | KMICHICT4_G | CC
11695 | KMICHICT5_G | CC
11696 | KMICHIST6_G | CC
12322 | ENNSTRAC_1G | CC
12323 | ENNSTRAC_2G | CC
12411 | FPLEFR1A_G | CC
12412 | FPLEFR1B_G | CC
12413 | FPLEFR1C_G | CC
12414 | FPLEFR1S_G | CC
12421 | FPLEFR2A_G | CC
12422 | FPLEFR2B_G | CC
12423 | FPLEFR2C_G | CC
12424 | FPLEFR2S_G | CC
12440 | PARKD_1SVC8 | GST
12449 | PARKD_2SVC8 | GST
13116 | TGATEWAY_1G | CC
13117 | TGATEWAY_2G | CC
13118 | TGATEWAY_3G | CC
13119 | TGATEWAY_4G | CC
13131 | CALFREST_1G | CC
13132 | CALFREST_2G | CC
13133 | CALFREST_3G | CC
13134 | CALFREST_4G | CC
13135 | CALFREST_5G | CC
13136 | CALFREST_6G | CC
13432 | SANDOW_5G | LIGCO
32798 | BRYN_TAMUGEN | GST
32883 | BRYN_DNSBY3 | GST
32884 | BRYN_DNSBY13 | GST
32886 | BRYN_ATKINS3 | GST
32887 | BRYN_ATKINS6 | GST
32888 | BRYN_ATKINS7 | GGT
32890 | BRYN_ATKINS4 | GST
32891 | BRYN_ATKINS5 | GST
32892 | BRYN_DNSBY14 | GST
36998 | RDCNYNG1 | Wind
38332 | TNWDWRDU2_8 | Wind
38437 | TNSRBNMESA9 | Wind
38580 | TNBP_CGN1_8 | Cogen
38590 | TNBP_CGN2_8 | Cogen
38600 | TNBP_CGN3_8 | Cogen
38611 | TNBPAMCG1_8 | Cogen
38612 | TNBPAMCG2_8 | Cogen
38613 | TNBPAMCG3_8 | Cogen
38614 | TNBPAMCG4_8 | Cogen
38615 | TNBPAMCG5_8 | Cogen
38690 | TNBP_CGN4_8 | Cogen
38711 | TNTXCTY1CG8 | Cogen
38712 | TNTXCTY2CG8 | Cogen
38713 | TNTXCTY3CG8 | Cogen
38714 | TNTXCTY4CG8 | Cogen
39190 | TNSLCGN1__8 | Cogen
39470 | TNDOWCGNSG8 | Cogen
39480 | TNDOWCGNGG8 | Cogen
39760 | TNSCLP1___8 | Cogen
39770 | TNSCLP2___8 | Cogen
39775 | TNSCLP4___8 | Cogen
39790 | TNSCLP3___8 | Cogen
39960 | TNTNPONE_18 | LIGCO
39970 | TNTNPONE_28 | LIGCO
48500 | APD_GT1_8005 | Cogen
48510 | AK_GT1__8040 | Cogen
48511 | LPE_GT1_8070 | GGT
48512 | LPE_GT2_8075 | GGT
48513 | LPE_GT3_8080 | GGT
48514 | LPE_GT4_8085 | GGT
48520 | BSF_GT1_8070 | Cogen
48520 | BSF_GT1_8070 | Cogen
48521 | BVE_GT1_GT1 | CC
48522 | BVE_GT2_5035 | CC
48523 | BVE_ST1_GN1 | CC
48531 | BYU_GT1_8075 | Cogen
48532 | BYU_GT2_8055 | Cogen
48533 | BYU_GT3_8060 | Cogen
48534 | BYU_GT4_8065 | Cogen
48551 | CAL_GT1_8045 | Cogen
48552 | CAL_ST1_8000 | Cogen
48561 | CTL_GT2_8130 | Cogen
48562 | CTL_GT3_8135 | Cogen
48563 | CTL_GT4_8140 | Cogen
48564 | CTL_GN1_8145 | Cogen
48565 | CTL_GN2_8155 | Cogen
48581 | CBY_GN1_1 | GSC
48582 | CBY_GN2_2 | GSC
48583 | CBY_GT4_1 | GSC
48584 | CBY_GT4_2 | CC
48585 | CBY_ST4_1 | CC
48591 | CHE_GT2_5030 | Cogen
48593 | CHE_GT1_8015 | Cogen
48594 | CHE_GN4_8025 | Cogen
48595 | BTE_GT2_8075 | CC
48596 | BTE_GT3_8045 | CC
48597 | BTE_GT4_8055 | CC
48598 | BTE_ST1_8070 | CC
48611 | DIB_GT1_8080 | Cogen
48612 | DIB_GT2_8075 | Cogen
48613 | DIB_ST1_8085 | Cogen
48614 | DIB_GT3_8090 | Cogen
48641 | DPEC_GT15040 | CC
48642 | DPEC_GT25025 | CC
48643 | DPEC_GT35010 | CC
48644 | DPEC_GT45070 | CC
48645 | DPEC_ST55065 | CC
48651 | EP_1_2 | Cogen
48651 | EP_1_2 | Cogen
48671 | FTR_GT1_5105 | CC
48672 | FTR_GT2_5110 | CC
48673 | FTR_GT3_5085 | CC
48674 | FTR_CN4_5095 | CC
48690 | GBY_GN5_5 | GSC
48691 | GBY_73741085 | GGT
48691 | GBY_73741085 | GGT
48692 | GBY_81821075 | GGT
48692 | GBY_81821075 | GGT
48693 | GBY_83841065 | GGT
48693 | GBY_83841065 | GGT
48721 | LEG_1___1 | LIGCO
48722 | LEG_2___2 | LIGCO
48730 | MNS_GT | Cogen
48731 | CBE_GT1 | CC
48732 | CBE_GT2 | CC
48733 | CBE_ST12 | CC
48734 | CBE_GT3 | CC
48735 | CBE_GT4 | CC
48736 | CBE_ST34 | CC
48740 | PSG_GN2_8050 | Cogen
48741 | PSG_GT2_8040 | Cogen
48742 | PSG_GT3_8060 | Cogen
48761 | PR_GT1__9040 | Cogen
48772 | PHR_GN2_2 | GSC
48791 | PSA_GT1_8160 | Cogen
48792 | PSA_GT2_8155 | Cogen
48793 | PSA_GT3_8150 | Cogen
48794 | PSA_GT4_8145 | Cogen
48795 | PSA_GT5_8140 | Cogen
48796 | PSA_GN1_8165 | Cogen
48797 | PSA_GT6_8135 | Cogen
48811 | CVC_GT3_5045 | Cogen
48812 | CVC_GT2_5020 | Cogen
48813 | CVC_GT1_5035 | Cogen
48814 | CVC_ST5_5040 | Cogen
48815 | CVC_GT4_8005 | Cogen
48820 | SHELLG1_3015 | Cogen
48821 | SHELLG2 | Cogen
48822 | SHELLG3_3020 | Cogen
48822 | SHELLG3_3020 | Cogen
48841 | SJS_GT1_GT1 | Cogen
48842 | SJS_GT2_GT2 | Cogen
48845 | SOL_GT1 | Solar
48851 | SRB_GN1_1 | GST
48852 | SRB_GN2_2 | GST
48853 | SRB_GN3_3 | GST
48854 | SRB_GN4_4 | GST
48855 | SRB_GT211035 | GGT
48855 | SRB_GT211035 | GGT
48873 | THW_ST3_ST_3 | CC
48874 | THW_ST4_ST_4 | CC
48875 | THW_3132 | CC
48875 | THW_3132 | CC
48877 | THW_3334 | CC
48877 | THW_3334 | CC
48879 | THW_4142 | CC
48879 | THW_4142 | CC
48881 | THW_4344 | CC
48881 | THW_4344 | CC
48883 | THW_GT1_GT_1 | GGT
48885 | THW_5152 | GGT
48885 | THW_5152 | GGT
48886 | THW_5354 | GGT
48886 | THW_5354 | GGT
48887 | THW_5556 | GGT
48887 | THW_5556 | GGT
48911 | TGF_GT1_8000 | Cogen
48921 | WAP_GN1_1 | GST
48922 | WAP_GN2_2 | GST
48923 | WAP_GN3_3 | GST
48924 | WAP_GN4_4 | GSC
48925 | WAP_GN5_5 | LIGCO
48926 | WAP_GN6_6 | LIGCO
48927 | WAP_GN7_7 | LIGCO
48928 | WAP_GN8_8 | LIGCO
48929 | WAPGT21_GT1 | GGT
49803 | EXN_15GT | Cogen
49804 | EXN_16GT | Cogen
49805 | EXN_17GT | Cogen
49826 | EXN938GT | Cogen
49828 | EXN941GT | Cogen
49829 | EXN942GT | Cogen
49830 | EXN943GT | Cogen
49831 | EXN944GT | Cogen
49832 | EXN945GT | Cogen
49837 | EXN_GT | Cogen
49838 | EXN_14GT | Cogen
49851 | DOW17000 | Cogen
49858 | DOW38100 | Cogen
49859 | DOW38200 | Cogen
49860 | DOW38300 | Cogen
49862 | DOW39100 | Cogen
49863 | DOW39200 | Cogen
49865 | DOW41000 | Cogen
49866 | DOW42000 | Cogen
49869 | DOW49000 | Cogen
49870 | DOW61000 | Cogen
49871 | DOW62000 | Cogen
49872 | DOW63000 | Cogen
49873 | DOW64000 | Cogen
49876 | DOW65000 | Cogen
49877 | DOW66000 | Cogen
49878 | DOW67000 | Cogen
49882 | DOW81000 | Cogen
49884 | DOW82000 | Cogen
49885 | DOW83000 | Cogen
49886 | DOW84000 | Cogen
60000 | DSKY2 | Wind
60003 | KING_NE1A | Wind
60005 | KING_SE1A | Wind
60007 | KING_SW1A | Wind
60016 | WOODWRD11A | Wind
60017 | ORNNWP1 | Wind
60018 | DSKY1 | Wind
60019 | KING_NW1A | Wind
60052 | WILDHRS11A | Wind
60053 | WILDHRS21A | Wind
60057 | CALLAHAN1A | Wind
60058 | BUFF_GAP1A | Wind
60060 | CIRELLO | Wind
60063 | BUFF_GAP1B | Wind
60066 | H_HOLLOW1A | Wind
60068 | HHOLLOW21A | Wind
60070 | HHOLLOW31A | Wind
60072 | HHOLLOW41A | Wind
60081 | WHRLWIND1A | Wind
60201 | RIO DRCS | AVR
60202 | FRNDDRCS | AVR
71051 | L_BITTCR1_1N | Wind
71054 | L_SWEETW1_1N | Wind
71057 | L_SWEETW1_2N | Wind
71059 | L_SWEETW1_3N | Wind
71060 | L_SWEETW1_4N | Wind
76031 | L_GASCCR1_1N | Wind
76091 | L_DIVIDE1_1N | Wind
80003 | MILHWYS | AVR
80010 | EPLVT1 | AVR
80012 | LAR | DCTie
80051 | FOR #8 | Cogen
80052 | FOR #9 | Cogen
80053 | FOR #10 | Cogen
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80080 | GWINDT11A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80081 | GWINDT21A | Wind
80137 | CSDR89 | DCTie
80137 | CSDR89 | DCTie
80138 | CSDR7 | DCTie
80139 | CSDR56 | DCTie
80139 | CSDR56 | DCTie
80140 | CSDR11 | DCTie
80180 | PNSCALT11A | Wind
80180 | PNSCALT11A | Wind
80181 | PNSCALT21A | Wind
80181 | PNSCALT21A | Wind
80223 | REYSHR G | Cogen
80224 | VISTRONG1 | Cogen
80225 | VISTRONG2 | Cogen
80226 | ALCOA G | Cogen
80227 | AIRCO G | Cogen
80265 | LARECU40A | GGT
80266 | LARECU50A | GGT
88198 | BEEVILLE | AVR
88253 | HAMILTON | BLT
88299 | ZAPATA | BLT
88508 | FALFURRI | AVR