| PRR Number |  | PRR Title | Primary Frequency Response from WGRs |
| --- | --- | --- | --- |
| Date Posted |  |  |  |
| Protocol Sections Requiring Revision |  | 2.1, Definitions 5.9.1.1, Governor in Service 5.9.1.3, Wind-powered Generation Resource (WGR) Primary Frequency Response (new) |  |
| Requested Resolution |  | Normal |  |
| Revision Description |  | This Protocol Revision Request (PRR) adds a requirement for wind generator control systems to be programmed to respond to frequency deviations by controlling Wind-powered Generation Resource (WGR) real power output in a way that is similar to governor response for conventional generators |  |
| Reason for Revision |  | As WGRs displace more and more conventional generation, there will be a growing need for WGRs to replace the primary frequency response capability not being provided by the Off-line conventional generators. WGR primary frequency response shall be of particular value if frequency increases occur. |  |
| Overall Market Benefit |  | Maintain system frequency better with additional wind generation in ERCOT which shall allow greater utilization of wind generation. |  |
| Overall Market Impact |  | Additional costs for hardware and software for WGRs as well as some limits on WGR technology which may be utilized; thus increasing capital costs of WGRs. Some reduction in individual WGR output as wind is “spilled” whenever frequency increases above the dead-band. Significant reduction in production costs since more wind generation can be allowed on the ERCOT System. |  |
| Consumer Impact |  | Reduced fuel costs. |  |
| Credit Implications (Yes or No, and summary of impact) |  | Unknown |  |
| Relevance to Nodal Market (Yes or No, and summary of impact) |  | Yes, applicable to Nodal also. |  |
| Nodal Protocol Sections Requiring Revision |  | 2.1, Definitions 8.5.1.1, Governor in Service 8.5.3, Title (new) |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | WGR software and hardware. | Less than $500,000 per new WGR |
|  | 2 | Lost production due to high frequency. | $1,000,000 to $100,000,000 plus, depending on implementation settings |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Provides automatic response to frequency, primarily to high frequency excursions, in addition to the response from conventional generation units. Should help avoid excessive frequency excursions. | Monetary impact of frequency excursions is difficult to estimate |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Ken Donohoo on behalf of the Reliability and Operations Subcommittee (ROS) |
| E-mail Address |  |
| Company |  |
| Phone Number |  |
| Cell Number |  |
| Market Segment |  |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

Proposed Protocol Language Revision

2.1	Definitions

Primary Frequency Response

The automatic and naturally occurring responses to system frequency deviations provided by turbine governors and Loads within the first few seconds of a reportable frequency event.

5.9.1.1	Governor in Service

At all times a Generation Resource is On-line its turbine governor shall remain in service and be allowed to respond to all changes in system frequency.  Generation Entities shall not reduce governor response on individual Resources during abnormal conditions without ERCOT’s consent (conveyed by way of the Generation Entity’s Qualified Scheduling Entity (QSE)) unless equipment damage is imminent. All generators that have capacity available to either increase output or decrease output in Real Time must provide governor response which may make use of that available capacity.  Only Generation Resources providing Regulation Service Up (RGSU), Regulation Service Down (RGSD), and Responsive Reserve Service, as specified in Protocol Section 6.5 Ancillary Services Selection and Requirements, shall be required to reserve capacity that may also be used to provide governor response.

If a Generation Resource trips Off-line due to governor response problems, the Generation Entity shall immediately report the change in the status of the Resource to ERCOT and the QSE.

5.9.1.3		Wind-powered Generation Resource (WGR) Primary Frequency Response

WGRs with Generation Interconnect Agreements signed after December 1, 2009 shall provide an immediate real power primary frequency response, proportional to frequency deviations from 60 Hz, similar to governor response.  The WGR automatic control system design shall have an adjustable dead band that can be set as specified in the ERCOT Operating Guides.  The rate of real power response to frequency deviations shall be similar to or more responsive than the droop characteristic of 5% used by conventional generators.  For WGRs with Generation Interconnect Agreements executed prior to December 1, 2009, those not already equipped with proportional primary frequency response shall by December 1, 2011 acquire that capability.  Those WGRs that cannot technically be retrofitted with proportional primary frequency response capability shall submit an attestation to ERCOT, within 90 Business Days of the effective date of this PRR, explaining the technical infeasibility.  At ERCOT’s sole discretion, those WGRs for whom proportional primary frequency response is technically infeasible may be granted a permanent exemption from the requirement.  ERCOT shall make a determination within 180 Business Days.  If ERCOT does not grant an exemption, the WGR shall acquire the capability to provide proportional primary frequency response within twenty four (24) months of being notified of that determination.