## Slide 1: Primary Frequency Response – draft PRR – for ROS, July 2009
The Wind Operations Task Force presents this draft PRR for ROS’ consideration and vote.
New def: Primary Frequency Response = “The automatic and naturally occurring responses to system frequency deviations provided by turbine governors and Loads within the first few seconds of a reportable frequency event.”
This PRR requires all generators that have capacity available must provide governor response.
This PRR requires new WGRs (signed IA after 12/1) to provide primary frequency response, similar to 5% droop.
Nonconsensus issue: Retrofitting older WGRs (see yellow highlight on page 3) – whether to tackle this now or later. Technical infeasibility exception allowed.