# 2010 CSC Study

Version 0.3

Document Revisions

| Date | Version | Description | Author(s) |
| --- | --- | --- | --- |
| 07/16/2009 | 0.1 | First draft | Chris Ngai |
| 07/17/2009 | 0.2 | Formatted and added congestion data. | Isabel Flores |
| 07/20/2009 | 0.3 | Corrections to Section 3 & updated table of contents | Isabel Flores |

Table of Contents

2010 CSC Study	1

2010 CSC Analysis	1

1.	Background	1

2.	2010 Significant Changes to the ERCOT Grid	1

3.	Transfer Study	2

4.	Evaluation of Current Congestion Events	3

5.	Projection of Future Congestion	5

6.	Cluster Analysis	6

6.1.	Scenario 1a	8

6.2.	Scenario 1b	9

6.3.	Scenario 2a	10

6.4.	Scenario 2b	11

6.5.	Scenario 3a	12

6.6.	Scenario 3b	13

6.7.	Scenario 4	14

6.8.	Scenario 5	15

6.9.	Scenario 7	16

6.10.	Scenario 8	17

6.11.	Scenario 9	18

6.12.	Scenario 10	19

6.13.	Scenario 11	20

# 2010 CSC Analysis

# Background

Protocol Section 7.2.1 requires ERCOT Staff to conduct an annual analysis to determine the upcoming year’s Commercially Significant Constraints (CSCs).  This analysis may include a transfer study, an evaluation of past congestion costs, and a projection of congestion costs for the upcoming year; ERCOT’s analysis includes all of these features.

# 2010 Significant Changes to the ERCOT Grid

Per the May 2009 TPIT, these are the significant transmission projects scheduled to go in-service by the end of 2010:

- Hutto Switch and 345/138 kV autotransformer (June 2010)

- Sandow Switch - Sandow Third 138 kV line (May 2010)

- Sandow Switch Third 345/138 kV autotransformer (May 2010)

- Anderson to Westover Hills - New 138kV Transmission Line (June 2010)

- Sandow Switch - Elgin Switch 138 kV line (Oct 2010)

- Decker to Techridge 138kV Circuit Relocation (Nov 2010)

- Rothwood 345/138 kV substation (May 2010)

Generation projects scheduled to go in-service:

2010

- BM Davis Repower Project (March 2010)

- JK Spruce 2 (June 2010)

- Jack County 2 (May 2010)

- Formosa #11 (December 2010)

- Formosa #12 (December 2010)

2009

- Nueces Bay Repower Project (November 2009)

- Pearsall (August 2009)

- TECO-Central (April 2009)

- Nacogdoches (September 2009)

- Lufkin (September 2009)

- Dansby 3 (2009)

Wind

| (MWs) | 2009 | 2010 |
| --- | --- | --- |
| West | 8339.2 | 8339.2 |
| North | 693.5 | 693.5 |
| South | 773 | 871 |

Generation being suspended after September 2009:

| Name | MW | Bus |
| --- | --- | --- |
| Tradinghouse Unit 1 | 563 | 3403 |
| Morgan Creek Unit 5 | 137 | 1037 |
| Sweetwater Cogen Unit 1 | 30 | 1416 |
| Sweetwater CT1 | 72 | 1417 |
| Sweetwater CT2 | 68 | 1418 |
| Sweetwater CT3 | 61 | 1419 |
| North Lake 1 | 156 | 2381 |
| North Lake 2 | 181 | 2382 |
| North Lake 3 | 329 | 2383 |
| Decordova SES Unit 1 | 779 | 1889 |
| Lake Creek SES Unit 1 | 75 | 3416 |
| Lake Creek SES Unit 2 | 222 | 3417 |

# Transfer Study

The Steady State Working Group (SSWG) 2009 Data Set A 2010 summer peak base case was used for the transfer analysis.  A congestion management (CM) zone to CM zone transfer analysis was performed by mapping all generators to their respective 2009 CM zones.  New generation units were mapped to their assumed CM zone.

Transfer analysis was performed for the following zone to zone generation transfers:

- West to North

- South to North

- North to South

- North to Houston

- North to West

- West to South

The results of the transfer studies are presented in the attached spreadsheet:

# Evaluation of Current Congestion Events

The tables (Table 1a-e) below contain estimated of costs for inter-zonal congestion assigned to contingency and overloaded elements based on those identified when determining CSC limits during real-time operations:

North to South (Table 1a)

| Contingency | Overloaded Element | Cost |
| --- | --- | --- |
| Temple Pecan Creek - Trading house SES & Temple Switch – Lake Creek SES 345 kV | Waco Atco-Waco Woodway | $ 53,046,567 |
| Temple Pecan Creek - Trading house SES & Temple Switch – Lake Creek SES 345 kV | Goldwaithe - Evant | $ 2,808,480 |
| Temple Pecan Creek - Trading house SES & Temple Switch – Lake Creek SES 345 kV | Waco Atco-Cotton Belt | $ 173,144 |
| Lake Creek SES-Temple Switch 345kV | Temple Pecan Crk-Tradinghouse 345kV | $ 120,326 |
| Temple Pecan Creek - Trading house SES & Temple Switch – Lake Creek SES 345 kV | Temple-Temple Pecan Crk | $ 16,590 |

South to North (Table 1b)

| Contingency | Overloaded Element | Cost |
| --- | --- | --- |
| Temple Switch-Sandow Switch 345kV | Austrop – Sandow Switch 345kV | ($ 7,675,044) |

West to North (Table 1c)

| Contingency | Overloaded Element | Cost |
| --- | --- | --- |
| Stability Limit |  | $ 2,227,059 |
| Graham-Long Creek | Murray - Paint Creek 138kV | $ 957,333 |

Note: Out of 2,403 binding intervals for the West to North CSC 2,032 have been due to the Stability Limit.

North to West (Table 1d)

| Contingency | Overloaded Element | Cost |
| --- | --- | --- |
| DCKT Long Creek – Sweetwater Cogen & Abilene Mulberry Creek 345 kV | Murray – Paint Creek 138kV | $ 986,176 |

North to Houston (Table 1e)

| Contingency | Overloaded Element | Cost |
| --- | --- | --- |
| Roans Prairie-King & Singleton-Tomball345kV | Singleton-TH Wharton345kV | $ 1,376,793 |
| THWharton-Jewett & Obrien - Gibbons Creek 345kV | Voltage (VSAT) | $ 1,104,756 |
| DCKT Gibbons Creek – O’Brien & Singleton – TH Wharton 345kV | Peters – Flewellen 138kV | $ 793,935 |
| TH Wharton-Singleton & Jewett-Singleton 345kV | Peters – Flewellen 138kV | $ 456,052 |
| Singleton – O'brien 345kV | Voltage (VSAT) | $ 239,267 |
| O’Brien – Singleton 345kV | Jewett-Singleton 345kV | $ 49,113 |
| O’Brien-THWharton345kV | Singleton-TH Wharton345kV | $ 19,693 |
| Gibbons Creek – Singleton 345kV | Jewett-Singleton 345kV | $ 2,935 |

Recurring Congestion - days

Table 2 shows recurring congestion in days for the January through June timeframe these are the top congested contingency and overloaded element pairs observed during real-time:

| Contingency | Overloaded Element | Total |
| --- | --- | --- |
| Aspermont - Spur 138KV | Jayton - Spur 69 kV | 61 |
| San Miguel - Dilley Switch 138KV | Derby – Pearsall 69KV | 50 |
| Abilene South - Eskota 138KV | Trent - Merkel 69KV | 43 |
| Comanche Peak SES - Decordova SES & Wolf Hollow - Rocky Creek 345KV | Concord 345/138KV autotransformer | 39 |
| Santa Anna - Ballinger 138KV | Ballinger - Humble 69KV | 34 |
| Oasis - PH Robinson 345KV | Garrott - Midtown 138KV | 26 |
| Basecase | Menard – San Angelo Power Station 138 kV | 25 |
| Dilley Switch - North Laredo 138KV | North Laredo - Asherton 138KV | 25 |
| Aspermont - Spur 138KV | Spur 138/69KV autotransformer | 21 |
| Menard - Gillespie 138KV | Menard 138/69KV autotransformer | 19 |
| Aspermont - Spur 138KV | Matador – Paducah 69KV | 18 |
| Abilene South - Eskota Switch 138KV | Eskota Switch 138/69KV autotransformer | 17 |

Table 2: Counts provided are for the number of days these pairs appeared as congested.

For local congestion incurred during the period February through June, 2008, these are the top congested contingency and overload element pairs thus far:

| Contingency | Overloaded Element | Cost |
| --- | --- | --- |
| Base-case; Graham SES-Long Creek 345kV Sandow Switch-Austrop 345kV | SAPS - Menard 138kV | $ 12,006,612 |
| Ballinger - Santa Anna 138kV | Ballinger - Humble 69kV | $ 8,513,994 |
| Valley Import |  | $ 5,101,300 |
|  | Capacity Shortage | $ 4,158,447 |
| Comanche Peak SES - DeCordova SES & Wolf Hollow - Rocky Creek 345kV | Concord 345/138kV Autotransformer | $ 3,968,846 |
| Menard - Gillespie 138kV | Menard Auto | $ 3,620,392 |
| Watermill - DeSoto Switch - Cedar Hill Switch 345kV | Watermill - DeSoto | $ 3,549,488 |
| Comanche Peak SES - DeCordova SES & Wolf Hollow - Rocky Creek 345kV | Venus Switch - Comanche Peak 345kV | $ 3,515,768 |
| Skyline to Marion & Elm Creek 345 | Marion - Hill Country 345kV | $ 3,159,056 |
| Ballinger - San Angelo Red Creek 138kV | Miles - Rowena 69kV | $ 3,074,447 |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Long Creek SES | San Angelo Power Station -Shrew Tap | $ 2,923,976 |
| Watermill - West Levee SW & Sargent Road | Watermill - DeSoto | $ 1,832,359 |
| Area Security - Valley |  | $ 1,718,466 |
| Comanche Peak SES-DeCordova SES & Wolf Hollow-Rocky Creek 345kV | Comanche Peak SES - Parker Switch 345KV | $ 1,652,826 |
| Comanche Peak SES-DeCordova SES-Wolf Hollow 345kV | Parker Switch - Benbrook Switch 345KV | $ 1,160,067 |
| Lon Hill - Coleto Creek 345kV | Warburton - Victoria 138kV | $ 1,098,875 |
| Lytton S/HC Tap | Austrop outage | $ 948,231 |
| Watermill Swithch - DeSoto Switch-Cedar Hill Switch | West Levee Auto #5 | $ 914,588 |
| Austrop - Lost Pines 345kV | Winchester - Fayetteville 138kV | $ 895,574 |
| Oklaunion - Fisher Road - Bowman 345kV | Vernon - Grayback 69kV | $ 891,532 |
| Roanoke Switch - West Denton & Lewisville Switch 345kV | West Denton - Airport 138kV | $ 872,109 |
| Austrop 345/138kV Autotransformer T1/T2 | Austrop 345/138kV Autotransformer T2/T1 | $ 861,714 |
| Tradinghouse - Venus Switch 345kV | Rogers Hill - Elm Mott 138kV | $ 839,174 |

Table 3: Dollars shown are estimates and not Settlement quality.  Local congestion costs have totaled an estimated $100 million for January through June; the element pairs shown above represent 67% of the total estimated costs.

# Projection of Future Congestion

The attached spreadsheet contains the 2010 annual congestion report from the latest Medium Term PASA report.  The elements are sorted based on shadow price.

# Cluster Analysis

All clustering analyses were performed using the 2010 Data Set A Summer peak case.  A summary of the scenarios follows.  In all scenarios Horse Hollow has clustered in the South zone.

| Scenario | W_N & N_W | N_S & S_N | N_H | Zones | Notes |
| --- | --- | --- | --- | --- | --- |
| 1a | Sweetwater-Long Creek/ Abilene Mulberry Creek-Long Creek 345-kV dckt | Lake Creek-Temple/ Tradinghouse-Temple Pecan Creek 345-kV dckt | Singleton-Obrien/ Singleton-TH Wharton 345-kV dckt | 4 | Pre-contingency |
| 1b | same as 1a | same as 1a | same as 1a | 4 | Post-contingency |
| 2a | same as 1a | same as 1a | same as 1a | 3 | Pre-contingency |
| 2b | same as 1a | same as 1a | same as 1a | 3 | Post-contingency |
| 3a | same as 1a | same as 1a | same as 1a | 5 | Pre-contingency |
| 3b | same as 1a | same as 1a | same as 1a | 5 | Post-contingency |
| 4 | Graham-Long Creek/ Graham-Cook Field Road 345-kV dckt | same as 1a | same as 1a | 4 | Pre-contingency |
| 5 | same as 1a | same as 1a | same as 1a | 4 | W-S: SAPS-Menard & Brownwood-Goldthwaite |
| 6 | Graham-Long Creek/ Graham-Cook Field Road 345-kV dckt; removes N_W | same as 1a for N_S; removes S_N | same as 1a | 4 | Pre-contingency; the clustering result is the same as Scenario 4, therefore, the diagram has been omitted. |
| 7 | Graham-Long Creek/ Graham-Cook Field Road 345-kV dckt |  |  | 4 | W-S: SAPS-Menard & Brownwood-Goldthwaite Exclude: S_N & N_W |
| 8 | Stability Limit monitored lines; N_W removed | same as 1a | same as 1a | 4 | W-S: SAPS-Menard & Brownwood-Goldthwaite Exclude: N_W |
| 9 | Stability Limit monitored lines; N_W removed | same as 1a | same as 1a | 4 | W-S: SAPS-Menard & Brownwood-Goldthwaite |
| 10 | Graham-Long Creek/ Graham-Cook Field Road 345-kV dckt; removes N_W | same as 1a | same as 1a | 4 | W-S: SAPS-Menard Exclude: N_W |
| 11 | Graham to Parker and Graham to Benbrook 345-kV dckt | same as 1a | same as 1a | 4 |  |

## Scenario 1a

Scenario 1a was clustered using the pre-contingency 2010 DSA SUM1 base case.  The 2009 CSCs were used and the model was clustered into four zones.

## Scenario 1b

Scenario 1b was clustered using the post-contingency (Fisher to Bowman 345kV line) 2010 DSA SUM1 base case.  The 2009 CSCs were used and the model was clustered into four zones.

## Scenario 2a

Scenario 2a was clustered using the pre-contingency 2010 DSA SUM1 base case.  The 2009 CSCs were used with the exception the model was clustered into three zones; the Houston zone merges with the South zone.

## Scenario 2b

Scenario 2b was clustered using the post-contingency (Fisher to Bowman 345kV line) 2010 DSA SUM1 base case.  The 2009 CSCs were used with the exception the model was clustered into three zones; Houston combines with the South zone.

## Scenario 3a

Scenario 3a was clustered using the pre-contingency 2010 DSA SUM1 base case.  The 2009 CSCs were used with the exception the model was clustered into five zones.

## Scenario 3b

Scenario 3b was clustered using the post-contingency 2010 DSA SUM1 base case.  The 2009 CSCs were used with the exception the model was clustered into five zones.

## Scenario 4

Scenario 4a was clustered using the pre-contingency 2010 DSA SUM1 base case.  The 2009 CSCs for N_S, S_N, and N_H, were used; the W-N and N-W CSCs were defined as Graham to Long Creek and Graham to Cook Field.  The model was clustered into four zones.  .

## Scenario 5

Scenario 5 was clustered using the pre-contingency 2010 DSA SUM1 base case.  The 2009 CSCs were used and the model was clustered into four zones.  The W-S CSC was added and defined as SAPS to Menard and Brownwood to Goldthwaite in this scenario.

## Scenario 7

Scenario 7 was clustered using the pre-contingency 2010 DSA SUM1 base case.  The 2009 CSCs were used for N_S and N_H; W_N was defined as Graham to Long Creek and Graham to Cook Field.  S_N and N_W were removed; a W-S CSC was added with SAPS-Menard and Brownwood-Goldthwaite as the CSC.  The model was clustered into four zones.

## Scenario 8

Scenario 8 was clustered using the pre-contingency 2010 DSA SUM1 base case.  The model was clustered into four zones.  The 2009 CSCs were used for N_S, S_N, and N_H; the N_W CSC was removed.  The W_N CSC was defined using the Stability Limit monitored lines which are:

- Graham – Cook Field

- Jacksboro – Bowman

- Graham – Tonkawa

- Bowman – Graham

- Comanche Switch – Red Creek

- Graham – Long Creek

## Scenario 9

Scenario 9 was clustered using the pre-contingency 2010 DSA SUM1 base case.  The model was clustered into four zones.  The 2009 CSCs were used for N_S, S_N, and N_H; the N_W CSC was removed.  The W_N CSC was defined using the Stability Limit monitored lines which are:

- Graham – Cook Field

- Jacksboro – Bowman

- Graham – Tonkawa

- Bowman – Graham

- Comanche Switch – Red Creek

- Graham – Long Creek

A W-S CSC was added and defined as SAPS to Menard and Brownwood to Goldthwaite.

## Scenario 10

Scenario 10 was clustered using the pre-contingency 2010 DSA SUM1 base case.  The model was clustered into four zones.  The 2009 CSCs for N_S, S_N, and N_H; the N-W and W-N CSCs were defined as Graham to Long Creek and Graham to Cook Field.  The W-S CSC was added and defined as SAPS to Menard.

## Scenario 11

Scenario 11 was clustered using the pre-contingency 2010 DSA SUM1 base case.  The model was clustered into four zones.  The 2009 CSCs were used for N_S, S_N, and N_H; the N-W and W-N CSCs were defined as Graham to Parker and Graham to Benbrook.