## Slide 1: Congestion Management Work Group Update
For WMS 7-22-09
Marguerite Wagner
PSEG TX

## Slide 2: Topics Discussed
Met 6/23, 7/8
  CRE Selection Criteria PRR 816
  Changes to NS CRE
  2010 Zone Discussion Timeline

## Slide 3: PRR 816 CRE Determination
CMWG comments submitted 7/8/09
PRR 816 – Four Criteria Test for CREs
  Threshold weighted shift factor/PTDFs
  Resource concentration
  Boundary generation
  Correlation of CRE to the zone
PRR provides flexibility for ERCOT to propose CREs that seem reasonable, using the tests as guidelines

## Slide 4: CRE Selection Criteria Overview
Threshold weighted shift factor/PTDFs
  Use PTDF instead of SF; PTDF is reference bus independent
  Screens to find resources that have material impact on resolving constraint
Boundary generation
  Identifies generators with negative impacts to CSCs for generators not in their “native” zone
Concentration of Effective Generation
  Identifies situations where only a couple of generators have a large impact on constraint—such cases likely better managed locally
Correlation of CRE to its zone
  Screens to ensure that CREs are parallel to their CSC

## Slide 5: Changes to NS CRE 6/30/09
Issue: More timely/complete notification of potential changes to CRE configuration would assist market in supporting ERCOT’s efforts to maintain reliability
Recommendation—Need to develop procedures around PCAP submission, review, & criteria for approval—seek WMS endorsement for CMWG, OGRR TF or ROS

## Slide 6: Excerpt from 6/30/09 ERCOT Market Notice on Change to NS CRE
NOTICE DATE: June 30, 2009
NOTICE TYPE: M-B063009-01 Operations
SHORT DESCRIPTION: ERCOT/ONCOR has developed a system equipment status change which was implemented at 5:10 PM on Monday, June 29, 2009
INTENDED AUDIENCE: All Market Participants
DAY AFFECTED: 5:10 PM Monday, June 29, 2009, through 8:00 AM Tuesday, September 1, 2009
LONG DESCRIPTION: ERCOT has requested that ONCOR open the 138 kV line from Waco West to Temple Elm Creek at Cotton Belt. This equipment status change is for the Waco area in response to the system needs in managing the North to South Commercially Significant Constraint (CSC) transfer and to mitigate the constraint on the North to South CSC in response to the recent high temperatures.
As a result, the 69 kV lines from Waco West to McGregor TU and from Waco West to Temple will be radial during this period.
ADDITIONAL INFORMATION: This change is effective through September 1, 2009. During forced outages or extreme weather in the affected area, the lines may be required to be connected for support or restoring load.
The equipment which will change is listed at: http://mospublic.ercot.com/ercot/jsp/planned_trans_out.jsp and was posted at 5:13 PM June 29, 2009.
Additionally, this switching is expected to improve North to South transfer capability by as much as 200 MW, which will aid ERCOT in reliably managing transfers North to South.

## Slide 7: Waco Woodway - Waco-Atco – Cottonwood are NS CREs
Opened the 138 kV line from Waco West to Temple Elm Creek at Cotton Belt
And in reverse are CREs for SN
Temple Elm Creek
Waco W
Cotton Belt
Change Resulted in Increased NS Flow of ~ 180-200 MW

## Slide 8: Timeline of Changes to NS CRE 6/30/09
Week of 6/24 NS, SH CSCs active, high demand > 62 GW
6/25 date on response contained in Email to RPG sent Saturday 6/27 describing that zonal works for resolving Waco line
6/30 date of Market Notice indicating ERCOT/TO change in operation of CRE. Status of line normally closed in was opened—through Sept 1
Average flow rating of line increased by ~ 180 MW
ERCOT discussions w/ TO to raise line ratings
6/26/09 Unexpected resource outage
Affects NS constraint
Loss of Tradinghouse - Temple Pecan Creek 345KV overloads Waco Atco - Cotton Belt 138KV –started showing up in 3/7/09 Grid Ops Reports, also in April/May & June
7/8 CMWG – ERCOT commits to studying returning CRE to original configuration when Resource(s) returns to service –

## Slide 9: Discussion
Few rules around Pre Contingency Action Plans (PCAP)—4 presently in use
  Bellville S 138/69 kV Auto
  Graham Switch – Long Creek 345 kV dbl ct [NW CRE]
  Temple Pecan Creek – Tradinghouse / Temple Switch – Lake Creek dbl Ct [SN CSC]
  Hamilton Sonora 138 kV line
PCAP inherently has market impact—particularly those for CSCs/CREs
  2 approved (above) plus recent change to Waco area  3 existing PCAPs directly affect CSC flows
  PCAP” for Waco Area Issue transformed into “Normal State”
  ERCOT takes action using PCAP as basis for action before any contingency or overload is occurring
  Potentially impacts pricing and flows on CSC which can work counter to market design to use BES to solve CSC Congestion
Criteria for ERCOT PCAP approval  need to be clear and well defined Recommend WMS create a workgroup or direct CMWG or as ROS—OGRR TF to develop criteria for
  Clearly defining/establishing reliability need for PCAP
  For communicating PCAP type actions—when requested, when approved, when used
  Criteria for removing PCAP actions once system has recovered

## Slide 10: Timeline for 2010 Zone Determination
ERCOT to provide initial analysis 7/17
CMWG to meet 7/24, 8/4, 8/10
WMS Vote: CSC/CRE Package or separate?
  Recommendation on CSCs to Aug 19 WMS  Sept 3 TAC—Sept or Oct BOD—but CREs might not be in package
  Recommendation on CSC/CRE to Sept 16 WMS Oct 1 TAC, Oct 20 BOD
Protocol Deadline is 11/1
Potentially new way to determine CREs—pending approval of PRR 816

## Slide 11: Upcoming Work Items for CMWG
2010 CSCs/Zones
  July 24
  August 4
  August 10
  August 20
Nodal
  CCT
Next Meeting 7/24