| PRR Number | 816 | PRR Title | CRE Determination Criteria |  |
| --- | --- | --- | --- | --- |
| Timeline | Urgent | Recommended Action |  | Approval |
| Date of Decision |  | July 23, 2009 |  |  |
| Protocol Sections Requiring Revision |  | 7.2.3, Determining Closely Related Elements (CREs) 7.2.3.1, CRE Criteria (new) 7.2.3.1.1, Power Transfer Distribution Factor (PTDF) Threshold (new) 7.2.3.1.2, Generation Concentration (new) 7.2.3.1.3, Boundary Generation Resources (new) 7.2.3.1.4, CRE Correlation to CSC (new) 7.2.3.1.5, Intra-Year CRE Recommendation and Approval (new) |  |  |
| Proposed Effective Date |  | September 1, 2009 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Revision Description |  | This Protocol Revision Request (PRR) establishes a set of four criteria for determining if a candidate contingency/limiting element pair qualify as a Closely Related Element (CRE). |  |  |
| Overall Market Benefit |  | Clarifies CRE selection process—should facilitate mid-year updates if any are needed. |  |  |
| Overall Market Impact |  | Positive—more closely allows Market Participants to study ERCOT’s CRE recommendations. |  |  |
| Consumer Impact |  | Neutral to positive. |  |  |
| Credit Impacts |  | To be determined. |  |  |
| Procedural History |  | - On 6/22/09, PRR816 was posted. - On 6/24/09, the motion to grant PRR816 Urgent status passed via PRS email vote. - On 6/26/09, Shell Energy comments were posted. - On 7/10/09, Congestion Management Working Group (CMWG) comments were posted. - On 7/16/09, the CEO Revision Request Review was posted. - On 7/21/09, an Impact Analysis was posted. - On 7/23/09, PRS considered PRR816. |  |  |
| PRS Decision |  | On 7/23/09, PRS unanimously voted to recommend approval of PRR816 as amended by CMWG comments. The Consumer Market Segment was not present for the vote. |  |  |
| Summary of PRS Discussion |  | On 7/23/09, Shell Energy comments were discussed. It was noted that CMWG discussed the concept proposed by Shell Energy to target Local Congestion, but did not feel that additional revisions were necessary. ERCOT Staff stated that it believed that the revisions proposed by Shell Energy were not necessary for ERCOT to have the flexibility to propose CRE candidates that pass the CRE criteria in Sections 7.2.3.1.2 and 7.2.3.1.3 but fail the CRE criteria in Sections 7.2.3.1.1 and 7.2.3.1.4. |  |  |

Quantitative Impacts and Benefits

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Not applicable. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Effective use of zonal Balancing Energy Service to resolve congestion. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Shell Energy 062609 | Proposed revisions providing that if a CRE candidate passes the CRE criteria in Sections 7.2.3.1.2 and 7.2.3.1.3, yet fails the CRE criteria in Sections 7.2.3.1.1 and 7.2.3.1.4, the candidate shall be submitted to ROS and WMS for operation solution with urgency. |
| CMWG 071009 | Proposed revisions regarding determination of Boundary Generation Resources and other minor clarifications. |

| Original Sponsor |  |
| --- | --- |
| Name | Marguerite Wagner on behalf of CMWG |
| Company | PSEG Texas |
| Market Segment | Independent Generator |

Proposed Protocol Language Revision

7.2.3	Determining Closely Related Elements (CREs)

ERCOT shall evaluate each contingency element/limiting element pair (constraint) combination to determine if deployment of zonal Balancing Energy will be effective for managing the post-contingency flow on the limiting element.  Based on this evaluation, ERCOT shall develop proposed CREs and a list of contingencies for managing CSC and CRE related Congestion.  ERCOT shall present all proposed CREs and a list of contingencies for managing CSC and CRE related Congestion, including justification for their inclusion, to the appropriate ERCOT TAC subcommittee for approval.  For each year, ERCOT staff shall identify potential CREs using, at a minimum, the following process:

(1)	Using the same loaddata and flow limits used to determmine the transfer capability between congestion zones that are Terminal Zones for CSCs.  Terminal Zones means the pair of zones containing the endpoints of the CSC for which a particular candidate CRE is proposed.

(2)	Identify contingency/limiting element pairs that are binding for transfers between zones for up to one hundred fifty percent (150%) of the transfer capability identified in paragraph (1) above.

(3)	The limiting elements that meet the CRE criteria below for all contingency/limiting pair elements may be submitted to TAC for approval.

ERCOT may propose additional CREs as provided under this Section, provided the results of the tests below are submitted as well as a description of a need for the CRE.  If a proposed CRE fails any of the tests below, ERCOT shall provide an explanation of the reason ERCOT believes the proposed element should nevertheless be designated a CRE.

7.2.3.1	CRE Criteria

Each of the following criteria will use the post-contingency generation Shift Factors of the candidate contingency/limiting element pairs.  In order for a CRE to pass, all constraints identified in Section 7.2.3, Determining Closely Related Elements (CREs), associated with the CRE should pass the tests below.

7.2.3.1.1	Power Transfer Distribution Factor (PTDF) Threshold

(1)	The Power Transfer Distribution Factor (PTDF) measures the impact of power flow between a pair of locations on a particular transmission element.

(2)	“Terminal Zones” means the pair of zones containing the endpoints of the CSC for which a particular candidate CRE is proposed.

(3)	Determine the weighted average PTDF between the Terminal Zones of the candidate CRE by calculating the Shift Factor difference between the source and sink zones.  The weighted averages will only consider generation technologies that would be responsive to price signals.  For the source zone, the technologies excluded are:

(a)	Cogeneration;

(b)	Nuclear;

(c)	Hydro; and

(d)	DC Ties.

For the sink zone, the technologies excluded are:

(a)	Wind;

(b)	Cogeneration;

(c)	Nuclear;

(d)	Hydro;

(e)	Coal; and

(f)	DC Ties.

(4)	In order for the limiting element of the contingency limiting element pair to qualify as a CRE, the weighted average PTDF between the Terminal Zones for that element should be greater than 0.05, and the ratio of the PTDF to the line rating of the limiting element shall be greater than 0.0002 (e.g., the threshold PTDF for a line rated at 250 MVA is 250 * 0.0002 or 0.05).  However, if the weighted average PTDF between the Terminal Zones for the candidate CRE is greater than 0.2, then the candidate CRE would satisfy this criterion.

7.2.3.1.2	Generation Concentration

ERCOT shall determine the concentration of effective generation responsive to the constraint on both the incremental and decremental sides of the constraint.

(1)	Calculate the PTDF of all generators as the Shift Factor of the generator relative to the proposed CRE minus the generation weighted average Shift Factor of each CSC Terminal Zone relative to the proposed CRE.  For example, for a CRE candidate for the West to North CSC, the PTDFs on the CRE of all generators would be calculated relative to the North Zone for the decremental side of the CRE, and the PTDFs on the CRE of all generators would be calculated relative to the West Zone for the incremental side of the CRE.

(2)	For movable generation capacity (in any zone) equal to twice the CRE rating and having the greatest impact on the CRE on incremental side, calculate their generation weighted average PTDF with respect to the decremental Terminal Zone of the CSC.  This calculation is done by sorting the moveable generation capacity list from greatest to least absolute value PTDF on the CRE, summing the moveable capacity down to the first generator where the sum of the moveable capacity is just greater than twice the rating of the proposed CRE, and then calculating the generation weighted average PTDF for that amount of moveable capacity with respect to the decremental Terminal Zone of the CSC.  In the example above, the decremental zone is the West Zone.

(3)	For movable generation capacity (in any zone) equal to twice the CRE rating (using the same flow limits as for TCR modeling) and having the greatest impact on the CRE on decremental side, calculate their generation weighted average PTDF with respect to the incremental Terminal Zone of the CSC.  This calculation is done by sorting the moveable generation capacity list from greatest to least absolute value PTDF on the CRE, summing the moveable capacity down to the first generator where the sum of the moveable capacity is just greater than twice the rating of the proposed CRE, and then calculating the generation weighted average PTDF for that amount of moveable capacity with respect to the incremental Terminal Zone of the CSC.  In the example above, the incremental zone is the North Zone.

(4)	In order for the limiting element of the contingency limiting element pair to qualify as a CRE, incremental movable generation capacity equal to twice the CRE’s rating should not have a generation weighted average PTDF on the CRE greater than twice the zonal average PTDF on the CRE of the incremental Terminal Zone of the CSC.  Similarly, decremental movable generation capacity equal to twice the CRE’s rating should not have a generation weighted average PTDF on the CRE greater than twice the zonal average PTDF on the CRE of the decremental Terminal Zone of the CSC.

7.2.3.1.3	Boundary Generation Resources

ERCOT shall determine the impact error due to Boundary Generation Resources as follows:

(1)	For each generator, find the generator’s PTDF on the CRE to each Congestion Zone and select the Congestion Zone to which the generator’s PTDF on the CRE has the lowest absolute value;

(2)	If the Congestion Zone selected in paragraph (1) above is different from the generator’s designated Congestion Zone, then that generator is a Boundary Generation Resource;

(3)	Determine the impact error of a Boundary Generation Resource by multiplying the difference between the absolute value of the generator’s PTDF on the CRE to its designated Congestion Zone minus the absolute value of the generator’s PTDF on the CRE to the Congestion Zone selected in paragraph (1) above times its maximum capacity.

In order for the limiting element of the contingency-limiting element pair to qualify as a CRE, the sum of the impact errors of all Boundary Generation Resources should be less than or equal to thirty percent (30%) of the rating of the CRE (using the same flow limits as for TCR modeling).

7.2.3.1.4	CRE Correlation to CSC

ERCOT shall determine the correlation of the CRE to its designated CSC by calculating the percentage error in deployment as follows:

(1)	For the CRE and its CSC, determine their PTDFs for each pair of Congestion Zones using the method described in paragraph (3) of Section 7.2.3.1.1, Power Transfer Distribution Factor (PTDF) Threshold.

(2)	Calculate a scaling factor “A” by dividing the CSC PTDF for the CSC’s Terminal Zones by the CRE PTDF for the CSC’s Terminal Zones, i.e., A = (CSC PTDF)/(CRE PTDF), both PTDFs being for the CSC Terminal Zones.

(3)	Determine the error in deployment for each pair of Congestion Zones, Bp, by subtracting the product of A times the CRE PTDF from the CSC PTDF for the same pair of Congestion Zone, i.e. Bp = (CSC PTDF)p – A*(CRE PTDF)p, where p is one pair of Congestion Zones.

(4)	Determine the percentage error in deployment by dividing Bp by the CSC PTDF for the CSC’s Terminal Zones.

In order for the limiting element of the contingency limiting element pair to qualify as a CRE, the maximum absolute value of percentage error of deployment should be less than fifty percent (50%).

7.2.3.1.5	Intra-Year CRE Recommendation and Approval

During the effective year, ERCOT may propose modifications to the list of CREs or the approved list of contingencies for managing CSC and CRE related congestion, including the expected duration of those modifications, as needed to more closely represent actual system constraints that can be effectively resolved by Zonal Balancing Energy deployments.  Any modifications to the list of CREs or the approved list of contingencies for managing CSC and CRE related congestion will not affect Congestion Zone definition or composition, nor will they affect CSC definitions.  ERCOT shall present modifications proposed to the list of CREs or the approved list of contingencies for managing CSC and CRE related congestion after the start of the year to TAC for approval.  TAC will have seven (7) days to take action on the proposed modification.  If TAC takes no action within seven (7) days, the proposed modification shall be deemed approved.