## W-N
AC FCITC MULTIPLE TRANSFER REPORT
PSS(tm)MUST 8.1.1 -- Managing and Utilizing System Transmission -- MON, JUL 27 2009 17:54
10SUM1 -2010 SUMMER ON-PEAK BASE CASE - ERCOT SSWG PASS 8
UPDATED 07/01/2009 - ERCOT PSSE VER 30.0 CSC CONS. DISPATCH
Case.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\Annual_2010_Basecase_v2_HH_adjusted_v29.sav
Subsys.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\MUST_SUBfile.sub
Monit.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\alltx.mon
Contin.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\ERCOT_CON_File_MUST_05292009_modified_no_D_no_openBus_no_singleline.con
Exclud.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\MUST_Exclude_List_08.exc
Reporting the first 500 violations per transfer | To | Transfer Level | AC FCITC | DC FCITC | Delta FCITC | Limiting Constraint | Contingency | Ncon | PreShift | PostShift | Rating | AC TDF | DC TDF
WEST | NORTH_I | 5000 | 739 | 720.9 | 18.1 | L: 1318 CHINAGRV 138 1398 RADIUMMT 138 1 |  |  | 76.4 | 104.9 | 105 | 0.03867 | 0.04017
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 898.3 | 875.3 | 22.9 | L: 1318 CHINAGRV 138 1398 RADIUMMT 138 1 |  |  | 73.3 | 104.9 | 105 | 0.03517 | 0.03653
[7 empty] | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 1111.1 | 1035 | 76.1 | L: 1427 FISHERRD 138 1448 WCHTFLLS 138 1 |  |  | 214.9 | 260 | 260 | 0.04061 | 0.04232
[7 empty] | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 1478.1 | 1366.1 | 111.9 | L: 1426 FISHRDSS 138 1427 FISHERRD 138 1 |  |  | 227.7 | 287.4 | 287 | 0.04036 | 0.04232
[7 empty] | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 1478.8 | 1441.1 | 37.7 | L: 1032 MRGNCRK_ 138 1341 SWTRDTAP 138 1 |  |  | 135 | 186.2 | 186 | 0.0346 | 0.03446
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 1903.1 | 1790.8 | 112.3 | L: 1025 FSCOGEN_ 345 1030 MRGNCRK_ 345 1 |  |  | 660.5 | 962.1 | 956 | 0.15851 | 0.15828
|  |  | TDF_Sign |  |  |  | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 1906 | 1792.1 | 113.8 | L: 1025 FSCOGEN_ 345 1030 MRGNCRK_ 345 1 |  |  | 663.2 | 958.6 | 956 | 0.15499 | 0.15656
|  |  | NotConv |  |  |  | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 1906 | 1792.1 | 113.8 | L: 1025 FSCOGEN_ 345 1030 MRGNCRK_ 345 1 |  |  | 663.2 | 958.6 | 956 | 0.15499 | 0.15656
|  |  | NotConv |  |  |  | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 1962.8 | 1950.6 | 12.2 | L: 1302 MULESHOE 138 1307 KEYLYNTE 138 1 |  |  | 56.4 | 186 | 186 | 0.06602 | 0.06672
[7 empty] | C: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 | 947
Open 1300 EXSHARNR 138 1301 WILLOWVA 138 1
|  |  | 1934.1 | 1950.6 | -16.4 | L: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 |  |  | 59.5 | 186 | 186 | 0.06538 | -0.06672
[7 empty] | C: 1302 MULESHOE 138 1307 KEYLYNTE 138 1 | 952
Open 1302 MULESHOE 138 1307 KEYLYNTE 138 1
|  |  | 2039.4 | 2053.6 | -14.2 | L: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 |  |  | 52.7 | 186 | 186 | 0.06536 | -0.06672
[7 empty] | C: 1163 LAMESA_8 138 1307 KEYLYNTE 138 1 | 867
Open 1163 LAMESA_8 138 1307 KEYLYNTE 138 1
|  |  | 2047.2 | 2053.6 | -6.4 | L: 1163 LAMESA_8 138 1307 KEYLYNTE 138 1 |  |  | 49.4 | 184.5 | 186 | 0.06598 | -0.06672
|  |  | NotConv |  |  |  | C: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 | 947
Open 1300 EXSHARNR 138 1301 WILLOWVA 138 1
|  |  | 1970.5 | 2061.5 | -91 | L: 1334 CHNGOWNR 138 1339 ESKOTA_8 138 1 |  |  | 94.8 | 213.9 | 214 | 0.06044 | -0.05932
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2111.4 | 2096.8 | 14.6 | L: 1302 MULESHOE 138 1307 KEYLYNTE 138 1 |  |  | 46.7 | 186 | 186 | 0.06596 | 0.06672
[7 empty] | C: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 | 948
Open 1300 EXSHARNR 138 1309 BLUFCKTA 138 1
|  |  | 2038.1 | 2096.8 | -58.7 | L: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 |  |  | 51.6 | 184 | 186 | 0.06492 | 0.06672
|  |  | NotConv |  |  |  | C: 1302 MULESHOE 138 1307 KEYLYNTE 138 1 | 952
Open 1302 MULESHOE 138 1307 KEYLYNTE 138 1
|  |  | 2272.3 | 2114.5 | 157.8 | L: 1421 WILLOWCK 345 1436 PARKER_5 345 1 |  |  | 681.7 | 1072.3 | 1072 | 0.1719 | 0.18122
[7 empty] | C: 1429 JACKSBRO 345 1730 KRUMW_5 345 11 | 92
Open 1429 JACKSBRO 345 1730 KRUMW_5 345 1
|  |  | 2174.7 | 2199.9 | -25.1 | L: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 |  |  | 44.9 | 186 | 186 | 0.06484 | 0.06672
[7 empty] | C: 1163 LAMESA_8 138 1307 KEYLYNTE 138 1 | 867
Open 1163 LAMESA_8 138 1307 KEYLYNTE 138 1
|  |  | 2218.9 | 2199.9 | 19.1 | L: 1163 LAMESA_8 138 1307 KEYLYNTE 138 1 |  |  | 39.8 | 186 | 186 | 0.06589 | -0.06672
[7 empty] | C: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 | 948
Open 1300 EXSHARNR 138 1309 BLUFCKTA 138 1
|  |  | 2256 | 2353.8 | -97.8 | L: 1334 CHNGOWNR 138 1339 ESKOTA_8 138 1 |  |  | 90.1 | 213.9 | 214 | 0.05485 | -0.05387
[7 empty] | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 2236.3 | 2391.9 | -155.6 | L: 1464 WFALLS_S 138 1478 ARROWHD_ 138 1 |  |  | 68.2 | 140.1 | 143 | 0.03215 | -0.03341
|  |  | NotConv |  |  |  | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 2288.9 | 2404.2 | -115.3 | L: 1334 CHNGOWNR 138 76319 MCELMUR 138 1 |  |  | 94.6 | 234.4 | 234 | 0.06106 | 0.05932
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2405.7 | 2424.9 | -19.2 | L: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 |  |  | 36.8 | 186.5 | 186 | 0.06219 | -0.0616
[7 empty] | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2288.2 | 2464 | -175.8 | L: 76317 POTTERTP 138 76319 MCELMUR 138 1 |  |  | 91.5 | 234 | 234.2 | 0.06229 | -0.05932
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2711 | 2473.5 | 237.6 | L: 1876 WLFHOLW_ 345 1880 ROCKYCRK 345 1 |  |  | 923.2 | 1065 | 1072 | 0.05232 | 0.05485
|  |  | NotConv |  |  |  | C: 1890 DECRDOVA 345 1900 COMCHPKW 345 11 | 593
Open 1890 DECRDOVA 345 1900 COMCHPKW 345 1
|  |  | 2363.2 | 2518.6 | -155.3 | L: 6260 ABSO4A 138 76317 POTTERTP 138 1 |  |  | 88.7 | 232.6 | 234 | 0.06091 | -0.05932
|  |  | NotConv |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2570.2 | 2556.5 | 13.6 | L: 6235 ABMULCW7 345 71050 BITTERCR 345 1 |  |  | 471 | 1041.2 | 1072 | 0.22188 | -0.23608
|  |  | TDF_Sign |  |  |  | C: 76009 L_TWINBU 345 76090 L_DIVIDE 345 16 | 611
Open 76009 L_TWINBU 345 76090 L_DIVIDE 345 1
|  |  | 2550.1 | 2583.2 | -33.1 | L: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 |  |  | 29.8 | 186.2 | 186 | 0.06132 | 0.0616
[7 empty] | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2657.4 | 2611.4 | 46 | L: 6235 ABMULCW7 345 71050 BITTERCR 345 1 |  |  | 417.4 | 1071.8 | 1072 | 0.24628 | -0.25319
[7 empty] | C: 1414 CHAMPNCR 345 1420 SWEETWTR 345 11 | 67
Open 1414 CHAMPNCR 345 1420 SWEETWTR 345 1
|  |  | 2583 | 2613.5 | -30.5 | L: 6235 ABMULCW7 345 71050 BITTERCR 345 1 |  |  | 417.4 | 1056.7 | 1072 | 0.24753 | -0.25319
|  |  | NotConv |  |  |  | C: 1420 SWEETWTR 345 1439 LONCREK2 345 11 | 69
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 1745.3 | 2619.1 | -873.8 | L: 1371 MURRY_P8 138 1431 GRHAMSES 138 1 |  |  | 11.4 | 91.5 | 143 | 0.04594 | 0.05962
|  |  | NotConv |  |  |  | C:COOKFIELD / LONGCREEK - GRAHAM8 | 912
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 2632 | 2635.7 | -3.6 | L: 1371 MURRY_P8 138 1431 GRHAMSES 138 1 |  |  | 12.4 | 142.8 | 143 | 0.04955 | 0.05968
[7 empty] | C:GRAHAM - LONGCREEK / LONGCREEK - COOKFIELD8 | 911
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1439 LONCREK2 345 1442 COKFIELD 345 1
|  |  | 2777.8 | 2716.8 | 61 | L: 1048 TONKAWA_ 345 1430 GRHAMSES 345 1 |  |  | 337.1 | 1072.1 | 1072 | 0.2646 | 0.27207
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2595.6 | 2731.1 | -135.5 | L: 1334 CHNGOWNR 138 76319 MCELMUR 138 1 |  |  | 89.9 | 234.1 | 234 | 0.05553 | 0.05387
[7 empty] | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 2802.8 | 2734 | 68.7 | L: 1371 MURRY_P8 138 1431 GRHAMSES 138 1 |  |  | 17.8 | 149.7 | 143 | 0.04706 | 0.05953
|  |  | TDF_Sign |  |  |  | C:SWEETWATER / MULBERRY - LONGCREEK8 | 910
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 2760.6 | 2772 | -11.4 | L: 1371 MURRY_P8 138 6169 PAIP4B 138 1 |  |  | 10.6 | 155 | 155 | 0.05232 | -0.05962
[7 empty] | C:COOKFIELD / LONGCREEK - GRAHAM8 | 912
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 2796.2 | 2788.4 | 7.8 | L: 1371 MURRY_P8 138 6169 PAIP4B 138 1 |  |  | 11.4 | 150.1 | 155 | 0.0496 | -0.05968
|  |  | TDF_Sign |  |  |  | C:GRAHAM - LONGCREEK / LONGCREEK - COOKFIELD8 | 911
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1439 LONCREK2 345 1442 COKFIELD 345 1
|  |  | 2649.3 | 2797 | -147.8 | L: 76317 POTTERTP 138 76319 MCELMUR 138 1 |  |  | 86.8 | 234.2 | 234.2 | 0.05563 | -0.05387
[7 empty] | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 2814.6 | 2810 | 4.6 | L: 1425 FISHRDSS 345 1426 FISHRDSS 138 1 |  |  | 331.4 | 501.2 | 501 | 0.06036 | 0.06081
[7 empty] | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 2877 | 2834 | 43.1 | L: 1425 FISHRDSS 345 6100 OKLA7A 345 1 |  |  | 497.8 | 1097.2 | 1072 | 0.20832 | -0.20032
|  |  | TDF_Sign |  |  |  | C:COOKFIELD / LONGCREEK - GRAHAM8 | 912
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 3229.8 | 2854.6 | 375.3 | L: 1425 FISHRDSS 345 6100 OKLA7A 345 1 |  |  | 493.1 | 1148.7 | 1072 | 0.20298 | -0.20058
|  |  | TDF_Sign |  |  |  | C:GRAHAM - LONGCREEK / LONGCREEK - COOKFIELD8 | 911
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1439 LONCREK2 345 1442 COKFIELD 345 1
|  |  | 2681.7 | 2857.1 | -175.4 | L: 6260 ABSO4A 138 76317 POTTERTP 138 1 |  |  | 84 | 233.6 | 234 | 0.05577 | -0.05387
[7 empty] | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 2972.9 | 2887.2 | 85.7 | L: 1371 MURRY_P8 138 6169 PAIP4B 138 1 |  |  | 16.1 | 156.2 | 155 | 0.04713 | -0.05953
|  |  | NotConv |  |  |  | C:SWEETWATER / MULBERRY - LONGCREEK8 | 910
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 2709.1 | 2898.3 | -189.2 | L: 1032 MRGNCRK_ 138 1333 MCDDONAL 138 1 |  |  | 70.7 | 185.9 | 186 | 0.04251 | -0.04039
[7 empty] | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2709.1 | 2898.3 | -189.2 | L: 1032 MRGNCRK_ 138 1333 MCDDONAL 138 1 |  |  | 70.7 | 185.9 | 186 | 0.04251 | -0.04039
[7 empty] | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2726.1 | 2899.5 | -173.4 | L: 1032 MRGNCRK_ 138 1333 MCDDONAL 138 1 |  |  | 70.5 | 186 | 186 | 0.04237 | -0.04046
[7 empty] | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 2884.9 | 2930 | -45.1 | L: 1048 TONKAWA_ 345 1430 GRHAMSES 345 1 |  |  | 247.6 | 1038 | 1072 | 0.27395 | 0.28537
|  |  | NotConv |  |  |  | C:SWEETWATER / MULBERRY - LONGCREEK8 | 910
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 2929.9 | 2967 | -37.1 | L: 1021 MIDLET_5 345 1022 MIDLNDE_ 345 1 |  |  | 606.1 | 956.1 | 956 | 0.11947 | -0.11863
[7 empty] | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 3052.3 | 2969 | 83.4 | L: 1048 TONKAWA_ 345 1430 GRHAMSES 345 1 |  |  | 257.3 | 1072.6 | 1072 | 0.26711 | 0.27804
[7 empty] | C:COOKFIELD / LONGCREEK - GRAHAM8 | 912
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 2913 | 2978.1 | -65.1 | L: 1021 MIDLET_5 345 1022 MIDLNDE_ 345 1 |  |  | 607.9 | 955.6 | 956 | 0.11935 | -0.11756
[7 empty] | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2913 | 2978.1 | -65.1 | L: 1021 MIDLET_5 345 1022 MIDLNDE_ 345 1 |  |  | 607.9 | 955.6 | 956 | 0.11935 | -0.11756
[7 empty] | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2995.1 | 3006.8 | -11.7 | L: 1448 WCHTFLLS 138 1480 RATHGBER 138 1 |  |  | 88 | 185.7 | 186 | 0.03262 | 0.03341
[7 empty] | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 3102.2 | 3071.7 | 30.5 | L: 1425 FISHRDSS 345 6100 OKLA7A 345 1 |  |  | 461.8 | 1072 | 1072 | 0.19672 | -0.19673
[7 empty] | C:SWEETWATER / MULBERRY - LONGCREEK8 | 910
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 2308.4 | 3084 | -775.6 | L: 1339 ESKOTA_8 138 1341 SWTRDTAP 138 1 |  |  | 107.8 | 191.2 | 214 | 0.03613 | -0.03446
|  |  | NotConv |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3278.7 | 3107.7 | 171 | L: 1441 COMCHESS 138 1650 COMANCHE 138 1 |  |  | 9.1 | 185.6 | 186 | 0.05381 | 0.0572
[7 empty] | C: 1440 COMCHESS 345 1900 COMCHPKW 345 11 | 119
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
|  |  | 2813.8 | 3124.8 | -310.9 | L: 76009 L_TWINBU 345 B$0034 TWA1 1.00 1 |  |  | 195.5 | 308.2 | 308 | 0.04008 | 0.03705
[7 empty] | C: 6444 SARC7A 345 76009 L_TWINBU 345 14 | 83
Open 6444 SARC7A 345 76009 L_TWINBU 345 1
|  |  | 2864 | 3128.8 | -264.8 | L: 76011 L_TWINBU 138 B$0034 TWA1 1.00 1 |  |  | 197.7 | 307.7 | 308 | 0.03843 | -0.03705
[7 empty] | C: 6444 SARC7A 345 76009 L_TWINBU 345 14 | 83
Open 6444 SARC7A 345 76009 L_TWINBU 345 1
|  |  | 2856 | 3131.7 | -275.6 | L: 6444 SARC7A 345 76009 L_TWINBU 345 1 |  |  | 452.3 | 1284.4 | 1315 | 0.29136 | -0.27442
|  |  | TDF_Sign |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2932.9 | 3134.8 | -201.9 | L: 1021 MIDLET_5 345 1025 FSCOGEN_ 345 1 |  |  | 496.2 | 956 | 956 | 0.1568 | 0.15828
[7 empty] | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 3374.5 | 3146.7 | 227.8 | L: 1421 WILLOWCK 345 1436 PARKER_5 345 1 |  |  | 521.6 | 1072 | 1072 | 0.1631 | 0.17478
[7 empty] | C: 1430 GRHAMSES 345 1436 PARKER_5 345 21 | 97
Open 1430 GRHAMSES 345 1436 PARKER_5 345 2
|  |  | 3374.5 | 3146.7 | 227.8 | L: 1421 WILLOWCK 345 1436 PARKER_5 345 1 |  |  | 521.6 | 1072 | 1072 | 0.1631 | 0.17478
[7 empty] | C: 1430 GRHAMSES 345 1436 PARKER_5 345 11 | 96
Open 1430 GRHAMSES 345 1436 PARKER_5 345 1
|  |  | 3099 | 3147.8 | -48.8 | L: 1309 BLUFCKTA 138 1318 CHINAGRV 138 1 |  |  | 62.9 | 186 | 186 | 0.03972 | 0.0793
[7 empty] | C: 1064 SUN_8 138 1067 GOLDENSW 138 1 | 781
Open 1064 SUN_8 138 1067 GOLDENSW 138 1
|  |  | 2902 | 3150.9 | -248.8 | L: 1021 MIDLET_5 345 1025 FSCOGEN_ 345 1 |  |  | 498.9 | 956.1 | 956 | 0.15754 | 0.15656
[7 empty] | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2902 | 3150.9 | -248.8 | L: 1021 MIDLET_5 345 1025 FSCOGEN_ 345 1 |  |  | 498.9 | 956.1 | 956 | 0.15754 | 0.15656
[7 empty] | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 3439.2 | 3167.4 | 271.8 | L: 1441 COMCHESS 138 1650 COMANCHE 138 1 |  |  | 13.7 | 187.8 | 186 | 0.05062 | 0.05463
|  |  | NotConv |  |  |  | C: COMCHESS1_5-COMCHPKW_5 & STPHNVIL_8-CMPKSTUP_88 | 749
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
Open 1641 STPHNVIL 138 2278 CMPKSTUP 138 1
|  |  | 3188.2 | 3180.7 | 7.6 | L: 1430 GRHAMSES 345 1442 COKFIELD 345 1 |  |  | 197.9 | 1036.4 | 1072 | 0.26302 | -0.27662
|  |  | TDF_Sign |  |  |  | C: 1430 GRHAMSES 345 1435 LONGCREK 345 11 | 95
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
|  |  | 3324.2 | 3193.5 | 130.7 | L: 1430 GRHAMSES 345 1435 LONGCREK 345 1 |  |  | 197.1 | 1072.1 | 1072 | 0.26321 | -0.2762
[7 empty] | C: 1430 GRHAMSES 345 1442 COKFIELD 345 11 | 98
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 3118.3 | 3197.2 | -78.9 | L: 1310 KNAPP_8 138 1312 SCURYCHV 138 1 |  |  | 9.3 | 124.4 | 124 | 0.03693 | 0.04131
[7 empty] | C: 1309 BLUFCKTA 138 1318 CHINAGRV 138 1 | 966
Open 1309 BLUFCKTA 138 1318 CHINAGRV 138 1
|  |  | 3288.6 | 3202.1 | 86.5 | L: 1435 LONGCREK 345 6230 ABMULCE7 345 1 |  |  | 109.1 | 1072.2 | 1072 | 0.29288 | -0.30422
[7 empty] | C: 1414 CHAMPNCR 345 1420 SWEETWTR 345 11 | 67
Open 1414 CHAMPNCR 345 1420 SWEETWTR 345 1
|  |  | 3193.6 | 3202.9 | -9.4 | L: 1030 MRGNCRK_ 345 71050 BITTERCR 345 1 |  |  | 407.5 | 955.7 | 956 | 0.17166 | 0.16942
[7 empty] | C: 76009 L_TWINBU 345 76090 L_DIVIDE 345 16 | 611
Open 76009 L_TWINBU 345 76090 L_DIVIDE 345 1
|  |  | 3162.2 | 3204.6 | -42.4 | L: 1435 LONGCREK 345 6230 ABMULCE7 345 1 |  |  | 109 | 1032.7 | 1072 | 0.29208 | -0.30422
|  |  | NotConv |  |  |  | C: 1420 SWEETWTR 345 1439 LONCREK2 345 11 | 69
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 3247.3 | 3218.1 | 29.2 | L: 1030 MRGNCRK_ 345 71050 BITTERCR 345 1 |  |  | 351.4 | 956.2 | 956 | 0.18625 | 0.18653
[7 empty] | C: 1414 CHAMPNCR 345 1420 SWEETWTR 345 11 | 67
Open 1414 CHAMPNCR 345 1420 SWEETWTR 345 1
|  |  | 3216.6 | 3220.9 | -4.3 | L: 1030 MRGNCRK_ 345 71050 BITTERCR 345 1 |  |  | 351.4 | 952.8 | 956 | 0.18696 | 0.18653
|  |  | NotConv |  |  |  | C: 1420 SWEETWTR 345 1439 LONCREK2 345 11 | 69
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 3356.4 | 3221.3 | 135.1 | L: 1430 GRHAMSES 345 1435 LONGCREK 345 1 |  |  | 188.1 | 1071.9 | 1072 | 0.26332 | -0.27671
[7 empty] | C: 1439 LONCREK2 345 1442 COKFIELD 345 11 | 117
Open 1439 LONCREK2 345 1442 COKFIELD 345 1
|  |  | 3374.9 | 3229.6 | 145.2 | L: 1439 LONCREK2 345 1442 COKFIELD 345 1 |  |  | 180 | 1074.2 | 1072 | 0.26498 | 0.27751
|  |  | TDF_Sign |  |  |  | C: 1430 GRHAMSES 345 1435 LONGCREK 345 11 | 95
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
|  |  | 3219.1 | 3263.1 | -43.9 | L: 1640 LINGLVLL 138 1642 FLATCRK_ 138 1 |  |  | 30 | 67.4 | 84 | 0.01163 | -0.03507
|  |  | NotConv |  |  |  | C: 1440 COMCHESS 345 6444 SARC7A 345 11 | 120
Open 1440 COMCHESS 345 6444 SARC7A 345 1
|  |  | 3404.5 | 3331.6 | 72.9 | L: 1435 LONGCREK 345 6230 ABMULCE7 345 1 |  |  | 227.4 | 1072.5 | 1072 | 0.24824 | -0.25753
[7 empty] | C: 1425 FISHRDSS 345 6100 OKLA7A 345 11 | 86
Open 1425 FISHRDSS 345 6100 OKLA7A 345 1
|  |  | 3244.5 | 3378.6 | -134.1 | L: 1334 CHNGOWNR 138 1339 ESKOTA_8 138 1 |  |  | 71.8 | 213.9 | 214 | 0.0438 | -0.04301
[7 empty] | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3381.6 | 3382.1 | -0.5 | L: 1649 HASSE_P8 138 1650 COMANCHE 138 1 |  |  | 14.1 | 174.8 | 186 | 0.04753 | -0.0572
|  |  | NotConv |  |  |  | C: 1440 COMCHESS 345 1900 COMCHPKW 345 11 | 119
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
|  |  | 3467.3 | 3382.8 | 84.5 | L: 1624 LEONSW_8 138 1642 FLATCRK_ 138 1 |  |  | 36.2 | 81.6 | 84 | 0.0131 | 0.03539
|  |  | LowSens |  |  |  | C: 1440 COMCHESS 345 6444 SARC7A 345 11 | 120
Open 1440 COMCHESS 345 6444 SARC7A 345 1
|  |  | 3359.6 | 3403.1 | -43.5 | L: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 |  |  | 10.6 | 186.2 | 186 | 0.05226 | -0.05328
Base Case
|  |  | 3440.8 | 3429.1 | 11.7 | L: 1309 BLUFCKTA 138 1318 CHINAGRV 138 1 |  |  | 23.5 | 186.1 | 186 | 0.04726 | 0.05992
[7 empty] | C: 1302 MULESHOE 138 1307 KEYLYNTE 138 1 | 952
Open 1302 MULESHOE 138 1307 KEYLYNTE 138 1
|  |  | 2302.8 | 3454.7 | -1151.9 | L: 1649 HASSE_P8 138 1650 COMANCHE 138 1 |  |  | 12.6 | 114.9 | 186 | 0.04444 | -0.05463
|  |  | NotConv |  |  |  | C: COMCHESS1_5-COMCHPKW_5 & STPHNVIL_8-CMPKSTUP_88 | 749
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
Open 1641 STPHNVIL 138 2278 CMPKSTUP 138 1
|  |  | 3492.1 | 3468.7 | 23.4 | L: 1414 CHAMPNCR 345 1420 SWEETWTR 345 1 |  |  | 315.5 | 1074.5 | 1072 | 0.21733 | 0.21934
|  |  | TDF_Sign |  |  |  | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3492.1 | 3474 | 18.1 | L: 1420 SWEETWTR 345 1439 LONCREK2 345 1 |  |  | 311.1 | 1074.4 | 1072 | 0.21858 | 0.21934
|  |  | TDF_Sign |  |  |  | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3529.9 | 3510.1 | 19.8 | L: 1309 BLUFCKTA 138 1318 CHINAGRV 138 1 |  |  | 26.9 | 186.3 | 186 | 0.04516 | 0.05992
[7 empty] | C: 1163 LAMESA_8 138 1307 KEYLYNTE 138 1 | 867
Open 1163 LAMESA_8 138 1307 KEYLYNTE 138 1
|  |  | 2810.3 | 3527 | -716.7 | L: 1018 MOSS_5 345 1028 ODESEHV_ 345 1 |  |  | 745.5 | 1071.9 | 1072 | 0.11615 | -0.09604
[7 empty] | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 2832.9 | 3540.1 | -707.2 | L: 1018 MOSS_5 345 1028 ODESEHV_ 345 1 |  |  | 746.7 | 1071.8 | 1072 | 0.11475 | -0.09533
[7 empty] | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2832.9 | 3540.1 | -707.2 | L: 1018 MOSS_5 345 1028 ODESEHV_ 345 1 |  |  | 746.7 | 1071.8 | 1072 | 0.11475 | -0.09533
[7 empty] | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 3151.2 | 3561.6 | -410.4 | L: 1398 RADIUMMT 138 6161 PAIP4A 138 1 |  |  | 40 | 155.1 | 155 | 0.03651 | 0.03278
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3812.7 | 3573.2 | 239.5 | L: 1430 GRHAMSES 345 1436 PARKER_5 345 2 |  |  | 321.8 | 1062.4 | 1072 | 0.19422 | 0.21028
|  |  | NotConv |  |  |  | C: 1430 GRHAMSES 345 1436 PARKER_5 345 11 | 96
Open 1430 GRHAMSES 345 1436 PARKER_5 345 1
|  |  | 3812.7 | 3573.2 | 239.5 | L: 1430 GRHAMSES 345 1436 PARKER_5 345 1 |  |  | 321.8 | 1062.4 | 1072 | 0.19422 | 0.21028
|  |  | NotConv |  |  |  | C: 1430 GRHAMSES 345 1436 PARKER_5 345 21 | 97
Open 1430 GRHAMSES 345 1436 PARKER_5 345 2
|  |  | 3703.7 | 3575.6 | 128.1 | L: 1900 COMCHPKW 345 1902 JHNSONSW 345 1 |  |  | 1184.3 | 1631.1 | 1631 | 0.12063 | 0.11875
[7 empty] | C: WLFHOLW_5-ROCKYCRK_5 & DECRDOVA_5-COMCHPKW_59 | 277
Open 1876 WLFHOLW_ 345 1880 ROCKYCRK 345 1
Open 1890 DECRDOVA 345 1900 COMCHPKW 345 1
|  |  | 3522.7 | 3586.2 | -63.5 | L: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 |  |  | 12.8 | 185.9 | 186 | 0.04913 | 0.05328
Base Case
|  |  | 2249.6 | 3588.2 | -1338.6 | L: 6444 SARC7A 345 76009 L_TWINBU 345 1 |  |  | 428 | 993.2 | 1315 | 0.25123 | -0.24604
|  |  | NotConv |  |  |  | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 3195 | 3594.7 | -399.8 | L: 1640 LINGLVLL 138 1642 FLATCRK_ 138 1 |  |  | 25.7 | 55.1 | 84 | 0.0092 | -0.03028
|  |  | NotConv |  |  |  | C:COOKFIELD / LONGCREEK - GRAHAM8 | 912
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 3268 | 3601.4 | -333.5 | L: 1640 LINGLVLL 138 1642 FLATCRK_ 138 1 |  |  | 25.9 | 56.9 | 84 | 0.00948 | -0.03029
|  |  | NotConv |  |  |  | C:GRAHAM - LONGCREEK / LONGCREEK - COOKFIELD8 | 911
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1439 LONCREK2 345 1442 COKFIELD 345 1
|  |  | 3479.3 | 3629.8 | -150.5 | L: 1478 ARROWHD_ 138 1480 RATHGBER 138 1 |  |  | 69.6 | 184.5 | 186 | 0.033 | -0.03341
|  |  | NotConv |  |  |  | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 3471.1 | 3656.5 | -185.5 | L: 1301 WILLOWVA 138 1308 GAILLYNT 138 1 |  |  | 36.3 | 186.1 | 186 | 0.04316 | 0.04106
[7 empty] | C: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 | 947
Open 1300 EXSHARNR 138 1301 WILLOWVA 138 1
|  |  | 3044.3 | 3675.6 | -631.3 | L: 1870 BENBRK_B 345 1875 BENBRK_B 138 1 |  |  | 475.8 | 570 | 570 | 0.03094 | 0.03094
[7 empty] | C: 1869 BENBRK_A 345 1874 BENBRK_A 138 11 | 550
Open 1869 BENBRK_A 345 1874 BENBRK_A 138 1
|  |  | 3495.2 | 3703 | -207.8 | L: 1302 MULESHOE 138 1308 GAILLYNT 138 1 |  |  | 34.3 | 185.9 | 186 | 0.04338 | -0.04106
[7 empty] | C: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 | 947
Open 1300 EXSHARNR 138 1301 WILLOWVA 138 1
|  |  | 2486.1 | 3729.7 | -1243.6 | L: 1624 LEONSW_8 138 1642 FLATCRK_ 138 1 |  |  | 31.8 | 47 | 84 | 0.00613 | 0.0306
|  |  | NotConv |  |  |  | C:COOKFIELD / LONGCREEK - GRAHAM8 | 912
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 3275.3 | 3736.3 | -461 | L: 1624 LEONSW_8 138 1642 FLATCRK_ 138 1 |  |  | 31.9 | 65.2 | 84 | 0.01015 | 0.03061
|  |  | NotConv |  |  |  | C:GRAHAM - LONGCREEK / LONGCREEK - COOKFIELD8 | 911
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1439 LONCREK2 345 1442 COKFIELD 345 1
|  |  | 3901.2 | 3744.6 | 156.7 | L: 1414 CHAMPNCR 345 1420 SWEETWTR 345 1 |  |  | 193.9 | 1110.5 | 1072 | 0.23495 | 0.2375
|  |  | TDF_Sign |  |  |  | C: 1435 LONGCREK 345 6230 ABMULCE7 345 11 | 109
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 3740.6 | 3749.4 | -8.9 | L: 1420 SWEETWTR 345 1439 LONCREK2 345 1 |  |  | 187.3 | 1057.2 | 1072 | 0.23256 | 0.2375
|  |  | TDF_Sign |  |  |  | C: 1435 LONGCREK 345 6230 ABMULCE7 345 11 | 109
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 2807.5 | 3776.2 | -968.7 | L: 1018 MOSS_5 345 1022 MIDLNDE_ 345 1 |  |  | 606.8 | 947.7 | 1052 | 0.1214 | 0.11863
|  |  | NotConv |  |  |  | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 3499.2 | 3777 | -277.8 | L: 1869 BENBRK_A 345 1874 BENBRK_A 138 1 |  |  | 443.9 | 598.6 | 599 | 0.04421 | 0.04582
[7 empty] | C: 1870 BENBRK_B 345 1873 BENBRK_5 345 11 | 551
Open 1870 BENBRK_B 345 1873 BENBRK_5 345 1
|  |  | 2815.9 | 3794.7 | -978.8 | L: 1018 MOSS_5 345 1022 MIDLNDE_ 345 1 |  |  | 608.7 | 948.4 | 1052 | 0.12064 | 0.11756
|  |  | NotConv |  |  |  | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2815.9 | 3794.7 | -978.8 | L: 1018 MOSS_5 345 1022 MIDLNDE_ 345 1 |  |  | 608.7 | 948.4 | 1052 | 0.12064 | 0.11756
|  |  | NotConv |  |  |  | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 3576 | 3851.1 | -275.1 | L: 1334 CHNGOWNR 138 76319 MCELMUR 138 1 |  |  | 71.6 | 231.8 | 234 | 0.04482 | 0.04301
|  |  | TDF_Sign |  |  |  | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3974.6 | 3864.9 | 109.8 | L: 1430 GRHAMSES 345 1436 PARKER_5 345 2 |  |  | 353 | 1033 | 1072 | 0.17108 | 0.18628
|  |  | TDF_Sign |  |  |  | C: 1421 WILLOWCK 345 1436 PARKER_5 345 11 | 73
Open 1421 WILLOWCK 345 1436 PARKER_5 345 1
|  |  | 3974.6 | 3864.9 | 109.8 | L: 1430 GRHAMSES 345 1436 PARKER_5 345 1 |  |  | 353 | 1033 | 1072 | 0.17108 | 0.18628
|  |  | TDF_Sign |  |  |  | C: 1421 WILLOWCK 345 1436 PARKER_5 345 11 | 73
Open 1421 WILLOWCK 345 1436 PARKER_5 345 1
|  |  | 3633.4 | 3894.1 | -260.7 | L: 1301 WILLOWVA 138 1308 GAILLYNT 138 1 |  |  | 26.3 | 185.5 | 186 | 0.04383 | 0.04106
[7 empty] | C: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 | 948
Open 1300 EXSHARNR 138 1309 BLUFCKTA 138 1
|  |  | 2919.3 | 3911.6 | -992.3 | L: 1430 GRHAMSES 345 1442 COKFIELD 345 1 |  |  | 180.9 | 811.5 | 1072 | 0.21602 | -0.22864
|  |  | NotConv |  |  |  | C: 1048 TONKAWA_ 345 1430 GRHAMSES 345 1 | 760
Open 1048 TONKAWA_ 345 1430 GRHAMSES 345 1
|  |  | 3756.5 | 3917.9 | -161.4 | L: 1431 GRHAMSES 138 1601 GRAHAME_ 138 1 |  |  | 78.7 | 204.6 | 210 | 0.03351 | 0.03339
|  |  | TDF_Sign |  |  |  | C: 1430 GRHAMSES 345 1436 PARKER_5 345 21 | 97
Open 1430 GRHAMSES 345 1436 PARKER_5 345 2
|  |  | 3756.5 | 3917.9 | -161.4 | L: 1431 GRHAMSES 138 1601 GRAHAME_ 138 1 |  |  | 78.7 | 204.6 | 210 | 0.03351 | 0.03339
|  |  | TDF_Sign |  |  |  | C: 1430 GRHAMSES 345 1436 PARKER_5 345 11 | 96
Open 1430 GRHAMSES 345 1436 PARKER_5 345 1
|  |  | 3001.9 | 3933.6 | -931.7 | L: 76317 POTTERTP 138 76319 MCELMUR 138 1 |  |  | 68.5 | 199.8 | 234.2 | 0.04375 | -0.04301
|  |  | LowSens |  |  |  | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3302.5 | 3936.4 | -634 | L: 1414 CHAMPNCR 345 1420 SWEETWTR 345 1 |  |  | 297.8 | 936.8 | 1072 | 0.19351 | 0.1978
|  |  | LowSens |  |  |  | C:MRGNCRK - BITTER CREEK - MULBERRY8 | 855
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 1955.8 | 3938.2 | -1982.4 | L: 1431 GRHAMSES 138 1601 GRAHAME_ 138 1 |  |  | 71.1 | 133.9 | 210 | 0.03214 | 0.03545
|  |  | NotConv |  |  |  | C: 1440 COMCHESS 345 6444 SARC7A 345 11 | 120
Open 1440 COMCHESS 345 6444 SARC7A 345 1
|  |  | 3662.3 | 3940.7 | -278.4 | L: 1302 MULESHOE 138 1308 GAILLYNT 138 1 |  |  | 24.3 | 186 | 186 | 0.04414 | -0.04106
[7 empty] | C: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 | 948
Open 1300 EXSHARNR 138 1309 BLUFCKTA 138 1
|  |  | 3911.3 | 3942.3 | -31 | L: 1420 SWEETWTR 345 1439 LONCREK2 345 1 |  |  | 293.1 | 1084.6 | 1072 | 0.20236 | 0.1978
|  |  | TDF_Sign |  |  |  | C:MRGNCRK - BITTER CREEK - MULBERRY8 | 855
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2639.1 | 3949.2 | -1310.1 | L: 1430 GRHAMSES 345 1435 LONGCREK 345 1 |  |  | 177.3 | 716.1 | 1072 | 0.20415 | -0.22776
|  |  | TDF_Sign |  |  |  | C: 1048 TONKAWA_ 345 1430 GRHAMSES 345 1 | 760
Open 1048 TONKAWA_ 345 1430 GRHAMSES 345 1
|  |  | 3010.9 | 3955 | -944.1 | L: 1398 RADIUMMT 138 6161 PAIP4A 138 1 |  |  | 37.7 | 129.8 | 155 | 0.03058 | 0.03009
|  |  | TDF_Sign |  |  |  | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 1986.3 | 3967.7 | -1981.4 | L: 76009 L_TWINBU 345 76090 L_DIVIDE 345 1 |  |  | 579.6 | 1146.2 | 1676.2 | 0.28529 | -0.27551
|  |  | NotConv |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2398.3 | 3967.9 | -1569.6 | L: 1439 LONCREK2 345 1442 COKFIELD 345 1 |  |  | 162.8 | 685.9 | 1072 | 0.21809 | 0.22953
|  |  | TDF_Sign |  |  |  | C: 1048 TONKAWA_ 345 1430 GRHAMSES 345 1 | 760
Open 1048 TONKAWA_ 345 1430 GRHAMSES 345 1
|  |  | 3532.5 | 3971.9 | -439.4 | L: 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1 |  |  | 493.7 | 986.5 | 1072 | 0.13952 | -0.1431
|  |  | NotConv |  |  |  | C: 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1 | 737
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2864.3 | 3975.4 | -1111 | L: 1430 GRHAMSES 345 1442 COKFIELD 345 1 |  |  | 253.1 | 823.3 | 1072 | 0.19907 | -0.20548
|  |  | TDF_Sign |  |  |  | C: 1425 FISHRDSS 345 6100 OKLA7A 345 11 | 86
Open 1425 FISHRDSS 345 6100 OKLA7A 345 1
|  |  | 2929.8 | 4008.8 | -1079 | L: 6260 ABSO4A 138 76317 POTTERTP 138 1 |  |  | 65.7 | 192.1 | 234 | 0.04313 | -0.04301
|  |  | NotConv |  |  |  | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 4006.6 | 4018 | -11.4 | L: 1430 GRHAMSES 345 1436 PARKER_5 345 1 |  |  | 284.9 | 1042.5 | 1072 | 0.18908 | 0.19636
|  |  | NotConv |  |  |  | C: 1429 JACKSBRO 345 1430 GRHAMSES 345 11 | 90
Open 1429 JACKSBRO 345 1430 GRHAMSES 345 1
|  |  | 4006.6 | 4018 | -11.4 | L: 1430 GRHAMSES 345 1436 PARKER_5 345 2 |  |  | 284.9 | 1042.5 | 1072 | 0.18908 | 0.19636
|  |  | NotConv |  |  |  | C: 1429 JACKSBRO 345 1430 GRHAMSES 345 11 | 90
Open 1429 JACKSBRO 345 1430 GRHAMSES 345 1
|  |  | 4217.8 | 4032.5 | 185.3 | L: 1876 WLFHOLW_ 345 1880 ROCKYCRK 345 1 |  |  | 797.4 | 1054.3 | 1072 | 0.06092 | 0.06612
|  |  | TDF_Sign |  |  |  | C:VENUS_N5-JHNSONSW_P5 & VENUS_N5-COMCHPKW_59 | 323
Open 393 CONCORD 345 394 CONCORD 138 1
Open 1891 DECRDOVA 138 2281 GODLEY_8 138 1
Open 1900 COMCHPKW 345 1902 JHNSONSW 345 1
Open 1902 JHNSONSW 345 1907 VENUS_N5 345 1
|  |  | 3034.6 | 4037.8 | -1003.1 | L: 1439 LONCREK2 345 1442 COKFIELD 345 1 |  |  | 235.9 | 851.5 | 1072 | 0.20286 | 0.20637
|  |  | NotConv |  |  |  | C: 1425 FISHRDSS 345 6100 OKLA7A 345 11 | 86
Open 1425 FISHRDSS 345 6100 OKLA7A 345 1
|  |  | 3902.1 | 4057.5 | -155.4 | L: 1030 MRGNCRK_ 345 1414 CHAMPNCR 345 1 |  |  | 314.2 | 1072.1 | 1072 | 0.19422 | 0.18798
[7 empty] | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 4082.7 | 4091.2 | -8.4 | L: 6235 ABMULCW7 345 71050 BITTERCR 345 1 |  |  | 330.2 | 1071.9 | 1072 | 0.18166 | -0.18335
Base Case
|  |  | 2440.7 | 4120.1 | -1679.4 | L: 1064 SUN_8 138 1311 SACROC_8 138 1 |  |  | 36 | 70.3 | 143 | 0.01408 | 0.04232
|  |  | NotConv |  |  |  | C: 1309 BLUFCKTA 138 1318 CHINAGRV 138 1 | 966
Open 1309 BLUFCKTA 138 1318 CHINAGRV 138 1
|  |  | 2452.6 | 4929 | -2476.5 | L: 1571 ORAN1_8 138 1599 BARTON_8 138 1 |  |  | 36.5 | 105 | 186 | 0.02793 | -0.03045
|  |  | NotConv |  |  |  | C: PARKER_5-ROANOKE3T5 & ROANOKE1_5-ALLIANCE1_59 | 285
Open 1436 PARKER_5 345 1845 ROANOKE3 345 1
Open 1851 ROANOKE1 345 1855 ALLIANCE 345 1
Note on A11: PTI: Exporting Subsystem
Note on B11: PTI: Importing Subsystem
Note on C11: PTI: Maximum Test Level
Note on D11: PTI: AC First Contingency Incremental Transfer Capability
Note on E11: PTI: DC First Contingency Incremental Transfer Capability
Note on F11: PTI: Difference between AC FCITC and DC FCITC
Note on G11: PTI: Branch, Flowgate or Interface
Note on H11: PTI: Limiting Contingency. Review MUST options for reporting options
Note on I11: PTI: Contingency Index
Note on J11: PTI: MW Flow before the transfer
Note on K11: PTI: MW Flow after the transfer
Note on L11: PTI: Rating (Base case or Contingent)
Note on M11: PTI: AC Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case
Note on N11: PTI: DC Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case

## S-N
AC FCITC MULTIPLE TRANSFER REPORT
PSS(tm)MUST 8.1.1 -- Managing and Utilizing System Transmission -- MON, JUL 27 2009 17:54
10SUM1 -2010 SUMMER ON-PEAK BASE CASE - ERCOT SSWG PASS 8
UPDATED 07/01/2009 - ERCOT PSSE VER 30.0 CSC CONS. DISPATCH
Case.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\Annual_2010_Basecase_v2_HH_adjusted_v29.sav
Subsys.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\MUST_SUBfile.sub
Monit.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\alltx.mon
Contin.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\ERCOT_CON_File_MUST_05292009_modified_no_D_no_openBus_no_singleline.con
Exclud.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\MUST_Exclude_List_08.exc
Reporting the first 500 violations per transfer | To | Transfer Level | AC FCITC | DC FCITC | Delta FCITC | Limiting Constraint | Contingency | Ncon | PreShift | PostShift | Rating | AC TDF | DC TDF
SOUTH | NORTH_I | 5000 | -1925.9 | -2040.1 | 114.2 | L: 8458 B_DAVIS4 138 8883 RODD_FLD 138 1 |  |  | 447.4 | 320.5 | 320 | 0.06588 | 0.0671
[7 empty] | C: WESTSIDE4A-CABANISS4A & AIRLINE4-CABANISS4A7 | 195
Open 8485 WESTSIDE 138 8882 CABANISS 138 1
Open 8490 AIRLINE4 138 8882 CABANISS 138 1
|  |  | -1925.9 | -2040.1 | 114.2 | L: 8458 B_DAVIS4 138 8883 RODD_FLD 138 1 |  |  | 447.4 | 320.5 | 320 | 0.06588 | 0.0671
[7 empty] | C:AIRLINE - WESTSIDE6 | 851
Open 8490 AIRLINE4 138 8882 CABANISS 138 1
Open 8485 WESTSIDE 138 8882 CABANISS 138 1
|  |  | -1887 | -2040.1 | 153.1 | L: 8490 AIRLINE4 138 8882 CABANISS 138 1 |  |  | 442.7 | 320.4 | 320 | 0.06481 | 0.0671
[7 empty] | C: 8458 B_DAVIS4 138 8883 RODD_FLD 138 15 | 199
Open 8458 B_DAVIS4 138 8883 RODD_FLD 138 1
|  |  | -1887.7 | -2040.1 | 152.4 | L: 8490 AIRLINE4 138 8882 CABANISS 138 1 |  |  | 442.8 | 320.4 | 320 | 0.06486 | 0.0671
[7 empty] | C:DAVIS - HOLLY6 | 849
Open 8458 B_DAVIS4 138 8883 RODD_FLD 138 1
Open 8486 HOLLY44A 138 8883 RODD_FLD 138 1
|  |  | -1926.5 | -2040.1 | 113.6 | L: 8458 B_DAVIS4 138 8883 RODD_FLD 138 1 |  |  | 447.3 | 320.5 | 320 | 0.06586 | 0.0671
[7 empty] | C: 8490 AIRLINE4 138 8882 CABANISS 138 15 | 242
Open 8490 AIRLINE4 138 8882 CABANISS 138 1
|  |  | -1564 | -1693.2 | 129.2 | L: 8485 WESTSIDE 138 8882 CABANISS 138 1 |  |  | 421.5 | 320 | 320 | 0.06492 | -0.0671
[7 empty] | C: 8458 B_DAVIS4 138 8883 RODD_FLD 138 15 | 199
Open 8458 B_DAVIS4 138 8883 RODD_FLD 138 1
|  |  | -1566.4 | -1693.2 | 126.7 | L: 8485 WESTSIDE 138 8882 CABANISS 138 1 |  |  | 421.8 | 320 | 320 | 0.06497 | -0.0671
[7 empty] | C:DAVIS - HOLLY6 | 849
Open 8458 B_DAVIS4 138 8883 RODD_FLD 138 1
Open 8486 HOLLY44A 138 8883 RODD_FLD 138 1
|  |  | -1073.1 | -1144.2 | 71.1 | L: 8486 HOLLY44A 138 8883 RODD_FLD 138 1 |  |  | 391.1 | 320 | 320 | 0.06629 | -0.0671
[7 empty] | C: WESTSIDE4A-CABANISS4A & AIRLINE4-CABANISS4A7 | 195
Open 8485 WESTSIDE 138 8882 CABANISS 138 1
Open 8490 AIRLINE4 138 8882 CABANISS 138 1
|  |  | -1072.7 | -1144.2 | 71.5 | L: 8486 HOLLY44A 138 8883 RODD_FLD 138 1 |  |  | 391.1 | 320 | 320 | 0.06624 | -0.0671
[7 empty] | C: 8490 AIRLINE4 138 8882 CABANISS 138 15 | 242
Open 8490 AIRLINE4 138 8882 CABANISS 138 1
|  |  | -1073.1 | -1144.2 | 71.1 | L: 8486 HOLLY44A 138 8883 RODD_FLD 138 1 |  |  | 391.1 | 320 | 320 | 0.06629 | -0.0671
[7 empty] | C:AIRLINE - WESTSIDE6 | 851
Open 8490 AIRLINE4 138 8882 CABANISS 138 1
Open 8485 WESTSIDE 138 8882 CABANISS 138 1
|  |  | -1016.8 | -1144.2 | 127.3 | L: 8490 AIRLINE4 138 8882 CABANISS 138 1 |  |  | 385.9 | 320 | 320 | 0.06475 | 0.0671
[7 empty] | C: 8486 HOLLY44A 138 8883 RODD_FLD 138 15 | 235
Open 8486 HOLLY44A 138 8883 RODD_FLD 138 1
|  |  | -666.5 | -797.2 | 130.8 | L: 8485 WESTSIDE 138 8882 CABANISS 138 1 |  |  | 363.7 | 320 | 320 | 0.06554 | -0.0671
[7 empty] | C: B_DAVIS4A-AIRLINE4 & HOLLY44A-RODD_FLD4A7 | 57
Open 8458 B_DAVIS4 138 8490 AIRLINE4 138 1
Open 8486 HOLLY44A 138 8883 RODD_FLD 138 1
|  |  | -38.4 | -490.8 | 452.4 | L: 2427 WATMLL_W 345 3123 TRINDAD1 345 1 |  |  | 1073.3 | 1072.2 | 1072 | 0.02848 | -0.03293
[7 empty] | C:WATERMILL-LIMESTONE9 | 346
Open 2427 WATMLL_W 345 2435 WATMLL_1 345 1
Open 2428 WATMLL_E 345 46020 LIMEST__ 345 1
Open 2435 WATMLL_1 345 46020 LIMEST__ 345 2
|  |  | 70.1 | -363.3 | 433.4 | L: 2427 WATMLL_W 345 3123 TRINDAD1 345 1 |  |  | 1069 | 1071.1 | 1072 | 0.02886 | -0.03311
|  |  | NotConv |  |  |  | C:LIMEST: Watmille _1(46020-2428) & Watmille _2 (4607 | 519
Open 2428 WATMLL_E 345 46020 LIMEST__ 345 1
Open 2435 WATMLL_1 345 46020 LIMEST__ 345 2
|  |  | -419.3 | -328.6 | -90.7 | L: 44010 W_A_P___ 138 44651 SIENNA02 138 02 |  |  | 484.9 | 478.3 | 478 | 0.01585 | 0.03034
[7 empty] | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 213.5 | -13.5 | 227 | L: 8458 B_DAVIS4 138 8492 WOOLRIDG 138 1 |  |  | 312.7 | 320.1 | 320 | 0.03433 | 0.03775
[7 empty] | C: B_DAVIS4A-AIRLINE4 & HOLLY44A-RODD_FLD4A7 | 57
Open 8458 B_DAVIS4 138 8490 AIRLINE4 138 1
Open 8486 HOLLY44A 138 8883 RODD_FLD 138 1
|  |  | 261 | 155.3 | 105.7 | L: 7184 L_MCCALA 138 7188 L_REDWOO 138 1 |  |  | 424.8 | 441.2 | 441.2 | 0.0631 | 0.05411
[7 empty] | C: L_AUSTRO5_1Y-L_ZORN__5_2Y & L_ZORN__5_1Y-LYTTON348 | 518
Open 7040 L_AUSTRO 345 7045 L_ZORN__ 345 1
Open 7042 L_ZORN__ 345 9074 LYTTON34 345 1
|  |  | 851.5 | 174.3 | 677.2 | L: 44010 W_A_P___ 138 44651 SIENNA02 138 02 |  |  | 459.4 | 478 | 478 | 0.02188 | 0.03116
[7 empty] | C: KIOWA_5-KIOWAPP_5 & KIOWA_5-KIOWAPP_58 | 893
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 1
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 2
|  |  | 441.3 | 183.5 | 257.8 | L: 8458 B_DAVIS4 138 8490 AIRLINE4 138 1 |  |  | 306.2 | 319.6 | 320 | 0.03047 | 0.03137
[7 empty] | C: B_DAVIS4A-WOOLRIDG4A & B_DAVIS4A-PHARAOH4A7 | 54
Open 8458 B_DAVIS4 138 8492 WOOLRIDG 138 1
Open 8458 B_DAVIS4 138 8493 PHARAOH4 138 1
|  |  | 302.9 | 265.2 | 37.7 | L: 44020 ALIEF___ 138 44671 STAFRD09 138 09 |  |  | 376.8 | 384.1 | 384 | 0.02422 | -0.03761
[7 empty] | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 851.5 | 307.3 | 544.2 | L: 44010 W_A_P___ 138 44651 SIENNA02 138 02 |  |  | 459.4 | 478 | 478 | 0.02188 | 0.03116
[7 empty] | C: 1690 VALLYSES 345 11690 KIOWA_5 345 11 | 332
Open 1690 VALLYSES 345 11690 KIOWA_5 345 1
|  |  | 329.6 | 338.5 | -9 | L: 3668 RNDROCK1 138 7366 L_CHIEBR 138 1 |  |  | 206.1 | 220.1 | 220 | 0.04273 | 0.04233
[7 empty] | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 725.5 | 542.3 | 183.2 | L: 8490 AIRLINE4 138 8492 WOOLRIDG 138 1 |  |  | 294 | 320 | 320 | 0.03585 | -0.03775
[7 empty] | C: B_DAVIS4A-AIRLINE4 & HOLLY44A-RODD_FLD4A7 | 57
Open 8458 B_DAVIS4 138 8490 AIRLINE4 138 1
Open 8486 HOLLY44A 138 8883 RODD_FLD 138 1
|  |  | 611.4 | 629.8 | -18.4 | L: 3668 RNDROCK1 138 7288 L_WELLBR 138 1 |  |  | 368.4 | 428.9 | 429 | 0.09891 | -0.09906
[7 empty] | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 918 | 635.1 | 282.9 | L: 44010 W_A_P___ 138 44671 STAFRD09 138 09 |  |  | 415.3 | 440 | 440 | 0.02688 | 0.03761
[7 empty] | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 695.2 | 683.4 | 11.8 | L: 7343 L_GEORGE 138 7366 L_CHIEBR 138 1 |  |  | 190.5 | 220.2 | 219.9 | 0.04274 | -0.04233
[7 empty] | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 1237.3 | 712.3 | 524.9 | L: 44020 ALIEF___ 138 44671 STAFRD09 138 09 |  |  | 347.8 | 383.9 | 384 | 0.02917 | -0.03856
[7 empty] | C: KIOWA_5-KIOWAPP_5 & KIOWA_5-KIOWAPP_58 | 893
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 1
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 2
|  |  | 729.3 | 718.1 | 11.3 | L: 3668 RNDROCK1 138 7288 L_WELLBR 138 1 |  |  | 342.1 | 429 | 429 | 0.11917 | -0.12133
[7 empty] | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 764.2 | 743.3 | 20.9 | L: 7188 L_REDWOO 138 7192 L_SANMAR 138 1 |  |  | 393.1 | 441.2 | 441.2 | 0.063 | 0.05411
[7 empty] | C: L_AUSTRO5_1Y-L_ZORN__5_2Y & L_ZORN__5_1Y-LYTTON348 | 518
Open 7040 L_AUSTRO 345 7045 L_ZORN__ 345 1
Open 7042 L_ZORN__ 345 9074 LYTTON34 345 1
|  |  | 768.2 | 749.4 | 18.8 | L: 3668 RNDROCK1 138 7366 L_CHIEBR 138 1 |  |  | 183.3 | 219.5 | 220 | 0.04715 | 0.04781
[7 empty] | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 1237.2 | 835.4 | 401.9 | L: 44020 ALIEF___ 138 44671 STAFRD09 138 09 |  |  | 347.8 | 383.9 | 384 | 0.02917 | -0.03856
[7 empty] | C: 1690 VALLYSES 345 11690 KIOWA_5 345 11 | 332
Open 1690 VALLYSES 345 11690 KIOWA_5 345 1
|  |  | 1107.7 | 843.2 | 264.5 | L: 3124 TRINDAD2 345 3134 RICHLND2 345 1 |  |  | 877.4 | 956.1 | 956 | 0.07103 | -0.07571
[7 empty] | C: VENUS_S5-BIGBRN__5 & VENUS_N5-BIGBRN__59 | 62
Open 1906 VENUS_S5 345 3380 BIGBRN__ 345 1
Open 1907 VENUS_N5 345 3380 BIGBRN__ 345 1
|  |  | 959.5 | 885.6 | 73.9 | L: 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1 |  |  | 866.1 | 1072 | 1072 | 0.21459 | -0.21824
[7 empty] | C: 3413 TEMPSSLT 345 3429 SANDOW__ 345 12 | 991
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
|  |  | 963.1 | 889.1 | 73.9 | L: 3413 TEMPSSLT 345 3429 SANDOW__ 345 1 |  |  | 865.9 | 1072 | 1072 | 0.21405 | -0.21772
[7 empty] | C: 3414 TEMP_SS_ 345 3429 SANDOW__ 345 12 | 994
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 1277.6 | 1021.4 | 256.1 | L: 8458 B_DAVIS4 138 8490 AIRLINE4 138 1 |  |  | 281.2 | 320.1 | 320 | 0.03048 | 0.03137
[7 empty] | C: B_DAVIS4A-WOOLRIDG4A & AIRLINE4-PHARAOH4A7 | 53
Open 8458 B_DAVIS4 138 8492 WOOLRIDG 138 1
Open 8490 AIRLINE4 138 8493 PHARAOH4 138 1
|  |  | 1113 | 1054.7 | 58.3 | L: 7343 L_GEORGE 138 7366 L_CHIEBR 138 1 |  |  | 166.7 | 219.4 | 219.9 | 0.04733 | -0.04781
[7 empty] | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 1716.4 | 1073.2 | 643.1 | L: 44010 W_A_P___ 138 44671 STAFRD09 138 09 |  |  | 386.3 | 439.9 | 440 | 0.03123 | 0.03856
[7 empty] | C: KIOWA_5-KIOWAPP_5 & KIOWA_5-KIOWAPP_58 | 893
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 1
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 2
|  |  | 1361 | 1114.8 | 246.1 | L: 7104 L_WIRTZ_ 138 7126 L_FERGUS 138 2 |  |  | 181.7 | 220.6 | 220.6 | 0.02859 | -0.03293
[7 empty] | C: L_SHERSH8_1Y-L_FERGUS8_1Y & L_WIRTZ_8_1Y-L_FERGUS8 | 554
Open 7102 L_SHERSH 138 7126 L_FERGUS 138 1
Open 7104 L_WIRTZ_ 138 7126 L_FERGUS 138 1
|  |  | 1716.3 | 1196.3 | 520.1 | L: 44010 W_A_P___ 138 44671 STAFRD09 138 09 |  |  | 386.3 | 439.9 | 440 | 0.03123 | 0.03856
[7 empty] | C: 1690 VALLYSES 345 11690 KIOWA_5 345 11 | 332
Open 1690 VALLYSES 345 11690 KIOWA_5 345 1
|  |  | 1246.7 | 1196.3 | 50.4 | L: 3668 RNDROCK1 138 3670 RNDRCKNE 138 1 |  |  | 106.9 | 214 | 214 | 0.08591 | 0.08716
[7 empty] | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 1202.6 | 1213 | -10.4 | L: 7343 L_GEORGE 138 7347 L_RIVERY 138 1 |  |  | 168.9 | 220.4 | 220.6 | 0.04284 | 0.04233
[7 empty] | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2247.4 | 1219.5 | 1027.8 | L: 80168 LARVFTS 230 86105 CID-230 230 2 |  |  | 51.6 | 319.8 | 320 | 0.11931 | -0.27502
Base Case
|  |  | 1614.3 | 1242.6 | 371.7 | L: 47660 GARROT__ 138 47705 MIDTWN__ 138 90 |  |  | 237 | 282 | 282 | 0.02785 | 0.0333
[7 empty] | C:DEPWTR: Lydell Ckt. 70_70 (40460-41000) & Goodye7 | 362
Open 40460 DEPWTR__ 138 40650 GDYEAR__ 138 70
Open 40460 DEPWTR__ 138 41000 LYDELL__ 138 70
|  |  | 1277.8 | 1269.7 | 8.1 | L: 3414 TEMP_SS_ 345 3415 TEMP_SS_ 138 1 |  |  | 377.6 | 543 | 543 | 0.12943 | 0.1307
[7 empty] | C: LAKE_CRK1_5-AEP_SS__5 & AEP_PEC__5-AEP_SS__59 | 247
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
Open 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1
|  |  | 1401.1 | 1359.9 | 41.2 | L: 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1 |  |  | 717.5 | 1072 | 1072 | 0.253 | -0.25424
[7 empty] | C: AEPSSLT__5-SANDOW__5 & AEPSSLT__5-SALADOSS_59 | 248
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3413 TEMPSSLT 345 3699 SALADOSS 345 1
|  |  | 1434.5 | 1365.9 | 68.6 | L: 47660 GARROT__ 138 47705 MIDTWN__ 138 90 |  |  | 239.8 | 282.4 | 282 | 0.02969 | 0.03266
[7 empty] | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 1471.2 | 1400.2 | 71.1 | L: 3422 KILL_SS_ 345 3423 KILL_SS_ 138 1 |  |  | 432.5 | 515.2 | 515 | 0.05621 | 0.05817
[7 empty] | C: LAKE_CRK1_5-AEP_SS__5 & AEP_PEC__5-AEP_SS__59 | 247
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
Open 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1
|  |  | 1581 | 1413.4 | 167.5 | L: 3124 TRINDAD2 345 3134 RICHLND2 345 1 |  |  | 817.8 | 956.3 | 956 | 0.08764 | -0.09171
[7 empty] | C:LIMEST: Watmille _1(46020-2428) & Watmille _2 (4607 | 519
Open 2428 WATMLL_E 345 46020 LIMEST__ 345 1
Open 2435 WATMLL_1 345 46020 LIMEST__ 345 2
|  |  | 2113.9 | 1419.5 | 694.4 | L: 80168 LARVFTS 230 86105 CID-230 230 2 |  |  | 50.2 | 312.7 | 390 | 0.12417 | -0.27502
|  |  | NotConv |  |  |  | C: 8825 SURRCFE4 138 86107 CUF-138 138 15 | 385
Open 8825 SURRCFE4 138 86107 CUF-138 138 1
|  |  | 1453.8 | 1429.8 | 24 | L: 3668 RNDROCK1 138 3670 RNDRCKNE 138 1 |  |  | 116.2 | 213.5 | 214 | 0.06699 | 0.0681
[7 empty] | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 1611.8 | 1443.8 | 168 | L: 3124 TRINDAD2 345 3134 RICHLND2 345 1 |  |  | 814.7 | 956.3 | 956 | 0.08784 | -0.09183
[7 empty] | C:WATERMILL-LIMESTONE9 | 346
Open 2427 WATMLL_W 345 2435 WATMLL_1 345 1
Open 2428 WATMLL_E 345 46020 LIMEST__ 345 1
Open 2435 WATMLL_1 345 46020 LIMEST__ 345 2
|  |  | 1704.5 | 1471.3 | 233.2 | L: 8458 B_DAVIS4 138 8490 AIRLINE4 138 1 |  |  | 268.1 | 320 | 320 | 0.03046 | 0.03137
[7 empty] | C: AIRLINE4-WOOLRIDG4A & AIRLINE4-PHARAOH4A7 | 52
Open 8490 AIRLINE4 138 8492 WOOLRIDG 138 1
Open 8490 AIRLINE4 138 8493 PHARAOH4 138 1
|  |  | 2143.4 | 1474.1 | 669.3 | L: 80168 LARVFTS 230 86105 CID-230 230 2 |  |  | 51.6 | 292.5 | 390 | 0.11238 | -0.27502
|  |  | TDF_Sign |  |  |  | C:N_BELT: T_H_W Ckt. 97_97 (46100-45500) & N_Belt7 | 554
Open 45500 T_H_W___ 345 46100 N_BELT__ 345 97
Open 46100 N_BELT__ 345 46110 N_BELT__ 138 A1
|  |  | 2143.4 | 1474.1 | 669.3 | L: 80168 LARVFTS 230 86105 CID-230 230 2 |  |  | 51.6 | 292.5 | 390 | 0.11238 | -0.27502
|  |  | TDF_Sign |  |  |  | C: 7087 L_CORONA 138 7103 L_BUCKRA 138 14 | 386
Open 7087 L_CORONA 138 7103 L_BUCKRA 138 1
|  |  | 1569.1 | 1523.5 | 45.6 | L: 7343 L_GEORGE 138 7347 L_RIVERY 138 1 |  |  | 145.6 | 220.1 | 220.6 | 0.04751 | 0.04781
[7 empty] | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 1828.9 | 1596.7 | 232.2 | L: 47660 GARROT__ 138 47705 MIDTWN__ 138 90 |  |  | 225.9 | 282.5 | 282 | 0.03097 | 0.03312
[7 empty] | C: KIOWA_5-KIOWAPP_5 & KIOWA_5-KIOWAPP_58 | 893
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 1
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 2
|  |  | 1606.5 | 1617.5 | -11.1 | L: 3665 PFLGRVIL 138 7336 L_GILLCR 138 1 |  |  | 148.5 | 213.5 | 214 | 0.04043 | -0.04032
[7 empty] | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 1404.7 | 1624 | -219.3 | L: 2432 TRICRN1_ 345 2433 SGVLSW1_ 345 1 |  |  | 1024.8 | 1072.1 | 1072 | 0.03363 | 0.03565
[7 empty] | C:WATERMILL-TRINIDAD/TRICORNER9 | 349
Open 2427 WATMLL_W 345 3123 TRINDAD1 345 1
Open 2428 WATMLL_E 345 2432 TRICRN1_ 345 1
|  |  | 2318.7 | 1692.4 | 626.2 | L: 80168 LARVFTS 230 80169 LARVFTS 138 1 |  |  | 49.5 | 340.9 | 450 | 0.1257 | 0.27502
|  |  | NotConv |  |  |  | Base Case
|  |  | 2209 | 1801.5 | 407.5 | L: 80168 LARVFTS 230 80169 LARVFTS 138 1 |  |  | 47.8 | 342.3 | 495 | 0.13329 | 0.27502
|  |  | NotConv |  |  |  | C: 8825 SURRCFE4 138 86107 CUF-138 138 15 | 385
Open 8825 SURRCFE4 138 86107 CUF-138 138 1
|  |  | 1795.6 | 1843.1 | -47.5 | L: 7346 L_GABRIE 138 7347 L_RIVERY 138 1 |  |  | 143.1 | 220.6 | 220.6 | 0.04314 | -0.04233
[7 empty] | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2310 | 1856.1 | 454 | L: 80168 LARVFTS 230 80169 LARVFTS 138 1 |  |  | 49.5 | 333.4 | 495 | 0.12292 | 0.27502
|  |  | NotConv |  |  |  | C: 6562 FRIEND_R 138 76579 L_FORTLA 138 14 | 179
Open 6562 FRIEND_R 138 76579 L_FORTLA 138 1
|  |  | 2314.6 | 1856.1 | 458.6 | L: 80168 LARVFTS 230 80169 LARVFTS 138 1 |  |  | 49.5 | 336.8 | 495 | 0.12415 | 0.27502
|  |  | NotConv |  |  |  | C: 9148 HICRSMB1 138 9263 SALEMWLK 138 15 | 503
Open 9148 HICRSMB1 138 9263 SALEMWLK 138 1
|  |  | 2269.5 | 1871.2 | 398.2 | L: 47705 MIDTWN__ 138 47707 MIDRCLS_ 138 90 |  |  | 219.3 | 285.1 | 285 | 0.029 | 0.0333
[7 empty] | C:DEPWTR: Lydell Ckt. 70_70 (40460-41000) & Goodye7 | 362
Open 40460 DEPWTR__ 138 40650 GDYEAR__ 138 70
Open 40460 DEPWTR__ 138 41000 LYDELL__ 138 70
|  |  | 2269.5 | 1871.2 | 398.2 | L: 47707 MIDRCLS_ 138 47730 POLK____ 138 90 |  |  | 219.3 | 285.1 | 285 | 0.029 | 0.0333
[7 empty] | C:DEPWTR: Lydell Ckt. 70_70 (40460-41000) & Goodye7 | 362
Open 40460 DEPWTR__ 138 40650 GDYEAR__ 138 70
Open 40460 DEPWTR__ 138 41000 LYDELL__ 138 70
|  |  | 1999.9 | 1914.9 | 85 | L: 7310 L_SIMGID 138 7324 L_BUTLER 138 1 |  |  | 117.8 | 220.7 | 220.6 | 0.05143 | 0.05228
[7 empty] | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 1958.9 | 1928.1 | 30.7 | L: 3429 SANDOW__ 345 7040 L_AUSTRO 345 1 |  |  | 502.6 | 956 | 956 | 0.2315 | -0.23251
[7 empty] | C: 7040 L_AUSTRO 345 13429 SAND_TXU 345 24 | 320
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 1806.4 | 1946.4 | -140 | L: 7200 L_CANYON 138 7515 L_ROHR__ 138 1 |  |  | 153 | 220.7 | 220.6 | 0.03747 | 0.03301
[7 empty] | C: L_AUSTRO5_1Y-L_ZORN__5_2Y & L_ZORN__5_1Y-LYTTON348 | 518
Open 7040 L_AUSTRO 345 7045 L_ZORN__ 345 1
Open 7042 L_ZORN__ 345 9074 LYTTON34 345 1
|  |  | 1927.7 | 1958 | -30.3 | L: 3413 TEMPSSLT 345 3414 TEMP_SS_ 345 1 |  |  | 464.7 | 1072 | 1072 | 0.31508 | 0.31616
[7 empty] | C: 3414 TEMP_SS_ 345 3429 SANDOW__ 345 12 | 994
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2012.5 | 1965.9 | 46.7 | L: 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1 |  |  | 566 | 1071.6 | 1072 | 0.25122 | -0.25422
[7 empty] | C: 3413 TEMPSSLT 345 3414 TEMP_SS_ 345 12 | 990
Open 3413 TEMPSSLT 345 3414 TEMP_SS_ 345 1
|  |  | 2033.9 | 2006.7 | 27.2 | L: 47705 MIDTWN__ 138 47707 MIDRCLS_ 138 90 |  |  | 222.1 | 285 | 285 | 0.03094 | 0.03266
[7 empty] | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2033.9 | 2006.8 | 27.2 | L: 47707 MIDRCLS_ 138 47730 POLK____ 138 90 |  |  | 222.1 | 285 | 285 | 0.03094 | 0.03266
[7 empty] | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2106.1 | 2081.3 | 24.8 | L: 7346 L_GABRIE 138 7347 L_RIVERY 138 1 |  |  | 120.8 | 220.6 | 220.6 | 0.04743 | -0.04781
[7 empty] | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 1906.7 | 2084.4 | -177.7 | L: 7501 L_GOFORT 138 7515 L_ROHR__ 138 1 |  |  | 149 | 220.6 | 220.6 | 0.03752 | -0.03301
[7 empty] | C: L_AUSTRO5_1Y-L_ZORN__5_2Y & L_ZORN__5_1Y-LYTTON348 | 518
Open 7040 L_AUSTRO 345 7045 L_ZORN__ 345 1
Open 7042 L_ZORN__ 345 9074 LYTTON34 345 1
|  |  | 2146.1 | 2087.6 | 58.5 | L: 3429 SANDOW__ 345 7040 L_AUSTRO 345 1 |  |  | 529.4 | 956 | 956 | 0.19879 | -0.20032
[7 empty] | C: 3429 SANDOW__ 345 13429 SAND_TXU 345 13 | 17
Open 3429 SANDOW__ 345 13429 SAND_TXU 345 1
|  |  | 2168.1 | 2135.3 | 32.8 | L: 3650 ELGIN_SS 138 7324 L_BUTLER 138 1 |  |  | 106.5 | 218.4 | 220 | 0.05158 | -0.05228
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 2195.9 | 2181.6 | 14.3 | L: 47705 MIDTWN__ 138 47707 MIDRCLS_ 138 90 |  |  | 187.2 | 274.9 | 285 | 0.03996 | 0.04451
|  |  | NotConv |  |  |  | C:SANFLP-EUREKA_09 (47380-45750)[MSL &1] & WHITOK-JE7 | 808
Open 46600 WHITOK__ 345 47300 JENETA__ 345 72
Open 45750 EUREKA__ 138 47383 SANFLP87 138 9
Open 47380 SANFLP__ 138 47383 SANFLP87 138 9
|  |  | 2195.9 | 2181.6 | 14.3 | L: 47707 MIDRCLS_ 138 47730 POLK____ 138 90 |  |  | 187.2 | 274.9 | 285 | 0.03996 | 0.04451
|  |  | NotConv |  |  |  | C:SANFLP-EUREKA_09 (47380-45750)[MSL &1] & WHITOK-JE7 | 808
Open 46600 WHITOK__ 345 47300 JENETA__ 345 72
Open 45750 EUREKA__ 138 47383 SANFLP87 138 9
Open 47380 SANFLP__ 138 47383 SANFLP87 138 9
|  |  | 2210.7 | 2254.4 | -43.8 | L: 2432 TRICRN1_ 345 3124 TRINDAD2 345 1 |  |  | 972.7 | 1069.3 | 1072 | 0.04371 | -0.04487
|  |  | NotConv |  |  |  | C:LIMEST: Watmille _1(46020-2428) & Watmille _2 (4607 | 519
Open 2428 WATMLL_E 345 46020 LIMEST__ 345 1
Open 2435 WATMLL_1 345 46020 LIMEST__ 345 2
|  |  | 2178.8 | 2257 | -78.2 | L: 3415 TEMP_SS_ 138 3420 TEMP_PEC 138 1 |  |  | 153.6 | 479.6 | 493 | 0.14962 | 0.1556
|  |  | NotConv |  |  |  | C: LAKE_CRK1_5-AEP_SS__5 & AEP_PEC__5-AEP_SS__59 | 247
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
Open 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1
|  |  | 2308.3 | 2275.1 | 33.2 | L: 7040 L_AUSTRO 345 13429 SAND_TXU 345 2 |  |  | 534.7 | 1070.4 | 1072 | 0.23209 | 0.23256
|  |  | NotConv |  |  |  | C:SAND-AUSTROP & SAND AUTO9 | 300
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 3429 SANDOW__ 345 13430 SAND_TXU 138 1
|  |  | 2320.1 | 2317.8 | 2.2 | L: 44100 BRAZOS__ 138 44280 FTBEND__ 138 09 |  |  | 203.5 | 264.3 | 280 | 0.0262 | -0.03176
|  |  | NotConv |  |  |  | C:CEDARP-CENTER_97 (40000-40240) & CENTER-P_H_R__978 | 106
Open 40000 CEDARP__ 345 40240 CENTER__ 345 97
Open 40240 CENTER__ 345 42000 P_H_R___ 345 97
|  |  | 2280.5 | 2322.7 | -42.2 | L: 2432 TRICRN1_ 345 3124 TRINDAD2 345 1 |  |  | 969.2 | 1069.5 | 1072 | 0.04398 | -0.04502
|  |  | NotConv |  |  |  | C:WATERMILL-LIMESTONE9 | 346
Open 2427 WATMLL_W 345 2435 WATMLL_1 345 1
Open 2428 WATMLL_E 345 46020 LIMEST__ 345 1
Open 2435 WATMLL_1 345 46020 LIMEST__ 345 2
|  |  | 2319.6 | 2323.7 | -4.1 | L: 3522 HILLBORO 138 3546 WHITNEY_ 138 1 |  |  | 205.7 | 276.6 | 287 | 0.03057 | -0.03267
|  |  | NotConv |  |  |  | C: VENUS_S5-THOUSE__5 & VENUS_N5-THOUSE__59 | 61
Open 1906 VENUS_S5 345 3405 THOUSE__ 345 1
Open 1907 VENUS_N5 345 3405 THOUSE__ 345 1
|  |  | 2319.5 | 2356.9 | -37.3 | L: 3594 MCGREG_T 138 13662 TEMPELMC 138 1 |  |  | 60.4 | 202.7 | 214 | 0.06135 | -0.06441
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2297.7 | 2383.1 | -85.4 | L: 3668 RNDROCK1 138 7288 L_WELLBR 138 1 |  |  | 312.3 | 428.2 | 429 | 0.05046 | -0.05076
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEPSSLT__5-SALADOSS_59 | 248
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3413 TEMPSSLT 345 3699 SALADOSS 345 1
|  |  | 2321.1 | 2418.6 | -97.5 | L: 3682 MILANO_M 138 3683 MINERVA1 138 1 |  |  | 118.6 | 208.1 | 214 | 0.03854 | -0.03791
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2194.4 | 2435.7 | -241.3 | L: 8121 BLESSING 138 8125 LOLITA4A 138 1 |  |  | 111.7 | 208.7 | 211 | 0.04419 | -0.03984
|  |  | NotConv |  |  |  | C:LON HILL - WHITEPOINT CKT #17 | 97
Open 5915 SO_TEX__ 345 8956 WHITEPT 345 1
Open 8455 LON_HILL 345 8956 WHITEPT 345 1
|  |  | 2318 | 2437.5 | -119.6 | L: 7040 L_AUSTRO 345 13429 SAND_TXU 345 2 |  |  | 501.2 | 1037.3 | 1072 | 0.23129 | 0.23208
|  |  | NotConv |  |  |  | C: 3429 SANDOW__ 345 7040 L_AUSTRO 345 13 | 16
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
|  |  | 2309.9 | 2453.7 | -143.7 | L: 7335 L_HOLATA 138 9217 HOWARDLN 138 1 |  |  | 344.6 | 480 | 480 | 0.05861 | -0.05623
[7 empty] | C: 7334 L_MCNEIL 138 9079 MCNEILN 138 14 | 643
Open 7334 L_MCNEIL 138 9079 MCNEILN 138 1
|  |  | 2319.3 | 2455.8 | -136.5 | L: 3668 RNDROCK1 138 7366 L_CHIEBR 138 1 |  |  | 145.8 | 217.6 | 220 | 0.03096 | 0.03058
|  |  | NotConv |  |  |  | C: 7524 L_SEWARD 138 7525 L_LEANDE 138 14 | 722
Open 7524 L_SEWARD 138 7525 L_LEANDE 138 1
|  |  | 2319.5 | 2465.7 | -146.2 | L: 3665 PFLGRVIL 138 7336 L_GILLCR 138 1 |  |  | 114 | 208.9 | 214 | 0.04092 | -0.04042
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 2320.5 | 2488.6 | -168.1 | L: 32 ROBERTSO 138 3682 MILANO_M 138 1 |  |  | 116.4 | 205.9 | 214 | 0.03855 | -0.03791
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2321.5 | 2494.5 | -173 | L: 44100 BRAZOS__ 138 44280 FTBEND__ 138 09 |  |  | 185.4 | 260.9 | 280 | 0.03252 | -0.03773
|  |  | NotConv |  |  |  | C:W_A_P_: Obrien Ckt. 98_98 (44500-44000) & Obrien8 | 172
Open 44000 W_A_P___ 345 44500 OBRIEN__ 345 98
Open 44000 W_A_P___ 345 44500 OBRIEN__ 345 99
|  |  | 2321.5 | 2494.5 | -173 | L: 44100 BRAZOS__ 138 44280 FTBEND__ 138 09 |  |  | 185.4 | 260.9 | 280 | 0.03252 | -0.03773
|  |  | NotConv |  |  |  | C:OBRIEN-W_A_P__98 (44000-44500) & OBRIEN-W_A_P__998 | 111
Open 44000 W_A_P___ 345 44500 OBRIEN__ 345 98
Open 44000 W_A_P___ 345 44500 OBRIEN__ 345 99
|  |  | 2319.7 | 2543.9 | -224.2 | L: 44010 W_A_P___ 138 44652 SIENNA05 138 05 |  |  | 398.4 | 460 | 478 | 0.02654 | 0.03071
|  |  | NotConv |  |  |  | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2260.6 | 2551 | -290.4 | L: 8121 BLESSING 138 8125 LOLITA4A 138 1 |  |  | 108.8 | 208.5 | 211 | 0.04413 | -0.03963
|  |  | NotConv |  |  |  | C: 5915 SO_TEX__ 345 8956 WHITEPT 345 13 | 676
Open 5915 SO_TEX__ 345 8956 WHITEPT 345 1
|  |  | 2227.4 | 2562 | -334.5 | L: 3666 HUTTOSS1 138 3696 HUTTOSS_ 345 1 |  |  | 301 | 653.7 | 686 | 0.15832 | 0.17249
|  |  | TDF_Sign |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2320.4 | 2595.3 | -274.9 | L: 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1 |  |  | 328.8 | 989.6 | 1072 | 0.28482 | -0.28652
|  |  | NotConv |  |  |  | C: 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 12 | 976
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2319.8 | 2611.3 | -291.4 | L: 8490 AIRLINE4 138 8882 CABANISS 138 1 |  |  | 211 | 299.4 | 320 | 0.03807 | 0.03944
|  |  | NotConv |  |  |  | Base Case
|  |  | 2320.3 | 2641.9 | -321.6 | L: 44180 DEWALT__ 138 44691 TELVEW02 138 02 |  |  | 399.2 | 460.2 | 478 | 0.02629 | -0.03034
|  |  | NotConv |  |  |  | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2319.3 | 2653.9 | -334.6 | L: 8121 BLESSING 138 8125 LOLITA4A 138 1 |  |  | 105.4 | 206.9 | 211 | 0.04373 | -0.03941
|  |  | NotConv |  |  |  | C:SO_TEX: SO_TEX-Hillje_44 (5915-44200) & SO_TEX-Wh7 | 693
Open 5915 SO_TEX__ 345 8956 WHITEPT 345 1
Open 5915 SO_TEX__ 345 44200 HILLJE 345 1
|  |  | 2320.3 | 2729.3 | -409 | L: 2432 TRICRN1_ 345 3124 TRINDAD2 345 1 |  |  | 986.5 | 1057.3 | 1072 | 0.03054 | -0.03114
|  |  | NotConv |  |  |  | C: VENUS_S5-BIGBRN__5 & VENUS_N5-BIGBRN__59 | 62
Open 1906 VENUS_S5 345 3380 BIGBRN__ 345 1
Open 1907 VENUS_N5 345 3380 BIGBRN__ 345 1
|  |  | 2320.1 | 2770.6 | -450.6 | L: 3593 SPGVALLY 138 3594 MCGREG_T 138 1 |  |  | 44 | 178.9 | 214 | 0.05815 | -0.06103
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2118 | 2824.3 | -706.3 | L: 3422 KILL_SS_ 345 3423 KILL_SS_ 138 1 |  |  | 386.5 | 482.8 | 515 | 0.04546 | 0.04527
|  |  | NotConv |  |  |  | C: 3413 TEMPSSLT 345 3414 TEMP_SS_ 345 12 | 990
Open 3413 TEMPSSLT 345 3414 TEMP_SS_ 345 1
|  |  | 2156.3 | 2870.7 | -714.4 | L: 3593 SPGVALLY 138 13591 COTTONB_ 138 1 |  |  | 38.3 | 163.8 | 214 | 0.05822 | 0.06103
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2172.4 | 2884.5 | -712.1 | L: 3675 ROGERS1A 138 13430 SAND_TXU 138 1 |  |  | 312.7 | 440.3 | 478 | 0.05873 | -0.056
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2171.8 | 2901.7 | -729.9 | L: 86106 CUF-230 230 86107 CUF-138 138 1 |  |  | 0.1 | 299.7 | 400 | 0.13795 | 0.1378
|  |  | NotConv |  |  |  | C: 86104 CID-138 138 86106 CUF-230 230 16 | 684
Open 86104 CID-138 138 86106 CUF-230 230 1
|  |  | 2172.3 | 2902.4 | -730.1 | L: 86104 CID-138 138 86106 CUF-230 230 1 |  |  | 0 | 299.7 | 400 | 0.13795 | -0.1378
|  |  | NotConv |  |  |  | C: 86106 CUF-230 230 86107 CUF-138 138 16 | 688
Open 86106 CUF-230 230 86107 CUF-138 138 1
|  |  | 2216.5 | 2914.3 | -697.8 | L: 44100 BRAZOS__ 138 44280 FTBEND__ 138 09 |  |  | 127 | 182.1 | 220 | 0.02488 | -0.03144
|  |  | NotConv |  |  |  | Base Case
|  |  | 2170 | 2933.2 | -763.2 | L: 7343 L_GEORGE 138 7366 L_CHIEBR 138 1 |  |  | 131.3 | 198.1 | 219.9 | 0.03076 | -0.03058
|  |  | NotConv |  |  |  | C: 7524 L_SEWARD 138 7525 L_LEANDE 138 14 | 722
Open 7524 L_SEWARD 138 7525 L_LEANDE 138 1
|  |  | 2223.6 | 2936.8 | -713.2 | L: 3413 TEMPSSLT 345 3429 SANDOW__ 345 1 |  |  | 682.4 | 979 | 1072 | 0.1334 | -0.13019
|  |  | NotConv |  |  |  | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2221 | 2950 | -729 | L: 3415 TEMP_SS_ 138 3675 ROGERS1A 138 1 |  |  | 309.1 | 439.8 | 478 | 0.05884 | -0.056
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2215.9 | 2961.4 | -745.4 | L: 3592 WACOATCO 138 13591 COTTONB_ 138 1 |  |  | 33.4 | 162 | 214 | 0.05802 | -0.06103
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2293.5 | 2970.4 | -676.9 | L: 44010 W_A_P___ 138 44652 SIENNA05 138 05 |  |  | 372.6 | 435 | 478 | 0.02723 | 0.03155
|  |  | NotConv |  |  |  | C: KIOWA_5-KIOWAPP_5 & KIOWA_5-KIOWAPP_58 | 893
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 1
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 2
|  |  | 2329.2 | 2997.9 | -668.7 | L: 86104 CID-138 138 86105 CID-230 230 1 |  |  | 25.5 | 324.6 | 400 | 0.1284 | 0.13357
|  |  | NotConv |  |  |  | C: 86106 CUF-230 230 86107 CUF-138 138 16 | 688
Open 86106 CUF-230 230 86107 CUF-138 138 1
|  |  | 2243.1 | 3000.3 | -757.2 | L: 86106 CUF-230 230 86107 CUF-138 138 1 |  |  | 0.2 | 299.8 | 400 | 0.13359 | 0.13327
|  |  | NotConv |  |  |  | C: 86104 CID-138 138 86105 CID-230 230 16 | 683
Open 86104 CID-138 138 86105 CID-230 230 1
|  |  | 2284 | 3012.4 | -728.4 | L: 86104 CID-138 138 86105 CID-230 230 1 |  |  | 51.3 | 355.6 | 400 | 0.13324 | 0.13781
|  |  | NotConv |  |  |  | C: 86105 CID-230 230 86107 CUF-138 138 16 | 687
Open 86105 CID-230 230 86107 CUF-138 138 1
|  |  | 2284.5 | 3013.1 | -728.6 | L: 86105 CID-230 230 86107 CUF-138 138 1 |  |  | 51.3 | 353.9 | 400 | 0.13246 | -0.13781
|  |  | NotConv |  |  |  | C: 86104 CID-138 138 86105 CID-230 230 16 | 683
Open 86104 CID-138 138 86105 CID-230 230 1
|  |  | 2300.6 | 3026.7 | -726.1 | L: 1906 VENUS_S5 345 3405 THOUSE__ 345 1 |  |  | 578.7 | 926.1 | 1072 | 0.15099 | -0.16059
|  |  | NotConv |  |  |  | C: 1907 VENUS_N5 345 3405 THOUSE__ 345 11 | 623
Open 1907 VENUS_N5 345 3405 THOUSE__ 345 1
|  |  | 2319.8 | 3053.8 | -734 | L: 44020 ALIEF___ 138 44671 STAFRD09 138 09 |  |  | 167.1 | 246.2 | 309 | 0.03413 | -0.04481
|  |  | NotConv |  |  |  | Base Case
|  |  | 2320.4 | 3059.3 | -738.9 | L: 44010 W_A_P___ 138 44652 SIENNA05 138 05 |  |  | 298 | 395.8 | 478 | 0.04216 | 0.05605
|  |  | NotConv |  |  |  | C:H_O_C_-W_A_P__02 (44010-44180)[MSL &1] & H_O_C_-KA7 | 710
Open 44010 W_A_P___ 138 44651 SIENNA02 138 2
Open 44180 DEWALT__ 138 44691 TELVEW02 138 2
Open 44390 KARSTN__ 138 44692 TELVEW26 138 26
Open 47150 H_O_C___ 138 47170 CH_O_C__ 138 26
|  |  | 2318.6 | 3064.2 | -745.6 | L: 3413 TEMPSSLT 345 3429 SANDOW__ 345 1 |  |  | 656.6 | 966.2 | 1072 | 0.13355 | -0.13109
|  |  | NotConv |  |  |  | C: KIOWA_5-KIOWAPP_5 & KIOWA_5-KIOWAPP_58 | 893
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 1
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 2
|  |  | 2297.5 | 3065.8 | -768.4 | L: 44180 DEWALT__ 138 44691 TELVEW02 138 02 |  |  | 373.7 | 435.7 | 478 | 0.02697 | -0.03116
|  |  | NotConv |  |  |  | C: KIOWA_5-KIOWAPP_5 & KIOWA_5-KIOWAPP_58 | 893
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 1
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 2
|  |  | 2305 | 3092.9 | -787.9 | L: 3402 LAKE_CRK 345 3409 LAKE_CRK 345 2 |  |  | 318.2 | 866 | 1072 | 0.23766 | -0.24495
|  |  | NotConv |  |  |  | C: THOUSE__5-LAKE_CRK1_5 & THOUSE__5-AEP_PEC__59 | 245
Open 3405 THOUSE__ 345 3409 LAKE_CRK 345 1
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
|  |  | 2319.7 | 3093.8 | -774.2 | L: 7500 L_TURNER 138 7501 L_GOFORT 138 1 |  |  | 119.1 | 206 | 220.6 | 0.03747 | -0.03301
|  |  | NotConv |  |  |  | C: L_AUSTRO5_1Y-L_ZORN__5_2Y & L_ZORN__5_1Y-LYTTON348 | 518
Open 7040 L_AUSTRO 345 7045 L_ZORN__ 345 1
Open 7042 L_ZORN__ 345 9074 LYTTON34 345 1
|  |  | 2318.1 | 3101.1 | -783 | L: 47660 GARROT__ 138 47705 MIDTWN__ 138 90 |  |  | 133.8 | 208 | 247 | 0.03199 | 0.03634
|  |  | NotConv |  |  |  | Base Case
|  |  | 2327.9 | 3105.5 | -777.5 | L: 86105 CID-230 230 86107 CUF-138 138 1 |  |  | 28.6 | 310.4 | 400 | 0.12106 | -0.13357
|  |  | NotConv |  |  |  | C: 86104 CID-138 138 86106 CUF-230 230 16 | 684
Open 86104 CID-138 138 86106 CUF-230 230 1
|  |  | 2283.2 | 3107.6 | -824.4 | L: 86104 CID-138 138 86106 CUF-230 230 1 |  |  | 14.2 | 290.8 | 400 | 0.12115 | -0.13327
|  |  | NotConv |  |  |  | C: 86105 CID-230 230 86107 CUF-138 138 16 | 687
Open 86105 CID-230 230 86107 CUF-138 138 1
|  |  | 2290.8 | 3124.4 | -833.6 | L: 7084 L_GRAPMI 138 7087 L_CORONA 138 1 |  |  | 105.5 | 188.7 | 220.6 | 0.03631 | -0.03764
|  |  | NotConv |  |  |  | C: L_BUCHAN9_1Y-L_BURNET9_1Y & L_BURNET8_1Y-L_WIRTZ_8 | 552
Open 7092 L_BUCHAN 69.0 7097 L_BURNET 69.0 1
Open 7100 L_BURNET 138 7104 L_WIRTZ_ 138 1
|  |  | 2319.1 | 3139.8 | -820.7 | L: 1907 VENUS_N5 345 3405 THOUSE__ 345 1 |  |  | 553.5 | 909 | 1072 | 0.15328 | -0.16309
|  |  | NotConv |  |  |  | C: 1906 VENUS_S5 345 3405 THOUSE__ 345 11 | 615
Open 1906 VENUS_S5 345 3405 THOUSE__ 345 1
|  |  | 2297.5 | 3198.8 | -901.3 | L: 44180 DEWALT__ 138 44691 TELVEW02 138 02 |  |  | 373.7 | 435.7 | 478 | 0.02697 | -0.03116
|  |  | NotConv |  |  |  | C: 1690 VALLYSES 345 11690 KIOWA_5 345 11 | 332
Open 1690 VALLYSES 345 11690 KIOWA_5 345 1
|  |  | 2318.3 | 3220.7 | -902.4 | L: 44100 BRAZOS__ 138 44231 CFLEWLN_ 138 09 |  |  | 177 | 237.5 | 280 | 0.02611 | 0.03176
|  |  | NotConv |  |  |  | C:CEDARP-CENTER_97 (40000-40240) & CENTER-P_H_R__978 | 106
Open 40000 CEDARP__ 345 40240 CENTER__ 345 97
Open 40240 CENTER__ 345 42000 P_H_R___ 345 97
|  |  | 2318.5 | 3254.4 | -936 | L: 44100 BRAZOS__ 138 44231 CFLEWLN_ 138 09 |  |  | 158.8 | 234 | 280 | 0.03244 | 0.03773
|  |  | NotConv |  |  |  | C:OBRIEN-W_A_P__98 (44000-44500) & OBRIEN-W_A_P__998 | 111
Open 44000 W_A_P___ 345 44500 OBRIEN__ 345 98
Open 44000 W_A_P___ 345 44500 OBRIEN__ 345 99
|  |  | 2318.5 | 3254.4 | -936 | L: 44100 BRAZOS__ 138 44231 CFLEWLN_ 138 09 |  |  | 158.8 | 234 | 280 | 0.03244 | 0.03773
|  |  | NotConv |  |  |  | C:W_A_P_: Obrien Ckt. 98_98 (44500-44000) & Obrien8 | 172
Open 44000 W_A_P___ 345 44500 OBRIEN__ 345 98
Open 44000 W_A_P___ 345 44500 OBRIEN__ 345 99
|  |  | 2319 | 3281.2 | -962.2 | L: 3380 BIGBRN__ 345 3391 JEWETT_N 345 1 |  |  | 576.7 | 927 | 1072 | 0.15103 | -0.15246
|  |  | NotConv |  |  |  | C:WATERMILL-LIMESTONE9 | 346
Open 2427 WATMLL_W 345 2435 WATMLL_1 345 1
Open 2428 WATMLL_E 345 46020 LIMEST__ 345 1
Open 2435 WATMLL_1 345 46020 LIMEST__ 345 2
|  |  | 2317.5 | 3298.3 | -980.8 | L: 7065 L_DOBYVI 138 7084 L_GRAPMI 138 1 |  |  | 99.2 | 183.2 | 220.6 | 0.03622 | -0.03764
|  |  | NotConv |  |  |  | C: L_BUCHAN9_1Y-L_BURNET9_1Y & L_BURNET8_1Y-L_WIRTZ_8 | 552
Open 7092 L_BUCHAN 69.0 7097 L_BURNET 69.0 1
Open 7100 L_BURNET 138 7104 L_WIRTZ_ 138 1
|  |  | 2320 | 3349.2 | -1029.2 | L: 7064 L_LAMPAS 138 7065 L_DOBYVI 138 1 |  |  | 97.4 | 181.5 | 220.6 | 0.03622 | -0.03764
|  |  | NotConv |  |  |  | C: L_BUCHAN9_1Y-L_BURNET9_1Y & L_BURNET8_1Y-L_WIRTZ_8 | 552
Open 7092 L_BUCHAN 69.0 7097 L_BURNET 69.0 1
Open 7100 L_BURNET 138 7104 L_WIRTZ_ 138 1
|  |  | 2319.5 | 3390 | -1070.5 | L: 7084 L_GRAPMI 138 7087 L_CORONA 138 1 |  |  | 92.8 | 179.1 | 220.6 | 0.03718 | -0.03868
|  |  | NotConv |  |  |  | C: L_EBABSM8_1Y-L_BURNET8_1Y & L_BURNET9_1Y-L_BERTRA8 | 547
Open 7060 L_EBABSM 138 7100 L_BURNET 138 1
Open 7097 L_BURNET 69.0 7520 L_BERTRA 69.0 1
|  |  | 2319.9 | 3399.9 | -1079.9 | L: 3682 MILANO_M 138 3683 MINERVA1 138 1 |  |  | 59.3 | 161.5 | 214 | 0.04406 | -0.04539
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2320.3 | 3443.1 | -1122.8 | L: 1906 VENUS_S5 345 3405 THOUSE__ 345 1 |  |  | 615.8 | 904.8 | 1072 | 0.12454 | -0.1319
|  |  | NotConv |  |  |  | C:WATERMILL-LIMESTONE9 | 346
Open 2427 WATMLL_W 345 2435 WATMLL_1 345 1
Open 2428 WATMLL_E 345 46020 LIMEST__ 345 1
Open 2435 WATMLL_1 345 46020 LIMEST__ 345 2
|  |  | 2319.1 | 3458.3 | -1139.2 | L: 32 ROBERTSO 138 3682 MILANO_M 138 1 |  |  | 57.1 | 159.3 | 214 | 0.04405 | -0.04539
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2317.7 | 3478.9 | -1161.2 | L: 7288 L_WELLBR 138 7335 L_HOLATA 138 1 |  |  | 225.7 | 369.1 | 441 | 0.06186 | -0.06177
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 2317 | 3507 | -1190 | L: 3682 MILANO_M 138 3683 MINERVA1 138 1 |  |  | 71.9 | 162.5 | 214 | 0.0391 | -0.04018
|  |  | TDF_Sign |  |  |  | C: LAKE_CRK1_5-AEP_SS__5 & AEP_PEC__5-AEP_SS__59 | 247
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
Open 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1
|  |  | 2254.8 | 3513.3 | -1258.6 | L: 3591 WACOWOOD 138 3592 WACOATCO 138 1 |  |  | 18.7 | 134.3 | 214 | 0.05127 | -0.06103
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2317.6 | 3545.9 | -1228.3 | L: 3666 HUTTOSS1 138 3670 RNDRCKNE 138 1 |  |  | 54.7 | 226.8 | 332 | 0.07424 | -0.08716
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 2232.2 | 3551.7 | -1319.5 | L: 1906 VENUS_S5 345 11901 BRITNRD1 345 1 |  |  | 870.9 | 991.8 | 1072 | 0.05417 | 0.05623
|  |  | NotConv |  |  |  | C: VENUS_S5-LIGGETTA1_5 & VENUS_N5-LIGGETTA2_58 | 682
Open 1906 VENUS_S5 345 1921 LIGGETTA 345 1
Open 1907 VENUS_N5 345 1916 LIGGETTA 345 1
|  |  | 2320.6 | 3559.2 | -1238.6 | L: 7065 L_DOBYVI 138 7084 L_GRAPMI 138 1 |  |  | 86.8 | 172.8 | 220.6 | 0.03705 | -0.03868
|  |  | NotConv |  |  |  | C: L_EBABSM8_1Y-L_BURNET8_1Y & L_BURNET9_1Y-L_BERTRA8 | 547
Open 7060 L_EBABSM 138 7100 L_BURNET 138 1
Open 7097 L_BURNET 69.0 7520 L_BERTRA 69.0 1
|  |  | 2240.6 | 3573.1 | -1332.4 | L: 32 ROBERTSO 138 3682 MILANO_M 138 1 |  |  | 69.7 | 157.4 | 214 | 0.03913 | -0.04018
|  |  | LowSens |  |  |  | C: LAKE_CRK1_5-AEP_SS__5 & AEP_PEC__5-AEP_SS__59 | 247
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
Open 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1
|  |  | 2319.7 | 3593.7 | -1274 | L: 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1 |  |  | 136.6 | 729.7 | 1072 | 0.25568 | -0.2855
|  |  | NotConv |  |  |  | C: THOUSE__5-LAKE_CRK1_5 & THOUSE__5-AEP_PEC__59 | 245
Open 3405 THOUSE__ 345 3409 LAKE_CRK 345 1
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
|  |  | 2320.1 | 3601.8 | -1281.8 | L: 5915 SO_TEX__ 345 44200 HILLJE 345 1 |  |  | 868 | 1040.7 | 1125 | 0.07447 | 0.06301
|  |  | NotConv |  |  |  | C:DOW345-SO_TEX_18 (5915-42500) & DOW345-SO_TEX_277 | 830
Open 5915 SO_TEX__ 345 42500 DOW_____ 345 18
Open 5915 SO_TEX__ 345 42500 DOW_____ 345 27
|  |  | 2321 | 3608.7 | -1287.7 | L: 7064 L_LAMPAS 138 7065 L_DOBYVI 138 1 |  |  | 85 | 171 | 220.6 | 0.03705 | -0.03868
|  |  | NotConv |  |  |  | C: L_EBABSM8_1Y-L_BURNET8_1Y & L_BURNET9_1Y-L_BERTRA8 | 547
Open 7060 L_EBABSM 138 7100 L_BURNET 138 1
Open 7097 L_BURNET 69.0 7520 L_BERTRA 69.0 1
|  |  | 2323.1 | 3612.6 | -1289.5 | L: 3402 LAKE_CRK 345 3405 THOUSE__ 345 2 |  |  | 96.6 | 631.7 | 956 | 0.23036 | 0.25795
|  |  | NotConv |  |  |  | C: THOUSE__5-LAKE_CRK1_5 & THOUSE__5-AEP_PEC__59 | 245
Open 3405 THOUSE__ 345 3409 LAKE_CRK 345 1
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
|  |  | 2318.2 | 3625.7 | -1307.5 | L: 2410 NORWD_1T 345 2420 CHILSW1_ 345 1 |  |  | 1445.8 | 1556.4 | 1631 | 0.04773 | -0.05212
|  |  | NotConv |  |  |  | C:WATERMILL-SARGENT RD/WEST LEVEE9 | 348
Open 2398 WLEVEE1_ 345 2997 WATMLL_2 345 1
Open 2427 WATMLL_W 345 2946 SARGT1_5 345 1
Open 2427 WATMLL_W 345 2997 WATMLL_2 345 1
|  |  | 2308.4 | 3685.1 | -1376.7 | L: 3429 SANDOW__ 345 7040 L_AUSTRO 345 1 |  |  | 452.7 | 767.8 | 956 | 0.13647 | -0.13584
|  |  | NotConv |  |  |  | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2320.8 | 3766.5 | -1445.7 | L: 3668 RNDROCK1 138 3670 RNDRCKNE 138 1 |  |  | 15.7 | 137.9 | 214 | 0.05263 | 0.05298
|  |  | NotConv |  |  |  | C: JARREL-L_GABRIE9_1Y & L_GABRIE8_1Y-L_RIVERY8_1Y8 | 652
Open 7346 L_GABRIE 138 7347 L_RIVERY 138 1
Open 7346 L_GABRIE 138 7523 L_GLASSC 138 1
|  |  | 2317 | 3769.3 | -1452.3 | L: 3123 TRINDAD1 345 3133 RICHLND1 345 1 |  |  | 778.4 | 946.5 | 1072 | 0.07254 | -0.0745
|  |  | NotConv |  |  |  | C:WATERMILL-LIMESTONE9 | 346
Open 2427 WATMLL_W 345 2435 WATMLL_1 345 1
Open 2428 WATMLL_E 345 46020 LIMEST__ 345 1
Open 2435 WATMLL_1 345 46020 LIMEST__ 345 2
|  |  | 2198.6 | 3776.2 | -1577.6 | L: 44390 KARSTN__ 138 44692 TELVEW26 138 26 |  |  | 274.8 | 360.2 | 478 | 0.03883 | 0.05189
|  |  | NotConv |  |  |  | C:H_O_C_-W_A_P__02 (44010-44180)[MSL &1] & H_O_C_-W_7 | 709
Open 44010 W_A_P___ 138 44651 SIENNA02 138 2
Open 44180 DEWALT__ 138 44691 TELVEW02 138 2
Open 44010 W_A_P___ 138 44652 SIENNA05 138 5
Open 44081 BLURIG05 138 47150 H_O_C___ 138 5
|  |  | 2319.9 | 3790 | -1470.2 | L: 1907 VENUS_N5 345 3405 THOUSE__ 345 1 |  |  | 561.3 | 860.8 | 1072 | 0.12913 | -0.13437
|  |  | NotConv |  |  |  | C:WATERMILL-LIMESTONE9 | 346
Open 2427 WATMLL_W 345 2435 WATMLL_1 345 1
Open 2428 WATMLL_E 345 46020 LIMEST__ 345 1
Open 2435 WATMLL_1 345 46020 LIMEST__ 345 2
|  |  | 2144.2 | 3812.1 | -1667.9 | L: 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1 |  |  | 465.4 | 808.6 | 1072 | 0.16004 | -0.15862
|  |  | NotConv |  |  |  | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2323.6 | 3882.2 | -1558.6 | L: 7042 L_ZORN__ 345 9074 LYTTON34 345 1 |  |  | 526.8 | 905.1 | 1100 | 0.16281 | 0.14602
|  |  | NotConv |  |  |  | C: L_AUSTRO5_1Y-L_ZORN__5_2Y & L_ZORN__5_2Y-L_CLEASP8 | 519
Open 7040 L_AUSTRO 345 7045 L_ZORN__ 345 1
Open 7045 L_ZORN__ 345 7050 L_CLEASP 345 1
|  |  | 2189.3 | 3884.1 | -1694.9 | L: 5915 SO_TEX__ 345 44200 HILLJE 345 1 |  |  | 838.6 | 993.1 | 1125 | 0.07055 | 0.06534
|  |  | NotConv |  |  |  | C:ELMCRK-SO_TEX_2 (5133-5915) & SO_TEX-HILLJE_64 (7 | 882
Open 5133 ELMCREEK 345 5915 SO_TEX__ 345 2
Open 5915 SO_TEX__ 345 44200 HILLJE 345 64
|  |  | 2197.6 | 3907 | -1709.3 | L: 7084 L_GRAPMI 138 7087 L_CORONA 138 1 |  |  | 89 | 161.6 | 220.6 | 0.03304 | -0.03364
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2120.7 | 3943.4 | -1822.7 | L: 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1 |  |  | 432.3 | 774.5 | 1072 | 0.16134 | -0.15978
|  |  | NotConv |  |  |  | C: KIOWA_5-KIOWAPP_5 & KIOWA_5-KIOWAPP_58 | 893
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 1
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 2
|  |  | 2148.7 | 3970 | -1821.3 | L: 3413 TEMPSSLT 345 3414 TEMP_SS_ 345 1 |  |  | 279.3 | 712.2 | 1072 | 0.20148 | 0.20716
|  |  | NotConv |  |  |  | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2322.2 | 3985 | -1662.9 | L: 1906 VENUS_S5 345 3405 THOUSE__ 345 1 |  |  | 453.6 | 792.5 | 1072 | 0.14592 | -0.15343
|  |  | NotConv |  |  |  | C: BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N59 | 237
Open 3380 BIGBRN__ 345 3390 JEWETT_S 345 1
Open 3380 BIGBRN__ 345 3391 JEWETT_N 345 1
|  |  | 2305.4 | 4026.2 | -1720.7 | L: 1907 VENUS_N5 345 3405 THOUSE__ 345 1 |  |  | 616.5 | 859.5 | 1072 | 0.10539 | -0.11103
|  |  | NotConv |  |  |  | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2281 | 4029.4 | -1748.4 | L: 3688 JARRELL_ 138 7346 L_GABRIE 138 1 |  |  | 46.9 | 141.4 | 214 | 0.04142 | -0.04113
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2104.8 | 4080.9 | -1976.1 | L: 3413 TEMPSSLT 345 3414 TEMP_SS_ 345 1 |  |  | 244.5 | 672.7 | 1072 | 0.20345 | 0.20848
|  |  | NotConv |  |  |  | C: KIOWA_5-KIOWAPP_5 & KIOWA_5-KIOWAPP_58 | 893
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 1
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 2
|  |  | 2321.3 | 4084.7 | -1763.4 | L: 3436 WACO_W1_ 138 3591 WACOWOOD 138 1 |  |  | 45.7 | 111.2 | 214 | 0.02821 | -0.06103
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2274.1 | 4089.1 | -1815 | L: 3380 BIGBRN__ 345 3390 JEWETT_S 345 1 |  |  | 451.7 | 796.6 | 1072 | 0.15167 | -0.15317
|  |  | NotConv |  |  |  | C:WATERMILL-LIMESTONE9 | 346
Open 2427 WATMLL_W 345 2435 WATMLL_1 345 1
Open 2428 WATMLL_E 345 46020 LIMEST__ 345 1
Open 2435 WATMLL_1 345 46020 LIMEST__ 345 2
|  |  | 2292.9 | 4090.4 | -1797.4 | L: 44551 QUAIL02_ 138 44651 SIENNA02 138 02 |  |  | 437.1 | 497.2 | 561 | 0.02619 | -0.03034
|  |  | NotConv |  |  |  | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2303.2 | 4101.6 | -1798.5 | L: 7065 L_DOBYVI 138 7084 L_GRAPMI 138 1 |  |  | 82.7 | 158.7 | 220.6 | 0.03299 | -0.03364
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2285.7 | 4110.7 | -1824.9 | L: 7288 L_WELLBR 138 7335 L_HOLATA 138 1 |  |  | 237.5 | 353 | 441 | 0.05054 | -0.04981
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2112.9 | 4134.1 | -2021.2 | L: 44310 HAYES___ 138 44312 HAYES09_ 138 09 |  |  | 290.1 | 356.5 | 440 | 0.03143 | -0.03761
|  |  | NotConv |  |  |  | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2317.3 | 4134.2 | -1816.8 | L: 44020 ALIEF___ 138 44312 HAYES09_ 138 09 |  |  | 293.9 | 369.3 | 440 | 0.03255 | 0.03761
|  |  | NotConv |  |  |  | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2319.1 | 4158.5 | -1839.4 | L: 7064 L_LAMPAS 138 7065 L_DOBYVI 138 1 |  |  | 80.9 | 157.5 | 220.6 | 0.033 | -0.03364
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2319.6 | 4216.9 | -1897.4 | L: 1904 WEBB3_5 345 11901 BRITNRD1 345 1 |  |  | 835.2 | 960.8 | 1072 | 0.05414 | -0.05623
|  |  | NotConv |  |  |  | C: VENUS_S5-LIGGETTA1_5 & VENUS_N5-LIGGETTA2_58 | 682
Open 1906 VENUS_S5 345 1921 LIGGETTA 345 1
Open 1907 VENUS_N5 345 1916 LIGGETTA 345 1
|  |  | 2164.6 | 4217.6 | -2052.9 | L: 3422 KILL_SS_ 345 3423 KILL_SS_ 138 1 |  |  | 381 | 443 | 515 | 0.02866 | 0.03144
|  |  | LowSens |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2319.1 | 4232.1 | -1913 | L: 1906 VENUS_S5 345 3380 BIGBRN__ 345 1 |  |  | 867 | 965 | 1072 | 0.04224 | -0.04285
|  |  | NotConv |  |  |  | C: TRINDAD1_5-RICHLND1_5 & TRINDAD2_5-RICHLND2_59 | 231
Open 3123 TRINDAD1 345 3133 RICHLND1 345 1
Open 3124 TRINDAD2 345 3134 RICHLND2 345 1
|  |  | 2157.7 | 4265.9 | -2108.1 | L: 7042 L_ZORN__ 345 9074 LYTTON34 345 1 |  |  | 536.8 | 856.5 | 1100 | 0.14819 | 0.13038
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-L_ZORN__5_28 | 664
Open 7040 L_AUSTRO 345 7045 L_ZORN__ 345 1
Open 7040 L_AUSTRO 345 7048 L_GARFIE 345 1
|  |  | 2157.7 | 4265.9 | -2108.1 | L: 7042 L_ZORN__ 345 9074 LYTTON34 345 1 |  |  | 536.8 | 856.5 | 1100 | 0.14819 | 0.13038
|  |  | NotConv |  |  |  | C: L_AUSTRO5_1Y-L_ZORN__5_2Y & L_AUSTRO5_1Y-L_GARFIE8 | 517
Open 7040 L_AUSTRO 345 7045 L_ZORN__ 345 1
Open 7040 L_AUSTRO 345 7048 L_GARFIE 345 1
|  |  | 2296.4 | 4292.1 | -1995.7 | L: 3123 TRINDAD1 345 3133 RICHLND1 345 1 |  |  | 805.6 | 935 | 1072 | 0.05635 | -0.05795
|  |  | NotConv |  |  |  | C: VENUS_S5-BIGBRN__5 & VENUS_N5-BIGBRN__59 | 62
Open 1906 VENUS_S5 345 3380 BIGBRN__ 345 1
Open 1907 VENUS_N5 345 3380 BIGBRN__ 345 1
|  |  | 2177 | 4298.7 | -2121.7 | L: 3594 MCGREG_T 138 13662 TEMPELMC 138 1 |  |  | 64.8 | 135.8 | 214 | 0.0326 | -0.03423
|  |  | NotConv |  |  |  | C: LAKE_CRK1_5-AEP_SS__5 & AEP_PEC__5-AEP_SS__59 | 247
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
Open 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1
|  |  | 2145.9 | 4321.8 | -2176 | L: 7335 L_HOLATA 138 9217 HOWARDLN 138 1 |  |  | 205.1 | 340.9 | 480 | 0.06329 | -0.064
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 2226.4 | 4338.4 | -2112 | L: 3665 PFLGRVIL 138 3666 HUTTOSS1 138 1 |  |  | 54.1 | 131.6 | 214 | 0.03478 | 0.04032
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2185.3 | 4346.8 | -2161.4 | L: 7310 L_SIMGID 138 7324 L_BUTLER 138 1 |  |  | 77.2 | 146.8 | 220.6 | 0.03185 | 0.03278
|  |  | NotConv |  |  |  | C: L_SIMGID8_1Y-L_BASTCI8_1Y & L_SIMGID8_1Y-L_AUSTRO8 | 621
Open 7310 L_SIMGID 138 7322 L_BASTCI 138 1
Open 7310 L_SIMGID 138 7328 L_AUSTRO 138 1
|  |  | 2249.1 | 4351.7 | -2102.6 | L: 47310 JENETA__ 138 47461 WESTWD3_ 138 25 |  |  | 324.6 | 396.5 | 478 | 0.03193 | 0.03406
|  |  | NotConv |  |  |  | C:OBRIEN-W_A_P__98 (44000-44500) & OBRIEN-W_A_P__998 | 111
Open 44000 W_A_P___ 345 44500 OBRIEN__ 345 98
Open 44000 W_A_P___ 345 44500 OBRIEN__ 345 99
|  |  | 2249.1 | 4351.7 | -2102.6 | L: 47310 JENETA__ 138 47461 WESTWD3_ 138 25 |  |  | 324.6 | 396.5 | 478 | 0.03193 | 0.03406
|  |  | NotConv |  |  |  | C:W_A_P_: Obrien Ckt. 98_98 (44500-44000) & Obrien8 | 172
Open 44000 W_A_P___ 345 44500 OBRIEN__ 345 98
Open 44000 W_A_P___ 345 44500 OBRIEN__ 345 99
|  |  | 2191.2 | 4412.9 | -2221.6 | L: 3640 SALADO1_ 138 3688 JARRELL_ 138 1 |  |  | 33.6 | 122.6 | 214 | 0.04061 | -0.04113
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2150.6 | 4437 | -2286.4 | L: 3666 HUTTOSS1 138 3670 RNDRCKNE 138 1 |  |  | 38.8 | 174.3 | 332 | 0.06303 | -0.0681
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2242.4 | 4462.9 | -2220.5 | L: 7310 L_SIMGID 138 7324 L_BUTLER 138 1 |  |  | 73.5 | 144.9 | 220.6 | 0.03186 | 0.03278
|  |  | NotConv |  |  |  | C: L_SIMGID8_1Y-L_AUSTRO8_1Y & L_BASTCI8_1Y-L_WEBBER8 | 624
Open 7310 L_SIMGID 138 7328 L_AUSTRO 138 1
Open 7322 L_BASTCI 138 7329 L_WEBBER 138 1
|  |  | 2322.3 | 4475.7 | -2153.4 | L: 44551 QUAIL02_ 138 44651 SIENNA02 138 02 |  |  | 411.6 | 475 | 561 | 0.02731 | -0.03116
|  |  | NotConv |  |  |  | C: KIOWA_5-KIOWAPP_5 & KIOWA_5-KIOWAPP_58 | 893
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 1
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 2
|  |  | 2315.8 | 4486.4 | -2170.7 | L: 44310 HAYES___ 138 44312 HAYES09_ 138 09 |  |  | 261.2 | 339.1 | 440 | 0.03361 | -0.03856
|  |  | NotConv |  |  |  | C: KIOWA_5-KIOWAPP_5 & KIOWA_5-KIOWAPP_58 | 893
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 1
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 2
|  |  | 2266.8 | 4486.5 | -2219.7 | L: 44020 ALIEF___ 138 44312 HAYES09_ 138 09 |  |  | 265 | 340.3 | 440 | 0.0332 | 0.03856
|  |  | NotConv |  |  |  | C: KIOWA_5-KIOWAPP_5 & KIOWA_5-KIOWAPP_58 | 893
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 1
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 2
|  |  | 2318 | 4515.8 | -2197.8 | L: 3666 HUTTOSS1 138 3696 HUTTOSS_ 345 1 |  |  | 188.5 | 416.9 | 686 | 0.09853 | 0.1467
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 1776.8 | 4534.9 | -2758.1 | L: 7044 L_MARION 345 7178 L_MARION 138 1 |  |  | 410.8 | 478 | 478 | 0.0378 | 0.03015
[7 empty] | C: L_ZORN__5_1Y-L_MARION5_1Y & L_MARION5_1Y-L_CLEASP8 | 524
Open 7042 L_ZORN__ 345 7044 L_MARION 345 1
Open 7044 L_MARION 345 7050 L_CLEASP 345 1
|  |  | 2302.3 | 4555.1 | -2252.8 | L: 3283 BUTLERMT 138 3392 JEWETT1_ 138 1 |  |  | 69.1 | 139 | 214 | 0.03037 | -0.03143
|  |  | NotConv |  |  |  | C: BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N59 | 237
Open 3380 BIGBRN__ 345 3390 JEWETT_S 345 1
Open 3380 BIGBRN__ 345 3391 JEWETT_N 345 1
|  |  | 2270.4 | 4555.2 | -2284.8 | L: 3688 JARRELL_ 138 7346 L_GABRIE 138 1 |  |  | 20.9 | 111.6 | 214 | 0.03995 | -0.04249
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 2313.9 | 4591.3 | -2277.4 | L: 7040 L_AUSTRO 345 7045 L_ZORN__ 345 1 |  |  | 425.8 | 798.8 | 1103.1 | 0.16118 | -0.1462
|  |  | NotConv |  |  |  | C: L_ZORN__5_1Y-LYTTON34 & L_GARFIE5_1Y-LYTTON348 | 526
Open 7042 L_ZORN__ 345 9074 LYTTON34 345 1
Open 7048 L_GARFIE 345 9074 LYTTON34 345 1
|  |  | 2305.3 | 4595.6 | -2290.3 | L: 7040 L_AUSTRO 345 13429 SAND_TXU 345 2 |  |  | 448.7 | 761.4 | 1072 | 0.13561 | 0.13505
|  |  | NotConv |  |  |  | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2320.1 | 4608.6 | -2288.5 | L: 44081 BLURIG05 138 47150 H_O_C___ 138 05 |  |  | 215.3 | 313.4 | 478 | 0.04229 | 0.05605
|  |  | NotConv |  |  |  | C:H_O_C_-W_A_P__02 (44010-44180)[MSL &1] & H_O_C_-KA7 | 710
Open 44010 W_A_P___ 138 44651 SIENNA02 138 2
Open 44180 DEWALT__ 138 44691 TELVEW02 138 2
Open 44390 KARSTN__ 138 44692 TELVEW26 138 26
Open 47150 H_O_C___ 138 47170 CH_O_C__ 138 26
|  |  | 2302.1 | 4636 | -2333.9 | L: 44010 W_A_P___ 138 44342 IMPERL05 138 05 |  |  | 385.3 | 445.6 | 526 | 0.02617 | 0.03052
|  |  | NotConv |  |  |  | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2266.8 | 4670.9 | -2404 | L: 3412 TEMP_PEC 345 3420 TEMP_PEC 138 1 |  |  | 322.3 | 547.2 | 750 | 0.09919 | 0.09424
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2318.7 | 4672 | -2353.3 | L: 139 LAKEBELT 138 3610 BELTON1_ 138 1 |  |  | 13.3 | 116.9 | 237 | 0.04468 | -0.0479
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2318.4 | 4698.3 | -2379.8 | L: 3650 ELGIN_SS 138 7324 L_BUTLER 138 1 |  |  | 65.6 | 139.7 | 220 | 0.03198 | -0.03278
|  |  | NotConv |  |  |  | C: L_SIMGID8_1Y-L_BASTCI8_1Y & L_SIMGID8_1Y-L_AUSTRO8 | 621
Open 7310 L_SIMGID 138 7322 L_BASTCI 138 1
Open 7310 L_SIMGID 138 7328 L_AUSTRO 138 1
|  |  | 2262.1 | 4698.4 | -2436.3 | L: 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1 |  |  | 255.4 | 652.1 | 1072 | 0.17533 | -0.18031
|  |  | NotConv |  |  |  | C: VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N58 | 985
Open 1906 VENUS_S5 345 1939 MDLTHELP 345 1
Open 1907 VENUS_N5 345 1940 MDLTHELP 345 1
|  |  | 2321 | 4709.5 | -2388.5 | L: 44551 QUAIL02_ 138 44651 SIENNA02 138 02 |  |  | 379.5 | 445.1 | 561 | 0.02823 | -0.03661
|  |  | NotConv |  |  |  | C:CEDARP-CENTER_97 (40000-40240) & CENTER-P_H_R__978 | 106
Open 40000 CEDARP__ 345 40240 CENTER__ 345 97
Open 40240 CENTER__ 345 42000 P_H_R___ 345 97
|  |  | 2319.8 | 4732.6 | -2412.8 | L: 44390 KARSTN__ 138 44692 TELVEW26 138 26 |  |  | 224.6 | 316.6 | 478 | 0.03966 | 0.05189
|  |  | NotConv |  |  |  | C:H_O_C_-W_A_P__02 (44180-47150)[MSL &1] & H_O_C_-W_7 | 708
Open 44010 W_A_P___ 138 44652 SIENNA05 138 5
Open 44081 BLURIG05 138 47150 H_O_C___ 138 5
Open 44082 BLURIG02 138 44180 DEWALT__ 138 2
Open 44082 BLURIG02 138 47150 H_O_C___ 138 2
|  |  | 2320.9 | 4741.5 | -2420.6 | L: 7192 L_SANMAR 138 7502 L_KYLE__ 138 1 |  |  | 245.2 | 352.7 | 441.2 | 0.04632 | 0.04035
|  |  | NotConv |  |  |  | C: L_AUSTRO5_1Y-L_ZORN__5_2Y & L_ZORN__5_1Y-LYTTON348 | 518
Open 7040 L_AUSTRO 345 7045 L_ZORN__ 345 1
Open 7042 L_ZORN__ 345 9074 LYTTON34 345 1
|  |  | 2318.9 | 4764.5 | -2445.6 | L: 3279 LONGLKTA 138 3283 BUTLERMT 138 1 |  |  | 62.8 | 133.2 | 214 | 0.03036 | -0.03143
|  |  | NotConv |  |  |  | C: BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N59 | 237
Open 3380 BIGBRN__ 345 3390 JEWETT_S 345 1
Open 3380 BIGBRN__ 345 3391 JEWETT_N 345 1
|  |  | 2319.7 | 4772 | -2452.3 | L: 7334 L_MCNEIL 138 7336 L_GILLCR 138 1 |  |  | 68.5 | 271.1 | 493 | 0.08734 | 0.08829
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 2319 | 4779.9 | -2460.9 | L: 3380 BIGBRN__ 345 3390 JEWETT_S 345 1 |  |  | 240.3 | 641.6 | 1072 | 0.17306 | -0.17424
|  |  | NotConv |  |  |  | C: VENUS_S5-THOUSE__5 & VENUS_N5-THOUSE__59 | 61
Open 1906 VENUS_S5 345 3405 THOUSE__ 345 1
Open 1907 VENUS_N5 345 3405 THOUSE__ 345 1
|  |  | 2320.7 | 4797.8 | -2477.2 | L: 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1 |  |  | 226.8 | 639.5 | 1072 | 0.17787 | -0.1814
|  |  | NotConv |  |  |  | C: KIOWA_5-KIOWAPP_5 & KIOWA_5-KIOWAPP_58 | 893
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 1
Open 11690 KIOWA_5 345 11697 KIOWAPP_ 345 2
|  |  | 2318.4 | 4814.4 | -2496 | L: 3650 ELGIN_SS 138 7324 L_BUTLER 138 1 |  |  | 61.8 | 136 | 220 | 0.03198 | -0.03278
|  |  | NotConv |  |  |  | C: L_SIMGID8_1Y-L_AUSTRO8_1Y & L_BASTCI8_1Y-L_WEBBER8 | 624
Open 7310 L_SIMGID 138 7328 L_AUSTRO 138 1
Open 7322 L_BASTCI 138 7329 L_WEBBER 138 1
|  |  | 2320.1 | 4842.5 | -2522.4 | L: 7060 L_EBABSM 138 7100 L_BURNET 138 1 |  |  | 74.9 | 140.8 | 220.6 | 0.02839 | -0.03044
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 2318 | 4847 | -2529.1 | L: 1907 VENUS_N5 345 3380 BIGBRN__ 345 1 |  |  | 830.2 | 935.6 | 1072 | 0.04547 | -0.04523
|  |  | NotConv |  |  |  | C: TRINDAD1_5-RICHLND1_5 & TRINDAD2_5-RICHLND2_59 | 231
Open 3123 TRINDAD1 345 3133 RICHLND1 345 1
Open 3124 TRINDAD2 345 3134 RICHLND2 345 1
|  |  | 2320.9 | 4879.8 | -2558.8 | L: 44310 HAYES___ 138 44312 HAYES09_ 138 09 |  |  | 213.6 | 296.2 | 440 | 0.03558 | -0.04539
|  |  | NotConv |  |  |  | C:CEDARP-CENTER_97 (40000-40240) & CENTER-P_H_R__978 | 106
Open 40000 CEDARP__ 345 40240 CENTER__ 345 97
Open 40240 CENTER__ 345 42000 P_H_R___ 345 97
|  |  | 2320.9 | 4879.8 | -2558.9 | L: 44020 ALIEF___ 138 44312 HAYES09_ 138 09 |  |  | 217.1 | 299.5 | 440 | 0.03551 | 0.04539
|  |  | NotConv |  |  |  | C:CEDARP-CENTER_97 (40000-40240) & CENTER-P_H_R__978 | 106
Open 40000 CEDARP__ 345 40240 CENTER__ 345 97
Open 40240 CENTER__ 345 42000 P_H_R___ 345 97
|  |  | 2319.4 | 4887.6 | -2568.2 | L: 7040 L_AUSTRO 345 7045 L_ZORN__ 345 1 |  |  | 435.8 | 781.5 | 1103.1 | 0.14905 | -0.13528
|  |  | NotConv |  |  |  | C: L_ZORN__5_1Y-L_MARION5_1Y & L_ZORN__5_1Y-LYTTON348 | 523
Open 7042 L_ZORN__ 345 7044 L_MARION 345 1
Open 7042 L_ZORN__ 345 9074 LYTTON34 345 1
|  |  | 2315.9 | 4899.5 | -2583.7 | L: 3425 BELLCTY_ 138 3640 SALADO1_ 138 1 |  |  | 23.3 | 110.6 | 214 | 0.03771 | -0.04113
|  |  | NotConv |  |  |  | C: AEPSSLT__5-SANDOW__5 & AEP_SS__5-SANDOW__59 | 250
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3414 TEMP_SS_ 345 3429 SANDOW__ 345 1
|  |  | 2320.6 | 4914.7 | -2594.1 | L: 7042 L_ZORN__ 345 7044 L_MARION 345 1 |  |  | 442.6 | 800.3 | 1103.1 | 0.15414 | -0.13244
|  |  | NotConv |  |  |  | C: L_ZORN__5_2Y-L_CLEASP5_1Y & L_CLEASP5_1Y-L_RIONOG8 | 539
Open 7045 L_ZORN__ 345 7050 L_CLEASP 345 1
Open 7050 L_CLEASP 345 7051 L_RIONOG 345 2
|  |  | 2321 | 4926.4 | -2605.4 | L: 3640 SALADO1_ 138 3688 JARRELL_ 138 1 |  |  | 14.4 | 99 | 214 | 0.03644 | -0.04249
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 2320.8 | 4952 | -2631.2 | L: 44010 W_A_P___ 138 44342 IMPERL05 138 05 |  |  | 263.6 | 353.2 | 526 | 0.0386 | 0.05145
|  |  | NotConv |  |  |  | C:H_O_C_-W_A_P__02 (44010-44180)[MSL &1] & H_O_C_-W_7 | 709
Open 44010 W_A_P___ 138 44651 SIENNA02 138 2
Open 44180 DEWALT__ 138 44691 TELVEW02 138 2
Open 44010 W_A_P___ 138 44652 SIENNA05 138 5
Open 44081 BLURIG05 138 47150 H_O_C___ 138 5
|  |  | 2319.3 | 4982.3 | -2662.9 | L: 7060 L_EBABSM 138 7063 L_NARUNA 138 1 |  |  | 71.6 | 137.3 | 221 | 0.02834 | 0.03044
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 2319.4 | 4982.7 | -2663.3 | L: 7198 L_LEHIGH 138 7502 L_KYLE__ 138 1 |  |  | 234.8 | 342.3 | 440 | 0.04636 | -0.04035
|  |  | NotConv |  |  |  | C: L_AUSTRO5_1Y-L_ZORN__5_2Y & L_ZORN__5_1Y-LYTTON348 | 518
Open 7040 L_AUSTRO 345 7045 L_ZORN__ 345 1
Open 7042 L_ZORN__ 345 9074 LYTTON34 345 1
|  |  | 2320 | 4986 | -2666 | L: 3593 SPGVALLY 138 3594 MCGREG_T 138 1 |  |  | 48.4 | 120.8 | 214 | 0.0312 | -0.03294
|  |  | NotConv |  |  |  | C: LAKE_CRK1_5-AEP_SS__5 & AEP_PEC__5-AEP_SS__59 | 247
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
Open 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1
Note on A11: PTI: Exporting Subsystem
Note on B11: PTI: Importing Subsystem
Note on C11: PTI: Maximum Test Level
Note on D11: PTI: AC First Contingency Incremental Transfer Capability
Note on E11: PTI: DC First Contingency Incremental Transfer Capability
Note on F11: PTI: Difference between AC FCITC and DC FCITC
Note on G11: PTI: Branch, Flowgate or Interface
Note on H11: PTI: Limiting Contingency. Review MUST options for reporting options
Note on I11: PTI: Contingency Index
Note on J11: PTI: MW Flow before the transfer
Note on K11: PTI: MW Flow after the transfer
Note on L11: PTI: Rating (Base case or Contingent)
Note on M11: PTI: AC Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case
Note on N11: PTI: DC Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case

## N-S
AC FCITC MULTIPLE TRANSFER REPORT
PSS(tm)MUST 8.1.1 -- Managing and Utilizing System Transmission -- MON, JUL 27 2009 17:54
10SUM1 -2010 SUMMER ON-PEAK BASE CASE - ERCOT SSWG PASS 8
UPDATED 07/01/2009 - ERCOT PSSE VER 30.0 CSC CONS. DISPATCH
Case.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\Annual_2010_Basecase_v2_HH_adjusted_v29.sav
Subsys.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\MUST_SUBfile.sub
Monit.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\alltx.mon
Contin.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\ERCOT_CON_File_MUST_05292009_modified_no_D_no_openBus_no_singleline.con
Exclud.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\MUST_Exclude_List_08.exc
Reporting the first 500 violations per transfer | To | Transfer Level | AC FCITC | DC FCITC | Delta FCITC | Limiting Constraint | Contingency | Ncon | PreShift | PostShift | Rating | AC TDF | DC TDF
NORTH | SOUTH_I | 5000 | -1009.9 | -1153.5 | 143.6 | L: 818 OLINGER 138 968 BENDAVIS 138 1 |  |  | 247.3 | 218 | 218 | 0.02896 | 0.03174
[7 empty] | C:OLINGER-SWINDELL & OLINGER-FIREWHEEL & ELMGROVE-BE8 | 327
Open 812 SWINDELL 138 818 OLINGER 138 1
Open 818 OLINGER 138 821 FIREWHEE 138 1
Open 855 ELMGROVE 138 968 BENDAVIS 138 1
|  |  | 2832.6 | 2801.8 | 30.8 | L: 3436 WACO_W1_ 138 3591 WACOWOOD 138 1 |  |  | 45.7 | 214 | 214 | 0.0594 | 0.06378
[7 empty] | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2993.3 | 2921.8 | 71.5 | L: 3650 ELGIN_SS 138 13430 SAND_TXU 138 1 |  |  | 80.9 | 213.6 | 214 | 0.04431 | -0.04521
[7 empty] | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 3058.6 | 3348.6 | -289.9 | L: 3591 WACOWOOD 138 3592 WACOATCO 138 1 |  |  | 18.7 | 194.4 | 214 | 0.05745 | 0.06378
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 3761.4 | 3622 | 139.4 | L: 44645 SNGLTN_3 345 45500 T_H_W___ 345 98 |  |  | 914.9 | 1438.1 | 1450 | 0.1391 | 0.14219
|  |  | NotConv |  |  |  | C:SNGLTN - TOMBAL_74 (44645-46500) & ROANS - KING_757 | 984
Open 40600 ROANS___ 345 45972 KUYDAL75 345 75
Open 40900 KING____ 345 45972 KUYDAL75 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 3666.6 | 3667.2 | -0.6 | L: 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1 |  |  | 141.6 | 1064.2 | 1072 | 0.25164 | 0.305
|  |  | NotConv |  |  |  | C: 3405 THOUSE__ 345 3412 TEMP_PEC 345 12 | 967
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
|  |  | 3652.1 | 3697.7 | -45.7 | L: 3402 LAKE_CRK 345 3405 THOUSE__ 345 2 |  |  | 96.6 | 956.1 | 956 | 0.23534 | -0.26507
[7 empty] | C: THOUSE__5-LAKE_CRK1_5 & THOUSE__5-AEP_PEC__59 | 245
Open 3405 THOUSE__ 345 3409 LAKE_CRK 345 1
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
|  |  | 3717.1 | 3717.7 | -0.6 | L: 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1 |  |  | 136.6 | 1063 | 1072 | 0.24923 | 0.30073
|  |  | NotConv |  |  |  | C: THOUSE__5-LAKE_CRK1_5 & THOUSE__5-AEP_PEC__59 | 245
Open 3405 THOUSE__ 345 3409 LAKE_CRK 345 1
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
|  |  | 3752.5 | 3747.3 | 5.2 | L: 3668 RNDROCK1 138 3670 RNDRCKNE 138 1 |  |  | 106.9 | 213.8 | 214 | 0.02849 | -0.08639
[7 empty] | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 3904.5 | 3785.8 | 118.7 | L: 3405 THOUSE__ 345 3412 TEMP_PEC 345 1 |  |  | 140.3 | 1072.5 | 1072 | 0.23875 | 0.29002
[7 empty] | C: 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 12 | 976
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 3968.6 | 3850.2 | 118.4 | L: 173 CRAWFORD 138 177 BOSQUE 138 1 |  |  | 47.8 | 237.2 | 237 | 0.04774 | -0.04938
[7 empty] | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 3875.3 | 3872.2 | 3.2 | L: 3415 TEMP_SS_ 138 3420 TEMP_PEC 138 1 |  |  | 153.6 | 468 | 493 | 0.08112 | -0.16394
|  |  | NotConv |  |  |  | C: LAKE_CRK1_5-AEP_SS__5 & AEP_PEC__5-AEP_SS__59 | 247
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
Open 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1
|  |  | 3835.4 | 3876.7 | -41.3 | L: 3592 WACOATCO 138 13591 COTTONB_ 138 1 |  |  | 33.4 | 213.9 | 214 | 0.04705 | 0.06378
[7 empty] | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 3959.3 | 3963.5 | -4.2 | L: 3593 SPGVALLY 138 13591 COTTONB_ 138 1 |  |  | 38.3 | 217.1 | 214 | 0.04517 | -0.06378
|  |  | TDF_Sign |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4075.7 | 4035.1 | 40.6 | L: 165 WINDSORS 138 173 CRAWFORD 138 1 |  |  | 38.7 | 237.4 | 237 | 0.04875 | -0.04938
[7 empty] | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4002.2 | 4059.3 | -57 | L: 3593 SPGVALLY 138 3594 MCGREG_T 138 1 |  |  | 44 | 214 | 214 | 0.04248 | 0.06378
[7 empty] | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4130.3 | 4099.9 | 30.4 | L: 3668 RNDROCK1 138 3670 RNDRCKNE 138 1 |  |  | 3.2 | 213.5 | 214 | 0.05093 | -0.05187
[7 empty] | C: 7334 L_MCNEIL 138 7336 L_GILLCR 138 14 | 640
Open 7334 L_MCNEIL 138 7336 L_GILLCR 138 1
|  |  | 4101.8 | 4102.4 | -0.6 | L: 3594 MCGREG_T 138 13662 TEMPELMC 138 1 |  |  | 60.4 | 209.8 | 214 | 0.03643 | 0.06732
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4307.5 | 4108.5 | 199.1 | L: 3666 HUTTOSS1 138 3670 RNDRCKNE 138 1 |  |  | 54.7 | 332.1 | 332 | 0.06439 | 0.08639
[7 empty] | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 4069.8 | 4113.3 | -43.5 | L: 3412 TEMP_PEC 345 3420 TEMP_PEC 138 1 |  |  | 167.3 | 757.1 | 750 | 0.14492 | 0.15256
|  |  | TDF_Sign |  |  |  | C: LAKE_CRK1_5-AEP_SS__5 & AEP_PEC__5-AEP_SS__59 | 247
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
Open 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1
|  |  | 4448.4 | 4177.9 | 270.5 | L: 3407 ELM_MOTT 138 3575 WACONCST 138 1 |  |  | 189.3 | 326 | 326 | 0.03073 | 0.03176
[7 empty] | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4154.4 | 4184.3 | -29.9 | L: 3413 TEMPSSLT 345 3414 TEMP_SS_ 345 1 |  |  | 106 | 1071.6 | 1072 | 0.23242 | -0.24294
[7 empty] | C: Contingency>T9899_C8 | 915
Open 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99
Open 44645 SNGLTN_3 345 45500 T_H_W___ 345 98
|  |  | 4154.4 | 4184.3 | -29.9 | L: 3413 TEMPSSLT 345 3414 TEMP_SS_ 345 1 |  |  | 106 | 1071.6 | 1072 | 0.23242 | -0.24294
[7 empty] | C:SNGLTN - T_H_W__98 (44645-45500) & SNGLTN - OBRIEN8 | 112
Open 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99
Open 44645 SNGLTN_3 345 45500 T_H_W___ 345 98
|  |  | 4236.3 | 4200.2 | 36.1 | L: 161 MCGREGOR 138 165 WINDSORS 138 1 |  |  | 30.7 | 236.5 | 237 | 0.0486 | -0.04938
[7 empty] | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4060.4 | 4249 | -188.7 | L: 3413 TEMPSSLT 345 3414 TEMP_SS_ 345 1 |  |  | 110.7 | 1033.6 | 1072 | 0.2273 | -0.23651
|  |  | NotConv |  |  |  | C:SNGLTN - TOMBAL_74 (44645-46500) & ROANS - KING_757 | 984
Open 40600 ROANS___ 345 45972 KUYDAL75 345 75
Open 40900 KING____ 345 45972 KUYDAL75 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 4463 | 4311.7 | 151.3 | L: 137 MOODY 138 161 MCGREGOR 138 1 |  |  | 25.4 | 237 | 237 | 0.04743 | -0.04938
[7 empty] | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4145.3 | 4339.2 | -193.9 | L: 3610 BELTON1_ 138 13610 BELTONSW 138 1 |  |  | 199.6 | 326.2 | 326 | 0.03053 | 0.03034
[7 empty] | C: AEPSSLT__5-SANDOW__5 & AEPSSLT__5-SALADOSS_59 | 248
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3413 TEMPSSLT 345 3699 SALADOSS 345 1
|  |  | 4362 | 4391.2 | -29.2 | L: 137 MOODY 138 141 MOFFAT 138 1 |  |  | 21.5 | 234.2 | 237 | 0.04876 | 0.04938
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4664.5 | 4460.3 | 204.2 | L: 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99 |  |  | 757.9 | 1450.3 | 1450 | 0.14842 | -0.15161
[7 empty] | C:SNGLTN - TOMBAL_74 (44645-46500) & ROANS - KING_757 | 984
Open 40600 ROANS___ 345 45972 KUYDAL75 345 75
Open 40900 KING____ 345 45972 KUYDAL75 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 4519.7 | 4491.3 | 28.4 | L: 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1 |  |  | 215 | 1072.1 | 1072 | 0.18965 | 0.28133
[7 empty] | C: 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 12 | 988
Open 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1
|  |  | 4467 | 4498.7 | -31.7 | L: 3668 RNDROCK1 138 3670 RNDRCKNE 138 1 |  |  | 34.3 | 213.8 | 214 | 0.04018 | -0.04003
[7 empty] | C:AUSTROP1 & AUSTROP26 | 723
Open 7328 L_AUSTRO 138 9040 AUSTROP 345 1
Open 7328 L_AUSTRO 138 9040 AUSTROP 345 2
|  |  | 4702 | 4519.1 | 182.9 | L: 1690 VALLYSES 345 2373 ANNASW_5 345 1 |  |  | 1632.8 | 1792.6 | 1793 | 0.03398 | 0.03406
[7 empty] | C: FARMVLSW_5-VAL_STH_5 & VAL_STH_5-ANNASW_59 | 321
Open 1685 FARMVLSW 345 1729 VAL_STH_ 345 1
Open 1729 VAL_STH_ 345 2373 ANNASW_5 345 1
|  |  | 4687.2 | 4534.6 | 152.5 | L: 139 LAKEBELT 138 141 MOFFAT 138 1 |  |  | 14.4 | 237.2 | 237 | 0.04754 | -0.04938
[7 empty] | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4586.5 | 4618.6 | -32.1 | L: 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1 |  |  | 328.8 | 1077.4 | 1072 | 0.16323 | 0.30321
|  |  | NotConv |  |  |  | C: 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 12 | 976
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4795.9 | 4701.5 | 94.4 | L: 3666 HUTTOSS1 138 3670 RNDRCKNE 138 1 |  |  | 93.8 | 331.8 | 332 | 0.04962 | 0.05187
[7 empty] | C: 7334 L_MCNEIL 138 7336 L_GILLCR 138 14 | 640
Open 7334 L_MCNEIL 138 7336 L_GILLCR 138 1
|  |  | 4916.8 | 4756.1 | 160.7 | L: 3425 BELLCTY_ 138 3640 SALADO1_ 138 1 |  |  | 25.6 | 214.2 | 214 | 0.03836 | 0.04177
[7 empty] | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 5000 | 4846.3 | 153.7 | L: 3666 HUTTOSS1 138 3696 HUTTOSS_ 345 1 |  |  | 188.5 | 687.1 | 686 | 0.09972 | -0.1464
|  |  | TDF_Sign |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 4912.5 | 4893.2 | 19.3 | L: 3425 BELLCTY_ 138 3640 SALADO1_ 138 1 |  |  | 63.7 | 213.5 | 214 | 0.0305 | 0.03114
[7 empty] | C: AEPSSLT__5-SANDOW__5 & AEPSSLT__5-SALADOSS_59 | 248
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3413 TEMPSSLT 345 3699 SALADOSS 345 1
|  |  | 4704.4 | 4943.5 | -239.1 | L: 3633 HARKHTS_ 138 13610 BELTONSW 138 1 |  |  | 181.2 | 325.8 | 326 | 0.03076 | -0.03034
[7 empty] | C: AEPSSLT__5-SANDOW__5 & AEPSSLT__5-SALADOSS_59 | 248
Open 3413 TEMPSSLT 345 3429 SANDOW__ 345 1
Open 3413 TEMPSSLT 345 3699 SALADOSS 345 1
|  |  | 4981.2 | 4954.1 | 27.1 | L: 32 ROBERTSO 138 3682 MILANO_M 138 1 |  |  | 57.1 | 213.5 | 214 | 0.0314 | 0.05471
[7 empty] | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 5000 | 4970.5 | 29.5 | L: 3425 BELLCTY_ 138 3640 SALADO1_ 138 1 |  |  | 68 | 208 | 214 | 0.02801 | 0.03006
|  |  | NoLimit |  |  |  | C: HUTTOSS__5-SALADOSS_5 & HUTTOSS__5-SALADOSS_59 | 256
Open 3696 HUTTOSS_ 345 3699 SALADOSS 345 1
Open 3696 HUTTOSS_ 345 3699 SALADOSS 345 2
Note on A11: PTI: Exporting Subsystem
Note on B11: PTI: Importing Subsystem
Note on C11: PTI: Maximum Test Level
Note on D11: PTI: AC First Contingency Incremental Transfer Capability
Note on E11: PTI: DC First Contingency Incremental Transfer Capability
Note on F11: PTI: Difference between AC FCITC and DC FCITC
Note on G11: PTI: Branch, Flowgate or Interface
Note on H11: PTI: Limiting Contingency. Review MUST options for reporting options
Note on I11: PTI: Contingency Index
Note on J11: PTI: MW Flow before the transfer
Note on K11: PTI: MW Flow after the transfer
Note on L11: PTI: Rating (Base case or Contingent)
Note on M11: PTI: AC Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case
Note on N11: PTI: DC Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case

## N-H
AC FCITC MULTIPLE TRANSFER REPORT
PSS(tm)MUST 8.1.1 -- Managing and Utilizing System Transmission -- MON, JUL 27 2009 17:54
10SUM1 -2010 SUMMER ON-PEAK BASE CASE - ERCOT SSWG PASS 8
UPDATED 07/01/2009 - ERCOT PSSE VER 30.0 CSC CONS. DISPATCH
Case.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\Annual_2010_Basecase_v2_HH_adjusted_v29.sav
Subsys.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\MUST_SUBfile.sub
Monit.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\alltx.mon
Contin.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\ERCOT_CON_File_MUST_05292009_modified_no_D_no_openBus_no_singleline.con
Exclud.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\MUST_Exclude_List_08.exc
Reporting the first 500 violations per transfer | To | Transfer Level | AC FCITC | DC FCITC | Delta FCITC | Limiting Constraint | Contingency | Ncon | PreShift | PostShift | Rating | AC TDF | DC TDF
NORTH | HOUSTON_I | 5000 | -1010.6 | -1153.5 | 142.9 | L: 818 OLINGER 138 968 BENDAVIS 138 1 |  |  | 247.3 | 218 | 218 | 0.02894 | 0.03174
[7 empty] | C:OLINGER-SWINDELL & OLINGER-FIREWHEEL & ELMGROVE-BE8 | 327
Open 812 SWINDELL 138 818 OLINGER 138 1
Open 818 OLINGER 138 821 FIREWHEE 138 1
Open 855 ELMGROVE 138 968 BENDAVIS 138 1
|  |  | 2006.5 | 1804.8 | 201.8 | L: 47150 H_O_C___ 138 47331 KNIGHT08 138 08 |  |  | 327.2 | 384.4 | 384 | 0.02849 | 0.03052
[7 empty] | C:BELAIR-GARROT_37 (47015-47320) & H_O_C_-GARROT_907 | 909
Open 47015 BELAIR__ 138 47320 KIRBY___ 138 37
Open 47150 H_O_C___ 138 47155 CH_O_C__ 138 90
Open 47155 CH_O_C__ 138 47660 GARROT__ 138 90
|  |  | 1975.6 | 1971.2 | 4.3 | L: 44645 SNGLTN_3 345 45500 T_H_W___ 345 98 |  |  | 914.9 | 1450 | 1450 | 0.27088 | 0.26126
[7 empty] | C:SNGLTN - TOMBAL_74 (44645-46500) & ROANS - KING_757 | 984
Open 40600 ROANS___ 345 45972 KUYDAL75 345 75
Open 40900 KING____ 345 45972 KUYDAL75 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 2322.9 | 2739.6 | -416.7 | L: 47660 GARROT__ 138 47705 MIDTWN__ 138 90 |  |  | 189.8 | 282 | 282 | 0.0397 | 0.03509
[7 empty] | C:SNGLTN - TOMBAL_74 (44645-46500) & ROANS - KING_757 | 984
Open 40600 ROANS___ 345 45972 KUYDAL75 345 75
Open 40900 KING____ 345 45972 KUYDAL75 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 2678.4 | 2757.8 | -79.3 | L: 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99 |  |  | 757.9 | 1450 | 1450 | 0.25839 | -0.24521
[7 empty] | C:SNGLTN - TOMBAL_74 (44645-46500) & ROANS - KING_757 | 984
Open 40600 ROANS___ 345 45972 KUYDAL75 345 75
Open 40900 KING____ 345 45972 KUYDAL75 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 2560.5 | 2852.5 | -292 | L: 42500 DOW_____ 345 B$0040 DOW A3 1.00 A3 |  |  | 294.4 | 500.1 | 500 | 0.08035 | 0.08301
[7 empty] | C:3Wnd: OPEN B$0041 DOW A4 A46 | 170
Open 42500 DOW_____ 345 B$0041 DOW A4 1.00 A4
Open 42515 DOW_____ 138 B$0041 DOW A4 1.00 A4
Open 49985 DOW_A4_T 14.4 B$0041 DOW A4 1.00 A4
|  |  | 2560.6 | 2852.6 | -292 | L: 42500 DOW_____ 345 B$0041 DOW A4 1.00 A4 |  |  | 294.4 | 500.1 | 500 | 0.08036 | 0.08301
[7 empty] | C:3Wnd: OPEN B$0040 DOW A3 A36 | 169
Open 42500 DOW_____ 345 B$0040 DOW A3 1.00 A3
Open 42515 DOW_____ 138 B$0040 DOW A3 1.00 A3
Open 49984 DOW_A3_T 14.4 B$0040 DOW A3 1.00 A3
|  |  | 2688.3 | 2854.1 | -165.8 | L: 42515 DOW_____ 138 B$0040 DOW A3 1.00 A3 |  |  | 288.8 | 500.3 | 500 | 0.07868 | -0.08301
[7 empty] | C:3Wnd: OPEN B$0041 DOW A4 A46 | 170
Open 42500 DOW_____ 345 B$0041 DOW A4 1.00 A4
Open 42515 DOW_____ 138 B$0041 DOW A4 1.00 A4
Open 49985 DOW_A4_T 14.4 B$0041 DOW A4 1.00 A4
|  |  | 2678.8 | 2854.1 | -175.3 | L: 42515 DOW_____ 138 B$0041 DOW A4 1.00 A4 |  |  | 289.2 | 500.3 | 500 | 0.07879 | -0.08301
[7 empty] | C:3Wnd: OPEN B$0040 DOW A3 A36 | 169
Open 42500 DOW_____ 345 B$0040 DOW A3 1.00 A3
Open 42515 DOW_____ 138 B$0040 DOW A3 1.00 A3
Open 49984 DOW_A3_T 14.4 B$0040 DOW A3 1.00 A3
|  |  | 3125.7 | 2990.3 | 135.4 | L: 47150 H_O_C___ 138 47331 KNIGHT08 138 08 |  |  | 289.5 | 383 | 384 | 0.02991 | 0.03052
|  |  | LowSens |  |  |  | C:GARROT: H_O_C (47155 CH_O_C Ckt. 90)&1_90 [MSL &7 | 440
Open 47150 H_O_C___ 138 47155 CH_O_C__ 138 90
Open 47155 CH_O_C__ 138 47660 GARROT__ 138 90
Open 47320 KIRBY___ 138 47660 GARROT__ 138 37
|  |  | 3125.7 | 2990.3 | 135.4 | L: 47150 H_O_C___ 138 47331 KNIGHT08 138 08 |  |  | 289.5 | 383 | 384 | 0.02991 | 0.03052
|  |  | LowSens |  |  |  | C:BELAIR-GARROT_37 (47320-47660) & H_O_C_-GARROT_907 | 910
Open 47150 H_O_C___ 138 47155 CH_O_C__ 138 90
Open 47155 CH_O_C__ 138 47660 GARROT__ 138 90
Open 47320 KIRBY___ 138 47660 GARROT__ 138 37
|  |  | 3065.7 | 3044 | 21.8 | L: 44645 SNGLTN_3 345 45500 T_H_W___ 345 98 |  |  | 645.5 | 1470.3 | 1450 | 0.26903 | 0.26126
|  |  | TDF_Sign |  |  |  | C: Contingency>T7475_A8 | 914
Open 2352 RNRTPL_W 138 2524 PL_COIT1 138 1
Open 2353 RNRTPL_E 138 2521 PL_COIT2 138 1
Open 2510 ALLENSW_ 138 2526 PL_CUSTR 138 1
Open 2521 PL_COIT2 138 2523 PL_TENNY 138 1
Open 2524 PL_COIT1 138 2526 PL_CUSTR 138 1
Open 40600 ROANS___ 345 44645 SNGLTN_3 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 3234.7 | 3287 | -52.3 | L: 44645 SNGLTN_3 345 45500 T_H_W___ 345 98 |  |  | 578.9 | 1450 | 1450 | 0.26931 | 0.26126
[7 empty] | C:SNGLTN - TOMBAL_74 (44645-46500) & SNGLTN - ROANS_7 | 977
Open 40600 ROANS___ 345 44645 SNGLTN_3 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 3117.1 | 3302.2 | -185.1 | L: 40700 GRNBYU__ 345 40716 GRNBYU__ 138 A2 |  |  | 340.4 | 503.7 | 504 | 0.05238 | 0.05272
[7 empty] | C:GRNBYU345: King Ckt. 74_74 (40700-40900) & Green7 | 429
Open 40700 GRNBYU__ 345 40710 GRNBYU__ 138 A1
Open 40700 GRNBYU__ 345 40900 KING____ 345 74
|  |  | 2748.9 | 3336 | -587.1 | L: 47705 MIDTWN__ 138 47707 MIDRCLS_ 138 90 |  |  | 172 | 285 | 285 | 0.04112 | 0.03509
[7 empty] | C:SNGLTN - TOMBAL_74 (44645-46500) & ROANS - KING_757 | 984
Open 40600 ROANS___ 345 45972 KUYDAL75 345 75
Open 40900 KING____ 345 45972 KUYDAL75 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 2748.9 | 3336 | -587.1 | L: 47707 MIDRCLS_ 138 47730 POLK____ 138 90 |  |  | 172 | 285 | 285 | 0.04112 | 0.03509
[7 empty] | C:SNGLTN - TOMBAL_74 (44645-46500) & ROANS - KING_757 | 984
Open 40600 ROANS___ 345 45972 KUYDAL75 345 75
Open 40900 KING____ 345 45972 KUYDAL75 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 3153.1 | 3364.7 | -211.6 | L: 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74 |  |  | 1014.2 | 1924 | 1924 | 0.28852 | 0.26566
[7 empty] | C:SNGLTN - T_H_W__98 (44645-45500) & SNGLTN - OBRIEN8 | 112
Open 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99
Open 44645 SNGLTN_3 345 45500 T_H_W___ 345 98
|  |  | 3153.1 | 3364.7 | -211.6 | L: 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74 |  |  | 1014.2 | 1924 | 1924 | 0.28852 | 0.26566
[7 empty] | C: Contingency>T9899_C8 | 915
Open 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99
Open 44645 SNGLTN_3 345 45500 T_H_W___ 345 98
|  |  | 3256.7 | 3431.7 | -175.1 | L: 40700 GRNBYU__ 345 40716 GRNBYU__ 138 A2 |  |  | 323 | 508.2 | 504 | 0.05689 | 0.05597
|  |  | TDF_Sign |  |  |  | C:GRNBYU345: Sheldon Ckt. 74_74 (40700-41430) & Gr7 | 425
Open 40700 GRNBYU__ 345 40710 GRNBYU__ 138 A1
Open 40700 GRNBYU__ 345 41430 SHELDN__ 345 74
|  |  | 3256.7 | 3431.7 | -175.1 | L: 40700 GRNBYU__ 345 40716 GRNBYU__ 138 A2 |  |  | 323 | 508.2 | 504 | 0.05689 | 0.05597
|  |  | TDF_Sign |  |  |  | C:GRNBYU345: Sheldon Ckt. 75_75 (40700-41430) & Gr7 | 422
Open 40700 GRNBYU__ 345 40710 GRNBYU__ 138 A1
Open 40700 GRNBYU__ 345 41430 SHELDN__ 345 75
|  |  | 3544.6 | 3467 | 77.6 | L: 3391 JEWETT_N 345 44645 SNGLTN_3 345 1 |  |  | 522.1 | 1450.9 | 1450 | 0.26204 | 0.26472
|  |  | NotConv |  |  |  | C: GIBN_CREK_5-SNGLTN_345 & GIBN_CREK_5-SNGLTN_3459 | 427
Open 967 GIBN_CRE 345 44645 SNGLTN_3 345 75
Open 967 GIBN_CRE 345 44645 SNGLTN_3 345 99
|  |  | 3544.6 | 3467 | 77.6 | L: 3391 JEWETT_N 345 44645 SNGLTN_3 345 1 |  |  | 522.1 | 1450.9 | 1450 | 0.26204 | 0.26472
|  |  | NotConv |  |  |  | C:GIBN_CREK - SNGLTN_75 (967-44645) & GIBN_CREK - SN7 | 990
Open 967 GIBN_CRE 345 44645 SNGLTN_3 345 75
Open 967 GIBN_CRE 345 44645 SNGLTN_3 345 99
|  |  | 3562.3 | 3527.1 | 35.2 | L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 75 |  |  | 738.3 | 1630.8 | 1631 | 0.25053 | 0.24989
[7 empty] | C: 967 GIBN_CRE 345 44645 SNGLTN_3 345 99 | 647
Open 967 GIBN_CRE 345 44645 SNGLTN_3 345 99
|  |  | 3562.3 | 3527.1 | 35.2 | L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 99 |  |  | 738.3 | 1630.8 | 1631 | 0.25053 | 0.24989
[7 empty] | C: 967 GIBN_CRE 345 44645 SNGLTN_3 345 75 | 646
Open 967 GIBN_CRE 345 44645 SNGLTN_3 345 75
|  |  | 3838.4 | 3661.2 | 177.2 | L: 47320 KIRBY___ 138 47660 GARROT__ 138 37 |  |  | 394.4 | 526 | 526 | 0.0343 | 0.03423
[7 empty] | C:H_O_C_-STADIM_08 (47150-47420)[MSL &1] & H_O_C_-GA7 | 796
Open 47150 H_O_C___ 138 47331 KNIGHT08 138 8
Open 47331 KNIGHT08 138 47420 STADIM__ 138 8
Open 47150 H_O_C___ 138 47155 CH_O_C__ 138 90
Open 47155 CH_O_C__ 138 47660 GARROT__ 138 90
|  |  | 3700.4 | 3715.1 | -14.7 | L: 975 JKCREEK1 345 3400 TWIN_OAK 345 1 |  |  | 572.7 | 1375.8 | 1376 | 0.21704 | -0.21293
[7 empty] | C: JEWETT_S5-T_H_W___345B & JEWETT_N5-TOMBAL__345B8 | 823
Open 3390 JEWETT_S 345 44645 SNGLTN_3 345 1
Open 3391 JEWETT_N 345 44645 SNGLTN_3 345 1
|  |  | 3700.4 | 3715.1 | -14.7 | L: 975 JKCREEK1 345 3400 TWIN_OAK 345 1 |  |  | 572.7 | 1375.8 | 1376 | 0.21704 | -0.21293
[7 empty] | C:JEWETT - SNGLTN_74 (3390-44645) & JEWETT - SNGLTN_7 | 987
Open 3390 JEWETT_S 345 44645 SNGLTN_3 345 1
Open 3391 JEWETT_N 345 44645 SNGLTN_3 345 1
|  |  | 3676.6 | 3741.9 | -65.3 | L: 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99 |  |  | 527 | 1486.5 | 1450 | 0.26097 | -0.24521
|  |  | TDF_Sign |  |  |  | C: Contingency>T7475_A8 | 914
Open 2352 RNRTPL_W 138 2524 PL_COIT1 138 1
Open 2353 RNRTPL_E 138 2521 PL_COIT2 138 1
Open 2510 ALLENSW_ 138 2526 PL_CUSTR 138 1
Open 2521 PL_COIT2 138 2523 PL_TENNY 138 1
Open 2524 PL_COIT1 138 2526 PL_CUSTR 138 1
Open 40600 ROANS___ 345 44645 SNGLTN_3 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 3783.6 | 3837.6 | -53.9 | L: 3390 JEWETT_S 345 44645 SNGLTN_3 345 1 |  |  | 440.1 | 1450 | 1450 | 0.26693 | 0.2612
[7 empty] | C:GIBN_CREK - SNGLTN_75 (967-44645) & GIBN_CREK - SN7 | 990
Open 967 GIBN_CRE 345 44645 SNGLTN_3 345 75
Open 967 GIBN_CRE 345 44645 SNGLTN_3 345 99
|  |  | 3783.6 | 3837.6 | -53.9 | L: 3390 JEWETT_S 345 44645 SNGLTN_3 345 1 |  |  | 440.1 | 1450 | 1450 | 0.26693 | 0.2612
[7 empty] | C: GIBN_CREK_5-SNGLTN_345 & GIBN_CREK_5-SNGLTN_3459 | 427
Open 967 GIBN_CRE 345 44645 SNGLTN_3 345 75
Open 967 GIBN_CRE 345 44645 SNGLTN_3 345 99
|  |  | 3892 | 3845.1 | 46.9 | L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 75 |  |  | 705.3 | 1645.8 | 1631 | 0.24166 | 0.2377
|  |  | TDF_Sign |  |  |  | C:SNGLTN:Singleton-Gibbons_99_99(44645-967) & Single7 | 668
Open 967 GIBN_CRE 345 44645 SNGLTN_3 345 99
Open 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99
|  |  | 3410 | 3908.9 | -498.9 | L: 47660 GARROT__ 138 47705 MIDTWN__ 138 90 |  |  | 146.3 | 281.9 | 282 | 0.03976 | 0.03509
[7 empty] | C:SNGLTN - TOMBAL_74 (44645-46500) & SNGLTN - ROANS_7 | 977
Open 40600 ROANS___ 345 44645 SNGLTN_3 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 3936.7 | 4001.2 | -64.5 | L: 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99 |  |  | 460.6 | 1480.8 | 1450 | 0.25917 | -0.24521
|  |  | TDF_Sign |  |  |  | C:SNGLTN - TOMBAL_74 (44645-46500) & SNGLTN - ROANS_7 | 977
Open 40600 ROANS___ 345 44645 SNGLTN_3 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 3976.2 | 4129.6 | -153.4 | L: 40700 GRNBYU__ 345 40716 GRNBYU__ 138 A2 |  |  | 222.2 | 399.9 | 400 | 0.04468 | 0.04553
Base Case
|  |  | 4426.7 | 4189.2 | 237.6 | L: 47320 KIRBY___ 138 47660 GARROT__ 138 37 |  |  | 365 | 523.8 | 526 | 0.03586 | 0.03631
|  |  | TDF_Sign |  |  |  | C:MEADOW: Meadow - Oasis_99(43030-43035) & Meadow -7 | 534
Open 42000 P_H_R___ 345 43030 MEADOW 345 99
Open 43030 MEADOW 345 43035 OASIS___ 345 99
|  |  | 4426.7 | 4189.2 | 237.6 | L: 47320 KIRBY___ 138 47660 GARROT__ 138 37 |  |  | 365 | 523.8 | 526 | 0.03586 | 0.03631
|  |  | TDF_Sign |  |  |  | C:BF_NAPH_NAOA9 | 479
Open 42000 P_H_R___ 345 43030 MEADOW 345 99
Open 43030 MEADOW 345 43035 OASIS___ 345 99
|  |  | 4303.2 | 4280.4 | 22.8 | L: 46500 TOMBAL__ 345 46510 TOMBAL__ 138 A1 |  |  | 575.9 | 1000 | 1000 | 0.09856 | 0.0997
[7 empty] | C:TOMBAL: Tomball - Rothwood_74(46500-46290)[MSL &1]8 | 118
Open 45971 KUYDAL74 345 46290 ROTHWOOD 345 74
Open 45971 KUYDAL74 345 46500 TOMBAL__ 345 74
Open 46500 TOMBAL__ 345 46510 TOMBAL__ 138 A2
|  |  | 3605.3 | 4287.8 | -682.6 | L: 47660 GARROT__ 138 47705 MIDTWN__ 138 90 |  |  | 133.3 | 282.1 | 282 | 0.04128 | 0.03509
[7 empty] | C: Contingency>T7475_A8 | 914
Open 2352 RNRTPL_W 138 2524 PL_COIT1 138 1
Open 2353 RNRTPL_E 138 2521 PL_COIT2 138 1
Open 2510 ALLENSW_ 138 2526 PL_CUSTR 138 1
Open 2521 PL_COIT2 138 2523 PL_TENNY 138 1
Open 2524 PL_COIT1 138 2526 PL_CUSTR 138 1
Open 40600 ROANS___ 345 44645 SNGLTN_3 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 4266.9 | 4323.9 | -57 | L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 75 |  |  | 520.9 | 1631.1 | 1631 | 0.26018 | 0.25481
[7 empty] | C:JEWETT - SNGLTN_74 (3390-44645) & JEWETT - SNGLTN_7 | 987
Open 3390 JEWETT_S 345 44645 SNGLTN_3 345 1
Open 3391 JEWETT_N 345 44645 SNGLTN_3 345 1
|  |  | 4266.9 | 4323.9 | -57 | L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 99 |  |  | 520.9 | 1631.1 | 1631 | 0.26018 | 0.25481
[7 empty] | C: JEWETT_S5-T_H_W___345B & JEWETT_N5-TOMBAL__345B8 | 823
Open 3390 JEWETT_S 345 44645 SNGLTN_3 345 1
Open 3391 JEWETT_N 345 44645 SNGLTN_3 345 1
|  |  | 4266.9 | 4323.9 | -57 | L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 99 |  |  | 520.9 | 1631.1 | 1631 | 0.26018 | 0.25481
[7 empty] | C:JEWETT - SNGLTN_74 (3390-44645) & JEWETT - SNGLTN_7 | 987
Open 3390 JEWETT_S 345 44645 SNGLTN_3 345 1
Open 3391 JEWETT_N 345 44645 SNGLTN_3 345 1
|  |  | 3955.4 | 4334.1 | -378.8 | L: 40600 ROANS___ 345 45972 KUYDAL75 345 75 |  |  | 692.5 | 1710.4 | 1710 | 0.25733 | 0.23177
[7 empty] | C: Contingency>T9899_C8 | 915
Open 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99
Open 44645 SNGLTN_3 345 45500 T_H_W___ 345 98
|  |  | 3955.4 | 4334.1 | -378.8 | L: 40600 ROANS___ 345 45972 KUYDAL75 345 75 |  |  | 692.5 | 1710.4 | 1710 | 0.25733 | 0.23177
[7 empty] | C:SNGLTN - T_H_W__98 (44645-45500) & SNGLTN - OBRIEN8 | 112
Open 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99
Open 44645 SNGLTN_3 345 45500 T_H_W___ 345 98
|  |  | 4338.3 | 4404.1 | -65.9 | L: 967 GIBN_CRE 345 975 JKCREEK1 345 1 |  |  | 414.1 | 1376 | 1376 | 0.22172 | -0.21694
[7 empty] | C: JEWETT_S5-T_H_W___345B & JEWETT_N5-TOMBAL__345B8 | 823
Open 3390 JEWETT_S 345 44645 SNGLTN_3 345 1
Open 3391 JEWETT_N 345 44645 SNGLTN_3 345 1
|  |  | 4338.3 | 4404.1 | -65.9 | L: 967 GIBN_CRE 345 975 JKCREEK1 345 1 |  |  | 414.1 | 1376 | 1376 | 0.22172 | -0.21694
[7 empty] | C:JEWETT - SNGLTN_74 (3390-44645) & JEWETT - SNGLTN_7 | 987
Open 3390 JEWETT_S 345 44645 SNGLTN_3 345 1
Open 3391 JEWETT_N 345 44645 SNGLTN_3 345 1
|  |  | 3828.3 | 4505.3 | -677 | L: 47705 MIDTWN__ 138 47707 MIDRCLS_ 138 90 |  |  | 128.6 | 285.1 | 285 | 0.04089 | 0.03509
[7 empty] | C:SNGLTN - TOMBAL_74 (44645-46500) & SNGLTN - ROANS_7 | 977
Open 40600 ROANS___ 345 44645 SNGLTN_3 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 3828.3 | 4505.3 | -677.1 | L: 47707 MIDRCLS_ 138 47730 POLK____ 138 90 |  |  | 128.6 | 285.1 | 285 | 0.04089 | 0.03509
[7 empty] | C:SNGLTN - TOMBAL_74 (44645-46500) & SNGLTN - ROANS_7 | 977
Open 40600 ROANS___ 345 44645 SNGLTN_3 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 4539.2 | 4510.8 | 28.4 | L: 44645 SNGLTN_3 345 45500 T_H_W___ 345 98 |  |  | 478.9 | 1137.1 | 1137 | 0.14499 | 0.14324
Base Case
|  |  | 4609.3 | 4513.5 | 95.9 | L: 46510 TOMBAL__ 138 46512 TOMBAL81 138 81 |  |  | 288.1 | 526 | 526 | 0.05161 | 0.0511
[7 empty] | C:ROTHWD - TOMBAL_74 (46290-46500) [MSL &1] & KING -7 | 981
Open 40600 ROANS___ 345 45972 KUYDAL75 345 75
Open 40900 KING____ 345 45972 KUYDAL75 345 75
Open 45971 KUYDAL74 345 46290 ROTHWOOD 345 74
Open 45971 KUYDAL74 345 46500 TOMBAL__ 345 74
|  |  | 4735.3 | 4553.3 | 182 | L: 1690 VALLYSES 345 2373 ANNASW_5 345 1 |  |  | 1632.8 | 1792.3 | 1793 | 0.03368 | 0.03381
|  |  | NotConv |  |  |  | C: FARMVLSW_5-VAL_STH_5 & VAL_STH_5-ANNASW_59 | 321
Open 1685 FARMVLSW 345 1729 VAL_STH_ 345 1
Open 1729 VAL_STH_ 345 2373 ANNASW_5 345 1
|  |  | 4528.8 | 4555.8 | -27 | L: 3391 JEWETT_N 345 44645 SNGLTN_3 345 1 |  |  | 424.9 | 1450.1 | 1450 | 0.22636 | 0.22348
[7 empty] | C: GIBN_CREK_5-JKCREEK1 & GIBN_CREK_5-TWIN_OAK__59 | 423
Open 967 GIBN_CRE 345 975 JKCREEK1 345 1
Open 967 GIBN_CRE 345 3400 TWIN_OAK 345 1
|  |  | 4272.8 | 4670.4 | -397.6 | L: 40900 KING____ 345 45972 KUYDAL75 345 75 |  |  | 619.7 | 1709.5 | 1710 | 0.25504 | -0.23177
[7 empty] | C:SNGLTN - T_H_W__98 (44645-45500) & SNGLTN - OBRIEN8 | 112
Open 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99
Open 44645 SNGLTN_3 345 45500 T_H_W___ 345 98
|  |  | 4272.8 | 4670.4 | -397.6 | L: 40900 KING____ 345 45972 KUYDAL75 345 75 |  |  | 619.7 | 1709.5 | 1710 | 0.25504 | -0.23177
[7 empty] | C: Contingency>T9899_C8 | 915
Open 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99
Open 44645 SNGLTN_3 345 45500 T_H_W___ 345 98
|  |  | 4865.1 | 4863.9 | 1.2 | L: 3390 JEWETT_S 345 44645 SNGLTN_3 345 1 |  |  | 353.6 | 1449.6 | 1450 | 0.22528 | 0.22443
[7 empty] | C: GIBN_CREK_5-JKCREEK1 & GIBN_CREK_5-TWIN_OAK__59 | 423
Open 967 GIBN_CRE 345 975 JKCREEK1 345 1
Open 967 GIBN_CRE 345 3400 TWIN_OAK 345 1
|  |  | 3254.9 | 4883.1 | -1628.2 | L: 3402 LAKE_CRK 345 3405 THOUSE__ 345 2 |  |  | 96.6 | 628.6 | 956 | 0.16347 | -0.20072
|  |  | NotConv |  |  |  | C: THOUSE__5-LAKE_CRK1_5 & THOUSE__5-AEP_PEC__59 | 245
Open 3405 THOUSE__ 345 3409 LAKE_CRK 345 1
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
|  |  | 4000.5 | 4884.2 | -883.8 | L: 47705 MIDTWN__ 138 47707 MIDRCLS_ 138 90 |  |  | 115.5 | 285.3 | 285 | 0.04244 | 0.03509
[7 empty] | C: Contingency>T7475_A8 | 914
Open 2352 RNRTPL_W 138 2524 PL_COIT1 138 1
Open 2353 RNRTPL_E 138 2521 PL_COIT2 138 1
Open 2510 ALLENSW_ 138 2526 PL_CUSTR 138 1
Open 2521 PL_COIT2 138 2523 PL_TENNY 138 1
Open 2524 PL_COIT1 138 2526 PL_CUSTR 138 1
Open 40600 ROANS___ 345 44645 SNGLTN_3 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 4000.5 | 4884.3 | -883.8 | L: 47707 MIDRCLS_ 138 47730 POLK____ 138 90 |  |  | 115.5 | 285.3 | 285 | 0.04244 | 0.03509
[7 empty] | C: Contingency>T7475_A8 | 914
Open 2352 RNRTPL_W 138 2524 PL_COIT1 138 1
Open 2353 RNRTPL_E 138 2521 PL_COIT2 138 1
Open 2510 ALLENSW_ 138 2526 PL_CUSTR 138 1
Open 2521 PL_COIT2 138 2523 PL_TENNY 138 1
Open 2524 PL_COIT1 138 2526 PL_CUSTR 138 1
Open 40600 ROANS___ 345 44645 SNGLTN_3 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 4830.9 | 4968.6 | -137.7 | L: 46550 TRSWIG__ 138 46571 CWESFLD_ 138 66 |  |  | 104 | 258 | 280 | 0.03187 | -0.03641
|  |  | NotConv |  |  |  | C:KING - ROTHWD_74 (40900-46290) & KING - ROANS_75 (7 | 982
Open 40600 ROANS___ 345 45972 KUYDAL75 345 75
Open 40900 KING____ 345 45972 KUYDAL75 345 75
Open 40900 KING____ 345 46290 ROTHWOOD 345 74
Note on A11: PTI: Exporting Subsystem
Note on B11: PTI: Importing Subsystem
Note on C11: PTI: Maximum Test Level
Note on D11: PTI: AC First Contingency Incremental Transfer Capability
Note on E11: PTI: DC First Contingency Incremental Transfer Capability
Note on F11: PTI: Difference between AC FCITC and DC FCITC
Note on G11: PTI: Branch, Flowgate or Interface
Note on H11: PTI: Limiting Contingency. Review MUST options for reporting options
Note on I11: PTI: Contingency Index
Note on J11: PTI: MW Flow before the transfer
Note on K11: PTI: MW Flow after the transfer
Note on L11: PTI: Rating (Base case or Contingent)
Note on M11: PTI: AC Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case
Note on N11: PTI: DC Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case

## N-W
AC FCITC MULTIPLE TRANSFER REPORT
PSS(tm)MUST 8.1.1 -- Managing and Utilizing System Transmission -- MON, JUL 27 2009 17:54
10SUM1 -2010 SUMMER ON-PEAK BASE CASE - ERCOT SSWG PASS 8
UPDATED 07/01/2009 - ERCOT PSSE VER 30.0 CSC CONS. DISPATCH
Case.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\Annual_2010_Basecase_v2_HH_adjusted_v29.sav
Subsys.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\MUST_SUBfile.sub
Monit.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\alltx.mon
Contin.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\ERCOT_CON_File_MUST_05292009_modified_no_D_no_openBus_no_singleline.con
Exclud.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\MUST_Exclude_List_08.exc
Reporting the first 500 violations per transfer | To | Transfer Level | AC FCITC | DC FCITC | Delta FCITC | Limiting Constraint | Contingency | Ncon | PreShift | PostShift | Rating | AC TDF | DC TDF
NORTH | WEST_I | 5000 | -1006.3 | -1153.5 | 147.2 | L: 818 OLINGER 138 968 BENDAVIS 138 1 |  |  | 247.3 | 218 | 218 | 0.02907 | 0.03174
[7 empty] | C:OLINGER-SWINDELL & OLINGER-FIREWHEEL & ELMGROVE-BE8 | 327
Open 812 SWINDELL 138 818 OLINGER 138 1
Open 818 OLINGER 138 821 FIREWHEE 138 1
Open 855 ELMGROVE 138 968 BENDAVIS 138 1
|  |  | 1821.6 | 1563.7 | 257.9 | L: 1624 LEONSW_8 138 1642 FLATCRK_ 138 1 |  |  | 36.2 | 84 | 84 | 0.02624 | -0.03087
[7 empty] | C: 1440 COMCHESS 345 6444 SARC7A 345 11 | 120
Open 1440 COMCHESS 345 6444 SARC7A 345 1
|  |  | 1884.7 | 1863.4 | 21.3 | L: 2372 COLLINSS 345 2373 ANNASW_5 345 1 |  |  | 1626.5 | 1721.1 | 1721 | 0.05018 | -0.05076
[7 empty] | C: MOSES_5-MOSES1_T5 & MOSES1_T5-ALLENSW2_59 | 20
Open 1695 MOSES_5 345 1696 MOSES1_T 345 1
Open 1696 MOSES1_T 345 2514 ALLENSW2 345 1
Open 2461 ROYSE_N5 345 2513 ALLENSW1 345 1
|  |  | 1895 | 1879.6 | 15.4 | L: 2372 COLLINSS 345 2373 ANNASW_5 345 1 |  |  | 1626 | 1721.1 | 1721 | 0.05019 | -0.05076
[7 empty] | C: MOSES1_T5-ALLENSW2_5 & ROYSE_N5-ALLENSW1_59 | 28
Open 1696 MOSES1_T 345 2514 ALLENSW2 345 1
Open 2461 ROYSE_N5 345 2513 ALLENSW1 345 1
|  |  | 2299.1 | 2264.7 | 34.3 | L: 1371 MURRY_P8 138 1431 GRHAMSES 138 1 |  |  | 17.8 | 137.8 | 143 | 0.05221 | -0.05442
|  |  | NotConv |  |  |  | C:SWEETWATER / MULBERRY - LONGCREEK8 | 910
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 2377.2 | 2308.3 | 68.9 | L: 2372 COLLINSS 345 2373 ANNASW_5 345 1 |  |  | 1625.2 | 1721.1 | 1721 | 0.04034 | -0.04126
[7 empty] | C: FARMVLSW_5-ROYSE_N5 & FARMVLSW_5-ROYSE_S58 | 793
Open 1685 FARMVLSW 345 2461 ROYSE_N5 345 1
Open 1685 FARMVLSW 345 2478 ROYSE_S5 345 1
|  |  | 2693.9 | 2538.3 | 155.6 | L: 1371 MURRY_P8 138 6169 PAIP4B 138 1 |  |  | 16.1 | 155 | 155 | 0.05155 | 0.05442
[7 empty] | C:SWEETWATER / MULBERRY - LONGCREEK8 | 910
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 2217.2 | 2916.8 | -699.7 | L: 1371 MURRY_P8 138 1431 GRHAMSES 138 1 |  |  | 12.4 | 106.2 | 143 | 0.04229 | -0.04413
|  |  | NotConv |  |  |  | C:GRAHAM - LONGCREEK / LONGCREEK - COOKFIELD8 | 911
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1439 LONCREK2 345 1442 COKFIELD 345 1
|  |  | 2983.3 | 2924.3 | 59 | L: 1371 MURRY_P8 138 1431 GRHAMSES 138 1 |  |  | 29.2 | 138.8 | 143 | 0.03674 | -0.0381
|  |  | NotConv |  |  |  | C: 1435 LONGCREK 345 6230 ABMULCE7 345 11 | 109
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 3083.9 | 3096.8 | -12.9 | L: 6230 ABMULCE7 345 B$0011 AMCAE 1.00 1 |  |  | 140.7 | 280.4 | 280 | 0.04529 | 0.04796
[7 empty] | C: 6230 ABMULCE7 345 6235 ABMULCW7 345 13 | 878
Open 6230 ABMULCE7 345 6235 ABMULCW7 345 1
|  |  | 3073.1 | 3101.9 | -28.8 | L: 6232 MULBE RS 138 B$0011 AMCAE 1.00 1 |  |  | 129.4 | 279.4 | 280 | 0.0488 | -0.04796
[7 empty] | C: 6230 ABMULCE7 345 6235 ABMULCW7 345 13 | 878
Open 6230 ABMULCE7 345 6235 ABMULCW7 345 1
|  |  | 3410.4 | 3247.9 | 162.5 | L: 6232 MULBE RS 138 6288 MULBE RL 138 BP |  |  | 123.3 | 284 | 287 | 0.04712 | 0.04796
|  |  | NotConv |  |  |  | C: 6230 ABMULCE7 345 6235 ABMULCW7 345 13 | 878
Open 6230 ABMULCE7 345 6235 ABMULCW7 345 1
|  |  | 3412.8 | 3247.9 | 165 | L: 6228 ABNW4A 138 6288 MULBE RL 138 1 |  |  | 123.3 | 271.2 | 287 | 0.04333 | -0.04796
|  |  | NotConv |  |  |  | C: 6230 ABMULCE7 345 6235 ABMULCW7 345 13 | 878
Open 6230 ABMULCE7 345 6235 ABMULCW7 345 1
|  |  | 3025.3 | 3248.3 | -223 | L: 1309 BLUFCKTA 138 1318 CHINAGRV 138 1 |  |  | 79.3 | 185.8 | 186 | 0.03522 | -0.03263
[7 empty] | C: 1032 MRGNCRK_ 138 1064 SUN_8 138 1 | 747
Open 1032 MRGNCRK_ 138 1064 SUN_8 138 1
|  |  | 3251.8 | 3254.1 | -2.3 | L: 1371 MURRY_P8 138 6169 PAIP4B 138 1 |  |  | 11.4 | 147.6 | 155 | 0.04189 | 0.04413
|  |  | TDF_Sign |  |  |  | C:GRAHAM - LONGCREEK / LONGCREEK - COOKFIELD8 | 911
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1439 LONCREK2 345 1442 COKFIELD 345 1
|  |  | 3363.8 | 3315 | 48.8 | L: 1371 MURRY_P8 138 6169 PAIP4B 138 1 |  |  | 26.7 | 150.5 | 155 | 0.0368 | 0.0381
|  |  | NotConv |  |  |  | C: 1435 LONGCREK 345 6230 ABMULCE7 345 11 | 109
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 3197.4 | 3341 | -143.7 | L: 2361 CRLTN_NW 345 2372 COLLINSS 345 1 |  |  | 923.2 | 1071.3 | 1072 | 0.04631 | -0.04648
|  |  | NotConv |  |  |  | C: MOSES_5-MOSES1_T5 & MOSES1_T5-ALLENSW2_59 | 20
Open 1695 MOSES_5 345 1696 MOSES1_T 345 1
Open 1696 MOSES1_T 345 2514 ALLENSW2 345 1
Open 2461 ROYSE_N5 345 2513 ALLENSW1 345 1
|  |  | 3188.7 | 3346.2 | -157.5 | L: 2361 CRLTN_NW 345 2372 COLLINSS 345 1 |  |  | 923.1 | 1071.8 | 1072 | 0.04665 | -0.04648
[7 empty] | C: MOSES1_T5-ALLENSW2_5 & ROYSE_N5-ALLENSW1_59 | 28
Open 1696 MOSES1_T 345 2514 ALLENSW2 345 1
Open 2461 ROYSE_N5 345 2513 ALLENSW1 345 1
|  |  | 3195.7 | 3384.4 | -188.8 | L: 1309 BLUFCKTA 138 1318 CHINAGRV 138 1 |  |  | 77.2 | 186 | 186 | 0.03406 | -0.03201
[7 empty] | C: 1305 SNYDER_8 138 1318 CHINAGRV 138 1 | 957
Open 1305 SNYDER_8 138 1318 CHINAGRV 138 1
|  |  | 3230.8 | 3398.1 | -167.3 | L: 1309 BLUFCKTA 138 1318 CHINAGRV 138 1 |  |  | 68.8 | 186 | 186 | 0.03629 | -0.0343
[7 empty] | C: 1305 SNYDER_8 138 1311 SACROC_8 138 1 | 956
Open 1305 SNYDER_8 138 1311 SACROC_8 138 1
|  |  | 3033.2 | 3400.3 | -367.2 | L: 6230 ABMULCE7 345 B$0011 AMCAE 1.00 1 |  |  | 161.4 | 264.9 | 280 | 0.03413 | 0.03907
|  |  | NotConv |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3341.3 | 3406.7 | -65.4 | L: 6232 MULBE RS 138 B$0011 AMCAE 1.00 1 |  |  | 150.1 | 263.9 | 280 | 0.03407 | -0.03907
|  |  | NotConv |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3429.4 | 3429.9 | -0.5 | L: 1464 WFALLS_S 138 1478 ARROWHD_ 138 1 |  |  | 68.2 | 139.8 | 143 | 0.02087 | 0.06008
|  |  | NotConv |  |  |  | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 3416.8 | 3463.7 | -46.8 | L: 6230 ABMULCE7 345 B$0011 AMCAE 1.00 1 |  |  | 154.3 | 277.9 | 280 | 0.03618 | 0.03676
|  |  | NotConv |  |  |  | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 3416.8 | 3470.4 | -53.5 | L: 6232 MULBE RS 138 B$0011 AMCAE 1.00 1 |  |  | 154.3 | 277.9 | 280 | 0.03618 | -0.03676
|  |  | NotConv |  |  |  | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 3518.3 | 3518.9 | -0.5 | L: 1435 LONGCREK 345 6230 ABMULCE7 345 1 |  |  | 109 | 1029.2 | 1072 | 0.26153 | 0.33223
|  |  | NotConv |  |  |  | C: 1420 SWEETWTR 345 1439 LONCREK2 345 11 | 69
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 2085.9 | 3521.1 | -1435.3 | L: 1435 LONGCREK 345 6230 ABMULCE7 345 1 |  |  | 109.1 | 565.3 | 1072 | 0.21871 | 0.33223
|  |  | NotConv |  |  |  | C: 1414 CHAMPNCR 345 1420 SWEETWTR 345 11 | 67
Open 1414 CHAMPNCR 345 1420 SWEETWTR 345 1
|  |  | 2047 | 3524.2 | -1477.3 | L: 1435 LONGCREK 345 6230 ABMULCE7 345 1 |  |  | 107.7 | 553 | 1072 | 0.21755 | 0.33158
|  |  | NotConv |  |  |  | C: 1030 MRGNCRK_ 345 1414 CHAMPNCR 345 1 | 736
Open 1030 MRGNCRK_ 345 1414 CHAMPNCR 345 1
|  |  | 2770.4 | 3585.8 | -815.5 | L: 6232 MULBE RS 138 6288 MULBE RL 138 BP |  |  | 142.7 | 242.3 | 287 | 0.03595 | 0.03907
|  |  | NotConv |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2192.5 | 3585.8 | -1393.3 | L: 6228 ABNW4A 138 6288 MULBE RL 138 1 |  |  | 142.7 | 195.1 | 287 | 0.02388 | -0.03907
|  |  | TDF_Sign |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3777.4 | 3660.8 | 116.6 | L: 6232 MULBE RS 138 6288 MULBE RL 138 BP |  |  | 147.1 | 280.3 | 287 | 0.03527 | 0.03676
|  |  | NotConv |  |  |  | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 3523.7 | 3660.8 | -137.1 | L: 6228 ABNW4A 138 6288 MULBE RL 138 1 |  |  | 147.1 | 268.9 | 287 | 0.03456 | -0.03676
|  |  | NotConv |  |  |  | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 3743.9 | 3970.8 | -226.9 | L: 2361 CRLTN_NW 345 2372 COLLINSS 345 1 |  |  | 920.6 | 1071.1 | 1072 | 0.04021 | -0.04034
|  |  | NotConv |  |  |  | C: 2370 COLLINSS 138 2372 COLLINSS 345 12 | 35
Open 2370 COLLINSS 138 2372 COLLINSS 345 1
|  |  | 3093.6 | 4034.8 | -941.1 | L: 1032 MRGNCRK_ 138 1332 COSDEN_8 138 1 |  |  | 22.8 | 106.8 | 143 | 0.02714 | 0.03368
|  |  | NotConv |  |  |  | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 1789.9 | 4066 | -2276.1 | L: 1032 MRGNCRK_ 138 1332 COSDEN_8 138 1 |  |  | 22.7 | 63.1 | 143 | 0.02253 | 0.03353
|  |  | NotConv |  |  |  | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 1789.9 | 4066 | -2276.1 | L: 1032 MRGNCRK_ 138 1332 COSDEN_8 138 1 |  |  | 22.7 | 63.1 | 143 | 0.02253 | 0.03353
|  |  | NotConv |  |  |  | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 3788.4 | 4089.6 | -301.2 | L: 1649 HASSE_P8 138 1650 COMANCHE 138 1 |  |  | 14.1 | 172.1 | 186 | 0.04171 | 0.04366
|  |  | NotConv |  |  |  | C: 1440 COMCHESS 345 1900 COMCHPKW 345 11 | 119
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
|  |  | 3399.2 | 4172.8 | -773.6 | L: 1478 ARROWHD_ 138 1480 RATHGBER 138 1 |  |  | 69.6 | 136.2 | 186 | 0.01959 | 0.06008
|  |  | NotConv |  |  |  | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 3977.8 | 4353.1 | -375.2 | L: 1690 VALLYSES 345 2373 ANNASW_5 345 1 |  |  | 1632.8 | 1776.4 | 1793 | 0.03608 | 0.03536
|  |  | NotConv |  |  |  | C: FARMVLSW_5-VAL_STH_5 & VAL_STH_5-ANNASW_59 | 321
Open 1685 FARMVLSW 345 1729 VAL_STH_ 345 1
Open 1729 VAL_STH_ 345 2373 ANNASW_5 345 1
|  |  | 3164 | 4375.2 | -1211.2 | L: 1649 HASSE_P8 138 1650 COMANCHE 138 1 |  |  | 12.6 | 134.2 | 186 | 0.03846 | 0.04189
|  |  | TDF_Sign |  |  |  | C: COMCHESS1_5-COMCHPKW_5 & STPHNVIL_8-CMPKSTUP_88 | 749
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
Open 1641 STPHNVIL 138 2278 CMPKSTUP 138 1
|  |  | 3780 | 4415.1 | -635 | L: 1636 DUBLIN1_ 138 1649 HASSE_P8 138 1 |  |  | 31.9 | 163.2 | 186 | 0.03473 | 0.03568
|  |  | NotConv |  |  |  | C: 1440 COMCHESS 345 1900 COMCHPKW 345 11 | 119
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
|  |  | 3954.8 | 4449.1 | -494.3 | L: 1441 COMCHESS 138 1650 COMANCHE 138 1 |  |  | 9.1 | 163.1 | 186 | 0.03894 | -0.04366
|  |  | NotConv |  |  |  | C: 1440 COMCHESS 345 1900 COMCHPKW 345 11 | 119
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
|  |  | 2229.1 | 4506.4 | -2277.2 | L: 1596 GRAHAMSW 138 1599 BARTON_8 138 1 |  |  | 15.6 | 97.7 | 186 | 0.03686 | -0.03819
|  |  | NotConv |  |  |  | C: 1431 GRHAMSES 138 1433 GRHAMSES 20.0 11 | 99
Open 1431 GRHAMSES 138 1433 GRHAMSES 20.0 1
|  |  | 3012.4 | 4519.3 | -1506.9 | L: 1448 WCHTFLLS 138 1480 RATHGBER 138 1 |  |  | 88 | 92.1 | 186 | 0.00136 | -0.06008
|  |  | NotConv |  |  |  | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 3100.2 | 4524.1 | -1424 | L: 1435 LONGCREK 345 6230 ABMULCE7 345 1 |  |  | 33.1 | 706.5 | 1072 | 0.21722 | 0.23022
|  |  | NotConv |  |  |  | Base Case
|  |  | 3354.3 | 4579.8 | -1225.5 | L: 1596 GRAHAMSW 138 1599 BARTON_8 138 1 |  |  | 26.1 | 133.4 | 186 | 0.03201 | -0.04366
|  |  | NotConv |  |  |  | C: 1440 COMCHESS 345 6444 SARC7A 345 11 | 120
Open 1440 COMCHESS 345 6444 SARC7A 345 1
|  |  | 1370.7 | 4628.3 | -3257.6 | L: 1322 BIGSPRIG 138 1332 COSDEN_8 138 1 |  |  | 14.7 | 32.2 | 143 | 0.01274 | -0.03368
|  |  | NotConv |  |  |  | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 1380.8 | 4662.2 | -3281.5 | L: 1322 BIGSPRIG 138 1332 COSDEN_8 138 1 |  |  | 15 | 31.9 | 143 | 0.01223 | -0.03353
|  |  | NotConv |  |  |  | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 1380.8 | 4662.2 | -3281.5 | L: 1322 BIGSPRIG 138 1332 COSDEN_8 138 1 |  |  | 15 | 31.9 | 143 | 0.01223 | -0.03353
|  |  | NotConv |  |  |  | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 3065.3 | 4677.4 | -1612.1 | L: 1596 GRAHAMSW 138 1599 BARTON_8 138 1 |  |  | 25.3 | 127.1 | 186 | 0.03322 | -0.03926
|  |  | NotConv |  |  |  | C:Miller - Stephenville7 | 250
Open 295 STEPHENV 138 296 STPHNVLT 138 1
Open 296 STPHNVLT 138 331 RWMILLER 138 1
Open 296 STPHNVLT 138 1641 STPHNVIL 138 1
Open 295 STEPHENV 138 299 STEPHNVI 69.0 1
|  |  | 3815.9 | 4749.9 | -933.9 | L: 1441 COMCHESS 138 1650 COMANCHE 138 1 |  |  | 13.7 | 146.2 | 186 | 0.03472 | -0.04189
|  |  | NotConv |  |  |  | C: COMCHESS1_5-COMCHPKW_5 & STPHNVIL_8-CMPKSTUP_88 | 749
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
Open 1641 STPHNVIL 138 2278 CMPKSTUP 138 1
|  |  | 3250.4 | 4800.9 | -1550.5 | L: 1636 DUBLIN1_ 138 1649 HASSE_P8 138 1 |  |  | 27.7 | 133.6 | 186 | 0.03258 | 0.03384
|  |  | NotConv |  |  |  | C: COMCHESS1_5-COMCHPKW_5 & STPHNVIL_8-CMPKSTUP_88 | 749
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
Open 1641 STPHNVIL 138 2278 CMPKSTUP 138 1
|  |  | 3340 | 4982.3 | -1642.3 | L: 1048 TONKAWA_ 345 1430 GRHAMSES 345 1 |  |  | 247.6 | 630.2 | 1072 | 0.11452 | -0.2625
|  |  | NotConv |  |  |  | C:SWEETWATER / MULBERRY - LONGCREEK8 | 910
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
Note on A11: PTI: Exporting Subsystem
Note on B11: PTI: Importing Subsystem
Note on C11: PTI: Maximum Test Level
Note on D11: PTI: AC First Contingency Incremental Transfer Capability
Note on E11: PTI: DC First Contingency Incremental Transfer Capability
Note on F11: PTI: Difference between AC FCITC and DC FCITC
Note on G11: PTI: Branch, Flowgate or Interface
Note on H11: PTI: Limiting Contingency. Review MUST options for reporting options
Note on I11: PTI: Contingency Index
Note on J11: PTI: MW Flow before the transfer
Note on K11: PTI: MW Flow after the transfer
Note on L11: PTI: Rating (Base case or Contingent)
Note on M11: PTI: AC Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case
Note on N11: PTI: DC Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case

## W-S
AC FCITC MULTIPLE TRANSFER REPORT
PSS(tm)MUST 8.1.1 -- Managing and Utilizing System Transmission -- MON, JUL 27 2009 17:54
10SUM1 -2010 SUMMER ON-PEAK BASE CASE - ERCOT SSWG PASS 8
UPDATED 07/01/2009 - ERCOT PSSE VER 30.0 CSC CONS. DISPATCH
Case.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\Annual_2010_Basecase_v2_HH_adjusted_v29.sav
Subsys.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\MUST_SUBfile.sub
Monit.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\alltx.mon
Contin.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\ERCOT_CON_File_MUST_05292009_modified_no_D_no_openBus_no_singleline.con
Exclud.File C:\Documents and Settings\cngai\Desktop\2010 CSC Determination\MUST_Exclude_List_08.exc
Reporting the first 500 violations per transfer | To | Transfer Level | AC FCITC | DC FCITC | Delta FCITC | Limiting Constraint | Contingency | Ncon | PreShift | PostShift | Rating | AC TDF | DC TDF
WEST | SOUTH_I | 5000 | 748.7 | 731.6 | 17.2 | L: 1318 CHINAGRV 138 1398 RADIUMMT 138 1 |  |  | 76.4 | 104.9 | 105 | 0.03814 | 0.03959
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 915.9 | 889.5 | 26.3 | L: 1318 CHINAGRV 138 1398 RADIUMMT 138 1 |  |  | 73.3 | 105 | 105 | 0.03462 | 0.03594
[7 empty] | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 1163.5 | 1078.7 | 84.8 | L: 1427 FISHERRD 138 1448 WCHTFLLS 138 1 |  |  | 214.9 | 260.1 | 260 | 0.03889 | 0.04061
[7 empty] | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 1532.7 | 1423.9 | 108.9 | L: 1426 FISHRDSS 138 1427 FISHERRD 138 1 |  |  | 227.7 | 287.1 | 287 | 0.03877 | 0.04061
[7 empty] | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 1499.5 | 1461.3 | 38.2 | L: 1032 MRGNCRK_ 138 1341 SWTRDTAP 138 1 |  |  | 135 | 185.9 | 186 | 0.03393 | 0.03398
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 1863.8 | 1811.7 | 52.1 | L: 1025 FSCOGEN_ 345 1030 MRGNCRK_ 345 1 |  |  | 663.2 | 956.3 | 956 | 0.15722 | 0.15487
[7 empty] | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 1863.8 | 1811.7 | 52.1 | L: 1025 FSCOGEN_ 345 1030 MRGNCRK_ 345 1 |  |  | 663.2 | 956.3 | 956 | 0.15722 | 0.15487
[7 empty] | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 1889.1 | 1811.8 | 77.3 | L: 1025 FSCOGEN_ 345 1030 MRGNCRK_ 345 1 |  |  | 660.5 | 956.5 | 956 | 0.15671 | 0.15645
[7 empty] | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 1890 | 1859.1 | 31 | L: 1421 WILLOWCK 345 1436 PARKER_5 345 1 |  |  | 681.7 | 1054.2 | 1072 | 0.19712 | 0.20611
|  |  | NotConv |  |  |  | C: 1429 JACKSBRO 345 1730 KRUMW_5 345 11 | 92
Open 1429 JACKSBRO 345 1730 KRUMW_5 345 1
|  |  | 1962.8 | 1950.6 | 12.2 | L: 1302 MULESHOE 138 1307 KEYLYNTE 138 1 |  |  | 56.4 | 186 | 186 | 0.06602 | 0.06672
[7 empty] | C: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 | 947
Open 1300 EXSHARNR 138 1301 WILLOWVA 138 1
|  |  | 1934 | 1950.6 | -16.5 | L: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 |  |  | 59.5 | 186 | 186 | 0.06538 | -0.06672
[7 empty] | C: 1302 MULESHOE 138 1307 KEYLYNTE 138 1 | 952
Open 1302 MULESHOE 138 1307 KEYLYNTE 138 1
|  |  | 2039.4 | 2053.6 | -14.2 | L: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 |  |  | 52.7 | 186 | 186 | 0.06537 | -0.06672
[7 empty] | C: 1163 LAMESA_8 138 1307 KEYLYNTE 138 1 | 867
Open 1163 LAMESA_8 138 1307 KEYLYNTE 138 1
|  |  | 2070.3 | 2053.6 | 16.6 | L: 1163 LAMESA_8 138 1307 KEYLYNTE 138 1 |  |  | 49.4 | 186 | 186 | 0.06597 | -0.06672
[7 empty] | C: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 | 947
Open 1300 EXSHARNR 138 1301 WILLOWVA 138 1
|  |  | 1998.8 | 2075.7 | -76.9 | L: 1334 CHNGOWNR 138 1339 ESKOTA_8 138 1 |  |  | 94.8 | 214 | 214 | 0.05962 | -0.05891
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 1563.6 | 2096.8 | -533.2 | L: 1302 MULESHOE 138 1307 KEYLYNTE 138 1 |  |  | 46.7 | 150.1 | 186 | 0.06612 | 0.06672
|  |  | NotConv |  |  |  | C: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 | 948
Open 1300 EXSHARNR 138 1309 BLUFCKTA 138 1
|  |  | 2069.2 | 2096.8 | -27.6 | L: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 |  |  | 51.6 | 186 | 186 | 0.06491 | 0.06672
[7 empty] | C: 1302 MULESHOE 138 1307 KEYLYNTE 138 1 | 952
Open 1302 MULESHOE 138 1307 KEYLYNTE 138 1
|  |  | 2516.9 | 2164.6 | 352.3 | L: 1876 WLFHOLW_ 345 1880 ROCKYCRK 345 1 |  |  | 923.2 | 1071.8 | 1072 | 0.05907 | 0.06267
[7 empty] | C: 1890 DECRDOVA 345 1900 COMCHPKW 345 11 | 593
Open 1890 DECRDOVA 345 1900 COMCHPKW 345 1
|  |  | 2174.6 | 2199.9 | -25.2 | L: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 |  |  | 44.9 | 186 | 186 | 0.06484 | 0.06672
[7 empty] | C: 1163 LAMESA_8 138 1307 KEYLYNTE 138 1 | 867
Open 1163 LAMESA_8 138 1307 KEYLYNTE 138 1
|  |  | 2189.2 | 2199.9 | -10.6 | L: 1163 LAMESA_8 138 1307 KEYLYNTE 138 1 |  |  | 39.8 | 184 | 186 | 0.06588 | -0.06672
|  |  | NotConv |  |  |  | C: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 | 948
Open 1300 EXSHARNR 138 1309 BLUFCKTA 138 1
|  |  | 2291.3 | 2371.6 | -80.3 | L: 1334 CHNGOWNR 138 1339 ESKOTA_8 138 1 |  |  | 90.1 | 214.6 | 214 | 0.05431 | -0.05346
[7 empty] | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 2327.1 | 2420.7 | -93.6 | L: 1334 CHNGOWNR 138 76319 MCELMUR 138 1 |  |  | 94.6 | 233.7 | 234 | 0.05978 | 0.05891
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2429.1 | 2432.6 | -3.5 | L: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 |  |  | 36.8 | 186.5 | 186 | 0.06161 | -0.0614
[7 empty] | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2363.6 | 2480.9 | -117.3 | L: 76317 POTTERTP 138 76319 MCELMUR 138 1 |  |  | 91.5 | 234.6 | 234.2 | 0.06054 | -0.05891
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2451.7 | 2489.2 | -37.5 | L: 1464 WFALLS_S 138 1478 ARROWHD_ 138 1 |  |  | 68.2 | 143 | 143 | 0.0305 | -0.03211
[7 empty] | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 2290.8 | 2535.9 | -245.1 | L: 6260 ABSO4A 138 76317 POTTERTP 138 1 |  |  | 88.7 | 227.7 | 234 | 0.06069 | -0.05891
|  |  | NotConv |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2577.4 | 2553 | 24.4 | L: 6235 ABMULCW7 345 71050 BITTERCR 345 1 |  |  | 471 | 1072.1 | 1072 | 0.23323 | -0.23641
[7 empty] | C: 76009 L_TWINBU 345 76090 L_DIVIDE 345 16 | 611
Open 76009 L_TWINBU 345 76090 L_DIVIDE 345 1
|  |  | 2546.7 | 2591.5 | -44.8 | L: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 |  |  | 29.8 | 185.6 | 186 | 0.06114 | 0.0614
[7 empty] | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2674.3 | 2644.6 | 29.8 | L: 6235 ABMULCW7 345 71050 BITTERCR 345 1 |  |  | 417.4 | 1071.9 | 1072 | 0.24476 | -0.25002
[7 empty] | C: 1414 CHAMPNCR 345 1420 SWEETWTR 345 11 | 67
Open 1414 CHAMPNCR 345 1420 SWEETWTR 345 1
|  |  | 2668.1 | 2646.7 | 21.4 | L: 6235 ABMULCW7 345 71050 BITTERCR 345 1 |  |  | 417.4 | 1072 | 1072 | 0.24535 | -0.25002
[7 empty] | C: 1420 SWEETWTR 345 1439 LONCREK2 345 11 | 69
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 2696.3 | 2700 | -3.7 | L: 1371 MURRY_P8 138 1431 GRHAMSES 138 1 |  |  | 11.4 | 142.6 | 143 | 0.04866 | 0.05783
[7 empty] | C:COOKFIELD / LONGCREEK - GRAHAM8 | 912
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 2896.4 | 2714.4 | 182 | L: 1421 WILLOWCK 345 1436 PARKER_5 345 1 |  |  | 521.6 | 1072 | 1072 | 0.19001 | 0.20262
[7 empty] | C: 1430 GRHAMSES 345 1436 PARKER_5 345 11 | 96
Open 1430 GRHAMSES 345 1436 PARKER_5 345 1
|  |  | 2896.4 | 2714.4 | 182 | L: 1421 WILLOWCK 345 1436 PARKER_5 345 1 |  |  | 521.6 | 1072 | 1072 | 0.19001 | 0.20262
[7 empty] | C: 1430 GRHAMSES 345 1436 PARKER_5 345 21 | 97
Open 1430 GRHAMSES 345 1436 PARKER_5 345 2
|  |  | 1812.4 | 2719.9 | -907.5 | L: 1371 MURRY_P8 138 1431 GRHAMSES 138 1 |  |  | 12.4 | 91.4 | 143 | 0.0436 | 0.05783
|  |  | NotConv |  |  |  | C:GRAHAM - LONGCREEK / LONGCREEK - COOKFIELD8 | 911
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1439 LONCREK2 345 1442 COKFIELD 345 1
|  |  | 2617.7 | 2751.8 | -134.1 | L: 1334 CHNGOWNR 138 76319 MCELMUR 138 1 |  |  | 89.9 | 234 | 234 | 0.05505 | 0.05346
[7 empty] | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 2697.4 | 2760.8 | -63.4 | L: 1048 TONKAWA_ 345 1430 GRHAMSES 345 1 |  |  | 337.1 | 1061 | 1072 | 0.26837 | 0.26774
|  |  | NotConv |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2645.4 | 2818.2 | -172.9 | L: 76317 POTTERTP 138 76319 MCELMUR 138 1 |  |  | 86.8 | 233.9 | 234.2 | 0.05561 | -0.05346
[7 empty] | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 2517.7 | 2833.3 | -315.7 | L: 1371 MURRY_P8 138 1431 GRHAMSES 138 1 |  |  | 17.8 | 124.7 | 143 | 0.04246 | 0.05745
|  |  | NotConv |  |  |  | C:SWEETWATER / MULBERRY - LONGCREEK8 | 910
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 2538.4 | 2856.7 | -318.3 | L: 1640 LINGLVLL 138 1642 FLATCRK_ 138 1 |  |  | 13.9 | 55.1 | 84 | 0.01625 | -0.03416
|  |  | NotConv |  |  |  | C: 1440 COMCHESS 345 1441 COMCHESS 138 11 | 118
Open 1440 COMCHESS 345 1441 COMCHESS 138 1
|  |  | 2990.3 | 2857.6 | 132.7 | L: 1371 MURRY_P8 138 6169 PAIP4B 138 1 |  |  | 10.6 | 155 | 155 | 0.04828 | -0.05783
[7 empty] | C:COOKFIELD / LONGCREEK - GRAHAM8 | 912
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 3020.1 | 2877.5 | 142.7 | L: 1371 MURRY_P8 138 6169 PAIP4B 138 1 |  |  | 11.4 | 155.2 | 155 | 0.04762 | -0.05783
[7 empty] | C:GRAHAM - LONGCREEK / LONGCREEK - COOKFIELD8 | 911
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1439 LONCREK2 345 1442 COKFIELD 345 1
|  |  | 2766.2 | 2878.8 | -112.5 | L: 6260 ABSO4A 138 76317 POTTERTP 138 1 |  |  | 84 | 233.6 | 234 | 0.05409 | -0.05346
[7 empty] | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 3115.6 | 2894.1 | 221.5 | L: 1425 FISHRDSS 345 6100 OKLA7A 345 1 |  |  | 497.8 | 1071.9 | 1072 | 0.18427 | -0.19616
[7 empty] | C:COOKFIELD / LONGCREEK - GRAHAM8 | 912
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 3199.7 | 2905.9 | 293.8 | L: 3436 WACO_W1_ 138 3591 WACOWOOD 138 1 |  |  | 45.7 | 213.7 | 214 | 0.0525 | 0.0615
[7 empty] | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2643.8 | 2910.9 | -267.1 | L: 76009 L_TWINBU 345 B$0034 TWA1 1.00 1 |  |  | 195.5 | 308.5 | 308 | 0.04276 | 0.03977
[7 empty] | C: 6444 SARC7A 345 76009 L_TWINBU 345 14 | 83
Open 6444 SARC7A 345 76009 L_TWINBU 345 1
|  |  | 2951.7 | 2912.6 | 39.2 | L: 1425 FISHRDSS 345 1426 FISHRDSS 138 1 |  |  | 331.4 | 493.8 | 501 | 0.05502 | 0.05867
|  |  | TDF_Sign |  |  |  | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 3681.7 | 2914.4 | 767.3 | L: 1640 LINGLVLL 138 1642 FLATCRK_ 138 1 |  |  | 30 | 84.6 | 84 | 0.01483 | -0.03927
[7 empty] | C: 1440 COMCHESS 345 6444 SARC7A 345 11 | 120
Open 1440 COMCHESS 345 6444 SARC7A 345 1
|  |  | 2042 | 2914.7 | -872.7 | L: 76011 L_TWINBU 138 B$0034 TWA1 1.00 1 |  |  | 197.7 | 278.6 | 308 | 0.03962 | -0.03977
|  |  | NotConv |  |  |  | C: 6444 SARC7A 345 76009 L_TWINBU 345 14 | 83
Open 6444 SARC7A 345 76009 L_TWINBU 345 1
|  |  | 3161.5 | 2919 | 242.5 | L: 1425 FISHRDSS 345 6100 OKLA7A 345 1 |  |  | 493.1 | 1071.9 | 1072 | 0.18309 | -0.19616
[7 empty] | C:GRAHAM - LONGCREEK / LONGCREEK - COOKFIELD8 | 911
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1439 LONCREK2 345 1442 COKFIELD 345 1
|  |  | 2735.8 | 2924.1 | -188.2 | L: 1032 MRGNCRK_ 138 1333 MCDDONAL 138 1 |  |  | 70.7 | 185.6 | 186 | 0.04198 | -0.04004
[7 empty] | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2735.8 | 2924.1 | -188.2 | L: 1032 MRGNCRK_ 138 1333 MCDDONAL 138 1 |  |  | 70.7 | 185.6 | 186 | 0.04198 | -0.04004
[7 empty] | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2743.8 | 2927.8 | -184 | L: 1032 MRGNCRK_ 138 1333 MCDDONAL 138 1 |  |  | 70.5 | 186 | 186 | 0.04211 | -0.04007
[7 empty] | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 3137.3 | 2992 | 145.3 | L: 1371 MURRY_P8 138 6169 PAIP4B 138 1 |  |  | 16.1 | 154.9 | 155 | 0.04427 | -0.05745
[7 empty] | C:SWEETWATER / MULBERRY - LONGCREEK8 | 910
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 3260.2 | 2993.4 | 266.8 | L: 1048 TONKAWA_ 345 1430 GRHAMSES 345 1 |  |  | 247.6 | 1074.7 | 1072 | 0.2537 | 0.27932
|  |  | TDF_Sign |  |  |  | C:SWEETWATER / MULBERRY - LONGCREEK8 | 910
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 2864.8 | 3001.4 | -136.6 | L: 1021 MIDLET_5 345 1022 MIDLNDE_ 345 1 |  |  | 606.1 | 959.3 | 956 | 0.1233 | -0.11727
|  |  | NotConv |  |  |  | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 2993 | 3010.3 | -17.3 | L: 1021 MIDLET_5 345 1022 MIDLNDE_ 345 1 |  |  | 607.9 | 929.9 | 956 | 0.10757 | -0.11631
|  |  | NotConv |  |  |  | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2993 | 3010.3 | -17.3 | L: 1021 MIDLET_5 345 1022 MIDLNDE_ 345 1 |  |  | 607.9 | 929.9 | 956 | 0.10757 | -0.11631
|  |  | NotConv |  |  |  | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 3011.2 | 3011.6 | -0.5 | L: 1624 LEONSW_8 138 1642 FLATCRK_ 138 1 |  |  | 19.6 | 70.3 | 84 | 0.01683 | 0.03416
|  |  | NotConv |  |  |  | C: 1440 COMCHESS 345 1441 COMCHESS 138 11 | 118
Open 1440 COMCHESS 345 1441 COMCHESS 138 1
|  |  | 3253.7 | 3019 | 234.7 | L: 1048 TONKAWA_ 345 1430 GRHAMSES 345 1 |  |  | 257.3 | 1072.2 | 1072 | 0.25045 | 0.27343
[7 empty] | C:COOKFIELD / LONGCREEK - GRAHAM8 | 912
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 2849.1 | 3024.8 | -175.8 | L: 1654 ZEPHYR_P 138 1655 BRNWDSW_ 138 1 |  |  | 86.4 | 184.9 | 191 | 0.03459 | 0.03669
|  |  | TDF_Sign |  |  |  | C:COMANCHE SW-STEPHENVILLE-BROWNWOOD-DUBLIN8 | 743
Open 277 HASSE 69.0 1649 HASSE_P8 138 1
Open 1441 COMCHESS 138 1650 COMANCHE 138 1
Open 1441 COMCHESS 138 1661 BRNWD1_8 138 1
Open 1636 DUBLIN1_ 138 1637 DUBLIN1_ 69.0 1
Open 1636 DUBLIN1_ 138 1641 STPHNVIL 138 1
Open 1636 DUBLIN1_ 138 1649 HASSE_P8 138 1
Open 1649 HASSE_P8 138 1650 COMANCHE 138 1
|  |  | 3229.1 | 3044.2 | 184.9 | L: 1900 COMCHPKW 345 1902 JHNSONSW 345 1 |  |  | 1184.3 | 1630.8 | 1631 | 0.13829 | 0.13947
[7 empty] | C: WLFHOLW_5-ROCKYCRK_5 & DECRDOVA_5-COMCHPKW_59 | 277
Open 1876 WLFHOLW_ 345 1880 ROCKYCRK 345 1
Open 1890 DECRDOVA 345 1900 COMCHPKW 345 1
|  |  | 3537.4 | 3049.2 | 488.2 | L: 1624 LEONSW_8 138 1642 FLATCRK_ 138 1 |  |  | 36.2 | 84.1 | 84 | 0.01353 | 0.03927
[7 empty] | C: 1440 COMCHESS 345 6444 SARC7A 345 11 | 120
Open 1440 COMCHESS 345 6444 SARC7A 345 1
|  |  | 3636.1 | 3091.4 | 544.7 | L: 3650 ELGIN_SS 138 13430 SAND_TXU 138 1 |  |  | 80.9 | 218.8 | 214 | 0.03792 | -0.04273
|  |  | TDF_Sign |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 2919.8 | 3110.7 | -190.9 | L: 6444 SARC7A 345 76009 L_TWINBU 345 1 |  |  | 452.3 | 1314.6 | 1315 | 0.29533 | -0.27627
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 1559.5 | 3127.2 | -1567.7 | L: 1339 ESKOTA_8 138 1341 SWTRDTAP 138 1 |  |  | 107.8 | 161 | 214 | 0.03412 | -0.03398
|  |  | NotConv |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3078.2 | 3129.2 | -51 | L: 1448 WCHTFLLS 138 1480 RATHGBER 138 1 |  |  | 88 | 186.2 | 186 | 0.0319 | 0.03211
[7 empty] | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 3035.9 | 3152.1 | -116.1 | L: 1309 BLUFCKTA 138 1318 CHINAGRV 138 1 |  |  | 62.9 | 180.8 | 186 | 0.03885 | 0.07919
|  |  | NotConv |  |  |  | C: 1064 SUN_8 138 1067 GOLDENSW 138 1 | 781
Open 1064 SUN_8 138 1067 GOLDENSW 138 1
|  |  | 2389.4 | 3158.8 | -769.4 | L: 1425 FISHRDSS 345 6100 OKLA7A 345 1 |  |  | 461.8 | 907.3 | 1072 | 0.18647 | -0.1913
|  |  | NotConv |  |  |  | C:SWEETWATER / MULBERRY - LONGCREEK8 | 910
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 3020.3 | 3171.5 | -151.2 | L: 1021 MIDLET_5 345 1025 FSCOGEN_ 345 1 |  |  | 496.2 | 955.7 | 956 | 0.15214 | 0.15645
[7 empty] | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 3003.2 | 3178 | -174.8 | L: 1654 ZEPHYR_P 138 1655 BRNWDSW_ 138 1 |  |  | 83 | 184.1 | 191 | 0.03365 | 0.03591
|  |  | NotConv |  |  |  | C:COMANCHE SW-STEPHENVILLE-BROWNWOOD8 | 734
Open 1441 COMCHESS 138 1650 COMANCHE 138 1
Open 1441 COMCHESS 138 1661 BRNWD1_8 138 1
|  |  | 2210.8 | 3185.2 | -974.5 | L: 1021 MIDLET_5 345 1025 FSCOGEN_ 345 1 |  |  | 498.9 | 849.8 | 956 | 0.15874 | 0.15487
|  |  | NotConv |  |  |  | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 2210.8 | 3185.2 | -974.5 | L: 1021 MIDLET_5 345 1025 FSCOGEN_ 345 1 |  |  | 498.9 | 849.8 | 956 | 0.15874 | 0.15487
|  |  | NotConv |  |  |  | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 3214.9 | 3196.7 | 18.2 | L: 1030 MRGNCRK_ 345 71050 BITTERCR 345 1 |  |  | 407.5 | 956 | 956 | 0.17062 | 0.16975
[7 empty] | C: 76009 L_TWINBU 345 76090 L_DIVIDE 345 16 | 611
Open 76009 L_TWINBU 345 76090 L_DIVIDE 345 1
|  |  | 3110.8 | 3205.7 | -95 | L: 1310 KNAPP_8 138 1312 SCURYCHV 138 1 |  |  | 9.3 | 123.8 | 124 | 0.03681 | 0.0412
[7 empty] | C: 1309 BLUFCKTA 138 1318 CHINAGRV 138 1 | 966
Open 1309 BLUFCKTA 138 1318 CHINAGRV 138 1
|  |  | 2142 | 3213.5 | -1071.5 | L: 1640 LINGLVLL 138 1642 FLATCRK_ 138 1 |  |  | 25.7 | 31.8 | 84 | 0.00286 | -0.03387
|  |  | NotConv |  |  |  | C:COOKFIELD / LONGCREEK - GRAHAM8 | 912
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 1602.4 | 3232 | -1629.6 | L: 1430 GRHAMSES 345 1442 COKFIELD 345 1 |  |  | 197.9 | 609.8 | 1072 | 0.25709 | -0.27223
|  |  | NotConv |  |  |  | C: 1430 GRHAMSES 345 1435 LONGCREK 345 11 | 95
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
|  |  | 3401.7 | 3246.1 | 155.6 | L: 1430 GRHAMSES 345 1435 LONGCREK 345 1 |  |  | 197.1 | 1072 | 1072 | 0.2572 | -0.27173
[7 empty] | C: 1430 GRHAMSES 345 1442 COKFIELD 345 11 | 98
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 3326.6 | 3273.8 | 52.8 | L: 1030 MRGNCRK_ 345 71050 BITTERCR 345 1 |  |  | 351.4 | 956 | 956 | 0.18176 | 0.18336
[7 empty] | C: 1414 CHAMPNCR 345 1420 SWEETWTR 345 11 | 67
Open 1414 CHAMPNCR 345 1420 SWEETWTR 345 1
|  |  | 3334.8 | 3276.7 | 58.1 | L: 1030 MRGNCRK_ 345 71050 BITTERCR 345 1 |  |  | 351.4 | 956 | 956 | 0.1813 | 0.18336
[7 empty] | C: 1420 SWEETWTR 345 1439 LONCREK2 345 11 | 69
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 2436.5 | 3280.4 | -843.9 | L: 1430 GRHAMSES 345 1435 LONGCREK 345 1 |  |  | 188.1 | 815.1 | 1072 | 0.25732 | -0.27173
|  |  | NotConv |  |  |  | C: 1439 LONCREK2 345 1442 COKFIELD 345 11 | 117
Open 1439 LONCREK2 345 1442 COKFIELD 345 1
|  |  | 3556.8 | 3292.3 | 264.5 | L: 1439 LONCREK2 345 1442 COKFIELD 345 1 |  |  | 180 | 1071.4 | 1072 | 0.25064 | 0.27223
[7 empty] | C: 1430 GRHAMSES 345 1435 LONGCREK 345 11 | 95
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
|  |  | 1656.4 | 3298.2 | -1641.8 | L: 1654 ZEPHYR_P 138 1655 BRNWDSW_ 138 1 |  |  | 80.5 | 132.6 | 191 | 0.03144 | 0.03328
|  |  | NotConv |  |  |  | C: 1656 BRNWD_S_ 138 1661 BRNWD1_8 138 11 | 300
Open 1656 BRNWD_S_ 138 1661 BRNWD1_8 138 1
|  |  | 2442.9 | 3299.4 | -856.5 | L: 1435 LONGCREK 345 6230 ABMULCE7 345 1 |  |  | 109.1 | 811.9 | 1072 | 0.28771 | -0.29525
|  |  | NotConv |  |  |  | C: 1414 CHAMPNCR 345 1420 SWEETWTR 345 11 | 67
Open 1414 CHAMPNCR 345 1420 SWEETWTR 345 1
|  |  | 2442.9 | 3302 | -859.1 | L: 1435 LONGCREK 345 6230 ABMULCE7 345 1 |  |  | 109 | 806.9 | 1072 | 0.28567 | -0.29525
|  |  | NotConv |  |  |  | C: 1420 SWEETWTR 345 1439 LONCREK2 345 11 | 69
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 4233.2 | 3331.8 | 901.4 | L: 44645 SNGLTN_3 345 45500 T_H_W___ 345 98 |  |  | 914.9 | 1348.9 | 1450 | 0.10253 | 0.15457
|  |  | TDF_Sign |  |  |  | C:SNGLTN - TOMBAL_74 (44645-46500) & ROANS - KING_757 | 984
Open 40600 ROANS___ 345 45972 KUYDAL75 345 75
Open 40900 KING____ 345 45972 KUYDAL75 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 3879.7 | 3338 | 541.7 | L: 1876 WLFHOLW_ 345 1880 ROCKYCRK 345 1 |  |  | 797.4 | 1072 | 1072 | 0.07078 | 0.07988
[7 empty] | C:VENUS_N5-JHNSONSW_P5 & VENUS_N5-COMCHPKW_59 | 323
Open 393 CONCORD 345 394 CONCORD 138 1
Open 1891 DECRDOVA 138 2281 GODLEY_8 138 1
Open 1900 COMCHPKW 345 1902 JHNSONSW 345 1
Open 1902 JHNSONSW 345 1907 VENUS_N5 345 1
|  |  | 3365.1 | 3369.8 | -4.6 | L: 1624 LEONSW_8 138 1642 FLATCRK_ 138 1 |  |  | 31.8 | 84.2 | 84 | 0.01558 | 0.03387
[7 empty] | C:COOKFIELD / LONGCREEK - GRAHAM8 | 912
Open 1430 GRHAMSES 345 1435 LONGCREK 345 1
Open 1430 GRHAMSES 345 1442 COKFIELD 345 1
|  |  | 3774.4 | 3386.6 | 387.9 | L: 1430 GRHAMSES 345 1436 PARKER_5 345 2 |  |  | 321.8 | 1072.1 | 1072 | 0.19879 | 0.22186
[7 empty] | C: 1430 GRHAMSES 345 1436 PARKER_5 345 11 | 96
Open 1430 GRHAMSES 345 1436 PARKER_5 345 1
|  |  | 3774.4 | 3386.6 | 387.9 | L: 1430 GRHAMSES 345 1436 PARKER_5 345 1 |  |  | 321.8 | 1072.1 | 1072 | 0.19879 | 0.22186
[7 empty] | C: 1430 GRHAMSES 345 1436 PARKER_5 345 21 | 97
Open 1430 GRHAMSES 345 1436 PARKER_5 345 2
|  |  | 3344.5 | 3389.5 | -45 | L: 1334 CHNGOWNR 138 1339 ESKOTA_8 138 1 |  |  | 71.8 | 219.7 | 214 | 0.04421 | -0.04288
|  |  | LowSens |  |  |  | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3331 | 3399.7 | -68.7 | L: 1869 BENBRK_A 345 1874 BENBRK_A 138 1 |  |  | 443.9 | 599.4 | 599 | 0.04669 | 0.05091
[7 empty] | C: 1870 BENBRK_B 345 1873 BENBRK_5 345 11 | 551
Open 1870 BENBRK_B 345 1873 BENBRK_5 345 1
|  |  | 3378.9 | 3410.6 | -31.7 | L: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 |  |  | 10.6 | 186 | 186 | 0.0519 | -0.05316
Base Case
|  |  | 3424.6 | 3426.2 | -1.6 | L: 1309 BLUFCKTA 138 1318 CHINAGRV 138 1 |  |  | 23.5 | 185.5 | 186 | 0.04732 | 0.05997
[7 empty] | C: 1302 MULESHOE 138 1307 KEYLYNTE 138 1 | 952
Open 1302 MULESHOE 138 1307 KEYLYNTE 138 1
|  |  | 3388.5 | 3444.8 | -56.3 | L: 1435 LONGCREK 345 6230 ABMULCE7 345 1 |  |  | 227.4 | 1030.5 | 1072 | 0.23701 | -0.24907
|  |  | NotConv |  |  |  | C: 1425 FISHRDSS 345 6100 OKLA7A 345 11 | 86
Open 1425 FISHRDSS 345 6100 OKLA7A 345 1
|  |  | 3867.9 | 3473 | 394.9 | L: 3591 WACOWOOD 138 3592 WACOATCO 138 1 |  |  | 18.7 | 214.5 | 214 | 0.05063 | 0.0615
[7 empty] | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4075 | 3496.4 | 578.6 | L: 3402 LAKE_CRK 345 3405 THOUSE__ 345 2 |  |  | 96.6 | 955.6 | 956 | 0.21079 | -0.28033
[7 empty] | C: THOUSE__5-LAKE_CRK1_5 & THOUSE__5-AEP_PEC__59 | 245
Open 3405 THOUSE__ 345 3409 LAKE_CRK 345 1
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
|  |  | 3507.1 | 3507.1 | 0 | L: 1309 BLUFCKTA 138 1318 CHINAGRV 138 1 |  |  | 26.9 | 185.8 | 186 | 0.04531 | 0.05997
[7 empty] | C: 1163 LAMESA_8 138 1307 KEYLYNTE 138 1 | 867
Open 1163 LAMESA_8 138 1307 KEYLYNTE 138 1
|  |  | 2929.3 | 3522.3 | -593 | L: 1441 COMCHESS 138 1654 ZEPHYR_P 138 1 |  |  | 91 | 188 | 214 | 0.03312 | 0.03669
|  |  | LowSens |  |  |  | C:COMANCHE SW-STEPHENVILLE-BROWNWOOD-DUBLIN8 | 743
Open 277 HASSE 69.0 1649 HASSE_P8 138 1
Open 1441 COMCHESS 138 1650 COMANCHE 138 1
Open 1441 COMCHESS 138 1661 BRNWD1_8 138 1
Open 1636 DUBLIN1_ 138 1637 DUBLIN1_ 69.0 1
Open 1636 DUBLIN1_ 138 1641 STPHNVIL 138 1
Open 1636 DUBLIN1_ 138 1649 HASSE_P8 138 1
Open 1649 HASSE_P8 138 1650 COMANCHE 138 1
|  |  | 3502.4 | 3526.2 | -23.8 | L: 1414 CHAMPNCR 345 1420 SWEETWTR 345 1 |  |  | 315.5 | 1072.3 | 1072 | 0.21608 | 0.21576
[7 empty] | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3521.8 | 3531.6 | -9.8 | L: 1420 SWEETWTR 345 1439 LONCREK2 345 1 |  |  | 311.1 | 1072.6 | 1072 | 0.21622 | 0.21576
[7 empty] | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 1785.6 | 3561.4 | -1775.9 | L: 6444 SARC7A 345 76009 L_TWINBU 345 1 |  |  | 428 | 874.4 | 1315 | 0.25 | -0.24789
|  |  | NotConv |  |  |  | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 2953.6 | 3562.8 | -609.2 | L: 1018 MOSS_5 345 1028 ODESEHV_ 345 1 |  |  | 745.5 | 1071.9 | 1072 | 0.1105 | -0.09507
[7 empty] | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 1772.4 | 3570.3 | -1797.9 | L: 1441 COMCHESS 138 1650 COMANCHE 138 1 |  |  | 9.1 | 89.7 | 186 | 0.04543 | 0.04979
|  |  | NotConv |  |  |  | C: 1440 COMCHESS 345 1900 COMCHPKW 345 11 | 119
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
|  |  | 1718.8 | 3573.5 | -1854.8 | L: 1018 MOSS_5 345 1028 ODESEHV_ 345 1 |  |  | 746.7 | 947.1 | 1072 | 0.11656 | -0.09443
|  |  | NotConv |  |  |  | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 1718.8 | 3573.5 | -1854.8 | L: 1018 MOSS_5 345 1028 ODESEHV_ 345 1 |  |  | 746.7 | 947.1 | 1072 | 0.11656 | -0.09443
|  |  | NotConv |  |  |  | C:MRGNCRK - QUAIL / LONGSHORE8 | 966
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 3965.4 | 3574.9 | 390.5 | L: 1430 GRHAMSES 345 1436 PARKER_5 345 2 |  |  | 353 | 1071.9 | 1072 | 0.1813 | 0.20139
[7 empty] | C: 1421 WILLOWCK 345 1436 PARKER_5 345 11 | 73
Open 1421 WILLOWCK 345 1436 PARKER_5 345 1
|  |  | 3965.4 | 3574.9 | 390.5 | L: 1430 GRHAMSES 345 1436 PARKER_5 345 1 |  |  | 353 | 1071.9 | 1072 | 0.1813 | 0.20139
[7 empty] | C: 1421 WILLOWCK 345 1436 PARKER_5 345 11 | 73
Open 1421 WILLOWCK 345 1436 PARKER_5 345 1
|  |  | 3594.1 | 3594.1 | 0 | L: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 |  |  | 12.8 | 186.1 | 186 | 0.04821 | 0.05316
Base Case
|  |  | 3183.2 | 3621.9 | -438.7 | L: 1398 RADIUMMT 138 6161 PAIP4A 138 1 |  |  | 40 | 155.2 | 155 | 0.03619 | 0.03224
[7 empty] | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3709.8 | 3639.2 | 70.6 | L: 1441 COMCHESS 138 1650 COMANCHE 138 1 |  |  | 13.7 | 170 | 186 | 0.04214 | 0.04755
|  |  | TDF_Sign |  |  |  | C: COMCHESS1_5-COMCHPKW_5 & STPHNVIL_8-CMPKSTUP_88 | 749
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
Open 1641 STPHNVIL 138 2278 CMPKSTUP 138 1
|  |  | 3468.8 | 3656.5 | -187.8 | L: 1301 WILLOWVA 138 1308 GAILLYNT 138 1 |  |  | 36.3 | 185.9 | 186 | 0.04313 | 0.04106
[7 empty] | C: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 | 947
Open 1300 EXSHARNR 138 1301 WILLOWVA 138 1
|  |  | 2702.9 | 3683.1 | -980.2 | L: 1870 BENBRK_B 345 1875 BENBRK_B 138 1 |  |  | 475.8 | 570.2 | 570 | 0.03493 | 0.03087
[7 empty] | C: 1869 BENBRK_A 345 1874 BENBRK_A 138 11 | 550
Open 1869 BENBRK_A 345 1874 BENBRK_A 138 1
|  |  | 4078 | 3686.2 | 391.8 | L: 1441 COMCHESS 138 1654 ZEPHYR_P 138 1 |  |  | 87.6 | 213.6 | 214 | 0.03089 | 0.03591
[7 empty] | C:COMANCHE SW-STEPHENVILLE-BROWNWOOD8 | 734
Open 1441 COMCHESS 138 1650 COMANCHE 138 1
Open 1441 COMCHESS 138 1661 BRNWD1_8 138 1
|  |  | 3494.7 | 3703 | -208.3 | L: 1302 MULESHOE 138 1308 GAILLYNT 138 1 |  |  | 34.3 | 185.9 | 186 | 0.04337 | -0.04106
[7 empty] | C: 1300 EXSHARNR 138 1301 WILLOWVA 138 1 | 947
Open 1300 EXSHARNR 138 1301 WILLOWVA 138 1
|  |  | 3940.9 | 3777.5 | 163.4 | L: 1478 ARROWHD_ 138 1480 RATHGBER 138 1 |  |  | 69.6 | 187.9 | 186 | 0.03001 | -0.03211
|  |  | LowSens |  |  |  | C: 1422 BOWMAN_5 345 1425 FISHRDSS 345 11 | 77
Open 1422 BOWMAN_5 345 1425 FISHRDSS 345 1
|  |  | 1941.5 | 3788.9 | -1847.4 | L: 1876 WLFHOLW_ 345 1880 ROCKYCRK 345 1 |  |  | 774.1 | 913.9 | 1072 | 0.07202 | 0.07657
|  |  | NotConv |  |  |  | C: 1900 COMCHPKW 345 1902 JHNSONSW 345 11 | 605
Open 1900 COMCHPKW 345 1902 JHNSONSW 345 1
|  |  | 4004.3 | 3795.3 | 209 | L: 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1 |  |  | 141.6 | 1000.3 | 1072 | 0.21445 | 0.29471
|  |  | NotConv |  |  |  | C: 3405 THOUSE__ 345 3412 TEMP_PEC 345 12 | 967
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
|  |  | 3631.7 | 3820 | -188.3 | L: 1018 MOSS_5 345 1022 MIDLNDE_ 345 1 |  |  | 606.8 | 1052.6 | 1052 | 0.12274 | 0.11727
[7 empty] | C: ABMULCE7-BLF_CRK7A & SARC7A-BLF_CRK7A8 | 898
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 6230 ABMULCE7 345 60040 BLF_CRK7 345 1
Open 6444 SARC7A 345 60040 BLF_CRK7 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
Open 32859 BRYN_JK_ 138 32882 BRYN_TAB 138 1
Open 32881 BRYN_KUR 138 32897 BRYN_DSB 138 1
|  |  | 3809.6 | 3835.8 | -26.2 | L: 1018 MOSS_5 345 1022 MIDLNDE_ 345 1 |  |  | 608.7 | 1016.9 | 1052 | 0.10717 | 0.11631
|  |  | NotConv |  |  |  | C:QUAIL / LONGSHORE - MRGNCRK8 | 907
Open 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 3786.7 | 3838.8 | -52.1 | L: 1414 CHAMPNCR 345 1420 SWEETWTR 345 1 |  |  | 193.9 | 1041.1 | 1072 | 0.22374 | 0.23167
|  |  | NotConv |  |  |  | C: 1435 LONGCREK 345 6230 ABMULCE7 345 11 | 109
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 4017.1 | 3843.8 | 173.3 | L: 1420 SWEETWTR 345 1439 LONCREK2 345 1 |  |  | 187.3 | 1071.9 | 1072 | 0.2202 | 0.23167
[7 empty] | C: 1435 LONGCREK 345 6230 ABMULCE7 345 11 | 109
Open 1435 LONGCREK 345 6230 ABMULCE7 345 1
|  |  | 1931.5 | 3846.5 | -1915.1 | L: 1441 COMCHESS 138 1654 ZEPHYR_P 138 1 |  |  | 85.2 | 145.8 | 214 | 0.0314 | 0.03328
|  |  | NotConv |  |  |  | C: 1656 BRNWD_S_ 138 1661 BRNWD1_8 138 11 | 300
Open 1656 BRNWD_S_ 138 1661 BRNWD1_8 138 1
|  |  | 3852.1 | 3852.7 | -0.6 | L: 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1 |  |  | 136.6 | 979.2 | 1072 | 0.21874 | 0.29019
|  |  | NotConv |  |  |  | C: THOUSE__5-LAKE_CRK1_5 & THOUSE__5-AEP_PEC__59 | 245
Open 3405 THOUSE__ 345 3409 LAKE_CRK 345 1
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
|  |  | 2830.5 | 3863.4 | -1032.9 | L: 1430 GRHAMSES 345 1436 PARKER_5 345 1 |  |  | 284.9 | 796 | 1072 | 0.18058 | 0.20422
|  |  | TDF_Sign |  |  |  | C: 1429 JACKSBRO 345 1430 GRHAMSES 345 11 | 90
Open 1429 JACKSBRO 345 1430 GRHAMSES 345 1
|  |  | 2830.5 | 3863.4 | -1032.9 | L: 1430 GRHAMSES 345 1436 PARKER_5 345 2 |  |  | 284.9 | 796 | 1072 | 0.18058 | 0.20422
|  |  | TDF_Sign |  |  |  | C: 1429 JACKSBRO 345 1430 GRHAMSES 345 11 | 90
Open 1429 JACKSBRO 345 1430 GRHAMSES 345 1
|  |  | 3616.4 | 3863.5 | -247.1 | L: 1334 CHNGOWNR 138 76319 MCELMUR 138 1 |  |  | 71.6 | 234.2 | 234 | 0.04496 | 0.04288
[7 empty] | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3858.4 | 3864 | -5.6 | L: 1870 BENBRK_B 345 1875 BENBRK_B 138 1 |  |  | 409 | 571.1 | 570 | 0.04202 | 0.04341
|  |  | LowSens |  |  |  | C: BENBRK_B_T5-SYCMRCRK1_5 & WLFHOLW_5-ROCKYCRK_58 | 698
Open 1870 BENBRK_B 345 1935 SYCMRCRK 345 1
Open 1876 WLFHOLW_ 345 1880 ROCKYCRK 345 1
|  |  | 3741.2 | 3885.5 | -144.3 | L: 1649 HASSE_P8 138 1650 COMANCHE 138 1 |  |  | 14.1 | 154.2 | 186 | 0.03747 | -0.04979
|  |  | NotConv |  |  |  | C: 1440 COMCHESS 345 1900 COMCHPKW 345 11 | 119
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
|  |  | 1941.2 | 3894.1 | -1952.9 | L: 1301 WILLOWVA 138 1308 GAILLYNT 138 1 |  |  | 26.3 | 105 | 186 | 0.04055 | 0.04106
|  |  | NotConv |  |  |  | C: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 | 948
Open 1300 EXSHARNR 138 1309 BLUFCKTA 138 1
|  |  | 3902.4 | 3903 | -0.6 | L: 3405 THOUSE__ 345 3412 TEMP_PEC 345 1 |  |  | 140.3 | 971.5 | 1072 | 0.21299 | 0.28131
|  |  | NotConv |  |  |  | C: 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 12 | 976
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2962.3 | 3921.7 | -959.3 | L: 76009 L_TWINBU 345 76090 L_DIVIDE 345 1 |  |  | 579.6 | 1472.5 | 1676.2 | 0.30143 | -0.27874
|  |  | TDF_Sign |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3926.5 | 3927.1 | -0.6 | L: 3668 RNDROCK1 138 3670 RNDRCKNE 138 1 |  |  | 106.9 | 186.1 | 214 | 0.02016 | -0.08243
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 1952.1 | 3930 | -1977.9 | L: 173 CRAWFORD 138 177 BOSQUE 138 1 |  |  | 47.8 | 135.5 | 237 | 0.04496 | -0.04837
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 3662.8 | 3940.7 | -277.9 | L: 1302 MULESHOE 138 1308 GAILLYNT 138 1 |  |  | 24.3 | 186 | 186 | 0.04415 | -0.04106
[7 empty] | C: 1300 EXSHARNR 138 1309 BLUFCKTA 138 1 | 948
Open 1300 EXSHARNR 138 1309 BLUFCKTA 138 1
|  |  | 3810.4 | 3946.3 | -136 | L: 76317 POTTERTP 138 76319 MCELMUR 138 1 |  |  | 68.5 | 243.3 | 234.2 | 0.04587 | -0.04288
|  |  | TDF_Sign |  |  |  | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3968.6 | 3969.2 | -0.6 | L: 1649 HASSE_P8 138 1650 COMANCHE 138 1 |  |  | 12.6 | 166.6 | 186 | 0.03881 | -0.04755
|  |  | NotConv |  |  |  | C: COMCHESS1_5-COMCHPKW_5 & STPHNVIL_8-CMPKSTUP_88 | 749
Open 1440 COMCHESS 345 1900 COMCHPKW 345 1
Open 1641 STPHNVIL 138 2278 CMPKSTUP 138 1
|  |  | 3842.1 | 3974.3 | -132.2 | L: 1430 GRHAMSES 345 1442 COKFIELD 345 1 |  |  | 180.9 | 962 | 1072 | 0.2033 | -0.22503
|  |  | LowSens |  |  |  | C: 1048 TONKAWA_ 345 1430 GRHAMSES 345 1 | 760
Open 1048 TONKAWA_ 345 1430 GRHAMSES 345 1
|  |  | 3991.3 | 3991.9 | -0.6 | L: 3415 TEMP_SS_ 138 3420 TEMP_PEC 138 1 |  |  | 153.6 | 439.2 | 493 | 0.07155 | -0.15902
|  |  | NotConv |  |  |  | C: LAKE_CRK1_5-AEP_SS__5 & AEP_PEC__5-AEP_SS__59 | 247
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
Open 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1
|  |  | 4044.7 | 4005.4 | 39.4 | L: 1030 MRGNCRK_ 345 1058 LONGSHOR 345 1 |  |  | 493.7 | 1072.2 | 1072 | 0.14304 | -0.1419
[7 empty] | C: 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1 | 737
Open 1030 MRGNCRK_ 345 11016 QUAILSW_ 345 1
|  |  | 3953.7 | 4009 | -55.2 | L: 1414 CHAMPNCR 345 1420 SWEETWTR 345 1 |  |  | 297.8 | 1072.3 | 1072 | 0.19589 | 0.19422
[7 empty] | C:MRGNCRK - BITTER CREEK - MULBERRY8 | 855
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3956 | 4014.9 | -59 | L: 1420 SWEETWTR 345 1439 LONCREK2 345 1 |  |  | 293.1 | 1072.1 | 1072 | 0.19691 | 0.19422
[7 empty] | C:MRGNCRK - BITTER CREEK - MULBERRY8 | 855
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 2481.5 | 4016.4 | -1534.9 | L: 1430 GRHAMSES 345 1435 LONGCREK 345 1 |  |  | 177.3 | 697.1 | 1072 | 0.20947 | -0.22396
|  |  | NotConv |  |  |  | C: 1048 TONKAWA_ 345 1430 GRHAMSES 345 1 | 760
Open 1048 TONKAWA_ 345 1430 GRHAMSES 345 1
|  |  | 4020.2 | 4020.8 | -0.6 | L: 3592 WACOATCO 138 13591 COTTONB_ 138 1 |  |  | 33.4 | 196.9 | 214 | 0.04067 | 0.0615
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2943.2 | 4021.8 | -1078.7 | L: 6260 ABSO4A 138 76317 POTTERTP 138 1 |  |  | 65.7 | 190.4 | 234 | 0.04235 | -0.04288
|  |  | NotConv |  |  |  | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 3876.6 | 4043.8 | -167.2 | L: 1430 GRHAMSES 345 1442 COKFIELD 345 1 |  |  | 253.1 | 1072 | 1072 | 0.21125 | -0.202
[7 empty] | C: 1425 FISHRDSS 345 6100 OKLA7A 345 11 | 86
Open 1425 FISHRDSS 345 6100 OKLA7A 345 1
|  |  | 3962 | 4047.2 | -85.2 | L: 1439 LONCREK2 345 1442 COKFIELD 345 1 |  |  | 162.8 | 1072.6 | 1072 | 0.22961 | 0.22503
[7 empty] | C: 1048 TONKAWA_ 345 1430 GRHAMSES 345 1 | 760
Open 1048 TONKAWA_ 345 1430 GRHAMSES 345 1
|  |  | 3085.6 | 4102.7 | -1017.1 | L: 1431 GRHAMSES 138 1601 GRAHAME_ 138 1 |  |  | 78.7 | 173.2 | 210 | 0.03064 | 0.03189
|  |  | NotConv |  |  |  | C: 1430 GRHAMSES 345 1436 PARKER_5 345 11 | 96
Open 1430 GRHAMSES 345 1436 PARKER_5 345 1
|  |  | 3085.6 | 4102.7 | -1017.1 | L: 1431 GRHAMSES 138 1601 GRAHAME_ 138 1 |  |  | 78.7 | 173.2 | 210 | 0.03064 | 0.03189
|  |  | NotConv |  |  |  | C: 1430 GRHAMSES 345 1436 PARKER_5 345 21 | 97
Open 1430 GRHAMSES 345 1436 PARKER_5 345 2
|  |  | 3803.3 | 4102.8 | -299.6 | L: 1431 GRHAMSES 138 1601 GRAHAME_ 138 1 |  |  | 71.1 | 209.7 | 210 | 0.03645 | 0.03402
[7 empty] | C: 1440 COMCHESS 345 6444 SARC7A 345 11 | 120
Open 1440 COMCHESS 345 6444 SARC7A 345 1
|  |  | 4110.1 | 4110.7 | -0.6 | L: 3593 SPGVALLY 138 13591 COTTONB_ 138 1 |  |  | 38.3 | 197.4 | 214 | 0.03871 | -0.0615
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4118.5 | 4114.9 | 3.7 | L: 1064 SUN_8 138 1311 SACROC_8 138 1 |  |  | 36 | 139 | 143 | 0.02502 | 0.04238
|  |  | NotConv |  |  |  | C: 1309 BLUFCKTA 138 1318 CHINAGRV 138 1 | 966
Open 1309 BLUFCKTA 138 1318 CHINAGRV 138 1
|  |  | 4097.2 | 4118.8 | -21.6 | L: 165 WINDSORS 138 173 CRAWFORD 138 1 |  |  | 38.7 | 217.2 | 237 | 0.04356 | -0.04837
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 3930.6 | 4125 | -194.4 | L: 1439 LONCREK2 345 1442 COKFIELD 345 1 |  |  | 235.9 | 1072 | 1072 | 0.21273 | 0.202
[7 empty] | C: 1425 FISHRDSS 345 6100 OKLA7A 345 11 | 86
Open 1425 FISHRDSS 345 6100 OKLA7A 345 1
|  |  | 4072.9 | 4132.9 | -59.9 | L: 6235 ABMULCW7 345 71050 BITTERCR 345 1 |  |  | 330.2 | 1072.5 | 1072 | 0.18224 | -0.1815
Base Case
|  |  | 1539 | 4136.3 | -2597.3 | L: 1030 MRGNCRK_ 345 1414 CHAMPNCR 345 1 |  |  | 314.2 | 599.7 | 1072 | 0.18551 | 0.1844
|  |  | NotConv |  |  |  | C: 6235 ABMULCW7 345 71050 BITTERCR 345 13 | 884
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 4073.9 | 4148.3 | -74.5 | L: 3407 ELM_MOTT 138 3575 WACONCST 138 1 |  |  | 189.3 | 307.1 | 326 | 0.02892 | 0.03198
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 2125.4 | 4157.7 | -2032.3 | L: 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99 |  |  | 757.9 | 1069.6 | 1450 | 0.14663 | -0.16265
|  |  | NotConv |  |  |  | C:SNGLTN - TOMBAL_74 (44645-46500) & ROANS - KING_757 | 984
Open 40600 ROANS___ 345 45972 KUYDAL75 345 75
Open 40900 KING____ 345 45972 KUYDAL75 345 75
Open 44645 SNGLTN_3 345 46500 TOMBAL__ 345 74
|  |  | 2806.3 | 4210.1 | -1403.8 | L: 3593 SPGVALLY 138 3594 MCGREG_T 138 1 |  |  | 44 | 118.2 | 214 | 0.02645 | 0.0615
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 981.5 | 4244.7 | -3263.2 | L: 3412 TEMP_PEC 345 3420 TEMP_PEC 138 1 |  |  | 167.3 | 279.8 | 750 | 0.1146 | 0.14784
|  |  | NotConv |  |  |  | C: LAKE_CRK1_5-AEP_SS__5 & AEP_PEC__5-AEP_SS__59 | 247
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
Open 3412 TEMP_PEC 345 3414 TEMP_SS_ 345 1
|  |  | 1890.3 | 4255.2 | -2364.9 | L: 3594 MCGREG_T 138 13662 TEMPELMC 138 1 |  |  | 60.4 | 56.3 | 214 | -0.00214 | 0.06491
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4065.5 | 4287.4 | -221.9 | L: 161 MCGREGOR 138 165 WINDSORS 138 1 |  |  | 30.7 | 208.2 | 237 | 0.04367 | -0.04837
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4288.9 | 4305.6 | -16.7 | L: 3666 HUTTOSS1 138 3670 RNDRCKNE 138 1 |  |  | 54.7 | 294.5 | 332 | 0.05591 | 0.08243
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
|  |  | 4144.2 | 4401.2 | -256.9 | L: 137 MOODY 138 161 MCGREGOR 138 1 |  |  | 25.4 | 205.2 | 237 | 0.04339 | -0.04837
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 3339.2 | 4482.3 | -1143.2 | L: 137 MOODY 138 141 MOFFAT 138 1 |  |  | 21.5 | 165.9 | 237 | 0.04324 | 0.04837
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 3547.7 | 4493 | -945.3 | L: 76009 L_TWINBU 345 76090 L_DIVIDE 345 1 |  |  | 553.9 | 1678 | 1676.2 | 0.31684 | -0.2488
|  |  | NotConv |  |  |  | C:MRGNCRK - BITTER CREEK / SWEET WATER - LONGCREEK8 | 970
Open 1030 MRGNCRK_ 345 71050 BITTERCR 345 1
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
|  |  | 2857.6 | 4549 | -1691.4 | L: 1655 BRNWDSW_ 138 7070 L_GOLDTH 138 1 |  |  | 22.1 | 155.3 | 265 | 0.04661 | 0.05309
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 3198.7 | 4575.4 | -1376.8 | L: 1030 MRGNCRK_ 345 1048 TONKAWA_ 345 1 |  |  | 255.8 | 783.3 | 1072 | 0.16492 | 0.17861
|  |  | TDF_Sign |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 4136.5 | 4628.7 | -492.2 | L: 139 LAKEBELT 138 141 MOFFAT 138 1 |  |  | 14.4 | 195.1 | 237 | 0.04368 | -0.04837
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 3408.8 | 4646.6 | -1237.8 | L: 7068 L_EVANT_ 138 7070 L_GOLDTH 138 1 |  |  | 8.4 | 144.8 | 220 | 0.04 | -0.04652
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4086.5 | 4759.6 | -673.1 | L: 7066 L_ADAMSV 138 7068 L_EVANT_ 138 1 |  |  | 8.9 | 162 | 220 | 0.03746 | -0.04652
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4273 | 4762.5 | -489.5 | L: 3413 TEMPSSLT 345 3414 TEMP_SS_ 345 1 |  |  | 98.4 | 874.6 | 1072 | 0.18165 | -0.22351
|  |  | NotConv |  |  |  | C: GIBN_CREK_5-SNGLTN_345 & GIBN_CREK_5-SNGLTN_3459 | 427
Open 967 GIBN_CRE 345 44645 SNGLTN_3 345 75
Open 967 GIBN_CRE 345 44645 SNGLTN_3 345 99
|  |  | 2347.2 | 4764.9 | -2417.6 | L: 6150 SPUR4A 138 6158 ASPM4A 138 1 |  |  | 22.6 | 96.1 | 170 | 0.03131 | 0.03137
|  |  | NotConv |  |  |  | C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | 971
Open 1420 SWEETWTR 345 1439 LONCREK2 345 1
Open 6235 ABMULCW7 345 71050 BITTERCR 345 1
|  |  | 1710.6 | 4824.3 | -3113.6 | L: 1902 JHNSONSW 345 1907 VENUS_N5 345 1 |  |  | 968.8 | 1157.9 | 1595 | 0.11058 | 0.12584
|  |  | LowSens |  |  |  | C: WLFHOLW_5-ROCKYCRK_5 & DECRDOVA_5-COMCHPKW_59 | 277
Open 1876 WLFHOLW_ 345 1880 ROCKYCRK 345 1
Open 1890 DECRDOVA 345 1900 COMCHPKW 345 1
|  |  | 3217.1 | 4826.4 | -1609.3 | L: 3413 TEMPSSLT 345 3414 TEMP_SS_ 345 1 |  |  | 99.3 | 663 | 1072 | 0.17522 | -0.22251
|  |  | NotConv |  |  |  | C: GIBN_CREK_5-JKCREEK1 & GIBN_CREK_5-TWIN_OAK__59 | 423
Open 967 GIBN_CRE 345 975 JKCREEK1 345 1
Open 967 GIBN_CRE 345 3400 TWIN_OAK 345 1
|  |  | 4226.8 | 4846.2 | -619.4 | L: 3413 TEMPSSLT 345 3414 TEMP_SS_ 345 1 |  |  | 156.7 | 865 | 1072 | 0.16757 | -0.21643
|  |  | NotConv |  |  |  | C: AEPLE_N1_8-AEPELMC__8 & AEPLE_N1_8-AEPELMC__89 | 255
Open 3608 TEMPLE_N 138 13662 TEMPELMC 138 1
Open 3608 TEMPLE_N 138 13662 TEMPELMC 138 2
|  |  | 4134.7 | 4856.9 | -722.2 | L: 7064 L_LAMPAS 138 7066 L_ADAMSV 138 1 |  |  | 11.1 | 159.6 | 220 | 0.03591 | -0.04652
|  |  | NotConv |  |  |  | C: THOUSE__5-AEP_PEC__5 & LAKE_CRK1_5-AEP_SS__59 | 246
Open 3405 THOUSE__ 345 3412 TEMP_PEC 345 1
Open 3409 LAKE_CRK 345 3414 TEMP_SS_ 345 1
|  |  | 4269.2 | 4968.3 | -699.1 | L: 3425 BELLCTY_ 138 3640 SALADO1_ 138 1 |  |  | 25.6 | 166.5 | 214 | 0.03301 | 0.03999
|  |  | NotConv |  |  |  | C: SANDOW__5-L_AUSTRO5_1Y & L_AUSTRO5_1Y-SAND_TXU_59 | 253
Open 3429 SANDOW__ 345 7040 L_AUSTRO 345 1
Open 7040 L_AUSTRO 345 13429 SAND_TXU 345 2
Note on A11: PTI: Exporting Subsystem
Note on B11: PTI: Importing Subsystem
Note on C11: PTI: Maximum Test Level
Note on D11: PTI: AC First Contingency Incremental Transfer Capability
Note on E11: PTI: DC First Contingency Incremental Transfer Capability
Note on F11: PTI: Difference between AC FCITC and DC FCITC
Note on G11: PTI: Branch, Flowgate or Interface
Note on H11: PTI: Limiting Contingency. Review MUST options for reporting options
Note on I11: PTI: Contingency Index
Note on J11: PTI: MW Flow before the transfer
Note on K11: PTI: MW Flow after the transfer
Note on L11: PTI: Rating (Base case or Contingent)
Note on M11: PTI: AC Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case
Note on N11: PTI: DC Transfer Distribution Factor, OTDF for the Contigency, PTDF for the base case