## Classes
Package | Internal Class Name | Class | Inheritance Path | Name Space | Documentation | CPSM Nerc | ABB / MMS | Areva / EMS | ABB / OS | Nexant / CRR | PTI / Planning | Lodestar / Settlement data | StereoType | Abstract | NMMS Label
61970 | iec61970CIMVersion | iec61970CIMVersion | Domain | cim | This is the IEC 61970 CIM version number assigned to this UML model file. cim61970_v002 was created from cim10_v000_WG13cimIssues_61968_Rev6_22Feb2005 that is the merged wg13 and wg14 models. The content has a number of wg13 issue resolutions. | TRUE | TRUE | TRUE | TRUE |  | FALSE |  |  | FALSE | iec61970CIMVersion
CIMCore | BasePower | BasePower | IdentifiedObject | cim | The BasePower class defines the base power and base voltages that are used in the per unit calculations. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | BasePower
CIMCore | BaseVoltage | BaseVoltage | IdentifiedObject | cim | Collection of BaseVoltages which is used to verify that the BusbarSection.BaseVoltage and other voltage attributes in the CIM are given a value existing in the collection. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | BaseVoltage
CIMCore | BasicIntervalSchedule | BasicIntervalSchedule | IdentifiedObject | cim | Schedule of values at points in time. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Basic Interval Schedule
CIMCore | Bay | Bay | EquipmentContainer; PowerSystemResource; IdentifiedObject | cim | A collection of power system resources (within a given substation) including conducting equipment, protection relays, measurements, and telemetry. | TRUE | TRUE | FALSE | FALSE |  | FALSE |  |  | FALSE | Bay
CIMCore | Company | Company | IdentifiedObject | cim | A company is a legal entity that owns and operates power system resources and is a party to interchange and transmission contracts. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Company
CIMCore | ConductingEquipment | ConductingEquipment | Equipment; PowerSystemResource; IdentifiedObject | cim | The parts of the power system that are designed to carry current or that are conductively connected therewith. ConductingEquipment is contained within an EquipmentContainer that may be a Substation, or a VoltageLevel or a Bay within a Substation. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | TRUE | ConductingEquipment
CIMCore | ControlHouseEquipment | ControlHouseEquipment | PowerSystemResource; IdentifiedObject | cim | Equipment in a substation control house. Covers things such as fire alarms, ambient temperature, door alarms, and spares. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | ControlHouseEquipment
CIMCore | Curve | Curve | IdentifiedObject | cim | Relationship between an independent variable (X-axis) and one or two dependent variables (Y1-axis and Y2-axis). Curves can also serve as schedules. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | TRUE | Curve
CIMCore | CurveData | CurveData | IdentifiedObject | cim | Data point values for defining a curve or schedule. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | CurveSchedData
CIMCore | Equipment | Equipment | PowerSystemResource; IdentifiedObject | cim | The parts of a power system that are physical devices, electronic or mechanical. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | TRUE | Equipment
CIMCore | EquipmentContainer | EquipmentContainer | PowerSystemResource; IdentifiedObject | cim | A modeling construct to provide a root class for all Equipment classes. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | TRUE | EquipmentContainer
CIMCore | GeographicalRegion | GeographicalRegion | IdentifiedObject | cim | A geographical region of a power system network model. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Geographical Region
CIMCore | IdentifiedObject | IdentifiedObject | Domain | cim | This is a root class to provide common naming attributes for all classes needing naming attributes. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | TRUE | Identified Object
CIMCore | IrregularIntervalSchedule | IrregularIntervalSchedule | BasicIntervalSchedule; IdentifiedObject | cim | The schedule has TimePoints where the time between them varies. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Irregular Interval Schedule
CIMCore | IrregularTimePoint | IrregularTimePoint | Domain | cim | TimePoints for a schedule where the time between the points varies. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Irregular Time Point
CIMCore | ModelingAuthority | ModelingAuthority | IdentifiedObject | cim | A Modeling Authority is an entity responsible for supplying and maintaining the data defining a specific set of objects in a network model. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Modeling Authority
CIMCore | ModelingAuthoritySet | ModelingAuthoritySet | IdentifiedObject | cim | A Modeling Authority Set is a group of objects in a network model where the data is supplied and maintained by the same Modeling Authority. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Modeling Authority Set
CIMCore | PowerSystemResource | PowerSystemResource | IdentifiedObject | cim | A power system resource can be an item of equipment such as a Switch, an EquipmentContainer containing many individual items of equipment such as a Substation, or an organisational entity such as Company or SubControlArea. This provides for the nesting of collections of PowerSystemResources within other PowerSystemResources. For example, a Switch could be a member of a Substation and a Substation could be a member of a division of a Company. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | TRUE | PowerSystemResource
CIMCore | PSRType | PSRType | IdentifiedObject | cim | Classifying instances of the same class, e.g. overhead and underground ACLineSegments. This classification mechanism is intended to provide flexibility outside the scope of this standard, i.e. provide customisation that is non standard. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | PSRType
CIMCore | RegularIntervalSchedule | RegularIntervalSchedule | BasicIntervalSchedule; IdentifiedObject | cim | The schedule has TimePoints where the time between them is constant. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | RegularIntervalSchedule
CIMCore | RegularTimePoint | RegularTimePoint | Domain | cim | TimePoints for a schedule where the time between the points is constant. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Regular Time Point
CIMCore | SubControlArea | SubControlArea | PowerSystemResource; IdentifiedObject | cim | An area defined for the purpose of tracking interchange with surrounding areas via tie points; may or may not serve as a control area. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | SubControlArea
CIMCore | SubGeographicalRegion | SubGeographicalRegion | IdentifiedObject | cim | A subset of a geographical region of a power system network model. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Sub Geographical Region
CIMCore | Substation | Substation | EquipmentContainer; PowerSystemResource; IdentifiedObject | cim | A collection of equipment for purposes other than generation or utilization, through which electric energy in bulk is passed for the purposes of switching or modifying its characteristics. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Substation
CIMCore | Terminal | Terminal | IdentifiedObject | cim | An electrical connection point to a piece of conducting equipment. Terminals are connected at physical connection points called 'connectivity nodes'. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Terminal
CIMCore | Unit | Unit | IdentifiedObject | cim | Quantity being measured. The Unit.name shall be unique among all specified quantities and describe the quantity. The Unit.aliasName is meant to be used for localization. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Unit
CIMCore | VoltageLevel | VoltageLevel | EquipmentContainer; PowerSystemResource; IdentifiedObject | cim | A collection of equipment at one common system voltage forming a switchgear. The equipment typically consist of breakers, busbars, instrumentation, control, regulationand protection devices as well as assemblies of all these. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | VoltageLevel
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | SteamSupply; PowerSystemResource; IdentifiedObject | cim | Boiling water reactor used as a steam supply to a steam turbine. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | BWRSteamSupply
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | PrimeMover; PowerSystemResource; IdentifiedObject | cim | A prime mover that is typically fueled by gas or light oil. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | CombustionTurbine
CIMGenerationDynamics | CTTEMPMWCurve | CTTEMPMWCurve | Domain | cim | Relationship between the combustion turbine's power output rating in gross MW (X-axis) and the ambient air temperature in temperature units (Y-axis). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | CTTempMWCurve
CIMGenerationDynamics | DrumBoiler | DrumBoiler | FossilSteamSupply; SteamSupply; PowerSystemResource; IdentifiedObject | cim | Drum boiler. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | DrumBoiler
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | SteamSupply; PowerSystemResource; IdentifiedObject | cim | Fossil fueled boiler (e.g., coal, oil, gas) | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | TRUE | FossilSteamSupply
CIMGenerationDynamics | HeatRecoveryBoiler | HeatRecoveryBoiler | FossilSteamSupply; SteamSupply; PowerSystemResource; IdentifiedObject | cim | The heat recovery system associated with combustion turbines in order to produce steam for combined cycle plants. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | HeatRecoveryBoiler
CIMGenerationDynamics | HydroTurbine | HydroTurbine | PrimeMover; PowerSystemResource; IdentifiedObject | cim | A water driven prime mover. Typical turbine types are: Francis, Kaplan, and Pelton. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | HydroTurbine
CIMGenerationDynamics | PrimeMover | PrimeMover | PowerSystemResource; IdentifiedObject | cim | The machine used to develop mechanical energy used to drive a generator. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | TRUE | PrimeMover
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | SteamSupply; PowerSystemResource; IdentifiedObject | cim | Pressurized water reactor used as a steam supply to a steam turbine. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | PWRSteamSupply
CIMGenerationDynamics | SteamSupply | SteamSupply | PowerSystemResource; IdentifiedObject | cim | Steam supply for steam turbine. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | TRUE | SteamSupply
CIMGenerationDynamics | SteamTurbine | SteamTurbine | PrimeMover; PowerSystemResource; IdentifiedObject | cim | Steam turbine | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | SteamTurbine
CIMGenerationDynamics | Subcritical | Subcritical | FossilSteamSupply; SteamSupply; PowerSystemResource; IdentifiedObject | cim | Once-through subcritical boiler. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Subcritical
CIMGenerationDynamics | Supercritical | Supercritical | FossilSteamSupply; SteamSupply; PowerSystemResource; IdentifiedObject | cim | Once-through supercritical boiler. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Supercritical
CIMLoadModel | AreaLossCurve | AreaLossCurve | Curve; IdentifiedObject | cim | The relationship between total area MW losses (Y-axis) and total area MW load (X-axis). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | AreaLossCurve
CIMLoadModel | ConformLoad | ConformLoad | EnergyConsumer; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | ConformLoad represent loads that follow a daily load change pattern where the pattern can be used to scale the load with a system load. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | ConformLoad
CIMLoadModel | ConformLoadGroup | ConformLoadGroup | LoadGroup; IdentifiedObject | cim | Loads that follows a daily and seasonal load variation pattern. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | ConformLoadGroup
CIMLoadModel | ConformLoadSchedule | ConformLoadSchedule | SeasonDayTypeSchedule; RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | A curve of load versus time (X-axis) showing the active power values (Y1-axis) and reactive power (Y2-axis) for each unit of the period covered. This curve represents a typical pattern of load over the time period for a given day type and season. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | ConformLoadSchedule
CIMLoadModel | CustomerLoad | CustomerLoad | ConformLoad; EnergyConsumer; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A meter for measuring customer energy consumption. The typeName attribute indicates the type of customer meter. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | CustomerLoad
CIMLoadModel | DayType | DayType | IdentifiedObject | cim | Group of similar days, e.g., Mon/Tue/Wed, Thu/Fri, Sat/Sun, Holiday1, Holiday2 | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | DayType
CIMLoadModel | EnergyArea | EnergyArea | IdentifiedObject | cim | The class describes an area having energy production or consumption. The class is the basis for further specialization. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | EnergyArea
CIMLoadModel | InductionMotorLoad | InductionMotorLoad | NonConformLoad; EnergyConsumer; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | Large three phase induction motor load. The typeName attribute indicates the type of induction motor (1 = wound rotor) (2 = squirrel cage). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | InductionMotorLoad
CIMLoadModel | Load | Load | ConformLoad; EnergyConsumer; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A generic equivalent for an energy consumer on a transmission or distribution voltage level. It may be under load management and also has cold load pick up characteristics. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Load
CIMLoadModel | LoadArea | LoadArea | EnergyArea; IdentifiedObject | cim | A Load Area is a subdivision of a network company. Group of loads (i.e., energy consumers). | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | LoadArea
CIMLoadModel | LoadDemandModel | LoadDemandModel | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | A curve of load versus time (X-axis) showing the values of MW (Y1-axis) and MVAr (Y2-axis) for each unit of the period covered. This curve represents a typical pattern of load over the time period for a given day type and season. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | LoadDemandModel
CIMLoadModel | LoadGroup | LoadGroup | IdentifiedObject | cim | The class is the third level in a hierarchical structure for grouping of loads for the purpose of load flow load scaling. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | LoadGroup
CIMLoadModel | NonConformLoad | NonConformLoad | EnergyConsumer; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | NonConformLoad represent loads that do not follow a daily load change pattern and changes are not correlated with the daily load change pattern. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | NonConformLoad
CIMLoadModel | NonConformLoadGroup | NonConformLoadGroup | LoadGroup; IdentifiedObject | cim | Loads that do not follow a daily and seasonal load variation pattern. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | NonConformLoadGroup
CIMLoadModel | NonConformLoadSchedule | NonConformLoadSchedule | SeasonDayTypeSchedule; RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | An active power (Y1-axis) and reactive power (Y2-axis) schedule (curves) versus time (X-axis) for non-conforming loads, e.g., large industrial load or power station service (where modeled). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | NonConformLoadSchedule
CIMLoadModel | PowerCutZone | PowerCutZone | PowerSystemResource; IdentifiedObject | cim | An area or zone of the power system which is used for load shedding purposes. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | PowerCutZone
CIMLoadModel | Season | Season | IdentifiedObject | cim | A specified time period of the year, e.g., Spring, Summer, Fall, Winter. Season Types may be defined with starting and ending month and day. All defined season types must make up one year. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Season
CIMLoadModel | SeasonDayTypeSchedule | SeasonDayTypeSchedule | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | The schedule specialize RegularIntervalSchedule with type curve data for a specific type of day and season. This means that curves of this type cover a 24 hour period. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | SeasonDayTypeSchedule
CIMLoadModel | StationSupply | StationSupply | EnergyConsumer; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | Station supply. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | StationSupply
CIMLoadModel | SubLoadArea | SubLoadArea | EnergyArea; IdentifiedObject | cim | The class is the second level in a hierarchical structure for grouping of loads for the purpose of load flow load scaling. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | SubLoadArea
CIMMeas | Accumulator | Accumulator | Measurement; IdentifiedObject | cim | Accumulator represents a accumulated (counted) Measurement, e.g. an energy value. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Accumulator
CIMMeas | AccumulatorLimit | AccumulatorLimit | Limit; IdentifiedObject | cim | Limit values for Accumulator measurements. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | AccumulatorLimit
CIMMeas | AccumulatorLimitSet | AccumulatorLimitSet | LimitSet; IdentifiedObject | cim | An AccumulatorLimitSet specifies a set of Limits that are associated with an Accumulator measurement. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | AccumulatorLimitSet
CIMMeas | AccumulatorValue | AccumulatorValue | MeasurementValue; IdentifiedObject | cim | AccumulatorValue represents a accumulated (counted) MeasurementValue. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | AccumulatorValue
CIMMeas | Analog | Analog | Measurement; IdentifiedObject | cim | Analog represents an analog Measurement. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Analog
CIMMeas | AnalogLimit | AnalogLimit | Limit; IdentifiedObject | cim | Limit values for Analog measurements. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | AnalogLimit
CIMMeas | AnalogLimitSet | AnalogLimitSet | LimitSet; IdentifiedObject | cim | An AnalogLimitSet specifies a set of Limits that are associated with an Analog measurement. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | AnalogLimitSet
CIMMeas | AnalogValue | AnalogValue | MeasurementValue; IdentifiedObject | cim | AnalogValue represents an analog MeasurementValue. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | AnalogValue
CIMMeas | Command | Command | Control; IdentifiedObject | cim | A Command is a discrete control used for supervisory control. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Command
CIMMeas | Control | Control | IdentifiedObject | cim | Control is used for supervisory/device control. It represents control outputs that are used to change the state in a process, e.g. close or open breaker, a set point value or a raise lower command. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Control
CIMMeas | ControlType | ControlType | IdentifiedObject | cim | Specifies the type of Control, e.g. BreakerOn/Off, GeneratorVoltageSetPoint, TieLineFlow etc. The ControlType.name shall be unique among all specified types and describe the type. The ControlType.aliasName is meant to be used for localization. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | ControlType
CIMMeas | Discrete | Discrete | Measurement; IdentifiedObject | cim | Discrete represents a discrete Measurement, i.e. a Measurement reprsenting discrete values, e.g. a Breaker position. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Discrete
CIMMeas | DiscreteValue | DiscreteValue | MeasurementValue; IdentifiedObject | cim | DiscreteValue represents a discrete MeasurementValue. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | DiscreteValue
CIMMeas | Limit | Limit | IdentifiedObject | cim | Specifies one limit value for a Measurement. A Measurement typically has several limits that are kept together by the LimitSet class. The actual meaning and use of a Limit instance (i.e., if it is an alarm or warning limit or if it is a high or low limit) is not captured in the Limit class. However the name of a Limit instance may indicate both meaning and use. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Limit
CIMMeas | LimitSet | LimitSet | IdentifiedObject | cim | Specifies a set of Limits that are associated with a Measurement. A Measurement may have several LimitSets corresponding to seasonal or other changing conditions. The condition is captured in the name and description attributes. The same LimitSet may be used for several Measurements. In particular percentage limits are used this way. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | LimitSet
CIMMeas | Measurement | Measurement | IdentifiedObject | cim | A Measurement represents any measured, calculated or non-measured non-calculated quantity. Any piece of equipment may contain Measurements, e.g. a substation may have temperature measurements and door open indications, a transformer may have oil temperature and tank pressure measurements, a bay may contain a number of power flow measurements and a Breaker may contain a switch status measurement. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | TRUE | Measurement
CIMMeas | MeasurementType | MeasurementType | IdentifiedObject | cim | Specifies the type of Measurement, e.g. IndoorTemperature, OutDoorTemperature, BusVoltage, GeneratorVoltage, LineFlow etc. The MeasurementType.name shall be unique among all specified types and describe the type. The MeasurementType.aliasName is meant to be used for localization. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | MeasurementType
CIMMeas | MeasurementValue | MeasurementValue | IdentifiedObject | cim | The current state for a measurement. A state value is an instance of a measurement from a specific source. Measurements can be associated with many state values, each representing a different source for the measurement. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | MeasurementValue
CIMMeas | MeasurementValueQuality | MeasurementValueQuality | Quality61850; IdentifiedObject | cim | Measurement quality flags. Bits 0-10 are defined for substation automation in draft IEC 61850 part 7-3. Bits 11-15 are reserved for future expansion by that document. Bits 16-31 are reserved for EMS applications. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | MeasurementValueQuality
CIMMeas | MeasurementValueSource | MeasurementValueSource | IdentifiedObject | cim | MeasurementValueSource describes the alternative sources updating a MeasurementValue. User conventions for how to use the MeasurementValueSource attributes are described in the introduction to IEC 61970-301. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | MeasurementValueSource
CIMMeas | Quality61850 | Quality61850 | IdentifiedObject | cim | Quality flags in this class are as defined in IEC 61850, except for estimatorReplaced, which has been included in this class for convenience. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Quality61850
CIMMeas | SetPoint | SetPoint | Control; IdentifiedObject | cim | A SetPoint is an analog control used for supervisory control. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | SetPoint
CIMMeas | StringMeasurement | StringMeasurement | Measurement; IdentifiedObject | cim | StringMeasurement represents a measurement with values of type string. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | StringMeasurement
CIMMeas | StringMeasurementValue | StringMeasurementValue | MeasurementValue; IdentifiedObject | cim | StringMeasurementValue represents a measurement value of type string. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | StringMeasurementValue
CIMMeas | ValueAliasSet | ValueAliasSet | IdentifiedObject | cim | Describes the translation of a set of values into a name. Each ValueAliasSet has a name, description etc. A specific Measurement may represent a discrete state like Open, Closed, Intermediate etc. This requires a translation from the MeasurementValue.value number to a string, e.g. 0-]'Invalid', 1-]'Open', 2-]'Closed', 3-]'Intermediate'. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | ValueAliasSet
CIMMeas | ValueToAlias | ValueToAlias | IdentifiedObject | cim | Describes the translation of one particular value into a name, e.g. 1-]'Open'. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | ValueToAlias
CIMOutage | ClearanceTag | ClearanceTag | IdentifiedObject | cim | A clearance tag that is used to authorize and schedule work on conducting equipment in the field. Tagged equipment is not available for commercial service. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | ClearanceTag
CIMOutage | OutageSchedule | OutageSchedule | IrregularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | The period of time that a piece of equipment is out of service, for example, for maintenance or testing; including the equipment's MW rating while under maintenance. The X-axis represents absolute time and the Y-axis represents the equipment's available rating while out of service. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | OutageSchedule
CIMOutage | SwitchingOperation | SwitchingOperation | IdentifiedObject | cim | A SwitchingOperation is used to define individual switch operations for an OutageSchedule. This OutageSchedule may be associated with another item of Substation such as a Transformer, Line, or Generator; or with the Switch itself as a PowerSystemResource. A Switch may be referenced by many OutageSchedules. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | SwitchingOperation
CIMProduction | AccountBalance | AccountBalance | Curve; IdentifiedObject | cim |  | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | AccountBalance
CIMProduction | AirCompressor | AirCompressor | PowerSystemResource; IdentifiedObject | cim | Combustion turbine air compressor which is an integral part of a compressed air energy storage (CAES) plant. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | AirCompressor
CIMProduction | CAESPlant | CAESPlant | PowerSystemResource; IdentifiedObject | cim | Compressed air energy storage plant. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | CAESPlant
CIMProduction | CogenerationPlant | CogenerationPlant | PowerSystemResource; IdentifiedObject | cim | A set of thermal generating units for the production of electrical energy and process steam (usually from the output of the steam turbines). The steam sendout is typically used for industrial purposes or for municipal heating and cooling. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | CogenerationPlant
CIMProduction | CombinedCyclePlant | CombinedCyclePlant | PowerSystemResource; IdentifiedObject | cim | A set of combustion turbines and steam turbines where the exhaust heat from the combustion turbines is recovered to make steam for the steam turbines, resulting in greater overall plant efficiency | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | CombinedCyclePlant
CIMProduction | EmissionAccount | EmissionAccount | AccountBalance; Curve; IdentifiedObject | cim | Accounts for tracking emissions usage and credits for thermal generating units. A unit may have zero or more emission accounts, and will typically have one for tracking usage and one for tracking credits. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | EmissionAccount
CIMProduction | EmissionCurve | EmissionCurve | Curve; IdentifiedObject | cim | Relationship between the unit's emission rate in units of mass per hour (Y-axis) and output in MW (X-axis) for a given type of emission. This curve applies when only one type of fuel is being burned. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | EmissionCurve
CIMProduction | FossilFuel | FossilFuel | IdentifiedObject | cim | The fossil fuel consumed by the non-nuclear thermal generating units, e.g., coal, oil, gas. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | FossilFuel
CIMProduction | FuelAllocationSchedule | FuelAllocationSchedule | Curve; IdentifiedObject | cim | The amount of fuel of a given type which is allocated for consumption over a specified period of time. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | FuelAllocationSchedule
CIMProduction | GeneratingUnit | GeneratingUnit | Equipment; PowerSystemResource; IdentifiedObject | cim | A single or set of synchronous machines for converting mechanical power into alternating-current power. For example, individual machines within a set may be defined for scheduling purposes while a single control signal is derived for the set. In this case there would be a GeneratingUnit for each member of the set and an additional GeneratingUnit corresponding to the set. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | GeneratingUnit
CIMProduction | GenUnitOpCostCurve | GenUnitOpCostCurve | Curve; IdentifiedObject | cim | Relationship between unit operating cost in. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | GenUnitOpCostCurve
CIMProduction | GenUnitOpSchedule | GenUnitOpSchedule | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | The generating unit's Operator-approved current operating schedule (or plan), typically produced with the aid of unit commitment type analyses. The X-axis represents absolute time. The Y1-axis represents the status (0=off-line and unavailable: 1=available: 2=must run: 3=must run at fixed MW value: etc.). The Y2-axis represents the must run fixed MW value where required. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | GenUnitOpSchedule
CIMProduction | GrossToNetMWCurve | GrossToNetMWCurve | Curve; IdentifiedObject | cim | Relationship between the generating unit's gross MW output on the X-axis (measured at the terminals of the machine(s)) and the generating unit's net MW output on the Y-axis (based on utility-defined measurements at the power station). Station service load. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | GrossToNetMWCurve
CIMProduction | HeatInputCurve | HeatInputCurve | Curve; IdentifiedObject | cim | Relationship between unit heat input in MBtu per hour for main fuel (Y1-axis) and supplemental fuel (Y2-axis) versus unit output in MW (X-axis). The quantity of main fuel used to sustain generation at this output level is prorated for throttling between definition points. The quantity of supplemental fuel used at this output level is fixed and not prorated. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | HeatInputCurve
CIMProduction | HeatRateCurve | HeatRateCurve | Curve; IdentifiedObject | cim | Relationship between unit heat rate in MBtu/hour per MW (Y-axis) and unit output in MW (X-axis). The heat input is from all fuels. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | HeatRateCurve
CIMProduction | HydroGenEfficiencyCurve | HydroGeneratingEfficiencyCurve | Curve; IdentifiedObject | cim | Relationship between unit efficiency in percent and unit output in MW for a given net head in meters. The relationship between efficiency, discharge, head, and power output is expressed as follows: E =KP/HQ Where: (E=%) (P=MW) (H=m) (Q=m3/s) (K=constant) For example, a curve instance for a given net head could relate efficiency (Y-axis) versus MW output (X-axis) or versus discharge on the X-axis. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | HydroGeneratingEfficiencyCurve
CIMProduction | HydroGeneratingUnit | HydroGeneratingUnit | GeneratingUnit; Equipment; PowerSystemResource; IdentifiedObject | cim | A generating unit whose prime mover is a hydraulic turbine (e.g., Francis, Pelton, Kaplan) | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | HydroGeneratingUnit
CIMProduction | HydroPowerPlant | HydroPowerPlant | PowerSystemResource; IdentifiedObject | cim | A hydro power station which can generate or pump. When generating, the generator turbines receive there water from an upper reservoir. When pumping, the pumps receive their water from a lower reservoir. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | HydroPowerPlant
CIMProduction | HydroPump | HydroPump | PowerSystemResource; IdentifiedObject | cim | A synchronous motor-driven pump, typically associated with a pumped storage plant. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | HydroPump
CIMProduction | HydroPumpOpSchedule | HydroPumpOpSchedule | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | The hydro pump's Operator-approved current operating schedule (or plan), typically produced with the aid of unit commitment type analyses.The unit's operating schedule status is typically given as: (0=unavailable) (1=avilable to startup or shutdown) (2=must pump). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | HydroPumpOpSchedule
CIMProduction | IncrementalHeatRateCurve | IncrementalHeatRateCurve | Curve; IdentifiedObject | cim | Relationship between unit incremental heat rate in (delta MBtu/hour) per (delta MW )and unit output in MW. The IHR curve represents the slope of the HeatInputCurve. Note that the 'incremental heat rate' and the 'heat rate' have the same engineering units, i.e., MBtu/MWh. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | IncrementalHeatRateCurve
CIMProduction | InflowForecast | InflowForecast | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | Natural water inflow to a reservoir, usually forecasted from predicted rain and snowmelt. Typically in one hour increments for up to 10 days. The forecast is given in average cubic meters per second over the time increment. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | InflowForecast
CIMProduction | LevelVsVolumeCurve | LevelVsVolumeCurve | Curve; IdentifiedObject | cim | Relationship between reservoir volume in millions of cubic meters and reservoir level in meters. The curve values are: x axis - Level, y 1 axis - Volume. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | LevelVsVolumeCurve
CIMProduction | PenstockLossCurve | PenstockLossCurve | Curve; IdentifiedObject | cim | Relationship between penstock head loss (in meters) and total discharge through the penstock (in cubic meters per second). One or more turbines may be connected to the same penstock. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | PenstockLossCurve
CIMProduction | Reservoir | Reservoir | PowerSystemResource; IdentifiedObject | cim | A water storage facility within a hydro system, including: ponds, lakes, lagoons, and rivers. The storage is usually behind some type of dam. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Reservoir
CIMProduction | ShutdownCurve | ShutdownCurve | Curve; IdentifiedObject | cim | Relationship between the rate in gross MW/minute (Y-axis) at which a unit should be shutdown and its present gross MW output (X-axis). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | ShutdownCurve
CIMProduction | StartIgnFuelCurve | StartIgnFuelCurve | Curve; IdentifiedObject | cim | The quantity of ignition fuel (Y-axis) used to restart and repay the auxiliary power consumed versus the number of hours (X-axis) the unit was off line. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | StartIgnFuelCurve
CIMProduction | StartMainFuelCurve | StartMainFuelCurve | Curve; IdentifiedObject | cim | The quantity of main fuel (Y-axis) used to restart and repay the auxiliary power consumed versus the number of hours (X-axis) the unit was off line. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | StartMainFuelCurve
CIMProduction | StartRampCurve | StartRampCurve | Curve; IdentifiedObject | cim | Rate in gross MW/minute (Y-axis) at which a unit can be loaded versus the number of hours (X-axis) the unit was off line. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | StartRampCurve
CIMProduction | StartupModel | StartupModel | IdentifiedObject | cim | Unit start up characteristics depending on how long the unit has been off line. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | StartupModel
CIMProduction | SteamSendoutSchedule | SteamSendoutSchedule | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | The cogeneration plant's steam sendout schedule in klb/hour versus time. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | SteamSendoutSchedule
CIMProduction | TailbayLossCurve | TailbayLossCurve | Curve; IdentifiedObject | cim | Relationship between tailbay head loss (in meters on the Y-axis) and the total discharge into the power station's tailbay (in m3/sec on the X-axis) . There could be more than one curve depending on the level of the tailbay reservoir or river level. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | TailbayLossCurve
CIMProduction | TargetLevelSchedule | TargetLevelSchedule | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | Reservoir water level targets from advanced studies or 'rule curves'. Typically in one hour increments for up to 10 days. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | TargetLevelSchedule
CIMProduction | ThermalGeneratingUnit | ThermalGeneratingUnit | GeneratingUnit; Equipment; PowerSystemResource; IdentifiedObject | cim | A generating unit whose prime mover could be a steam turbine, combustion turbine, or diesel engine. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | ThermalGeneratingUnit
CIMProtection | CurrentRelay | CurrentRelay | ProtectionEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A device that checks current flow values in any direction or designated direction. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | CurrentRelay
CIMProtection | ProtectionEquipment | ProtectionEquipment | Equipment; PowerSystemResource; IdentifiedObject | cim | An electrical device designed to respond to input conditions in a prescribed manner and after specified conditions are met to cause contact operation or similar abrupt change in associated electric control circuits, or simply to display the detected condition. Protection equipment are associated with conducting equipment and usually operate circuit breakers. For protection relays, the typeName attribute is a type identifier as specified by IEC 61850 with a Pro_ prefix, e.g. Pro_OVR for overvoltage relay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | ProtectionEquipment
CIMProtection | RecloseSequence | RecloseSequence | IdentifiedObject | cim | A reclose sequence (open and close) is defined for each possible reclosure of a breaker. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | RecloseSequence
CIMProtection | SynchrocheckRelay | SynchrocheckRelay | ProtectionEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A device that operates when two AC circuits are within the desired limits of frequency, phase angle, and voltage, to permit or to cause the paralleling of these two circuits. Used to prevent the paralleling of non-synchronous topological islands. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | SynchrocheckRelay
CIMSCADA | CommunicationLink | CommunicationLink | PowerSystemResource; IdentifiedObject | cim | The connection to remote units is through one or more communication links. Reduntant links may exist. The CommunicationLink class inherit PowerSystemResource. The intention is to allow CommunicationLinks to have Measurements. These Measurements can be used to model link status as operational, out of service, unit failure etc. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | CommunicationLink
CIMSCADA | RemoteControl | RemoteControl | RemotePoint; IdentifiedObject | cim | Remote controls are ouputs that are sent by the remote unit to actuators in the process. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | RemoteControl
CIMSCADA | RemotePoint | RemotePoint | IdentifiedObject | cim | For a RTU remote points correspond to telemetered values or control outputs. Other units (e.g. control centers) usually also contain calculated values. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | RemotePoint
CIMSCADA | RemoteSource | RemoteSource | RemotePoint; IdentifiedObject | cim | Remote sources are state variables that are telemetered or calculated within the remote unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | RemoteSource
CIMSCADA | RemoteUnit | RemoteUnit | PowerSystemResource; IdentifiedObject | cim | A remote unit can be a RTU, IED, substation control system, control center etc. The communication with the remote unit can be through various standard protocols (e.g. IEC 61870, IEC 61850) or non standard protocols (e.g. DNP, RP570 etc.). A remote unit contain remote data points that might be telemetered, collected or calculated. The RemoteUnit class inherit PowerSystemResource. The intention is to allow RemotUnits to have Measurements. These Measurements can be used to model unit status as operational, out of service, unit failure etc. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | RemoteUnit
CIMTopology | ConnectivityNode | ConnectivityNode | IdentifiedObject | cim | Connectivity nodes are points where terminals of conducting equipment are connected together with zero impedance. | TRUE | TRUE | TRUE | FALSE |  | TRUE |  |  | FALSE | ConnectivityNode
CIMTopology | TopologicalIsland | TopologicalIsland | IdentifiedObject | cim | An electrically connected subset of the network. Topological islands can change as the current network state changes (i.e., disconnect switches, breakers, etc. change state). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | TopologicalIsland
CIMTopology | TopologicalNode | TopologicalNode | IdentifiedObject | cim | A set of connectivity nodes that, in the current network state, are connected together through closed switches. Topological nodes can change as the current network state changes (i.e., switches, breakers, etc. change state). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | TopologicalNode
CIMWires | ACLineSegment | ACLineSegment | Conductor; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A wire or combination of wires, with consistent electrical characteristics, building a single electrical system, used to carry alternating current between points in the power system. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | ACLineSegment
CIMWires | Breaker | Breaker | ProtectedSwitch; Switch; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A mechanical switching device capable of making, carrying, and breaking currents under normal circuit conditions and also making, carrying for a specified time, and breaking currents under specified abnormal circuit conditions e.g. those of short circuit. The typeName is the type of breaker, e.g., oil, air blast, vacuum, SF6. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Breaker
CIMWires | BusbarSection | BusbarSection | Connector; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A conductor, or group of conductors, that serve to connect conducting equipment. Voltage measurements are typically obtained from PTs that are connected to busbar sections. A bus bar section may have one or more terminals. The typeName attribute indicates the type of bus bar section, e.g.: Main, Transfer. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | BusbarSection
CIMWires | CompositeSwitch | CompositeSwitch | EquipmentContainer; PowerSystemResource; IdentifiedObject | cim | A model of a set of individual Switches normally enclosed within the same cabinet and possibly with interlocks that restrict the combination of switch positions. These are typically found in medium voltage distribution networks. A CompositeSwitch could represent a Ring-Main-Unit (RMU), or pad-mounted switchgear, with primitive internal devices such as an internal bus-bar plus 3 or 4 internal switches each of which may individually be open or closed. A CompositeSwitch and a set of contained Switches can also be used to represent a multi-position switch e.g. a switch that can connect a circuit to Ground, Open or Busbar. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | CompositeSwitch
CIMWires | Conductor | Conductor | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | Combination of conducting material with consistent electrical characteristics, building a single electrical system, used to carry current between points in the power system. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | TRUE | Conductor
CIMWires | ConductorType | ConductorType | Domain | cim | Wire or cable conductor (per IEEE specs). A specific type of wire or combination of wires not insulated from one another, suitable for carrying electric current. It may be bare or insulated. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | ConductorType
CIMWires | Connector | Connector | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A conductor, or group of conductors, with negligible impedance, that serve to connect other conducting equipment within a single substation and are modelled with a single logical terminal. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | TRUE | Connector
CIMWires | DCLineSegment | DCLineSegment | Conductor; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A wire or combination of wires not insulated from one another, with consistent electrical characteristics, used to carry direct current between points in the DC region of the power system. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | DCLineSegment
CIMWires | Disconnector | Disconnector | Switch; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A manually operated or motor operated mechanical switching device used for changing the connections in a circuit, or for isolating a circuit or equipment from a source of power. It is required to open or close circuits when negligible current is broken or made. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Disconnector
CIMWires | EnergyConsumer | EnergyConsumer | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | Generic user of energy - a point of consumption on the power system model | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | EnergyConsumer
CIMWires | EquivalentSource | EquivalentSource | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A generic equivalent for an energy supplier on a transmission or distribution voltage level. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | EquivalentSource
CIMWires | Feeder | Feeder | PowerSystemResource; IdentifiedObject | cim | A static collection of conducting equipment originating at a main distribution center and supplying one or more secondary distribution centers, one or more branch-circuit distribution centers, or any combination of these two types of equipment. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Feeder
CIMWires | FrequencyConverter | FrequencyConverter | RegulatingCondEq; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A device to convert from one frequency to another (e.g., frequency F1 to F2) comprises a pair of FrequencyConverter instances. One converts from F1 to DC, the other converts the DC to F2. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | FrequencyConverter
CIMWires | Fuse | Fuse | Switch; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | An overcurrent protective device with a circuit opening fusible part that is heated and severed by the passage of overcurrent through it. A fuse is considered a switching device because it breaks current. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Fuse
CIMWires | Ground | Ground | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A common point for connecting grounded conducting equipment such as shunt capacitors. The power system model can have more than one ground. The typeName indicates the type of ground, e.g., mesh, earth rod. It is recommended to use GroundDisconnector instead of Ground class when applying CIM. In case of grounding a shunt compensator use Compensator of type SHUNT. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Ground
CIMWires | GroundDisconnector | GroundDisconnector | Switch; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A manually operated or motor operated mechanical switching device used for isolating a circuit or equipment from Ground. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | GroundDisconnector
CIMWires | HeatExchanger | HeatExchanger | Equipment; PowerSystemResource; IdentifiedObject | cim | Equipment for the cooling of electrical equipment and the extraction of heat. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | HeatExchanger
CIMWires | Jumper | Jumper | Switch; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A short section of conductor with negligible impedance which can be manually removed and replaced if the circuit is de-energized. Note that zero-impedance branches can be modelled by an ACLineSegment with a zero impedance ConductorType. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Jumper
CIMWires | Junction | Junction | Connector; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A point where one or more conducting equipments are connected with zero resistance. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Junction
CIMWires | Line | Line | EquipmentContainer; PowerSystemResource; IdentifiedObject | cim | A component part of a system extending between adjacent substations or from a substation to an adjacent interconnection point. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Line
CIMWires | LoadBreakSwitch | LoadBreakSwitch | ProtectedSwitch; Switch; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A mechanical switching device capable of making, carrying, and breaking currents under normal operating conditions. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | LoadBreakSwitch
CIMWires | MVArCapabilityCurve | MVArCapabilityCurve | Curve; IdentifiedObject | cim | Describes MVAR limits for the unit over the complete MW range of the unit. The curve values are: x axis - Unit MW output, y1 axis - Minimum MVAR limit, y2 axis - Maximum MVAR limit | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | MVArCapabilityCurve
CIMWires | Plant | Plant | EquipmentContainer; PowerSystemResource; IdentifiedObject | cim | A Plant is a collection of equipment for purposes of generation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Plant
CIMWires | PowerTransformer | PowerTransformer | Equipment; PowerSystemResource; IdentifiedObject | cim | An electrical device consisting of two or more coupled windings, with or without a magnetic core, for introducing mutual coupling between electric circuits. Transformers can be used to control voltage and phase shift (MW flow). The typeName attribute indicates type of transformer. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | PowerTransformer
CIMWires | ProtectedSwitch | ProtectedSwitch | Switch; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A ProtectedSwitch is a switching device that can be operated by ProtectionEquipment. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | ProtectedSwitch
CIMWires | RectifierInverter | RectifierInverter | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | Bi-directional AC-DC conversion equipment that can be used to control DC current, DC voltage, DC power flow, or firing angle. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | RectifierInverter
CIMWires | RegulatingCondEq | RegulatingCondEq | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | RegulatingCondEq is a type of ConductingEquipment that can regulate Measurements and have a RegulationSchedule. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | TRUE | RegulatingCondEq
CIMWires | RegulationSchedule | RegulationSchedule | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | cim | A pre-established pattern over time for a controlled variable, e.g., busbar voltage. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | RegulationSchedule
CIMWires | SeriesCompensator | SeriesCompensator | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A Series Compensator is a series capacitor or reactor or an AC transmission line without charging susceptance. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | SeriesCompensator
CIMWires | ShuntCompensator | ShuntCompensator | RegulatingCondEq; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A shunt capacitor or reactor or switchable bank of shunt capacitors or reactors. A section of a shunt compensator is an individual capacitor or reactor. Negative values for mVArPerSection and nominalMVAr indicate that the compensator is a reactor. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | ShuntCompensator
CIMWires | StaticVarCompensator | StaticVarCompensator | RegulatingCondEq; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A facility for providing variable and controllable shunt reactive power. The SVC typically consists of a stepdown transformer, filter, thyristor-controlled reactor, and thyristor-switched capacitor arms. The SVC may operate in fixed MVar output mode or in voltage control mode. When in voltage control mode, the output of the SVC will be proportional to the deviation of voltage at the controlled bus from the voltage setpoint. The SVC characteristic slope defines the proportion. If the voltage at the controlled bus is equal to the voltage setpoint, the SVC MVar output is zero. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | StaticVarCompensator
CIMWires | Switch | Switch | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A generic device designed to close, or open, or both, one or more electric circuits. The typeName attribute may be used to indicate that the database switch does not represent a corresponding real device but has been introduced for modeling purposes only. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Switch
CIMWires | SynchronousMachine | SynchronousMachine | RegulatingCondEq; ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | An electromechanical device that operates synchronously with the network. It is a single machine operating either as a generator or synchronous condenser or pump. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | SynchronousMachine
CIMWires | TapChanger | TapChanger | PowerSystemResource; IdentifiedObject | cim | Mechanism for changing transformer winding tap positions. The typeName attribute indicates type of changer, designated as 'Fixed' or 'LTC.' | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | TapChanger
CIMWires | TransformerWinding | TransformerWinding | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | cim | A winding is associated with each defined terminal of a transformer (or phase shifter). | TRUE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | TransformerWinding
CIMWires | TransmissionCorridor | TransmissionCorridor | Domain | cim | A corridor containing one or more rights of way. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | TransmissionCorridor
CIMWires | VoltageControlZone | VoltageControlZone | PowerSystemResource; IdentifiedObject | cim | An area of the power system network which is defined for secondary voltage control purposes. A voltage control zone consists of a collection of substations with a designated bus bar section whose voltage will be controlled. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | VoltageControlZone
CIMWires | WindingTest | WindingTest | Domain | cim | Physical winding test data for the winding/tap pairs of a transformer (or phase shifter). This test data can be used to derive other attributes of specific transformer or phase shifter models. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | WindingTest
CIMWires | WireArrangement | WireArrangement | Domain | cim | Identification, spacing and configuration of the wires of a ConductorType, with reference to their type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | WireArrangement
CIMWires | WireType | WireType | Domain | cim | Wire conductor (per IEEE specs). A specific type of wire or combination of wires, not insulated from each other, suitable for carrying electrical current. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | WireType
Common | Domain | Domain | Domain | spc | The root of all object types. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | TRUE | Domain
EnergyScheduling | AreaReserveSpec | AreaReserveSpec | Domain | cim | The control area's reserve specification. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | AreaReserveSpec
EnergyScheduling | EnergyTransaction | EnergyTransaction | IdentifiedObject | cim | Specifies the schedule for energy transfers between interchange areas that are necessary to satisfy the associated interchange transaction. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | EnergyTransaction
EnergyScheduling | HostControlArea | HostControlArea | PowerSystemResource; IdentifiedObject | cim | A HostControlArea has a set of tie points and a set of generator controls (i.e., AGC). It also has a total load, including transmission and distribution losses. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | HostControlArea
Engineering_sysTreeCategory | RootType | RootType | Domain | rdf |  | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | RootType
Engineering_sysTreeCategory | sysGeneralCategory | sysGeneralCategory | sysTreeCategory | spc | Folder for organizing general data. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | sysGeneralCategory
Engineering_sysTreeCategory | sysTreeCategory | sysTreeCategory | Domain | spc | Abstract: Tree Category | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | TRUE | sysTreeCategory
ETX | Address | Address | Domain | etx |  | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Address
ETX | AggregateHub | AggregateHub | IdentifiedObject | etx | Aggregate HUB. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  |  | FALSE | AggregateHub
ETX | AncillaryQualification | AncillaryQualification | IdentifiedObject | etx | Ancillary qualification. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  |  | FALSE | Ancillary Qualification
ETX | Configuration | Configuration | IdentifiedObject | etx | Configuration options for combined cycle units. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Configuration
ETX | ConfigurationMember | ConfigurationMember | IdentifiedObject | etx | Configuration Member of CCP Configuration. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | ConfigurationMember
ETX | Contact | Contact | Address | etx |  | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | Contact
ETX | ControllableLoadResource | ControllableLoadResource | EnergyConsumerResource; Equipment; PowerSystemResource; IdentifiedObject | etx | Controllable Load Resource. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | ControllableLoadResource
ETX | DCTie | DCTie | IdentifiedObject | etx | A generator and Load modeling a DC Tie. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | DCTie
ETX | ElectricalBus | ElectricalBus | IdentifiedObject | etx | An electrical device ... | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | ElectricalBus
ETX | EndCap | EndCap | ConductingEquipment; Equipment; PowerSystemResource; IdentifiedObject | etx | A cap to terminate the line or device. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | EndCap
ETX | EnergyConsumerResource | EnergyConsumerResource | Equipment; PowerSystemResource; IdentifiedObject | etx | Energy Consumer Resource. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | EnergyConsumerResource
ETX | EPSMeter | EPSMeter | IdentifiedObject | etx | ERCOT Polled Settlement Meter. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | EPSMeter
ETX | ERCOTVersion | ERCOTVersion | Domain | etx | This is the version of the ERCOT Data Dictionary. | FALSE | TRUE | TRUE | TRUE |  | FALSE |  |  | FALSE | ERCOT Version
ETX | ESI_ID | ESI_ID | IdentifiedObject | etx | Residential Meter ID. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | ESI_ID
ETX | FlowgateElement | FlowgateElement | IdentifiedObject | etx | Market based element defining a region for energy production. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  |  | FALSE | FlowgateElement
ETX | FlowgateGroup | FlowgateGroup | Monitored; IdentifiedObject | etx | Grouping of market based elements defining a region for energy production. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Flowgate Group
ETX | HUBBus | HUBBus | IdentifiedObject | etx | A collection of buses that are located within a HUB. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  |  | FALSE | HUBBus
ETX | IccpQualityConversion | IccpQualityConversion | IdentifiedObject | etx | Denotes a re-mapping of a specific set of ICCP input quality and data source flags to a given output set of quality and data source flags. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | IccpQualityConversion
ETX | IccpQualityConversionSet | IccpQualityConversionSet | IdentifiedObject | etx | A set of ICCP quality and data conversions. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | IccpQualityConversionSet
ETX | LoadResource | LoadResource | EnergyConsumerResource; Equipment; PowerSystemResource; IdentifiedObject | etx | Load Resource. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Load Resource
ETX | LogicalConfiguration | LogicalConfiguration | IdentifiedObject | etx | Logical Configuration. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | LogicalConfiguration
ETX | MeterConfiguration | MeterConfiguration | IdentifiedObject | etx | Grouping of EPS meters that create a configuration. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  |  | FALSE | MeterConfiguration
ETX | ModelBuild | ModelBuild | Domain | etx | Contains model build specific information. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  |  | FALSE | ModelBuild
ETX | Operatorship | Operatorship | IdentifiedObject | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Operatorship
ETX | Ownership | Ownership | IdentifiedObject | etx |  | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Ownership
ETX | PricingVector | PricingVector | IdentifiedObject | etx | Location where the metered price is calculated. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | PricingVector
ETX | PrivateAreaNetwork | PrivateAreaNetwork | IdentifiedObject | etx | A group of generators and loads comprising a private network. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | PrivateAreaNetwork
ETX | PseudoTerminal | PseudoTerminal | Terminal; IdentifiedObject | etx | The pseudo terminal to provide UI support. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | PseudoTerminal
ETX | ResourceNode | ResourceNode | IdentifiedObject | etx | A Settlement Point. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  |  | FALSE | ResourceNode
ETX | SettlementHUB | SettlementHUB | IdentifiedObject | etx | Settlement Point for ERCOT HUB. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  |  | FALSE | SettlementHUB
ETX | SettlementLoadZone | SettlementLoadZone | IdentifiedObject | etx | Settlement Point for ERCOT Load Zones. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  |  | FALSE | SettlementLoadZone
ETX | SettlementNOIELoadZone | SettlementNOIELoadZone | IdentifiedObject | etx | Settlement Point for ERCOT NOIE Load Zones. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  |  | FALSE | SettlementNOIELoadZone
ETX | SupportLoadData | SupportLoadData | IdentifiedObject | etx | Supplemental Information for Loads. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | SupportLoadData
ETX | TransformerKluge | TransformerKluge | IdentifiedObject | etx | Containment Structure for 3 2-winding transformers to indicate it is in fact a 3 winding transformer. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | TransformerKluge
ETX | TransState | TransState | IdentifiedObject | etx | Defines the availabe from and to Transition States for the Combine Cycle Configurations. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  |  | FALSE | TransState
ETX_ABB | LimitLogicType | LimitLogicType | IdentifiedObject | etx | Limit Logic Type (LLT) can be a special class that defines which limits are to be applied to monitored facilities (i.e., branches and transformers) during nominal contingency configuration. A monitored branch can be associated with up to three different LLTs, corresponding to the DAM and RUC processes. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | LimitLogicType
ETX_ABB | SwitchSchedule | SwitchSchedule | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | etx | Curve for representing breaker schedules. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | SwitchSchedule
ETX_ABB | SyncMachineSchedule | SyncMachineSchedule | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | etx | Curve for representing generator real and reactive power schedules. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | SyncMachineSchedule
ETX_ABB | TapSchedule | TapSchedule | RegularIntervalSchedule; BasicIntervalSchedule; IdentifiedObject | etx | Curve to represent tap position schedules. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | TapSchedule
ETX_Areva | GenerationType | GenerationType | IdentifiedObject | etx | The type of generation used for totals. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | GenerationType
ETX_Areva | NuclearGeneratingUnit | NuclearGeneratingUnit | GeneratingUnit; Equipment; PowerSystemResource; IdentifiedObject | etx |  | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | NuclearGeneratingUnit
ETX_Areva | PhysicalTiePoint | PhysicalTiePoint | PowerSystemResource; IdentifiedObject | etx | specific tie point in one control area. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | PhysicalTiePoint
ETX_Areva | RampRateCurve | RampRateCurve | Curve; IdentifiedObject | etx | Defines the ramp rate curve used by GeneratingUnit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  |  | FALSE | RampRateCurve
ETX_Areva | ResourceController | ResourceController | EquipmentContainer; PowerSystemResource; IdentifiedObject | etx | A plant controller. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | ResourceController
ETX_Areva | TapRatioCurve | TapRatioCurve | Curve; IdentifiedObject | etx | Tap ratio tables for 3-winding transformers.Specify a transformer's per-unit voltage tap ratio as a function of LTC tapposition. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | TapRatioCurve
ETX_Areva | TieCorridor | TieCorridor | IdentifiedObject | etx | Tie Corridor. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | TieCorridor
ETX_Areva | TieEnd | TieEnd | PowerSystemResource; IdentifiedObject | etx | A group of tie lines terminating in one control area. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | TieEnd
ETX_Areva | TieLine | TieLine | IdentifiedObject | etx | Tie Line. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | TieLine
ETX_Areva | WindGeneratingUnit | WindGeneratingUnit | GeneratingUnit; Equipment; PowerSystemResource; IdentifiedObject | etx |  | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | WindGeneratingUnit
ETXContingency | ContingencyElement | ContingencyElement | IdentifiedObject | etx | An element of a system event to be studied by contingency analysis, representing a change in status of a single piece of equipment. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Contingency Element
ETXContingency | ContingencyGroup | ContingencyGroup | IdentifiedObject | etx | Used for activation of groups of contingencies. Contingencies can belong to multiple groups. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | ContingencyGroup
ETXContingency | ContingencyGroupMember | ContingencyGroupMember | IdentifiedObject | etx | Used for the many to many relationship between Contigency and ContigencyGroup. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | ContingencyGroupMember
ETXLoadModel | EnergyConsumerAltConnection | EnergyConsumerAltConnection | IdentifiedObject | etx | Alternate connection of load. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | EnergyConsumerAlternateConnection
ETXLoadModel | LoadType | LoadType | IdentifiedObject | etx | Shared attributes for a loads of the same type. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | LoadType
ETXMonitoring | AngleDifference | AngleDifference | Monitored; IdentifiedObject | etx | The angle difference between two points in the network. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | AngleDifference
ETXMonitoring | AngleDifferenceLimit | AngleDifferenceLimit | Limit; IdentifiedObject | etx | A limit on the angle difference. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | AngleDifferenceLimit
ETXMonitoring | AngleDifferenceLimitSet | AngleDifferenceLimitSet | LimitSet; IdentifiedObject | etx | Limit set on angle difference. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | AngleDifferenceLimitSet
ETXMonitoring | BranchGroup | BranchGroup | Monitored; IdentifiedObject | etx | Directed sum of terminal flows. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | BranchGroup
ETXMonitoring | BranchGroupTerminal | BranchGroupTerminal | IdentifiedObject | etx | Directed terminal flow to add into BranchGroup. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | BranchGroupTerminal
ETXMonitoring | Monitored | Monitored | IdentifiedObject | etx | Something that is monitored. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Monitored
ETXMonitoring | MonitoredGroup | MonitoredGroup | IdentifiedObject | etx | Groups monitored elements. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | MonitoredGroup
ETXMonitoring | VLSBusBarMonitored | VLSBusBarMonitored | Monitored; IdentifiedObject | etx | BusBarSection is monitored. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | VLSBusBarMonitored
ETXMonitoring | VoltageLimit | VoltageLimit | Limit; IdentifiedObject | etx | A voltage limit of a specific level. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | VoltageLimit
ETXMonitoring | VoltageLimitSet | VoltageLimitSet | LimitSet; IdentifiedObject | etx | Set of potentially shared voltage limits at various levels. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | VoltageLimitSet
ETXMonitoring | VoltageMonitored | VoltageMonitored | Monitored; IdentifiedObject | etx | Voltage level is monitored. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | VoltageMonitored
ETXNetwork | AccuracyClass | AccuracyClass | IdentifiedObject | etx | Holds accuracy information for measurement, generation and load schedules. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | AccuracyClass
ETXNetwork | PhaseShifterImpedanceCurve | PhaseShifterImpedanceCurve | Curve; IdentifiedObject | etx | phase shifter impedance as a function of the phase shifter's angle in degrees. X is the phase shift in degrees, and Y is multiplied by a phase shifter's nominal impedance to get the corrected impedance. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | PhaseShifterImpedanceCurve
ETXNetwork | StationSupplyWRCurve | StationSupplyWRCurve | Curve; IdentifiedObject | etx | StationSupply real and reactive curve on generation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | StationSupplyWRCurve
ETXNetwork | TransformerImpedanceCurve | TransformerImpedanceCurve | Curve; IdentifiedObject | etx | Transformer impedance correction.Model transformer impedance as a function of the LTC tap position in per unit. The data pattern is similar to PhaseShifterImpedanceCurve. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | TransformerImpedanceCurve
ETXPlanning | ConnectivityNodeGroup | ConnectivityNodeGroup | PlanningBay; EquipmentContainer; PowerSystemResource; IdentifiedObject | etx | Group of connectivity nodes. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | ConnectivityNodeGroup
ETXPlanning | PlanningArea | PlanningArea | IdentifiedObject | etx | Planning area. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | PlanningArea
ETXPlanning | PlanningBay | PlanningBay | EquipmentContainer; PowerSystemResource; IdentifiedObject | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | TRUE | PlanningBay
ETXPlanning | PlanningZone | PlanningZone | IdentifiedObject | etx | Planning zone. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | PlanningZone
ETXPlanning | PlanningZoneGroup | PlanningZoneGroup | IdentifiedObject | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | PlanningZoneGroup
ETXRASE | Gate | Gate | IdentifiedObject | etx | Special protection scheme gate. Evaluates to boolean. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Gate
ETXRASE | GateInputPin | GateInputPin | IdentifiedObject | etx | Input pin for a special protection scheme gate. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | GateInputPin
ETXRASE | PinBranchGroup | PinBranchGroup | GateInputPin; IdentifiedObject | etx | Branch flow summation input pin for RAS. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | PinBranchGroup
ETXRASE | PinFlow | PinFlow | GateInputPin; IdentifiedObject | etx | Network solution flow input pin for RAS. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | PinFlow
ETXRASE | PinGate | PinGate | GateInputPin; IdentifiedObject | etx | Input pin that maps to a Gate for RAS. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | PinGate
ETXRASE | PinSwitch | PinSwitch | GateInputPin; IdentifiedObject | etx | Input pin that maps to network solution switch status for RAS. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | PinSwitch
ETXRASE | PinTriggerCondition | PinTriggerCondition | GateInputPin; IdentifiedObject | etx | Input pin that maps to a TriggerCondition for RAS. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | PinTriggerCondition
ETXRASE | PinVoltage | PinVoltage | GateInputPin; IdentifiedObject | etx | Input pin that maps to a network voltage for RAS. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | PinVoltage
ETXRASE | PrivateProtectiveActions | PrivateProtectiveActions | ProtectiveActions; IdentifiedObject | etx | Protective actions that are private to a RemedialActionScheme trigger condition. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | PrivateProtectiveActions
ETXRASE | ProtActACLineSegment | ProtActACLineSegment | ProtectiveAction; IdentifiedObject | etx | Protective action to put an ACLineSegment in-service/out-of-service. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Protective Action ACLineSegment
ETXRASE | ProtActAnalog | ProtActAnalog | ProtectiveAction; IdentifiedObject | etx | Base class for protective actions that are non-switching. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Protective Action Analog
ETXRASE | ProtActEnergyConsumer | ProtActEnergyConsumer | ProtActAnalog; ProtectiveAction; IdentifiedObject | etx | RAS protective action associated with a load instance. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Protective Action Energy Consumer
ETXRASE | ProtActSeriesCompensator | ProtActSeriesCompensator | ProtectiveAction; IdentifiedObject | etx | Protective action to put a series compensator in-service/out-of-service. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Protective Action SeriesCompensator
ETXRASE | ProtActStationReduction | ProtActStationReduction | ProtActAnalog; ProtectiveAction; IdentifiedObject | etx | Protective action to reduce station generation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Protective Action Station Reduction
ETXRASE | ProtActSwitch | ProtActSwitch | ProtectiveAction; IdentifiedObject | etx | Protective action to move a switch. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Protective Action Switch
ETXRASE | ProtActSynchronousMachine | ProtActSynchronousMachine | ProtActAnalog; ProtectiveAction; IdentifiedObject | etx | Protective action to change output of a synchronous machine. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Protective Action Synchronous Machine
ETXRASE | ProtActTransformerWinding | ProtActTransformerWinding | ProtectiveAction; IdentifiedObject | etx | Protective action to put a TransformerWinding in-service/out-of-service. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Protective Action Transformer Winding
ETXRASE | ProtectiveAction | ProtectiveAction | IdentifiedObject | etx | Base class for a protective action for RAS. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | ProtectiveAction
ETXRASE | ProtectiveActions | ProtectiveActions | IdentifiedObject | etx | Base class for RAS protective actions sets. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | ProtectiveActions
ETXRASE | ProtectiveActionShared | ProtectiveActionShared | ProtectiveAction; IdentifiedObject | etx | Protective actions that can be shared among triggers. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | ProtectiveActionShared
ETXRASE | RemedialActionScheme | RemedialActionScheme | IdentifiedObject | etx | Remedial action scheme or special protection scheme. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | RemedialActionScheme
ETXRASE | SharedProtectiveActions | SharedProtectiveActions | ProtectiveActions; IdentifiedObject | etx | Protective actions that are shared among RemedialActionScheme trigger conditions. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | SharedProtectiveActions
ETXRASE | Stage | Stage | IdentifiedObject | etx | State of a remedial action scheme. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Stage
ETXRASE | StageTrigger | StageTrigger | IdentifiedObject | etx | Condition that is triggered within a stage and has remedial actions. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | StageTrigger
ETXRASE | TriggerCondition | TriggerCondition | IdentifiedObject | etx | A set of gates that can trigger remedial actions. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | TriggerCondition
ETXRating | DynamicElement | DynamicElement | IdentifiedObject | etx | Dynamically rated element, Line, Branch, or Transformer. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | DynamicElement
ETXRating | MonitoredRating | MonitoredRating | Monitored; IdentifiedObject | etx | Rating for monitored data. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | MonitoredRating
ETXRating | OwnerShareLimits | OwnerShareLimits | PowerSystemResource; IdentifiedObject | etx | Owner share limits. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | OwnerShareLimits
ETXRating | OwnerShareRating | OwnerShareRating | PowerSystemResource; IdentifiedObject | etx |  | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | OwnerShareRating
ETXRating | Rating | Rating | AnalogLimitSet; LimitSet; IdentifiedObject | etx | Rating set for static or dynamic limits. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Rating
ETXRating | WeatherStation | WeatherStation | IdentifiedObject | etx | Dynamic Ratings Weather Stations. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Weather Stations
ETXRating | WeatherStationAlt | WeatherStationAlt | IdentifiedObject | etx | Dynamic Ratings Weather Stations provided by TDSPs. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Weather Station (Alternate)
ETXRegulation | LoadBasedRegulationCurve | LoadBasedRegulationCurve | Curve; IdentifiedObject | etx | Curve used to adjust voltage based on system load. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | LoadBasedRegulationCurve
ETXSCADA | AlternateLimit | AlternateLimit | IdentifiedObject | etx | specify alternate limits that apply when external conditions. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | AlternateLimti
ETXSCADA | AlternateLimitSet | AlternateLimitSet | IdentifiedObject | etx | Describes a set of alternate limits that apply under the same external condition | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | AlternateLimitSet
ETXSCADA | AnalogAlarmCategory | AnalogAlarmCategory | IdentifiedObject | etx | A reference table used to define analog alarm category information for the SCADA subsystem. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | AnalogAlarmCategory
ETXSCADA | AnalogLimitName | AnalogLimitName | IdentifiedObject | etx | A reference table used to define valid Limit names and parameters to be used when defining Limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | AnalogLimitName
ETXSCADA | AnalogName | AnalogName | IdentifiedObject | etx | A reference table used to define valid names for analog type measurement. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | AnalogName
ETXSCADA | Calculation | Calculation | IdentifiedObject | etx | Calculation is a type of MeasurementValueSource. It provides the calculated value for the measurement. The caculation is based on the formula defined in the referenced Function. A Calculation contains multiple CalculationArgument, each referencing a Measurement and assigned to a FunctionArgument. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Calculation
ETXSCADA | CalculationArgument | CalculationArgument | IdentifiedObject | etx | CalculationArgument serves the base class for argument of Calculation. Each CalculationArgument must be assigned to CalculationArgument serves the base class for argument of Calculation. Each CalculationArgument must be assigned to a FunctionArgument. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | TRUE | CalculationArgument
ETXSCADA | CalculationTriggerTimer | CalculationTriggerTimer | IdentifiedObject | etx | A reference table used to model SCADA calculation trigger timer. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | CalculationTriggerTimer
ETXSCADA | ConstantArgument | ConstantArgument | CalculationArgument; IdentifiedObject | etx | Reference to a ConstatntArgument used in a Calculation as a constant argument. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | ConstantArgument
ETXSCADA | ConstantValue | ConstantValue | MeasurementValue; IdentifiedObject | etx | ConstantValue represents a constant MeasurementValue. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | ConstantValue
ETXSCADA | ConversionTable | ConversionTable | IdentifiedObject | etx | specify a method of data conversion for measurements. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | ConversionTable
ETXSCADA | DeviceTypeName | DeviceTypeName | IdentifiedObject | etx | Scada Device Type Name. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | DeviceTypeName
ETXSCADA | DiscreteAlarmCategory | DiscreteAlarmCategory | IdentifiedObject | etx | A reference table used to model SCADA Discrete Alarm Category information. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | DiscreteAlarmCategory
ETXSCADA | DiscreteName | DiscreteName | IdentifiedObject | etx | A reference table used to define valid states for discrete measurements. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | DiscreteName
ETXSCADA | DiscreteType | DiscreteType | IdentifiedObject | etx | A reference tabl used to define parameters for switching devices, such as breakers or disconnects, in the SCADA topology model. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | DiscreteType
ETXSCADA | EquipmentType | EquipmentType | IdentifiedObject | etx | Type of GenericStationEquipment. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Equipment Type
ETXSCADA | ExceptionListDisplay | ExceptionListDisplay | IdentifiedObject | etx | Display groups. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | ExceptionListDisplay
ETXSCADA | Function | Function | IdentifiedObject | etx | A Function defines a numeric computation formula that can be reused by many Calculations. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Function
ETXSCADA | FunctionArgument | FunctionArgument | IdentifiedObject | etx | FunctionArgument defines the input arguments that are used in the computation defined by Function. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | FunctionArgument
ETXSCADA | GenericEquipment | GenericEquipment | Equipment; PowerSystemResource; IdentifiedObject | etx | A GenericEquipment is an Equipment that is not explicitly modeled in CIM, such as battery. Such equipments may need be modeled in SCADA, since they are tel-measured. A GenericEquipment may also represent a virtual or conceptual entity, such as TIE as modeled as a device in SCADA. Each GenericEquipment must be specified by a GenericEquipmentType. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | GenericEquipment
ETXSCADA | LimitAlarmCategory | LimitAlarmCategory | IdentifiedObject | etx | A reference table used to define parameters for SCADA limit alarm categories. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | LimitAlarmCategory
ETXSCADA | MeasurementArgument | MeasurementArgument | CalculationArgument; IdentifiedObject | etx | Each MeasurementArgument must reference a MeasurementValue. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | MeasurementArgument
ETXSCADA | MeasurementGroup | MeasurementGroup | IdentifiedObject | etx | A MeasurementGroup is a group of related measurements. Not all of Measurements need to be grouped. Only SCADA measurements need to be grouped. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | MeasurementGroup
ETXSCADA | MeasurementLocation | MeasurementLocation | IdentifiedObject | etx | A MeasurementLocation represents a physical location where a SCADA measurement is located. It could be a Terminal, an Equipment, or TapChanger, etc. Measurements resided in the same MeasurementLocation MUST contain the same association to the PSR or Terminal. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | MeasurementLocation
ETXSCADA | ModelVersion | ModelVersion | Domain | etx | Version information about model contents. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | ModelVersion
ETXSCADA | PermissionArea | PermissionArea | IdentifiedObject | etx | A reference table used to define valid areas of responsibility for SCADA measurements. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | PermissionArea
ETXSCADA | SetPointLock | SetPointLock | IdentifiedObject | etx | Setpoint Interlock. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | TRUE | SetPointLock
ETXSCADA | SetPointName | SetPointName | IdentifiedObject | etx | A reference table used to define Setpoint names and connectivity for switching devices, such as breakers or disconnects, in the SCADA topology model. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | SetPointName
ETXSCADA | Site | Site | IdentifiedObject | etx | The Sites table is used to define valid SCADA sites, including the local site. Each Point, Analog, and Count record in the model must be associated with a SCADA Site record in this table. Only data retrieved via intersite data will be associated with any site other than the local site name. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | Site
ETXSCADA | SitePermission | SitePermission | IdentifiedObject | etx | Permission of Site | FALSE | FALSE | TRUE | FALSE |  | FALSE |  |  | FALSE | SitePermission
Instance-Level Access Rights | PseudoCompany | PseudoCompany | Company; IdentifiedObject | spc | The pseudo company is a holder for specifying instance-level access rights to all member companies without having to explicitly create the individual relationships. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | PseudoCompany
MarketOperations | Contingency | Contingency | IdentifiedObject | cim | An event threatening system reliability, consisting of one or more consistency elements. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  |  | FALSE | Contingency
Protection | FrequencyRelay | FrequencyRelay | ProtectionEquipment; Equipment; PowerSystemResource; IdentifiedObject | etx | A device that operates when frequency is below low setting or above high setting. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | FrequencyRelay
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | ProtectionEquipment; Equipment; PowerSystemResource; IdentifiedObject | etx | A device that operates when frequency is below low setting or above high setting. This device has 3 sets of high/low settings. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | GenericUnderfrequencyRelay
Protection | VoltageRelay | VoltageRelay | ProtectionEquipment; Equipment; PowerSystemResource; IdentifiedObject | spc | A device that protects generators and loads against high or low frequencies. Usually there are 3 frequency levels associated with each relay. For each frequency level the equipent is outaged when under/over frequency persists until delay time expires. The relay can outage more than one load feeder for each frequency level. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | VoltageRelay
RDF_Import | sysOrphan | sysOrphan | Domain | spc | This a container for instances when a parent could not be found for during rdf import of CPSM data. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | sysOrphan
RDF_Import | sysOrphans | sysOrphans | sysTreeCategory | spc | This is a master container for instances when a parent which could not be found during rdf import of CPSM data. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | sysOrphans
RDF_Import | sysRdfContainer | sysRdfContainer | Domain | spc | This a description of where orphan instances have to be placed in the instance tree during rdf import of CPSM data. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | sysRdfContainer
RDF_Import | sysRdfContainers | sysRdfContainers | sysTreeCategory | spc | This a container for descriptions of where rdf instances have to be placed in the instance tree during rdf import. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | sysRdfContainers
Reservation | ServicePoint | ServicePoint | IdentifiedObject | cim | The defined termination points of a transmission path. Service points are defined from the viewpoint of the transmission service. Each service point is contained within (or on the boundary of) an interchange area. CTM - A service point is source or destination of a transaction. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | ServicePoint
Reservation | TiePoint | TiePoint | IdentifiedObject | cim | Site of an interface between interchange areas. The tie point can be a network branch (e.g., transmission line or transformer) or a switching device. For transmission lines, the interchange area boundary is usually at a designated point such as the middle of the line. Line end metering is then corrected for line losses. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | TiePoint
Reservation | TransmissionPath | TransmissionPath | Domain | cim | An electrical connection, link, or line consisting of one or more parallel transmission elements between two areas of the interconnected electric systems, or portions thereof. TransmissionCorridor and TransmissionRightOfWay refer to legal aspects. The TransmissionPath refers to the segments between a TransmissionProvider's ServicePoints. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  |  | FALSE | TransmissionPath

## Attributes
Package | Internal Class Name | Class | Internal Attribute Name | Attribute | Data Type | Initial Value | Name Space | Documentation | CPSM Nerc | ABB / MMS | Areva / EMS | ABB / OS | Nexant / CRR | PTI / Planning | Lodestar / Settlement data | Required | Lower Level | Upper Level | NMMS Label
61970 | iec61970CIMVersion | iec61970CIMVersion | date | date | String30 | 2006-12-18 | cim | Date. | TRUE | TRUE | TRUE | TRUE |  | FALSE |  | TRUE |  |  | date
61970 | iec61970CIMVersion | iec61970CIMVersion | version | version | String30 | cim6197011v00 | cim | Version | TRUE | TRUE | TRUE | TRUE |  | FALSE |  | TRUE |  |  | version
CIMCore | BasePower | BasePower | basePower | basePower | ApparentPower |  | cim | Definition of base power. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Base Power
CIMCore | BaseVoltage | BaseVoltage | nominalVoltage | nominalVoltage | Voltage |  | cim | The PowerSystemResource's base voltage. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 1100 | 0 | Nominal Voltage
CIMCore | BasicIntervalSchedule | BasicIntervalSchedule | startTime | startTime | Time |  | cim | Start Time. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Start Time
CIMCore | BasicIntervalSchedule | BasicIntervalSchedule | value1Unit | value1Unit | String20 |  | cim | Value 1 Unit. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value 1 Unit
CIMCore | BasicIntervalSchedule | BasicIntervalSchedule | value2Unit | value2Unit | String20 |  | cim | Value 2 Unit. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value 2 Unit
CIMCore | Bay | Bay | bayEnergyMeasFlag | bayEnergyMeasFlag | Boolean | FALSE | cim | Indicates the presence/absence of kWh/kvarh measurements. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | bay Energy Measurement Flag
CIMCore | Bay | Bay | bayPowerMeasFlag | bayPowerMeasFlag | Boolean | FALSE | cim | Indicates the presence/absence of MW/MVAr measurements. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | bay Power Measurement Flag
CIMCore | Bay | Bay | breakerConfiguration | breakerConfiguration | EnumBreakerConfiguration |  | cim | Breaker configuration. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Breaker Configuration
CIMCore | Bay | Bay | busBarConfiguration | busBarConfiguration | EnumBusbarConfiguration |  | cim | Busbar configuration. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Busbar Configuration
CIMCore | Company | Company | CompanyType | companyType | EnumCompanyType |  | cim | The type of company, e.g.: pool, municipal, private. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Company Type
CIMCore | Company | Company | Cooperative | Cooperative | Boolean | FALSE | etx | Cooperative boolean. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cooperative
CIMCore | Company | Company | DUNS | DUNS | String20 |  | etx | DUNS Number | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | DUNS
CIMCore | Company | Company | Municipality | Municipality | Boolean | FALSE | etx | Municipality boolean. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Municipality
CIMCore | Company | Company | PrimaryPhone | PrimaryPhone | String20 | (999) 999-9999 x____ | etx | Primary Phone number for contact. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Primary Phone
CIMCore | Company | Company | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number owners. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
CIMCore | Company | Company | qseId | qseId | String14 |  | etx | A 14 character QSE ID used for ERCOT LFC. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | QSE ID
CIMCore | Company | Company | qseOpaId | qseOpaId | String6 |  | etx | A 6 character QSE OPA ID for the QSE operating in the QSE Simulator. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | QSE OPA ID
CIMCore | Company | Company | SecondaryPhone | SecondaryPhone | String20 | (999) 999-9999 x____ | etx | Secondary Phone number for contact. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Secondary Phone
CIMCore | Company | Company | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
CIMCore | ConductingEquipment | ConductingEquipment | phases | phases | PhaseCode |  | cim | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phases
CIMCore | ConductingEquipment | ConductingEquipment | remove | remove | Boolean | FALSE | etx | The equipment is removed from the network. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Remove
CIMCore | ConductingEquipment | ConductingEquipment | removeEnable | removeEnable | Boolean | FALSE | etx | The equipment can be removed from the network. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Remove Enable
CIMCore | ControlHouseEquipment | ControlHouseEquipment | controlHouseEquipType | controlHouseEquipType | EnumControlHouseEquipmentType |  | cim | Type of control house equipment. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control House Equipment Type
CIMCore | Curve | Curve | curveStyle | curveStyle | EnumCurveStyle |  | cim | The style or shape of the curve. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Curve Style
CIMCore | Curve | Curve | xAxisUnits | xUnit | String20 |  | cim | The X-axis units of measure. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | X Axis Units
CIMCore | Curve | Curve | y1AxisUnits | y1Unit | String20 |  | cim | The Y1-axis units of measure. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Y1 Axis Units
CIMCore | Curve | Curve | y2AxisUnits | y2Unit | String20 |  | cim | The Y2-axis units of measure. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Y2 Axis Units
CIMCore | CurveData | CurveData | xAxisData | xvalue | DoubleFloat | 0 | cim | The data value of the X-axis variable, depending on the X-axis units | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | X Axis Data
CIMCore | CurveData | CurveData | y1AxisData | y1value | DoubleFloat | 0 | cim | The data value of the first Y-axis variable, depending on the Y-axis units | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Y1 Axis Data
CIMCore | CurveData | CurveData | y2AxisData | y2value | DoubleFloat |  | cim | The data value of the second Y-axis variable (if present), depending on the Y-axis units | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Y2 Axis Data
CIMCore | Equipment | Equipment | DAM_Monitored | DAM_Monitored | Boolean | FALSE | etx | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | DAM Monitored
CIMCore | Equipment | Equipment | DAM_Secured | DAM_Secured | Boolean | TRUE | etx | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | DAM Secured
CIMCore | Equipment | Equipment | height | height | Integer | 0 | spc | height | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | height
CIMCore | Equipment | Equipment | label_height | label_height | Integer | 0 | spc | label height | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | label height
CIMCore | Equipment | Equipment | label_width | label_width | Integer | 0 | spc | label width | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | label width
CIMCore | Equipment | Equipment | label_xval | label_xval | Integer | 0 | spc | label x co-ordinate | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | label x co-ordinate
CIMCore | Equipment | Equipment | label_yval | label_yval | Integer | 0 | spc | label y co-ordinate | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | label y co-ordinate
CIMCore | Equipment | Equipment | OUSPriority | OUSPriority | Integer |  | etx | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | OUS Priority
CIMCore | Equipment | Equipment | psseid | psseid | String2 |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | PSS®E ID
CIMCore | Equipment | Equipment | RUC_Monitored | RUC_Monitored | Boolean | FALSE | etx | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | RUC Monitored
CIMCore | Equipment | Equipment | RUC_Secured | RUC_Secured | Boolean | TRUE | etx | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | RUC Secured
CIMCore | Equipment | Equipment | width | width | Integer | 0 | spc | width | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | width
CIMCore | Equipment | Equipment | xval | xval | Integer | 0 | spc | x co-ordinate | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | x co-ordinate
CIMCore | Equipment | Equipment | yval | yval | Integer | 0 | spc | y co-ordinate | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | y co-ordinate
CIMCore | IdentifiedObject | IdentifiedObject | aliasName | aliasName | String100 |  | cim | Free text name of the object or instance. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Alias Name
CIMCore | IdentifiedObject | IdentifiedObject | Description | description | String1000 |  | cim | Description of the object or instance. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Description
CIMCore | IdentifiedObject | IdentifiedObject | localName | localName | String30 |  | cim | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Local Name
CIMCore | IdentifiedObject | IdentifiedObject | mRID | mRID | String100 |  | cim | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Model Resource ID
CIMCore | IdentifiedObject | IdentifiedObject | pathName | pathName | String500 |  | cim | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Path Name
CIMCore | IrregularTimePoint | IrregularTimePoint | time | time | Seconds |  | cim | The time is relative the BasicTimeSchedule.startTime. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time
CIMCore | IrregularTimePoint | IrregularTimePoint | value1 | value1 | Float |  | cim | Value 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value 1
CIMCore | IrregularTimePoint | IrregularTimePoint | value2 | value2 | Float |  | cim | Value 2. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value 2
CIMCore | PowerSystemResource | PowerSystemResource | Latitude | Latitude | Float |  | etx | Latiitude coordinates. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Latitude
CIMCore | PowerSystemResource | PowerSystemResource | Longitude | Longitude | Float |  | etx | Longitude coordinates. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Longitude
CIMCore | PowerSystemResource | PowerSystemResource | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
CIMCore | RegularIntervalSchedule | RegularIntervalSchedule | endTime | endTime | Time |  | cim | End Time. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | End Time
CIMCore | RegularIntervalSchedule | RegularIntervalSchedule | timeStep | timeStep | Seconds |  | cim | Time Step | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Time Step
CIMCore | RegularTimePoint | RegularTimePoint | rtName | rtName | String100 |  | etx | Equivalent of IdentifiedObject.name. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | RT Name
CIMCore | RegularTimePoint | RegularTimePoint | sequenceNumber | sequenceNumber | Integer |  | cim | Sequence Number. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Sequence Number
CIMCore | RegularTimePoint | RegularTimePoint | value1 | value1 | DoubleFloat |  | cim | Value 1. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value 1
CIMCore | RegularTimePoint | RegularTimePoint | value2 | value2 | DoubleFloat |  | cim | Value 2. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value 2
CIMCore | SubControlArea | SubControlArea | ControlAreaNumber | ControlAreaNumber | Integer |  | etx | The SubControlArea is extended to include a ControlAreaNumber attribute to determine ordering of the areas (e.g., for display purposes). The values must be positive, unique, 1-relative, sequential integers without gaps. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Control Area Number
CIMCore | SubControlArea | SubControlArea | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number Alternate Areas and Zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
CIMCore | SubGeographicalRegion | SubGeographicalRegion | isWeatherZone | isWeatherZone | Bool | FALSE | etx | Indicates whether a SubGeographicalRegion is a Weather Zone. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | is WeatherZone
CIMCore | SubGeographicalRegion | SubGeographicalRegion | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number Alternate Areas and Zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
CIMCore | Substation | Substation | abnormalForAlarm | abnormalForAlarm | Boolean | FALSE | etx | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Abnormal For Alarm
CIMCore | Substation | Substation | abnormalForSCADA | abnormalForSCADA | Boolean | FALSE | etx | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Abnormal For SCADA
CIMCore | Substation | Substation | alarmLocation | alarmLocation | String8 |  | etx | Alarm location, must match LOC.ID_LOC in the Alarm database. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Alarm Location
CIMCore | Substation | Substation | audibleTone | audibleTone | Boolean | FALSE | etx | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Audible Tone
CIMCore | Substation | Substation | forNetwork | forNetwork | Bool | FALSE | etx | This flag is used to indicate this substation is used by Network application. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | for Network
CIMCore | Substation | Substation | forScada | forScada | Bool | FALSE | etx | This flag is used to indicate this substation is used by SCADA application. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | for Scada
CIMCore | Substation | Substation | inhibitAbnormalForAlarm | inhibitAbnormalForAlarm | Boolean | FALSE | etx | Permanently Inhibit the flag of abnormalForAlarm . | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Abnormal For Alarm
CIMCore | Substation | Substation | inhibitAbnormalForSCADA | inhibitAbnormalForSCADA | Boolean | FALSE | etx | Permanently Inhibit the flag of abnormalForSCADA. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Abnormal For SCADA
CIMCore | Substation | Substation | inhibitAudibleTone | inhibitAudibleTone | Boolean | FALSE | etx | Permanently Inhibit the flag of audibleTone. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Audible Tone
CIMCore | Substation | Substation | inhibitLoggingAndAlarmList | inhibitLoggingAndAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Logging and Alarm List
CIMCore | Substation | Substation | inhibitUnackAlarmList | inhibitUnacknowledgedAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Unacknowledged Alarm List
CIMCore | Substation | Substation | initiallyInhibit | initiallyInhibit | Boolean | FALSE | etx | A flag indicating that when the system first comes online, alarm indications for this SCADA entiry will initially be inhibited. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Initially Inhibit
CIMCore | Substation | Substation | loggingAndAlarmList | loggingAndAlarmList | Boolean | FALSE | etx | A flag indicating that SCADA will issue neither an alarm nor an event. Therefore, entries will appear in the neither the alarm list nor the event logs. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Logging and Alarm List
CIMCore | Substation | Substation | overrideDefaultInhibitDef | overrideDefaultInhibitDefinition | Boolean | FALSE | etx | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Override Default Inhibit Definition
CIMCore | Substation | Substation | unacknowledgedAlarmList | unacknowledgedAlarmList | Boolean | FALSE | etx | A flag ndicating that SCADA will issue an event to the event log, but will not issue unacknowledged alarm indications to the alarm list. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Unacknowledged Alarm List
CIMCore | Terminal | Terminal | edgeVal | edgeVal | String500 |  | spc | edgeVal is a concatenation of all edge coordinates. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Edge Val
CIMCore | Terminal | Terminal | fromxoffset | fromxoffset | Integer | 0 | spc | From X offset | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | From X offset
CIMCore | Terminal | Terminal | fromxperm | fromxperm | Integer | 0 | spc | From X perm | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | From X perm
CIMCore | Terminal | Terminal | fromyoffset | fromyoffset | Integer | 0 | spc | From Y offset | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | From Y offset
CIMCore | Terminal | Terminal | fromyperm | fromyperm | Integer | 0 | spc | From Y perm | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | From Y perm
CIMCore | Terminal | Terminal | height | height | Integer | 0 | spc | height | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | height
CIMCore | Terminal | Terminal | label_height | label_height | Integer | 0 | spc | label height | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | label height
CIMCore | Terminal | Terminal | label_width | label_width | Integer | 0 | spc | label width | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | label width
CIMCore | Terminal | Terminal | label_xval | label_xval | Integer | 0 | spc | label x co-ordinate | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | label x co-ordinate
CIMCore | Terminal | Terminal | label_yval | label_yval | Integer | 0 | spc | label y co-ordinate | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | label y co-ordinate
CIMCore | Terminal | Terminal | near | near | Boolean | FALSE | etx | Flag indicating whether the terminal is a near terminal of a branch. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Near
CIMCore | Terminal | Terminal | PSSEBusName | PSSEBusName | String12 |  | etx | Store the PSS™E bus name that will be associated with the grouping of Connectivity Nodes in Option 2. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | PSS/E Bus Name
CIMCore | Terminal | Terminal | PSSEBusNumber | PSSEBusNumber | Integer |  | etx | Attribute will be used to store the PSS™E bus number that will be associated with the grouping of Connectivity Nodes in Option 2. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 99997 | 1 | PSS/E Bus Number
CIMCore | Terminal | Terminal | toxoffset | toxoffset | Integer | 0 | spc | To X offset | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | To X offset
CIMCore | Terminal | Terminal | toxperm | toxperm | Integer | 0 | spc | To X perm | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | To X perm
CIMCore | Terminal | Terminal | toyoffset | toyoffset | Integer | 0 | spc | To Y offset | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | To Y offset
CIMCore | Terminal | Terminal | toyperm | toyperm | Integer | 0 | spc | To Y perm | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | To Y perm
CIMCore | Terminal | Terminal | width | width | Integer | 0 | spc | width | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | width
CIMCore | Terminal | Terminal | xval | xval | Integer | 0 | spc | x co-ordinate | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | x co-ordinate
CIMCore | Terminal | Terminal | yval | yval | Integer | 0 | spc | y co-ordinate | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | y co-ordinate
CIMCore | VoltageLevel | VoltageLevel | highVoltageLimit | highVoltageLimit | Voltage |  | cim | The bus bar's high voltage limit in kV | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1100 | 0 | High Voltage Limit
CIMCore | VoltageLevel | VoltageLevel | lowVoltageLimit | lowVoltageLimit | Voltage |  | cim | The bus bar's low voltage limit in kV. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1100 | 0 | Low Voltage Limit
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | highPowerLimit | highPowerLimit | PU | 0.1 | cim | High Power Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | High Power Limit
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | inCoreThermalTC | inCoreThermalTC | Seconds | 10.9 | cim | In-Core Thermal Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | In Core Thermal TC
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | integralGain | integralGain | RateOfChange | 0.386 | cim | Integral Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 4 | 0.04 | Integral Gain
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | lowerLimit | lowerLimit | PU | 0.56 | cim | Initial Lower Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Lower Limit
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | lowPowerLimit | lowPowerLimit | PU | 0.1 | cim | Low Power Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Low Power Limit
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | pressureLimit | pressureLimit | PU | 0.09 | cim | Pressure Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Pressure Limit
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | pressureSetpointGA | pressureSetpointGA | Float | 0.222 | cim | Pressure Setpoint Gain Adjuster | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 2 | 0.02 | Pressure Setpoint GA
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | pressureSetpointTC1 | pressureSetpointTC1 | Seconds | 9 | cim | Pressure Setpoint Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 1 | Pressure Setpoint TC1
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | pressureSetpointTC2 | pressureSetpointTC2 | Seconds | 3 | cim | Pressure Setpoint Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 30 | 0 | Pressure Setpoint TC2
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | proportionalGain | proportionalGain | Float | 0 | cim | Proportional Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Proportional Gain
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux1 | rfAux1 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux1
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux2 | rfAux2 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux2
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux3 | rfAux3 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux3
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux4 | rfAux4 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux4
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux5 | rfAux5 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux5
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux6 | rfAux6 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux6
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux7 | rfAux7 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux7
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux8 | rfAux8 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux8
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rodPatternConstant | rodPatternConstant | Float | 0.32 | cim | Constant Associated With Rod Pattern | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Rod Pattern Constant
CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | upperLimit | upperLimit | PU | 1.05 | cim | Initial Upper Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1.5 | 0 | Upper Limit
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | ambientTemp | ambientTemp | Temperature | 15 | cim | Default ambient temperature to be used in modeling applications | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 30 | 0 | Ambient Temp
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | auxPowerVersusFrequency | auxPowerVersusFrequency | PowerVersusFrequency |  | cim | Off-nominal frequency effect on turbine auxiliaries. Per unit reduction in auxiliary MW consumption versus per unit reduction in frequency (from rated frequency). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Aux Power Versus Frequency
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | auxPowerVersusVoltage | auxPowerVersusVoltage | PowerVersusVoltage |  | cim | Off-nominal voltage effect on turbine auxiliaries. Per unit reduction in auxiliary MW consumption versus per unit reduction in auxiliary bus voltage (from a specified voltage level). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Aux Power Versus Voltage
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | capabiltiyVersusFrequency | capabiltiyVersusFrequency | PowerVersusFrequency |  | cim | Off-nominal frequency effect on turbine capability. Per unit reduction in unit MW capability versus per unit reduction in frequency (from rated frequency). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Capability Versus Frequency
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | fractionPlcControl | fractionPlcControl | PerCent |  | etx | Fraction of the PLC Control. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fraction of the PLC Control
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | freqAffectAux | freqAffectAux | Frequency |  | etx | Frequency above which auxiliaries are unaffected. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Affected Auxiliaries
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | governorDeadband | governorDeadband | PU |  | etx | Governor Dead Band | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Governor Dead Band
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | heatRecoveryFlag | heatRecoveryFlag | Boolean | FALSE | cim | Flag that is set to true if the combustion turbine is associated with a heat recovery boiler | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Heat Recovery Flag
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | lrmLowerLimit | lrmLowerLimit | PU |  | etx | Load Reference Motor Lower Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Lower Limit
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | lrmLowerRateLimit | lrmLowerRateLimit | RateOfChange |  | etx | Load Reference Motor Lower Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Lower Rate Limit
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | lrmRaiseRateLimit | lrmRaiseRateLimit | RateOfChange |  | etx | Load Reference Motor Raise Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Raise Rate Limit
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | lrmUpperLimit | lrmUpperLimit | PU |  | etx | Load Reference Motor Upper Limit.. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Upper Limit
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | powerMN | powerMN | ActivePower |  | etx | Power Based on Fuel Flow Minimum. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Power Minimum
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | powerMX | powerMX | ActivePower |  | etx | Power Based on Fuel Flow Maximum. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Power Maximum
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | powerVariationByTemp | powerVariationByTemp | PU | 0.11 | cim | Per unit change in power per (versus) unit change in ambient temperature | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0.01 | Power Variation By Temp
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | referenceTemp | referenceTemp | Temperature | 15 | cim | Reference temperature at which the output of the turbine was defined. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 30 | 0 | Reference Temp
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | regulationConstant | regulationConstant | PU |  | etx | Regulation Constant. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Regulation Constant
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | timeConstant | timeConstant | Seconds | 0.25 | cim | The time constant for the turbine. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 2 | 0.02 | Time Constant
CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | voltAffectAux | voltAffectAux | Voltage |  | etx | Voltage above which auxiliaries are unaffected. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Voltage Affected Auxiliaries
CIMGenerationDynamics | CTTEMPMWCurve | CTTEMPMWCurve | temperatureUnits | temperatureUnits | EnumTemperatureUnits |  | cim | The temperature units (C or F). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Temperature Units
CIMGenerationDynamics | DrumBoiler | DrumBoiler | drumBoilerRating | drumBoilerRating | Float |  | cim | Rating of drum boiler in steam units. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Drum Boiler Rating
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | auxPowerVersusFrequency | auxPowerVersusFrequency | PowerVersusFrequency |  | cim | Off nominal frequency effect on auxiliary real power. Per unit MW variation versus per unit frequency variation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Aux Power Versus Frequency
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | auxPowerVersusVoltage | auxPowerVersusVoltage | PowerVersusVoltage |  | cim | Off nominal voltage effect on auxiliary real power. Per unit MW variation versus per unit kV variation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Aux Power Versus Voltage
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | boilerControlMode | boilerControlMode | EnumBoilerControlMode |  | cim | The control mode of the boiler. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Boiler Control Mode
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | controlIC | controlIC | Float |  | cim | Integral Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Integral Constant
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | controlMWEB | controlMWEB | Ratio |  | cim | MW Error Bias | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control MW Error Bias
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | controlPC | controlPC | Float |  | cim | Proportional Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Proportional Constant
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | controlPEB | controlPEB | Ratio |  | cim | Pressure Error Bias | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Pressure Error Bias
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | controlPED | controlPED | PU |  | cim | Pressure Error Deadband | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Pressure Error Deadband
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | controlTC | controlTC | Float |  | cim | Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Time Constant
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | feedWaterIG | feedWaterIG | Ratio |  | cim | Feedwater Integral Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Feedwater Integral Gain
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | feedWaterPG | feedWaterPG | Ratio |  | cim | Feedwater Proportional Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Feedwater Proportional Gain
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | feedWaterTC | feedWaterTC | Seconds |  | cim | Feedwater Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Feedwater Time Constant
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | fuelDemandLimit | fuelDemandLimit | PU | 1 | cim | Fuel Demand Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Fuel Demand Limit
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | fuelSupplyDelay | fuelSupplyDelay | Seconds |  | cim | Fuel Delay | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Delay
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | fuelSupplyTC | fuelSupplyTC | Seconds |  | cim | Fuel Supply Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Supply Time Constant
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | mechPowerSensorLag | mechPowerSensorLag | Seconds | 1 | cim | Mechanical Power Sensor Lag | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 20 | 0 | Mech Power Sensor Lag
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | mWMaximumER | mWMaximumER | RateOfChange | 0.13 | cim | MW Maximum Error Rate Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | MW Maximum ER
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | mWMinimumER | mWMinimumER | RateOfChange | -0.13 | cim | MW Minimum Error Rate Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 0 | -1 | MW Minimum ER
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | pressureCtrlDG | pressureCtrlDG | Ratio |  | cim | Pressure Control Derivative Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pressure Control Derivative Gain
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | pressureCtrlG | pressureCtrlG | Ratio |  | cim | Pressure Control Integratl Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pressure Control Integratl Gain
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | pressureCtrlPG | pressureCtrlPG | Ratio |  | cim | Pressure Control Proportional Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pressure Control Proportional Gain
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | pressureFeedback | pressureFeedback | Integer | 1 | cim | Pressure Feedback Indicator | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 4 | 0 | Pressure Feedback
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | superHeater1Capacity | superHeater1Capacity | Float |  | cim | Drum/Primary Superheater Capacity | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Drum/Primary Superheater Capacity
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | superHeater2Capacity | superHeater2Capacity | Float |  | cim | Secondary Superheater Capacity | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Secondary Superheater Capacity
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | superHeaterPipePD | superHeaterPipePD | Float |  | cim | Superheater Pipe Pressure Drop Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Superheater Pipe Pressure Drop Constant
CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | throttlePressureSP | throttlePressureSP | PU | 1 | cim | Throttle Pressure Setpoint | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Throttle Pressure SP
CIMGenerationDynamics | HeatRecoveryBoiler | HeatRecoveryBoiler | steamSupplyRating2 | steamSupplyRating2 | Float |  | cim | The steam supply rating in kilopounds per hour, if dual pressure boiler. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Steam Supply Rating 2
CIMGenerationDynamics | HydroTurbine | HydroTurbine | backlashWidth | backlashWidth | PU |  | etx | Backlash Width. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Backlash Width
CIMGenerationDynamics | HydroTurbine | HydroTurbine | fractionPlcControl | fractionPlcControl | PerCent |  | etx | Fraction of the PLC Control. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fraction of the PLC Control
CIMGenerationDynamics | HydroTurbine | HydroTurbine | gateCloseRateLimit | gateCloseRateLimit | RateOfChange |  | etx | Gate Close Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gate Close Rate Limit
CIMGenerationDynamics | HydroTurbine | HydroTurbine | gateLowerLimit | gateLowerLimit | PU |  | etx | Gate Lower Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gate Lower Limit
CIMGenerationDynamics | HydroTurbine | HydroTurbine | gateOpenRateLimit | gateOpenRateLimit | RateOfChange |  | etx | Gate Open Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gate Open Rate Limit
CIMGenerationDynamics | HydroTurbine | HydroTurbine | gateRateLimit | gateRateLimit | RateOfChange |  | cim | Gate Rate Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gate Rate Limit
CIMGenerationDynamics | HydroTurbine | HydroTurbine | gateUpperLimit | gateUpperLimit | PU |  | cim | Gate Upper Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gate Upper Limit
CIMGenerationDynamics | HydroTurbine | HydroTurbine | lrmLowerLimit | lrmLowerLimit | PU |  | etx | Load Reference Motor Lower Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Lower Limit
CIMGenerationDynamics | HydroTurbine | HydroTurbine | lrmLowerRateLimit | lrmLowerRateLimit | RateOfChange |  | etx | Load Reference Motor Lower Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Lower Rate Limit
CIMGenerationDynamics | HydroTurbine | HydroTurbine | lrmRaiseRateLimit | lrmRaiseRateLimit | RateOfChange |  | etx | Load Reference Motor Raise Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Raise Rate Limit
CIMGenerationDynamics | HydroTurbine | HydroTurbine | lrmUpperLimit | lrmUpperLimit | PU |  | etx | Load Reference Motor Upper Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Upper Limit
CIMGenerationDynamics | HydroTurbine | HydroTurbine | maxEffMWatMaxHead | maxEffMWatMaxHead | ActivePower |  | cim | Maximum efficiency MW at maximum head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Efficiency MW at Max Head
CIMGenerationDynamics | HydroTurbine | HydroTurbine | maxEffMWatMinHead | maxEffMWatMinHead | ActivePower |  | cim | Maximum efficiency MW at minimum head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Efficiency MW at Min Head
CIMGenerationDynamics | HydroTurbine | HydroTurbine | speedRating | speedRating | Integer |  | cim | Rated speed in revolutions per minute. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Speed Rating
CIMGenerationDynamics | HydroTurbine | HydroTurbine | speedRegulation | speedRegulation | PU |  | cim | Speed Regulation | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Speed Regulation
CIMGenerationDynamics | HydroTurbine | HydroTurbine | transientDroopTime | transientDroopTime | Seconds | 64 | cim | Transient Droop Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 500 | 1 | Transient Droop Time
CIMGenerationDynamics | HydroTurbine | HydroTurbine | transientRegulation | transientRegulation | PU | 0.125 | cim | Transient Regulation | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 2 | 0.01 | Transient Regulation
CIMGenerationDynamics | HydroTurbine | HydroTurbine | turbineRating | turbineRating | ActivePower |  | cim | Rated turbine power in MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Turbine Rating
CIMGenerationDynamics | HydroTurbine | HydroTurbine | turbineType | turbineType | EnumTurbineType |  | cim | Type of turbine, e.g.: Francis, Pelton, Kaplan. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Turbine Type
CIMGenerationDynamics | HydroTurbine | HydroTurbine | waterStartingTime | waterStartingTime | Seconds | 2 | cim | Water Starting Time | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 20 | 0.2 | Water Starting Time
CIMGenerationDynamics | PrimeMover | PrimeMover | primeMoverRating | primeMoverRating | Float |  | cim | Rating of prime mover. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Prime Mover Rating
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coldLegFBLagTC | coldLegFBLagTC | PU | 4.065 | cim | Cold Leg Feedback Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 40 | 0.4 | Cold Leg FBLag TC
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coldLegFBLeadTC1 | coldLegFBLeadTC1 | PU | 3.56 | cim | Cold Leg Feedback Lead Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 35 | 0.35 | Cold Leg FB Lead TC1
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coldLegFBLeadTC2 | coldLegFBLeadTC2 | PU | 3.94 | cim | Cold Leg Feedback Lead Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 40 | 0.4 | Cold Leg FB Lead TC2
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coldLegFG1 | coldLegFG1 | PU | 8.05 | cim | Cold Leg Feedback Gain 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 80 | 0.8 | Cold Leg FG1
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coldLegFG2 | coldLegFG2 | PU | 0.974 | cim | Cold Leg Feedback Gain 2 | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 10 | 0.01 | Cold Leg FG2
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coldLegLagTC | coldLegLagTC | PU | 4.67 | cim | Cold Leg Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 46 | 0.46 | Cold Leg Lag TC
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coreHTLagTC1 | coreHTLagTC1 | PU | 2.105 | cim | Core Heat Transfer Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 20 | 0.2 | Core HTLag TC1
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coreHTLagTC2 | coreHTLagTC2 | PU | 20.835 | cim | Core Heat Transfer Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 200 | 2 | Core HTLag TC2
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coreNeutronicsEffTC | coreNeutronicsEffTC | PU | 12.195 | cim | Core Neutronics Effective Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 120 | 1.2 | Core Neutronics Eff TC
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coreNeutronicsHT | coreNeutronicsHT | PU | 0.032 | cim | Core Neutronics And Heat Transfer | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 0.3 | 0.003 | Core Neutronics HT
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | feedbackFactor | feedbackFactor | PU | 7.25 | cim | Feedback Factor | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 70 | 0.07 | Feedback Factor
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | hotLegLagTC | hotLegLagTC | PU | 3.19 | cim | Hot Leg Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 32 | 0.32 | Hot Leg Lag TC
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | hotLegSteamGain | hotLegSteamGain | PU | 1.3 | cim | Hot Leg Steam Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 13 | 0.13 | Hot Leg Steam Gain
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | hotLegToColdLegGain | hotLegToColdLegGain | PU | 0.397 | cim | Hot Leg To Cold Leg Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 4 | 0.04 | Hot Leg To Cold Leg Gain
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | pressureCG | pressureCG | PU | 0.75 | cim | Pressure Control Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 7.5 | 0.075 | Pressure CG
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | steamFlowFG | steamFlowFG | PU | 0.54 | cim | Steam Flow Feedback Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 5.4 | 0.054 | Steam Flow FG
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | steamPressureDropLagTC | steamPressureDropLagTC | PU | 1.56 | cim | Steam Pressure Drop Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 15 | 0.15 | Steam Pressure Drop Lag TC
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | steamPressureFG | steamPressureFG | PU | 1 | cim | Steam Pressure Feedback Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 10 | 0.1 | Steam Pressure FG
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | throttlePressureFactor | throttlePressureFactor | PU | 0.613 | cim | Throttle Pressure Factor | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 6 | 0.06 | Throttle Pressure Factor
CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | throttlePressureSP | throttlePressureSP | PU | 1 | cim | Throttle Pressure Setpoint | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Throttle Pressure SP
CIMGenerationDynamics | SteamSupply | SteamSupply | steamSupplyRating | steamSupplyRating | Float |  | cim | Rating of steam supply. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Steam Supply Rating
CIMGenerationDynamics | SteamTurbine | SteamTurbine | crossoverTC | crossoverTC | Seconds | 0 | cim | Crossover Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Crossover TC
CIMGenerationDynamics | SteamTurbine | SteamTurbine | cvLowerLimit | cvLowerLimit | PU |  | etx | Control Valve Lower Limits. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Valve Lower Limits
CIMGenerationDynamics | SteamTurbine | SteamTurbine | cvLowerRateLimit | cvLowerRateLimit | RateOfChange |  | etx | Control Valve Lower Rate Limits. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Valve Lower Rate Limits
CIMGenerationDynamics | SteamTurbine | SteamTurbine | cvRaiseRateLimit | cvRaiseRateLimit | RateOfChange |  | etx | Control Valve Raise Rate Limits. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Valve Raise Rate Limits
CIMGenerationDynamics | SteamTurbine | SteamTurbine | cvUpperLimit | cvUpperLimit | PU |  | etx | Control Valve Upper Limits. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Valve Upper Limits
CIMGenerationDynamics | SteamTurbine | SteamTurbine | fractionPlcControl | fractionPlcControl | PerCent |  | etx | Fraction of the PLC Control. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fraction of the PLC Control
CIMGenerationDynamics | SteamTurbine | SteamTurbine | governorDeadband | governorDeadband | PU |  | etx | Governor Dead Band | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Governor Dead Band
CIMGenerationDynamics | SteamTurbine | SteamTurbine | lrmLowerLimit | lrmLowerLimit | PU |  | etx | Load Reference Motor Lower Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Lower Limit
CIMGenerationDynamics | SteamTurbine | SteamTurbine | lrmLowerRateLimit | lrmLowerRateLimit | RateOfChange |  | etx | Load Reference Motor Lower Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Lower Rate Limit
CIMGenerationDynamics | SteamTurbine | SteamTurbine | lrmRaiseRateLimit | lrmRaiseRateLimit | RateOfChange |  | etx | Load Reference Motor Raise Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Raise Rate Limit
CIMGenerationDynamics | SteamTurbine | SteamTurbine | lrmUpperLimit | lrmUpperLimit | PU |  | etx | Load Reference Motor Upper Limit.. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Upper Limit
CIMGenerationDynamics | SteamTurbine | SteamTurbine | regulationConstant | regulationConstant | PU |  | etx | Regulation Constant. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Regulation Constant
CIMGenerationDynamics | SteamTurbine | SteamTurbine | reheater1TC | reheater1TC | Seconds | 8 | cim | First Reheater Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Reheater1 TC
CIMGenerationDynamics | SteamTurbine | SteamTurbine | reheater2TC | reheater2TC | Seconds | 0 | cim | Second Reheater Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Reheater2 TC
CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft1PowerHP | shaft1PowerHP | Fraction | 0.3 | cim | Fraction Of Power From Shaft 1 High Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft1 Power HP
CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft1PowerIP | shaft1PowerIP | Fraction | 0.7 | cim | Fraction Of Power From Shaft 1 Intermediate Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft1 Power IP
CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft1PowerLP1 | shaft1PowerLP1 | Fraction | 0 | cim | Fraction Of Power From Shaft 1 First Low Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft1 Power LP1
CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft1PowerLP2 | shaft1PowerLP2 | Fraction | 0 | cim | Fraction Of Power From Shaft 1 Second Low Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft1 Power LP2
CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft2PowerHP | shaft2PowerHP | Fraction |  | cim | Fraction Of Power From Shaft 2 High Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Shaft2 Power HP
CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft2PowerIP | shaft2PowerIP | Fraction | 0 | cim | Fraction Of Power From Shaft 2 Intermediate Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft2 Power IP
CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft2PowerLP1 | shaft2PowerLP1 | Fraction | 0 | cim | Fraction Of Power From Shaft 2 First Low Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft2 Power LP1
CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft2PowerLP2 | shaft2PowerLP2 | Fraction | 0 | cim | Fraction Of Power From Shaft 2 Second Low Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft2 Power LP2
CIMGenerationDynamics | SteamTurbine | SteamTurbine | slidingPressureScalingFactor | slidingPressureScalingFactor | PerCent |  | etx | Sliding Pressure Scaling Factor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Sliding Pressure Scaling Factor
CIMGenerationDynamics | SteamTurbine | SteamTurbine | steamChestTC | steamChestTC | Seconds | 0 | cim | Steam Chest Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Steam Chest TC
CIMLoadModel | DayType | DayType | endTime | endTime | AbsoluteDateTime |  | etx | Time daytype ends | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | End Time
CIMLoadModel | DayType | DayType | FriFlag | FriFlag | Bool | FALSE | etx | Indicates whether Friday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Fri Flag
CIMLoadModel | DayType | DayType | MonFlag | MonFlag | Bool | FALSE | etx | Indicates whether Monday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Mon Flag
CIMLoadModel | DayType | DayType | SatFlag | SatFlag | Bool | FALSE | etx | Indicates whether Saturday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Sat Flag
CIMLoadModel | DayType | DayType | startTime | startTime | AbsoluteDateTime |  | etx | Time daytype starts | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Start Time
CIMLoadModel | DayType | DayType | SunFlag | SunFlag | Bool | FALSE | etx | Indicates whether Sunday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Sun Flag
CIMLoadModel | DayType | DayType | ThursFlag | ThursFlag | Bool | FALSE | etx | Indicates whether Thursday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Thurs Flag
CIMLoadModel | DayType | DayType | TuesFlag | TuesFlag | Bool | FALSE | etx | Indicates whether Tuesday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Tues Flag
CIMLoadModel | DayType | DayType | WedFlag | WedFlag | Bool | FALSE | etx | Indicates whether Wednesday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Wed Flag
CIMLoadModel | InductionMotorLoad | InductionMotorLoad | r | r | DoubleFloat |  | etx | motor r. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | r
CIMLoadModel | InductionMotorLoad | InductionMotorLoad | rtransformer | rtransformer | Float |  | etx | stepup transformer r. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | r Transformer
CIMLoadModel | InductionMotorLoad | InductionMotorLoad | varhighlimit | varhighlimit | Float |  | etx | motor var high limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Var High Limit
CIMLoadModel | InductionMotorLoad | InductionMotorLoad | varlowlimit | varlowlimit | Float |  | etx | motor var low limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Var Low Limit
CIMLoadModel | InductionMotorLoad | InductionMotorLoad | x | x | DoubleFloat |  | etx | motor x. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | x
CIMLoadModel | InductionMotorLoad | InductionMotorLoad | xtransformer | xtransformer | Float |  | etx | stepup transformer x. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | x Transformer
CIMLoadModel | Load | Load | feederLoadMgtFactor | feederLoadMgtFactor | PerCent |  | cim | The feeder's contribution to load management, in percent. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Feeder Load Mgt Factor
CIMLoadModel | Load | Load | loadAllocationFactor | loadAllocationFactor | Float |  | cim | Permit assignment of loads on a participation factor basis. Given three equivalent loads with factors of 10, 25 and 15, a feeder load of 100 amps could be allocated on the feeder as 20, 50 and 30 amps. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Allocation Factor
CIMLoadModel | Load | Load | mVArColdPickUpFactor | mVArColdPickUpFactor | PerCent |  | cim | The amount of nominal feeder MVAr that is picked up cold, in percent. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | MVAR Cold Pick Up Factor
CIMLoadModel | Load | Load | mWColdPickUpFactor | mWColdPickUpFactor | PerCent |  | cim | The amount of nominal feeder MW that is picked up cold, in percent. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | MW Cold Pick Up Factor
CIMLoadModel | Load | Load | phaseAmpRating | phaseAmpRating | CurrentFlow |  | cim | The rated individual phase amperes. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phase Amp Rating
CIMLoadModel | LoadArea | LoadArea | forecastEnabled | forecastEnabled | Boolean | FALSE | etx | Forecast enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Forecast Enabled
CIMLoadModel | LoadArea | LoadArea | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number Alternate Areas and Zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
CIMLoadModel | LoadGroup | LoadGroup | forecastEnabled | forecastEnabled | Boolean | FALSE | etx | Forecast enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Forecast Enabled
CIMLoadModel | PowerCutZone | PowerCutZone | cutLevel1 | cutLevel1 | PerCent |  | cim | First level (amount) of load to cut as a percentage of total zone load. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cut Level 1
CIMLoadModel | PowerCutZone | PowerCutZone | cutLevel2 | cutLevel2 | PerCent |  | cim | Second level (amount) of load to cut as a percentage of total zone load. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cut Level 2
CIMLoadModel | Season | Season | endDate | endDate | AbsoluteDateTime |  | cim | Date season ends. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | End Date
CIMLoadModel | Season | Season | SeasonName | name | EnumSeasonName |  | cim | Name of the Season. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Season Name
CIMLoadModel | Season | Season | startDate | startDate | AbsoluteDateTime |  | cim | Date season starts. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Start Date
CIMLoadModel | StationSupply | StationSupply | step | step | Boolean | FALSE | etx | Schedule is step function. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Step
CIMLoadModel | SubLoadArea | SubLoadArea | forecastEnabled | forecastEnabled | Boolean | FALSE | etx | Forecast enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Forecast Enabled
CIMMeas | Accumulator | Accumulator | maxValue | maxValue | Integer |  | cim | Normal value range maximum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  | 0 | Max Value
CIMMeas | AccumulatorLimit | AccumulatorLimit | value | value | Integer |  | cim | The value to supervise against. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Value
CIMMeas | AccumulatorValue | AccumulatorValue | value | value | Integer |  | cim | Value of measurement. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Value
CIMMeas | Analog | Analog | forNetwork | forNetwork | Bool | FALSE | etx | If true then this measurement is only for network monitoring. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | for Network
CIMMeas | Analog | Analog | maxValue | maxValue | Float |  | cim | Normal value range maximum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Value
CIMMeas | Analog | Analog | minValue | minValue | Float |  | cim | Normal value range minimum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Value
CIMMeas | Analog | Analog | normalValue | normalValue | Float |  | cim | Normal measurement value, e.g., used for percentage calculations. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Normal Value
CIMMeas | Analog | Analog | positiveFlowIn | positiveFlowIn | Boolean | FALSE | cim | If true then this measurement is a MW, MVAR or AMPS with the convention that a positive value measured at the Terminal means power is flowing into the related PowerSystemResource. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Positive Flow In
CIMMeas | Analog | Analog | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
CIMMeas | AnalogLimit | AnalogLimit | deadband | deadband | PerCent |  | etx | Amount, expressed as a percentage of the range between upper and lower threshold, used in the limit comparison to eliminate extraneous alarms generated when an analog value oscillates around a limit. When either threshold is null, the percentage is that of the non?null limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Deadband
CIMMeas | AnalogLimit | AnalogLimit | forbiddenRegion | forbiddenRegion | Boolean | FALSE | etx | T = The analog is in violation if it is smaller than the Upper Threshold and larger than the Lower Threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Forbidden Region
CIMMeas | AnalogLimit | AnalogLimit | ignoreLimitChecking | ignoreLimitChecking | Boolean | FALSE | etx | T = The limit should be ignored when checking the analog for limit violations. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Ignore Limit Checking
CIMMeas | AnalogLimit | AnalogLimit | limitType | limitType | EnumLimitType |  | etx | Type of limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Limit Type
CIMMeas | AnalogLimit | AnalogLimit | lowerThreshold | lowerThreshold | Float |  | etx | The value below which the analog is considered in violation of the limit. When the Upper Threshold is null, only the Lower Threshold is checked for violation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Lower Threshold
CIMMeas | AnalogLimit | AnalogLimit | upperThreshold | upperThreshold | Float |  | etx | The value above which the analog is considered in violation of the limit. When the low limit is null, only the high limit is checked for violation. This value must be greater then the Lower Threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Upper Threshold
CIMMeas | AnalogLimit | AnalogLimit | usePercentage | usePercentage | Boolean | FALSE | etx | T = The value displayed in the deadband field (below) is the percentage deadband. Otherwise, the value displayed is the numeric deadband. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Use Percentage
CIMMeas | AnalogLimit | AnalogLimit | value | value | DoubleFloat |  | cim | The value to supervise against. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value
CIMMeas | AnalogLimit | AnalogLimit | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temporary attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
CIMMeas | AnalogValue | AnalogValue | abnormalAlarmDelayTime | abnormalAlarmDelayTime | Integer |  | etx | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the violated state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Abnormal Alarm Delay Time
CIMMeas | AnalogValue | AnalogValue | allowSELECTStep | allowSELECTStep | Boolean | FALSE | etx | TRUE = a separate SELECT action is allowed (but not required) prior to the supervisory control action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Allow SELECT Step
CIMMeas | AnalogValue | AnalogValue | autoAckAndDeleteAlarms | autoAckAndDeleteAlarms | Boolean | FALSE | etx | Automatically acknowledge and delete alarms if the Analog is manually entered or successfully controlled by the operator to a normal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Auto Ack and Delete Alarms
CIMMeas | AnalogValue | AnalogValue | autoAcknowledge | autoAcknowledge | Boolean | FALSE | etx | When set to true, this flag specifies that alarms will be automatically acknowledged on return to normal. This will only occur if the Alarm Return to Violations flag is not set on the Limit Names table. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Auto Acknowledge
CIMMeas | AnalogValue | AnalogValue | controlDemandScan | controlDemandScan | Boolean | FALSE | etx | True = Issues a demand scan request to the RTU at a configurable number of seconds after any successful control requests are issued. This feature is primarily used by measurements with a slow scan rate to provide more timely feedback on the success or failure of the control operation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Control Demand Scan
CIMMeas | AnalogValue | AnalogValue | controlMMISequence | controlMMISequence | Boolean | FALSE | etx | true = override any default settings. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Control MMI Sequence
CIMMeas | AnalogValue | AnalogValue | enableAutoSEReplacement | enableAutoSEReplacement | Boolean | FALSE | etx | TRUE = Allow automatic State Estimator replacement. Automatically substitute the display value with a good quality state estimated value if the quality of the telemetered analog becomes SUSPECT. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Enable Auto SE Replacement
CIMMeas | AnalogValue | AnalogValue | fromStateEstimator | fromStateEstimator | Boolean | FALSE | etx | When set to true, this flag specifies the source of the data is state estimator. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | From State Estimator
CIMMeas | AnalogValue | AnalogValue | historicalRecordingDeadband | historicalRecordingDeadband | PerCent |  | etx | Threshold (percentage currently recorded analog data) above which additional data points should not retained. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Historical Recording Deadband
CIMMeas | AnalogValue | AnalogValue | invertAnalogViaSecondarySite | invertAnalogViaSecondarySite | Boolean | FALSE | etx | TRUE = Negate the analog value when received from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Analog Via Secondary Site
CIMMeas | AnalogValue | AnalogValue | invertSign | invertSign | Boolean | FALSE | etx | When set to true, this flag specifies that the analog value, as received by SCADA, is inverted before using in other applications. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Sign
CIMMeas | AnalogValue | AnalogValue | negateValueReceivedFromISD | negateValueReceivedFromISD | Boolean | FALSE | etx | When set to true, this flag specifies that the polarity of the analog value received via ISD will be switched. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Negate Value Received from ISD
CIMMeas | AnalogValue | AnalogValue | negativeUniPolarClamping | negativeUniPolarClamping | Boolean | FALSE | etx | True = positive values will be forced (clamped) to zero before updating into the database. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Negative Uni-Polar Clamping
CIMMeas | AnalogValue | AnalogValue | peakData | peakData | Boolean | FALSE | etx | When set to true, this flag specifies that the Peak Data Processing task will sample this analog. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Peak Data
CIMMeas | AnalogValue | AnalogValue | positiveUniPolarClamping | positiveUniPolarClamping | Boolean | FALSE | etx | TRUE = negative values will be forced (clamped) to zero before updating into the database. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Positive Uni-Polar Clamping
CIMMeas | AnalogValue | AnalogValue | requireEXECUTEStep | requireEXECUTEStep | Boolean | FALSE | etx | True = a supervisory control action is not initiated when a control action is received, and must wait for an additional EXECUTE action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Require EXECUTE Step
CIMMeas | AnalogValue | AnalogValue | requireSELECTStep | requireSELECTStep | Boolean | FALSE | etx | TRUE = a separate SELECT action is required before a supervisory control action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Require SELECT Step
CIMMeas | AnalogValue | AnalogValue | returnToNormalAlarmDelayTime | returnToNormalAlarmDelayTime | Integer |  | etx | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the normal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Return to Normal Alarm Delay Time
CIMMeas | AnalogValue | AnalogValue | seDeadband | seDeadband | Float |  | etx | Display values of good quality which are different than a good quality state-estimated value by more than this amount are considered anomalous, and automatically substituted with the state-estimated value, if the global Automatic State-Estimator Replacement function is enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | SE Deadband
CIMMeas | AnalogValue | AnalogValue | skipLimitChecking | skipLimitChecking | Boolean | FALSE | etx | When set to true, this flag specifies disable reasonability limit checking for this analog. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Skip Limit Checking
CIMMeas | AnalogValue | AnalogValue | timeDelay | timeDelay | Integer |  | etx | The number of seconds after the control request is successfully issued before sending a demand scan request to the associated RTU. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Time Delay
CIMMeas | AnalogValue | AnalogValue | value | value | Float |  | cim | Value of measurement. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value
CIMMeas | AnalogValue | AnalogValue | zeroClampingDeadband | zeroClampingDeadband | Float |  | etx | If value is greater than zero, then any value between zero and the entered value will be forced (clamped) to zero for update into the database. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Zero Clamping Deadband
CIMMeas | Command | Command | normalValue | normalValue | Integer |  | cim | Normal value for Control.value e.g. used for percentage scaling. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Normal Value
CIMMeas | Command | Command | value | value | Integer |  | cim | The value representing the actuator output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value
CIMMeas | Control | Control | operationInProgress | operationInProgress | Boolean | FALSE | cim | Indicates that a client is currently sending control commands that has not completed. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Operation In Progress
CIMMeas | Control | Control | timeStamp | timeStamp | AbsoluteDateTime |  | cim | The last time a control output was sent. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time Stamp
CIMMeas | Discrete | Discrete | maxValue | maxValue | Integer |  | cim | Normal value range maximum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Value
CIMMeas | Discrete | Discrete | minValue | minValue | Integer |  | cim | Normal value range minimum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Value
CIMMeas | Discrete | Discrete | normalValue | normalValue | Integer |  | cim | Normal measurement value, e.g., used for percentage calculations. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Normal Value
CIMMeas | Discrete | Discrete | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
CIMMeas | DiscreteValue | DiscreteValue | abnormalAlarmDelayTime | abnormalAlarmDelayTime | Integer |  | etx | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the abnormal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Abnormal Alarm Delay Time
CIMMeas | DiscreteValue | DiscreteValue | allowControlFromForeignSites | allowControlFromForeignSites | Boolean | FALSE | etx | True = Another site may issue a control on this point. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Allow Control from Foreign Sites
CIMMeas | DiscreteValue | DiscreteValue | allowMultipleRaiseOrLower | allowMultipleRaiseOrLower | Boolean | FALSE | etx | True = Multiple Tap Raise and Lower commands may be issued consecutively without re-selecting the... | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Allow Multiple Raise or Lower
CIMMeas | DiscreteValue | DiscreteValue | allowSELECTStep | allowSELECTStep | Boolean | FALSE | etx | TRUE = a separate SELECT action is allowed (but not required) prior to the supervisory control action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Allow SELECT Step
CIMMeas | DiscreteValue | DiscreteValue | autoAckAndDeleteAlarms | autoAckAndDeleteAlarms | Boolean | FALSE | etx | True = Automatically acknowledge and delete alarms if the Point is manually entered or successfully controlled by the operator to a normal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Auto Ack and Delete Alarms
CIMMeas | DiscreteValue | DiscreteValue | autoAcknowledge | autoAcknowledge | Boolean | FALSE | etx | True = alarms will be automatically acknowledged on return to normal. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Auto Acknowledge
CIMMeas | DiscreteValue | DiscreteValue | controlDemandScan | controlDemandScan | Boolean | FALSE | etx | True = Issues a demand scan request to the RTU at a configurable number of seconds after any successful control requests are issued. This feature is primarily used by measurements with a slow scan rate to provide more timely feedback on the success or failure of the control operation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Control Demand Scan
CIMMeas | DiscreteValue | DiscreteValue | feedbackAnalog | feedbackAnalog | String4 |  | etx | True = The Analog Name which is configured to provide feedback of the associated analog value for control completion checks of Raise/Lower supervisory controls. The chosen Analog must be modeled under the same Device as the controlling Point record. This field is optional. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Feedback Analog
CIMMeas | DiscreteValue | DiscreteValue | invertExtStatusViaISD | invertExtendedStatusViaISD | Boolean | FALSE | etx | True = The extended status bit (XIS) will be inverted when received from the primary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Extended Status via ISD
CIMMeas | DiscreteValue | DiscreteValue | invertExtStatusViaSecSite | invertExtendedStatusViaSecSite | Boolean | FALSE | etx | True = The extended status bit (XIS) will be inverted when received from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Extended Status Via Sec Site
CIMMeas | DiscreteValue | DiscreteValue | invertStatus | invertStatus | Boolean | FALSE | etx | True = The status point value, as received by SCADA, is inverted before using in other applications. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Status
CIMMeas | DiscreteValue | DiscreteValue | invertStatusBitRcvdViaISD | invertStatusBitReceivedViaISD | Boolean | FALSE | etx | True = The status bit (SIS) will be inverted when received from the primary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Status Bit Received Via ISD
CIMMeas | DiscreteValue | DiscreteValue | invertStatusBitRcvdVia2Site | invertStatusBitReceivedViaSecSite | Boolean | FALSE | etx | True = The status bit (SIS) will be inverted when received from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Status Bit Received Via Sec Site
CIMMeas | DiscreteValue | DiscreteValue | logForControlIssued | logForControlIssued | Boolean | FALSE | etx | True = Controls issued on this point will be logged in the system activity log. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Log for Control Issued
CIMMeas | DiscreteValue | DiscreteValue | momentaryChangeDetection | momentaryChangeDetection | Boolean | FALSE | etx | True = a momentary change detection status will be returned. Momentary change detection status informs the computer of changes that occur between scans. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Momentary Change Detection
CIMMeas | DiscreteValue | DiscreteValue | noISDDownload | noISDDownload | Boolean | FALSE | etx | True = Even though the Point is associated with a remote site, the Point will not be included in the Intersite Data download request for status values to the remote site. The remote site is only used for determining which site to send Supervisory Controls to. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | No ISD Download
CIMMeas | DiscreteValue | DiscreteValue | noWarningIfHanging | noWarningIfHanging | Boolean | FALSE | etx | Don't issue warning message if a lone Topology Node is defined, which is not defined on any other record within the Substation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | No Warning if Hanging
CIMMeas | DiscreteValue | DiscreteValue | requireEXECUTEStep | requireEXECUTEStep | Boolean | FALSE | etx | True = a supervisory control action is not initiated when a control action is received, and must wait for an additional EXECUTE action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Require EXECUTE Step
CIMMeas | DiscreteValue | DiscreteValue | requireSELECTStep | requireSELECTStep | Boolean | FALSE | etx | TRUE = a separate SELECT action is required before a supervisory control action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Require SELECT Step
CIMMeas | DiscreteValue | DiscreteValue | returnToNormalAlarmDelayTime | returnToNormalAlarmDelayTime | Integer |  | etx | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the normal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Return to Normal Alarm Delay Time
CIMMeas | DiscreteValue | DiscreteValue | statusBitLiveIndication | statusBitLiveIndication | Boolean | FALSE | etx | T = S bit true indicates LIVE, false indicates DEAD; F = S bit true indicates DEAD, false indicates LIVE. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | status Bit Live Indication
CIMMeas | DiscreteValue | DiscreteValue | tapChangerTimeout | tapChangerTimeout | Integer |  | etx | The timeout between steps of a multiple raise/lower supervisory control sequence for a tap changer. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Tap Changer Timeout
CIMMeas | DiscreteValue | DiscreteValue | threeState | threeState | Boolean | FALSE | etx | True = A three-state point is modeled. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Three State
CIMMeas | DiscreteValue | DiscreteValue | timeDelay | timeDelay | Integer |  | etx | Demand Scan After Control is configured for this point, enter the number of seconds after the control request is successfully issued before sending a demand scan request to the associated RTU. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Time Delay
CIMMeas | DiscreteValue | DiscreteValue | value | value | Integer |  | cim | Value of measurement. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value
CIMMeas | LimitSet | LimitSet | forNetwork | forNetwork | Bool | FALSE | etx | If true then this measurement is only for network monitoring. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | for Network
CIMMeas | LimitSet | LimitSet | isPercentageLimits | isPercentageLimits | Boolean | FALSE | cim | Tells if the limit values are in percentage of normalValue or the specified Unit for Measurements and Controls. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Is Percentage Limits
CIMMeas | LimitSet | LimitSet | type | type | EnumLimitSetType |  | etx | Type. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Type
CIMMeas | LimitSet | LimitSet | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temporary attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
CIMMeas | Measurement | Measurement | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temp Attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Zonal Attribute
CIMMeas | MeasurementValue | MeasurementValue | abnormalForAlarm | abnormalForAlarm | Boolean | FALSE | etx | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Abnormal For Alarm
CIMMeas | MeasurementValue | MeasurementValue | abnormalForSCADA | abnormalForSCADA | Boolean | FALSE | etx | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Abnormal For SCADA
CIMMeas | MeasurementValue | MeasurementValue | audibleTone | audibleTone | Boolean | FALSE | etx | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Audible Tone
CIMMeas | MeasurementValue | MeasurementValue | blockViaPrimarySite | blockViaPrimarySite | Boolean | FALSE | etx | Block Value and Quality update via Primary Site: Do not allow update from the primary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Block via Primary Site
CIMMeas | MeasurementValue | MeasurementValue | blockViaSecondarySite | blockViaSecondarySite | Boolean | FALSE | etx | Block Value and Quality update via Secondary Site: Do not allow update from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Block via Secondary Site
CIMMeas | MeasurementValue | MeasurementValue | byPass | byPass | Boolean | FALSE | etx | When set to true, this flag specifies allowing bypass entry of Suspect values if telemetered from a remote site or SCADA Front End. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | byPass
CIMMeas | MeasurementValue | MeasurementValue | cstatus | cstatus | Boolean | FALSE | etx | True when value represents status of communication path component. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Component Status
CIMMeas | MeasurementValue | MeasurementValue | dataSetPeriod | dataSetPeriod | Integer |  | etx | ICCP data set period used for the measurement. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ICCP Data Set Period
CIMMeas | MeasurementValue | MeasurementValue | fromCalculation | fromCalculation | Boolean | FALSE | etx | Value is from calculation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | from Calculation
CIMMeas | MeasurementValue | MeasurementValue | fromExternalProgram | fromExternalProgram | Boolean | FALSE | etx | When set to true, this flag specifies the source of the data is an external program. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | From External Program
CIMMeas | MeasurementValue | MeasurementValue | fromManualEntry | fromManualEntry | Boolean | FALSE | etx | Value is from manual entry. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | from Manual Entry
CIMMeas | MeasurementValue | MeasurementValue | fromRemote | fromRemote | Boolean | FALSE | etx | Value is from remote. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | from Remote
CIMMeas | MeasurementValue | MeasurementValue | habcName | habcName | String60 |  | etx | Connection ID of value using HABConnect. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | HABC Name
CIMMeas | MeasurementValue | MeasurementValue | iccpVmd | iccpVmd | Boolean | FALSE | etx | True when value has VMD scope. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | VMD Scope
CIMMeas | MeasurementValue | MeasurementValue | inhibitAbnormalForAlarm | inhibitAbnormalForAlarm | Boolean | FALSE | etx | Permanently Inhibit the flag of abnormalForAlarm. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Abnormal For Alarm
CIMMeas | MeasurementValue | MeasurementValue | inhibitAbnormalForSCADA | inhibitAbnormalForSCADA | Boolean | FALSE | etx | Permanently Inhibit the flag of abnormalForSCADA. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Abnormal For SCADA
CIMMeas | MeasurementValue | MeasurementValue | inhibitAudibleTone | inhibitAudibleTone | Boolean | FALSE | etx | Permanently Inhibit the flag of audibleTone. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Audible Tone
CIMMeas | MeasurementValue | MeasurementValue | inhibitLoggingAndAlarmList | inhibitLoggingAndAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Logging and Alarm List
CIMMeas | MeasurementValue | MeasurementValue | inhibitUnackAlarmList | inhibitUnacknowledgedAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Unacknowledged Alarm List
CIMMeas | MeasurementValue | MeasurementValue | initiallyInhibit | initiallyInhibit | Boolean | FALSE | etx | A flag indicating that when the system first comes online, alarm indications for this SCADA entry will initially be inhibited. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Initially Inhibit
CIMMeas | MeasurementValue | MeasurementValue | isdName | isdName | String60 |  | etx | Dollar-separacted SCADA Composite ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ISD Name
CIMMeas | MeasurementValue | MeasurementValue | loggingAndAlarmList | loggingAndAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Logging and Alarm List
CIMMeas | MeasurementValue | MeasurementValue | mappedInOag | mappedInOag | Boolean | FALSE | etx | T = This data-point is also represented in the OAG model as a data item (designated member of a data packet). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Mapped In OAG
CIMMeas | MeasurementValue | MeasurementValue | notInService | notInService | Boolean | FALSE | etx | flag indicating not in service. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Not In Service
CIMMeas | MeasurementValue | MeasurementValue | overrideDefaultnhibitDef | overrideDefaultInhibitDefinition | Boolean | FALSE | etx | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Override Default Inhibit Definition
CIMMeas | MeasurementValue | MeasurementValue | recordHistoricalData | recordHistoricalData | Boolean | FALSE | etx | When set to true, this flag specifies that state changes on the analog are recorded in the historical data review file. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Record Historical Data
CIMMeas | MeasurementValue | MeasurementValue | RsCalculated | RsCalculated | Boolean | FALSE | etx | Remote site normally calculated. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Remote Site Normally Calculated
CIMMeas | MeasurementValue | MeasurementValue | RsExtern | RsExtern | Boolean | FALSE | etx | Remote site normally estimated. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Remote Site Normally Estimated
CIMMeas | MeasurementValue | MeasurementValue | RsManual | RsManual | Boolean | FALSE | etx | Remote site normally manually entered. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Remote Site Normally Manually Entered
CIMMeas | MeasurementValue | MeasurementValue | RsTelemetered | RsTelemetered | Boolean | FALSE | etx | Remote site normally telemetered. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Remote Site Normally Telemetered
CIMMeas | MeasurementValue | MeasurementValue | ScanRate | ScanRate | Integer |  | etx | ICCP scan rate used for the measurement. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Scan Rate
CIMMeas | MeasurementValue | MeasurementValue | sensorAccuracy | sensorAccuracy | PerCent |  | cim | The limit, expressed as a percentage of the sensor maximum, that errors will not exceed when the sensor is used under reference conditions. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Sensor Accuracy
CIMMeas | MeasurementValue | MeasurementValue | tabularDisplayPriority | tabularDisplayPriority | Integer |  | etx | Priority of tabulay display. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Tabular Display Priority
CIMMeas | MeasurementValue | MeasurementValue | timeStamp | timeStamp | AbsoluteDateTime |  | cim | The time when the value was last updated. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time Stamp
CIMMeas | MeasurementValue | MeasurementValue | unacknowledgedAlarmList | unacknowledgedAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Unacknowledged Alarm List
CIMMeas | MeasurementValue | MeasurementValue | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temp Attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
CIMMeas | MeasurementValueQuality | MeasurementValueQuality | hasCOV | hasCOV | Boolean | FALSE | etx | Whether or not ICCP item has Change of Value modifier. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | has COV
CIMMeas | MeasurementValueQuality | MeasurementValueQuality | hasQuality | hasQuality | Boolean | FALSE | etx | Whether or not ICCP item has Quality modifier. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | has Quality
CIMMeas | MeasurementValueQuality | MeasurementValueQuality | hasTimestamp | hasTimestamp | Boolean | FALSE | etx | Whether or not ICCP item has Timestamp modifier. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | has Timestamp
CIMMeas | MeasurementValueQuality | MeasurementValueQuality | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temporary attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
CIMMeas | MeasurementValueSource | MeasurementValueSource | biverAus | biverAus | String32 |  | etx | Bilateral Table Version for ICCP connection from Austin. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Austin - Bilateral Table Version
CIMMeas | MeasurementValueSource | MeasurementValueSource | biverTay | biverTay | String32 |  | etx | Bilateral Table Version for ICCP connection from Taylor. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Taylor - Bilateral Table Version
CIMMeas | MeasurementValueSource | MeasurementValueSource | BufferTime | BufferTime | Integer |  | etx | Buffer time to apply to datasets created for this remote. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Buffer Time
CIMMeas | MeasurementValueSource | MeasurementValueSource | defaultDataSetPeriod | defaultDataSetPeriod | Integer | 10 | etx | ICCP data set period used for the measurement(seconds). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ICCP Default Data Set Period
CIMMeas | MeasurementValueSource | MeasurementValueSource | GraceTime | GraceTime | Integer |  | etx | Grace time to apply to datasets created for this remote. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Grace Time
CIMMeas | MeasurementValueSource | MeasurementValueSource | iccpDomainAus | iccpDomainAus | String32 |  | etx | Remote Domain name for ICCP connection from Austin. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Austin - Remote Domain
CIMMeas | MeasurementValueSource | MeasurementValueSource | iccpDomainTay | iccpDomainTay | String32 |  | etx | Remote Domain name for ICCP connection from Taylor. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Taylor - Remote Domain
CIMMeas | MeasurementValueSource | MeasurementValueSource | IntegrityPeriod | IntegrityPeriod | Integer |  | etx | Integrity time to apply to datasets created for this remote. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ICCP Integrity Period
CIMMeas | MeasurementValueSource | MeasurementValueSource | lnkapp | lnkapp | String8 |  | etx | ICCPLINK' for ICCP remote sites. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Link App
CIMMeas | MeasurementValueSource | MeasurementValueSource | MaxDisPerDataset | MaxDisPerDataset | Integer |  | etx | Maximun number of dataitems to put in datasets for this remote. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Dataitems per Dataset
CIMMeas | MeasurementValueSource | MeasurementValueSource | maxScanRate | maxScanRate | Integer |  | etx | Minimum seconds between scan requests. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Scan Rate
CIMMeas | MeasurementValueSource | MeasurementValueSource | notInService | notInService | Boolean | FALSE | etx | false if REMOTE is ready for data exchange. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Not In Service?
CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool1 | pbool1 | Boolean | FALSE | etx | Protocol-Specific Flag 1. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 1
CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool2 | pbool2 | Boolean | FALSE | etx | Protocol-Specific Flag 2. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 2
CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool3 | pbool3 | Boolean | FALSE | etx | Protocol-Specific Flag 3. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 3
CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool4 | pbool4 | Boolean | FALSE | etx | Protocol-Specific Flag 4. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 4
CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool5 | pbool5 | Boolean | FALSE | etx | Protocol-Specific Flag 5. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 5
CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool6 | pbool6 | Boolean | FALSE | etx | Protocol-Specific Flag 6. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 6
CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool7 | pbool7 | Boolean | FALSE | etx | Protocol-Specific Flag 7. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 7
CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool8 | pbool8 | Boolean | FALSE | etx | Protocol-Specific Flag 8. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 8
CIMMeas | MeasurementValueSource | MeasurementValueSource | protocolVersion | protocolVersion | Integer |  | etx | Version of ICCP protocol used (2000 or 1996). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Protocol Version
CIMMeas | MeasurementValueSource | MeasurementValueSource | remoteIdAus | remoteIdAus | String16 |  | etx | Name of remote site for connection from Austin. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Austin - Remote Id
CIMMeas | MeasurementValueSource | MeasurementValueSource | remoteIdTay | remoteIdTay | String16 |  | etx | Name of remote site for connection from Taylor. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Taylor - Remote Id
CIMMeas | MeasurementValueSource | MeasurementValueSource | savecaseType | savecaseType | EnumSavecaseType |  | etx | To be set by an ERCOT Modeling Engineer. This value indicates the type of the remote site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | savecaseType
CIMMeas | MeasurementValueSource | MeasurementValueSource | trsfr | trsfr | Integer |  | etx | Protocol-specific value. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol Specific Value
CIMMeas | MeasurementValueSource | MeasurementValueSource | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temp Attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
CIMMeas | Quality61850 | Quality61850 | badReference | badReference | Boolean | FALSE | cim | Measurement value may be incorrect due to a reference being out of calibration. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Bad Reference
CIMMeas | Quality61850 | Quality61850 | estimatorReplaced | estimatorReplaced | Boolean | FALSE | cim | Value has been replaced by State Estimator. estimatorReplaced is not an IEC61850 quality bit but has been put in this class for convenience. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Estimator Replaced
CIMMeas | Quality61850 | Quality61850 | failure | failure | Boolean | FALSE | cim | This identifier indicates that a supervision function has detected an internal or external failure, e.g. communication failure. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Failure
CIMMeas | Quality61850 | Quality61850 | oldData | oldData | Boolean | FALSE | cim | Measurement value is old and possibly invalid, as it has not been successfully updated during a specified time interval. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Old Data
CIMMeas | Quality61850 | Quality61850 | operatorBlocked | operatorBlocked | Boolean | FALSE | cim | Measurement value is blocked and hence unavailable for transmission. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Operator Blocked
CIMMeas | Quality61850 | Quality61850 | oscillatory | oscillatory | Boolean | FALSE | cim | To prevent some overload of the communication it is sensible to detect and suppress oscillating (fast changing) binary inputs. If a signal changes in a defined time (tosc) twice in the same direction (from 0 to 1 or from 1 to 0) then oscillation is detected and the detail quality identifier 'oscillatory' is set. If it is detected a configured numbers of transient changes could be passed by. In this time the validity status 'questionable' is set. If after this defined numbers of changes the signal is still in the oscillating state the value shall be set either to the opposite state of the previous stable value or to a defined default value. In this case the validity status 'questionable' is reset and 'invalid' is set as long as the signal is oscillating. If it is configured such that no transient changes should be passed by then the validity status 'invalid' is set immediately in addition to the detail quality identifier 'oscillatory' (used for status information only). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Oscillatory
CIMMeas | Quality61850 | Quality61850 | outOfRange | outOfRange | Boolean | FALSE | cim | Measurement value is beyond a predefined range of value. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Out of Range
CIMMeas | Quality61850 | Quality61850 | overFlow | overFlow | Boolean | FALSE | cim | Measurement value is beyond the capability of being represented properly. For example, a counter value overflows from maximum count back to a value of zero. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Flow
CIMMeas | Quality61850 | Quality61850 | source | source | EnumSource | 0 | cim | Source gives information related to the origin of a value. The value may be acquired from the process, defaulted or substituted. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Source
CIMMeas | Quality61850 | Quality61850 | suspect | suspect | Boolean | FALSE | cim | A correlation function has detected that the value is not consitent with other values. Typically set by a network State Estimator. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Suspect
CIMMeas | Quality61850 | Quality61850 | test | test | Boolean | FALSE | cim | Measurement value is transmitted for test purposes. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Test
CIMMeas | Quality61850 | Quality61850 | validity | validity | EnumValidity | 0 | cim | Validity may be good, questionable or invalid. Refer to the Validity enumeration for more details. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Validity
CIMMeas | SetPoint | SetPoint | allowControlFromForeignSites | allowControlFromForeignSites | Boolean | FALSE | etx | CONTROLLED AT REMOTE SITE: T = Another site may issue this setpoint. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Allow Control From Foreign Sites
CIMMeas | SetPoint | SetPoint | audibleTone | audibleTone | Boolean | FALSE | etx | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | audible Tone
CIMMeas | SetPoint | SetPoint | deadBand | deadBand | Float |  | etx | SETPOINT ANALOG DEADBAND (STATIC). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Deadband
CIMMeas | SetPoint | SetPoint | inhibitAudibleTone | inhibitAudibleTone | Boolean | FALSE | etx | Permanently Inhibit the flag of audibleTone. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | inhibit Audible Tone
CIMMeas | SetPoint | SetPoint | inhibitLoggingAndAlarmList | inhibitLoggingAndAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | inhibit Logging And Alarm List
CIMMeas | SetPoint | SetPoint | inhibitUnackAlarmList | inhibitUnacknowledgedAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | inhibit Unacknowledged Alarm List
CIMMeas | SetPoint | SetPoint | initiallyInhibit | initiallyInhibit | Boolean | FALSE | etx | A flag indicating that when the system first comes online, alarm indications for this SCADA entry will initially be inhibited. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | initially Inhibit
CIMMeas | SetPoint | SetPoint | loggingAndAlarmList | loggingAndAlarmList | Boolean | FALSE | etx | A flag indicating that SCADA will issue neither an alarm nor an event. Therefore, entries will appear in the neither the alarm list nor the event logs. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | logging And Alarm List
CIMMeas | SetPoint | SetPoint | maxValue | maxValue | Float |  | cim | Normal value range maximum for any of the Control.value. Used for scaling, e.g. in bar graphs. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Value
CIMMeas | SetPoint | SetPoint | minValue | minValue | Float |  | cim | Normal value range minimum for any of the Control.value. Used for scaling, e.g. in bar graphs. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Value
CIMMeas | SetPoint | SetPoint | noLog | noLog | Boolean | FALSE | etx | T = Setpoints issued on this analog are not logged. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | No Log
CIMMeas | SetPoint | SetPoint | normalValue | normalValue | Float |  | cim | Normal value for Control.value e.g. used for percentage scaling. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Normal Value
CIMMeas | SetPoint | SetPoint | notInService | notInService | Boolean | FALSE | etx | Amount by which the analog value may vaFloat. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Not In Service
CIMMeas | SetPoint | SetPoint | overrideDefaultInhibitDef | overrideDefaultInhibitDefinition | Boolean | FALSE | etx | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | override Default Inhibit Definition
CIMMeas | SetPoint | SetPoint | timeOut | timeOut | Integer |  | etx | DEVICE OPERATION TIME LIMIT - This value indicates the device operation time limit in seconds. If the setpoint request was successfully transmitted to the RTU and the associated analog does not show that the device moved to the required value within this period, the setpoint operation is considered failed. A zero indicates an indefinite operation time limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Time Out
CIMMeas | SetPoint | SetPoint | unackAlarmList | unacknowledgedAlarmList | Boolean | FALSE | etx | A flag indicating that SCADA will issue an event to the event log, but will not issue unacknowledged alarm indications to the alarm list. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | unacknowledged Alarm List
CIMMeas | SetPoint | SetPoint | value | value | Float |  | cim | The value representing the actuator output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value
CIMMeas | SetPoint | SetPoint | waitTime | waitTime | Integer |  | etx | Wait time. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Wait Time
CIMMeas | SetPoint | SetPoint | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temporary attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
CIMMeas | StringMeasurementValue | StringMeasurementValue | value | value | String100 |  | cim | Value of measurement. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value
CIMMeas | ValueToAlias | ValueToAlias | value | value | Integer |  | cim | The value that is mapped. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value
CIMOutage | ClearanceTag | ClearanceTag | authorityName | authorityName | String100 |  | cim | The name of the person who is authorized to issue the tag. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Authority Name
CIMOutage | ClearanceTag | ClearanceTag | clearanceTagType | clearanceTagType | EnumClearanceTagType |  | cim | The type of tag, depending on the purpose of the work to be performed and/or the type of supervisory control allowed. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Clearance Tag Type
CIMOutage | ClearanceTag | ClearanceTag | deenergizeReqFlag | deenergizeReqFlag | Boolean | FALSE | cim | Flag = YES if equipment must be deenergized. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | De-Energize Req Flag
CIMOutage | ClearanceTag | ClearanceTag | groundReqFlag | groundReqFlag | Boolean | FALSE | cim | Flag = YES if equipment must be grounded. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Ground Req Flag
CIMOutage | ClearanceTag | ClearanceTag | phaseCheckReqFlag | phaseCheckReqFlag | Boolean | FALSE | cim | Flag = YES if equipment phasing must be checked. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phase Check Req Flag
CIMOutage | ClearanceTag | ClearanceTag | tagIssueTime | tagIssueTime | AbsoluteDateTime |  | cim | The time at which the clearance tag was issued. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tag Issue Time
CIMOutage | ClearanceTag | ClearanceTag | workDescription | workDescription | String1000 |  | cim | Description of the work to be performed. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Work Description
CIMOutage | ClearanceTag | ClearanceTag | workEndTime | workEndTime | AbsoluteDateTime |  | cim | The time at which the clearance tag is scheduled to be removed. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Work End Time
CIMOutage | ClearanceTag | ClearanceTag | workStartTime | workStartTime | AbsoluteDateTime |  | cim | WorkStartTime | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Work Start Time
CIMOutage | SwitchingOperation | SwitchingOperation | newState | newState | EnumSwitchState |  | cim | New State. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | New State
CIMOutage | SwitchingOperation | SwitchingOperation | operationTime | operationTime | AbsoluteDateTime |  | cim | Time of operation in same units as OutageSchedule.xAxixUnits. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Operation Time
CIMProduction | AirCompressor | AirCompressor | airCompressorRating | airCompressorRating | Float |  | cim | Rating of the CAES air compressor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Air Compressor Rating
CIMProduction | CAESPlant | CAESPlant | energyStorageCapacity | energyStorageCapacity | EnergyAsMWh |  | cim | The rated energy storage capacity in megawatt-hours. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Energy Storage Capacity
CIMProduction | CAESPlant | CAESPlant | ratedCapacityMW | ratedCapacityMW | ActivePower |  | cim | The CAES plant's gross rated generating capacity in MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Rated Capacity MW
CIMProduction | CogenerationPlant | CogenerationPlant | cogenHPSendoutRating | cogenHPSendoutRating | Float |  | cim | The high pressure steam sendout, in klb/hour | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cogen HPSendout Rating
CIMProduction | CogenerationPlant | CogenerationPlant | cogenHPSteamRating | cogenHPSteamRating | Float |  | cim | The high pressure steam rating, in psi | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cogen HPSteam Rating
CIMProduction | CogenerationPlant | CogenerationPlant | cogenLPSendoutRating | cogenLPSendoutRating | Float |  | cim | The low pressure steam sendout, in klb/hour | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cogen LPSendout Rating
CIMProduction | CogenerationPlant | CogenerationPlant | cogenLPSteamRating | cogenLPSteamRating | Float |  | cim | The low pressure steam rating, in psi | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cogen LPSteam Rating
CIMProduction | CogenerationPlant | CogenerationPlant | cogenPlantMWRating | cogenPlantMWRating | ActivePower |  | cim | The rated output MW of the cogeneration plant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cogen Plant MWRating
CIMProduction | CombinedCyclePlant | CombinedCyclePlant | blockLoadTransfer | blockLoadTransfer | Boolean | FALSE | etx | Block load transfer. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Block Load Transfer
CIMProduction | CombinedCyclePlant | CombinedCyclePlant | combCyclePlantRating | combCyclePlantRating | ActivePower |  | cim | The combined cycle plant's output rating, in MW | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Comb Cycle Plant Rating
CIMProduction | CombinedCyclePlant | CombinedCyclePlant | commercialOperationsDate | commercialOperationsDate | Date |  | etx | Date commercial operations started. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Commercial Operations Date
CIMProduction | CombinedCyclePlant | CombinedCyclePlant | GstTpspiMax | GstTpspiMax | Float |  | etx | GstTpspiMax | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | GstTpspiMax
CIMProduction | CombinedCyclePlant | CombinedCyclePlant | GstTpspiMin | GstTpspiMin | Float |  | etx | GstTpspiMin | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | GstTpspiMin
CIMProduction | CombinedCyclePlant | CombinedCyclePlant | GtMax | GtMax | Float |  | etx | GtMax | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | GtMax
CIMProduction | CombinedCyclePlant | CombinedCyclePlant | GtMin | GtMin | Float |  | etx | GtMin | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | GtMin
CIMProduction | CombinedCyclePlant | CombinedCyclePlant | LogicalResourceNodeName | LogicalResourceNodeName | String12 |  | etx | Logical resource node name. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Logical Resource Node Name
CIMProduction | CombinedCyclePlant | CombinedCyclePlant | qualificationStatus | qualificationStatus | Boolean | FALSE | etx | Qualification status. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Qualification Status
CIMProduction | CombinedCyclePlant | CombinedCyclePlant | resourceCategory | resourceCategory | String50 |  | etx | Type of resource. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Type of Resource
CIMProduction | CombinedCyclePlant | CombinedCyclePlant | wfrmcr | wfrmcr | Boolean | FALSE | etx | wfrmcr. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | wfrmcr
CIMProduction | EmissionAccount | EmissionAccount | emissionType | emissionType | EnumEmissionType |  | cim | The type of emission, for example sulfur dioxide (SO2). The y1AxisUnits of the curve contains the unit of measure (e.g. kg) and the emissionType is the type of emission (e.g. sulfer dioxide). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emission Type
CIMProduction | EmissionAccount | EmissionAccount | emissionValueSource | emissionValueSource | EnumEmissionValueSource |  | cim | The source of the emission value: Measured or Calculated. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emission Value Source
CIMProduction | EmissionCurve | EmissionCurve | emissionContent | emissionContent | Emission |  | cim | The emission content per quantity of fuel burned. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emission Content
CIMProduction | EmissionCurve | EmissionCurve | emissionType | emissionType | EnumEmissionType |  | cim | The type of emission, which also gives the production rate measurement unit. The y1AxisUnits of the curve contains the unit of measure (e.g. kg) and the emissionType is the type of emission (e.g. sulfer dioxide). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emission Type
CIMProduction | EmissionCurve | EmissionCurve | netGrossMWFlag | netGrossMWFlag | Boolean | FALSE | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net Gross MW Flag
CIMProduction | FossilFuel | FossilFuel | fossilFuelType | fossilFuelType | EnumFuelType |  | cim | The type of fossil fuel, such as coal, oil, or gas. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fossil Fuel Type
CIMProduction | FossilFuel | FossilFuel | fuelCost | fuelCost | CostPerHeatUnit |  | cim | The cost in terms of heat value for the given type of fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Cost
CIMProduction | FossilFuel | FossilFuel | fuelDispatchCost | fuelDispatchCost | CostPerHeatUnit |  | cim | The cost of fuel used for economic dispatching which includes: fuel cost, transportation cost, and incremental maintenance cost. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Dispatch Cost
CIMProduction | FossilFuel | FossilFuel | fuelEffFactor | fuelEffFactor | PU |  | cim | The efficiency factor for the fuel (per unit) in terms of the effective MBtu absorbed. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Efficiency Factor
CIMProduction | FossilFuel | FossilFuel | fuelHandlingCosgt | fuelHandlingCosgt | CostPerHeatUnit |  | cim | Handling and processing cost associated with this fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Handling Cost
CIMProduction | FossilFuel | FossilFuel | fuelHeatContent | fuelHeatContent | Float |  | cim | The amount of heat (Btu) per weight (or volume) of the given type of fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Heat Content
CIMProduction | FossilFuel | FossilFuel | fuelMixture | fuelMixture | PerCent |  | cim | The amount in percent of the given type of fuel , when multiple fuels are being consumed. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Mixture
CIMProduction | FossilFuel | FossilFuel | fuelSulfur | fuelSulfur | PU |  | cim | The fuel's fraction of pollution credit per unit of heat content (MBtu). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Sulfur
CIMProduction | FossilFuel | FossilFuel | highMWBreakpoint | highMWBreakpoint | ActivePower |  | cim | The MW output level of the unit at which the given type of fuel is switched on. This fuel (e.g., oil) is sometimes used to supplement the base fuel (e.g., coal) at high MW output levels. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | High MW Breakpoint
CIMProduction | FossilFuel | FossilFuel | lowMWBreakpoint | lowMWBreakpoint | ActivePower |  | cim | The MW output level of the unit at which the given type of fuel is switched off. This fuel (e.g., oil) is sometimes used to stabilize the base fuel (e.g., coal) at low MW output levels. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Low MW Breakpoint
CIMProduction | FuelAllocationSchedule | FuelAllocationSchedule | fuelAllocationEndDate | fuelAllocationEndDate | AbsoluteDateTime |  | cim | The end time and date of the fuel allocation schedule. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Allocation End Date
CIMProduction | FuelAllocationSchedule | FuelAllocationSchedule | fuelAllocationStartDate | fuelAllocationStartDate | AbsoluteDateTime |  | cim | The start time and date of the fuel allocation schedule. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Allocation Start Date
CIMProduction | FuelAllocationSchedule | FuelAllocationSchedule | fuelType | fuelType | EnumFuelType |  | cim | The type of fuel, which also indicates the corresponding measurement unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Type
CIMProduction | FuelAllocationSchedule | FuelAllocationSchedule | maxFuelAllocation | maxFuelAllocation | Float |  | cim | The maximum amount fuel that is allocated for consumption for the scheduled time period. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Fuel Allocation
CIMProduction | FuelAllocationSchedule | FuelAllocationSchedule | minFuelAllocation | minFuelAllocation | Float |  | cim | The minimum amount fuel that is allocated for consumption for the scheduled time period, e.g., based on a 'take-or-pay' contract. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Fuel Allocation
CIMProduction | GeneratingUnit | GeneratingUnit | allocSpinResMW | allocSpinResMW | ActivePower |  | cim | The planned unused capacity (spinning reserve) which can be used to support emergency load. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Alloc Spin Res MW
CIMProduction | GeneratingUnit | GeneratingUnit | autoCntrlMarginMW | autoCntrlMarginMW | ActivePower |  | cim | The planned unused capacity which can be used to support automatic control overruns, in MW. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Auto Control Margin MW
CIMProduction | GeneratingUnit | GeneratingUnit | baseMW | baseMW | ActivePower |  | cim | For dispatchable units, this value represents the economic MW basepoint, for units that are not dispatchable, this value represents the fixed generation value. The value must be between the operating low and high limits. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Base MW
CIMProduction | GeneratingUnit | GeneratingUnit | blackStart | blackStart | Bool | FALSE | etx | TRUE - Unit is qualified to black start. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Black Start
CIMProduction | GeneratingUnit | GeneratingUnit | blockLoadTransfer | blockLoadTransfer | Boolean | FALSE | etx | Block load transfer. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Block Load Transfer
CIMProduction | GeneratingUnit | GeneratingUnit | coldStartTime | coldStartTime | Float |  | etx | Cold start time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Cold start time
CIMProduction | GeneratingUnit | GeneratingUnit | commercialOperationsDate | commercialOperationsDate | Date |  | etx | Commericial operations date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Commercial Operations Date
CIMProduction | GeneratingUnit | GeneratingUnit | controlDeadband | controlDeadband | ActivePower |  | cim | Unit control error deadband. When a unit's desired MW change is less than this deadband, then no control pulses will be sent to the unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Deadband
CIMProduction | GeneratingUnit | GeneratingUnit | ControlPulseHigh | controlPulseHigh | Seconds | 0.5 | cim | Pulse high limit which is the largest control pulse that the unit can respond to. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Control Pulse High
CIMProduction | GeneratingUnit | GeneratingUnit | ControlPulseLow | controlPulseLow | Seconds | 0.5 | cim | Pulse low limit which is the smallest control pulse that the unit can respond to. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Control Pulse Low
CIMProduction | GeneratingUnit | GeneratingUnit | controlResponseRate | controlResponseRate | PowerROCPerSec | 2 | cim | MW change for a control pulse of one second in the most responsive loading level of the unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Control Response Rate
CIMProduction | GeneratingUnit | GeneratingUnit | dispReserveFlag | dispReserveFlag | Boolean | FALSE | cim | Display Reserve Flag | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Disp Reserve Flag
CIMProduction | GeneratingUnit | GeneratingUnit | Efficiency | efficiency | PU | 1 | cim | The efficiency of the unit in converting mechanical energy, from the prime mover, into electrical energy. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE | 1.2 | 0.001 | Efficiency
CIMProduction | GeneratingUnit | GeneratingUnit | energyMinMW | energyMinMW | HeatPerHour |  | cim | Energy Minimum MW. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Energy Min MW
CIMProduction | GeneratingUnit | GeneratingUnit | fastStartFlag | fastStartFlag | Boolean | FALSE | cim | Fast Start Flag. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Fast Start Flag
CIMProduction | GeneratingUnit | GeneratingUnit | freqBias | freqBias | Float |  | etx | Unit Regulating Frequency Bias as MW per 0.1 Hz. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Frequency Bias
CIMProduction | GeneratingUnit | GeneratingUnit | freqDevDeadband | freqDevDeadband | Float |  | etx | Frequency deviation deadband for Feed-Forward correction. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Frequencey Deviation Deadband
CIMProduction | GeneratingUnit | GeneratingUnit | frequencyDeadBandHz | frequencyDeadBandHz | Float |  | etx | Allowable deviation of the unit frequency. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Deadband HZ
CIMProduction | GeneratingUnit | GeneratingUnit | fuelPriority | fuelPriority | Priority |  | cim | Fuel Priority. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Priority
CIMProduction | GeneratingUnit | GeneratingUnit | genControlMode | genControlMode | EnumGeneratorControlMode |  | cim | Select the unit control mode as Setpoint (S) or Pulse (P). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Generator Control Mode
CIMProduction | GeneratingUnit | GeneratingUnit | genControlSource | genControlSource | EnumGeneratorControlSource |  | cim | The source of controls for a generating unit, i.e., Unavailable, Off-AGC, On-AGC, Plant Control. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Gen Control Source
CIMProduction | GeneratingUnit | GeneratingUnit | OperatingMode | genOperatingMode | EnumGeneratorOperatingMode | 0 | cim | Operating mode for secondary control, e.g.: Off, Manual, Fixed, LFC, AGC, EDC, RPN, MRN, or REG. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Generator Operating Mode
CIMProduction | GeneratingUnit | GeneratingUnit | GovernorMPL | governorMPL | PU | 1 | cim | Governor motor position limit. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Governor MPL
CIMProduction | GeneratingUnit | GeneratingUnit | GovernorSCD | governorSCD | PerCent | 5 | cim | Governor Speed Changer Droop. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Governor Speed Changer Droop
CIMProduction | GeneratingUnit | GeneratingUnit | highControlLimit | highControlLimit | ActivePower |  | cim | High limit for secondary (AGC) control. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | High Control Limit
CIMProduction | GeneratingUnit | GeneratingUnit | highReasonabilityLimit | highReasonabilityLimit | ActivePower |  | etx | High reasonability limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | High Reasonability Limit
CIMProduction | GeneratingUnit | GeneratingUnit | highRsnbltyRampRateLimit | highReasonabilityRampRateLimit | ActivePower |  | etx | High reasonability ramp rate limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | High Reasonability Ramp Rate Limit
CIMProduction | GeneratingUnit | GeneratingUnit | hotintTime | hotintTime | Float |  | etx | Hot-to-intermediate time (Seasonal). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Hot-to-intermediate time (Seasonal)
CIMProduction | GeneratingUnit | GeneratingUnit | hotStartTime | hotStartTime | Float |  | etx | Hot start time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Hot start time
CIMProduction | GeneratingUnit | GeneratingUnit | initialMW | initialMW | ActivePower |  | cim | Default generation for use when the operating type is fixed. An entry is required because the unit may later be placed in a fixed operating type mode even though that may not be the initial selection. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Initial MW
CIMProduction | GeneratingUnit | GeneratingUnit | intColdTime | intColdTime | Float |  | etx | Intermediate-to-cold time (Seasonal). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Intermediate-to-cold time (Seasonal)
CIMProduction | GeneratingUnit | GeneratingUnit | intStartTime | intStartTime | Float |  | etx | Intermediate start time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Intermediate start time
CIMProduction | GeneratingUnit | GeneratingUnit | longPF | longPF | ParticipationFactor |  | cim | Additional information is not available. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Long PF
CIMProduction | GeneratingUnit | GeneratingUnit | lowControlLimit | lowControlLimit | ActivePower |  | cim | Low limit for secondary (AGC) control. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Low Control Limit
CIMProduction | GeneratingUnit | GeneratingUnit | lowerRampRate | lowerRampRate | PowerROCPerMin |  | cim | Lower Ramp Rate. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Lower Ramp Rate
CIMProduction | GeneratingUnit | GeneratingUnit | lowReasonabilityLimit | lowReasonabilityLimit | ActivePower |  | etx | Low reasonability limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Low Reasonability Limit
CIMProduction | GeneratingUnit | GeneratingUnit | lowRsnbltyRampRateLimit | lowReasonabilityRampRateLimit | ActivePower |  | etx | Low reasonability ramp rate limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Low Reasonability Ramp Rate Limit
CIMProduction | GeneratingUnit | GeneratingUnit | maxCapacityLimit | maxCapacityLimit | Integer |  | etx | MAXIMUM POSSIBLE CAPACITY. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Capacity Limit
CIMProduction | GeneratingUnit | GeneratingUnit | maxDailyStarts | maxDailyStarts | Float |  | etx | Maximum daily starts (seasonal parameter). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum daily starts (seasonal parameter)
CIMProduction | GeneratingUnit | GeneratingUnit | maxDownRampRate | maxDownRampRate | Float |  | etx | DEFAULT MAXIMUM RAMP RATE IN DOWN DIRECTION. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Down Ramp Rate
CIMProduction | GeneratingUnit | GeneratingUnit | maxAllowableSpinngReserve | maximumAllowableSpinngReserve | ActivePower |  | cim | Maximum allowable spinning reserve. Spinning reserve will never be considered greater than this value regardless of the current operating point. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Allowable Spinning Reserve
CIMProduction | GeneratingUnit | GeneratingUnit | maximumCurrentCapacity | maximumCurrentCapacity | Float |  | etx | (MW) DEFAULT CURRENT MAX CAPACITY. OPERATOR ENTERABLE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Current Capacity
CIMProduction | GeneratingUnit | GeneratingUnit | maximumCurrentCapacityRef | maximumCurrentCapacityRef | Float |  | etx | (MW) Reference value for Advisory ECO maximum. Entered in modeling. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Current Capacity Ref
CIMProduction | GeneratingUnit | GeneratingUnit | MaximumEconomicMW | maximumEconomicMW | ActivePower |  | cim | Maximum high economic MW limit, that should not exceed the maximum operating MW limit. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 9999 | 0 | Maximum Economic MW
CIMProduction | GeneratingUnit | GeneratingUnit | maximumEconomicMWRef | maximumEconomicMWRef | Float |  | etx | Maximum economic dispatch reference value. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Economic MW Ref
CIMProduction | GeneratingUnit | GeneratingUnit | MaximumOperatingMW | maximumOperatingMW | ActivePower |  | cim | This is the maximum operating MW limit the dispatcher can enter for this unit. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Operating MW
CIMProduction | GeneratingUnit | GeneratingUnit | maxONTime | maxONTime | Float |  | etx | Maximum On-Line time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum On-Line time
CIMProduction | GeneratingUnit | GeneratingUnit | maxResponseReserveLimit | maxResponseReserveLimit | Float |  | etx | Maximum responsive reserve limit MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Response Reserve Limit
CIMProduction | GeneratingUnit | GeneratingUnit | maxSpinReserveContribution | maxSpinReserveContribution | Float |  | etx | Maximum Spinning Reserve Contribution. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Spin Reserve Contribution
CIMProduction | GeneratingUnit | GeneratingUnit | maxUpRampRate | maxUpRampRate | Float |  | etx | DEFAULT MAXIMUM RAMP RATE IN UP DIRECTION. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Up Ramp Rate
CIMProduction | GeneratingUnit | GeneratingUnit | maxWeeklyEnergy | maxWeeklyEnergy | Float |  | etx | Maximum weekly energy (seasonal parameter). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum weekly energy (seasonal parameter)
CIMProduction | GeneratingUnit | GeneratingUnit | maxWeeklyStarts | maxWeeklyStarts | Float |  | etx | Maximum weekly starts (seasonal parameter). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum weekly starts (seasonal parameter)
CIMProduction | GeneratingUnit | GeneratingUnit | minCapacityLimit | minCapacityLimit | Integer |  | etx | THE LOWEST CONTINUOUS ECONOMICAL CAPACITY LIMIT. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Capacity Limit
CIMProduction | GeneratingUnit | GeneratingUnit | MinimumEconomicMW | minimumEconomicMW | ActivePower | 0 | cim | Low economic MW limit that must be greater than or equal to the minimum operating MW limit. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 999 | 0 | Minimum Economic MW
CIMProduction | GeneratingUnit | GeneratingUnit | minimumOffTime | minimumOffTime | Seconds |  | cim | Minimum time interval between unit shutdown and startup. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Off Time
CIMProduction | GeneratingUnit | GeneratingUnit | MinimumOperatingMW | minimumOperatingMW | ActivePower | 0 | cim | This is the minimum operating MW limit the dispatcher can enter for this unit. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Operating MW
CIMProduction | GeneratingUnit | GeneratingUnit | minOFFTime | minOFFTime | Float |  | etx | Minimum Off-Line time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Off-Line time
CIMProduction | GeneratingUnit | GeneratingUnit | minONTime | minONTime | Float |  | etx | Minimum On-Line time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum On-Line time
CIMProduction | GeneratingUnit | GeneratingUnit | minResponseReserveLimit | minResponseReserveLimit | Float |  | etx | Minimum responsive reserve limit MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Response Reserve Limit
CIMProduction | GeneratingUnit | GeneratingUnit | modelDetail | modelDetail | Classification | 3 | cim | Detail level of the generator model data. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Model Detail
CIMProduction | GeneratingUnit | GeneratingUnit | normalPF | normalPF | ParticipationFactor | 1 | cim | Economic participation factor based on the slope of the unit incremental cost curve at the current operating point of the unit. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Normal PF
CIMProduction | GeneratingUnit | GeneratingUnit | onlineThresholdDeadbandPct | onlineThresholdDeadbandPercent | Float |  | etx | Unit online threshold deadband percentage. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Online Threshold Deadband Percent
CIMProduction | GeneratingUnit | GeneratingUnit | PenaltyFactor | penaltyFactor | PenaltyFactor | 1 | cim | The unit's penalty factor as calculated by the Network Sensitivity function. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Penalty Factor
CIMProduction | GeneratingUnit | GeneratingUnit | PrimaryFuelType | PrimaryFuelType | EnumERCOTFuelType |  | etx | Primary fuel type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Primary Fuel Type
CIMProduction | GeneratingUnit | GeneratingUnit | qualificationStatus | qualificationStatus | Boolean | FALSE | etx | Qualification status. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Qualification Status
CIMProduction | GeneratingUnit | GeneratingUnit | raiseRampRate | raiseRampRate | PowerROCPerMin |  | cim | Raise Ramp Rate | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Raise Ramp Rate
CIMProduction | GeneratingUnit | GeneratingUnit | ratedGrossMaxMW | ratedGrossMaxMW | ActivePower |  | cim | The unit's gross rated maximum capacity (Book Value). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Rated Gross Max MW
CIMProduction | GeneratingUnit | GeneratingUnit | ratedGrossMinMW | ratedGrossMinMW | ActivePower |  | cim | The gross rated minimum generation level which the unit can safely operate at while delivering power to the transmission grid. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Rated Gross Min MW
CIMProduction | GeneratingUnit | GeneratingUnit | ratedNetMaxMW | ratedNetMaxMW | ActivePower |  | cim | The net rated maximum capacity determined by subtracting the auxiliary power used to operate the internal plant machinery from the rated gross maximum capacity. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Rated Net Max MW
CIMProduction | GeneratingUnit | GeneratingUnit | reliabilityMustRun | reliabilityMustRun | Boolean | FALSE | etx | TRUE - Unit is qualified to reliability must run. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reliability Must Run
CIMProduction | GeneratingUnit | GeneratingUnit | reserveDiscountFactor | reserveDiscountFactor | Float |  | etx | Reserve Discount Factor. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reserve Discount Factor
CIMProduction | GeneratingUnit | GeneratingUnit | resourceCategory | resourceCategory | String50 |  | etx | Type of resource. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Type of Resource
CIMProduction | GeneratingUnit | GeneratingUnit | seasonalMaxSustainableRating | seasonalMaxSustainableRating | ActivePower |  | etx | Seasonal maximum sustainable rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Max Sustainable Rating
CIMProduction | GeneratingUnit | GeneratingUnit | seasonalMinEmergencyRating | seasonalMinEmergencyRating | ActivePower |  | etx | Seasonal minimum emergency rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Min Emergency Rating
CIMProduction | GeneratingUnit | GeneratingUnit | seasonalMinSustainableRating | seasonalMinSustainableRating | ActivePower |  | etx | Seasonal minimum sustainable rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Min Sustainable Rating
CIMProduction | GeneratingUnit | GeneratingUnit | SecondaryFuelType | SecondaryFuelType | EnumERCOTFuelType |  | etx | Secondary fuel type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Secondary Fuel Type
CIMProduction | GeneratingUnit | GeneratingUnit | shortPF | shortPF | ParticipationFactor |  | cim | Short Participation Factor | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Short PF
CIMProduction | GeneratingUnit | GeneratingUnit | spinningReserveMax | spinningReserveMax | Float |  | etx | Max spinning reserve from this unit. Usuallly derived from response rate. Applicable only to non-peakers. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Spinning Reserve Max
CIMProduction | GeneratingUnit | GeneratingUnit | spinReserveRamp | spinReserveRamp | PowerROCPerMin |  | cim | Spin Reserve Ramp | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Spin Reserve Ramp
CIMProduction | GeneratingUnit | GeneratingUnit | startupTime | startupTime | Seconds |  | cim | Time it takes to get the unit on-line, from the time that the prime mover mechanical power is applied. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Startup Time
CIMProduction | GeneratingUnit | GeneratingUnit | StepChange | stepChange | ActivePower | 5 | cim | Unit allowable step change which specifies the maximum stored energy in the boiler. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Step Change
CIMProduction | GeneratingUnit | GeneratingUnit | synCondenserCapable | synCondenserCapable | Boolean | FALSE | etx | Flag indicating whether the Resource is Synchronous Condenser capable. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Synchronous Condeser Capable?
CIMProduction | GeneratingUnit | GeneratingUnit | tieLinePF | tieLinePF | ParticipationFactor | 1 | cim | Unit frequency and tie-line regulation participation factor. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tie Line PF
CIMProduction | GeneratingUnit | GeneratingUnit | wfrmcr | wfrmcr | Boolean | FALSE | etx | wfrmcr. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | wfrmcr
CIMProduction | GenUnitOpCostCurve | GenUnitOpCostCurve | netGrossMWFlag | netGrossMWFlag | Boolean | FALSE | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net Gross MW Flag
CIMProduction | HeatInputCurve | HeatInputCurve | auxPowerMult | auxPowerMult | PU |  | cim | Power output - auxiliary power multiplier adjustment factor in per unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Aux Power Mult
CIMProduction | HeatInputCurve | HeatInputCurve | auxPowerOffset | auxPowerOffset | ActivePower |  | cim | Power output - auxiliary power offset adjustment factor in MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Aux Power Offset
CIMProduction | HeatInputCurve | HeatInputCurve | heatInputEff | heatInputEff | PU |  | cim | Heat input - efficiency multiplier adjustment factor in per unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Heat Input Efficiency
CIMProduction | HeatInputCurve | HeatInputCurve | heatInputOffset | heatInputOffset | HeatPerHour |  | cim | Heat input - offset adjustment factor in MBtu/hr. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Heat Input Offset
CIMProduction | HeatInputCurve | HeatInputCurve | netGrossMWFlag | netGrossMWFlag | Boolean | FALSE | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net Gross MW Flag
CIMProduction | HeatRateCurve | HeatRateCurve | baseHeat | baseHeat | Float |  | etx | (MBTU/HR) The amount of heat required at first MW point to maintain synchronization. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Base Heat
CIMProduction | HeatRateCurve | HeatRateCurve | netGrossMWFlag | netGrossMWFlag | Boolean | FALSE | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net Gross MW Flag
CIMProduction | HydroGeneratingUnit | HydroGeneratingUnit | HydroUnitWaterCost | hydroUnitWaterCost | Float |  | cim | The equivalent cost of water that drives the hydro turbine, expressed as (dollars/cubic meter). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Hydro Unit Water Cost
CIMProduction | HydroPowerPlant | HydroPowerPlant | dischargeTravelDelay | dischargeTravelDelay | Seconds |  | cim | Water travel delay from tailbay to next downstream hydro power station. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Discharge Travel Delay
CIMProduction | HydroPowerPlant | HydroPowerPlant | hydroPlantType | hydroPlantType | EnumHydroPlantType |  | cim | The type of hydro power plant, e.g.: Run-of-River, Pumped Storage, Major Storage, Minor Storage. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Hydro Plant Type
CIMProduction | HydroPowerPlant | HydroPowerPlant | penstockType | penstockType | EnumPenstockType |  | cim | Type and configuration of hydro plant penstock(s). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Penstock Type
CIMProduction | HydroPowerPlant | HydroPowerPlant | plantDischargeCapacity | plantDischargeCapacity | Float |  | cim | Total plant discharge capacity in cubic meters per second. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Plant Discharge Capacity
CIMProduction | HydroPowerPlant | HydroPowerPlant | plantMWGenRating | plantMWGenRating | ActivePower |  | cim | The hydro plant's generating rating in MW for rated head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Plant MW Gen Rating
CIMProduction | HydroPowerPlant | HydroPowerPlant | plantMWPumpRating | plantMWPumpRating | ActivePower |  | cim | The hydro plant's pumping rating in MW for rated head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Plant MW Pump Rating
CIMProduction | HydroPowerPlant | HydroPowerPlant | plantRatedHead | plantRatedHead | Float |  | cim | The plant's rated gross head in meters. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Plant Rated Head
CIMProduction | HydroPowerPlant | HydroPowerPlant | surgeTankCode | surgeTankCode | EnumSurgeTankCode |  | cim | A code describing the type (or absence) of surge tank that is associated with the hydro power plant. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Surge Tank Code
CIMProduction | HydroPowerPlant | HydroPowerPlant | surgeTankCrestLevel | surgeTankCrestLevel | WaterLevel |  | cim | The level at which the surge tank spills. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Surge Tank Crest Level
CIMProduction | HydroPump | HydroPump | pumpDischAtMaxHead | pumpDischAtMaxHead | Float |  | cim | The pumping discharge (m3/sec) under maximum head conditions, usually at full gate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pump Discharge at Max Head
CIMProduction | HydroPump | HydroPump | pumpDischAtMinHead | pumpDischAtMinHead | Float |  | cim | The pumping discharge (m3/sec) under minimum head conditions, usually at full gate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pump Discharge at Min Head
CIMProduction | HydroPump | HydroPump | pumpPowerAtMaxHead | pumpPowerAtMaxHead | ActivePower |  | cim | The pumping power (MW) under maximum head conditions, usually at full gate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pump Power at Max Head
CIMProduction | HydroPump | HydroPump | pumpPowerAtMinHead | pumpPowerAtMinHead | ActivePower |  | cim | The pumping power (MW) under minimum head conditions, usually at full gate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pump Power at Min Head
CIMProduction | IncrementalHeatRateCurve | IncrementalHeatRateCurve | netGrossMWFlag | netGrossMWFlag | Boolean | FALSE | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net Gross MW Flag
CIMProduction | Reservoir | Reservoir | activeStorageCapacity | activeStorageCapacity | Volume |  | cim | Storage volume (in Mm3) between the full supply level and the normal minimum operating level. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Active Storage Volume
CIMProduction | Reservoir | Reservoir | energyStorageRating | energyStorageRating | Float |  | cim | The reservoir's energy storage rating in MWh for given head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Energy Storage Rating
CIMProduction | Reservoir | Reservoir | fullSupplyLevel | fullSupplyLevel | WaterLevel |  | cim | Full supply level, above which water will spill. This can be the spillway crest level or the top of closed gates. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Full Supply Level
CIMProduction | Reservoir | Reservoir | grossCapacity | grossCapacity | Volume |  | cim | Total capacity of reservoir. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gross Capacity
CIMProduction | Reservoir | Reservoir | normalMinOperateLevel | normalMinOperateLevel | WaterLevel |  | cim | Normal minimum operating level below which the penstocks will draw air. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Normal Min Operate Level
CIMProduction | Reservoir | Reservoir | riverOutletWorks | riverOutletWorks | String100 |  | cim | River outlet works for riparian right releases or other purposes. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | River Outlet Works
CIMProduction | Reservoir | Reservoir | spillTravelDelay | spillTravelDelay | Seconds |  | cim | The spillway water travel delay to the next downstream reservoir. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Spill Travel Delay
CIMProduction | Reservoir | Reservoir | spillwayCapacity | spillwayCapacity | Float |  | cim | The flow capacity of the spillway in cubic meters per second. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Spillway Capacity
CIMProduction | Reservoir | Reservoir | spillwayCrestLength | spillwayCrestLength | Float |  | cim | The length of the spillway crest in meters. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Spillway Crest Length
CIMProduction | Reservoir | Reservoir | spillwayCrestLevel | spillwayCrestLevel | WaterLevel |  | cim | Spillway crest level above which water will spill. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Spillway Crest Level
CIMProduction | Reservoir | Reservoir | spillWayGateType | spillWayGateType | EnumSpillwayGateType |  | cim | Type of spillway gate, including parameters. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Spillway Gate Type
CIMProduction | ShutdownCurve | ShutdownCurve | shutdownCost | shutdownCost | Money |  | cim | Fixed shutdown cost. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Shutdown Cost
CIMProduction | ShutdownCurve | ShutdownCurve | shutdownDate | shutdownDate | AbsoluteDateTime |  | cim | The date and time of the most recent generating unit shutdown. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Shutdown Date
CIMProduction | StartIgnFuelCurve | StartIgnFuelCurve | ignitionFuelType | ignitionFuelType | EnumFuelType |  | cim | Type of ignition fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Ignition Fuel Type
CIMProduction | StartMainFuelCurve | StartMainFuelCurve | mainFuelType | mainFuelType | EnumFuelType |  | cim | Type of main fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Main Fuel Type
CIMProduction | StartRampCurve | StartRampCurve | hotStandbyRamp | hotStandbyRamp | PowerROCPerMin |  | cim | The startup ramp rate in gross MW/minute for a unit that is on hot standby. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Hot Standby Ramp
CIMProduction | StartupModel | StartupModel | fixedMaintCost | fixedMaintCost | CostPerHour |  | cim | Fixed Maintenance Cost. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fixed Maintenance Cost
CIMProduction | StartupModel | StartupModel | hotStandbyHeat | hotStandbyHeat | HeatPerHour |  | cim | The amount of heat input per hour required for hot standby operation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Hot Standby Heat
CIMProduction | StartupModel | StartupModel | incrementalMaintCost | incrementalMaintCost | CostPerEnergyUnit |  | cim | Incremental Maintenance Cost | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Incremental Maintenance Cost
CIMProduction | StartupModel | StartupModel | minimumDownTime | minimumDownTime | Hours |  | cim | The minimum number of hours the unit must be down before restart. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Down Time
CIMProduction | StartupModel | StartupModel | minimumRunTime | minimumRunTime | Hours |  | cim | The minimum number of hours the unit must be operating before being allowed to shut down. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Run Time
CIMProduction | StartupModel | StartupModel | riskFactorCost | riskFactorCost | Money |  | cim | The opportunity cost associated with the return in dollars. This represents the restart's 'share' of the unit depreciation and risk of an event which would damage the unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Risk Factor Cost
CIMProduction | StartupModel | StartupModel | startupCost | startupCost | Money |  | cim | Total miscellaneous start up costs. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Startup Cost
CIMProduction | StartupModel | StartupModel | startupDate | startupDate | AbsoluteDateTime |  | cim | The date and time of the most recent generating unit startup. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Startup Date
CIMProduction | StartupModel | StartupModel | startupPriority | startupPriority | Priority |  | cim | Startup priority within control area where lower numbers indicate higher priorities. More than one unit in an area may be assigned the same priority. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Startup Priority
CIMProduction | StartupModel | StartupModel | stbyAuxPowerMW | stbyAuxPowerMW | ActivePower |  | cim | The unit's auxiliary power consumption to maintain standby mode. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Standby Aux Power MW
CIMProduction | TargetLevelSchedule | TargetLevelSchedule | highLevelLimit | highLevelLimit | WaterLevel |  | cim | High target level limit, above which the reservoir operation will be penalized. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | High Level Limit
CIMProduction | TargetLevelSchedule | TargetLevelSchedule | lowLevelLimit | lowLevelLimit | WaterLevel |  | cim | Low target level limit, below which the reservoir operation will be penalized. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Low Level Limit
CIMProduction | ThermalGeneratingUnit | ThermalGeneratingUnit | boilerColdStartEnergy | boilerColdStartEnergy | Float |  | etx | Boiler cold start engergy (MBTU). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Boiler Cold Start Energy
CIMProduction | ThermalGeneratingUnit | ThermalGeneratingUnit | boilerEfficiency | boilerEfficiency | Float |  | etx | (%) BOILER EFFICIENCY FACTOR. THE HEAT RATE CURVE WILL BE DIVIDED BY THIS FACTOR TO ACCOUNT FOR A DIRTY BOILER OR ANY OTHER CAUSE FOR LOSS OF EFFICIENCY OF THE HEAT CYCLE. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Boiler Efficiency
CIMProduction | ThermalGeneratingUnit | ThermalGeneratingUnit | oMCost | oMCost | CostPerHeatUnit |  | cim | Operating and maintenance cost for the thermal unit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Operating-Maintenance Cost
CIMProduction | ThermalGeneratingUnit | ThermalGeneratingUnit | turbineColdStartEnergy | turbineColdStartEnergy | Float |  | etx | Turbine cold start energy MBTU (used by UC only). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Turbine Cold Start Energy
CIMProtection | CurrentRelay | CurrentRelay | currentLimit1 | currentLimit1 | CurrentFlow |  | cim | Current limit #1 for inverse time pickup. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Current Limit1
CIMProtection | CurrentRelay | CurrentRelay | currentLimit2 | currentLimit2 | CurrentFlow |  | cim | Current limit #2 for inverse time pickup. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Current Limit2
CIMProtection | CurrentRelay | CurrentRelay | currentLimit3 | currentLimit3 | CurrentFlow |  | cim | Current limit #3 for inverse time pickup. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Current Limit3
CIMProtection | CurrentRelay | CurrentRelay | instantTrip | instantTrip | CurrentFlow |  | etx | Instant trip current. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Instant Trip
CIMProtection | CurrentRelay | CurrentRelay | instantTripMva | instantTripMva | ApparentPower |  | etx | Instant trip apparent power | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Instant Trip MVa
CIMProtection | CurrentRelay | CurrentRelay | inverseTimeFlag | inverseTimeFlag | Boolean | FALSE | cim | True/False flag that indicates whether or not the current relay has inverse time characteristic. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Inverse Time Flag
CIMProtection | CurrentRelay | CurrentRelay | isDirectional | isDirectional | Boolean |  | etx | Is directional? | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Is Directional
CIMProtection | CurrentRelay | CurrentRelay | isMvaSetting | isMvaSetting | Boolean |  | etx | Is MVA Setting? | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Is MVA Setting
CIMProtection | CurrentRelay | CurrentRelay | lockoutTime | lockoutTime | Seconds |  | etx | Relay lockout time delay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Lockout Time
CIMProtection | CurrentRelay | CurrentRelay | mvaLimit1 | mvaLimit1 | ApparentPower |  | etx | MVA limit 1. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | mvaLimit1
CIMProtection | CurrentRelay | CurrentRelay | nominalMva | nominalMva | ApparentPower |  | etx | Nominal MVA. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | nominalMva
CIMProtection | CurrentRelay | CurrentRelay | pickup | pickup | CurrentFlow |  | etx | Pickup time. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pickup Time
CIMProtection | CurrentRelay | CurrentRelay | pickupMva | pickupMva | ApparentPower |  | etx | Pickup MVA. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | pickupMva
CIMProtection | CurrentRelay | CurrentRelay | resetTime | resetTime | Seconds |  | etx | Relay (disk) reset time delay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reset Time
CIMProtection | CurrentRelay | CurrentRelay | timeDelay1 | timeDelay1 | Seconds |  | cim | Inverse time delay #1 for current limit #1. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time Delay1
CIMProtection | CurrentRelay | CurrentRelay | timeDelay2 | timeDelay2 | Seconds |  | cim | Inverse time delay #2 for current limit #2. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time Delay2
CIMProtection | CurrentRelay | CurrentRelay | timeDelay3 | timeDelay3 | Seconds |  | cim | Inverse time delay #3 for current limit #3. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time Delay3
CIMProtection | ProtectionEquipment | ProtectionEquipment | highLimit | highLimit | Float |  | cim | The maximum allowable value. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | High Limit
CIMProtection | ProtectionEquipment | ProtectionEquipment | lockoutTimeHigh | lockoutTimeHigh | Seconds |  | etx | Lockout time high (in seconds). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | lockoutTimeHigh
CIMProtection | ProtectionEquipment | ProtectionEquipment | lockoutTimeLow | lockoutTimeLow | Seconds |  | etx | Lockout time low (in seconds). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | lockoutTimeLow
CIMProtection | ProtectionEquipment | ProtectionEquipment | lowLimit | lowLimit | Float |  | cim | The minimum allowable value. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Low Limit
CIMProtection | ProtectionEquipment | ProtectionEquipment | powerDirectionFlag | powerDirectionFlag | Boolean | FALSE | cim | Direction same as positive active power flow value. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Power Direction Flag
CIMProtection | ProtectionEquipment | ProtectionEquipment | relayDelayTime | relayDelayTime | Seconds | 0 | cim | The time delay in seconds from detection of abnormal conditions to relay operation | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Relay Delay Time
CIMProtection | ProtectionEquipment | ProtectionEquipment | relayDelayTimeHigh | relayDelayTimeHigh | Seconds |  | etx | Relay delay time high (in seconds). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | relayDelayTimeHigh
CIMProtection | ProtectionEquipment | ProtectionEquipment | relayDelayTimeLow | relayDelayTimeLow | Seconds |  | etx | Relay delay time low (in seconds). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | relayDelayTimeLow
CIMProtection | RecloseSequence | RecloseSequence | recloseDelay | recloseDelay | Seconds |  | cim | Indicates the time lapse before the reclose step will execute a reclose. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reclose Delay
CIMProtection | RecloseSequence | RecloseSequence | recloseStep | recloseStep | Integer |  | cim | Indicates the ordinal position of the reclose step relative to other steps in the sequence. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reclose Step
CIMProtection | SynchrocheckRelay | SynchrocheckRelay | maxAngleDiff | maxAngleDiff | AngleRadians |  | cim | The maximum allowable voltage vector phase angle difference across the open device. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Angle Diff
CIMProtection | SynchrocheckRelay | SynchrocheckRelay | maxAngleDiffDelay | maxAngleDiffDelay | Seconds |  | etx | Trip delay at maximum angle difference. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Angle Difference Delay
CIMProtection | SynchrocheckRelay | SynchrocheckRelay | maxFreqDiff | maxFreqDiff | Frequency |  | cim | The maximum allowable frequency difference across the open device. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Freq Diff
CIMProtection | SynchrocheckRelay | SynchrocheckRelay | maxFreqDiffDelay | maxFreqDiffDelay | Seconds |  | etx | Trip delay at maximum frequency difference. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Frequency Difference Delay
CIMProtection | SynchrocheckRelay | SynchrocheckRelay | maxVoltDiff | maxVoltDiff | Voltage |  | cim | The maximum allowable difference voltage across the open device. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Volt Diff
CIMProtection | SynchrocheckRelay | SynchrocheckRelay | minAngleDiffDelay | minAngleDiffDelay | Seconds |  | etx | Trip delay at minimum angle difference. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Angle Difference Delay
CIMProtection | SynchrocheckRelay | SynchrocheckRelay | minFreqDiffDelay | minFreqDiffDelay | Seconds |  | etx | Trip delay at minimum frequency difference. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Frequency Difference Delay
CIMSCADA | RemoteControl | RemoteControl | actuatorMaximum | actuatorMaximum | Float |  | cim | Actuator Maximum | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Actuator Maximum
CIMSCADA | RemoteControl | RemoteControl | actuatorMinimum | actuatorMinimum | Float |  | cim | Actuator Minimum | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Actuator Minimum
CIMSCADA | RemoteControl | RemoteControl | remoteControlled | remoteControlled | Boolean | FALSE | cim | Remote Controlled | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Remote Controlled
CIMSCADA | RemoteSource | RemoteSource | deadband | deadband | Float |  | cim | The smallest change in value to be reported. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband
CIMSCADA | RemoteSource | RemoteSource | scanInterval | scanInterval | Seconds |  | cim | The time interval between scans. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | scanInterval
CIMSCADA | RemoteSource | RemoteSource | sensorMaximum | sensorMaximum | Float |  | cim | The maximum value the telemetry item can return. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Sensor Maximum
CIMSCADA | RemoteSource | RemoteSource | sensorMinimum | sensorMinimum | Float |  | cim | The minimum value the telemetry item can return. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Sensor Minimum
CIMSCADA | RemoteUnit | RemoteUnit | remoteUnitType | remoteUnitType | EnumRemoteUnitType |  | cim | A remote unit can be a RTU, IED, substation control system, control center etc. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Remote Unit Type
CIMTopology | ConnectivityNode | ConnectivityNode | height | height | Integer | 0 | spc | height | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | height
CIMTopology | ConnectivityNode | ConnectivityNode | PSSEBusName | PSSEBusName | String12 |  | etx | Store the PSS™E bus name that will be associated with the most favored Connectivity Node in Connectivity Node to Bus Processing Option 1. | FALSE | FALSE | TRUE | FALSE |  | TRUE |  | FALSE |  |  | PSS/E Bus Name
CIMTopology | ConnectivityNode | ConnectivityNode | PSSEBusNumber | PSSEBusNumber | Integer |  | etx | The PSS/E bus number associated with this point in the network. This attribute should only be used to model ficticious PSS/E busbars that are not associated with physical busbar sections. | FALSE | FALSE | TRUE | FALSE |  | TRUE |  | FALSE | 99997 | 1 | PSS/E Bus Number
CIMTopology | ConnectivityNode | ConnectivityNode | SlackBusPriority | SlackBusPriority | Integer |  | etx | Swing Bus Definition. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Slack Bus Priority
CIMTopology | ConnectivityNode | ConnectivityNode | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
CIMTopology | ConnectivityNode | ConnectivityNode | width | width | Integer | 0 | spc | width | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | width
CIMTopology | ConnectivityNode | ConnectivityNode | xval | xval | Integer | 0 | spc | x co-ordinate | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | x co-ordinate
CIMTopology | ConnectivityNode | ConnectivityNode | yval | yval | Integer | 0 | spc | y co-ordinate | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | y co-ordinate
CIMTopology | TopologicalNode | TopologicalNode | energized | energized | Boolean | FALSE | cim | True if node energized. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Energized
CIMTopology | TopologicalNode | TopologicalNode | loadCarrying | loadCarrying | Boolean | FALSE | cim | True if node is load carrying. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Carrying
CIMTopology | TopologicalNode | TopologicalNode | netInjectionMVar | netInjectionMVar | ReactivePower |  | cim | Net injection MVAr | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net injection MVAr
CIMTopology | TopologicalNode | TopologicalNode | netInjectionMW | netInjectionMW | ActivePower |  | cim | Net injection MW | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net Injection MW
CIMTopology | TopologicalNode | TopologicalNode | observabilityFlag | observabilityFlag | Boolean | FALSE | cim | The observability status of the node. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Observability Flag
CIMTopology | TopologicalNode | TopologicalNode | phaseAngle | phaseAngle | AngleRadians |  | cim | Phase angle of node. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phase Angle
CIMTopology | TopologicalNode | TopologicalNode | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number Alternate Areas and Zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
CIMTopology | TopologicalNode | TopologicalNode | voltage | voltage | Voltage |  | cim | Voltage of node. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Voltage
CIMWires | ACLineSegment | ACLineSegment | emergencyMaxShadowPrice | emergencyMaxShadowPrice | DoubleFloat | 99999 | etx | States the Emergency Max Shadow price for a ACLineSegment. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emergency Max Shadow Price
CIMWires | ACLineSegment | ACLineSegment | fifteenMinuteMaxShadowPrice | fifteenMinuteMaxShadowPrice | DoubleFloat | 99999 | etx | States the 15 minute rating Max Shadow price for a ACLineSegment. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | 15 minute rating Max Shadow Price
CIMWires | ACLineSegment | ACLineSegment | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a ACLineSegment. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
CIMWires | Breaker | Breaker | ampRating | ampRating | CurrentFlow |  | cim | Fault interrupting rating in amperes. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Current Flow
CIMWires | Breaker | Breaker | InTransitTime | InTransitTime | Seconds | 0 | cim | The transition time from open to close, in seconds. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | In Transit Time
CIMWires | CompositeSwitch | CompositeSwitch | compositeSwitchType | compositeSwitchType | CompositeSwitchType |  | cim | An alphanumeric code that can be used as a reference to extar information such as the description of the interlocking scheme if any. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Composite Switch Type
CIMWires | Conductor | Conductor | b0ch | b0ch | Susceptance |  | cim | Zero sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 5 | 0 | b0ch
CIMWires | Conductor | Conductor | bch | bch | Susceptance |  | cim | Positive sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 50 | 0 | bch
CIMWires | Conductor | Conductor | g0ch | g0ch | Conductance |  | cim | Zero sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | g0ch
CIMWires | Conductor | Conductor | gch | gch | Conductance |  | cim | Positive sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | gch
CIMWires | Conductor | Conductor | length | length | LongLength |  | cim | Segment length for calculating line section capabilities (long length units). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Length
CIMWires | Conductor | Conductor | r | r | Resistance |  | cim | Positive sequence series resistance of the entire line section. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 500 | -500 | r
CIMWires | Conductor | Conductor | r0 | r0 | Resistance |  | cim | Zero sequence series resistance of the entire line section. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 500 | -500 | r0
CIMWires | Conductor | Conductor | x | x | Reactance |  | cim | Positive sequence series reactance of the entire line section. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 1000 | -1000 | x
CIMWires | Conductor | Conductor | x0 | x0 | Reactance |  | cim | Zero sequence series reactance of the entire line section. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 1000 | -1000 | x0
CIMWires | ConductorType | ConductorType | sheathReactance | sheathReactance | Reactance |  | cim | Reactance of the sheath for cable conductors. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Sheath Reactance
CIMWires | ConductorType | ConductorType | sheathResistance | sheathResistance | Resistance |  | cim | Resistance of the sheath for cable conductors. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Sheath Resistance
CIMWires | DCLineSegment | DCLineSegment | dcSegmentInductance | dcSegmentInductance | Inductance |  | cim | Inductance of the DC line segment, in millihenries. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | DC Segment Inductance
CIMWires | DCLineSegment | DCLineSegment | dcSegmentResistance | dcSegmentResistance | Resistance |  | cim | Resistance of the DC line segment, in ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | DC Segment Resistance
CIMWires | EnergyConsumer | EnergyConsumer | conformingLoadFlag | conformingLoadFlag | Boolean | TRUE | cim | Flag is set to YES if the load is conforming, i.e., tracks the area load to which the energy consumer belongs. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Conforming Load Flag
CIMWires | EnergyConsumer | EnergyConsumer | customerCount | customerCount | Counter |  | cim | Number of individual customers represented by this Demand. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Customer Count
CIMWires | EnergyConsumer | EnergyConsumer | maxMVAR | maxMVAR | Float |  | etx | Maximum Reactive POWER LOAD. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MVAR
CIMWires | EnergyConsumer | EnergyConsumer | maxMW | maxMW | Float |  | etx | Maximum REAL POWER LOAD. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MW
CIMWires | EnergyConsumer | EnergyConsumer | minMVAR | minMVAR | Float |  | etx | MINIMUM Reative POWER LOAD. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum MVAR
CIMWires | EnergyConsumer | EnergyConsumer | minMW | minMW | Float |  | etx | MINIMUM REAL POWER LOAD. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum MW
CIMWires | EnergyConsumer | EnergyConsumer | pFexp | pFexp | Exponent |  | cim | Exponent of per unit frequency effecting real power. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Real Power Frequency Exponent
CIMWires | EnergyConsumer | EnergyConsumer | pfixed | pfixed | ActivePower |  | cim | Real component of the load that is a fixed quantity, MW. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Fixed Real Power
CIMWires | EnergyConsumer | EnergyConsumer | pfixedPct | pfixedPct | PerCent |  | cim | Fixed MW as per cent of load area fixed MW. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Fixed Real Power Percent
CIMWires | EnergyConsumer | EnergyConsumer | pnom | pnom | ActivePower |  | cim | Nominal value for real power, MW. Nominal real power is adjusted according to the load profile selected for the consumer. It equates to one per unit in the load profile. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Nominal Real Power
CIMWires | EnergyConsumer | EnergyConsumer | pnomPct | pnomPct | PerCent |  | cim | Nominal MW as per cent of load group nominal MW. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Nominal Real Power Percent
CIMWires | EnergyConsumer | EnergyConsumer | powerFactor | powerFactor | PowerFactor |  | cim | Power factor for nominal portion of load. Defined as MW/MVA. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Power Factor
CIMWires | EnergyConsumer | EnergyConsumer | pVexp | pVexp | Exponent |  | cim | Exponent of per unit voltage effecting real power. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Real Power Voltage Exponent
CIMWires | EnergyConsumer | EnergyConsumer | qFexp | qFexp | Exponent |  | cim | Exponent of per unit frequency effecting reactive power | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reactive Power Frequency Exponent
CIMWires | EnergyConsumer | EnergyConsumer | qfixed | qfixed | ReactivePower |  | cim | Reactive component of the load that is a fixed quantity, MVAr. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Fixed Reactive Power
CIMWires | EnergyConsumer | EnergyConsumer | qfixedPct | qfixedPct | PerCent |  | cim | Fixed MVAr as per cent of load area fixed MVAr. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Fixed Reactive Power Percent
CIMWires | EnergyConsumer | EnergyConsumer | qnom | qnom | ReactivePower |  | cim | Nominal value for reactive power, MVAr. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Nominal Reactive Power
CIMWires | EnergyConsumer | EnergyConsumer | qnomPct | qnomPct | PerCent |  | cim | Nominal MVAr as per cent of load group nominal MVAr. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Nominal Reactive Power Percent
CIMWires | EnergyConsumer | EnergyConsumer | qVexp | qVexp | Exponent |  | cim | Exponent of per unit voltage effecting reactive power. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reactive Power Voltage Exponent
CIMWires | EquivalentSource | EquivalentSource | activePower | activePower | ActivePower |  | cim | High voltage source load. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Active Power
CIMWires | EquivalentSource | EquivalentSource | nominalVoltage | nominalVoltage | Voltage |  | cim | Phase-to-phase nominal voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Nominal Voltage
CIMWires | EquivalentSource | EquivalentSource | r | r | Resistance |  | cim | Positive sequence Thevenin resistance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Resistance
CIMWires | EquivalentSource | EquivalentSource | r0 | r0 | Resistance |  | cim | Zero sequence Thevenin resistance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zero Sequence Resistance
CIMWires | EquivalentSource | EquivalentSource | rn | rn | Resistance |  | cim | Negative sequence Thevenin resistance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Negative Sequence Resistance
CIMWires | EquivalentSource | EquivalentSource | voltageAngle | voltageAngle | AngleRadians |  | cim | Phase angle of a-phase open circuit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Voltage Angle
CIMWires | EquivalentSource | EquivalentSource | voltageMagnitude | voltageMagnitude | Voltage |  | cim | Phase-to-phase open circuit voltage magnitude. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Voltage Magnitude
CIMWires | EquivalentSource | EquivalentSource | x | x | Reactance |  | cim | Positive sequence Thevenin reactance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reactance
CIMWires | EquivalentSource | EquivalentSource | x0 | x0 | Reactance |  | cim | Zero sequence Thevenin reactance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zero Sequence Reactance
CIMWires | EquivalentSource | EquivalentSource | xn | xn | Reactance |  | cim | Negative sequence Thevenin reactance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Negative Sequence Reactance
CIMWires | FrequencyConverter | FrequencyConverter | frequency | frequency | Frequency |  | cim | Frequency on the AC side. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Frequency
CIMWires | FrequencyConverter | FrequencyConverter | maximumKV | maximumKV | Voltage |  | cim | The maximum voltage on the DC side at which the frequency converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum kV
CIMWires | FrequencyConverter | FrequencyConverter | maximumMW | maximumMW | ActivePower |  | cim | The maximum power on the DC side at which the frequence converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MW
CIMWires | FrequencyConverter | FrequencyConverter | minimumKV | minimumKV | Voltage |  | cim | The minimum voltage on the DC side at which the frequency converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum kV
CIMWires | FrequencyConverter | FrequencyConverter | minimumMW | minimumMW | ActivePower |  | cim | The minimum power on the DC side at which the frequence converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum MW
CIMWires | FrequencyConverter | FrequencyConverter | operatingMode | operatingMode | OperatingMode |  | cim | Operating mode for the frequency converter. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Operating Mode
CIMWires | Fuse | Fuse | ampRating | ampRating | CurrentFlow |  | cim | Fault interrupting rating in amperes. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Amp Rating
CIMWires | Line | Line | emergencyMaxShadowPrice | emergencyMaxShadowPrice | DoubleFloat | 99999 | etx | States the Emergency Max Shadow price for a Line. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emergency Max Shadow Price
CIMWires | Line | Line | fifteenMinuteMaxShadowPrice | fifteenMinuteMaxShadowPrice | DoubleFloat | 99999 | etx | States the 15 minute rating Max Shadow price for a Line. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | 15 minute rating Max Shadow Price
CIMWires | Line | Line | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a Line. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
CIMWires | LoadBreakSwitch | LoadBreakSwitch | ampRating | ampRating | CurrentFlow |  | cim | Current carrying capacity, expressed in amperes, of a wire or cable under stated thermal conditions | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | amp Rating
CIMWires | MVArCapabilityCurve | MVArCapabilityCurve | coolantTemperature | coolantTemperature | Temperature |  | cim | The machine's coolant temperature in degrees Celsius (e.g., ambient air or stator circulating water). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Coolant Temperature
CIMWires | MVArCapabilityCurve | MVArCapabilityCurve | hydrogenPressure | hydrogenPressure | Pressure |  | cim | The hydrogen coolant pressure. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Hydrogen Pressure
CIMWires | PowerTransformer | PowerTransformer | bmagSat | bmagSat | PerCent |  | cim | Core shunt magnetizing susceptance in the saturation region, in per cent. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Magnetizing Susceptance Saturation
CIMWires | PowerTransformer | PowerTransformer | emergencyMaxShadowPrice | emergencyMaxShadowPrice | DoubleFloat | 99999 | etx | States the Emergency Max Shadow price for a Line. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emergency Max Shadow Price
CIMWires | PowerTransformer | PowerTransformer | fifteenMinuteMaxShadowPrice | fifteenMinuteMaxShadowPrice | DoubleFloat | 99999 | etx | States the 15 minute rating Max Shadow price for a Transformer. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | 15 minute rating Max Shadow Price
CIMWires | PowerTransformer | PowerTransformer | magBaseKV | magBaseKV | Voltage |  | cim | The reference voltage at which the magnetizing saturation measurements were made. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Magnetizing Saturation Voltage
CIMWires | PowerTransformer | PowerTransformer | magSatFlux | magSatFlux | PerCent |  | cim | Core magnetizing saturation curve knee flux level. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Magnetizing Saturation Flux
CIMWires | PowerTransformer | PowerTransformer | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a Power Transformer. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
CIMWires | PowerTransformer | PowerTransformer | phases | phases | PhaseCode |  | cim | Describes the phases carried by a power transformer. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phases
CIMWires | PowerTransformer | PowerTransformer | transfCoolingType | transfCoolingType | EnumTransformerCoolingType |  | cim | Type of transformer cooling. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Transformer Cooling Type
CIMWires | PowerTransformer | PowerTransformer | transformerType | transformerType | EnumTransformerType |  | cim | Transformer Type. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Transformer Type
CIMWires | PowerTransformer | PowerTransformer | voltageSensitivity | voltageSensitivity | PerCent |  | etx | SENSITIVITY OF VOLTAGE TO THE TRANSFORMER tap ratio. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Voltage Sensitivity
CIMWires | RectifierInverter | RectifierInverter | bridges | bridges | Counter |  | cim | Number of bridges. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Bridges
CIMWires | RectifierInverter | RectifierInverter | commutatingReactance | commutatingReactance | Reactance |  | cim | Commutating reactance in ohms at AC bus frequency. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Commutating Reactance
CIMWires | RectifierInverter | RectifierInverter | commutatingResistance | commutatingResistance | Resistance |  | cim | Commutating resistance in ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Commutating Resistance
CIMWires | RectifierInverter | RectifierInverter | compoundResistance | compoundResistance | Resistance |  | cim | Compounding resistance in ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Compounding Resistance
CIMWires | RectifierInverter | RectifierInverter | frequency | frequency | Frequency |  | cim | Frequency on the AC side. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Frequency
CIMWires | RectifierInverter | RectifierInverter | maximumKV | maximumKV | Voltage |  | cim | The maximum voltage on the DC side at which the frequency converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum kV
CIMWires | RectifierInverter | RectifierInverter | maximumMW | maximumMW | ActivePower |  | cim | The maximum power on the DC side at which the frequence converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MW
CIMWires | RectifierInverter | RectifierInverter | minCompoundVoltage | minCompoundVoltage | Voltage |  | cim | Minimum compounded DC voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Compound Voltage
CIMWires | RectifierInverter | RectifierInverter | minimumKV | minimumKV | Voltage |  | cim | The minimum voltage on the DC side at which the frequency converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum kV
CIMWires | RectifierInverter | RectifierInverter | minimumMW | minimumMW | ActivePower |  | cim | The minimum power on the DC side at which the frequence converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum MW
CIMWires | RectifierInverter | RectifierInverter | operatingMode | operatingMode | OperatingMode |  | cim | Operating mode for the frequency converter. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Operating Mode
CIMWires | RectifierInverter | RectifierInverter | ratedKV | ratedKV | Voltage |  | cim | Rectifier/inverter primary base voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Rated kV
CIMWires | RegulatingCondEq | RegulatingCondEq | avrEnabled | avrEnabled | Boolean | FALSE | etx | T = Automatic voltage regulation enabled. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Automatic Voltage Regulation Enabled
CIMWires | RegulatingCondEq | RegulatingCondEq | loadBasedRegulationEnabled | loadBasedRegulationEnabled | Boolean | FALSE | etx | T = Load based voltage regulation enabled. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Load Based Regulation Enabled
CIMWires | RegulationSchedule | RegulationSchedule | lineDropCompensation | lineDropCompensation | Boolean | FALSE | cim | Flag to indicate that line drop compensation is to be applied. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Line Drop Compensation
CIMWires | RegulationSchedule | RegulationSchedule | lineDropR | lineDropR | Resistance |  | cim | Line drop resistance. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Line Drop Resistance
CIMWires | RegulationSchedule | RegulationSchedule | lineDropX | lineDropX | Reactance |  | cim | Line drop reactance. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Line Drop Reactance
CIMWires | SeriesCompensator | SeriesCompensator | emergencyMaxShadowPrice | emergencyMaxShadowPrice | DoubleFloat | 99999 | etx | States the Emergency Max Shadow price for a SeriesCompensator. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emergency Max Shadow Price
CIMWires | SeriesCompensator | SeriesCompensator | fifteenMinuteMaxShadowPrice | fifteenMinuteMaxShadowPrice | DoubleFloat | 99999 | etx | States the 15 minute Max Shadow price for a SeriesCompensator. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | 15 minute rating Max Shadow Price
CIMWires | SeriesCompensator | SeriesCompensator | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a SeriesCompensator. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
CIMWires | SeriesCompensator | SeriesCompensator | r | r | Resistance |  | cim | Positive sequence resistance of the capacitor bank. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Resistance
CIMWires | SeriesCompensator | SeriesCompensator | x | x | Reactance |  | cim | Positive sequence reactance of the capacitor bank. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reactance
CIMWires | ShuntCompensator | ShuntCompensator | aVRDelay | aVRDelay | Seconds |  | cim | Time delay in seconds required for the device to be connected or disconnected by automatic voltage regulation (AVR). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Automatic Voltage Regulation Delay
CIMWires | ShuntCompensator | ShuntCompensator | impedance | impedance | Impedance |  | cim | The positive sequence impedance of the capacitor. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Impedance
CIMWires | ShuntCompensator | ShuntCompensator | maximumkV | maximumkV | Voltage |  | cim | The maximum voltage at which the capacitor bank should operate. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum kV
CIMWires | ShuntCompensator | ShuntCompensator | maximumSections | maximumSections | Counter |  | cim | For a capacitor bank, the maximum number of sections that may be switched in. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Sections
CIMWires | ShuntCompensator | ShuntCompensator | minimumkV | minimumkV | Voltage |  | cim | The minimum voltage at which the capacitor bank should operate. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum kV
CIMWires | ShuntCompensator | ShuntCompensator | mVArPerSection | mVArPerSection | ReactivePower |  | cim | For a capacitor bank, the size in MVAr of each switchable section at the Nominal kV. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | mVAr Per Section
CIMWires | ShuntCompensator | ShuntCompensator | nominalkV | nominalkV | Voltage |  | cim | The nominal voltage at which the nominal MVAr was measured. This should normally be within 10% of the voltage at which the capacitor is connected to the network. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Nominal kV
CIMWires | ShuntCompensator | ShuntCompensator | nominalMVAr | nominalMVAr | ReactivePower |  | cim | Nominal MVAr output of the capacitor bank at the nominal kV. This number should be positive. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Nominal MVAr
CIMWires | ShuntCompensator | ShuntCompensator | normalSections | normalSections | Counter |  | cim | For a capacitor bank, the normal number of sections switched in. This number should correspond to the Nominal MVAr. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Normal Sections
CIMWires | ShuntCompensator | ShuntCompensator | switchingPriority | switchingPriority | Integer |  | etx | Switching priority number. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Switching Priority
CIMWires | ShuntCompensator | ShuntCompensator | switchOnCount | switchOnCount | Counter |  | cim | The switch on count since the capacitor count was last reset or initialized. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch On Count
CIMWires | ShuntCompensator | ShuntCompensator | switchOnDate | switchOnDate | AbsoluteDateTime |  | cim | The date and time when the capacitor bank was last switched on. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch On Date
CIMWires | ShuntCompensator | ShuntCompensator | voltSensitivity | voltSensitivity | PUkVPerMVAr |  | cim | Voltage sensitivity required for the device to regulate the bus voltage, in per unit voltage/MVAr. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Voltage Sensitivity
CIMWires | ShuntCompensator | ShuntCompensator | yPerSection | yPerSection | Admittance |  | cim | For a capacitor bank, the admittance of each switchable section. Calculated using the MVAr per section and corrected for network voltage. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Y Per Section
CIMWires | StaticVarCompensator | StaticVarCompensator | b | b | ReactivePower |  | etx | SVC Shunt Admittance. The StaticVarCompensator class has been extended to include a 'charging' attribute. The units are assumed to be in MVAR, as required by the CPSM Profile. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | b
CIMWires | StaticVarCompensator | StaticVarCompensator | CapacitiveRating | capacitiveRating | Reactance |  | cim | Maximum available capacitive reactive power. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Capacitive Rating
CIMWires | StaticVarCompensator | StaticVarCompensator | fixedMVAr | fixedMVAr | Float |  | etx | Fixed MVAr. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 0 |  | Fixed MVAR
CIMWires | StaticVarCompensator | StaticVarCompensator | highVoltageChangeThreshold | highVoltageChangeThreshold | Float |  | etx | The upper bound of the voltage threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | High Voltage Change Threshold
CIMWires | StaticVarCompensator | StaticVarCompensator | InductiveRating | inductiveRating | Reactance |  | cim | Maximum available inductive reactive power. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Inductive Rating
CIMWires | StaticVarCompensator | StaticVarCompensator | lowVoltageChangeThreshold | lowVoltageChangeThreshold | Float |  | etx | The lower bound of the voltage threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Low Voltage Change Threshold
CIMWires | StaticVarCompensator | StaticVarCompensator | maximumkV | maximumkV | Voltage |  | etx | SVC Voltage Regulation. The maximum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Maximum kV
CIMWires | StaticVarCompensator | StaticVarCompensator | maxTimeSteadyState | maxTimeSteadyState | Float |  | etx | The maximum duration allowed to exceed Q range in steady_state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Max Time Steady State
CIMWires | StaticVarCompensator | StaticVarCompensator | minimumkV | minimumkV | Voltage |  | etx | SVC Voltage Regulation. The minimum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Minimum kV
CIMWires | StaticVarCompensator | StaticVarCompensator | postContingencyMVARMax | postContingencyMVARMax | Float |  | etx | Post_contingency maximum MVAR limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Post Contingency MVAR Maximum
CIMWires | StaticVarCompensator | StaticVarCompensator | postContingencyMVARMin | postContingencyMVARMin | Float |  | etx | Post_contingency minimum MVAR limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Post Contingency MVAR Minimum
CIMWires | StaticVarCompensator | StaticVarCompensator | rampDelay | rampDelay | Float |  | etx | The desired time delay before ramp (Seconds). Entered by the database model builder. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Ramp Delay
CIMWires | StaticVarCompensator | StaticVarCompensator | rampDurationThreshold | rampDurationThreshold | Float |  | etx | The threshold ramp duration. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Ramp Duration Threshold
CIMWires | StaticVarCompensator | StaticVarCompensator | slope | slope | VoltagePerReactivePower |  | cim | The characteristics slope of an SVC defines how the reactive power output changes in proportion to the difference between the regulated bus voltage and the voltage setpoint. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | SVC Percentage Slope
CIMWires | StaticVarCompensator | StaticVarCompensator | steadyStateMVARMax | steadyStateMVARMax | Float |  | etx | Steady_state maximum MVAR limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Steady State MVAR Maximum
CIMWires | StaticVarCompensator | StaticVarCompensator | steadyStateMVARMin | steadyStateMVARMin | Float |  | etx | Steady_state minimum MVAR limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Steady State MVAR Minimum
CIMWires | StaticVarCompensator | StaticVarCompensator | sVCControlMode | sVCControlMode | EnumSVCControlMode |  | cim | SVC control mode | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | SVC Control Mode
CIMWires | StaticVarCompensator | StaticVarCompensator | voltageDeviation | voltageDeviation | Float |  | etx | SVC DEVIATION (+/-) FROM TARGET. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Voltage Deviation
CIMWires | StaticVarCompensator | StaticVarCompensator | voltageSetPoint | voltageSetPoint | Voltage |  | cim | The reactive power output of the SVC is proportional to the difference between the voltage at the regulated bus and the voltage setpoint. When the regulated bus voltage is equal to the voltage setpoint, the reactive power output is zero. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 1100 | 0 | SVC Setpoint Voltage
CIMWires | Switch | Switch | enableManualSwitching | enableManualSwitching | Boolean | FALSE | etx | T = Enables manual switching capability for the device. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Enable Manual Switching
CIMWires | Switch | Switch | initiallyOpen | initiallyOpen | Boolean | FALSE | etx | T = The initial breaker state for the online switching device model is open. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Initially Open
CIMWires | Switch | Switch | normalOpen | normalOpen | Boolean | FALSE | cim | The attribute is used in cases when no Measurement for the status value is present. If the Switch has a status measurment the Measurement.normalValue is expected to match with the Switch.normalOpen. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Normal Open
CIMWires | Switch | Switch | protectLockoutAfterAction | protectLockoutAfterAction | Boolean |  | etx | Protect lockout after action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | protectLockoutAfterAction
CIMWires | Switch | Switch | protectOverAction | protectOverAction | EnumSwitchState |  | etx | Protect over action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | protectOverAction
CIMWires | Switch | Switch | protectUnderAction | protectUnderAction | EnumSwitchState |  | etx | Protect under action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protect Under Action
CIMWires | Switch | Switch | switchedBySchedule | switchedBySchedule | Boolean | FALSE | etx | T = The switch will follow a switching schedule to change state in the network applications. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Switched By Schedule
CIMWires | Switch | Switch | switchOnCount | switchOnCount | Counter |  | cim | The switch on count since the switch was last reset or initialized. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch On Count
CIMWires | Switch | Switch | switchOnDate | switchOnDate | AbsoluteDateTime |  | cim | The date and time when the switch was last switched on. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch On Date
CIMWires | Switch | Switch | switchOperationOver | switchOperationOver | Boolean | FALSE | etx | Over Limit Violation Switch Operation (Open/Close). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch Operation Over
CIMWires | Switch | Switch | switchOperationUnder | switchOperationUnder | Boolean | FALSE | etx | Under Limit Violation Switch Operation (Open/Close). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch Operation Under
CIMWires | Switch | Switch | triggerNetworkSequence | triggerNetworkSequence | Boolean | FALSE | etx | T = The switch will trigger the real?time network application sequence when the switch changes state in SCADA. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Trigger Network Sequence
CIMWires | Switch | Switch | tripLockout | tripLockout | Boolean | FALSE | etx | Lockout after trip. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Trip Lockout
CIMWires | Switch | Switch | ZBR | ZBR | Boolean | FALSE | etx | Mark Switching devices that should be converted to Zero Impedance Branches in Connectivity Node to Bus Processing Option 1. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | Zero Impedance Branch?
CIMWires | SynchronousMachine | SynchronousMachine | aVRToManualLag | aVRToManualLag | Seconds |  | cim | Time delay, in seconds, required when switching from AVR to manual for a lagging MVAr violation. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | AVR to Manual Lag
CIMWires | SynchronousMachine | SynchronousMachine | aVRToManualLead | aVRToManualLead | Seconds |  | cim | Time delay, in seconds, required when switching from Automatic Voltage Regulation to Manual for a leading MVAr violation. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | AVR to Manual Lead
CIMWires | SynchronousMachine | SynchronousMachine | baseMVAr | baseMVAr | ReactivePower |  | cim | Default base MVAr value. This value represents the initial MVAr that can be used by any application function. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Base MVAr
CIMWires | SynchronousMachine | SynchronousMachine | condenserMW | condenserMW | ActivePower |  | cim | Condensor MW | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Condenser MW
CIMWires | SynchronousMachine | SynchronousMachine | coolantCondition | coolantCondition | Float |  | cim | Temperature or pressure of coolant medium. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Coolant Condition
CIMWires | SynchronousMachine | SynchronousMachine | coolantType | coolantType | EnumCoolantType |  | cim | Method of cooling the machine, e.g., air, hydrogen gas, water. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Coolant Type
CIMWires | SynchronousMachine | SynchronousMachine | damping | damping | Damping |  | cim | Damping torque coefficient, a proportionality constant that, when multiplied by the angular velocity of the rotor poles with respect to the magnetic field (frequency), results in the damping torque. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Damping
CIMWires | SynchronousMachine | SynchronousMachine | inertia | inertia | Inertia | 5 | cim | The energy stored in the rotor when operating at rated speed. This value is used in the accelerating power reference frame for operator training simulator solutions. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Inertia
CIMWires | SynchronousMachine | SynchronousMachine | manualToAVR | manualToAVR | Seconds |  | cim | Time delay, in seconds, required when switching from Manual to Automatic Voltage Regulation. This value is used in the accelerating power reference frame for powerflow solutions. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Manual to AVR
CIMWires | SynchronousMachine | SynchronousMachine | maximumKV | maximumKV | Voltage |  | cim | Maximum kV limit for the unit. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 1100 | 0 | Maximum KV
CIMWires | SynchronousMachine | SynchronousMachine | maximumMVAr | maximumMVAr | ReactivePower |  | cim | Maximum MVAr limit. This is the maximum (nameplate) limit for the unit. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MVAr
CIMWires | SynchronousMachine | SynchronousMachine | minimumKV | minimumKV | Voltage |  | cim | Minimum kV limit for the unit. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 1100 | 0 | Minimum KV
CIMWires | SynchronousMachine | SynchronousMachine | minimumMVAr | minimumMVAr | ReactivePower |  | cim | Minimum MVAr limit for the unit. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum MVAr
CIMWires | SynchronousMachine | SynchronousMachine | operatingMode | operatingMode | EnumSynchronousMachineOperatingMode |  | cim | Current mode of operation, i.e., generator or condenser. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Operating Mode
CIMWires | SynchronousMachine | SynchronousMachine | r | r | Resistance |  | cim | Positive sequence resistance of the synchronous machine. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | r
CIMWires | SynchronousMachine | SynchronousMachine | r0 | r0 | Resistance |  | cim | Zero sequence resistance of the synchronous machine. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | r0
CIMWires | SynchronousMachine | SynchronousMachine | ratedMVA | ratedMVA | ApparentPower |  | cim | Nameplate MVA rating for the unit. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Rated MVA
CIMWires | SynchronousMachine | SynchronousMachine | Reduce | Reduce | Boolean | FALSE | etx | Attribute will be used to mark generators on low voltage systems that should be reduced and attached directly to the Transmission Level. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | Reduce?
CIMWires | SynchronousMachine | SynchronousMachine | referencePriority | referencePriority | Integer |  | etx | Priority of unit for reference bus selection. 0 = don t care (default) 1 = highest priority. 2 is less than 1 and so on. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reference Priority
CIMWires | SynchronousMachine | SynchronousMachine | type | type | EnumSynchronousMachineType |  | cim | Modes that this synchronous machine can operate in, i.e., as a generator, condenser, or both. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Type
CIMWires | SynchronousMachine | SynchronousMachine | varManual | varManual | Boolean | FALSE | etx | Manually entered MVAR overrides capability curve. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | var Manual
CIMWires | SynchronousMachine | SynchronousMachine | x | x | Reactance | 0.12 | cim | Positive sequence reactance of the synchronous machine. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 500 | 0.001 | x
CIMWires | SynchronousMachine | SynchronousMachine | x0 | x0 | Reactance | 0.05 | cim | Zero sequence reactance of the synchronous machine. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 500 | 0.001 | x0
CIMWires | SynchronousMachine | SynchronousMachine | xDirectSubtrans | xDirectSubtrans | Reactance |  | cim | Direct-axis subtransient reactance, also known as X'd. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | X Direct Subtrans
CIMWires | SynchronousMachine | SynchronousMachine | xDirectSync | xDirectSync | Reactance |  | cim | Direct-axis synchronous reactance. The quotient of a sustained value of that AC component of armature voltage that is produced by the total direct-axis flux due to direct-axis armature current and the value of the AC component of this current, the machine running at rated speed. (Xd) | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | X Direct Sync
CIMWires | SynchronousMachine | SynchronousMachine | xDirectTrans | xDirectTrans | Reactance |  | cim | Direct-axis transient reactance, also known as X'd. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | X Direct Trans
CIMWires | SynchronousMachine | SynchronousMachine | xQuadSubtrans | xQuadSubtrans | Reactance |  | cim | Quadrature-axis subtransient reactance, also known as X'q. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | X Quad Subtrans
CIMWires | SynchronousMachine | SynchronousMachine | xQuadSync | xQuadSync | Reactance |  | cim | Quadrature-axis synchronous reactance (Xq) , the ratio of the component of reactive armature voltage, due to the quadrature-axis component of armature current, to this component of current, under steady state conditions and at rated frequency. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | X Quad Sync
CIMWires | SynchronousMachine | SynchronousMachine | xQuadTrans | xQuadTrans | Reactance |  | cim | Quadrature-axis transient reactance, also known as X'q. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | X Quad Trans
CIMWires | SynchronousMachine | SynchronousMachine | xSubtrans | xSubtrans | Reactance |  | etx | Subtransient reactance, also known as X''. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | x Direct Subtrans
CIMWires | SynchronousMachine | SynchronousMachine | xTrans | xTrans | Reactance |  | etx | Transient reactance, also known as X''. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | x Direct Trans
CIMWires | TapChanger | TapChanger | avrEnabled | avrEnabled | Boolean | FALSE | etx | T =Automatic Voltage Regulation is enabled. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | AVR Enabled
CIMWires | TapChanger | TapChanger | awrEnabled | awrEnabled | Boolean | FALSE | etx | T = automatic MW control is enabled. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | AWR Enabled
CIMWires | TapChanger | TapChanger | coupledToTransformer | coupledToTransformer | Boolean | FALSE | etx | T = indicates that the phase shifter is coupled to a transformer winding. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Coupled To Transformer
CIMWires | TapChanger | TapChanger | flowSensitivity | flowSensitivity | Float |  | etx | The sensitivity of the regulated MW flow to angle changes, in MW per degree. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Flow Sensitivity
CIMWires | TapChanger | TapChanger | highStep | highStep | TapStep | 0 | cim | Highest possible tap step position, advance from neutral. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 99 | 0 | High Step
CIMWires | TapChanger | TapChanger | InitialDelay | initialDelay | Seconds | 10 | cim | For an LTC, the delay for initial tap changer operation (first step change). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Initial Delay
CIMWires | TapChanger | TapChanger | loadBasedRegulationEnabled | loadBasedRegulationEnabled | Boolean | FALSE | etx | T = Load-Based Voltage Regulation is enabled. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Load-Based Regulation Enabled
CIMWires | TapChanger | TapChanger | lowStep | lowStep | TapStep | 0 | cim | Lowest possible tap step position, retard from neutral. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 99 | -99 | Low Step
CIMWires | TapChanger | TapChanger | maximumkV | maximumkV | Voltage |  | etx | The maximum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum kV
CIMWires | TapChanger | TapChanger | minimumkV | minimumkV | Voltage |  | etx | The minimum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum kV
CIMWires | TapChanger | TapChanger | neutralAngle | neutralAngle | AngleDegrees |  | etx | The CIM currently has no way of defining the angle associated with the neutral position of a TapChanger belonging to a phase shifter. Thus a neutralAngle attribute (measured in degrees) has been added to the TapChanger class. This attribute only appears in XML when the parent PowerTransformer is a phase shifter, i.e., when PowerTransformer.transformerType = 'phaseControl' or 'voltageAndPhaseControl'. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Neutral Angle
CIMWires | TapChanger | TapChanger | neutralKV | neutralKV | Voltage |  | cim | Voltage at which the winding operates at the neutral tap setting. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 1100 | 0 | Neutral KV
CIMWires | TapChanger | TapChanger | neutralStep | neutralStep | TapStep | 0 | cim | The neutral tap step position for this winding. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 99 | -99 | Neutral Step
CIMWires | TapChanger | TapChanger | normalStep | normalStep | TapStep | 0 | cim | The tap step position used in 'normal' network operation for this winding. For a 'Fixed' tap changer indicates the current physical tap setting. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 99 | -99 | Normal Step
CIMWires | TapChanger | TapChanger | parMaxMW | parMaxMW | ActivePower |  | etx | PAR maximum MW value (MW). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | PAR Maximum MW
CIMWires | TapChanger | TapChanger | parMinMW | parMinMW | ActivePower |  | etx | PAR minimum MW value (MW). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | PAR Minimum MW
CIMWires | TapChanger | TapChanger | parOptimization | parOptimization | Boolean | FALSE | etx | PAR optimization flag. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | PAR Optimization
CIMWires | TapChanger | TapChanger | parRampRate | parRampRate | ActivePower |  | etx | PAR optimiation ramp rate (MW per minute). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | PAR Ramp Rate
CIMWires | TapChanger | TapChanger | stepPhaseShiftIncrement | stepPhaseShiftIncrement | AngleDegrees |  | cim | Phase shift, in degrees, per step position. A positive value indicates a positive phase shift from the winding where the tap is located to the other winding (for a two-winding transformer), or to the ANDquot;TANDquot; point (for a three-winding transformer). | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Step Phase Shift Increment
CIMWires | TapChanger | TapChanger | stepVoltageIncrement | stepVoltageIncrement | PerCent | 0 | cim | Tap step increment, in per cent of nominal voltage, per step position. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Step Voltage Increment
CIMWires | TapChanger | TapChanger | SubsequentDelay | subsequentDelay | Seconds | 5 | cim | For an LTC, the delay for subsequent tap changer operation (second and later step changes). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Subsequent Delay
CIMWires | TapChanger | TapChanger | TculControlMode | tculControlMode | EnumTransformerControlMode |  | cim | For an LTC, the tap changer control mode, e.g.: Off, Local, Volt, MVAr. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | LTC Control Mode
CIMWires | TransformerWinding | TransformerWinding | b | b | Susceptance |  | cim | Magnetizing branch susceptance (B mag). | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 100 | -100 | b
CIMWires | TransformerWinding | TransformerWinding | bmagSat | bmagSat | Susceptance |  | etx | Shunt magnetizing susceptance in saturation region. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | bmag Sat
CIMWires | TransformerWinding | TransformerWinding | connectionType | connectionType | EnumWindingConnection | 1 | cim | The type of connection of the winding (e.g. Delta, Wye, zigzag). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Connection Type
CIMWires | TransformerWinding | TransformerWinding | emergencyMVA | emergencyMVA | ApparentPower | 99999 | cim | The MVA that the winding can carry under emergency conditions. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Emergency Rating
CIMWires | TransformerWinding | TransformerWinding | g | g | Conductance | 0 | cim | Magnetizing branch conductance (G mag). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999 | 0 | g
CIMWires | TransformerWinding | TransformerWinding | gmagSat | gmagSat | Conductance |  | etx | Shunt magnetizing conductance in saturation region. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | gmag Sat
CIMWires | TransformerWinding | TransformerWinding | grounded | grounded | Boolean | TRUE | cim | Set if the winding is grounded. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Grounded
CIMWires | TransformerWinding | TransformerWinding | insulationKV | insulationKV | Voltage |  | cim | Basic insulation level voltage rating. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Insulation kV
CIMWires | TransformerWinding | TransformerWinding | kneeSat | kneeSat | Float |  | etx | Agnetization curve saturation knee flux level (pu volts/pu hz) | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | knee Sat
CIMWires | TransformerWinding | TransformerWinding | r | r | Resistance |  | cim | Positive sequence series resistance of the winding. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 500 | 0 | r
CIMWires | TransformerWinding | TransformerWinding | r0 | r0 | Resistance |  | cim | Zero sequence series resistance of the winding. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 5000 | -5000 | r0
CIMWires | TransformerWinding | TransformerWinding | ratedKV | ratedKV | Voltage |  | cim | The rated voltage (phase-to-ground) of the winding, usually the same as the neutral voltage. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 1100 | 0.1 | Rated KV
CIMWires | TransformerWinding | TransformerWinding | ratedMVA | ratedMVA | ApparentPower | 99999 | cim | The normal rating, in MVA, for the winding. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  | 0 | Normal Rating
CIMWires | TransformerWinding | TransformerWinding | rground | rground | Resistance | 0 | cim | Ground resistance path through connected grounding transformer. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE | 10 | 0 | rground
CIMWires | TransformerWinding | TransformerWinding | shortTermMVA | shortTermMVA | ApparentPower | 99999 | cim | MVA that the winding can carry for a short period of time. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Short Term Rating
CIMWires | TransformerWinding | TransformerWinding | windingType | windingType | EnumWindingType |  | cim | The type of winding, i.e., Primary, Secondary, Tertiary, Quaternary. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Winding Type
CIMWires | TransformerWinding | TransformerWinding | x | x | Reactance |  | cim | Positive sequence series reactance of the winding. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 1000 | -1000 | x
CIMWires | TransformerWinding | TransformerWinding | x0 | x0 | Reactance |  | cim | Zero sequence series reactance of the winding. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 10000 | -10000 | x0
CIMWires | TransformerWinding | TransformerWinding | xground | xground | Reactance | 0 | cim | Ground reactance path through connected grounding transformer. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 9999 | 0 | x ground
CIMWires | WindingTest | WindingTest | excitingCurrent | excitingCurrent | ExcitingCurrent |  | cim | The exciting current % ('to' winding open-circuited) from the test report. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Exciting Current
CIMWires | WindingTest | WindingTest | fromTapStep | fromTapStep | TapStep |  | cim | The tap step number for the 'from' winding of the test pair. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | From Tap Step
CIMWires | WindingTest | WindingTest | leakageImpedance | leakageImpedance | Impedance |  | cim | The leakage impedance measured at the 'from' winding with the 'to' winding short-circuited and all other windings open-circuited. Leakage impedance is expressed in units based on the MVA and kV ratings of the 'from' winding. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Leakage Impedance
CIMWires | WindingTest | WindingTest | loadLoss | loadLoss | LoadLoss |  | cim | The load loss kW ('to' winding short-circuited) from the test report. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Loss
CIMWires | WindingTest | WindingTest | noLoadLoss | noLoadLoss | NoLoadLoss |  | cim | The no load loss kW 'to' winding open-circuited) from the test report. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | No Load Loss
CIMWires | WindingTest | WindingTest | phaseShift | phaseShift | AngleDegrees |  | cim | The phase shift measured at the open-circuited 'to' winding, with the 'from' winding set to the 'from' winding's rated voltage and all other windings open-circuited. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phase Shift
CIMWires | WindingTest | WindingTest | toTapStep | toTapStep | TapStep |  | cim | The tap step number for the 'to' winding of the test pair. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | To Tap Step
CIMWires | WindingTest | WindingTest | voltage | voltage | Voltage |  | cim | The voltage measured at the open-circuited 'to' winding, with the 'from' winding set to the 'from' winding's rated voltage and all other windings open-circuited. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Voltage
CIMWires | WireArrangement | WireArrangement | mountingPointX | mountingPointX | Integer |  | cim | Mounting point where wire One is mounted. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Mounting Point X
CIMWires | WireArrangement | WireArrangement | mountingPointY | mountingPointY | Integer |  | cim | Mounting point where wire Two is mounted. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Mounting Point Y
CIMWires | WireType | WireType | ampRating | ampRating | CurrentFlow |  | cim | Current carrying capacity, expressed in amperes, of a wire or cable under stated thermal conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Amp Rating
CIMWires | WireType | WireType | gMR | gMR | ShortLength |  | cim | Geometric Mean Radius. If we replace the conductor by a thin walled tube of radius GMR, then its reactance is identical to the reactance of the actual conductor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Geometric Mean Radius
CIMWires | WireType | WireType | phaseConductorCount | phaseConductorCount | Counter |  | cim | Number of conductor strands in the (symmetrical) bundle (1-12). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phase Conductor Count
CIMWires | WireType | WireType | phaseConductorSpacing | phaseConductorSpacing | ShortLength |  | cim | Distance between conductor strands in a (symmetrical) bundle (short length units). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Short Conductor Spacing
CIMWires | WireType | WireType | radius | radius | ShortLength |  | cim | The radius of the conductor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Radius
CIMWires | WireType | WireType | resistance | resistance | Resistance |  | cim | The resistance per unit length of the conductor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Resistance
EnergyScheduling | AreaReserveSpec | AreaReserveSpec | lowerRegMarginReqt | lowerRegMarginReqt | ActivePower | 20 | cim | Lower regulating margin requirement in MW, the amount of generation that can be dropped by control in 10 minutes | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Lower Reg Margin Reqt
EnergyScheduling | AreaReserveSpec | AreaReserveSpec | opReserveReqt | opReserveReqt | ActivePower | 500 | cim | Operating reserve requirement in MW, where operating reserve is the generating capability that is fully available within 30 minutes. Operating reserve is composed of primary reserve (t less than 10 min) and secondary reserve (10 less than t less than 30 min). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Op Reserve Reqt
EnergyScheduling | AreaReserveSpec | AreaReserveSpec | primaryReserveReqt | primaryReserveReqt | ActivePower | 40 | cim | Primary reserve requirement in MW, where primary reserve is generating capability that is fully available within 10 minutes. Primary reserve is composed of spinning reserve and quick-start reserve. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Primary Reserve Reqt
EnergyScheduling | AreaReserveSpec | AreaReserveSpec | raiseRegMarginReqt | raiseRegMarginReqt | ActivePower | 20 | cim | Raise regulating margin requirement in MW, the amount of generation that can be picked up by control in 10 minutes | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Raise Reg Margin Reqt
EnergyScheduling | AreaReserveSpec | AreaReserveSpec | spinningReserveReqt | spinningReserveReqt | ActivePower | 200 | cim | Spinning reserve requirement in MW, spinning reserve is generating capability that is presently synchronized to the network and is fully available within 10 minutes | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Spinning Reserve Reqt
EnergyScheduling | EnergyTransaction | EnergyTransaction | congestChargeMax | congestChargeMax | Money |  | cim | Maximum congestion charges in monetary units. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Congestion Charge Maximum
EnergyScheduling | EnergyTransaction | EnergyTransaction | deliveryPointMW | deliveryPointMW | ActivePower |  | cim | Delivery point typically expressed in MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Delivery Point MW
EnergyScheduling | EnergyTransaction | EnergyTransaction | energyMin | energyMin | ActivePower |  | cim | Transaction minimum MW if dispatchable. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Energy Min
EnergyScheduling | EnergyTransaction | EnergyTransaction | firmInterchangeFlag | firmInterchangeFlag | Boolean | FALSE | cim | Firm interchange flag indicates whether or not this energy transaction can be changed without potential financial consequences. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Firm Interchange Flag
EnergyScheduling | EnergyTransaction | EnergyTransaction | reason | reason | String100 |  | cim | Additional information is not available. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reason
EnergyScheduling | EnergyTransaction | EnergyTransaction | receiptPointMW | receiptPointMW | ActivePower |  | cim | Receipt point typically expressed in MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Receipt Point MW
EnergyScheduling | HostControlArea | HostControlArea | AreaControlMode | areaControlMode | EnumAreaControlModel | 0 | cim | The area's present control mode: (CF = constant frequency) or (CTL = constant tie-line) or (TLB = tie-line bias) or (OFF = off control) | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Area Control Mode
EnergyScheduling | HostControlArea | HostControlArea | assistEmergencyPriorityLevel | assistEmergencyPriorityLevel | Integer |  | etx | Assist Threshold. When the ACE is in emergency region, then all the units up to this Pritority level will have the desired priority level =1. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Assist Emergency Priority Level
EnergyScheduling | HostControlArea | HostControlArea | assistPriorityLevel | assistPriorityLevel | Integer |  | etx | Assist Threshold. When the ACE is in assist region, then all the units up to this Priority level will have the desired priority level =1. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Assist Priority Level
EnergyScheduling | HostControlArea | HostControlArea | balanceRampEnd | balanceRampEnd | Float |  | etx | Number of minutes into the period to end the balancing energy schedule ramp. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Balance Ramp End
EnergyScheduling | HostControlArea | HostControlArea | balanceRampStart | balanceRampStart | Float |  | etx | Number of minutes before the end of the period to start the balancing energy schedule ramp. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Balance Ramp Start
EnergyScheduling | HostControlArea | HostControlArea | costCO2 | costCO2 | Float |  | etx | Cost of CO2 in objective (Cost/UnitsCO2). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cost CO2
EnergyScheduling | HostControlArea | HostControlArea | costNOX | costNOX | Float |  | etx | Cost of NOX in objective (Cost/UnitsCO2). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cost NOX
EnergyScheduling | HostControlArea | HostControlArea | costSO2 | costSO2 | Float |  | etx | Cost of SO2 in objective (Cost/UnitsCO2). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cost SO2
EnergyScheduling | HostControlArea | HostControlArea | cycleTimeMultiplier | cycleTimeMultiplier | Integer |  | etx | AGC CONTROL CYCLE MULTIPLIER (AGC ONLY). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | cycle Time Multiplier
EnergyScheduling | HostControlArea | HostControlArea | deadbandAlarmACE | deadbandAlarmACE | Float |  | etx | ACE ALARM DEADBAND (EG: 2 MW). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Alarm ACE
EnergyScheduling | HostControlArea | HostControlArea | deadbandAutoInadvertent | deadbandAutoInadvertent | Integer |  | etx | DEADBAND FOR AUTOMATIC INADVERTENT (PEAK AND OFFPEAK) IN MWHR IF INADVERTENT VALUE IS WITHIN THIS DEADBAND AUTO PAYBACK IS DISABLED | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Auto Inadvertent
EnergyScheduling | HostControlArea | HostControlArea | deadbandFreqWarningAlarm | deadbandFrequencyWarningAlarm | Float |  | etx | DEADBAND ON WARNING ALARM THRESHOLD ON FREQUENCY (E.G. 0.05 HZ) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Frequency Warning Alarm
EnergyScheduling | HostControlArea | HostControlArea | deadbandIntegratedSCEAlarm | deadbandIntegratedSCEAlarm | Float |  | etx | INTEGRATED SCE ALARM DEADBAND. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Integrated SCE Alarm
EnergyScheduling | HostControlArea | HostControlArea | deadbandMultiplerNotTracking | deadbandMultiplerNotTracking | Float |  | etx | NOT TRACKING DEADBAND MULTIPLIER (EG: 2) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Multiplier Not Tracking
EnergyScheduling | HostControlArea | HostControlArea | deadbandNormalResponseACE | deadbandNormalResponseACE | Integer |  | etx | ACE DEADBAND; ACE LIMIT FOR NORMAL RESPONSE (EG: 5 MW) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Normal Response ACE
EnergyScheduling | HostControlArea | HostControlArea | deadbandPercentOpRsrvAlarm | deadbandPercentOpReserveAlarm | Integer |  | etx | OPERATING RESERVE ALARM DEADBAND (PERCENT OF OPER RESERVE REQUIREMENT) (EG: 5% ) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Percent Op Reserve Alarm
EnergyScheduling | HostControlArea | HostControlArea | deadbandPercentRegRsrvAlarm | deadbandPercentRegReserveAlarm | Integer |  | etx | REGULATING RESERVE ALARM DEADBAND (PERCENT OF REG RESERVE REQUIREMENT) (EG: 5% ) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Percent Reg Reserve Alarm
EnergyScheduling | HostControlArea | HostControlArea | deadbandPercentSpinRsrvAlarm | deadbandPercentSpinReserveAlarm | Integer |  | etx | SPINNING RESERVE ALARM DEADBAND (PERCENT OF ALARM LIMIT) (AGC ONLY) (EG: 5% ). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Percent Spin Reserve Alarm
EnergyScheduling | HostControlArea | HostControlArea | deadbandPercentTieLimitAlarm | deadbandPercentTieLimitAlarm | Float |  | etx | TIE LINE FLOW LIMIT ALARMS DEADBAND (% OF LIMIT) (EG: 1%) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Percent Tie Limit Alarm
EnergyScheduling | HostControlArea | HostControlArea | deadbandPercentTimeError | deadbandPercentTimeError | Integer |  | etx | TIME ERROR DEADBAND (PERCENT OF ALARM LIMIT) (EG:5%). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Percent Time Error
EnergyScheduling | HostControlArea | HostControlArea | deadbandVariableMaximum | deadbandVariableMaximum | Float |  | etx | High limit for the deadband variable (scalar). Used in the variable frequency bias calculation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Variable Maximum
EnergyScheduling | HostControlArea | HostControlArea | deadbandVariableMinimum | deadbandVariableMinimum | Float |  | etx | Low limit for the deadband variable (scalar). Used in the variable frequency bias calculation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Variable Minimum
EnergyScheduling | HostControlArea | HostControlArea | defaultLoadRelief | defaultLoadRelief | Float |  | etx | The percentage of the breakpoint's control area load MW value to use as the default for the breakpoint's load relief value if that value is null. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Default Load Relief
EnergyScheduling | HostControlArea | HostControlArea | deltaTime | deltaTime | Integer |  | etx | TIME DIFFERENCE BETWEEN EMS TIME ZONE AND REPORTING TIME ZONE. WHEN DELTA-TIME IS ADDED TO THE TIME IN THE EMS TIME ZONE, THE RESULT SHOULD BE THE CURRENT TIME IN THE REPORTING TIME ZONE. (Units?) | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Delta Time
EnergyScheduling | HostControlArea | HostControlArea | deployFreqThreshold | deployFreqThreshold | Float |  | etx | Deploy frequency threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Deploy Frequency Threshold
EnergyScheduling | HostControlArea | HostControlArea | filterTimeConstantJointACE | filterTimeConstantJointACE | Float |  | etx | Joint AGC ACE request filter time constant. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Filter Time Constant Joint ACE
EnergyScheduling | HostControlArea | HostControlArea | forGeneration | forGeneration | Bool | FALSE | etx | HostControlArea belongs to Generation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | for Generation
EnergyScheduling | HostControlArea | HostControlArea | forNetwork | forNetwork | Bool | FALSE | etx | HostControlArea Belongs to Network. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | for Network
EnergyScheduling | HostControlArea | HostControlArea | frequencyAlarmThreshold | frequencyAlarmThreshold | Float |  | etx | WARNING ALARM THRESHOLD ON FREQUENCY (E.G. 0.2 HZ) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Alarm Threshold
EnergyScheduling | HostControlArea | HostControlArea | frequencyBiasFactor | frequencyBiasFactor | Float |  | etx | AREA LOAD BIAS -LOAD FREQUENCY SENSITIVITY- (MW/0.1HZ) (EG: 0.2% AREA CAP). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Bias Factor
EnergyScheduling | HostControlArea | HostControlArea | frequencyBiasFactorManual | frequencyBiasFactorManual | Float |  | etx | Manually entered frequency bias in MW/0.1 Hz. Equal to FBIAS_OPA if manual entry of frequency bias is selected, otherwise it contains the most recent manually entered value of frequency bias. Modifiable online. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Bias Factor Manual
EnergyScheduling | HostControlArea | HostControlArea | frequencyNominalMaximum | frequencyNominalMaximum | Float |  | etx | SCHEDULED AREA FREQUENCY MAXIMUM (IN HZ; DEFAULT VALUE - 62 HZ). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Nominal Maximum
EnergyScheduling | HostControlArea | HostControlArea | frequencyNominalMinimum | frequencyNominalMinimum | Float |  | etx | SCHEDULED AREA FREQUENCY MINIMUM (IN HZ; DEFAULT VALUE - 58 HZ). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Nominal Minimum
EnergyScheduling | HostControlArea | HostControlArea | frequencyTrip | frequencyTrip | Float |  | etx | FREQUENCY OFFSET TO TRIP AGC OFF AND CREATE AGC CONTROL ALARM (E.G. 0.45 HZ) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Trip
EnergyScheduling | HostControlArea | HostControlArea | gainAssist | gainAssist | Float |  | etx | ASSIST GAIN ON ACE (EG: 3.0) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gain Assist
EnergyScheduling | HostControlArea | HostControlArea | gainEmergency | gainEmergency | Float |  | etx | EMERGENCY GAIN ON ACE. (EG: 10.0) (AGC ONLY) | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | gainEmergency
EnergyScheduling | HostControlArea | HostControlArea | gainEmergencyIntegral | gainEmergencyIntegral | Float |  | etx | EMERGENCY GAIN ON INTEGRAL ACE. (EG: 0.6) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gain Emergency Integral
EnergyScheduling | HostControlArea | HostControlArea | gainIntegralAssist | gainIntegralAssist | Float |  | etx | ASSIST GAIN ON INTEGRAL ACE. (EG: 0.4) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gain Integral Assist
EnergyScheduling | HostControlArea | HostControlArea | gainJointAGCPersistFeeback | gainJointAGCPersistancyFeeback | Float |  | etx | Joint agc persistency feedback gain. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gain Joint AGC Persistancy Feeback
EnergyScheduling | HostControlArea | HostControlArea | gainNominal | gainNominal | Float |  | etx | NOMINAL GAIN ON ACE (NORMAL REGULATING RESPONSE) (EG: 1.4) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gain Nominal
EnergyScheduling | HostControlArea | HostControlArea | gainNominalIntegral | gainNominalIntegral | Float |  | etx | NOMINAL GAIN ON INTEGRAL ACE. (EG: 0.1) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gain Nominal Integral
EnergyScheduling | HostControlArea | HostControlArea | governorResponseDeadband | governorResponseDeadband | Float |  | etx | Expected governor response frequency deviation deadband. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Governor Response Deadband
EnergyScheduling | HostControlArea | HostControlArea | internal | internal | Boolean | FALSE | etx | The MMS applications require that one of the HostControlAreas defined in the model be designated as the 'main' company. ERCOT may also opt for the decomposition of the model into areas, which requires an indication of which HostControlAreas are 'internal'. Note that the main designation is not necessarily synonymous with the internal designation since it is possible to have multiple internal HostControlAreas but only one main HostControlArea. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | internal
EnergyScheduling | HostControlArea | HostControlArea | jointAGCStallMW | jointAGCStallMW | Float |  | etx | Joint agc regulation MW amount that'll be issued at detected stall of ACE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Joint AGC Stall MW
EnergyScheduling | HostControlArea | HostControlArea | lamdaDeadband | lamdaDeadband | Float |  | etx | LAMBDA DEADBAND TO BE USED FOR PAYBACK OF INADVERTENT ACCUMULATION IN | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Lamda Deadband
EnergyScheduling | HostControlArea | HostControlArea | limitAssistResponseACE | limitAssistResponseACE | Integer |  | etx | ACE LIMIT FOR ASSIST RESPONSE (EG: 20 MW) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Limit Assist Response ACE
EnergyScheduling | HostControlArea | HostControlArea | limitEmergencyResponseACE | limitEmergencyResponseACE | Integer |  | etx | ACE LIMIT FOR EMERGENCY ASSIST RESPONSE (EG: 40 MW) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Limit Emergency Response ACE
EnergyScheduling | HostControlArea | HostControlArea | limitNonWindupIntegralACE | limitNonWindupIntegralACE | Integer |  | etx | NON-WINDUP LIMIT ON INTEGRAL OF ACE (MW-HR). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Limit Non-Windup Integral ACE
EnergyScheduling | HostControlArea | HostControlArea | loadReliefFirstMW | loadReliefFirstMW | Float |  | etx | The control area load MW value for the first breakpoint in the load relief table. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Relief First MW
EnergyScheduling | HostControlArea | HostControlArea | loadReliefLastMW | loadReliefLastMW | Float |  | etx | The control area load MW value for the last breakpoint in the load relief table. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Relief Last MW
EnergyScheduling | HostControlArea | HostControlArea | main | main | Boolean | FALSE | etx | The MMS applications require that one of the HostControlAreas defined in the model be designated as the 'main' company. ERCOT may also opt for the decomposition of the model into areas, which requires an indication of which HostControlAreas are 'internal'. Note that the main designation is not necessarily synonymous with the internal designation since it is possible to have multiple internal HostControlAreas but only one main HostControlArea. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | main
EnergyScheduling | HostControlArea | HostControlArea | maxAutoInadvertentPayback | maximumAutoInadvertentPayback | Float |  | etx | MAXIMUM VALUE OF AUTOMATIC INADVERTENT PAYBACK PERMITTED PER CYCLE IN MW/AGC-CYCLE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Auto Inadvertent Payback
EnergyScheduling | HostControlArea | HostControlArea | maximumInterchangeLossModel | maximumInterchangeLossModel | Float |  | etx | MAXIMUM INTERCHANGE FOR BOUNDARY DEFINITION FOR BINS FOR LOSS MODELLING.USED IN GENMODEL. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Interchange Loss Model
EnergyScheduling | HostControlArea | HostControlArea | maximumInterchangeSchedule | maximumInterchangeSchedule | Float |  | etx | MAX. INTERCHANGE SCHEDULE MW ALLOWED BEFORE ALARM IS ISSUED (AGC ONLY) (EG: 2000 MW) | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Interchange Schedule
EnergyScheduling | HostControlArea | HostControlArea | maxInterruptableLoadReserve | maximumInterruptableLoadReserve | Float |  | etx | Maximum interruptable load contribution to spinning or operating reserve. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Interruptable Load Reserve
EnergyScheduling | HostControlArea | HostControlArea | maximumJointACE | maximumJointACE | Float |  | etx | Maximum value of ACE before the request percentage is applied. The request percentage is only applied to the incremental value of ACE above this threshold. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Joint ACE
EnergyScheduling | HostControlArea | HostControlArea | maximumLoadLossModel | maximumLoadLossModel | Float |  | etx | MAXIMUM LOAD FOR BOUNDARY DEFINITION FOR BINS FOR LOSS MODELLING.USED IN GENMODEL. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Load Loss Model
EnergyScheduling | HostControlArea | HostControlArea | maximumMiscReserve | maximumMiscReserve | Integer |  | etx | Maximum miscellaneous reserve contribution. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Misc Reserve
EnergyScheduling | HostControlArea | HostControlArea | maximumObligationExportMW | maximumObligationExportMW | Float |  | etx | Maximum obligation Mw (Export) value used in the Target MW calculation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Obligation Export MW
EnergyScheduling | HostControlArea | HostControlArea | maximumObligationImportMW | maximumObligationImportMW | Float |  | etx | Maximum obligation Mw (Import) value used in the Target MW calculation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Obligation Import MW
EnergyScheduling | HostControlArea | HostControlArea | maximumTripACE | maximumTripACE | Integer |  | etx | VALUE OF ACE ABOVE WHICH AGC WILL PAUSE. VALUE MUST BE GREATER THAN OR EQUAL TO ACEALM_OPA, OR LESS THAN ZERO | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Trip ACE
EnergyScheduling | HostControlArea | HostControlArea | minimumInterchangeLossModel | minimumInterchangeLossModel | Float |  | etx | MINIMUM INTERCHANGE FOR BOUNDARY DEFINITION FOR BINS FOR LOSS MODELLING.USED IN GENMODEL. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Interchange Loss Model
EnergyScheduling | HostControlArea | HostControlArea | minimumJointACE | minimumJointACE | Float |  | etx | Minimum value of ACE before the request percentage is applied. The request percentage is only applied to the incremental value of ACE above this threshold. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Joint ACE
EnergyScheduling | HostControlArea | HostControlArea | minimumLoadLossModel | minimumLoadLossModel | Float |  | etx | MINIMUM LOAD FOR BOUNDARY DEFINITION FOR THE BINS FOR LOSS MODELLING USED IN SETTING UP BOUNDARIES IN GENMODEL. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Load Loss Model
EnergyScheduling | HostControlArea | HostControlArea | minimumPermissiveACE | minimumPermissiveACE | Integer |  | etx | MINIMUM ACE LEVEL FOR PERMISSIVE CONTROL (MW) (EG: 35 MW). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Permissive ACE
EnergyScheduling | HostControlArea | HostControlArea | minimumResponseRateAlarm | minimumResponseRateAlarm | Float |  | etx | MIN RESPONSE RATE ALARM LEVEL (MW/MIN) (EG: 0.10% AREA CAP) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Response Rate Alarm
EnergyScheduling | HostControlArea | HostControlArea | minutesFutureAdvisoryED | minutesFutureAdvisoryED | Float |  | etx | The number of minutes in the future to evaluate the load and transaction schedules at for the Advisory ED. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minutes Future Advisory ED
EnergyScheduling | HostControlArea | HostControlArea | minutesOperatingReserve | minutesOperatingReserve | Float |  | etx | Time period (in minutes) in which a unit's output can change to contribute to operating reserves. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minutes Operating Reserve
EnergyScheduling | HostControlArea | HostControlArea | minutesPendingFreqSchedule | minutesPendingFrequencySchedule | Float |  | etx | MINUTES FOR SENDING PENDING FREQUENCY SCHEDULE MESSAGE. (EG: 5 MIN). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minutes Pending Frequency Schedule
EnergyScheduling | HostControlArea | HostControlArea | minutesRegulatingReserve | minutesRegulatingReserve | Float |  | etx | Time period (in minutes) in which a unit's output can change to contribute to regulating reserves. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minutes Regulating Reserve
EnergyScheduling | HostControlArea | HostControlArea | minutesSpinningReserve | minutesSpinningReserve | Integer |  | etx | Time period (in minutes) in which a unit's output can change to contribute to spinning reserves. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minutes Spinning Reserve
EnergyScheduling | HostControlArea | HostControlArea | percentCapOpRsrvReqDefault | percentCapOpReserveReqDefault | Float |  | etx | AREA REGULATING RESERVE REQUIREMENT (MW) (EG: 3% AREA CAP) (AGC ONLY) INITIAL DEFAULT VALUE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Cap Op Reserve Req Default
EnergyScheduling | HostControlArea | HostControlArea | percentCapOpRsrvRequirement | percentCapOpReserveRequirement | Integer |  | etx | AREA OPERATING RESERVE REQUIREMENT (MW) (EG 8% AREA CAP) (AGC ONLY) INITIAL DEFAULT VALUE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Cap Op Reserve Requirement
EnergyScheduling | HostControlArea | HostControlArea | percentCapSpinRsrvReqDefault | percentCapSpinReserveReqDefault | Float |  | etx | AN EXCESSIVE ALARM WILL BE ISSUED IF THE INTEGRATED SCE EXCEEDS THIS THRESHOLD. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Cap Spin Reserve Req Default
EnergyScheduling | HostControlArea | HostControlArea | percentCapSpinRsrvReq | percentCapSpinReserveRequirement | Float |  | etx | SPINNING RESERVE REQUIREMENT (MW) (EG: 5% AREA CAP) (AGC ONLY) INITIAL DEFAULT VALUE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Cap Spin Reserve Requirement
EnergyScheduling | HostControlArea | HostControlArea | percentFrequencyBias | percentFrequencyBias | PerCent |  | etx | Percentage of frequency bias. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Frequency Bias
EnergyScheduling | HostControlArea | HostControlArea | percentIntegrationMissing | percentIntegrationMissing | Float |  | etx | percent threshold of missing samples in a regulation integration interval, if more than this percent samples are missing, quality (TRINBAD) for the interval’s integration will be declared 'bad' . | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Integration Missing
EnergyScheduling | HostControlArea | HostControlArea | percentJointAGCRequest | percentJointAGCRequest | Float |  | etx | Percentage of area ACE that requester area is asking from other area. This is enterable on the joint AGC display for requester area. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Joint AGC Request
EnergyScheduling | HostControlArea | HostControlArea | percentMWStepChangeAlarm | percentMWStepChangeAlarm | Float |  | etx | UNIT MW STEP CHANGE ALARM LEVEL (% OF UNIT CAPACITY) (EG:10%)(AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent MW Step Change Alarm
EnergyScheduling | HostControlArea | HostControlArea | percentObjectCO2 | percentObjectCO2 | Float |  | etx | Weighting factor for CO2 in Emissions Reduction Objective. Has range from 0 to 100%. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | percentObjectiveCO2
EnergyScheduling | HostControlArea | HostControlArea | percentObjectiveFuel | percentObjectiveFuel | Float |  | etx | Weighting factor for fuel in Emissions Reduction Objective. Has range from 0 to 100%. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Percent Objective Fuel
EnergyScheduling | HostControlArea | HostControlArea | percentObjectiveNOX | percentObjectiveNOX | Float |  | etx | Weighting factor for NOX in Emissions Reduction Objective. Has range from 0 to 100%. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Percent Objective NOX
EnergyScheduling | HostControlArea | HostControlArea | percentObjectiveSO2 | percentObjectiveSO2 | Float |  | etx | Weighting factor for SO2 in Emissions Reduction Objective. Has range from 0 to 100%. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Percent Objective SO2
EnergyScheduling | HostControlArea | HostControlArea | percentUnitNotTrackingAlarm | percentUnitNotTrackingAlarm | Float |  | etx | UNIT NOT TRACKING ALARM LEVEL (PERCENT OF EQUIVALENT MSR) (AGC ONLY) (EG: 20% ). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Unit Not Tracking Alarm
EnergyScheduling | HostControlArea | HostControlArea | rampDurationToStop | rampDurationToStop | Float |  | etx | RSG Ramp duration to stop time. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Ramp Duration To Stop
EnergyScheduling | HostControlArea | HostControlArea | rampDurationToTarget | rampDurationToTarget | Float |  | etx | RSG Ramp duration to target in Minutes. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Ramp Duration To Target
EnergyScheduling | HostControlArea | HostControlArea | scedFailureThreshold | scedFailureThreshold | Integer |  | etx | SCED failure threshold in seconds. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | SCED Failure Threshold
EnergyScheduling | HostControlArea | HostControlArea | secondsAGCCycle | secondsAGCCycle | Integer |  | etx | AGC CYCLE PERIOD IN SECONDS (EG: 4 SEC) (AGC ONLY) MUST BE AN INTEGER MULTIPLE OF THE CORRESPONDING SCADA SCAN PERIOD. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds AGC Cycle
EnergyScheduling | HostControlArea | HostControlArea | secondsAGCOff | secondsAGCOff | Float |  | etx | AGC WILL START CYCLING THIS MANY SECONDS AFTER INITIALIZATION. (EG: 0 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds AGC Off
EnergyScheduling | HostControlArea | HostControlArea | secondsAlarmResponse | secondsAlarmResponse | Float |  | etx | NOM TIME TO REPEAT ALARM INSUFFICIENT AREA RESPONSE CAPABILITY (SEC) (EG: 600 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Alarm Response
EnergyScheduling | HostControlArea | HostControlArea | secondsControlEcoDispatch | secondsControlEcoDispatch | Float |  | etx | NOMINAL CONTROL ED RATE (SEC) (EG: 300 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Control Eco Dispatch
EnergyScheduling | HostControlArea | HostControlArea | secondsDeadbandDynamicACE | secondsDeadbandDynamicACE | Integer |  | etx | DYNAMIC ACE DEADBAND TIME CONSTANT (AGC ONLY) (EG: 4 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Deadband Dynamic ACE
EnergyScheduling | HostControlArea | HostControlArea | secondsDeadbandTimeError | secondsDeadbandTimeError | Float |  | etx | The auto time error correction deadband (SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Deadband Time Error
EnergyScheduling | HostControlArea | HostControlArea | secondsEmergencyDisableJoint | secondsEmergencyDisableJoint | Float |  | etx | Number of seconds ACE can be in emergency region before joint AGC is disabled for all TIEs. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Emergency Disable Joint
EnergyScheduling | HostControlArea | HostControlArea | secondsEvaluateLossModel | secondsEvaluateLossModel | Float |  | etx | IT IS THE NOMINAL TIME BETWEEN RE-EVALUATIONS OF PENALTY FACTORS FROM HISTORICAL LOSS MODEL IF RTNET HAS NOT EXECUTED. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Evaluate Loss Model
EnergyScheduling | HostControlArea | HostControlArea | secondsJointAGCStall | secondsJointAGCStall | Float |  | etx | Joint agc ACE stall check time threshold (in seconds). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Joint AGC Stall
EnergyScheduling | HostControlArea | HostControlArea | secondsMaximumTimeCorrection | secondsMaximumTimeCorrection | Float |  | etx | The maximum amount of auto time error correction allowed (SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Maximum Time Correction
EnergyScheduling | HostControlArea | HostControlArea | secondsMinimumEcoDispatch | secondsMinimumEcoDispatch | Float |  | etx | MINIMUM TIME PERIOD ALLOWED BETWEEN ECONOMIC DISPATCH EXECUTIONS.(AGC) (EG: 10 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Minimum Eco Dispatch
EnergyScheduling | HostControlArea | HostControlArea | secondsMinStudyEcoDispatch | secondsMinimumStudyEcoDispatch | Float |  | etx | MINIMUM TIME BETWEEN STUDY ED EXECUTIONS (SEC) (EG: 20 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Minimum Study Eco Dispatch
EnergyScheduling | HostControlArea | HostControlArea | secondsPauseThenSuspend | secondsPauseThenSuspend | Integer |  | etx | NOMINAL TIME FOR AGC PAUSE BEFORE SUSPEND IF NECESSARY (EG: 20 SEC). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Pause Then Suspend
EnergyScheduling | HostControlArea | HostControlArea | secondsPrediction | secondsPrediction | Float |  | etx | PREDICTED TIME IN SEC FROM TNOW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Prediction
EnergyScheduling | HostControlArea | HostControlArea | secondsProductionCosting | secondsProductionCosting | Float |  | etx | nominal value for the periodicity of the production costing module in seconds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Production Costing
EnergyScheduling | HostControlArea | HostControlArea | secondsRegulationAllocation | secondsRegulationAllocation | Float |  | etx | Regulation Allocation limit period (in sec). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Reulation Allocation
EnergyScheduling | HostControlArea | HostControlArea | secondsReserveCalculations | secondsReserveCalculations | Integer |  | etx | NOMINAL TIME TO PERFORM RESERVE CALCULATIONS (SEC) (AGC ONLY) (EG: 20 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Reserve Calculations
EnergyScheduling | HostControlArea | HostControlArea | secondsStudyEcoDispatch | secondsStudyEcoDispatch | Float |  | etx | NOMINAL STUDY ED RATE (SEC) (EG: 600 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Study Eco Dispatch
EnergyScheduling | HostControlArea | HostControlArea | secondsTimeErrorAlarm | secondsTimeErrorAlarm | Float |  | etx | TIME ERROR ALARM LIMIT IN SECONDS (EG: 2 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Time Error Alarm
EnergyScheduling | HostControlArea | HostControlArea | secondsUnitNotTrackingTest | secondsUnitNotTrackingTest | Float |  | etx | NOM TIME TO RUN UNIT NOT TRACKING TEST (SEC) (AGC ONLY) (EG: 120 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Unit Not Tracking Test
EnergyScheduling | HostControlArea | HostControlArea | secondsZeroAssist | secondsZeroAssist | Float |  | etx | THRESHOLD TIME FOR ASSIST REGION IN SECONDS SINCE LAST ZERO CROSSING. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Zero Assist
EnergyScheduling | HostControlArea | HostControlArea | secondsZeroEmergency | secondsZeroEmergency | Float |  | etx | THRESHOLD TIME FOR EMERGENCY REGION IN SECONDS SINCE LAST ZERO CROSSING. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Zero Emergency
EnergyScheduling | HostControlArea | HostControlArea | secondsZeroNormal | secondsZeroNormal | Float |  | etx | THRESHOLD TIME FOR NORMAL REGION IN SECONDS SINCE LAST ZERO CROSSING. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Zero Normal
EnergyScheduling | HostControlArea | HostControlArea | tauFilterLoad | tauFilterLoad | Float |  | etx | TIME CONSTANT FOR FILTERING LOAD (SECS). (EG: 40 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tau Filter Load
EnergyScheduling | HostControlArea | HostControlArea | tauFrequency | tauFrequency | Float |  | etx | AREA FREQUENCY TIME CONSTANT (SECS) (EG: 10 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tau Frequency
EnergyScheduling | HostControlArea | HostControlArea | tauLongTerm | tauLongTerm | Float |  | etx | UNIT LONG TERM ACCOUNT (PULSE CALIBRATION) TIME CONSTANT (SEC) (AGC) (EG: CORRESP TO 1 DAY = 24*3600 = 86400 SEC). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tau Long Term
EnergyScheduling | HostControlArea | HostControlArea | tauRegulating | tauRegulating | Float |  | etx | REGULATING (AREA CONTROL) TIME CONSTANT (SEC) (E.G. 30 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tau Regulating
EnergyScheduling | HostControlArea | HostControlArea | tauShortTerm | tauShortTerm | Float |  | etx | UNIT SHORT TERM ACCOUNT (NOT TRACKING TEST) TIME CONSTANT (SEC) (AGC) (EG: 300 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tau Short Term
EnergyScheduling | HostControlArea | HostControlArea | timeErrorBias | timeErrorBias | Float |  | etx | (HZ/SEC) ACE EQUATION VARIABLE LITTLE B: AUTOMATIC TIME ERROR CORRECTION BIAS VALUE. * ENTER ABSOLUTE VALUE: NEGATION DONE IN THE CODE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time Error Bias
EnergyScheduling | HostControlArea | HostControlArea | triggerControlEcoDispatchMW | triggerControlEcoDispatchMW | Float |  | etx | MW CHANGE TO TRIGGER CONTROL ED EXECUTION (EG: 25MW) (AGC ONLY) | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Trigger Control Eco Dispatch MW
EnergyScheduling | HostControlArea | HostControlArea | triggerStudyEcoDispatchMW | triggerStudyEcoDispatchMW | Float |  | etx | MW CHANGE TO TRIGGER STUDY ED EXECUTION (EG: 50MW) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Trigger Study Eco Dispatch MW
EnergyScheduling | HostControlArea | HostControlArea | variableFrequencyBiasMaximum | variableFrequencyBiasMaximum | Float |  | etx | Variable frequency bias high limit in MW/0.1 Hz. Must be greater or equal to VFBMIN_OPA. Enterable offline. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Variable Frequency Bias Maximum
EnergyScheduling | HostControlArea | HostControlArea | variableFrequencyBiasMinimum | variableFrequencyBiasMinimum | Float |  | etx | Variable frequency bias low limit in MW/0.1 Hz. Must be less or equal to VFBMAX_OPA. Enterable offline. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Variable Frequency Bias Minimum
ETX | Address | Address | City | City | String500 |  | etx | City | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | City
ETX | Address | Address | County | County | String500 |  | etx | County | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | County
ETX | Address | Address | PostalCode | PostalCode | String500 |  | etx | Postal Code | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Postal Code
ETX | Address | Address | State | State | String500 |  | etx | State | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | State
ETX | Address | Address | Street1 | Street1 | String500 |  | etx | Street | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Street 1
ETX | Address | Address | Street2 | Street2 | String500 |  | etx | Street continued | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Street 2
ETX | AggregateHub | AggregateHub | hubCalculationMethod | hubCalculationMethod | EnumHubCalcType |  | etx | Hub calculation method. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Hub Calculation Method
ETX | AncillaryQualification | AncillaryQualification | blackStart | blackStart | Boolean | FALSE | etx | Black start.. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Black Start
ETX | AncillaryQualification | AncillaryQualification | blackStartEffectiveDate | blackStartEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (black start)
ETX | AncillaryQualification | AncillaryQualification | blackStartEndDate | blackStartEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (black start)
ETX | AncillaryQualification | AncillaryQualification | ccEffectiveDate | ccEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (condensor capable)
ETX | AncillaryQualification | AncillaryQualification | ccEndDate | ccEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (condensor capabile)
ETX | AncillaryQualification | AncillaryQualification | condensorCapable | condensorCapable | Boolean | FALSE | etx | Condensor capable. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Condensor Capable
ETX | AncillaryQualification | AncillaryQualification | dynamicSched | dynamicSched | Boolean | FALSE | etx | Dynamic scheduled. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Dynamic Scheduled
ETX | AncillaryQualification | AncillaryQualification | dynamicSchedEffectiveDate | dynamicSchedEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (dynamic sched)
ETX | AncillaryQualification | AncillaryQualification | dynamicSchedEndDate | dynamicSchedEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (dynamic sched)
ETX | AncillaryQualification | AncillaryQualification | emergencyQse | emergencyQse | Boolean | FALSE | etx | Emergency qse. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emergency Qse
ETX | AncillaryQualification | AncillaryQualification | emergencyQseEffectiveDate | emergencyQseEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (emergency qse)
ETX | AncillaryQualification | AncillaryQualification | emergencyQseEndDate | emergencyQseEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (emergency qse)
ETX | AncillaryQualification | AncillaryQualification | nonSpin | nonSpin | Boolean | FALSE | etx | Non spin. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Non Spin
ETX | AncillaryQualification | AncillaryQualification | nonSpinEffectiveDate | nonSpinEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (non-spin)
ETX | AncillaryQualification | AncillaryQualification | nonSpinEndDate | nonSpinEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (non-spin)
ETX | AncillaryQualification | AncillaryQualification | regDown | regDown | Boolean | FALSE | etx | Regulation down ancillary service. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reg Down
ETX | AncillaryQualification | AncillaryQualification | regDownEffectiveDate | regDownEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (down)
ETX | AncillaryQualification | AncillaryQualification | regDownEndDate | regDownEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (down)
ETX | AncillaryQualification | AncillaryQualification | regUp | regUp | Boolean | FALSE | etx | Regulation up ancillary service. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reg Up
ETX | AncillaryQualification | AncillaryQualification | regUpEffectiveDate | regUpEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (up)
ETX | AncillaryQualification | AncillaryQualification | regUpEndDate | regUpEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (up)
ETX | AncillaryQualification | AncillaryQualification | rmr | rmr | Boolean | FALSE | etx | RMR. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | RMR
ETX | AncillaryQualification | AncillaryQualification | rmrEffectiveDate | rmrEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (rmr)
ETX | AncillaryQualification | AncillaryQualification | rmrEndDate | rmrEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (rmr)
ETX | AncillaryQualification | AncillaryQualification | rrs | rrs | Boolean | FALSE | etx | Responsive reserve service. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Responsive Reserve Service
ETX | AncillaryQualification | AncillaryQualification | rrsUpEffectiveDate | rrsUpEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (rrs)
ETX | AncillaryQualification | AncillaryQualification | rrsUpEndDate | rrsUpEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (rrs)
ETX | AncillaryQualification | AncillaryQualification | ufr | ufr | Boolean | FALSE | etx | ufr. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | ufr
ETX | AncillaryQualification | AncillaryQualification | ufrEffectiveDate | ufrEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (ufr)
ETX | AncillaryQualification | AncillaryQualification | ufrEndDate | ufrEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (ufr)
ETX | AncillaryQualification | AncillaryQualification | virtualQse | virtualQse | Boolean | FALSE | etx | Virtual Qse. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Virtual Qse
ETX | AncillaryQualification | AncillaryQualification | virtualQseEffectiveDate | virtualQseEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (virtual qse)
ETX | AncillaryQualification | AncillaryQualification | virtualQseEndDate | virtualQseEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (virtual qse)
ETX | Configuration | Configuration | coldStartTime | coldStartTime | Float |  | etx | Cold start time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cold start time
ETX | Configuration | Configuration | highReasonabilityLimit | highReasonabilityLimit | ActivePower |  | etx | High reasonability limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | High Reasonability Limit
ETX | Configuration | Configuration | highRsnbltyRampRateLimit | highReasonabilityRampRateLimit | ActivePower |  | etx | High reasonability ramp rate limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | High Reasonability Ramp Rate Limit
ETX | Configuration | Configuration | hotintTime | hotintTime | Float |  | etx | Hot-to-intermediate time (Seasonal). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Hot-to-intermediate time - Seasonal
ETX | Configuration | Configuration | hotStartTime | hotStartTime | Float |  | etx | Hot start time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Hot start time
ETX | Configuration | Configuration | intColdTime | intColdTime | Float |  | etx | Intermediate-to-cold time (Seasonal). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Intermediate-to-cold time - Seasonal
ETX | Configuration | Configuration | intStartTime | intStartTime | Float |  | etx | Intermediate start time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Intermediate start time
ETX | Configuration | Configuration | lowReasonabilityLimit | lowReasonabilityLimit | ActivePower |  | etx | Low reasonability limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Low Reasonability Limit
ETX | Configuration | Configuration | lowRsnbltyRampRateLimit | lowReasonabilityRampRateLimit | ActivePower |  | etx | Low reasonability ramp rate limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Low Reasonability Ramp Rate Limit
ETX | Configuration | Configuration | maxDailyStarts | maxDailyStarts | Float |  | etx | Maximum daily starts (seasonal parameter). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum daily starts - Seasonal
ETX | Configuration | Configuration | maxONTime | maxONTime | Float |  | etx | Maximum On-Line time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum On-Line time
ETX | Configuration | Configuration | maxWeeklyEnergy | maxWeeklyEnergy | Float |  | etx | Maximum weekly energy (seasonal parameter). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum weekly energy - Seasonal
ETX | Configuration | Configuration | maxWeeklyStarts | maxWeeklyStarts | Float |  | etx | Maximum weekly starts (seasonal parameter). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum weekly starts - Seasonal
ETX | Configuration | Configuration | minOFFTime | minOFFTime | Float |  | etx | Minimum Off-Line time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Off-Line time
ETX | Configuration | Configuration | minONTime | minONTime | Float |  | etx | Minimum On-Line time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum On-Line time
ETX | Configuration | Configuration | primaryConfiguration | primaryConfiguration | Boolean | FALSE | etx | Primary configuration? | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Primary Configuration
ETX | Configuration | Configuration | qualificationStatus | qualificationStatus | Boolean | FALSE | etx | Qualification status. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Qualification Status
ETX | Configuration | Configuration | seasonalMaxEmergencyRating | seasonalMaxEmergencyRating | ActivePower |  | etx | Seasonal maximum emergency rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Max Emergency Rating
ETX | Configuration | Configuration | seasonalMaxSustainableRating | seasonalMaxSustainableRating | ActivePower |  | etx | Seasonal maximum sustainable rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Max Sustainable Rating
ETX | Configuration | Configuration | seasonalMinEmergencyRating | seasonalMinEmergencyRating | ActivePower |  | etx | Seasonal minimum emergency rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Min Emergency Rating
ETX | Configuration | Configuration | seasonalMinSustainableRating | seasonalMinSustainableRating | ActivePower |  | etx | Seasonal minimum sustainable rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Min Sustainable Rating
ETX | Configuration | Configuration | ShutdownFlag | ShutdownFlag | Boolean | FALSE | etx | Whether Combined Cycle Plant can be shut-down in this Logical Configuration? | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Shutdown Flag
ETX | Configuration | Configuration | StartupFlag | StartupFlag | Boolean | FALSE | etx | Whether Combined Cycle Plant can be started in this Logical Configuration? | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Startup Flag
ETX | ConfigurationMember | ConfigurationMember | primary | primary | Boolean | FALSE | etx | primary configuration. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Primary Configuration?
ETX | ConfigurationMember | ConfigurationMember | steam | steam | Boolean | FALSE | etx | Steam plant. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Steam Plant?
ETX | Contact | Contact | EmailAddress | EmailAddress | String500 |  | etx | Email Address | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Email Address
ETX | Contact | Contact | FirstName | FirstName | String500 |  | etx | First Name. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | First Name
ETX | Contact | Contact | LastName | LastName | String500 |  | etx | Last Name | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Last Name
ETX | Contact | Contact | PrimaryPhone | PrimaryPhone | String20 | (999) 999-9999 x____ | etx | Primary Phone number for contact. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Primary Phone
ETX | Contact | Contact | SecondaryPhone | SecondaryPhone | String20 | (999) 999-9999 x____ | etx | Secondary Phone number for contact. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Secondary Phone
ETX | ControllableLoadResource | ControllableLoadResource | maxDeploymentTime | maxDeploymentTime | Float |  | etx | Maximum deployment time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Deployment Time
ETX | ControllableLoadResource | ControllableLoadResource | maxWeeklyEnergy | maxWeeklyEnergy | Float |  | etx | Maximum weekly Energy. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Weekly Energy
ETX | ControllableLoadResource | ControllableLoadResource | minNoticeTime | minNoticeTime | Float |  | etx | Minimum Notice time (seconds). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Notice time (seconds)
ETX | ControllableLoadResource | ControllableLoadResource | rampRateSlopeDownLimit | rampRateSlopeDownLimit | Float |  | etx | Reasonability Limit for DOWN Ramp Rate. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Reasonability Limit for DOWN Ramp Rate
ETX | ControllableLoadResource | ControllableLoadResource | rampRateSlopeUpLimit | rampRateSlopeUpLimit | Float |  | etx | Reasonability Limit for UP Ramp Rate. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Reasonability Limit for UP Ramp Rate
ETX | DCTie | DCTie | DCTieLZName | DCTieLZName | String12 |  | etx | DC Tie Zone name for DC tie. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | DC Tie Zone name for DC tie
ETX | ElectricalBus | ElectricalBus | DisplayLMP | DisplayLMP | Boolean | TRUE | etx | Display LMP? | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Display LMP
ETX | EnergyConsumerResource | EnergyConsumerResource | blockLoadTransfer | blockLoadTransfer | Boolean | FALSE | etx | Block load transfer. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Block Load Transfer
ETX | EnergyConsumerResource | EnergyConsumerResource | commercialOperationsDate | commercialOperationsDate | Date |  | etx | Date commercial operations started. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Commercial Operations Date
ETX | EnergyConsumerResource | EnergyConsumerResource | loadFreqBias | loadFreqBias | Float |  | etx | Regulating Frequency Bias as MW per 0.1 Hz. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | loadFreqBias
ETX | EnergyConsumerResource | EnergyConsumerResource | loadFreqDevDeadband | loadFreqDevDeadband | Float |  | etx | Frequency deviation deadband for Feed-Forward correction (in Hz). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | loadFreqDevDeadband
ETX | EnergyConsumerResource | EnergyConsumerResource | loadId | loadId | String14 |  | etx | A 14 character load ID used in ERCOT LFC. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | loadId
ETX | EnergyConsumerResource | EnergyConsumerResource | loadSubStationId | loadSubStationId | String8 |  | etx | ID of load's substation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | loadSubStationId
ETX | EnergyConsumerResource | EnergyConsumerResource | maxDailyDeployment | maxDailyDeployment | Float |  | etx | Maximum daily deployments. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Daily Deployments
ETX | EnergyConsumerResource | EnergyConsumerResource | maxInterruptionTime | maxInterruptionTime | Float |  | etx | Maximum interruption time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Interruption Time
ETX | EnergyConsumerResource | EnergyConsumerResource | MaxPowerConsumption | MaxPowerConsumption | Float |  | etx | Maximum power consumption for resource. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Power Consumption
ETX | EnergyConsumerResource | EnergyConsumerResource | maxWeeklyDeployment | maxWeeklyDeployment | Float |  | etx | Maximum weekly deployments. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Weekly Deployments
ETX | EnergyConsumerResource | EnergyConsumerResource | minInterruptionTime | minInterruptionTime | Float |  | etx | Minimum interruption time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Interruption Time
ETX | EnergyConsumerResource | EnergyConsumerResource | MinPowerConsumption | MinPowerConsumption | Float |  | etx | Minimum power consumption for resource. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Power Consumption
ETX | EnergyConsumerResource | EnergyConsumerResource | minRestorationTime | minRestorationTime | Float |  | etx | Minimum restoration time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Restoration Time
ETX | EnergyConsumerResource | EnergyConsumerResource | qualificationStatus | qualificationStatus | Boolean | FALSE | etx | Qualification status. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Qualification Status
ETX | EnergyConsumerResource | EnergyConsumerResource | RelayType | RelayType | EnumRelayType |  | etx | Type of relay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Relay Type
ETX | EnergyConsumerResource | EnergyConsumerResource | resourceCategory | resourceCategory | String50 |  | etx | Type of resource. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Type of Resource
ETX | EnergyConsumerResource | EnergyConsumerResource | wfrmcr | wfrmcr | Boolean | FALSE | etx | wfrmcr. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | wfrmcr
ETX | EPSMeter | EPSMeter | AcceptedStatus | AcceptedStatus | Bool | FALSE | etx | EPS meter location has been accepted by settlements. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Accepted Status
ETX | EPSMeter | EPSMeter | RID | RID | String100 |  | etx | Resource number for EPS meter Identifier. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Resource ID
ETX | EPSMeter | EPSMeter | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
ETX | ERCOTVersion | ERCOTVersion | ContactEmail | ContactEmail | String30 | jmoseley@ercot.com | etx | Contact Email. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Contact Email
ETX | ERCOTVersion | ERCOTVersion | ContactPhoneNumber | ContactPhoneNumber | String14 | (512)248-6362 | etx | Contact Phone Number. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Contact Phone Number
ETX | ERCOTVersion | ERCOTVersion | date | date | String30 | 2009-06-01 | etx | Date. | FALSE | TRUE | TRUE | TRUE |  | FALSE |  | TRUE |  |  | date
ETX | ERCOTVersion | ERCOTVersion | ModelAdmin | ModelAdmin | String30 | John Moseley | etx | Model Administrator. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Model Administrator
ETX | ERCOTVersion | ERCOTVersion | version | version | String30 | ERCOT 1.21.1 | etx | Version. | FALSE | TRUE | TRUE | TRUE |  | FALSE |  | TRUE |  |  | version
ETX | FlowgateElement | FlowgateElement | biddable | biddable | Boolean | FALSE | etx | Biddable. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Biddable
ETX | FlowgateElement | FlowgateElement | endDate | endDate | Date |  | etx | End Date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | End Date
ETX | FlowgateElement | FlowgateElement | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a BranchGroup. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
ETX | FlowgateElement | FlowgateElement | monitored | monitored | Boolean | FALSE | etx | Monitored. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Monitored
ETX | FlowgateElement | FlowgateElement | positiveFlowIn | positiveFlowIn | Boolean | TRUE | etx | Determines metered direction of EPS meter. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Positive Flow In
ETX | FlowgateElement | FlowgateElement | principleElement | principleElement | Boolean | FALSE | etx | Principle element? | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Principle Element
ETX | FlowgateElement | FlowgateElement | rating | rating | DoubleFloat |  | etx | Rating. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Rating
ETX | FlowgateElement | FlowgateElement | startDate | startDate | Date |  | etx | Start Date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Start Date
ETX | FlowgateGroup | FlowgateGroup | defaultLimit | defaultLimit | DoubleFloat |  | etx | Default limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Default Limit
ETX | FlowgateGroup | FlowgateGroup | infB | infB | Float |  | etx | Impact Normalization Factor for Base Case. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 1 | 0 | infB
ETX | FlowgateGroup | FlowgateGroup | infC | infC | Float |  | etx | Impact Normalization Factor for Contingency. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 1 | 0 | infC
ETX | FlowgateGroup | FlowgateGroup | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a BranchGroup. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
ETX | FlowgateGroup | FlowgateGroup | rating | rating | Float |  | etx | Flowgate Group Rating. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | rating
ETX | FlowgateGroup | FlowgateGroup | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
ETX | FlowgateGroup | FlowgateGroup | thermalLimit | thermalLimit | Boolean | FALSE | etx | Is thermal limit? | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Thermal Limit
ETX | IccpQualityConversion | IccpQualityConversion | ICalculated | ICalculated | Boolean | FALSE | etx | I... calculated. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ICalculated
ETX | IccpQualityConversion | IccpQualityConversion | IEstimated | IEstimated | Boolean | FALSE | etx | I... estimated. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | IEstimated
ETX | IccpQualityConversion | IccpQualityConversion | IHeld | IHeld | Boolean | FALSE | etx | I... held. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | IHeld
ETX | IccpQualityConversion | IccpQualityConversion | IManual | IManual | Boolean | FALSE | etx | I... manual. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | IManual
ETX | IccpQualityConversion | IccpQualityConversion | INotValid | INotValid | Boolean | FALSE | etx | I... not valid. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | INotValid
ETX | IccpQualityConversion | IccpQualityConversion | ISuspect | ISuspect | Boolean | FALSE | etx | I... suspect. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ISuspect
ETX | IccpQualityConversion | IccpQualityConversion | ITelemetered | ITelemetered | Boolean | FALSE | etx | I... telemetered. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ITelemetered
ETX | IccpQualityConversion | IccpQualityConversion | IValid | IValid | Boolean | FALSE | etx | I... valid. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | IValid
ETX | IccpQualityConversion | IccpQualityConversion | OCalculated | OCalculated | Boolean | FALSE | etx | O... calculated. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OCalculated
ETX | IccpQualityConversion | IccpQualityConversion | OEstimated | OEstimated | Boolean | FALSE | etx | O... estimated. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OEstimated
ETX | IccpQualityConversion | IccpQualityConversion | OHeld | OHeld | Boolean | FALSE | etx | O... held. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OHeld
ETX | IccpQualityConversion | IccpQualityConversion | OManual | OManual | Boolean | FALSE | etx | O... manual. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OManual
ETX | IccpQualityConversion | IccpQualityConversion | ONotValid | ONotValid | Boolean | FALSE | etx | O... not valid. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ONotValid
ETX | IccpQualityConversion | IccpQualityConversion | OSuspect | OSuspect | Boolean | FALSE | etx | O... suspect. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OSuspect
ETX | IccpQualityConversion | IccpQualityConversion | OTelemetered | OTelemetered | Boolean | FALSE | etx | O... telemetered. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OTelemetered
ETX | IccpQualityConversion | IccpQualityConversion | OValid | OValid | Boolean | FALSE | etx | O... valid. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OValid
ETX | LoadResource | LoadResource | maxWeeklyEnergy | maxWeeklyEnergy | Float |  | etx | Maximum weekly Energy. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Weekly Energy
ETX | LoadResource | LoadResource | minNoticeTime | minNoticeTime | Float |  | etx | Minimum Notice time (seconds). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Notice time (seconds)
ETX | ModelBuild | ModelBuild | ModelBuilder | ModelBuilder | String30 |  | etx | Model Builder. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Model Builder
ETX | ModelBuild | ModelBuild | ModelBuildTime | ModelBuildTime | String30 |  | etx | Model Build Time. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Model Build Time
ETX | ModelBuild | ModelBuild | ModelDescription | ModelDescription | String100 |  | etx | Model Description. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Model Description
ETX | ModelBuild | ModelBuild | ModelProfile | ModelProfile | String30 |  | etx | Model Profile. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Model Profile
ETX | ModelBuild | ModelBuild | ValidDateRange | ValidDateRange | String30 |  | etx | Valid Date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Valid Date Range
ETX | Operatorship | Operatorship | operatePercent | operatePercent | Float |  | etx | Operator share percentage. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Operate Percent
ETX | Ownership | Ownership | ownPercent | ownPercent | Float |  | etx | Owner share percentage. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Own Percent
ETX | Ownership | Ownership | penaltyFactor | penaltyFactor | Float |  | etx | User entered penalty factor for loss calculations. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Penalty Factor
ETX | Ownership | Ownership | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
ETX | PricingVector | PricingVector | positiveFlowIn | positiveFlowIn | Boolean | TRUE | etx | Determines metered direction of EPS meter. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Positive Flow In
ETX | PricingVector | PricingVector | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
ETX | PrivateAreaNetwork | PrivateAreaNetwork | networkType | networkType | EnumPANType |  | etx | Type of Private Use Network. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Type of Private Use Network
ETX | SettlementLoadZone | SettlementLoadZone | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number Alternate Areas and Zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
ETX | SettlementNOIELoadZone | SettlementNOIELoadZone | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number Alternate Areas and Zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
ETX | SupportLoadData | SupportLoadData | p | p | DoubleFloat |  | etx | motor p. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | motor p
ETX | SupportLoadData | SupportLoadData | percentageFlag | percentageFlag | Boolean |  | etx | percentage flag | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | percentage flag
ETX | SupportLoadData | SupportLoadData | q | q | DoubleFloat |  | etx | motor q. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | motor q
ETX | SupportLoadData | SupportLoadData | r | r | DoubleFloat |  | etx | motor r. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | motor r
ETX | SupportLoadData | SupportLoadData | rating | rating | DoubleFloat |  | etx | motor rating. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | motor rating
ETX | SupportLoadData | SupportLoadData | ratiotransformer | ratiotransformer | DoubleFloat |  | etx | ratio transformer. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ratio transformer
ETX | SupportLoadData | SupportLoadData | rtransformer | rtransformer | Float |  | etx | stepup transformer r. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | stepup transformer r
ETX | SupportLoadData | SupportLoadData | varhighlimit | varhighlimit | Float |  | etx | motor var high limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | motor var high limit
ETX | SupportLoadData | SupportLoadData | varlowlimit | varlowlimit | Float |  | etx | motor var low limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | motor var low limit
ETX | SupportLoadData | SupportLoadData | x | x | DoubleFloat |  | etx | motor x. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | motor x
ETX | SupportLoadData | SupportLoadData | xtransformer | xtransformer | Float |  | etx | stepup transformer x. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | stepup transformer x
ETX | TransformerKluge | TransformerKluge | PSSE3WinderID | PSSE3WinderID | String2 |  | etx | Attribute will be used to store the three winding transformer ID and Mark which transformers are to be grouped as three winding Transformers. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | PSS/E 3 Winding ID
ETX | TransformerKluge | TransformerKluge | PSSE3Windername | PSSE3Windername | String12 |  | etx | Attribute will be used to store the three winding transformer name. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | PSS/E 3 Winding Name
ETX | TransState | TransState | upTransition | upTransition | Boolean | FALSE | cim | Flag indicating whether this is an UP transition or DOWN transition. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Up Transition?
ETX_ABB | LimitLogicType | LimitLogicType | postContLimitType | postContLimitType | EnumPostContLimitType |  | etx | Post Cont Limit Type | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Post-Cont Limit Type
ETX_ABB | LimitLogicType | LimitLogicType | preContLimitType | preContLimitType | EnumPreContLimitType |  | etx | Pre-Cont Limit Type | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pre-Cont Limit Type
ETX_Areva | RampRateCurve | RampRateCurve | Emergency | Emergency | Boolean | FALSE | etx | Denote the type of ramp rate. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Emergency
ETX_Areva | RampRateCurve | RampRateCurve | rampRateCurveId | rampRateCurveId | String5 |  | etx | Ramp Rate Curve ID. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Ramp Rate Curve ID
ETX_Areva | ResourceController | ResourceController | externalJointUnit | externalJointUnit | Boolean | FALSE | etx | external Joint Unit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | external Joint Unit
ETX_Areva | ResourceController | ResourceController | frequencyBias | frequencyBias | Float |  | etx | Frequency bias. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Frequency Bias
ETX_Areva | ResourceController | ResourceController | gross | gross | Boolean | FALSE | etx | Gross. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Gross
ETX_Areva | ResourceController | ResourceController | jointUnit | jointUnit | Boolean | FALSE | etx | joint Unit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | joint Unit
ETX_Areva | ResourceController | ResourceController | physical | physical | Boolean | FALSE | etx | physical. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | physical
ETX_Areva | TieCorridor | TieCorridor | maxInflowLimit | maxInflowLimit | Float |  | etx | Maximum MW inflow alarm limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MW Inflow Alarm Limit
ETX_Areva | TieCorridor | TieCorridor | maxOutflowLimit | maxOutflowLimit | Float |  | etx | Maximum MW outflow alarm limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MW Outflow Alarm Limit
ETX_Areva | TieCorridor | TieCorridor | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
ETX_Areva | TieCorridor | TieCorridor | tieId | tieId | String14 |  | etx | ID of Tie/ | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Tie ID
ETX_Areva | TieCorridor | TieCorridor | tieIsInternal | tieIsInternal | Boolean | FALSE | etx | True if Tie is internal. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Tie Is Internal?
ETX_Areva | TieEnd | TieEnd | participationFactorJointAGC | participationFactorJointAGC | Float |  | etx | Joint AGC participation factor. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Participation Factor Joint AGC
ETX_Areva | TieEnd | TieEnd | percentChangeAlarm | percentChangeAlarm | Float |  | etx | TiePointEnd MW STEP CHANGE ALARM LEVEL (% OF maximuInMW of TiePointEnd) (EG: 10%) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | percentChangeAlarm
ETX_Areva | TieEnd | TieEnd | priorityJointAGC | priorityJointAGC | Integer |  | etx | Joint AGC priority level. Lowest numbered ties will be used first. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Priority Joint AGC
ETX_Areva | TieEnd | TieEnd | tauJointAGCLoadFollowing | tauJointAGCLoadFollowing | Float |  | etx | Time constant for filtering joint AGC load following component (requester only).. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Tau Joint AGC Load Following
ETX_Areva | TieLine | TieLine | isATransLine | isATransLine | Boolean | FALSE | etx | True for transmission line, false for transformer. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Is a Transmission Line?
ETX_Areva | TieLine | TieLine | measAtNearEnd | measAtNearEnd | Boolean | FALSE | etx | TRUE - USE THE MEASUREMENT AT THE NEAR END OF THE LINE FALSE - USE THE MEASUREMENT AT THE FAR END OF THE LINE. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Measurement at Near End?
ETX_Areva | TieLine | TieLine | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
ETXContingency | ContingencyElement | ContingencyElement | cbFault | cbFault | Boolean | FALSE | etx | Indicates TRUE if this CB is included in post contingency and related to CB fault due to the dynamic redefinition logic. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | CB Fault
ETXContingency | ContingencyElement | ContingencyElement | status | status | Boolean | TRUE | etx | The status of contingency element, i.e. Open/Close for Switch, Removed or not for other conducting equipment. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Status
ETXContingency | ContingencyGroup | ContingencyGroup | maintainSubSystems | maintainSubSystems | Boolean | TRUE | etx | This field sets whether the subsystems for the contingencies in this CTGGroup are maintained even though the group is inactive. When Maintain Subsystems set ON, and Study is set OFF, CA maintains the contingency local subsystems for base case changes. If Maintain Subsystems is set OFF and Study is set OFF, the subsystems are deleted. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maintain Sub Systems
ETXContingency | ContingencyGroup | ContingencyGroup | study | study | Boolean | TRUE | etx | T=activate the contigencies in the group. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Study
ETXLoadModel | EnergyConsumerAltConnection | EnergyConsumerAltConnection | percentTransfer | percentTransfer | Float |  | etx | Percentage of load transferred from parent load to target load. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Percent Transfer
ETXLoadModel | LoadType | LoadType | expPFrequency | expPFrequency | Float |  | etx | Load watts are proportional to (V**WVEXP)*(F**WFEXP). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | exp P Frequency
ETXLoadModel | LoadType | LoadType | expPVoltage | expPVoltage | Float |  | etx | Exp P Voltage. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | exp P Voltage
ETXLoadModel | LoadType | LoadType | expQFrequency | expQFrequency | Float |  | etx | Load vars are proportional to (V**RVEXP)*(F**RFEXP). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | exp Q Frequency
ETXLoadModel | LoadType | LoadType | expQVoltage | expQVoltage | Float |  | etx | Exp Q Voltage. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | exp Q Voltage
ETXLoadModel | LoadType | LoadType | initialTime | initialTime | Integer |  | etx | The initial time on the cooling characteristic in seconds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Initial Time
ETXLoadModel | LoadType | LoadType | maxScaling | maxScaling | Float |  | etx | The maximum value that the load could be scaled by upon its reconection. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Scaling
ETXMonitoring | BranchGroup | BranchGroup | maximumActivePower | maximumActivePower | Float |  | etx | Maximum active power. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Active Power
ETXMonitoring | BranchGroup | BranchGroup | maximumReactivePower | maximumReactivePower | Float |  | etx | Maximum reactive power | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Reactive Power
ETXMonitoring | BranchGroup | BranchGroup | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a BranchGroup. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
ETXMonitoring | BranchGroup | BranchGroup | minimumActivePower | minimumActivePower | Float |  | etx | Minimum active power. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Active Power
ETXMonitoring | BranchGroup | BranchGroup | minimumReactivePower | minimumReactivePower | Float |  | etx | Minimum reactive power. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Reactive Power
ETXMonitoring | BranchGroup | BranchGroup | monitorActivePower | monitorActivePower | Boolean | FALSE | etx | Monitor active power. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Monitor Active Power
ETXMonitoring | BranchGroup | BranchGroup | monitorReactivePower | monitorReactivePower | Boolean | FALSE | etx | Monitor reactive power. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Monitor Reactive Power
ETXMonitoring | BranchGroup | BranchGroup | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
ETXMonitoring | BranchGroupTerminal | BranchGroupTerminal | positiveFlowIn | positiveFlowIn | Boolean | FALSE | etx | Positive Flow In. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Positive Flow In
ETXMonitoring | Monitored | Monitored | eligible | eligible | Boolean | FALSE | etx | Eligible. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Eligible
ETXMonitoring | MonitoredGroup | MonitoredGroup | active | active | Boolean | FALSE | etx | Active. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Active
ETXMonitoring | VoltageLimit | VoltageLimit | value | value | Float |  | etx | The value to supervise against. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value
ETXNetwork | AccuracyClass | AccuracyClass | adConverterError | adConverterError | Float |  | etx | A to D converter error. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ADConverterError
ETXNetwork | AccuracyClass | AccuracyClass | addEntered | addEntered | Boolean | FALSE | etx | T = add the value in the Standard Deviation (per Unit) field to the calculated standard deviation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Add Entered
ETXNetwork | AccuracyClass | AccuracyClass | base | base | Float |  | etx | Base value. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Base
ETXNetwork | AccuracyClass | AccuracyClass | breakPoint | breakPoint | Float |  | etx | Break point for uncertainty model. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Break Point
ETXNetwork | AccuracyClass | AccuracyClass | currentTransformerError | currentTransformerError | Float |  | etx | Current transformer error. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Current Transformer Error
ETXNetwork | AccuracyClass | AccuracyClass | defaultAccuracy | defaultAccuracy | Boolean | FALSE | etx | T = it is a defaulted accuracy record or manually inserted accuracy record. Manually inserted accuracy record could be assigned to SCADA analog observation or other modeled loads (LDs) and units (UNs). The defaulted accuracy record is inserted by the NETV. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Default Accuracy
ETXNetwork | AccuracyClass | AccuracyClass | standardDeviation | standardDeviation | Float |  | etx | Standard deviation for uncertainty model. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Standard Deviation
ETXNetwork | AccuracyClass | AccuracyClass | transducerMaxError | transducerMaxError | Float |  | etx | Transducer maximum error. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Transducer Maximum Error
ETXNetwork | AccuracyClass | AccuracyClass | useEntered | useEntered | Boolean | FALSE | etx | T = use the value in the Standard Deviation (per Unit) field as the standard deviation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Use Entered
ETXNetwork | AccuracyClass | AccuracyClass | voltageTransformerError | voltageTransformerError | Float |  | etx | Voltage tranformer error. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Voltage Transformer Error
ETXPlanning | ConnectivityNodeGroup | ConnectivityNodeGroup | PSSEBusName | PSSEBusName | String12 |  | etx | Store the PSS™E bus name that will be associated with the grouping of Connectivity Nodes in Option 2. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | PSS/E Bus Name
ETXPlanning | ConnectivityNodeGroup | ConnectivityNodeGroup | PSSEBusNumber | PSSEBusNumber | Integer |  | etx | Attribute will be used to store the PSS™E bus number that will be associated with the grouping of Connectivity Nodes in Option 2. | FALSE | FALSE | TRUE | FALSE |  | TRUE |  | TRUE |  |  | PSS/E Bus Number
ETXPlanning | PlanningArea | PlanningArea | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number areas. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
ETXPlanning | PlanningZone | PlanningZone | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
ETXRASE | Gate | Gate | changeThreshold | changeThreshold | Boolean | FALSE | etx | Use change limit for voltages. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Change Threshold
ETXRASE | Gate | Gate | emergencyThreshold | emergencyThreshold | Boolean | FALSE | etx | Use the branch emergency limit as threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Emergency Threshold
ETXRASE | Gate | Gate | gatetype | gatetype | EnumGateType |  | etx | Gate Type. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Gate Type
ETXRASE | Gate | Gate | level | level | Integer | 0 | etx | Level of the gate. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Level
ETXRASE | Gate | Gate | limitPercentage | limitPercentage | Float |  | etx | Percentage of the limit. 90% should enter 90. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Limit Percentage
ETXRASE | Gate | Gate | loadshedThreshold | loadshedThreshold | Boolean | FALSE | etx | Use the branch loadshed limit as threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Loadshed Threshold
ETXRASE | Gate | Gate | lowerThreshold | lowerThreshold | Boolean | FALSE | etx | Use lower limit (for FlowSummation and voltage). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Lower Threshold
ETXRASE | Gate | Gate | normalThreshold | normalThreshold | Boolean | FALSE | etx | Use the branch normal limit as threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Normal Threshold
ETXRASE | Gate | Gate | thresholdValue | thresholdValue | Float |  | etx | Threshold value for gate type of (GE,GT,LE,LT,NE,EQ) with single gate input | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Threshold Value
ETXRASE | Gate | Gate | upperThreshold | upperThreshold | Boolean | FALSE | etx | Use upper limit (for FlowSummation and voltage). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Upper Threshold
ETXRASE | Gate | Gate | useLimitThreshold | useLimitThreshold | Boolean | FALSE | etx | Use the branch limit as threashold value, otherwise use Gate::thresholdValue. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Use Limit Threshold
ETXRASE | GateInputPin | GateInputPin | flowMVA | flowMVA | Boolean | FALSE | etx | If true the input is a MVA. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Flow MVA
ETXRASE | GateInputPin | GateInputPin | flowMVAR | flowMVAR | Boolean | FALSE | etx | If true the input is a MVAR. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Flow MVAR
ETXRASE | GateInputPin | GateInputPin | flowMW | flowMW | Boolean | FALSE | etx | If true, the input is a MW. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Flow MW
ETXRASE | GateInputPin | GateInputPin | negate | negate | Boolean | FALSE | etx | If true, input is negated first and then input to the gate. only applicable to logical gates. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Negate
ETXRASE | GateInputPin | GateInputPin | useAbsoluteValue | useAbsoluteValue | Boolean | FALSE | etx | Use absolute value of input (only applies to analog inputs). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Use Absolute Value
ETXRASE | PinFlow | PinFlow | eitherEnd | eitherEnd | Boolean | FALSE | etx | True if doing status input on a branch and want to check if either end is out. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Either End
ETXRASE | PinFlow | PinFlow | inputIsFlow | inputIsFlow | Boolean | FALSE | etx | If true, the input is a flow, otherwise it is branch status. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Input Is Flow
ETXRASE | PinFlow | PinFlow | intoBus | intoBus | Boolean | FALSE | etx | Flow into the bus is positive. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Into Bus
ETXRASE | PinFlow | PinFlow | outOfBus | outOfBus | Boolean | FALSE | etx | Flow out of the bus is positive. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Out of Bus
ETXRASE | ProtActACLineSegment | ProtActACLineSegment | inService | inService | Boolean | FALSE | etx | If true the ACLineSegment is put in-service, otherwise out-of-service. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | In Service
ETXRASE | ProtActAnalog | ProtActAnalog | actionValue | actionValue | Float |  | etx | The value to reduce to or by. Used if no value from SCADA. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Action Value
ETXRASE | ProtActAnalog | ProtActAnalog | actionValueFromSCADA | actionValueFromSCADA | Boolean | FALSE | etx | True, the action value is obtained from SCADA otherwise from actionValue attribute. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Action Value From SCADA
ETXRASE | ProtActAnalog | ProtActAnalog | isReduceTo | isReduceTo | Boolean | FALSE | etx | If true, action is a 'reduce to' otherwise it is a 'reduce by'. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Is Reduce To
ETXRASE | ProtActSeriesCompensator | ProtActSeriesCompensator | inService | inService | Boolean | FALSE | etx | If true the SeriesCompensator is put in-service, otherwise out-of-service. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | In Service
ETXRASE | ProtActSwitch | ProtActSwitch | closeAction | closeAction | Boolean | FALSE | etx | If true close the switch, otherwise open switch. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Close Action
ETXRASE | ProtActTransformerWinding | ProtActTransformerWinding | inService | inService | Boolean | FALSE | etx | If true the Transformer is put in-service, otherwise out-of-service. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | In Service
ETXRASE | ProtectiveAction | ProtectiveAction | enableArming | enableArming | Boolean | FALSE | etx | Enable arming. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Enable Arming
ETXRASE | RemedialActionScheme | RemedialActionScheme | active | active | Boolean | FALSE | etx | User specified active. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Active
ETXRASE | RemedialActionScheme | RemedialActionScheme | isRAP | isRAP | Boolean | FALSE | etx | This is a remedial action plan (RAP). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Is RAP
ETXRASE | RemedialActionScheme | RemedialActionScheme | isRAS | isRAS | Boolean | FALSE | etx | This is a remedial action scheme (RAS). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Is RAS
ETXRating | DynamicElement | DynamicElement | line | line | Boolean | FALSE | etx | True if the dynamic element is a line. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Line?
ETXRating | DynamicElement | DynamicElement | transformer | transformer | Boolean | FALSE | etx | True if the dynamic element is a transformer. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Transformer?
ETXRating | DynamicElement | DynamicElement | zeroImpBranch | zeroImpBranch | Boolean | FALSE | etx | True if the dynamic element is a zero impedance branch. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Zero Impedance Branch?
ETXRating | OwnerShareLimits | OwnerShareLimits | highReasonabilityLimit | highReasonabilityLimit | ActivePower |  | etx | highReasonabilityLimit split based on the ownership percentage. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | High Reasonability Limit
ETXRating | OwnerShareLimits | OwnerShareLimits | lowReasonabilityLimit | lowReasonabilityLimit | ActivePower |  | etx | lowReasonabilityLimit split based on the ownership percentage. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Low Reasonability Limit
ETXRating | OwnerShareLimits | OwnerShareLimits | maxWeeklyEnergy | maxWeeklyEnergy | Float |  | etx | Maximum weekly energy (seasonal parameter) split based on the ownership percentage. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum weekly energy (seasonal parameter)
ETXRating | Rating | Rating | activateValue | activateValue | Float |  | etx | Temperature. It is used to pick the actual rating to supervise againist. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Activate Value
ETXRating | Rating | Rating | ratingType | ratingType | EnumRatingType |  | etx | Rating type: static (planning) or dynamic (temperature). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Rating Type
ETXRating | Rating | Rating | TempPoint | TempPoint | Integer |  | etx | Temperature Point index. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Temperature Point index
ETXRating | WeatherStationAlt | WeatherStationAlt | DynamicAdder | DynamicAdder | Integer | 0 | etx | Dynamic adder. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Dynamic Adder
ETXSCADA | AlternateLimit | AlternateLimit | highLimit | highLimit | Float |  | etx | High Limit: The threshold above which the analog is considered in violation of the limit. When the low limit is null, only the high limit is checked for violation. The High Limit must be greater then the Low Limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | High Limit
ETXSCADA | AlternateLimit | AlternateLimit | lowLimit | lowLimit | Float |  | etx | Low Limit: The threshold below which the analog is considered in violation of the limit. When the high limit is null, only the low limit is checked for violation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Low Limit
ETXSCADA | Calculation | Calculation | type | type | String30 |  | etx | Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Type
ETXSCADA | Calculation | Calculation | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temp Attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
ETXSCADA | CalculationArgument | CalculationArgument | referenceFlag | referenceFlag | Boolean |  | etx | The Boolean flag to indicate this arguement is a reference. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reference Flag
ETXSCADA | CalculationArgument | CalculationArgument | referenceName | referenceName | String4 |  | etx | If this is a Reference, name for the reference. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reference Name
ETXSCADA | CalculationArgument | CalculationArgument | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temporary attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
ETXSCADA | ConstantArgument | ConstantArgument | scalarValue | scalarValue | Float |  | etx | The scalar constant I/O parameter for a SCADA calculation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Scalar Value
ETXSCADA | ConstantValue | ConstantValue | value | value | Float |  | etx | The value of the SCADA constant argument. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value
ETXSCADA | Function | Function | subRoutine | subRoutine | String100 |  | etx | Function subroutine. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Subroutine
ETXSCADA | FunctionArgument | FunctionArgument | analogFlag | analogFlag | Boolean | FALSE | etx | Flag indicating this is input is an analog. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Analog Flag
ETXSCADA | FunctionArgument | FunctionArgument | constantFlag | constantFlag | Boolean | FALSE | etx | Flag indicating this is input is a constant. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Constant Flag
ETXSCADA | FunctionArgument | FunctionArgument | openFlag | openFlag | Boolean | FALSE | etx | Flag indicating any number of this type of argument can be included. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Open Flag
ETXSCADA | FunctionArgument | FunctionArgument | pointFlag | pointFlag | Boolean | FALSE | etx | Flag indicating this is input is a constant. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Point Flag
ETXSCADA | FunctionArgument | FunctionArgument | readFlag | readFlag | Boolean | FALSE | etx | Flag indicating this is an input to the function. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Read Flag
ETXSCADA | FunctionArgument | FunctionArgument | realFlag | realFlag | Boolean | FALSE | etx | Flag indicating this is input is a real (constant, analog, or count). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Real Flag
ETXSCADA | FunctionArgument | FunctionArgument | triggerFlag | triggerFlag | Boolean | FALSE | etx | Flag indicating the function runs when this argument changes. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Trigger Flag
ETXSCADA | FunctionArgument | FunctionArgument | writeFlag | writeFlag | Boolean | FALSE | etx | Flag indicating this is an output from the function. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Write Flag
ETXSCADA | MeasurementArgument | MeasurementArgument | triggerFlag | triggerFlag | Boolean | FALSE | etx | This reference record is an input to a calculation and triggers that calculation when referenced Measurement record changes. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | trigger Flag
ETXSCADA | MeasurementGroup | MeasurementGroup | bufferPeriod | bufferPeriod | ShortInt |  | etx | Number of seconds to wait for a cluster of exceptions to be reported. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | buffer Period
ETXSCADA | MeasurementGroup | MeasurementGroup | gracePeriod | gracePeriod | ShortInt |  | etx | Number of seconds to wait before declaring an expected scan 'late'. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | grace Period
ETXSCADA | MeasurementGroup | MeasurementGroup | integrityPeriod | integrityPeriod | ShortInt |  | etx | Number of seconds between integrity scans. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | integrity Period
ETXSCADA | MeasurementGroup | MeasurementGroup | scanPeriod | scanPeriod | ShortInt |  | etx | Number of seconds between scans. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | scan Period
ETXSCADA | MeasurementGroup | MeasurementGroup | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temp Attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
ETXSCADA | MeasurementLocation | MeasurementLocation | abnormalForAlarm | abnormalForAlarm | Boolean | FALSE | etx | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Abnormal For Alarm
ETXSCADA | MeasurementLocation | MeasurementLocation | abnormalForSCADA | abnormalForSCADA | Boolean | FALSE | etx | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Abnormal For SCADA
ETXSCADA | MeasurementLocation | MeasurementLocation | audibleTone | audibleTone | Boolean | FALSE | etx | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Audible Tone
ETXSCADA | MeasurementLocation | MeasurementLocation | farNodeNormallyEarthed | farNodeNormallyEarthed | Boolean | FALSE | etx | T = The far node of the location is normally earthed; if connected to an energized portion of the network, it is considered to be in an abnormal state. Without the normally open or normally grounded flags set, SCADA topology assumes the node is normally . | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | far Node Normally Earthed
ETXSCADA | MeasurementLocation | MeasurementLocation | farNodeNormallyOpen | farNodeNormallyOpen | Boolean | FALSE | etx | T = The far node of the location is normally open; if closed or grounded, it is considered to be in an abnormal state. Without the normally open or normally grounded flags set, SCADA topology assumes the node is normally closed (connected to at least two... | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | far Node Normally Open
ETXSCADA | MeasurementLocation | MeasurementLocation | farStation | farStation | String8 |  | etx | The 'far' station identifer for the location (as opposed to the local substation under which the device is modeled). Only used for device records which link substations, typically lines. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | far Station
ETXSCADA | MeasurementLocation | MeasurementLocation | inhibitAbnormalForAlarm | inhibitAbnormalForAlarm | Boolean | FALSE | etx | Permanently Inhibit the flag of abnormalForAlarm. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Abnormal For Alarm
ETXSCADA | MeasurementLocation | MeasurementLocation | inhibitAbnormalForSCADA | inhibitAbnormalForSCADA | Boolean | FALSE | etx | Permanently Inhibit the flag of abnormalForSCADA. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Abnormal For SCADA
ETXSCADA | MeasurementLocation | MeasurementLocation | inhibitAudibleTone | inhibitAudibleTone | Boolean | FALSE | etx | Permanently Inhibit the flag of audibleTone. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Audible Tone
ETXSCADA | MeasurementLocation | MeasurementLocation | inhibitLoggingAndAlarmList | inhibitLoggingAndAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Logging and Alarm List
ETXSCADA | MeasurementLocation | MeasurementLocation | inhibitUnackAlarmList | inhibitUnacknowledgedAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Unacknowledged Alarm List
ETXSCADA | MeasurementLocation | MeasurementLocation | initiallyInhibit | initiallyInhibit | Boolean | FALSE | etx | A flag indicating that when the system first comes online, alarm indications for this SCADA entry will initially be inhibited. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Initially Inhibit
ETXSCADA | MeasurementLocation | MeasurementLocation | loggingAndAlarmList | loggingAndAlarmList | Boolean | FALSE | etx | A flag indicating that SCADA will issue neither an alarm nor an event. Therefore, entries will appear in the neither the alarm list nor the event logs. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Logging and Alarm List
ETXSCADA | MeasurementLocation | MeasurementLocation | nearNodeNormallyEarthed | nearNodeNormallyEarthed | Boolean | FALSE | etx | T = The near node of the location is normally earthed; if connected to an energized portion of the network, it is considered to be in an abnormal state. Without the normally open or normally grounded flags set, SCADA topology assumes the node is normally. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | near Node Normally Earthed
ETXSCADA | MeasurementLocation | MeasurementLocation | nearNodeNormallyOpen | nearNodeNormallyOpen | Boolean | FALSE | etx | T = The near node of the location is normally open; if closed or grounded, it is considered to be in an abnormal state. Without the normally open or normally grounded flags set, SCADA topology assumes the node is normally closed (connected to at least two... | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | near Node Normally Open
ETXSCADA | MeasurementLocation | MeasurementLocation | normallyDead | normallyDead | Boolean | FALSE | etx | A flag indicating whether the location is normally dead. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Normally Dead
ETXSCADA | MeasurementLocation | MeasurementLocation | overrideDefaultnhibitDef | overrideDefaultInhibitDefinition | Boolean | FALSE | etx | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Override Default Inhibit Definition
ETXSCADA | MeasurementLocation | MeasurementLocation | unacknowledgedAlarmList | unacknowledgedAlarmList | Boolean | FALSE | etx | A flag ndicating that SCADA will issue an event to the event log, but will not issue unacknowledged alarm indications to the alarm list. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Unacknowledged Alarm List
ETXSCADA | ModelVersion | ModelVersion | date | date | AbsoluteDateTime |  | etx | Date upon which CIM XML file was produced. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | date
ETXSCADA | ModelVersion | ModelVersion | information | information | String100 |  | etx | Supplemental information, perhaps identifying the sources of the model or model changes. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | information
ETXSCADA | ModelVersion | ModelVersion | version | version | String30 |  | etx | Identifier by which various CIM XML files can be bound together. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | version
ETXSCADA | SetPointLock | SetPointLock | assignedToAnalog | assignedToAnalog | Boolean | FALSE | etx | Assigned to Analog. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | assigned To Analog
ETXSCADA | Site | Site | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temp Attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
MarketOperations | Contingency | Contingency | ActionType | ActionType | String100 |  | etx | Action Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Action Type
MarketOperations | Contingency | Contingency | activeMode | activeMode | EnumContingencyActiveMode |  | etx | Contingency active mode. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Active Mode
MarketOperations | Contingency | Contingency | DeviceName | DeviceName | String100 |  | etx | Device Name. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Device Name
MarketOperations | Contingency | Contingency | DeviceType | DeviceType | String100 |  | etx | Device Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Device Type
MarketOperations | Contingency | Contingency | enableCascading | enableCascading | Boolean | FALSE | etx | TRUE if Cascading contigency analysis needs to performed, default is FALSE. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Enable Cascading
MarketOperations | Contingency | Contingency | enableRedefinition | enableRedefinition | Boolean | FALSE | etx | T=enable F=disable dynamic redefinition. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Enable Redefinition
MarketOperations | Contingency | Contingency | enableSPS | enableSPS | Boolean | FALSE | etx | T=enable F=disable SPS functions. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Enable SPS
MarketOperations | Contingency | Contingency | endDate | endDate | AbsoluteDateTime | 2100-01-01 | etx | Final Date this Contingency is in use. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End Date
MarketOperations | Contingency | Contingency | generationLoss | generationLoss | Float |  | etx | The amount (in MW) of generation you expect the contingency to lose. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Generation Loss
MarketOperations | Contingency | Contingency | generatorParticipationFactor | generatorParticipationFactor | EnumGeneratorParticipationFactor |  | etx | Short/Long. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Generator Participation Factor
MarketOperations | Contingency | Contingency | loadLoss | loadLoss | Float |  | etx | The amount (in MW) of load you expect the contingency to lose. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Load Loss
MarketOperations | Contingency | Contingency | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a Contingency. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
MarketOperations | Contingency | Contingency | probabilityOfOccurance | probabilityOfOccurance | Float |  | etx | A number between 0 and 1. Contingencies with a probability less than 0.5 are considered 'low probability' contingencies. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Probability of Occurance
MarketOperations | Contingency | Contingency | processType | processType | EnumContingencyProcessType |  | etx | Contingency process type. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Process Type
MarketOperations | Contingency | Contingency | refactor | refactor | Boolean | FALSE | etx | Set to TRUE to force a partial refactorization method when updating the matrices for the contingency solution. The default is FALSE, in this case the software will automatically determine whether a factor update or partial refactorization is more efficient for the contingency being processed, and use the most efficient method. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Refactor
MarketOperations | Contingency | Contingency | responseTime | responseTime | Integer |  | etx | the time frame of response in seconds for the components associated with this contingency. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Response Time
MarketOperations | Contingency | Contingency | RunFlag | RunFlag | Boolean | TRUE | etx | Run Flag. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Run Flag
MarketOperations | Contingency | Contingency | startDate | startDate | AbsoluteDateTime | 2001-01-01 | etx | Starting Date this Contingency is expected to be in use. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Start Date
Protection | FrequencyRelay | FrequencyRelay | overFrequencyDelay | overFrequencyDelay | Seconds |  | etx | Over frequency trip delay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Frequency Trip Delay
Protection | FrequencyRelay | FrequencyRelay | overFrequencyLimit | overFrequencyLimit | Voltage |  | etx | Over frequency limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Frequency Limit
Protection | FrequencyRelay | FrequencyRelay | overFrequencyLockoutTime | overFrequencyLockoutTime | Seconds |  | etx | Lockout time when trip at over frequency. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Frequency Lockout Time
Protection | FrequencyRelay | FrequencyRelay | underFrequencyDelay | underFrequencyDelay | Seconds |  | etx | Under frequency trip delay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Under Frequency Trip Delay
Protection | FrequencyRelay | FrequencyRelay | underFrequencyLimit | underFrequencyLimit | Voltage |  | etx | Under frequency limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Under Frequency Limit
Protection | FrequencyRelay | FrequencyRelay | underFrequencyLockoutTime | underFrequencyLockoutTime | Seconds |  | etx | Lockout time when trip at under frequency. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Under Frequency Lockout Time
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | freq1 | freq1 | Float |  | etx | First point in under frequency relay characteristic - decrease load by ls1 factor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Freq 1
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | freq2 | freq2 | Float |  | etx | Second point in under frequency relay characteristic - decrease load by ls2 factor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Freq 2
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | freq3 | freq3 | Float |  | etx | Third point in under frequency relay characteristic - decrease load by ls3 factor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Freq 1
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | i | i | Integer |  | etx | Pointer to company/station. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | i
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | id | id | String30 |  | etx | Company/station that this frequency relay model belongs to. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | id
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | Is1 | Is1 | Float |  | etx | Load deration factor when frequency less than freq1. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Is 1
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | Is2 | Is2 | Float |  | etx | Load deration factor when frequency less than freq2. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Is 2
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | Is3 | Is3 | Float |  | etx | Load deration factor when frequency less than freq3. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Is 3
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | isle1 | isle1 | Integer |  | etx | Subscript of first island to trip in region one. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Isle 1
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | isle2 | isle2 | Integer |  | etx | Subscript of first island to trip in region two. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Isle 2
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | isle3 | isle3 | Integer |  | etx | Subscript of first island to trip in region three. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Isle 3
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | reset1 | reset1 | Boolean | FALSE | etx | Relay has been requested for reset from trip in region one. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reset 1
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | reset2 | reset2 | Boolean | FALSE | etx | Relay has been requested for reset from trip in region two. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reset 2
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | reset3 | reset3 | Boolean | FALSE | etx | Relay has been requested for reset from trip in region three. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reset 3
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | tripped1 | tripped1 | Boolean | FALSE | etx | Relay has tripped in region one. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tripped 1
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | tripped2 | tripped2 | Boolean | FALSE | etx | Relay has tripped in region two. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tripped 2
Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | tripped3 | tripped3 | Boolean | FALSE | etx | Relay has tripped in region three. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tripped 3
Protection | VoltageRelay | VoltageRelay | overVoltageDelay | overVoltageDelay | Seconds |  | etx | Over Voltage Trip Delay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Voltage Trip Delay
Protection | VoltageRelay | VoltageRelay | overVoltageLimit | overVoltageLimit | Voltage |  | etx | Over Voltage Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Voltage Limit
Protection | VoltageRelay | VoltageRelay | overVoltageLockoutTime | overVoltageLockoutTime | Seconds |  | etx | Lockout Time when Trip at Over Voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Voltage Lockout Time
Protection | VoltageRelay | VoltageRelay | underVoltageDelay | underVoltageDelay | Seconds |  | etx | Under Voltage Trip Delay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Under Voltage Trip Delay
Protection | VoltageRelay | VoltageRelay | underVoltageLimit | underVoltageLimit | Voltage |  | etx | Under Voltage Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Under Voltage Limit
Protection | VoltageRelay | VoltageRelay | underVoltageLockoutTime | underVoltageLockoutTime | Seconds |  | etx | Lockout Time when Trip at Under Voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Under Voltage Lockout Time
RDF_Import | sysRdfContainer | sysRdfContainer | TypeName | TypeName | String28 |  | spc | Specifies the type this container applies to. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Type Name
Reservation | TiePoint | TiePoint | tiePointMWRating | tiePointMWRating | ActivePower |  | cim | The MW rating of the tie point. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tie Point MW Rating
Reservation | TransmissionPath | TransmissionPath | availTransferCapability | availTransferCapability | ActivePower |  | cim | The available transmission capability of a transmission path for the reference direction. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Available Transfer Capability
Reservation | TransmissionPath | TransmissionPath | parallelPathFlag | parallelPathFlag | Boolean | FALSE | cim | Flag which indicates if the transmission path is also a designated interconnection 'parallel path'. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Parallel Path Flag
Reservation | TransmissionPath | TransmissionPath | totalTransferCapability | totalTransferCapability | ActivePower |  | cim | The total transmission capability of a transmission path in the reference direction. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Total Transfer Capability

## Associations
Package | ClassA | Association | ClassB | ClassARoleName (RDF RoleA) | ClassARoleName (RDF RoleB) | Cardinality RoleA | Cardinality RoleB | Association Type | Name Space | CPSM Nerc | ABB / MMS | Areva / EMS | ABB / OS | Nexant / CRR | PTI / Planning | Lodestar / Settlement data | NMMS Label
CIMCore | BasePower | MemberOf | BaseVoltage | BasePower | BaseVoltage | 0..1 | 0..1 | ParentChild | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | BaseVoltage
CIMCore | Bay | MemberOf | Substation | Contains_Bays | MemberOf_Substation | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Substation
CIMCore | Bay | MemberOf | VoltageLevel | Contains_Bays | MemberOf_VoltageLevel | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | FALSE | FALSE |  | FALSE |  | VoltageLevel
CIMCore | ConductingEquipment | UsesA | BaseVoltage | ConductingEquipments | BaseVoltage | 0..n | 0..1 | Reference | cim | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | BaseVoltage
CIMCore | ConductingEquipment | ProtectedBy | ProtectionEquipment | ConductingEquipments | ProtectionEquipments | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Protected By (ProtectionEquipment)
CIMCore | CurveData | HasA | Curve | CurveScheduleDatas | CurveSchedule | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | CurveSchedule
CIMCore | Equipment | MemberOf | EquipmentContainer | Contains_Equipments | MemberOf_EquipmentContainer | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | EquipmentContainer
CIMCore | Equipment | HasTypeOf | EquipmentType | GenericEquipment | EquipmentType | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has Type Of (EquipmentType)
CIMCore | Equipment | AssociatesDAM | LimitLogicType | Equipment | DAM_LLT | 0..1 | 0..n | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Associates DAM (LimitLogicType)
CIMCore | Equipment | AssociatesRUC | LimitLogicType | Equipment | RUC_LLT | 0..1 | 0..n | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Associates RUC (LimitLogicType)
CIMCore | IdentifiedObject | BelongsTo | ModelingAuthoritySet | IdentifiedObjects | ModelingAuthoritySet | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Belongs To (ModelingAuthoritySet)
CIMCore | IrregularTimePoint | MemberOf | IrregularIntervalSchedule | TimePoints | IntervalSchedule | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | IrregularIntervalSchedule
CIMCore | ModelingAuthoritySet | MemberOf | ModelingAuthority | ModelingAuthoritySets | ModelingAuthority | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Maintained By (ModelingAuthority)
CIMCore | PowerSystemResource | MemberOf | Company | Operates_PSRs | OperatedBy_Companies | 0..n | 0..1 | ParentChild | cim | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | Company
CIMCore | PowerSystemResource | OperatedBy | Operatorship | PowerSystemResource | Operatorship | 0..n | 0..n | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Operated By (Operatorship)
CIMCore | PowerSystemResource | OwnedBy | Ownership | PowerSystemResource | Ownership | 0..n | 0..n | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Own Percent (Ownership)
CIMCore | PSRType | HasA | PowerSystemResource | PSRType | PowerSystemResource | 0..1 | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (PSRType)
CIMCore | RegularTimePoint | MemberOf | RegularIntervalSchedule | TimePoints | IntervalSchedule | 0..n | 1 | ParentChild | cim | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | RegularIntervalSchedule
CIMCore | SubControlArea | Contains | GeneratingUnit | SubControlArea | GeneratingUnits | 0..1 | 0..n | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | GeneratingUnit
CIMCore | SubGeographicalRegion | MemberOf | GeographicalRegion | Regions | Region | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | GeographicalRegion
CIMCore | SubGeographicalRegion | References | HostControlArea | SubGeographicalRegion | HostControlArea | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (HostControlArea)
CIMCore | Substation | References | HostControlArea | Substation | HostControlArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (HostControlArea)
CIMCore | Substation | Has | PermissionArea | Substation | PermissionArea | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (PermissionArea)
CIMCore | Substation | MemberOf | SubControlArea | Contain_Substations | MemberOf_SubControlArea | 0..n | 0..1 | ParentChild | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | SubControlArea
CIMCore | Substation | MemberOf | SubGeographicalRegion | Substations | Region | 0..n | 0..1 | ParentChild | cim | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | SubGeographicalRegion
CIMCore | Substation | MemberOf | SubLoadArea | Substation | LoadZone | 0..n | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | LoadZone
CIMCore | Terminal | ExternalConnectionFor | ConductingEquipment | Terminals | ConductingEquipment | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | ConductingEquipment
CIMCore | Terminal | ConnectedTo | ConnectivityNode | Terminals | ConnectivityNode | 0..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | ConnectivityNode
CIMCore | VoltageLevel | HasA | BaseVoltage | VoltageLevel | BaseVoltage | 0..n | 1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | BaseVoltage
CIMCore | VoltageLevel | MemberOf | Substation | Contains_VoltageLevels | MemberOf_Substation | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | Substation
CIMGenerationDynamics | CombustionTurbine | Uses | HeatRecoveryBoiler | CombustionTurbines | HeatRecoveryBoiler | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | May Have (HeatRecoveryBoiler)
CIMGenerationDynamics | CTTEMPMWCurve | MemberOf | CombustionTurbine | CTTempMWCurve | CombustionTurbine | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | CombustionTurbine
CIMGenerationDynamics | SteamSupply | Supplies | SteamTurbine | SteamSupplys | SteamTurbines | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Supplies
CIMLoadModel | AreaLossCurve | HasA | LoadArea | AreaLossCurves | LoadArea | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | LoadArea
CIMLoadModel | ConformLoad | AssignedTo | ConformLoadGroup | EnergyConsumers | LoadGroup | 0..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | Assigned To (ConformLoadGroup)
CIMLoadModel | ConformLoadSchedule | MemberOf | ConformLoadGroup | ConformLoadSchedules | ConformLoadGroup | 0..n | 1 | ParentChild | cim | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | ConformLoadGroup
CIMLoadModel | LoadDemandModel | BasedOn | DayType | LoadDemandModels | DayType | 0..n | 0..1 | Attributive | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Based On (DayType)
CIMLoadModel | LoadDemandModel | MemberOf | EnergyConsumer | LoadDemandModels | EnergyConsumer | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | EnergyConsumer
CIMLoadModel | LoadDemandModel | BasedOn | Season | LoadDemandModels | BasisFor | 0..n | 0..1 | Attributive | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Based On (Season)
CIMLoadModel | LoadGroup | MemberOf | SubLoadArea | LoadGroups | SubLoadArea | 0..n | 1 | ParentChild | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | SubLoadArea
CIMLoadModel | NonConformLoad | AssignedTo | NonConformLoadGroup | EnergyConsumers | LoadGroup | 0..n | 0..1 | Reference | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Assigned To (NonConformLoadGroup)
CIMLoadModel | NonConformLoadSchedule | MemberOf | NonConformLoadGroup | NonConformLoadSchedules | NonConformLoadGroup | 0..n | 1 | ParentChild | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | NonConformLoadGroup
CIMLoadModel | SeasonDayTypeSchedule | BasedOn | DayType | SeasonDayTypeSchedules | DayType | 0..n | 0..1 | Attributive | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Based On (DayType)
CIMLoadModel | SeasonDayTypeSchedule | BasedOn | Season | SeasonDayTypeSchedules | Season | 0..n | 0..1 | Attributive | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Based On (Season)
CIMLoadModel | StationSupply | Follows | SynchronousMachine | StationSupply | SynchronousMachine | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Follows (SynchronousMachine)
CIMLoadModel | SubLoadArea | MemberOf | LoadArea | SubLoadAreas | LoadArea | 0..n | 1 | ParentChild | cim | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | LoadArea
CIMMeas | AccumulatorLimit | MemberOf | AccumulatorLimitSet | Limits | LimitSet | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | AccumulatorLimitSet
CIMMeas | AccumulatorLimitSet | Limits | Accumulator | LimitSets | Measurements | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Limits (Accumulator)
CIMMeas | AccumulatorValue | MemberOf | Accumulator | Contain_MeasurementValues | MemberOf_Measurement | 0..n | 1 | ParentChild | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Accumulator
CIMMeas | AnalogLimit | HasNameOf | AnalogLimitName | AnalogLimit | AnalogLimitName | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has Name Of (AnalogLimitName)
CIMMeas | AnalogLimit | MemberOf | AnalogLimitSet | Limits | LimitSet | 0..n | 1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | AnalogLimitSet
CIMMeas | AnalogLimit | BelongTo | LimitAlarmCategory | AnalogLimit | LimitAlarmCategory | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belong To (LimitAlarmCategory)
CIMMeas | AnalogLimitSet | Limits | Analog | LimitSets | Measurements | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | Analog
CIMMeas | AnalogValue | Has | AccuracyClass | AnalogValue | AccuracyClass | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (AccuracyClass)
CIMMeas | AnalogValue | MemberOf | Analog | Contain_MeasurementValues | MemberOf_Measurement | 0..n | 1 | ParentChild | cim | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | Analog
CIMMeas | AnalogValue | BelongTo | AnalogAlarmCategory | AnalogValue | AnalogAlarmCategory | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belong To (AnalogAlarmCategory)
CIMMeas | AnalogValue | Contain | AnalogLimit | AnalogValue | AnalogLimit | 0..n | 0..n | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Contain (AnalogLimit)
CIMMeas | AnalogValue | HasNameOf | AnalogName | AnalogValue | AnalogName | 0..n | 0..1 | Attributive | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has Name Of (AnalogName)
CIMMeas | AnalogValue | IncludedIn | ExceptionListDisplay | AnalogValue | ExceptionListDisplay | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Included In (ExceptionListDisplay)
CIMMeas | Command | ControlledBy | Discrete | ControlledBy_Control | MeasuredBy_Measurement | 0..1 | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Controlled By (Command)
CIMMeas | Control | UsesA | ControlType | Control | ControlType | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Uses A (ControlType)
CIMMeas | Control | Controls | RegulatingCondEq | Controls | ControlledBy_RegulatingCondEq | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Controls (RegulatingCondEq)
CIMMeas | Control | ControlledBy | RemoteControl | Control | RemoteControl | 1 | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Controlled By (RemoteControl)
CIMMeas | Control | Controls | Unit | Controls | Unit | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Controls (Unit)
CIMMeas | Discrete | AliasedBy | ValueAliasSet | Discrete | ValueAliasSet | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Aliased By (ValueAliasSet)
CIMMeas | DiscreteValue | Has | ConversionTable | DiscreteValue | ConversionTable | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (ConversionTable)
CIMMeas | DiscreteValue | MemberOf | Discrete | Contain_MeasurementValues | MemberOf_Measurement | 0..n | 1 | ParentChild | cim | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | Contains (Discrete)
CIMMeas | DiscreteValue | BelongTo | DiscreteAlarmCategory | DiscreteValue | DiscreteAlarmCategory | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belong To (DiscreteAlarmCategory)
CIMMeas | DiscreteValue | HasNameOf | DiscreteName | DiscreteValue | DiscreteName | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has Name Of (DiscreteName)
CIMMeas | DiscreteValue | HasTypeOf | DiscreteType | DiscreteValue | DiscreteType | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has Type Of (DiscreteType)
CIMMeas | DiscreteValue | IncludedIn | ExceptionListDisplay | DiscreteValue | ExceptionListDisplay | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Included In (ExceptionListDisplay)
CIMMeas | LimitSet | HasA | Season | LimitSets | Season | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (Season)
CIMMeas | Measurement | UsesA | LimitSet | Measurements | LimitSets | 0..n | 0..n | Reference | cim | TRUE | TRUE | FALSE | FALSE |  | FALSE |  | LimitSet
CIMMeas | Measurement | UsesA | MeasurementType | Measurements | MeasurementType | 0..n | 0..1 | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | MeasurementType
CIMMeas | Measurement | OperatedBy | Operatorship | Measurement | Operatorship | 0..n | 0..n | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Operated By (Operatorship)
CIMMeas | Measurement | OwnedBy | Ownership | Measurement | Ownership | 0..n | 0..n | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Owned By (Ownership)
CIMMeas | Measurement | MemberOf | PowerSystemResource | Contains_Measurements | MemberOf_PSR | 0..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | PowerSystemResource
CIMMeas | Measurement | MeasuredBy | Terminal | Measurements | Terminal | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Terminal
CIMMeas | Measurement | UsesA | Unit | Measurements | Unit | 0..n | 0..1 | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Unit
CIMMeas | MeasurementValue | CalculatedBy | Calculation | MeasurementValue | Calculation | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Calculated By (Calculation)
CIMMeas | MeasurementValue | References | IccpQualityConversionSet | MeasurementValue | IccpQualityConversionSet | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (IccpQualityConversionSet)
CIMMeas | MeasurementValue | GroupedBy | MeasurementGroup | MeasurementValue | MemberOf_MeasurementGroup | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Grouped By (MeasurementGroup)
CIMMeas | MeasurementValue | HasA | MeasurementValueSource | MeasurementValues | MeasurementValueSource | 0..n | 0..1 | Reference | cim | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | MeasurementValueSource
CIMMeas | MeasurementValue | LinksTo | RemoteSource | MeasurementValue | RemoteSource | 1 | 0..1 | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Links To (RemoteSource)
CIMMeas | MeasurementValue | BelongTo | Site | MeasurementValue | Site | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belong To (Site)
CIMMeas | MeasurementValue | HasSecondary | Site | MeasurementValue | SecondarySite | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has Secondary (Site)
CIMMeas | MeasurementValue | Has | SitePermission | MeasurementValue | SitePermission | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has (SitePermission)
CIMMeas | MeasurementValueQuality | MemberOf | MeasurementValue | MeasurementValueQuality | MeasurementValue | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | MeasurementValue
CIMMeas | MeasurementValueSource | MemberOf | Company | MeasurementValueSource | Company | 0..n | 1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Company
CIMMeas | SetPoint | ControlledBy | Analog | ControlledBy_Control | MeasuredBy_Measurement | 0..1 | 0..1 | ParentChild | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Analog
CIMMeas | SetPoint | Contain | AnalogValue | Setpoint | AnalogValue | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Contain (AnalogValue)
CIMMeas | SetPoint | HasNameOf | SetPointName | SetPoint | SetPointName | 0..n | 1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has Name Of (SetPointName)
CIMMeas | StringMeasurementValue | MemberOf | StringMeasurement | Contains_MeasurementValues | MemberOf_Measurement | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | StringMeasurement
CIMMeas | ValueAliasSet | Controls | Command | ValueAliasSet | Controls | 0..1 | 0..n | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Controls (Command)
CIMMeas | ValueToAlias | MemberOf | ValueAliasSet | Values | ValueAliasSet | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ValueAliasSet
CIMOutage | ClearanceTag | AssignedTo | ConductingEquipment | ClearanceTags | ConductingEquipment | 0..n | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Assigned To (ConductingEquipment)
CIMOutage | OutageSchedule | MemberOf | PowerSystemResource | OutageSchedule | PSR | 0..1 | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | PowerSystemResource
CIMOutage | OutageSchedule | OperatedBy | SwitchingOperation | OutageSchedule | SwitchingOperations | 0..1 | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Operated By (SwitchingOperation)
CIMProduction | AirCompressor | MemberOf | CAESPlant | Contain_AirCompressor | MemberOf_CAESPlant | 1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | CAESPlant
CIMProduction | AirCompressor | DrivenBy | CombustionTurbine | Drives_AirCompressor | DrivenBy_CombustionTurbine | 0..1 | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Driven By (CombustionTurbine)
CIMProduction | CombinedCyclePlant | References | ResourceController | CombinedCyclePlant | ResourceController | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | References (ResourceController)
CIMProduction | EmissionAccount | MemberOf | ThermalGeneratingUnit | EmmissionAccounts | ThermalGeneratingUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
CIMProduction | EmissionCurve | MemberOf | ThermalGeneratingUnit | EmissionCurves | ThermalGeneratingUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
CIMProduction | FossilFuel | Fuels | ThermalGeneratingUnit | FossilFuels | ThermalGeneratingUnit | 0..n | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Fuels (FossilFuel)
CIMProduction | FuelAllocationSchedule | Requires | FossilFuel | FuelAllocationSchedule | FossilFuel | 0..n | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Requires (FossilFuel)
CIMProduction | FuelAllocationSchedule | MemberOf | ThermalGeneratingUnit | FuelAllocationSchedules | ThermalGeneratingUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
CIMProduction | GeneratingUnit | PartOf | DCTie | GeneratingUnit | DCTie | 1 | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Part Of (DCTie)
CIMProduction | GeneratingUnit | HasA | GenerationType | GeneratingUnit | GenerationType | 0..n | 0..1 | Attributive | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (GenerationType)
CIMProduction | GeneratingUnit | PartOf | PrivateAreaNetwork | GeneratingUnit | PrivateAreaNetwork | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Part Of (PrivateAreaNetwork)
CIMProduction | GeneratingUnit | HasA | ResourceNode | GeneratingUnit_HasA | HasA_ResourceNode | 0..n | 0..1 | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (ResourceNode)
CIMProduction | GeneratingUnit | MemberOf | SubLoadArea | GeneratingUnit | SubLoadArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Member Of (SubLoadArea)
CIMProduction | GenUnitOpCostCurve | MemberOf | GeneratingUnit | GenUnitOpCostCurves | GeneratingUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | GeneratingUnit
CIMProduction | GenUnitOpSchedule | ScheduleFor | GeneratingUnit | GenUnitOpSchedule | GeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | GeneratingUnit
CIMProduction | GrossToNetMWCurve | MemberOf | GeneratingUnit | GrossToNetMWCurves | GeneratingUnit | 0..n | 0..1 | ParentChild | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | GeneratingUnit
CIMProduction | HeatInputCurve | MemberOf | ThermalGeneratingUnit | HeatInputCurve | ThermalGeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
CIMProduction | HeatRateCurve | MemberOf | ThermalGeneratingUnit | HeatRateCurve | ThermalGeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
CIMProduction | HydroGenEfficiencyCurve | HasA | HydroGeneratingUnit | HydroGeneratingEfficiencyCurves | HydroGeneratingUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroGeneratingUnit
CIMProduction | HydroGeneratingUnit | MemberOf | HydroPowerPlant | Contain_HydroGeneratingUnit | MemberOf_HydroPowerPlant | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroPowerPlant
CIMProduction | HydroPump | MemberOf | HydroPowerPlant | Contain_HydroPumps | MemberOf_HydroPowerPlant | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroPowerPlant
CIMProduction | HydroPump | DrivenBy | SynchronousMachine | Drives_HydroPump | DrivenBy_SynchronousMachine | 0..1 | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroPump
CIMProduction | HydroPumpOpSchedule | HasA | HydroPump | HydroPumpOpSchedule | HydroPump | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroPump
CIMProduction | IncrementalHeatRateCurve | MemberOf | ThermalGeneratingUnit | IncrementalHeatRateCurve | ThermalGeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
CIMProduction | InflowForecast | HasA | Reservoir | InflowForecast | Reservoir | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Reservoir
CIMProduction | LevelVsVolumeCurve | HasA | Reservoir | LevelVsVolumeCurve | Reservoir | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Reservoir
CIMProduction | PenstockLossCurve | HasA | HydroGeneratingUnit | PenstockLossCurve | HydroGeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroGeneratingUnit
CIMProduction | Reservoir | ProvidesWaterTo | HydroPowerPlant | Reservoir | HydroPowerPlants | 0..1 | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Provides Water To (HydroPowerPlants
CIMProduction | Reservoir | SpillsTo | Reservoir | SpillsInto | SpillsFrom | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Spills To (Reservoir)
CIMProduction | ShutdownCurve | MemberOf | ThermalGeneratingUnit | ShutdownCurve | ThermalGeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
CIMProduction | StartIgnFuelCurve | MemberOf | StartupModel | StartIgnFuelCurve | StartupModel | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | StartupModel
CIMProduction | StartMainFuelCurve | MemberOf | StartupModel | StartMainFuelCurve | StartupModel | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | StartupModel
CIMProduction | StartRampCurve | MemberOf | StartupModel | StartRampCurve | StartupModel | 0..1 | 1 | ParentChild | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | StartupModel
CIMProduction | StartupModel | MemberOf | ThermalGeneratingUnit | StartupModel | ThermalGeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
CIMProduction | SteamSendoutSchedule | MemberOf | CogenerationPlant | SteamSendoutSchedule | CogenerationPlant | 0..1 | 0..1 | ParentChild | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | CogenerationPlant
CIMProduction | TailbayLossCurve | HasA | HydroGeneratingUnit | TailbayLossCurve | HydroGeneratingUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroGeneratingUnit
CIMProduction | TargetLevelSchedule | HasA | Reservoir | TargetLevelSchedule | Reservoir | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Reservoir
CIMProduction | ThermalGeneratingUnit | MemberOf | CAESPlant | Contain_ThermalGeneratingUnit | MemberOf_CAESPlant | 0..1 | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Member Of (CAESPlant)
CIMProduction | ThermalGeneratingUnit | MemberOf | CogenerationPlant | Contain_ThermalGeneratingUnits | MemberOf_CogenerationPlant | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Member Of (CogenerationPlant)
CIMProduction | ThermalGeneratingUnit | MemberOf | CombinedCyclePlant | Contain_ThermalGeneratingUnits | MemberOf_CombinedCyclePlant | 0..n | 0..1 | Reference | cim | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | Member Of (CombinedCyclePlant)
CIMProtection | ProtectionEquipment | sensedBus | BusbarSection | ProtectionEquipment | BusbarSection | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | sensedBus (BusbarSection)
CIMProtection | ProtectionEquipment | Operates | Switch | OperatedBy_ProtectionEquipments | Operates_Switches | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Operates (Switch)
CIMProtection | ProtectionEquipment | HasA | Unit | ProtectionEquipments | Unit | 0..n | 1 | Attributive | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (Unit)
CIMProtection | RecloseSequence | MemberOf | Switch | RecloseSequences | Breaker | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Switch
CIMSCADA | RemotePoint | MemberOf | RemoteUnit | Contains_RemotePoints | MemberOf_RemoteUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | RemoteUnit
CIMSCADA | RemoteUnit | AttachedTo | CommunicationLink | Contain_RemoteUnits | MemberOf_CommunicationLinks | 0..n | 1..n | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Attached To (CommunicationLink)
CIMTopology | ConnectivityNode | BelongsTo | ConnectivityNodeGroup | ConnectivityNode | ConnectivityNodeGroup | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | ConnectivityNodeGroup
CIMTopology | ConnectivityNode | MemberOf | EquipmentContainer | ConnectivityNodes | MemberOf_EquipmentContainer | 0..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | EquipmentContainer
CIMTopology | ConnectivityNode | MemberOf | TopologicalNode | ConnectivityNodes | TopologicalNode | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TopologicalNode
CIMTopology | TopologicalNode | MemberOf | TopologicalIsland | TopologicalNodes | TopologicalIsland | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TopologicalIsland
CIMWires | ACLineSegment | BelongsTo | SubLoadArea | arrACLineSegment | ToLoadZone | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (LoadZone)
CIMWires | ACLineSegment | BelongsFrom | SubLoadArea | depACLineSegment | FromLoadZone | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs From (LoadZone)
CIMWires | CompositeSwitch | MemberOf | Substation | Contains_CompositeSwitches | MemberOf_Substation | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Substation
CIMWires | Conductor | MemberOf | ConductorType | Conductors | ConductorType | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Conductor
CIMWires | Conductor | AssignsLosses | SubControlArea | Conductor | SubControlArea | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Assigns Losses (SubControlArea)
CIMWires | EnergyConsumer | HasA | AccuracyClass | EnergyConsumer | AccuracyClass | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (AccuracyClass)
CIMWires | EnergyConsumer | PartOf | DCTie | EnergyConsumer | DCTie | 1 | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Part Of (DCTie)
CIMWires | EnergyConsumer | AssignedTo | LoadArea | EnergyConsumers | LoadArea | 0..n | 0..1 | Reference | cim | TRUE | TRUE | FALSE | FALSE |  | FALSE |  | LoadArea
CIMWires | EnergyConsumer | HasA | LoadType | EnergyConsumer | LoadType | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | LoadType
CIMWires | EnergyConsumer | BelongsTo | PlanningArea | EnergyConsumer | PlanningArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (PlanningArea)
CIMWires | EnergyConsumer | BelongsTo | PlanningZone | EnergyConsumer | PlanningZone | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (PlanningZone)
CIMWires | EnergyConsumer | MemberOf | PowerCutZone | EnergyConsumers | PowerCutZone | 1..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | PowerCutZone
CIMWires | EnergyConsumer | PartOf | PrivateAreaNetwork | EnergyConsumer | PrivateAreaNetwork | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Part Of (PrivateAreaNetwork)
CIMWires | EnergyConsumer | BelongsTo | SubLoadArea | LoadZone | EnergyConsumer | 0..n | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Belongs To (LoadZone)
CIMWires | EnergyConsumer | MemberOf | SubLoadArea | EnergyConsumers | LoadZone | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | LoadZone
CIMWires | HeatExchanger | MemberOf | PowerTransformer | HeatExchanger | PowerTransformer | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | PowerTransformer
CIMWires | Line | MemberOf | SubGeographicalRegion | Lines | Region | 0..n | 0..1 | ParentChild | cim | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | SubGeographicalRegion
CIMWires | MVArCapabilityCurve | HasA | SynchronousMachine | MVArCapabilityCurves | SynchronousMachines | 0..n | 1 | ParentChild | cim | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | SynchronousMachine
CIMWires | PowerTransformer | HasAMaster | PowerTransformer | PowerTransformer | PowerTransformer | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A Master (PowerTransformer)
CIMWires | RegulatingCondEq | RegulatedBy | LoadBasedRegulationCurve | RegulatingCondEq | LoadBasedRegulationCurve | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Regulated By (LoadBasedRegulationSchedule)
CIMWires | RegulatingCondEq | UsesA | Measurement | RegulatingCondEqs | Measurement | 0..n | 0..1 | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Uses A (Measurement)
CIMWires | RegulatingCondEq | HasA | RegulationSchedule | RegulatingCondEqs | RegulationSchedule | 0..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | RegulationSchedule
CIMWires | RegulatingCondEq | Regulates | Terminal | RegulatingCondEquipment | Terminal | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Regulates (Terminal)
CIMWires | RegulationSchedule | HasA | DayType | RegulationSchedule | DayType | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (DayType)
CIMWires | RegulationSchedule | HasA | Season | RegulationSchedule | Season | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (Season)
CIMWires | ShuntCompensator | SwitchedBy | Switch | ShuntCompensator | Switch | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Switched By (Switch)
CIMWires | Switch | MemberOf | CompositeSwitch | Switches | CompositeSwitch | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | CompositeSwitch
CIMWires | Switch | HasA | EnergyConsumerResource | Switch | LR | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HasA (LoadResource)
CIMWires | Switch | operatedDuringStartStop | GeneratingUnit | Switch | GeneratingUnit | 0..n | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | operatedDuringStartStop (GeneratingUnit)
CIMWires | Switch | OperatedBy | SwitchingOperation | Switches | SwitchingOperations | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Operated By (SwitchingOperation)
CIMWires | SynchronousMachine | HasA | AccuracyClass | SynchronousMachine | AccuracyClass | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (AccuracyClass)
CIMWires | SynchronousMachine | MemberOf | GeneratingUnit | Contains_SynchronousMachines | MemberOf_GeneratingUnit | 0..1 | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | GeneratingUnit
CIMWires | SynchronousMachine | HasDefault | MVArCapabilityCurve | InitiallyUsedBySynchronousMachine | InitiallyUsesMVArCapabilityCurve | 1..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | Has Default (MVArCapabilityCurve)
CIMWires | SynchronousMachine | Drives | PrimeMover | Drives_SynchronousMachine | DrivenBy_PrimeMover | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Drives (SynchronousMachine)
CIMWires | SynchronousMachine | BelongsTo | SubLoadArea | LoadZone | SynchronousMachine | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (LoadZone)
CIMWires | TapChanger | RegulatedBy | LoadBasedRegulationCurve | TapChanger | LoadBasedRegulationCurve | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Regulated By (LoadBasedRegulationCurve)
CIMWires | TapChanger | Regulates | Measurement | TapChangers | Measurement | 0..n | 0..1 | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Regulates (Measurement)
CIMWires | TapChanger | HasA | RegulationSchedule | TapChangers | RegulationSchedule | 0..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | RegulationSchedule
CIMWires | TapChanger | HasAMaster | TapChanger | TapChanger | TapChanger | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A Master (TapChanger)
CIMWires | TapChanger | HasA | TapRatioCurve | TapChanger | TapRatioCurve | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (TapRatioCurve)
CIMWires | TapChanger | Regulates | Terminal | TapChanger | Terminal | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Regulates (Terminal)
CIMWires | TapChanger | HasA | TransformerWinding | TapChangers | TransformerWinding | 0..n | 1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TransformerWinding
CIMWires | TransformerWinding | HasA | PowerTransformer | Contains_TransformerWindings | MemberOf_PowerTransformer | 0..n | 1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | PowerTransformer
CIMWires | TransformerWinding | To | WindingTest | To_TransformerWindings | To_WindingTest | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | To (WindingTest)
CIMWires | TransformerWinding | FromTest | WindingTest | From_TransferWinding | From_WindingTests | 1 | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | From (TransformerWinding)
CIMWires | VoltageControlZone | ControlledBy | BusbarSection | VoltageControlZone | BusbarSection | 0..1 | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Controlled By (BusbarSection)
CIMWires | VoltageControlZone | RegulatedBy | RegulationSchedule | VoltageControlZones | RegulationSchedule | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Regulated By (RegulationSchedule)
CIMWires | WireArrangement | MemberOf | ConductorType | WireArrangements | ConductorType | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ConductorType
CIMWires | WireArrangement | MemberOf | WireType | WireArrangements | WireType | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | WireType
Common | Domain | MemberOf | sysOrphan | Domain_MemberOf | MemberOf_sysOrphan | 0..n | 0..1 | ParentChild | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | sysOrphan
Engineering_sysTreeCategory | sysTreeCategory | OwnedBy | Ownership | sysTreeCategory | Ownership | 0..n | 0..n | Reference | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | OwnedBy (Ownership)
Engineering_sysTreeCategory | sysTreeCategory | MemberOf | RootType | sysTreeCategory_MemberOf | MemberOf_RootType | 0..n | 0..n | ParentChild | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | RootType
ETX | AggregateHub | HasA | SettlementHUB | AggregateHub | SettlementHUB | 0..n | 0..n | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (SettlementHub)
ETX | AncillaryQualification | MemberOf | CombinedCyclePlant | AncillaryQualification | CombinedCyclePlant | 0..1 | 0..1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | CombinedCyclePlant
ETX | AncillaryQualification | MemberOf | EnergyConsumerResource | AncillaryQualification | EnergyConsumerResource | 0..1 | 0..1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | EnergyConsumerResource
ETX | AncillaryQualification | MemberOf | GeneratingUnit | AncillaryQualification | GeneratingUnit | 0..1 | 0..1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | GeneratingUnit
ETX | Configuration | HasA | LogicalConfiguration | Configuration | LogicalConfiguration | 1..n | 0..1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | LogicalConfiguration
ETX | ConfigurationMember | IsMemberOf | Configuration | ConfigurationMember | Configuration | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Configuration
ETX | ConfigurationMember | HasA | ThermalGeneratingUnit | ConfigurationMember | ThermalGeneratingUnit | 0..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (ThermalGeneratingUnit)
ETX | ElectricalBus | MemberOf | ConnectivityNode | ElectricalBus_HasA | ConnectivityNode | 0..1 | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | ConnectivityNode
ETX | EnergyConsumerResource | HasA | EnergyConsumer | LR_HasA | HasA_EnergyConsumer | 0..n | 1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (EnergyConsumer)
ETX | EnergyConsumerResource | References | HostControlArea | EnergyConsumerResource | HostControlArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (HostControlArea)
ETX | EnergyConsumerResource | OperatedBy | Operatorship | EnergyConsumerResource | Operatorship | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Energy Consumer Operatorship
ETX | EnergyConsumerResource | OwnedBy | Ownership | EnergyConsumerResource | Ownership | 0..n | 0..n | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Energy Consumer Ownership
ETX | EnergyConsumerResource | HasA | ResourceNode | LoadResource | HasA_ResourceNode | 0..n | 0..1 | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (ResourceNode)
ETX | EPSMeter | HasA | Configuration | EPSMeter_HasA | Configuration | 0..n | 0..n | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (Configuration)
ETX | EPSMeter | HasA | GeneratingUnit | EPSMeter_HasA | GeneratingUnit | 0..n | 0..n | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (GeneratingUnit)
ETX | EPSMeter | HasA | MeterConfiguration | EPSMeter_HasA | MeterConfiguration | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | MeterConfiguration
ETX | EPSMeter | HasA | PricingVector | EPSMeter_HasA | HasA_PricingVector | 1 | 1..n | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (PricingVector)
ETX | FlowgateElement | HasA | ConductingEquipment | FlowgateElement | ConductingEquipment | 0..1 | 0..1 | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (ConductingEquipment)
ETX | FlowgateElement | MemberOf | FlowgateGroup | FlowgateElement | FlowgateGroup | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FlowgateGroup
ETX | FlowgateElement | HasA | Terminal | FlowgateElement | Terminal | 0..1 | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (Terminal)
ETX | HUBBus | HasA | ConnectivityNodeGroup | HasAHUBBus | HasAConnectivityNodes | 0..1 | 1..n | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (ConnectivityNodeGroup)
ETX | HUBBus | MemberOf | SettlementHUB | HubBus | SettlementHub | 1..n | 1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | SettlementHub
ETX | IccpQualityConversion | MemberOf | IccpQualityConversionSet | IccpQualityConversion | IccpQualityConversionSet | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | IccpQualityConversionSet
ETX | IccpQualityConversionSet | References | Ownership | IccpQualityConversionSet | Ownership | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (Ownership)
ETX | LogicalConfiguration | HasA | CombinedCyclePlant | LogicalConfiguration | CombinedCyclePlant | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | CombinedCyclePlant
ETX | Operatorship | MemberOf | Company | Operatorship_OperatesPartOf | Company | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Company
ETX | Operatorship | HasAPrimary | Contact | Operator_HasAPrimary | Contact | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A Primary (Contact)
ETX | Operatorship | HasASecondary | Contact | Operator_HasASecondary | Contact | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A Secondary (Contact)
ETX | Ownership | MemberOf | Company | Owner_OwnsPartOfCompany | Company | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Company
ETX | Ownership | HasAPrimary | Contact | Owner_HasAPrimary | Contact | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A Primary (Contact)
ETX | Ownership | HasASecondary | Contact | Owner_HasASecondary | Contact | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A Secondary (Contact)
ETX | PricingVector | MemberOf | ElectricalBus | PricingLocation | ElectricalBus | 0..n | 1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | ElectricalBus
ETX | PricingVector | HasA | Terminal | HasA_PricingVector | Terminal | 0..n | 1 | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (Terminal)
ETX | PrivateAreaNetwork | HasA | ResourceNode | PrivateAreaNetwork_HasA | HasA_ResourceNode | 0..1 | 0..n | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (ResourceNode)
ETX | PseudoTerminal | For | CombinedCyclePlant | PseudoTerminal | CombinedCyclePlant | 0..1 | 0..1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | CombinedCyclePlant
ETX | PseudoTerminal | For | GenericEquipment | PseudoTerminal | GenericEquipment | 0..1 | 0..1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | GenericEquipment
ETX | PseudoTerminal | For | OwnerShareLimits | PseudoTerminal | OwnerShareLimits | 0..1 | 0..1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | OwnerShareLimits
ETX | ResourceNode | MemberOf | ElectricalBus | ResourceNode | ElectricalBus | 0..1 | 1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | ElectricalBus
ETX | SettlementLoadZone | Contains | Substation | SettlementLoadZone | Substation | 0..1 | 1..n | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Contains (Substation)
ETX | SettlementNOIELoadZone | Contains | EnergyConsumer | SettlementNOIELoadZone | EnergyConsumer | 0..1 | 0..n | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Contains (EnergyConsumer)
ETX | SupportLoadData | BelongTo | ConformLoad | SupportLoadData | ConformLoad | 0..1 | 1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ConformLoad
ETX | TransformerKluge | HasA | PowerTransformer | TransformerKluge | PowerTransformer | 0..1 | 0..n | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (PowerTransformer)
ETX | TransState | FromConfig | Configuration | TransState_FromConfig | FromConfig_Configuration | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | From Config (Configuration)
ETX | TransState | ToConfig | Configuration | TransState_ToConfig | ToConfig_Configuration | 0..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | To Config (Configuration)
ETX_ABB | SwitchSchedule | HasA | DayType | SwitchSchedule | DayType | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (DayType)
ETX_ABB | SwitchSchedule | HasA | Season | SwitchSchedule | Season | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (Season)
ETX_ABB | SwitchSchedule | MemberOf | Switch | SwitchSchedules | Switch | 0..n | 1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Switch
ETX_ABB | SyncMachineSchedule | HasA | DayType | SyncMachineSchedule | DayType | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (DayType)
ETX_ABB | SyncMachineSchedule | HasA | Season | SyncMachineSchedule | Season | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (Season)
ETX_ABB | SyncMachineSchedule | MemberOf | SynchronousMachine | SyncMachineSchedules | SynchronousMachines | 0..n | 1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | SynchronousMachine
ETX_ABB | TapSchedule | HasA | DayType | TapSchedule | DayType | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (DayType)
ETX_ABB | TapSchedule | HasA | Season | TapSchedule | Season | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (Season)
ETX_ABB | TapSchedule | MemberOf | TapChanger | TapSchedules | TapChanger | 0..n | 1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TapChanger
ETX_Areva | PhysicalTiePoint | AssociatedWith | Terminal | PhysicalTiePoint | Terminal | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Associated With (Terminal)
ETX_Areva | RampRateCurve | MemberOf | Configuration | RampRateCurve | Configuration | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Configuration
ETX_Areva | RampRateCurve | MemberOf | EnergyConsumerResource | RampRateCurve | EnergyConsumerResource | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Member Of (EnergyConsumerResource)
ETX_Areva | RampRateCurve | MemberOf | GeneratingUnit | RampRateCurve | GeneratingUnit | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Member Of (GeneratingUnit)
ETX_Areva | ResourceController | MemberOf | Substation | ResourceController | Substation | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Substation
ETX_Areva | TieCorridor | PartOf | DCTie | TieCorridor | DCTie | 1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TieCorridorPartOfDCTie
ETX_Areva | TieCorridor | ConnectsFrom | HostControlArea | TieCorridor_Out | From_HostControlArea | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Connects From (HostControlArea)
ETX_Areva | TieCorridor | ConnectsTo | HostControlArea | TieCorridor_In | To_HostControlArea | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | HostControlArea
ETX_Areva | TieCorridor | ConnectsTo | SubLoadArea | TieCorridor_In | To_SubLoadArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Connects To (SubLoadArea
ETX_Areva | TieCorridor | ConnectsFrom | SubLoadArea | TieCorridor_Out | From_SubLoadArea | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Connects From (SubLoadArea)
ETX_Areva | TieEnd | MemberOf | PhysicalTiePoint | TieEnd | PhysicalTiePoint | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | PhysicalTiePoint
ETX_Areva | TieLine | Reference | Substation | TieLine | Substation | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reference (Substation)
ETX_Areva | TieLine | HasA | Terminal | TieLine | Terminal | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Terminal
ETX_Areva | TieLine | BelongsTo | TieCorridor | TieLine | TieCorridor | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TieCorridor
ETXContingency | ContingencyElement | MemberOf | Contingency | ContingencyElement | MemberOf_Contingency | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Contingency
ETXContingency | ContingencyElement | HasA | Equipment | ContingencyElement | Equipment | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (Equipment)
ETXContingency | ContingencyGroupMember | HasA | Contingency | ContingencyGroupMember | Contingency | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (Contingency)
ETXContingency | ContingencyGroupMember | IsMemberOf | ContingencyGroup | ContingencyGroupMember | ContingencyGroup | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | ContingencyGroup
ETXLoadModel | EnergyConsumerAltConnection | TransferFrom | EnergyConsumer | TransferTo | TransferFrom_EnergyConsumer | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | EnergyConsumer
ETXLoadModel | EnergyConsumerAltConnection | TransferTo | EnergyConsumer | TransferFrom | TransferTo_EnergyConsumer | 0..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Transfer To (EnergyConsumer)
ETXMonitoring | AngleDifference | MonitorNodeA | ConnectivityNode | AngleDifference | ConnectivityNodeA | 0..n | 1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Monitor Node A (ConnectivityNode)
ETXMonitoring | AngleDifference | MonitorNodeB | ConnectivityNode | AngleDifference | ConnectivityNodeB | 0..n | 1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Monitor Node B (ConnectivityNode)
ETXMonitoring | AngleDifferenceLimitSet | HasA | AngleDifference | AngleDifferenceLimitSet | AngleDifference | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (AngleDifference)
ETXMonitoring | BranchGroup | References | Terminal | BranchGroup | Terminals | 0..n | 0..n | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | References (Terminals)
ETXMonitoring | BranchGroup | ReferencesInverse | Terminal | BranchGroup | InvTerminal | 0..n | 0..n | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | References Inverse (Terminal)
ETXMonitoring | BranchGroupTerminal | MemberOf | BranchGroup | BranchGroupTerminal | BranchGroup | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | BranchGroup
ETXMonitoring | BranchGroupTerminal | References | Terminal | BranchGroupTerminal | Terminal | 0..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | References (Terminal)
ETXMonitoring | Monitored | MemberOf | MonitoredGroup | Monitored | MonitoredGroup | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | MonitoredGroup
ETXMonitoring | VLSBusBarMonitored | IsMonitored | BusbarSection | VLSBusBarMonitored | BusbarSection | 0..1 | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Is Monitored (BusbarSection)
ETXMonitoring | VLSBusBarMonitored | Uses | VoltageLimitSet | VLSBusBarMonitored | VoltageLimitSet | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Uses (VoltageLimitSet)
ETXMonitoring | VoltageLimit | HasA | VoltageLimitSet | VoltageLimit | VoltageLimitSet | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (VoltageLimitSet)
ETXMonitoring | VoltageMonitored | IsMonitored | VoltageLevel | VoltageMonitored | VoltageLevel | 0..1 | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Is Monitored (VoltageLevel)
ETXMonitoring | VoltageMonitored | Uses | VoltageLimitSet | VoltageMonitored | VoltageLimitSet | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Uses (VoltageLimitSet)
ETXNetwork | PhaseShifterImpedanceCurve | HasA | TapChanger | PhaseShifterImpedanceCurve | TapChanger | 0..1 | 0..1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TapChanger
ETXNetwork | StationSupplyWRCurve | HasA | StationSupply | StationSupplyWRCurve | StationSupply | 0..1 | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | StationSupply
ETXNetwork | TransformerImpedanceCurve | HasA | TransformerWinding | TransformerImpedanceCurve | TransformerWinding | 0..1 | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TransformerWinding
ETXPlanning | ConnectivityNodeGroup | BelongsTo | PlanningArea | ConnectivityNodeGroup | PlanningArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | PlanningArea
ETXPlanning | ConnectivityNodeGroup | BelongsTo | PlanningZone | ConnectivityNodeGroup | PlanningZone | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | PlanningZone
ETXPlanning | PlanningBay | BelongsTo | VoltageLevel | PlanningBay | VoltageLevel | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | VoltageLevel
ETXPlanning | PlanningZone | BelongsTo | PlanningZoneGroup | PlanningZone | PlanningZoneGroup | 1..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | PlanningZoneGroup
ETXRASE | Gate | MemberOf | TriggerCondition | Gate | MemberOf_TriggerCondition | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (TriggerCondition)
ETXRASE | GateInputPin | MemberOf | Gate | GateInputPin | MemberOf_Gate | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Gate
ETXRASE | PinBranchGroup | BelongsTo | BranchGroup | PinBranchGroup | BranchGroup | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (BranchGroup)
ETXRASE | PinFlow | HasA | Terminal | PinFlow | Terminal | 0..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (Terminal)
ETXRASE | PinGate | HasA | Gate | PinGate | Gate | 0..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (Gate)
ETXRASE | PinSwitch | HasA | Switch | PinSwitch | Switch | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (Switch)
ETXRASE | PinTriggerCondition | HasA | TriggerCondition | PinTriggerCondition | TriggerCondition | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (TriggerCondition)
ETXRASE | PinVoltage | HasA | ConnectivityNode | ConnectivityNode | PinVoltage | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (ConnectivityNode)
ETXRASE | PrivateProtectiveActions | ActionsOfTrigger | StageTrigger | PrivateProtectiveActions | StageTrigger | 1 | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Actions Of Trigger (StageTrigger)
ETXRASE | ProtActACLineSegment | Reference | ACLineSegment | ProtActACLineSegment | ACLineSegment | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reference (ACLineSegment)
ETXRASE | ProtActAnalog | ReduceBy | AnalogValue | ProtActAnalog | AnalogValue | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reduce By (AnalogValue)
ETXRASE | ProtActEnergyConsumer | References | EnergyConsumer | ProtActEnergyConsumer | EnergyConsumer | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (EnergyConsumer)
ETXRASE | ProtActSeriesCompensator | Reference | SeriesCompensator | ProtActSeriesCompensator | SeriesCompensator | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reference (SeriesCompensator)
ETXRASE | ProtActStationReduction | References | Substation | ProtActStationReduction | Substation | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (Substation)
ETXRASE | ProtActSwitch | Reference | Switch | ProtActSwitch | Switch | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (Switch)
ETXRASE | ProtActSynchronousMachine | References | SynchronousMachine | ProtActSynchronousMachine | SynchronousMachine | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (SynchronousMachine)
ETXRASE | ProtActTransformerWinding | Reference | TransformerWinding | ProtActTransformerWinding | TransformerWinding | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reference (TransformerWinding)
ETXRASE | ProtectiveAction | ArmedBy | DiscreteValue | ProtectiveAction | DiscreteValue | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Armed By (DiscreteValue)
ETXRASE | ProtectiveAction | Contains | ProtectiveActions | ProtectiveAction | ProtectiveActions | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | ProtectiveActions
ETXRASE | ProtectiveActionShared | Has | SharedProtectiveActions | ProtectiveActionShared | SharedProtectiveActions | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (SharedProtectiveActions)
ETXRASE | RemedialActionScheme | BelongsTo | Contingency | RemedialActionScheme | Contigency | 0..n | 0..n | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (Contingency)
ETXRASE | Stage | MemberOf | RemedialActionScheme | Stage | RemedialActionScheme | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has (RemedialActionScheme)
ETXRASE | StageTrigger | MemberOf | Stage | StageTrigger | Stage | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (Stage)
ETXRASE | StageTrigger | TriggeredBy | TriggerCondition | StageTrigger | TriggerCondition | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Triggered By (TriggerCondition)
ETXRASE | TriggerCondition | HasResulting | Gate | TriggerCondition | ResultingGate | 0..1 | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has Resulting (Gate)
ETXRASE | TriggerCondition | MemberOf | RemedialActionScheme | TriggerCondition | RemedialActionScheme | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has (TriggerCondition)
ETXRating | OwnerShareLimits | MemberOf | EnergyConsumerResource | OwnerShareLimits | EnergyConsumerResource | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | EnergyConsumerResource
ETXRating | OwnerShareLimits | MemberOf | GeneratingUnit | OwnerShareLimits | GeneratingUnit | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | GeneratingUnit
ETXRating | OwnerShareLimits | LimitsBy | Operatorship | OwnerShareLimits | Operatorship | 0..1 | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Limits By (Operatorship)
ETXRating | OwnerShareLimits | LimitsBy | Ownership | OwnerShareLimits | Ownership | 0..1 | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Limits By (Ownership)
ETXRating | OwnerShareLimits | HasA | RampRateCurve | OwnerShareLimits | RampRateCurve | 0..n | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (RampRateCurve)
ETXRating | OwnerShareRating | OwnedBy | DynamicElement | OwnerShareRating | DynamicElement | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Owned By (DynamicElement)
ETXRating | OwnerShareRating | MemberOf | Equipment | OwnerShareRating | Equipment | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Equipment
ETXRating | OwnerShareRating | RatedBy | Ownership | OwnerShareRating | Ownership | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Rated By (Ownership)
ETXRating | OwnerShareRating | Reference | WeatherStation | OwnerShareRating | WeatherStation | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reference (WeatherStation)
ETXRating | OwnerShareRating | Reference | WeatherStationAlt | OwnerShareRating | WeatherStationAlt | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reference (WeatherStationAlt)
ETXRating | Rating | IsMonitored | MonitoredRating | Rating | MonitoredRating | 1 | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Is Monitored (MonitoredRating)
ETXRating | Rating | MemberOf | OwnerShareRating | Rating | OwnerShareRating | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Member Of (OwnerShareRating)
ETXRating | Rating | Uses | Unit | Rating | Unit | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Uses (Unit)
ETXSCADA | AlternateLimit | BelongTo | AlternateLimitSet | AlternateLimit | AlternateLimitSet | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belong To (AlternateLimitSet)
ETXSCADA | AlternateLimit | Contain | AnalogLimit | AlternateLimit | AnalogLimit | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Contain (AnalogLimit)
ETXSCADA | AlternateLimit | BelongTo | LimitAlarmCategory | AnalogLimit | LimitAlarmCategory | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belong To (LimitAlarmCategory)
ETXSCADA | Calculation | TriggeredBy | CalculationTriggerTimer | Calculation | CalculationTriggerTimer | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Triggered By (CalculationTriggerTimer)
ETXSCADA | Calculation | Uses | Function | Calculation | Function | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Uses (Function)
ETXSCADA | Calculation | MemberOf | MeasurementLocation | Calculation | MeasurementLocation | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | MeasurementLocation
ETXSCADA | Calculation | SourceOf | MeasurementValue | Calculation | MeasurementValue | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Source Of (MeasurementValue)
ETXSCADA | CalculationArgument | MemberOf | Calculation | CalculationArgument | Calculation | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Contained By (Calculation)
ETXSCADA | CalculationArgument | AssignedTo | FunctionArgument | CalculationArgument | FunctionArgument | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Assigned To (FunctionArgument)
ETXSCADA | ConstantArgument | MappedTo | ConstantValue | ConstantArgument | ConstantValue | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Mapped To (ConstantValue)
ETXSCADA | FunctionArgument | MemberOf | Function | FunctionArgument | Function | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Function
ETXSCADA | MeasurementArgument | MappedTo | MeasurementValue | MeasurementArgument | MeasurementValue | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Mapped To (MeasurementValue)
ETXSCADA | MeasurementGroup | Contains | MeasurementLocation | MeasurementGroup | MeasurementLocation | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Contains (MeasurementLocation)
ETXSCADA | MeasurementLocation | HasTypeOf | DeviceTypeName | MeasurementLocation | DeviceTypeName | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has Type Of (DeviceTypeName)
ETXSCADA | MeasurementLocation | Has | PermissionArea | MeasurementLocation | PermissionArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (PermissionArea)
ETXSCADA | MeasurementLocation | MemberOf | PowerSystemResource | MeasurementLocation | MemberOf_PSR | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | PowerSystemResource
ETXSCADA | SetPointLock | AssignedTo | AnalogValue | SetPointLock | AnalogValue | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Assigned To (AnalogValue)
ETXSCADA | SetPointLock | AssignedTo | DiscreteValue | SetPointLock | DiscreteValue | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Assigned To (DiscreteValue)
ETXSCADA | SetPointLock | LockedBy | SetPoint | SetPointLock | SetPoint | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Locked By (SetPoint)
RDF_Import | sysOrphan | OwnedBy | Ownership | sysOrphan | Ownership | 0..n | 0..n | Reference | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Owned By (Ownership)
RDF_Import | sysOrphan | MemberOf | sysOrphans | sysOrphan_MemberOf | MemberOf_sysOrphans | 0..n | 0..1 | ParentChild | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | sysOrphans
RDF_Import | sysRdfContainer | HasA | Domain | sysRdfContainer_HasA | HasA_Domain | 0..1 | 0..1 | Reference | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Orphan Root
RDF_Import | sysRdfContainer | MemberOf | sysRdfContainers | sysRdfContainer_MemberOf | MemberOf_sysRdfContainers | 0..n | 0..1 | ParentChild | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | sysRdfContainers
Reservation | TransmissionPath | HasPOD | ServicePoint | HasAPOD_ | DeliveryPointFor | 0..n | 1..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | POD ServicePoint
Reservation | TransmissionPath | HasPOR | ServicePoint | HasAPOR_ | PointOfReceiptFor | 0..n | 1..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | POR ServicePoint

## DataTypes
Package | Data Type Name | Name Space | Documentation | NMMS Data Type Name
BaseDataTypes | Bool | spc | Boolean data type. | Bool
BaseDataTypes | Date | spc | Date | Date
BaseDataTypes | DateTime | spc | Date and time | DateTime
BaseDataTypes | Double | spc |  | Double
BaseDataTypes | DoubleFloat | spc | 8 byte float (real). | DoubleFloat
BaseDataTypes | Float | spc | 4 byte float (real) | Float
BaseDataTypes | Integer | spc | CIM base data type mapped to LongInt | Integer
BaseDataTypes | LongInt | spc | Signed 32 bit integer | LongInt
BaseDataTypes | LongString |  |  | LongString
BaseDataTypes | ShortInt | spc | Signed 16 bit integer | ShortInt
BaseDataTypes | UShortInt | spc | Unsigned 16 bit integer | UShortInt
BaseDataTypes | Time | spc | Time | Time
BaseDataTypes | String | spc |  | String
BaseDataTypes | Binary | spc | Binary data type. | Binary
CIMDataTypes | Integer | cim | A type with the value range -2**-31..2**31 -1 | Integer
CIMDataTypes | AbsoluteDateTime | cim | Date and time as 'yyyy-mm-ddThh:mm:ss.sss', which conforms with ISO 8601. UTC time zone is specified as 'yyyy-mm-ddThh:mm:ss.sssZ'. A local timezone relative UTC is specified as 'yyyy-mm-ddThh:mm:ss.sss-hh:mm'. | AbsoluteDateTime
CIMDataTypes | ActivePower | cim | Product of RMS value of the voltage and the RMS value of the in-phase component of the current (Megawatt) | ActivePower
CIMDataTypes | Admittance | cim | Ratio of current to voltage. | Admittance
CIMDataTypes | AngleDegrees | cim | Measurement of angle in degrees | AngleDegrees
CIMDataTypes | AngleRadians | cim | Phase angle in radians | AngleRadians
CIMDataTypes | ApparentPower | cim | Product of the RMS value of the voltage and the RMS value of the current (MegaVoltAmperes) | ApparentPower
CIMDataTypes | Boolean | cim | A type with the value space 0..1 where 0 means false and 1 means true. | Boolean
CIMDataTypes | Complex | cim | A real and imaginary pair of Float values. | Complex
CIMDataTypes | CompositeSwitchType | cim | An alphanumeric code that can be used as a reference to extar information such as the description of the interlocking scheme if any. | CompositeSwitchType
CIMDataTypes | Float | cim | A type defined by IEEE 754-1985 as double (OBSERVE, not as the IEEE 754-1985 float). The value range is m*2**e where the range of m is -2**52..2**52 -1 and the range of e is -1075..970. | Float
CIMDataTypes | LongDouble | cim | A type defined by IEEE 754-1985 as a long double. | LongDouble
CIMDataTypes | LongLong | cim | A type with the value range -2**63..2**63 -1 | LongLong
CIMDataTypes | Octet | cim | A type with the value range 0..255 | Octet
CIMDataTypes | Short | cim | A type with the value range -2**15..2**15 -1 | Short
CIMDataTypes | String | cim | A type consisting of a sequence of 8 bit characters. The character encoding is UTF-8. | String
CIMDataTypes | ULong | cim | A type with the value range 0..2**32 -1 | ULong
CIMDataTypes | ULongLong | cim | A type with the value range 0..2**64 -1 | ULongLong
CIMDataTypes | VoltagePerReactivePower | cim | Voltage variation with reactive power | VoltagePerReactivePower
CIMEnumerations | BoilerControlMode | cim | Boiler Control Mode | EnumBoilerControlMode
CIMEnumerations | BreakerConfiguration | cim | Switching arangement for Bay. | EnumBreakerConfiguration
CIMEnumerations | CompanyType | cim | Type of the company. | EnumCompanyType
CIMEnumerations | ControlHouseEquipmentType | cim | Type of control house equipment. | EnumControlHouseEquipmentType
CIMEnumerations | CurveStyle | cim |  | EnumCurveStyle
CIMEnumerations | WindingType | cim |  | EnumWindingType
CIMEnumerations | TransformerType | cim |  | EnumTransformerType
CIMEnumerations | TransformerControlMode | cim |  | EnumTransformerControlMode
CIMEnumerations | SynchronousMachineType | cim |  | EnumSynchronousMachineType
CIMEnumerations | SynchronousMachineOperatingMode | cim |  | EnumSynchronousMachineOperatingMode
CIMEnumerations | GeneratorControlSource | cim |  | EnumGeneratorControlSource
CIMEnumerations | BusbarConfiguration | cim |  | EnumBusbarConfiguration
CIMEnumerations | ClearanceTagType | cim |  | EnumClearanceTagType
CIMEnumerations | CoolantType | cim |  | EnumCoolantType
CIMEnumerations | AreaControlMode | cim | Present control mode of area | EnumAreaControlModel
CIMEnumerations | DayTypeName | cim |  | EnumDayTypeName
CIMEnumerations | EmissionType | cim |  | EnumEmissionType
CIMEnumerations | EmissionValueSource | cim |  | EnumEmissionValueSource
CIMEnumerations | FuelType | cim |  | EnumFuelType
CIMEnumerations | GeneratorControlMode | cim |  | EnumGeneratorControlMode
CIMEnumerations | GeneratorOperatingMode | cim |  | EnumGeneratorOperatingMode
CIMEnumerations | HydroPlantType | cim |  | EnumHydroPlantType
CIMEnumerations | Quantity | cim |  | EnumQuantity
CIMEnumerations | RampMethod | cim |  | EnumRampMethod
CIMEnumerations | RampStartMethod | cim |  | EnumRampStartMethod
CIMEnumerations | RampUnits | cim |  | EnumRampUnits
CIMEnumerations | RemoteUnitType | cim |  | EnumRemoteUnitType
CIMEnumerations | SeasonName | cim |  | EnumSeasonName
CIMEnumerations | Source | cim |  | EnumSource
CIMEnumerations | SwitchState | cim |  | EnumSwitchState
CIMEnumerations | TemperatureUnits | cim |  | EnumTemperatureUnits
CIMEnumerations | TurbineType | cim |  | EnumTurbineType
CIMEnumerations | Validity | cim |  | EnumValidity
CIMEnumerations | WindingConnection | cim |  | EnumWindingConnection
CIMEnumerations | PenstockType | cim | Type of hydro plant penstock. | EnumPenstockType
CIMEnumerations | SurgeTankCode | cim | Type (or absence) of surge tank that is associated with the hydro power plant. | EnumSurgeTankCode
CIMEnumerations | SpillwayGateType | cim | Type of spillway gate. | EnumSpillwayGateType
CIMEnumerations | TransformerCoolingType | cim |  | EnumTransformerCoolingType
CIMEnumerations | SVCControlMode | cim |  | EnumSVCControlMode
ETXEnumerations | EnumGeneratorParticipationFactor | etx |  | EnumGeneratorParticipationFactor
ETXEnumerations | EnumGateType | etx |  | EnumGateType
ETXEnumerations | LimitType | etx |  | EnumLimitType
ETXEnumerations | RatingType | etx |  | EnumRatingType
ETXEnumerations | LimitSetType | etx |  | EnumLimitSetType
ETXEnumerations | PreContLimitType | etx |  | EnumPreContLimitType
ETXEnumerations | PostContLimitType | etx |  | EnumPostContLimitType
ETXEnumerations | EnumContingencyActiveMode | etx |  | EnumContingencyActiveMode
ETXEnumerations | EnumContingencyProcessType | etx |  | EnumContingencyProcessType
ETXEnumerations | EnumRelayType | etx |  | EnumRelayType
ETXEnumerations | ERCOTFuelType | etx |  | EnumERCOTFuelType
ETXEnumerations | ERCOTHubCalcType | etx |  | EnumHubCalcType
ETXEnumerations | ERCOTPANType | etx |  | EnumPANType
ETXEnumerations | SavecaseType | etx | ICCP savecase type. | EnumSavecaseType
CIMEnumeration | CompanyType | cim | Type of the company. | EnumCompanyType

## DataTypes - Enum
Package | Data Type - Enumeration | Enumerator | Label | Namespace | Documentation | Internal Data Type Name | Internal Representation
CIMEnumerations | BoilerControlMode | coordinated | Coordinated Control | cim |  | EnumBoilerControlMode | 0
CIMEnumerations | BoilerControlMode | following | Boiler Following Control | cim |  | EnumBoilerControlMode | 1
CIMEnumerations | BreakerConfiguration | singleBreaker | single Breaker | cim |  | EnumBreakerConfiguration | 0
CIMEnumerations | BreakerConfiguration | breakerAndAHalf | breaker And A Half | cim |  | EnumBreakerConfiguration | 1
CIMEnumerations | BreakerConfiguration | doubleBreaker | double Breaker | cim |  | EnumBreakerConfiguration | 2
CIMEnumerations | BreakerConfiguration | noBreaker | no Breaker | cim |  | EnumBreakerConfiguration | 3
CIMEnumerations | CurveStyle | constantYValue | constantYValue | cim |  | EnumCurveStyle | 0
CIMEnumerations | CurveStyle | straightLineYValues | straightLineYValues | cim |  | EnumCurveStyle | 1
CIMEnumerations | CurveStyle | rampYValue | rampYValue | cim |  | EnumCurveStyle | 2
CIMEnumerations | CurveStyle | formula | formula | cim |  | EnumCurveStyle | 3
CIMEnumerations | WindingType | primary | primary | cim |  | EnumWindingType | 1
CIMEnumerations | WindingType | secondary | secondary | cim |  | EnumWindingType | 2
CIMEnumerations | WindingType | tertiary | tertiary | cim |  | EnumWindingType | 3
CIMEnumerations | WindingType | quaternary | quaternary | cim |  | EnumWindingType | 4
CIMEnumerations | TransformerType | fix | fix | cim |  | EnumTransformerType | 0
CIMEnumerations | TransformerType | voltageControl | voltageControl | cim |  | EnumTransformerType | 1
CIMEnumerations | TransformerType | phaseControl | phaseControl | cim |  | EnumTransformerType | 2
CIMEnumerations | TransformerType | voltageAndPhaseControl | voltageAndPhaseControl | cim |  | EnumTransformerType | 3
CIMEnumerations | TransformerControlMode | off | off | cim | off | EnumTransformerControlMode | 1
CIMEnumerations | TransformerControlMode | local | local | cim | local | EnumTransformerControlMode | 2
CIMEnumerations | TransformerControlMode | volt | volt | cim |  | EnumTransformerControlMode | 3
CIMEnumerations | TransformerControlMode | mVAr | mVAr | cim | mVAr | EnumTransformerControlMode | 4
CIMEnumerations | TransformerControlMode | MW | [not used] MW | cim | MW | EnumTransformerControlMode | 5
CIMEnumerations | SynchronousMachineType | generator | Generator | cim |  | EnumSynchronousMachineType | 0
CIMEnumerations | SynchronousMachineType | condenser | Condenser | cim |  | EnumSynchronousMachineType | 1
CIMEnumerations | SynchronousMachineType | generator_or_condenser | Both | cim |  | EnumSynchronousMachineType | 2
CIMEnumerations | SynchronousMachineOperatingMode | generator | Generator | cim |  | EnumSynchronousMachineOperatingMode | 0
CIMEnumerations | SynchronousMachineOperatingMode | condenser | Condenser | cim |  | EnumSynchronousMachineOperatingMode | 1
CIMEnumerations | GeneratorControlSource | Unavailable | Unavailable | cim |  | EnumGeneratorControlSource | 0
CIMEnumerations | GeneratorControlSource | offAGC | Off-AGC | cim |  | EnumGeneratorControlSource | 1
CIMEnumerations | GeneratorControlSource | onAGC | On-AGC | cim |  | EnumGeneratorControlSource | 2
CIMEnumerations | GeneratorControlSource | PlantControl | Plant Control | cim |  | EnumGeneratorControlSource | 3
CIMEnumerations | BusbarConfiguration | singleBus | Single Bus | cim |  | EnumBusbarConfiguration | 0
CIMEnumerations | BusbarConfiguration | doubleBus | Double Bus | cim |  | EnumBusbarConfiguration | 1
CIMEnumerations | BusbarConfiguration | mainWithTransfer | Main With Transfer | cim |  | EnumBusbarConfiguration | 2
CIMEnumerations | BusbarConfiguration | ringBus | Ring Bus | cim |  | EnumBusbarConfiguration | 3
CIMEnumerations | CoolantType | air | air | cim |  | EnumCoolantType | 0
CIMEnumerations | CoolantType | hydrogenGas | Hydrogen Gas | cim |  | EnumCoolantType | 1
CIMEnumerations | CoolantType | water | water | cim |  | EnumCoolantType | 2
CIMEnumerations | AreaControlMode | CF | CF | cim |  | EnumAreaControlModel | 0
CIMEnumerations | AreaControlMode | CTL | CTL | cim |  | EnumAreaControlModel | 1
CIMEnumerations | AreaControlMode | TLB | TLB | cim |  | EnumAreaControlModel | 2
CIMEnumerations | AreaControlMode | OFF | OFF | cim |  | EnumAreaControlModel | 3
CIMEnumerations | DayTypeName | weekday | weekday | cim |  | EnumDayTypeName | 0
CIMEnumerations | DayTypeName | weekend | weekend | cim |  | EnumDayTypeName | 1
CIMEnumerations | DayTypeName | holiday | holiday | cim |  | EnumDayTypeName | 2
CIMEnumerations | DayTypeName | Sunday | Sunday | etx |  | EnumDayTypeName | 10
CIMEnumerations | DayTypeName | Monday | Monday | etx |  | EnumDayTypeName | 11
CIMEnumerations | DayTypeName | Tuesday | Tuesday | etx |  | EnumDayTypeName | 12
CIMEnumerations | DayTypeName | Wednesday | Wednesday | etx |  | EnumDayTypeName | 13
CIMEnumerations | DayTypeName | Thursday | Thursday | etx |  | EnumDayTypeName | 14
CIMEnumerations | DayTypeName | Friday | Friday | etx |  | EnumDayTypeName | 15
CIMEnumerations | DayTypeName | Saturday | Saturday | etx |  | EnumDayTypeName | 16
CIMEnumerations | DayTypeName | Holiday1 | Holiday1 | etx |  | EnumDayTypeName | 20
CIMEnumerations | DayTypeName | Holiday2 | Holiday2 | etx |  | EnumDayTypeName | 21
CIMEnumerations | EmissionType | sulferDioxide | Sulfur Dioxide | cim |  | EnumEmissionType | 0
CIMEnumerations | EmissionType | carbonDioxide | Carbon Dioxide | cim |  | EnumEmissionType | 1
CIMEnumerations | EmissionType | nitrogenOxide | Nitrogen Oxide | cim |  | EnumEmissionType | 2
CIMEnumerations | EmissionType | hydrogenSulfide | Hydrogen Sulfide | cim |  | EnumEmissionType | 3
CIMEnumerations | EmissionType | chlorine | Chlorine | cim |  | EnumEmissionType | 4
CIMEnumerations | EmissionType | carbonDisulfide | Carbon Disulfide | cim |  | EnumEmissionType | 5
CIMEnumerations | EmissionValueSource | measured | Measured | cim |  | EnumEmissionValueSource | 0
CIMEnumerations | EmissionValueSource | calculated | Calculated | cim |  | EnumEmissionValueSource | 1
CIMEnumerations | FuelType | coal | Coal | cim |  | EnumFuelType | 0
CIMEnumerations | FuelType | oil | Oil | cim |  | EnumFuelType | 1
CIMEnumerations | FuelType | gas | Gas | cim |  | EnumFuelType | 2
CIMEnumerations | GeneratorControlMode | setpoint | Setpoint | cim |  | EnumGeneratorControlMode | 0
CIMEnumerations | GeneratorControlMode | pulse | Pulse | cim |  | EnumGeneratorControlMode | 1
CIMEnumerations | GeneratorOperatingMode | Off | Off | cim |  | EnumGeneratorOperatingMode | 0
CIMEnumerations | GeneratorOperatingMode | Manual | Manual | cim |  | EnumGeneratorOperatingMode | 1
CIMEnumerations | GeneratorOperatingMode | Fixed | Fixed | cim |  | EnumGeneratorOperatingMode | 2
CIMEnumerations | GeneratorOperatingMode | LFC | LFC | cim |  | EnumGeneratorOperatingMode | 3
CIMEnumerations | GeneratorOperatingMode | AGC | AGC | cim |  | EnumGeneratorOperatingMode | 4
CIMEnumerations | GeneratorOperatingMode | EDC | EDC | cim |  | EnumGeneratorOperatingMode | 5
CIMEnumerations | GeneratorOperatingMode | MRN | MRN | cim |  | EnumGeneratorOperatingMode | 6
CIMEnumerations | GeneratorOperatingMode | REG | REG | cim |  | EnumGeneratorOperatingMode | 7
CIMEnumerations | HydroPlantType | runOfRiver | Run of River | cim |  | EnumHydroPlantType | 0
CIMEnumerations | HydroPlantType | pumpedStorage | Pumped Storage | cim |  | EnumHydroPlantType | 1
CIMEnumerations | HydroPlantType | majorStorage | Major Storage | cim |  | EnumHydroPlantType | 2
CIMEnumerations | HydroPlantType | minorStorage | Minor Storage | cim |  | EnumHydroPlantType | 3
CIMEnumerations | Quantity | none | none | cim |  | EnumQuantity | 0
CIMEnumerations | Quantity | time | Time | cim |  | EnumQuantity | 1
CIMEnumerations | Quantity | activePower | Active Power | cim |  | EnumQuantity | 2
CIMEnumerations | Quantity | reactivePower | Reactive Power | cim |  | EnumQuantity | 3
CIMEnumerations | Quantity | currency | Currency | cim |  | EnumQuantity | 4
CIMEnumerations | Quantity | voltage | Voltage | cim |  | EnumQuantity | 5
CIMEnumerations | RampMethod | yUnitsPerMinute | y Units Per Minute | cim |  | EnumRampMethod | 0
CIMEnumerations | RampMethod | rampCompletionInMinutes | Ramp Completion In Minutes | cim |  | EnumRampMethod | 1
CIMEnumerations | RampStartMethod | zero | Zero | cim |  | EnumRampStartMethod | 0
CIMEnumerations | RampStartMethod | fiftyPerCent | Fifty PerCent | cim |  | EnumRampStartMethod | 1
CIMEnumerations | RampStartMethod | oneHundredPerCent | One Hundred PerCent | cim |  | EnumRampStartMethod | 2
CIMEnumerations | RampUnits | MWPerMinute | MW Per Minute | cim |  | EnumRampUnits | 0
CIMEnumerations | RampUnits | rampCompletionInMin | Ramp Completion In Minutes | cim |  | EnumRampUnits | 1
CIMEnumerations | RemoteUnitType | RTU | RTU | cim |  | EnumRemoteUnitType | 0
CIMEnumerations | RemoteUnitType | SubstationControlSystem | Substation Control System | cim |  | EnumRemoteUnitType | 1
CIMEnumerations | RemoteUnitType | ControlCenter | Control Center | cim |  | EnumRemoteUnitType | 2
CIMEnumerations | RemoteUnitType | IED | IED | cim |  | EnumRemoteUnitType | 3
CIMEnumerations | SeasonName | winter | Winter | cim |  | EnumSeasonName | 0
CIMEnumerations | SeasonName | spring | Spring | cim |  | EnumSeasonName | 1
CIMEnumerations | SeasonName | summer | Summer | cim |  | EnumSeasonName | 2
CIMEnumerations | SeasonName | fall | Fall | cim |  | EnumSeasonName | 3
CIMEnumerations | Source | PROCESS | PROCESS | cim |  | EnumSource | 0
CIMEnumerations | Source | DEFAULTED | DEFAULTED | cim |  | EnumSource | 1
CIMEnumerations | Source | SUBSTITUTED | SUBSTITUTED | cim |  | EnumSource | 2
CIMEnumerations | SwitchState | open | open | cim |  | EnumSwitchState | 0
CIMEnumerations | SwitchState | close | close | cim |  | EnumSwitchState | 1
CIMEnumerations | TemperatureUnits | celsius | Celsius | cim |  | EnumTemperatureUnits | 0
CIMEnumerations | TemperatureUnits | fahrenheit | Fahrenheit | cim |  | EnumTemperatureUnits | 1
CIMEnumerations | TurbineType | francis | francis | cim |  | EnumTurbineType | 0
CIMEnumerations | TurbineType | pelton | pelton | cim |  | EnumTurbineType | 1
CIMEnumerations | TurbineType | kaplan | kaplan | cim |  | EnumTurbineType | 2
CIMEnumerations | Validity | GOOD | GOOD | cim |  | EnumValidity | 0
CIMEnumerations | Validity | QUESTIONABLE | QUESTIONABLE | cim |  | EnumValidity | 1
CIMEnumerations | Validity | INVALID | INVALID | cim |  | EnumValidity | 2
CIMEnumerations | WindingConnection | D | D | cim |  | EnumWindingConnection | 0
CIMEnumerations | WindingConnection | Y | Y | cim |  | EnumWindingConnection | 1
CIMEnumerations | WindingConnection | Z | Z | cim |  | EnumWindingConnection | 2
CIMEnumerations | SVCControlMode | off | off | cim | off | EnumSVCControlMode | 0
CIMEnumerations | SVCControlMode | reactivePower | reactivePower | cim | reactive Power | EnumSVCControlMode | 1
CIMEnumerations | SVCControlMode | voltage | voltage | cim | voltage | EnumSVCControlMode | 2
ETXEnumerations | EnumGeneratorParticipationFactor | short | short | etx |  | EnumGeneratorParticipationFactor | 0
ETXEnumerations | EnumGeneratorParticipationFactor | long | long | etx |  | EnumGeneratorParticipationFactor | 1
ETXEnumerations | EnumGeneratorParticipationFactor | normal | normal | etx |  | EnumGeneratorParticipationFactor | 2
ETXEnumerations | EnumGateType | and | and | etx |  | EnumGateType | 0
ETXEnumerations | EnumGateType | or | or | etx |  | EnumGateType | 1
ETXEnumerations | EnumGateType | nor | nor | etx |  | EnumGateType | 2
ETXEnumerations | EnumGateType | nand | nand | etx |  | EnumGateType | 3
ETXEnumerations | EnumGateType | not | not | etx |  | EnumGateType | 4
ETXEnumerations | EnumGateType | ne | ne | etx |  | EnumGateType | 5
ETXEnumerations | EnumGateType | eq | eq | etx |  | EnumGateType | 6
ETXEnumerations | EnumGateType | le | le | etx |  | EnumGateType | 7
ETXEnumerations | EnumGateType | lt | lt | etx |  | EnumGateType | 8
ETXEnumerations | EnumGateType | ge | ge | etx |  | EnumGateType | 9
ETXEnumerations | EnumGateType | gt | gt | etx |  | EnumGateType | 10
ETXEnumerations | LimitType | normalRating | Normal Rating | etx |  | EnumLimitType | 0
ETXEnumerations | LimitType | fifteenminuteRating | Fifteen Minute Rating | etx |  | EnumLimitType | 1
ETXEnumerations | LimitType | twoHourRating | Two Hour Rating | etx |  | EnumLimitType | 2
ETXEnumerations | LimitType | conductorRating | Conductor Rating | etx |  | EnumLimitType | 3
ETXEnumerations | LimitType | RateOfChange | RateOfChange | etx |  | EnumLimitType | 4
ETXEnumerations | LimitType | Clamp | Clamp | etx |  | EnumLimitType | 5
ETXEnumerations | LimitType | High1 | High1 | etx |  | EnumLimitType | 11
ETXEnumerations | LimitType | High2 | High2 | etx |  | EnumLimitType | 12
ETXEnumerations | LimitType | High3 | High3 | etx |  | EnumLimitType | 13
ETXEnumerations | LimitType | High4 | High4 | etx |  | EnumLimitType | 14
ETXEnumerations | LimitType | High5 | High5 | etx |  | EnumLimitType | 15
ETXEnumerations | LimitType | High6 | High6 | etx |  | EnumLimitType | 16
ETXEnumerations | LimitType | Low1 | Low1 | etx |  | EnumLimitType | 21
ETXEnumerations | LimitType | Low2 | Low2 | etx |  | EnumLimitType | 22
ETXEnumerations | LimitType | Low3 | Low3 | etx |  | EnumLimitType | 23
ETXEnumerations | LimitType | Low4 | Low4 | etx |  | EnumLimitType | 24
ETXEnumerations | LimitType | Low5 | Low5 | etx |  | EnumLimitType | 25
ETXEnumerations | LimitType | Low6 | Low6 | etx |  | EnumLimitType | 26
ETXEnumerations | RatingType | dynamicRating | Dynamic Rating | etx |  | EnumRatingType | 0
ETXEnumerations | RatingType | staticRating | Static Rating | etx |  | EnumRatingType | 1
ETXEnumerations | LimitSetType | ratings | ratings | etx | device ratings | EnumLimitSetType | 0
ETXEnumerations | LimitSetType | limits | limits | etx | telemetry limits | EnumLimitSetType | 1
ETXEnumerations | LimitSetType | both | both | etx | apply to both device and telemetry measurements | EnumLimitSetType | 2
ETXEnumerations | PreContLimitType | none | none | etx |  | EnumPreContLimitType | 0
ETXEnumerations | PreContLimitType | normal | normal | etx |  | EnumPreContLimitType | 1
ETXEnumerations | PostContLimitType | none | none | etx |  | EnumPostContLimitType | 0
ETXEnumerations | PostContLimitType | normal | normal | etx |  | EnumPostContLimitType | 1
ETXEnumerations | PostContLimitType | LTE | LTE | etx |  | EnumPostContLimitType | 2
ETXEnumerations | PostContLimitType | MTE | MTE | etx |  | EnumPostContLimitType | 3
ETXEnumerations | PostContLimitType | STE | STE | etx |  | EnumPostContLimitType | 4
ETXEnumerations | EnumContingencyActiveMode | default | Default | etx |  | EnumContingencyActiveMode | 0
ETXEnumerations | EnumContingencyActiveMode | mustRun | Must Run | etx |  | EnumContingencyActiveMode | 1
ETXEnumerations | EnumContingencyActiveMode | noStudy | No Study | etx |  | EnumContingencyActiveMode | 2
ETXEnumerations | EnumContingencyProcessType | useFull | Use Full | etx |  | EnumContingencyProcessType | 1
ETXEnumerations | EnumContingencyProcessType | useWide | Use Wide | etx |  | EnumContingencyProcessType | 2
ETXEnumerations | EnumContingencyProcessType | useLocal | Use Local | etx |  | EnumContingencyProcessType | 3
ETXEnumerations | EnumRelayType | interruptible | interruptible | etx |  | EnumRelayType | 0
ETXEnumerations | EnumRelayType | controllable | controllable | etx |  | EnumRelayType | 1
ETXEnumerations | EnumRelayType | under-frequency | under-frequency | etx |  | EnumRelayType | 2
ETXEnumerations | ERCOTFuelType | AB | Agriculture byproducts, bagasse, straw, energy crops | etx |  | EnumERCOTFuelType | 0
ETXEnumerations | ERCOTFuelType | BFG | Blast-Furnace Gas | etx |  | EnumERCOTFuelType | 1
ETXEnumerations | ERCOTFuelType | BIT | Bituminous Coal | etx |  | EnumERCOTFuelType | 2
ETXEnumerations | ERCOTFuelType | BLQ | Black liquor | etx |  | EnumERCOTFuelType | 3
ETXEnumerations | ERCOTFuelType | DFO | Distillate Fuel Oil (Diesel, No1 Fuel Oil, No 2 Fuel Oil, No 4 Fuel Oil | etx |  | EnumERCOTFuelType | 4
ETXEnumerations | ERCOTFuelType | GEO | Geothermal | etx |  | EnumERCOTFuelType | 5
ETXEnumerations | ERCOTFuelType | JF | Jet Fuel | etx |  | EnumERCOTFuelType | 6
ETXEnumerations | ERCOTFuelType | KER | Kerosene | etx |  | EnumERCOTFuelType | 7
ETXEnumerations | ERCOTFuelType | LFG | Landfill gas | etx |  | EnumERCOTFuelType | 8
ETXEnumerations | ERCOTFuelType | LIG | Lignite | etx |  | EnumERCOTFuelType | 9
ETXEnumerations | ERCOTFuelType | MSW | Municipal solid waste (refuse) | etx |  | EnumERCOTFuelType | 10
ETXEnumerations | ERCOTFuelType | NA | Not available | etx |  | EnumERCOTFuelType | 11
ETXEnumerations | ERCOTFuelType | NG | Natural Gas | etx |  | EnumERCOTFuelType | 12
ETXEnumerations | ERCOTFuelType | NUC | Nuclear (uranium, plutonium, thorium) | etx |  | EnumERCOTFuelType | 13
ETXEnumerations | ERCOTFuelType | OBG | Other biomass gases (methane, digester gas) | etx |  | EnumERCOTFuelType | 14
ETXEnumerations | ERCOTFuelType | OBL | Other biomass liquids (ethanol, fish oil, waste alcohol, other gases) | etx |  | EnumERCOTFuelType | 15
ETXEnumerations | ERCOTFuelType | OBS | Other biomass solids (animal manure/waster, medical waste, paper pellets, paper derived fuel) | etx |  | EnumERCOTFuelType | 16
ETXEnumerations | ERCOTFuelType | OG | Other Gas (Butane, Coal Processes, Coke-oven coal, Methanol, Refinery gas, | etx |  | EnumERCOTFuelType | 17
ETXEnumerations | ERCOTFuelType | OTH | Other (batteries, chemicals, hydrogen pitch sulfur, misc technologies) | etx |  | EnumERCOTFuelType | 18
ETXEnumerations | ERCOTFuelType | PC | Petroleum Coke | etx |  | EnumERCOTFuelType | 19
ETXEnumerations | ERCOTFuelType | PG | Propane | etx |  | EnumERCOTFuelType | 20
ETXEnumerations | ERCOTFuelType | PUR | Purchased steam | etx |  | EnumERCOTFuelType | 21
ETXEnumerations | ERCOTFuelType | RFO | Residual fuel Oil (No 5 and No 6 Fuel Oil) | etx |  | EnumERCOTFuelType | 22
ETXEnumerations | ERCOTFuelType | SC | Coal-based synfuel and include briquettes, pellets, or extrusions, which are formed by binding materials and processes that recycle material | etx |  | EnumERCOTFuelType | 23
ETXEnumerations | ERCOTFuelType | SLW | Sludge waste | etx |  | EnumERCOTFuelType | 24
ETXEnumerations | ERCOTFuelType | SUB | Subbituminous Coal | etx |  | EnumERCOTFuelType | 25
ETXEnumerations | ERCOTFuelType | SUN | Solar (photovoltaic, thermal) | etx |  | EnumERCOTFuelType | 26
ETXEnumerations | ERCOTFuelType | TDF | Tires | etx |  | EnumERCOTFuelType | 27
ETXEnumerations | ERCOTFuelType | WAT | Water (conventional, pumped storage) | etx |  | EnumERCOTFuelType | 28
ETXEnumerations | ERCOTFuelType | WC | Waste/other coal | etx |  | EnumERCOTFuelType | 29
ETXEnumerations | ERCOTFuelType | WDL | Wood/wood waste liquids (red liquor, sludge wood spent sulfite liquor, other liquors) | etx |  | EnumERCOTFuelType | 30
ETXEnumerations | ERCOTFuelType | WDS | Wood/wood waste solids (peat, railroad ties, utility poles, wood chips, other solids) | etx |  | EnumERCOTFuelType | 31
ETXEnumerations | ERCOTFuelType | WND | Wind | etx |  | EnumERCOTFuelType | 32
ETXEnumerations | ERCOTFuelType | WO | Other Oil (butane, crude, liquid byproducts, oil waste, propane) | etx |  | EnumERCOTFuelType | 33
ETXEnumerations | ERCOTHubCalcType | ALL_ERCOT_345KV_HUBBUSES | ALL_ERCOT_345KV_HUBBUSES | etx |  | EnumHubCalcType | 1
ETXEnumerations | ERCOTHubCalcType | ERCOT_HUBS | ERCOT_HUBS | etx |  | EnumHubCalcType | 2
ETXEnumerations | ERCOTPANType | BLT_normally_in | Block Load Transfer normally included in ERCOT | etx |  | EnumPANType | 1
ETXEnumerations | ERCOTPANType | BLT_normally_out | Block Load Transfer normally excluded from ERCOT | etx |  | EnumPANType | 2
ETXEnumerations | ERCOTPANType | PrivateUseNetwork | Private Use Network | etx |  | EnumPANType | 3
ETXEnumerations | ERCOTPANType | SelfServing | Self Serving Load | etx |  | EnumPANType | 4
ETXEnumerations | ERCOTPANType | NonModeledGeneration | Non-Modeled Generation | etx |  | EnumPANType | 5
ETXEnumerations | ERCOTPANType | RetiredGeneration | Retired Generation | etx |  | EnumPANType | 6
ETXEnumerations | ERCOTPANType | MothballedGeneration | Mothballed Generation | etx |  | EnumPANType | 7
ETXEnumerations | SavecaseType | QSE | QSE | etx |  | EnumSavecaseType | 1
ETXEnumerations | SavecaseType | TSP | TSP | etx |  | EnumSavecaseType | 2
CIMEnumeration | CompanyType | CRRAH | CRRAH | etx | CRRAH | EnumCompanyType | 11
CIMEnumeration | CompanyType | DSP | DSP | etx | DSP | EnumCompanyType | 12
CIMEnumeration | CompanyType | ERCOT | ERCOT | etx | ERCOT | EnumCompanyType | 13
CIMEnumeration | CompanyType | LSE | LSE | etx | LSE | EnumCompanyType | 14
CIMEnumeration | CompanyType | PUCT | PUCT | etx | PUCT | EnumCompanyType | 15
CIMEnumeration | CompanyType | QSE | QSE | etx | QSE | EnumCompanyType | 16
CIMEnumeration | CompanyType | RE | RE | etx | RE | EnumCompanyType | 17
CIMEnumeration | CompanyType | TDSP | TDSP | etx | TDSP | EnumCompanyType | 18

## DataTypes - Value&Unit
Package | Data Type Name | DataType | Units | Namespace | Documentation
BaseDataTypes | Bool | Bool |  | spc | Boolean data type.
BaseDataTypes | Date | Date |  | spc | Date
BaseDataTypes | DateTime | DateTime |  | spc | Date and time
BaseDataTypes | Double | DoubleFloat |  | spc
BaseDataTypes | DoubleFloat | DoubleFloat |  | spc | 8 byte float (real).
BaseDataTypes | Float | Float |  | spc | 4 byte float (real)
BaseDataTypes | Integer | LongInt |  | spc | CIM base data type mapped to LongInt
BaseDataTypes | LongInt | LongInt |  | spc | Signed 32 bit integer
BaseDataTypes | LongString | String
BaseDataTypes | ShortInt | ShortInt |  | spc | Signed 16 bit integer
BaseDataTypes | UShortInt | UShortInt |  | spc | Unsigned 16 bit integer
BaseDataTypes | Time | Time |  | spc | Time
BaseDataTypes | String | String |  | spc
BaseDataTypes | Binary | Binary |  | spc | Binary data type.
CIMDataTypes | Integer | LongInt |  | cim | A type with the value range -2**-31..2**31 -1
CIMDataTypes | AbsoluteDateTime | DateTime |  | cim | Date and time as 'yyyy-mm-ddThh:mm:ss.sss', which conforms with ISO 8601. UTC time zone is specified as 'yyyy-mm-ddThh:mm:ss.sssZ'. A local timezone relative UTC is specified as 'yyyy-mm-ddThh:mm:ss.sss-hh:mm'.
CIMDataTypes | ActivePower | Float | MW | cim | Product of RMS value of the voltage and the RMS value of the in-phase component of the current (Megawatt)
CIMDataTypes | Admittance | Float |  | cim | Ratio of current to voltage.
CIMDataTypes | AngleDegrees | Float | Degree | cim | Measurement of angle in degrees
CIMDataTypes | AngleRadians | Float | Radian | cim | Phase angle in radians
CIMDataTypes | ApparentPower | Float | MVA | cim | Product of the RMS value of the voltage and the RMS value of the current (MegaVoltAmperes)
CIMDataTypes | Boolean | Bool |  | cim | A type with the value space 0..1 where 0 means false and 1 means true.
CIMDataTypes | Complex |  |  | cim | A real and imaginary pair of Float values.
CIMDataTypes | CompositeSwitchType | String |  | cim | An alphanumeric code that can be used as a reference to extar information such as the description of the interlocking scheme if any.
CIMDataTypes | Float | DoubleFloat |  | cim | A type defined by IEEE 754-1985 as double (OBSERVE, not as the IEEE 754-1985 float). The value range is m*2**e where the range of m is -2**52..2**52 -1 and the range of e is -1075..970.
CIMDataTypes | LongDouble |  |  | cim | A type defined by IEEE 754-1985 as a long double.
CIMDataTypes | LongLong |  |  | cim | A type with the value range -2**63..2**63 -1
CIMDataTypes | Octet |  |  | cim | A type with the value range 0..255
CIMDataTypes | Short | ShortInt |  | cim | A type with the value range -2**15..2**15 -1
CIMDataTypes | String | String100 |  | cim | A type consisting of a sequence of 8 bit characters. The character encoding is UTF-8.
CIMDataTypes | ULong |  |  | cim | A type with the value range 0..2**32 -1
CIMDataTypes | ULongLong |  |  | cim | A type with the value range 0..2**64 -1
CIMDataTypes | VoltagePerReactivePower | DoubleFloat | kV_per_MVAr | cim | Voltage variation with reactive power