## Attributes
Issue | Notes | Package | Internal Class Name | Class | Internal Attribute Name | Attribute | Data Type | Initial Value | Name Space | Documentation | CPSM Nerc | ABB / MMS | Areva / EMS | ABB / OS | Nexant / CRR | PTI / Planning | Lodestar / Settlement data | Required | Lower Level | Upper Level | NMMS Label
|  | 61970 | iec61970CIMVersion | iec61970CIMVersion | date | date | String30 | 2006-12-18 | cim | Date. | TRUE | TRUE | TRUE | TRUE |  | FALSE |  | TRUE |  |  | date
|  | 61970 | iec61970CIMVersion | iec61970CIMVersion | version | version | String30 | cim6197011v00 | cim | Version | TRUE | TRUE | TRUE | TRUE |  | FALSE |  | TRUE |  |  | version
|  | CIMCore | BasePower | BasePower | basePower | basePower | ApparentPower |  | cim | Definition of base power. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Base Power
|  | CIMCore | BaseVoltage | BaseVoltage | nominalVoltage | nominalVoltage | Voltage |  | cim | The PowerSystemResource's base voltage. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 1100 | 0 | Nominal Voltage
|  | CIMCore | BasicIntervalSchedule | BasicIntervalSchedule | startTime | startTime | Time |  | cim | Start Time. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Start Time
|  | CIMCore | BasicIntervalSchedule | BasicIntervalSchedule | value1Unit | value1Unit | String20 |  | cim | Value 1 Unit. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value 1 Unit
|  | CIMCore | BasicIntervalSchedule | BasicIntervalSchedule | value2Unit | value2Unit | String20 |  | cim | Value 2 Unit. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value 2 Unit
|  | CIMCore | Bay | Bay | bayEnergyMeasFlag | bayEnergyMeasFlag | Boolean | FALSE | cim | Indicates the presence/absence of kWh/kvarh measurements. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | bay Energy Measurement Flag
|  | CIMCore | Bay | Bay | bayPowerMeasFlag | bayPowerMeasFlag | Boolean | FALSE | cim | Indicates the presence/absence of MW/MVAr measurements. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | bay Power Measurement Flag
|  | CIMCore | Bay | Bay | breakerConfiguration | breakerConfiguration | EnumBreakerConfiguration |  | cim | Breaker configuration. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Breaker Configuration
|  | CIMCore | Bay | Bay | busBarConfiguration | busBarConfiguration | EnumBusbarConfiguration |  | cim | Busbar configuration. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Busbar Configuration
|  | CIMCore | Company | Company | CompanyType | companyType | EnumCompanyType |  | cim | The type of company, e.g.: pool, municipal, private. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Company Type
|  | CIMCore | Company | Company | Cooperative | Cooperative | Boolean | FALSE | etx | Cooperative boolean. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cooperative
|  | CIMCore | Company | Company | DUNS | DUNS | String20 |  | etx | DUNS Number | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | DUNS
|  | CIMCore | Company | Company | Municipality | Municipality | Boolean | FALSE | etx | Municipality boolean. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Municipality
|  | CIMCore | Company | Company | PrimaryPhone | PrimaryPhone | String20 | (999) 999-9999 x____ | etx | Primary Phone number for contact. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Primary Phone
|  | CIMCore | Company | Company | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number owners. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
|  | CIMCore | Company | Company | qseId | qseId | String14 |  | etx | A 14 character QSE ID used for ERCOT LFC. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | QSE ID
|  | CIMCore | Company | Company | qseOpaId | qseOpaId | String6 |  | etx | A 6 character QSE OPA ID for the QSE operating in the QSE Simulator. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | QSE OPA ID
|  | CIMCore | Company | Company | SecondaryPhone | SecondaryPhone | String20 | (999) 999-9999 x____ | etx | Secondary Phone number for contact. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Secondary Phone
|  | CIMCore | Company | Company | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
|  | CIMCore | ConductingEquipment | ConductingEquipment | phases | phases | PhaseCode |  | cim | Describes the phases carried by a conducting equipment. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phases
|  | CIMCore | ConductingEquipment | ConductingEquipment | remove | remove | Boolean | FALSE | etx | The equipment is removed from the network. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Remove
|  | CIMCore | ConductingEquipment | ConductingEquipment | removeEnable | removeEnable | Boolean | FALSE | etx | The equipment can be removed from the network. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Remove Enable
|  | CIMCore | ControlHouseEquipment | ControlHouseEquipment | controlHouseEquipType | controlHouseEquipType | EnumControlHouseEquipmentType |  | cim | Type of control house equipment. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control House Equipment Type
|  | CIMCore | Curve | Curve | curveStyle | curveStyle | EnumCurveStyle |  | cim | The style or shape of the curve. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Curve Style
|  | CIMCore | Curve | Curve | xAxisUnits | xUnit | String20 |  | cim | The X-axis units of measure. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | X Axis Units
|  | CIMCore | Curve | Curve | y1AxisUnits | y1Unit | String20 |  | cim | The Y1-axis units of measure. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Y1 Axis Units
|  | CIMCore | Curve | Curve | y2AxisUnits | y2Unit | String20 |  | cim | The Y2-axis units of measure. Valid values: MW, MVAr, kV (Source: 61970-452, Normative String Table). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Y2 Axis Units
|  | CIMCore | CurveData | CurveData | xAxisData | xvalue | DoubleFloat | 0 | cim | The data value of the X-axis variable, depending on the X-axis units | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | X Axis Data
|  | CIMCore | CurveData | CurveData | y1AxisData | y1value | DoubleFloat | 0 | cim | The data value of the first Y-axis variable, depending on the Y-axis units | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Y1 Axis Data
|  | CIMCore | CurveData | CurveData | y2AxisData | y2value | DoubleFloat |  | cim | The data value of the second Y-axis variable (if present), depending on the Y-axis units | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Y2 Axis Data
|  | CIMCore | Equipment | Equipment | DAM_Monitored | DAM_Monitored | Boolean | FALSE | etx | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | DAM Monitored
|  | CIMCore | Equipment | Equipment | DAM_Secured | DAM_Secured | Boolean | TRUE | etx | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | DAM Secured
|  | CIMCore | Equipment | Equipment | OUSPriority | OUSPriority | Integer |  | etx | An Outage Scheduler priority is included in all ConductingEquipment classes except BusbarSection and TransformerWinding. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | OUS Priority
|  | CIMCore | Equipment | Equipment | psseid | psseid | String2 |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly name units, loads, branches, and transformers. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | PSS®E ID
|  | CIMCore | Equipment | Equipment | RUC_Monitored | RUC_Monitored | Boolean | FALSE | etx | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | RUC Monitored
|  | CIMCore | Equipment | Equipment | RUC_Secured | RUC_Secured | Boolean | TRUE | etx | The Boolean flags to indicate which process(s) monitor the branch devices and by which process the devices is secured. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | RUC Secured
|  | CIMCore | IdentifiedObject | IdentifiedObject | aliasName | aliasName | String100 |  | cim | Free text name of the object or instance. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Alias Name
|  | CIMCore | IdentifiedObject | IdentifiedObject | Description | description | String1000 |  | cim | Description of the object or instance. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Description
|  | CIMCore | IdentifiedObject | IdentifiedObject | localName | localName | String30 |  | cim | The localName is a human readable name of the object. It is only used with objects organized in a naming hierarchy. The simplest naming hierarchy has just one parent (the root) giving a flat naming hierarchy. However, the naming hierarchy usually has several levels, e.g. Substation, VoltageLevel, Equipment etc. Children of the same parent have names that are unique among them. If the uniqueness requirement cannot be met IdentifiedObject.localName shall not be used, use IdentifiedObject.name instead. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Local Name
|  | CIMCore | IdentifiedObject | IdentifiedObject | mRID | mRID | String100 |  | cim | A Model Authority issues mRIDs. Given that each Model Authority has a unique id and this id is part of the mRID, then the mRID is globally unique. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Model Resource ID
|  | CIMCore | IdentifiedObject | IdentifiedObject | pathName | pathName | String500 |  | cim | The pathname is a system unique name composed from all IdentifiedObject.names in a standard naming hierarchy path from the object to the root. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Path Name
|  | CIMCore | IrregularTimePoint | IrregularTimePoint | time | time | Seconds |  | cim | The time is relative the BasicTimeSchedule.startTime. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time
|  | CIMCore | IrregularTimePoint | IrregularTimePoint | value1 | value1 | Float |  | cim | Value 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value 1
|  | CIMCore | IrregularTimePoint | IrregularTimePoint | value2 | value2 | Float |  | cim | Value 2. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value 2
|  | CIMCore | PowerSystemResource | PowerSystemResource | Latitude | Latitude | Float |  | etx | Latiitude coordinates. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Latitude
|  | CIMCore | PowerSystemResource | PowerSystemResource | Longitude | Longitude | Float |  | etx | Longitude coordinates. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Longitude
|  | CIMCore | PowerSystemResource | PowerSystemResource | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
|  | CIMCore | RegularIntervalSchedule | RegularIntervalSchedule | endTime | endTime | Time |  | cim | End Time. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | End Time
|  | CIMCore | RegularIntervalSchedule | RegularIntervalSchedule | timeStep | timeStep | Seconds |  | cim | Time Step | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Time Step
|  | CIMCore | RegularTimePoint | RegularTimePoint | rtName | rtName | String100 |  | etx | Equivalent of IdentifiedObject.name. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | RT Name
|  | CIMCore | RegularTimePoint | RegularTimePoint | sequenceNumber | sequenceNumber | Integer |  | cim | Sequence Number. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Sequence Number
|  | CIMCore | RegularTimePoint | RegularTimePoint | value1 | value1 | DoubleFloat |  | cim | Value 1. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value 1
|  | CIMCore | RegularTimePoint | RegularTimePoint | value2 | value2 | DoubleFloat |  | cim | Value 2. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value 2
|  | CIMCore | SubControlArea | SubControlArea | ControlAreaNumber | ControlAreaNumber | Integer |  | etx | The SubControlArea is extended to include a ControlAreaNumber attribute to determine ordering of the areas (e.g., for display purposes). The values must be positive, unique, 1-relative, sequential integers without gaps. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Control Area Number
|  | CIMCore | SubControlArea | SubControlArea | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number Alternate Areas and Zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
|  | CIMCore | SubGeographicalRegion | SubGeographicalRegion | isWeatherZone | isWeatherZone | Bool | FALSE | etx | Indicates whether a SubGeographicalRegion is a Weather Zone. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | is WeatherZone
|  | CIMCore | SubGeographicalRegion | SubGeographicalRegion | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number Alternate Areas and Zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
|  | CIMCore | Substation | Substation | abnormalForAlarm | abnormalForAlarm | Boolean | FALSE | etx | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Abnormal For Alarm
|  | CIMCore | Substation | Substation | abnormalForSCADA | abnormalForSCADA | Boolean | FALSE | etx | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Abnormal For SCADA
|  | CIMCore | Substation | Substation | alarmLocation | alarmLocation | String8 |  | etx | Alarm location, must match LOC.ID_LOC in the Alarm database. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Alarm Location
|  | CIMCore | Substation | Substation | audibleTone | audibleTone | Boolean | FALSE | etx | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Audible Tone
|  | CIMCore | Substation | Substation | forNetwork | forNetwork | Bool | FALSE | etx | This flag is used to indicate this substation is used by Network application. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | for Network
|  | CIMCore | Substation | Substation | forScada | forScada | Bool | FALSE | etx | This flag is used to indicate this substation is used by SCADA application. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | for Scada
|  | CIMCore | Substation | Substation | inhibitAbnormalForAlarm | inhibitAbnormalForAlarm | Boolean | FALSE | etx | Permanently Inhibit the flag of abnormalForAlarm . | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Abnormal For Alarm
|  | CIMCore | Substation | Substation | inhibitAbnormalForSCADA | inhibitAbnormalForSCADA | Boolean | FALSE | etx | Permanently Inhibit the flag of abnormalForSCADA. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Abnormal For SCADA
|  | CIMCore | Substation | Substation | inhibitAudibleTone | inhibitAudibleTone | Boolean | FALSE | etx | Permanently Inhibit the flag of audibleTone. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Audible Tone
|  | CIMCore | Substation | Substation | inhibitLoggingAndAlarmList | inhibitLoggingAndAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Logging and Alarm List
|  | CIMCore | Substation | Substation | inhibitUnackAlarmList | inhibitUnacknowledgedAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Unacknowledged Alarm List
|  | CIMCore | Substation | Substation | initiallyInhibit | initiallyInhibit | Boolean | FALSE | etx | A flag indicating that when the system first comes online, alarm indications for this SCADA entiry will initially be inhibited. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Initially Inhibit
|  | CIMCore | Substation | Substation | loggingAndAlarmList | loggingAndAlarmList | Boolean | FALSE | etx | A flag indicating that SCADA will issue neither an alarm nor an event. Therefore, entries will appear in the neither the alarm list nor the event logs. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Logging and Alarm List
|  | CIMCore | Substation | Substation | overrideDefaultInhibitDef | overrideDefaultInhibitDefinition | Boolean | FALSE | etx | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Override Default Inhibit Definition
|  | CIMCore | Substation | Substation | unacknowledgedAlarmList | unacknowledgedAlarmList | Boolean | FALSE | etx | A flag ndicating that SCADA will issue an event to the event log, but will not issue unacknowledged alarm indications to the alarm list. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Unacknowledged Alarm List
|  | CIMCore | Terminal | Terminal | near | near | Boolean | FALSE | etx | Flag indicating whether the terminal is a near terminal of a branch. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Near
|  | CIMCore | Terminal | Terminal | PSSEBusName | PSSEBusName | String12 |  | etx | Store the PSS™E bus name that will be associated with the grouping of Connectivity Nodes in Option 2. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | PSS/E Bus Name
|  | CIMCore | Terminal | Terminal | PSSEBusNumber | PSSEBusNumber | Integer |  | etx | Attribute will be used to store the PSS™E bus number that will be associated with the grouping of Connectivity Nodes in Option 2. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 99997 | 1 | PSS/E Bus Number
|  | CIMCore | VoltageLevel | VoltageLevel | highVoltageLimit | highVoltageLimit | Voltage |  | cim | The bus bar's high voltage limit in kV | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1100 | 0 | High Voltage Limit
|  | CIMCore | VoltageLevel | VoltageLevel | lowVoltageLimit | lowVoltageLimit | Voltage |  | cim | The bus bar's low voltage limit in kV. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1100 | 0 | Low Voltage Limit
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | highPowerLimit | highPowerLimit | PU | 0.1 | cim | High Power Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | High Power Limit
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | inCoreThermalTC | inCoreThermalTC | Seconds | 10.9 | cim | In-Core Thermal Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | In Core Thermal TC
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | integralGain | integralGain | RateOfChange | 0.386 | cim | Integral Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 4 | 0.04 | Integral Gain
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | lowerLimit | lowerLimit | PU | 0.56 | cim | Initial Lower Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Lower Limit
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | lowPowerLimit | lowPowerLimit | PU | 0.1 | cim | Low Power Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Low Power Limit
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | pressureLimit | pressureLimit | PU | 0.09 | cim | Pressure Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Pressure Limit
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | pressureSetpointGA | pressureSetpointGA | Float | 0.222 | cim | Pressure Setpoint Gain Adjuster | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 2 | 0.02 | Pressure Setpoint GA
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | pressureSetpointTC1 | pressureSetpointTC1 | Seconds | 9 | cim | Pressure Setpoint Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 1 | Pressure Setpoint TC1
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | pressureSetpointTC2 | pressureSetpointTC2 | Seconds | 3 | cim | Pressure Setpoint Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 30 | 0 | Pressure Setpoint TC2
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | proportionalGain | proportionalGain | Float | 0 | cim | Proportional Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Proportional Gain
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux1 | rfAux1 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux1
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux2 | rfAux2 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux2
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux3 | rfAux3 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux3
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux4 | rfAux4 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux4
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux5 | rfAux5 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux5
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux6 | rfAux6 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux6
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux7 | rfAux7 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux7
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rfAux8 | rfAux8 | PU |  | cim | Coefficient for modeling the effect of off-nominal frequency and voltage on recirculation and core flow, which affects the BWR power output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | rfAux8
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | rodPatternConstant | rodPatternConstant | Float | 0.32 | cim | Constant Associated With Rod Pattern | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Rod Pattern Constant
|  | CIMGenerationDynamics | BWRSteamSupply | BWRSteamSupply | upperLimit | upperLimit | PU | 1.05 | cim | Initial Upper Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1.5 | 0 | Upper Limit
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | ambientTemp | ambientTemp | Temperature | 15 | cim | Default ambient temperature to be used in modeling applications | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 30 | 0 | Ambient Temp
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | auxPowerVersusFrequency | auxPowerVersusFrequency | PowerVersusFrequency |  | cim | Off-nominal frequency effect on turbine auxiliaries. Per unit reduction in auxiliary MW consumption versus per unit reduction in frequency (from rated frequency). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Aux Power Versus Frequency
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | auxPowerVersusVoltage | auxPowerVersusVoltage | PowerVersusVoltage |  | cim | Off-nominal voltage effect on turbine auxiliaries. Per unit reduction in auxiliary MW consumption versus per unit reduction in auxiliary bus voltage (from a specified voltage level). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Aux Power Versus Voltage
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | capabiltiyVersusFrequency | capabiltiyVersusFrequency | PowerVersusFrequency |  | cim | Off-nominal frequency effect on turbine capability. Per unit reduction in unit MW capability versus per unit reduction in frequency (from rated frequency). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Capability Versus Frequency
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | fractionPlcControl | fractionPlcControl | PerCent |  | etx | Fraction of the PLC Control. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fraction of the PLC Control
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | freqAffectAux | freqAffectAux | Frequency |  | etx | Frequency above which auxiliaries are unaffected. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Affected Auxiliaries
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | governorDeadband | governorDeadband | PU |  | etx | Governor Dead Band | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Governor Dead Band
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | heatRecoveryFlag | heatRecoveryFlag | Boolean | FALSE | cim | Flag that is set to true if the combustion turbine is associated with a heat recovery boiler | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Heat Recovery Flag
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | lrmLowerLimit | lrmLowerLimit | PU |  | etx | Load Reference Motor Lower Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Lower Limit
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | lrmLowerRateLimit | lrmLowerRateLimit | RateOfChange |  | etx | Load Reference Motor Lower Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Lower Rate Limit
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | lrmRaiseRateLimit | lrmRaiseRateLimit | RateOfChange |  | etx | Load Reference Motor Raise Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Raise Rate Limit
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | lrmUpperLimit | lrmUpperLimit | PU |  | etx | Load Reference Motor Upper Limit.. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Upper Limit
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | powerMN | powerMN | ActivePower |  | etx | Power Based on Fuel Flow Minimum. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Power Minimum
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | powerMX | powerMX | ActivePower |  | etx | Power Based on Fuel Flow Maximum. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Power Maximum
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | powerVariationByTemp | powerVariationByTemp | PU | 0.11 | cim | Per unit change in power per (versus) unit change in ambient temperature | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0.01 | Power Variation By Temp
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | referenceTemp | referenceTemp | Temperature | 15 | cim | Reference temperature at which the output of the turbine was defined. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 30 | 0 | Reference Temp
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | regulationConstant | regulationConstant | PU |  | etx | Regulation Constant. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Regulation Constant
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | timeConstant | timeConstant | Seconds | 0.25 | cim | The time constant for the turbine. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 2 | 0.02 | Time Constant
|  | CIMGenerationDynamics | CombustionTurbine | CombustionTurbine | voltAffectAux | voltAffectAux | Voltage |  | etx | Voltage above which auxiliaries are unaffected. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Voltage Affected Auxiliaries
|  | CIMGenerationDynamics | CTTEMPMWCurve | CTTEMPMWCurve | temperatureUnits | temperatureUnits | EnumTemperatureUnits |  | cim | The temperature units (C or F). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Temperature Units
|  | CIMGenerationDynamics | DrumBoiler | DrumBoiler | drumBoilerRating | drumBoilerRating | Float |  | cim | Rating of drum boiler in steam units. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Drum Boiler Rating
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | auxPowerVersusFrequency | auxPowerVersusFrequency | PowerVersusFrequency |  | cim | Off nominal frequency effect on auxiliary real power. Per unit MW variation versus per unit frequency variation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Aux Power Versus Frequency
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | auxPowerVersusVoltage | auxPowerVersusVoltage | PowerVersusVoltage |  | cim | Off nominal voltage effect on auxiliary real power. Per unit MW variation versus per unit kV variation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Aux Power Versus Voltage
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | boilerControlMode | boilerControlMode | EnumBoilerControlMode |  | cim | The control mode of the boiler. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Boiler Control Mode
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | controlIC | controlIC | Float |  | cim | Integral Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Integral Constant
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | controlMWEB | controlMWEB | Ratio |  | cim | MW Error Bias | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control MW Error Bias
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | controlPC | controlPC | Float |  | cim | Proportional Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Proportional Constant
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | controlPEB | controlPEB | Ratio |  | cim | Pressure Error Bias | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Pressure Error Bias
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | controlPED | controlPED | PU |  | cim | Pressure Error Deadband | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Pressure Error Deadband
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | controlTC | controlTC | Float |  | cim | Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Time Constant
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | feedWaterIG | feedWaterIG | Ratio |  | cim | Feedwater Integral Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Feedwater Integral Gain
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | feedWaterPG | feedWaterPG | Ratio |  | cim | Feedwater Proportional Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Feedwater Proportional Gain
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | feedWaterTC | feedWaterTC | Seconds |  | cim | Feedwater Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Feedwater Time Constant
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | fuelDemandLimit | fuelDemandLimit | PU | 1 | cim | Fuel Demand Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Fuel Demand Limit
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | fuelSupplyDelay | fuelSupplyDelay | Seconds |  | cim | Fuel Delay | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Delay
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | fuelSupplyTC | fuelSupplyTC | Seconds |  | cim | Fuel Supply Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Supply Time Constant
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | mechPowerSensorLag | mechPowerSensorLag | Seconds | 1 | cim | Mechanical Power Sensor Lag | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 20 | 0 | Mech Power Sensor Lag
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | mWMaximumER | mWMaximumER | RateOfChange | 0.13 | cim | MW Maximum Error Rate Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | MW Maximum ER
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | mWMinimumER | mWMinimumER | RateOfChange | -0.13 | cim | MW Minimum Error Rate Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 0 | -1 | MW Minimum ER
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | pressureCtrlDG | pressureCtrlDG | Ratio |  | cim | Pressure Control Derivative Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pressure Control Derivative Gain
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | pressureCtrlG | pressureCtrlG | Ratio |  | cim | Pressure Control Integratl Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pressure Control Integratl Gain
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | pressureCtrlPG | pressureCtrlPG | Ratio |  | cim | Pressure Control Proportional Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pressure Control Proportional Gain
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | pressureFeedback | pressureFeedback | Integer | 1 | cim | Pressure Feedback Indicator | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 4 | 0 | Pressure Feedback
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | superHeater1Capacity | superHeater1Capacity | Float |  | cim | Drum/Primary Superheater Capacity | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Drum/Primary Superheater Capacity
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | superHeater2Capacity | superHeater2Capacity | Float |  | cim | Secondary Superheater Capacity | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Secondary Superheater Capacity
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | superHeaterPipePD | superHeaterPipePD | Float |  | cim | Superheater Pipe Pressure Drop Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Superheater Pipe Pressure Drop Constant
|  | CIMGenerationDynamics | FossilSteamSupply | FossilSteamSupply | throttlePressureSP | throttlePressureSP | PU | 1 | cim | Throttle Pressure Setpoint | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Throttle Pressure SP
|  | CIMGenerationDynamics | HeatRecoveryBoiler | HeatRecoveryBoiler | steamSupplyRating2 | steamSupplyRating2 | Float |  | cim | The steam supply rating in kilopounds per hour, if dual pressure boiler. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Steam Supply Rating 2
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | backlashWidth | backlashWidth | PU |  | etx | Backlash Width. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Backlash Width
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | fractionPlcControl | fractionPlcControl | PerCent |  | etx | Fraction of the PLC Control. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fraction of the PLC Control
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | gateCloseRateLimit | gateCloseRateLimit | RateOfChange |  | etx | Gate Close Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gate Close Rate Limit
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | gateLowerLimit | gateLowerLimit | PU |  | etx | Gate Lower Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gate Lower Limit
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | gateOpenRateLimit | gateOpenRateLimit | RateOfChange |  | etx | Gate Open Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gate Open Rate Limit
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | gateRateLimit | gateRateLimit | RateOfChange |  | cim | Gate Rate Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gate Rate Limit
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | gateUpperLimit | gateUpperLimit | PU |  | cim | Gate Upper Limit | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gate Upper Limit
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | lrmLowerLimit | lrmLowerLimit | PU |  | etx | Load Reference Motor Lower Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Lower Limit
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | lrmLowerRateLimit | lrmLowerRateLimit | RateOfChange |  | etx | Load Reference Motor Lower Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Lower Rate Limit
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | lrmRaiseRateLimit | lrmRaiseRateLimit | RateOfChange |  | etx | Load Reference Motor Raise Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Raise Rate Limit
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | lrmUpperLimit | lrmUpperLimit | PU |  | etx | Load Reference Motor Upper Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Upper Limit
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | maxEffMWatMaxHead | maxEffMWatMaxHead | ActivePower |  | cim | Maximum efficiency MW at maximum head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Efficiency MW at Max Head
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | maxEffMWatMinHead | maxEffMWatMinHead | ActivePower |  | cim | Maximum efficiency MW at minimum head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Efficiency MW at Min Head
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | speedRating | speedRating | Integer |  | cim | Rated speed in revolutions per minute. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Speed Rating
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | speedRegulation | speedRegulation | PU |  | cim | Speed Regulation | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Speed Regulation
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | transientDroopTime | transientDroopTime | Seconds | 64 | cim | Transient Droop Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 500 | 1 | Transient Droop Time
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | transientRegulation | transientRegulation | PU | 0.125 | cim | Transient Regulation | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 2 | 0.01 | Transient Regulation
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | turbineRating | turbineRating | ActivePower |  | cim | Rated turbine power in MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Turbine Rating
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | turbineType | turbineType | EnumTurbineType |  | cim | Type of turbine, e.g.: Francis, Pelton, Kaplan. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Turbine Type
|  | CIMGenerationDynamics | HydroTurbine | HydroTurbine | waterStartingTime | waterStartingTime | Seconds | 2 | cim | Water Starting Time | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 20 | 0.2 | Water Starting Time
|  | CIMGenerationDynamics | PrimeMover | PrimeMover | primeMoverRating | primeMoverRating | Float |  | cim | Rating of prime mover. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Prime Mover Rating
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coldLegFBLagTC | coldLegFBLagTC | PU | 4.065 | cim | Cold Leg Feedback Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 40 | 0.4 | Cold Leg FBLag TC
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coldLegFBLeadTC1 | coldLegFBLeadTC1 | PU | 3.56 | cim | Cold Leg Feedback Lead Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 35 | 0.35 | Cold Leg FB Lead TC1
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coldLegFBLeadTC2 | coldLegFBLeadTC2 | PU | 3.94 | cim | Cold Leg Feedback Lead Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 40 | 0.4 | Cold Leg FB Lead TC2
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coldLegFG1 | coldLegFG1 | PU | 8.05 | cim | Cold Leg Feedback Gain 1 | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 80 | 0.8 | Cold Leg FG1
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coldLegFG2 | coldLegFG2 | PU | 0.974 | cim | Cold Leg Feedback Gain 2 | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 10 | 0.01 | Cold Leg FG2
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coldLegLagTC | coldLegLagTC | PU | 4.67 | cim | Cold Leg Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 46 | 0.46 | Cold Leg Lag TC
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coreHTLagTC1 | coreHTLagTC1 | PU | 2.105 | cim | Core Heat Transfer Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 20 | 0.2 | Core HTLag TC1
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coreHTLagTC2 | coreHTLagTC2 | PU | 20.835 | cim | Core Heat Transfer Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 200 | 2 | Core HTLag TC2
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coreNeutronicsEffTC | coreNeutronicsEffTC | PU | 12.195 | cim | Core Neutronics Effective Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 120 | 1.2 | Core Neutronics Eff TC
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | coreNeutronicsHT | coreNeutronicsHT | PU | 0.032 | cim | Core Neutronics And Heat Transfer | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 0.3 | 0.003 | Core Neutronics HT
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | feedbackFactor | feedbackFactor | PU | 7.25 | cim | Feedback Factor | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 70 | 0.07 | Feedback Factor
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | hotLegLagTC | hotLegLagTC | PU | 3.19 | cim | Hot Leg Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 32 | 0.32 | Hot Leg Lag TC
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | hotLegSteamGain | hotLegSteamGain | PU | 1.3 | cim | Hot Leg Steam Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 13 | 0.13 | Hot Leg Steam Gain
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | hotLegToColdLegGain | hotLegToColdLegGain | PU | 0.397 | cim | Hot Leg To Cold Leg Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 4 | 0.04 | Hot Leg To Cold Leg Gain
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | pressureCG | pressureCG | PU | 0.75 | cim | Pressure Control Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 7.5 | 0.075 | Pressure CG
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | steamFlowFG | steamFlowFG | PU | 0.54 | cim | Steam Flow Feedback Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 5.4 | 0.054 | Steam Flow FG
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | steamPressureDropLagTC | steamPressureDropLagTC | PU | 1.56 | cim | Steam Pressure Drop Lag Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 15 | 0.15 | Steam Pressure Drop Lag TC
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | steamPressureFG | steamPressureFG | PU | 1 | cim | Steam Pressure Feedback Gain | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 10 | 0.1 | Steam Pressure FG
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | throttlePressureFactor | throttlePressureFactor | PU | 0.613 | cim | Throttle Pressure Factor | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 6 | 0.06 | Throttle Pressure Factor
|  | CIMGenerationDynamics | PWRSteamSupply | PWRSteamSupply | throttlePressureSP | throttlePressureSP | PU | 1 | cim | Throttle Pressure Setpoint | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Throttle Pressure SP
|  | CIMGenerationDynamics | SteamSupply | SteamSupply | steamSupplyRating | steamSupplyRating | Float |  | cim | Rating of steam supply. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Steam Supply Rating
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | crossoverTC | crossoverTC | Seconds | 0 | cim | Crossover Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Crossover TC
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | cvLowerLimit | cvLowerLimit | PU |  | etx | Control Valve Lower Limits. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Valve Lower Limits
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | cvLowerRateLimit | cvLowerRateLimit | RateOfChange |  | etx | Control Valve Lower Rate Limits. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Valve Lower Rate Limits
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | cvRaiseRateLimit | cvRaiseRateLimit | RateOfChange |  | etx | Control Valve Raise Rate Limits. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Valve Raise Rate Limits
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | cvUpperLimit | cvUpperLimit | PU |  | etx | Control Valve Upper Limits. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Valve Upper Limits
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | fractionPlcControl | fractionPlcControl | PerCent |  | etx | Fraction of the PLC Control. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fraction of the PLC Control
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | governorDeadband | governorDeadband | PU |  | etx | Governor Dead Band | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Governor Dead Band
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | lrmLowerLimit | lrmLowerLimit | PU |  | etx | Load Reference Motor Lower Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Lower Limit
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | lrmLowerRateLimit | lrmLowerRateLimit | RateOfChange |  | etx | Load Reference Motor Lower Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Lower Rate Limit
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | lrmRaiseRateLimit | lrmRaiseRateLimit | RateOfChange |  | etx | Load Reference Motor Raise Rate Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Raise Rate Limit
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | lrmUpperLimit | lrmUpperLimit | PU |  | etx | Load Reference Motor Upper Limit.. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Reference Motor Upper Limit
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | regulationConstant | regulationConstant | PU |  | etx | Regulation Constant. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Regulation Constant
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | reheater1TC | reheater1TC | Seconds | 8 | cim | First Reheater Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Reheater1 TC
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | reheater2TC | reheater2TC | Seconds | 0 | cim | Second Reheater Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Reheater2 TC
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft1PowerHP | shaft1PowerHP | Fraction | 0.3 | cim | Fraction Of Power From Shaft 1 High Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft1 Power HP
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft1PowerIP | shaft1PowerIP | Fraction | 0.7 | cim | Fraction Of Power From Shaft 1 Intermediate Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft1 Power IP
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft1PowerLP1 | shaft1PowerLP1 | Fraction | 0 | cim | Fraction Of Power From Shaft 1 First Low Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft1 Power LP1
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft1PowerLP2 | shaft1PowerLP2 | Fraction | 0 | cim | Fraction Of Power From Shaft 1 Second Low Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft1 Power LP2
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft2PowerHP | shaft2PowerHP | Fraction |  | cim | Fraction Of Power From Shaft 2 High Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Shaft2 Power HP
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft2PowerIP | shaft2PowerIP | Fraction | 0 | cim | Fraction Of Power From Shaft 2 Intermediate Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft2 Power IP
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft2PowerLP1 | shaft2PowerLP1 | Fraction | 0 | cim | Fraction Of Power From Shaft 2 First Low Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft2 Power LP1
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | shaft2PowerLP2 | shaft2PowerLP2 | Fraction | 0 | cim | Fraction Of Power From Shaft 2 Second Low Pressure Turbine output | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Shaft2 Power LP2
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | slidingPressureScalingFactor | slidingPressureScalingFactor | PerCent |  | etx | Sliding Pressure Scaling Factor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Sliding Pressure Scaling Factor
|  | CIMGenerationDynamics | SteamTurbine | SteamTurbine | steamChestTC | steamChestTC | Seconds | 0 | cim | Steam Chest Time Constant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Steam Chest TC
|  | CIMLoadModel | DayType | DayType | endTime | endTime | AbsoluteDateTime |  | etx | Time daytype ends | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | End Time
|  | CIMLoadModel | DayType | DayType | FriFlag | FriFlag | Bool | FALSE | etx | Indicates whether Friday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Fri Flag
|  | CIMLoadModel | DayType | DayType | MonFlag | MonFlag | Bool | FALSE | etx | Indicates whether Monday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Mon Flag
|  | CIMLoadModel | DayType | DayType | SatFlag | SatFlag | Bool | FALSE | etx | Indicates whether Saturday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Sat Flag
|  | CIMLoadModel | DayType | DayType | startTime | startTime | AbsoluteDateTime |  | etx | Time daytype starts | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Start Time
|  | CIMLoadModel | DayType | DayType | SunFlag | SunFlag | Bool | FALSE | etx | Indicates whether Sunday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Sun Flag
|  | CIMLoadModel | DayType | DayType | ThursFlag | ThursFlag | Bool | FALSE | etx | Indicates whether Thursday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Thurs Flag
|  | CIMLoadModel | DayType | DayType | TuesFlag | TuesFlag | Bool | FALSE | etx | Indicates whether Tuesday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Tues Flag
|  | CIMLoadModel | DayType | DayType | WedFlag | WedFlag | Bool | FALSE | etx | Indicates whether Wednesday is included in this Day Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Wed Flag
|  | CIMLoadModel | InductionMotorLoad | InductionMotorLoad | r | r | DoubleFloat |  | etx | motor r. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | r
|  | CIMLoadModel | InductionMotorLoad | InductionMotorLoad | rtransformer | rtransformer | Float |  | etx | stepup transformer r. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | r Transformer
|  | CIMLoadModel | InductionMotorLoad | InductionMotorLoad | varhighlimit | varhighlimit | Float |  | etx | motor var high limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Var High Limit
|  | CIMLoadModel | InductionMotorLoad | InductionMotorLoad | varlowlimit | varlowlimit | Float |  | etx | motor var low limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Var Low Limit
|  | CIMLoadModel | InductionMotorLoad | InductionMotorLoad | x | x | DoubleFloat |  | etx | motor x. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | x
|  | CIMLoadModel | InductionMotorLoad | InductionMotorLoad | xtransformer | xtransformer | Float |  | etx | stepup transformer x. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | x Transformer
|  | CIMLoadModel | Load | Load | feederLoadMgtFactor | feederLoadMgtFactor | PerCent |  | cim | The feeder's contribution to load management, in percent. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Feeder Load Mgt Factor
|  | CIMLoadModel | Load | Load | loadAllocationFactor | loadAllocationFactor | Float |  | cim | Permit assignment of loads on a participation factor basis. Given three equivalent loads with factors of 10, 25 and 15, a feeder load of 100 amps could be allocated on the feeder as 20, 50 and 30 amps. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Allocation Factor
|  | CIMLoadModel | Load | Load | mVArColdPickUpFactor | mVArColdPickUpFactor | PerCent |  | cim | The amount of nominal feeder MVAr that is picked up cold, in percent. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | MVAR Cold Pick Up Factor
|  | CIMLoadModel | Load | Load | mWColdPickUpFactor | mWColdPickUpFactor | PerCent |  | cim | The amount of nominal feeder MW that is picked up cold, in percent. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | MW Cold Pick Up Factor
|  | CIMLoadModel | Load | Load | phaseAmpRating | phaseAmpRating | CurrentFlow |  | cim | The rated individual phase amperes. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phase Amp Rating
|  | CIMLoadModel | LoadArea | LoadArea | forecastEnabled | forecastEnabled | Boolean | FALSE | etx | Forecast enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Forecast Enabled
|  | CIMLoadModel | LoadArea | LoadArea | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number Alternate Areas and Zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
|  | CIMLoadModel | LoadGroup | LoadGroup | forecastEnabled | forecastEnabled | Boolean | FALSE | etx | Forecast enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Forecast Enabled
|  | CIMLoadModel | PowerCutZone | PowerCutZone | cutLevel1 | cutLevel1 | PerCent |  | cim | First level (amount) of load to cut as a percentage of total zone load. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cut Level 1
|  | CIMLoadModel | PowerCutZone | PowerCutZone | cutLevel2 | cutLevel2 | PerCent |  | cim | Second level (amount) of load to cut as a percentage of total zone load. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cut Level 2
|  | CIMLoadModel | Season | Season | endDate | endDate | AbsoluteDateTime |  | cim | Date season ends. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | End Date
|  | CIMLoadModel | Season | Season | SeasonName | name | EnumSeasonName |  | cim | Name of the Season. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Season Name
|  | CIMLoadModel | Season | Season | startDate | startDate | AbsoluteDateTime |  | cim | Date season starts. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Start Date
|  | CIMLoadModel | StationSupply | StationSupply | step | step | Boolean | FALSE | etx | Schedule is step function. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Step
|  | CIMLoadModel | SubLoadArea | SubLoadArea | forecastEnabled | forecastEnabled | Boolean | FALSE | etx | Forecast enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Forecast Enabled
|  | CIMMeas | Accumulator | Accumulator | maxValue | maxValue | Integer |  | cim | Normal value range maximum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  | 0 | Max Value
|  | CIMMeas | AccumulatorLimit | AccumulatorLimit | value | value | Integer |  | cim | The value to supervise against. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Value
|  | CIMMeas | AccumulatorValue | AccumulatorValue | value | value | Integer |  | cim | Value of measurement. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Value
|  | CIMMeas | Analog | Analog | forNetwork | forNetwork | Bool | FALSE | etx | If true then this measurement is only for network monitoring. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | for Network
|  | CIMMeas | Analog | Analog | maxValue | maxValue | Float |  | cim | Normal value range maximum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Value
|  | CIMMeas | Analog | Analog | minValue | minValue | Float |  | cim | Normal value range minimum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Value
|  | CIMMeas | Analog | Analog | normalValue | normalValue | Float |  | cim | Normal measurement value, e.g., used for percentage calculations. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Normal Value
|  | CIMMeas | Analog | Analog | positiveFlowIn | positiveFlowIn | Boolean | FALSE | cim | If true then this measurement is a MW, MVAR or AMPS with the convention that a positive value measured at the Terminal means power is flowing into the related PowerSystemResource. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Positive Flow In
|  | CIMMeas | Analog | Analog | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
|  | CIMMeas | AnalogLimit | AnalogLimit | deadband | deadband | PerCent |  | etx | Amount, expressed as a percentage of the range between upper and lower threshold, used in the limit comparison to eliminate extraneous alarms generated when an analog value oscillates around a limit. When either threshold is null, the percentage is that of the non?null limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Deadband
|  | CIMMeas | AnalogLimit | AnalogLimit | forbiddenRegion | forbiddenRegion | Boolean | FALSE | etx | T = The analog is in violation if it is smaller than the Upper Threshold and larger than the Lower Threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Forbidden Region
|  | CIMMeas | AnalogLimit | AnalogLimit | ignoreLimitChecking | ignoreLimitChecking | Boolean | FALSE | etx | T = The limit should be ignored when checking the analog for limit violations. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Ignore Limit Checking
|  | CIMMeas | AnalogLimit | AnalogLimit | limitType | limitType | EnumLimitType |  | etx | Type of limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Limit Type
|  | CIMMeas | AnalogLimit | AnalogLimit | lowerThreshold | lowerThreshold | Float |  | etx | The value below which the analog is considered in violation of the limit. When the Upper Threshold is null, only the Lower Threshold is checked for violation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Lower Threshold
|  | CIMMeas | AnalogLimit | AnalogLimit | upperThreshold | upperThreshold | Float |  | etx | The value above which the analog is considered in violation of the limit. When the low limit is null, only the high limit is checked for violation. This value must be greater then the Lower Threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Upper Threshold
|  | CIMMeas | AnalogLimit | AnalogLimit | usePercentage | usePercentage | Boolean | FALSE | etx | T = The value displayed in the deadband field (below) is the percentage deadband. Otherwise, the value displayed is the numeric deadband. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Use Percentage
|  | CIMMeas | AnalogLimit | AnalogLimit | value | value | DoubleFloat |  | cim | The value to supervise against. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value
|  | CIMMeas | AnalogLimit | AnalogLimit | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temporary attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
|  | CIMMeas | AnalogValue | AnalogValue | abnormalAlarmDelayTime | abnormalAlarmDelayTime | Integer |  | etx | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the violated state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Abnormal Alarm Delay Time
|  | CIMMeas | AnalogValue | AnalogValue | allowSELECTStep | allowSELECTStep | Boolean | FALSE | etx | TRUE = a separate SELECT action is allowed (but not required) prior to the supervisory control action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Allow SELECT Step
|  | CIMMeas | AnalogValue | AnalogValue | autoAckAndDeleteAlarms | autoAckAndDeleteAlarms | Boolean | FALSE | etx | Automatically acknowledge and delete alarms if the Analog is manually entered or successfully controlled by the operator to a normal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Auto Ack and Delete Alarms
|  | CIMMeas | AnalogValue | AnalogValue | autoAcknowledge | autoAcknowledge | Boolean | FALSE | etx | When set to true, this flag specifies that alarms will be automatically acknowledged on return to normal. This will only occur if the Alarm Return to Violations flag is not set on the Limit Names table. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Auto Acknowledge
|  | CIMMeas | AnalogValue | AnalogValue | controlDemandScan | controlDemandScan | Boolean | FALSE | etx | True = Issues a demand scan request to the RTU at a configurable number of seconds after any successful control requests are issued. This feature is primarily used by measurements with a slow scan rate to provide more timely feedback on the success or failure of the control operation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Control Demand Scan
|  | CIMMeas | AnalogValue | AnalogValue | controlMMISequence | controlMMISequence | Boolean | FALSE | etx | true = override any default settings. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Control MMI Sequence
|  | CIMMeas | AnalogValue | AnalogValue | enableAutoSEReplacement | enableAutoSEReplacement | Boolean | FALSE | etx | TRUE = Allow automatic State Estimator replacement. Automatically substitute the display value with a good quality state estimated value if the quality of the telemetered analog becomes SUSPECT. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Enable Auto SE Replacement
|  | CIMMeas | AnalogValue | AnalogValue | fromStateEstimator | fromStateEstimator | Boolean | FALSE | etx | When set to true, this flag specifies the source of the data is state estimator. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | From State Estimator
|  | CIMMeas | AnalogValue | AnalogValue | historicalRecordingDeadband | historicalRecordingDeadband | PerCent |  | etx | Threshold (percentage currently recorded analog data) above which additional data points should not retained. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Historical Recording Deadband
|  | CIMMeas | AnalogValue | AnalogValue | invertAnalogViaSecondarySite | invertAnalogViaSecondarySite | Boolean | FALSE | etx | TRUE = Negate the analog value when received from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Analog Via Secondary Site
|  | CIMMeas | AnalogValue | AnalogValue | invertSign | invertSign | Boolean | FALSE | etx | When set to true, this flag specifies that the analog value, as received by SCADA, is inverted before using in other applications. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Sign
|  | CIMMeas | AnalogValue | AnalogValue | negateValueReceivedFromISD | negateValueReceivedFromISD | Boolean | FALSE | etx | When set to true, this flag specifies that the polarity of the analog value received via ISD will be switched. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Negate Value Received from ISD
|  | CIMMeas | AnalogValue | AnalogValue | negativeUniPolarClamping | negativeUniPolarClamping | Boolean | FALSE | etx | True = positive values will be forced (clamped) to zero before updating into the database. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Negative Uni-Polar Clamping
|  | CIMMeas | AnalogValue | AnalogValue | peakData | peakData | Boolean | FALSE | etx | When set to true, this flag specifies that the Peak Data Processing task will sample this analog. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Peak Data
|  | CIMMeas | AnalogValue | AnalogValue | positiveUniPolarClamping | positiveUniPolarClamping | Boolean | FALSE | etx | TRUE = negative values will be forced (clamped) to zero before updating into the database. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Positive Uni-Polar Clamping
|  | CIMMeas | AnalogValue | AnalogValue | requireEXECUTEStep | requireEXECUTEStep | Boolean | FALSE | etx | True = a supervisory control action is not initiated when a control action is received, and must wait for an additional EXECUTE action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Require EXECUTE Step
|  | CIMMeas | AnalogValue | AnalogValue | requireSELECTStep | requireSELECTStep | Boolean | FALSE | etx | TRUE = a separate SELECT action is required before a supervisory control action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Require SELECT Step
|  | CIMMeas | AnalogValue | AnalogValue | returnToNormalAlarmDelayTime | returnToNormalAlarmDelayTime | Integer |  | etx | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the normal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Return to Normal Alarm Delay Time
|  | CIMMeas | AnalogValue | AnalogValue | seDeadband | seDeadband | Float |  | etx | Display values of good quality which are different than a good quality state-estimated value by more than this amount are considered anomalous, and automatically substituted with the state-estimated value, if the global Automatic State-Estimator Replacement function is enabled. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | SE Deadband
|  | CIMMeas | AnalogValue | AnalogValue | skipLimitChecking | skipLimitChecking | Boolean | FALSE | etx | When set to true, this flag specifies disable reasonability limit checking for this analog. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Skip Limit Checking
|  | CIMMeas | AnalogValue | AnalogValue | timeDelay | timeDelay | Integer |  | etx | The number of seconds after the control request is successfully issued before sending a demand scan request to the associated RTU. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Time Delay
|  | CIMMeas | AnalogValue | AnalogValue | value | value | Float |  | cim | Value of measurement. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value
|  | CIMMeas | AnalogValue | AnalogValue | zeroClampingDeadband | zeroClampingDeadband | Float |  | etx | If value is greater than zero, then any value between zero and the entered value will be forced (clamped) to zero for update into the database. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Zero Clamping Deadband
|  | CIMMeas | Command | Command | normalValue | normalValue | Integer |  | cim | Normal value for Control.value e.g. used for percentage scaling. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Normal Value
|  | CIMMeas | Command | Command | value | value | Integer |  | cim | The value representing the actuator output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value
|  | CIMMeas | Control | Control | operationInProgress | operationInProgress | Boolean | FALSE | cim | Indicates that a client is currently sending control commands that has not completed. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Operation In Progress
|  | CIMMeas | Control | Control | timeStamp | timeStamp | AbsoluteDateTime |  | cim | The last time a control output was sent. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time Stamp
|  | CIMMeas | Discrete | Discrete | maxValue | maxValue | Integer |  | cim | Normal value range maximum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Value
|  | CIMMeas | Discrete | Discrete | minValue | minValue | Integer |  | cim | Normal value range minimum for any of the MeasurementValue.values. Used for scaling, e.g. in bar graphs or of telemetered raw values. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Value
|  | CIMMeas | Discrete | Discrete | normalValue | normalValue | Integer |  | cim | Normal measurement value, e.g., used for percentage calculations. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Normal Value
|  | CIMMeas | Discrete | Discrete | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
|  | CIMMeas | DiscreteValue | DiscreteValue | abnormalAlarmDelayTime | abnormalAlarmDelayTime | Integer |  | etx | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the abnormal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Abnormal Alarm Delay Time
|  | CIMMeas | DiscreteValue | DiscreteValue | allowControlFromForeignSites | allowControlFromForeignSites | Boolean | FALSE | etx | True = Another site may issue a control on this point. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Allow Control from Foreign Sites
|  | CIMMeas | DiscreteValue | DiscreteValue | allowMultipleRaiseOrLower | allowMultipleRaiseOrLower | Boolean | FALSE | etx | True = Multiple Tap Raise and Lower commands may be issued consecutively without re-selecting the... | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Allow Multiple Raise or Lower
|  | CIMMeas | DiscreteValue | DiscreteValue | allowSELECTStep | allowSELECTStep | Boolean | FALSE | etx | TRUE = a separate SELECT action is allowed (but not required) prior to the supervisory control action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Allow SELECT Step
|  | CIMMeas | DiscreteValue | DiscreteValue | autoAckAndDeleteAlarms | autoAckAndDeleteAlarms | Boolean | FALSE | etx | True = Automatically acknowledge and delete alarms if the Point is manually entered or successfully controlled by the operator to a normal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Auto Ack and Delete Alarms
|  | CIMMeas | DiscreteValue | DiscreteValue | autoAcknowledge | autoAcknowledge | Boolean | FALSE | etx | True = alarms will be automatically acknowledged on return to normal. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Auto Acknowledge
|  | CIMMeas | DiscreteValue | DiscreteValue | controlDemandScan | controlDemandScan | Boolean | FALSE | etx | True = Issues a demand scan request to the RTU at a configurable number of seconds after any successful control requests are issued. This feature is primarily used by measurements with a slow scan rate to provide more timely feedback on the success or failure of the control operation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Control Demand Scan
|  | CIMMeas | DiscreteValue | DiscreteValue | feedbackAnalog | feedbackAnalog | String4 |  | etx | True = The Analog Name which is configured to provide feedback of the associated analog value for control completion checks of Raise/Lower supervisory controls. The chosen Analog must be modeled under the same Device as the controlling Point record. This field is optional. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Feedback Analog
|  | CIMMeas | DiscreteValue | DiscreteValue | invertExtStatusViaISD | invertExtendedStatusViaISD | Boolean | FALSE | etx | True = The extended status bit (XIS) will be inverted when received from the primary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Extended Status via ISD
|  | CIMMeas | DiscreteValue | DiscreteValue | invertExtStatusViaSecSite | invertExtendedStatusViaSecSite | Boolean | FALSE | etx | True = The extended status bit (XIS) will be inverted when received from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Extended Status Via Sec Site
|  | CIMMeas | DiscreteValue | DiscreteValue | invertStatus | invertStatus | Boolean | FALSE | etx | True = The status point value, as received by SCADA, is inverted before using in other applications. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Status
|  | CIMMeas | DiscreteValue | DiscreteValue | invertStatusBitRcvdViaISD | invertStatusBitReceivedViaISD | Boolean | FALSE | etx | True = The status bit (SIS) will be inverted when received from the primary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Status Bit Received Via ISD
|  | CIMMeas | DiscreteValue | DiscreteValue | invertStatusBitRcvdVia2Site | invertStatusBitReceivedViaSecSite | Boolean | FALSE | etx | True = The status bit (SIS) will be inverted when received from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Invert Status Bit Received Via Sec Site
|  | CIMMeas | DiscreteValue | DiscreteValue | logForControlIssued | logForControlIssued | Boolean | FALSE | etx | True = Controls issued on this point will be logged in the system activity log. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Log for Control Issued
|  | CIMMeas | DiscreteValue | DiscreteValue | momentaryChangeDetection | momentaryChangeDetection | Boolean | FALSE | etx | True = a momentary change detection status will be returned. Momentary change detection status informs the computer of changes that occur between scans. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Momentary Change Detection
|  | CIMMeas | DiscreteValue | DiscreteValue | noISDDownload | noISDDownload | Boolean | FALSE | etx | True = Even though the Point is associated with a remote site, the Point will not be included in the Intersite Data download request for status values to the remote site. The remote site is only used for determining which site to send Supervisory Controls to. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | No ISD Download
|  | CIMMeas | DiscreteValue | DiscreteValue | noWarningIfHanging | noWarningIfHanging | Boolean | FALSE | etx | Don't issue warning message if a lone Topology Node is defined, which is not defined on any other record within the Substation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | No Warning if Hanging
|  | CIMMeas | DiscreteValue | DiscreteValue | requireEXECUTEStep | requireEXECUTEStep | Boolean | FALSE | etx | True = a supervisory control action is not initiated when a control action is received, and must wait for an additional EXECUTE action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Require EXECUTE Step
|  | CIMMeas | DiscreteValue | DiscreteValue | requireSELECTStep | requireSELECTStep | Boolean | FALSE | etx | TRUE = a separate SELECT action is required before a supervisory control action. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Require SELECT Step
|  | CIMMeas | DiscreteValue | DiscreteValue | returnToNormalAlarmDelayTime | returnToNormalAlarmDelayTime | Integer |  | etx | The number of seconds for the alarm to remain on the persistance alarm list before toning/alarming because it remained in the normal state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Return to Normal Alarm Delay Time
|  | CIMMeas | DiscreteValue | DiscreteValue | statusBitLiveIndication | statusBitLiveIndication | Boolean | FALSE | etx | T = S bit true indicates LIVE, false indicates DEAD; F = S bit true indicates DEAD, false indicates LIVE. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | status Bit Live Indication
|  | CIMMeas | DiscreteValue | DiscreteValue | tapChangerTimeout | tapChangerTimeout | Integer |  | etx | The timeout between steps of a multiple raise/lower supervisory control sequence for a tap changer. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Tap Changer Timeout
|  | CIMMeas | DiscreteValue | DiscreteValue | threeState | threeState | Boolean | FALSE | etx | True = A three-state point is modeled. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Three State
|  | CIMMeas | DiscreteValue | DiscreteValue | timeDelay | timeDelay | Integer |  | etx | Demand Scan After Control is configured for this point, enter the number of seconds after the control request is successfully issued before sending a demand scan request to the associated RTU. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  | 0 | Time Delay
|  | CIMMeas | DiscreteValue | DiscreteValue | value | value | Integer |  | cim | Value of measurement. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value
|  | CIMMeas | LimitSet | LimitSet | forNetwork | forNetwork | Bool | FALSE | etx | If true then this measurement is only for network monitoring. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | for Network
|  | CIMMeas | LimitSet | LimitSet | isPercentageLimits | isPercentageLimits | Boolean | FALSE | cim | Tells if the limit values are in percentage of normalValue or the specified Unit for Measurements and Controls. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Is Percentage Limits
|  | CIMMeas | LimitSet | LimitSet | type | type | EnumLimitSetType |  | etx | Type. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Type
|  | CIMMeas | LimitSet | LimitSet | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temporary attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
|  | CIMMeas | Measurement | Measurement | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temp Attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Zonal Attribute
|  | CIMMeas | MeasurementValue | MeasurementValue | abnormalForAlarm | abnormalForAlarm | Boolean | FALSE | etx | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Abnormal For Alarm
|  | CIMMeas | MeasurementValue | MeasurementValue | abnormalForSCADA | abnormalForSCADA | Boolean | FALSE | etx | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Abnormal For SCADA
|  | CIMMeas | MeasurementValue | MeasurementValue | audibleTone | audibleTone | Boolean | FALSE | etx | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Audible Tone
|  | CIMMeas | MeasurementValue | MeasurementValue | blockViaPrimarySite | blockViaPrimarySite | Boolean | FALSE | etx | Block Value and Quality update via Primary Site: Do not allow update from the primary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Block via Primary Site
|  | CIMMeas | MeasurementValue | MeasurementValue | blockViaSecondarySite | blockViaSecondarySite | Boolean | FALSE | etx | Block Value and Quality update via Secondary Site: Do not allow update from the secondary site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Block via Secondary Site
|  | CIMMeas | MeasurementValue | MeasurementValue | byPass | byPass | Boolean | FALSE | etx | When set to true, this flag specifies allowing bypass entry of Suspect values if telemetered from a remote site or SCADA Front End. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | byPass
|  | CIMMeas | MeasurementValue | MeasurementValue | cstatus | cstatus | Boolean | FALSE | etx | True when value represents status of communication path component. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Component Status
|  | CIMMeas | MeasurementValue | MeasurementValue | dataSetPeriod | dataSetPeriod | Integer |  | etx | ICCP data set period used for the measurement. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ICCP Data Set Period
|  | CIMMeas | MeasurementValue | MeasurementValue | fromCalculation | fromCalculation | Boolean | FALSE | etx | Value is from calculation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | from Calculation
|  | CIMMeas | MeasurementValue | MeasurementValue | fromExternalProgram | fromExternalProgram | Boolean | FALSE | etx | When set to true, this flag specifies the source of the data is an external program. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | From External Program
|  | CIMMeas | MeasurementValue | MeasurementValue | fromManualEntry | fromManualEntry | Boolean | FALSE | etx | Value is from manual entry. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | from Manual Entry
|  | CIMMeas | MeasurementValue | MeasurementValue | fromRemote | fromRemote | Boolean | FALSE | etx | Value is from remote. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | from Remote
|  | CIMMeas | MeasurementValue | MeasurementValue | habcName | habcName | String60 |  | etx | Connection ID of value using HABConnect. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | HABC Name
|  | CIMMeas | MeasurementValue | MeasurementValue | iccpVmd | iccpVmd | Boolean | FALSE | etx | True when value has VMD scope. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | VMD Scope
|  | CIMMeas | MeasurementValue | MeasurementValue | inhibitAbnormalForAlarm | inhibitAbnormalForAlarm | Boolean | FALSE | etx | Permanently Inhibit the flag of abnormalForAlarm. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Abnormal For Alarm
|  | CIMMeas | MeasurementValue | MeasurementValue | inhibitAbnormalForSCADA | inhibitAbnormalForSCADA | Boolean | FALSE | etx | Permanently Inhibit the flag of abnormalForSCADA. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Abnormal For SCADA
|  | CIMMeas | MeasurementValue | MeasurementValue | inhibitAudibleTone | inhibitAudibleTone | Boolean | FALSE | etx | Permanently Inhibit the flag of audibleTone. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Audible Tone
|  | CIMMeas | MeasurementValue | MeasurementValue | inhibitLoggingAndAlarmList | inhibitLoggingAndAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Logging and Alarm List
|  | CIMMeas | MeasurementValue | MeasurementValue | inhibitUnackAlarmList | inhibitUnacknowledgedAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Unacknowledged Alarm List
|  | CIMMeas | MeasurementValue | MeasurementValue | initiallyInhibit | initiallyInhibit | Boolean | FALSE | etx | A flag indicating that when the system first comes online, alarm indications for this SCADA entry will initially be inhibited. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Initially Inhibit
|  | CIMMeas | MeasurementValue | MeasurementValue | isdName | isdName | String60 |  | etx | Dollar-separacted SCADA Composite ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ISD Name
|  | CIMMeas | MeasurementValue | MeasurementValue | loggingAndAlarmList | loggingAndAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Logging and Alarm List
|  | CIMMeas | MeasurementValue | MeasurementValue | mappedInOag | mappedInOag | Boolean | FALSE | etx | T = This data-point is also represented in the OAG model as a data item (designated member of a data packet). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Mapped In OAG
|  | CIMMeas | MeasurementValue | MeasurementValue | notInService | notInService | Boolean | FALSE | etx | flag indicating not in service. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Not In Service
|  | CIMMeas | MeasurementValue | MeasurementValue | overrideDefaultnhibitDef | overrideDefaultInhibitDefinition | Boolean | FALSE | etx | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Override Default Inhibit Definition
|  | CIMMeas | MeasurementValue | MeasurementValue | recordHistoricalData | recordHistoricalData | Boolean | FALSE | etx | When set to true, this flag specifies that state changes on the analog are recorded in the historical data review file. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Record Historical Data
|  | CIMMeas | MeasurementValue | MeasurementValue | RsCalculated | RsCalculated | Boolean | FALSE | etx | Remote site normally calculated. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Remote Site Normally Calculated
|  | CIMMeas | MeasurementValue | MeasurementValue | RsExtern | RsExtern | Boolean | FALSE | etx | Remote site normally estimated. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Remote Site Normally Estimated
|  | CIMMeas | MeasurementValue | MeasurementValue | RsManual | RsManual | Boolean | FALSE | etx | Remote site normally manually entered. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Remote Site Normally Manually Entered
|  | CIMMeas | MeasurementValue | MeasurementValue | RsTelemetered | RsTelemetered | Boolean | FALSE | etx | Remote site normally telemetered. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Remote Site Normally Telemetered
|  | CIMMeas | MeasurementValue | MeasurementValue | sensorAccuracy | sensorAccuracy | PerCent |  | cim | The limit, expressed as a percentage of the sensor maximum, that errors will not exceed when the sensor is used under reference conditions. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Sensor Accuracy
|  | CIMMeas | MeasurementValue | MeasurementValue | tabularDisplayPriority | tabularDisplayPriority | Integer |  | etx | Priority of tabulay display. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Tabular Display Priority
|  | CIMMeas | MeasurementValue | MeasurementValue | timeStamp | timeStamp | AbsoluteDateTime |  | cim | The time when the value was last updated. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time Stamp
|  | CIMMeas | MeasurementValue | MeasurementValue | unacknowledgedAlarmList | unacknowledgedAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Unacknowledged Alarm List
|  | CIMMeas | MeasurementValue | MeasurementValue | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temp Attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
|  | CIMMeas | MeasurementValueQuality | MeasurementValueQuality | hasCOV | hasCOV | Boolean | FALSE | etx | Whether or not ICCP item has Change of Value modifier. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | has COV
|  | CIMMeas | MeasurementValueQuality | MeasurementValueQuality | hasQuality | hasQuality | Boolean | FALSE | etx | Whether or not ICCP item has Quality modifier. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | has Quality
|  | CIMMeas | MeasurementValueQuality | MeasurementValueQuality | hasTimestamp | hasTimestamp | Boolean | FALSE | etx | Whether or not ICCP item has Timestamp modifier. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | has Timestamp
|  | CIMMeas | MeasurementValueQuality | MeasurementValueQuality | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temporary attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | biverAus | biverAus | String32 |  | etx | Bilateral Table Version for ICCP connection from Austin. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Austin - Bilateral Table Version
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | biverTay | biverTay | String32 |  | etx | Bilateral Table Version for ICCP connection from Taylor. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Taylor - Bilateral Table Version
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | BufferTime | BufferTime | Integer |  | etx | Buffer time to apply to datasets created for this remote. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Buffer Time
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | defaultDataSetPeriod | defaultDataSetPeriod | Integer | 10 | etx | ICCP data set period used for the measurement(seconds). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ICCP Default Data Set Period
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | GraceTime | GraceTime | Integer |  | etx | Grace time to apply to datasets created for this remote. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Grace Time
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | iccpDomainAus | iccpDomainAus | String32 |  | etx | Remote Domain name for ICCP connection from Austin. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Austin - Remote Domain
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | iccpDomainTay | iccpDomainTay | String32 |  | etx | Remote Domain name for ICCP connection from Taylor. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Taylor - Remote Domain
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | IntegrityPeriod | IntegrityPeriod | Integer |  | etx | Integrity time to apply to datasets created for this remote. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ICCP Integrity Period
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | lnkapp | lnkapp | String8 |  | etx | ICCPLINK' for ICCP remote sites. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Link App
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | MaxDisPerDataset | MaxDisPerDataset | Integer |  | etx | Maximun number of dataitems to put in datasets for this remote. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Dataitems per Dataset
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | maxScanRate | maxScanRate | Integer |  | etx | Minimum seconds between scan requests. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Scan Rate
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | notInService | notInService | Boolean | FALSE | etx | false if REMOTE is ready for data exchange. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Not In Service?
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool1 | pbool1 | Boolean | FALSE | etx | Protocol-Specific Flag 1. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 1
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool2 | pbool2 | Boolean | FALSE | etx | Protocol-Specific Flag 2. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 2
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool3 | pbool3 | Boolean | FALSE | etx | Protocol-Specific Flag 3. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 3
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool4 | pbool4 | Boolean | FALSE | etx | Protocol-Specific Flag 4. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 4
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool5 | pbool5 | Boolean | FALSE | etx | Protocol-Specific Flag 5. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 5
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool6 | pbool6 | Boolean | FALSE | etx | Protocol-Specific Flag 6. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 6
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool7 | pbool7 | Boolean | FALSE | etx | Protocol-Specific Flag 7. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 7
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | pbool8 | pbool8 | Boolean | FALSE | etx | Protocol-Specific Flag 8. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol-Specific Flag 8
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | protocolVersion | protocolVersion | Integer |  | etx | Version of ICCP protocol used (2000 or 1996). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Protocol Version
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | remoteIdAus | remoteIdAus | String16 |  | etx | Name of remote site for connection from Austin. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Austin - Remote Id
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | remoteIdTay | remoteIdTay | String16 |  | etx | Name of remote site for connection from Taylor. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Taylor - Remote Id
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | savecaseType | savecaseType | EnumSavecaseType |  | etx | To be set by an ERCOT Modeling Engineer. This value indicates the type of the remote site. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | savecaseType
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | trsfr | trsfr | Integer |  | etx | Protocol-specific value. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Protocol Specific Value
|  | CIMMeas | MeasurementValueSource | MeasurementValueSource | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temp Attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
|  | CIMMeas | Quality61850 | Quality61850 | badReference | badReference | Boolean | FALSE | cim | Measurement value may be incorrect due to a reference being out of calibration. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Bad Reference
|  | CIMMeas | Quality61850 | Quality61850 | estimatorReplaced | estimatorReplaced | Boolean | FALSE | cim | Value has been replaced by State Estimator. estimatorReplaced is not an IEC61850 quality bit but has been put in this class for convenience. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Estimator Replaced
|  | CIMMeas | Quality61850 | Quality61850 | failure | failure | Boolean | FALSE | cim | This identifier indicates that a supervision function has detected an internal or external failure, e.g. communication failure. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Failure
|  | CIMMeas | Quality61850 | Quality61850 | oldData | oldData | Boolean | FALSE | cim | Measurement value is old and possibly invalid, as it has not been successfully updated during a specified time interval. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Old Data
|  | CIMMeas | Quality61850 | Quality61850 | operatorBlocked | operatorBlocked | Boolean | FALSE | cim | Measurement value is blocked and hence unavailable for transmission. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Operator Blocked
|  | CIMMeas | Quality61850 | Quality61850 | oscillatory | oscillatory | Boolean | FALSE | cim | To prevent some overload of the communication it is sensible to detect and suppress oscillating (fast changing) binary inputs. If a signal changes in a defined time (tosc) twice in the same direction (from 0 to 1 or from 1 to 0) then oscillation is detected and the detail quality identifier 'oscillatory' is set. If it is detected a configured numbers of transient changes could be passed by. In this time the validity status 'questionable' is set. If after this defined numbers of changes the signal is still in the oscillating state the value shall be set either to the opposite state of the previous stable value or to a defined default value. In this case the validity status 'questionable' is reset and 'invalid' is set as long as the signal is oscillating. If it is configured such that no transient changes should be passed by then the validity status 'invalid' is set immediately in addition to the detail quality identifier 'oscillatory' (used for status information only). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Oscillatory
|  | CIMMeas | Quality61850 | Quality61850 | outOfRange | outOfRange | Boolean | FALSE | cim | Measurement value is beyond a predefined range of value. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Out of Range
|  | CIMMeas | Quality61850 | Quality61850 | overFlow | overFlow | Boolean | FALSE | cim | Measurement value is beyond the capability of being represented properly. For example, a counter value overflows from maximum count back to a value of zero. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Flow
|  | CIMMeas | Quality61850 | Quality61850 | source | source | EnumSource | 0 | cim | Source gives information related to the origin of a value. The value may be acquired from the process, defaulted or substituted. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Source
|  | CIMMeas | Quality61850 | Quality61850 | suspect | suspect | Boolean | FALSE | cim | A correlation function has detected that the value is not consitent with other values. Typically set by a network State Estimator. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Suspect
|  | CIMMeas | Quality61850 | Quality61850 | test | test | Boolean | FALSE | cim | Measurement value is transmitted for test purposes. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Test
|  | CIMMeas | Quality61850 | Quality61850 | validity | validity | EnumValidity | 0 | cim | Validity may be good, questionable or invalid. Refer to the Validity enumeration for more details. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Validity
|  | CIMMeas | SetPoint | SetPoint | allowControlFromForeignSites | allowControlFromForeignSites | Boolean | FALSE | etx | CONTROLLED AT REMOTE SITE: T = Another site may issue this setpoint. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Allow Control From Foreign Sites
|  | CIMMeas | SetPoint | SetPoint | audibleTone | audibleTone | Boolean | FALSE | etx | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | audible Tone
|  | CIMMeas | SetPoint | SetPoint | deadBand | deadBand | Float |  | etx | SETPOINT ANALOG DEADBAND (STATIC). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Deadband
|  | CIMMeas | SetPoint | SetPoint | inhibitAudibleTone | inhibitAudibleTone | Boolean | FALSE | etx | Permanently Inhibit the flag of audibleTone. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | inhibit Audible Tone
|  | CIMMeas | SetPoint | SetPoint | inhibitLoggingAndAlarmList | inhibitLoggingAndAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | inhibit Logging And Alarm List
|  | CIMMeas | SetPoint | SetPoint | inhibitUnackAlarmList | inhibitUnacknowledgedAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | inhibit Unacknowledged Alarm List
|  | CIMMeas | SetPoint | SetPoint | initiallyInhibit | initiallyInhibit | Boolean | FALSE | etx | A flag indicating that when the system first comes online, alarm indications for this SCADA entry will initially be inhibited. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | initially Inhibit
|  | CIMMeas | SetPoint | SetPoint | loggingAndAlarmList | loggingAndAlarmList | Boolean | FALSE | etx | A flag indicating that SCADA will issue neither an alarm nor an event. Therefore, entries will appear in the neither the alarm list nor the event logs. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | logging And Alarm List
|  | CIMMeas | SetPoint | SetPoint | maxValue | maxValue | Float |  | cim | Normal value range maximum for any of the Control.value. Used for scaling, e.g. in bar graphs. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Value
|  | CIMMeas | SetPoint | SetPoint | minValue | minValue | Float |  | cim | Normal value range minimum for any of the Control.value. Used for scaling, e.g. in bar graphs. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Value
|  | CIMMeas | SetPoint | SetPoint | noLog | noLog | Boolean | FALSE | etx | T = Setpoints issued on this analog are not logged. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | No Log
|  | CIMMeas | SetPoint | SetPoint | normalValue | normalValue | Float |  | cim | Normal value for Control.value e.g. used for percentage scaling. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Normal Value
|  | CIMMeas | SetPoint | SetPoint | notInService | notInService | Boolean | FALSE | etx | Amount by which the analog value may vaFloat. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Not In Service
|  | CIMMeas | SetPoint | SetPoint | overrideDefaultInhibitDef | overrideDefaultInhibitDefinition | Boolean | FALSE | etx | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | override Default Inhibit Definition
|  | CIMMeas | SetPoint | SetPoint | timeOut | timeOut | Integer |  | etx | DEVICE OPERATION TIME LIMIT - This value indicates the device operation time limit in seconds. If the setpoint request was successfully transmitted to the RTU and the associated analog does not show that the device moved to the required value within this period, the setpoint operation is considered failed. A zero indicates an indefinite operation time limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Time Out
|  | CIMMeas | SetPoint | SetPoint | unackAlarmList | unacknowledgedAlarmList | Boolean | FALSE | etx | A flag indicating that SCADA will issue an event to the event log, but will not issue unacknowledged alarm indications to the alarm list. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | unacknowledged Alarm List
|  | CIMMeas | SetPoint | SetPoint | value | value | Float |  | cim | The value representing the actuator output. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value
|  | CIMMeas | SetPoint | SetPoint | waitTime | waitTime | Integer |  | etx | Wait time. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Wait Time
|  | CIMMeas | SetPoint | SetPoint | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temporary attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
|  | CIMMeas | StringMeasurementValue | StringMeasurementValue | value | value | String100 |  | cim | Value of measurement. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value
|  | CIMMeas | ValueToAlias | ValueToAlias | value | value | Integer |  | cim | The value that is mapped. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Value
|  | CIMOutage | ClearanceTag | ClearanceTag | authorityName | authorityName | String100 |  | cim | The name of the person who is authorized to issue the tag. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Authority Name
|  | CIMOutage | ClearanceTag | ClearanceTag | clearanceTagType | clearanceTagType | EnumClearanceTagType |  | cim | The type of tag, depending on the purpose of the work to be performed and/or the type of supervisory control allowed. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Clearance Tag Type
|  | CIMOutage | ClearanceTag | ClearanceTag | deenergizeReqFlag | deenergizeReqFlag | Boolean | FALSE | cim | Flag = YES if equipment must be deenergized. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | De-Energize Req Flag
|  | CIMOutage | ClearanceTag | ClearanceTag | groundReqFlag | groundReqFlag | Boolean | FALSE | cim | Flag = YES if equipment must be grounded. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Ground Req Flag
|  | CIMOutage | ClearanceTag | ClearanceTag | phaseCheckReqFlag | phaseCheckReqFlag | Boolean | FALSE | cim | Flag = YES if equipment phasing must be checked. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phase Check Req Flag
|  | CIMOutage | ClearanceTag | ClearanceTag | tagIssueTime | tagIssueTime | AbsoluteDateTime |  | cim | The time at which the clearance tag was issued. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tag Issue Time
|  | CIMOutage | ClearanceTag | ClearanceTag | workDescription | workDescription | String1000 |  | cim | Description of the work to be performed. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Work Description
|  | CIMOutage | ClearanceTag | ClearanceTag | workEndTime | workEndTime | AbsoluteDateTime |  | cim | The time at which the clearance tag is scheduled to be removed. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Work End Time
|  | CIMOutage | ClearanceTag | ClearanceTag | workStartTime | workStartTime | AbsoluteDateTime |  | cim | WorkStartTime | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Work Start Time
|  | CIMOutage | SwitchingOperation | SwitchingOperation | newState | newState | EnumSwitchState |  | cim | New State. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | New State
|  | CIMOutage | SwitchingOperation | SwitchingOperation | operationTime | operationTime | AbsoluteDateTime |  | cim | Time of operation in same units as OutageSchedule.xAxixUnits. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Operation Time
|  | CIMProduction | AirCompressor | AirCompressor | airCompressorRating | airCompressorRating | Float |  | cim | Rating of the CAES air compressor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Air Compressor Rating
|  | CIMProduction | CAESPlant | CAESPlant | energyStorageCapacity | energyStorageCapacity | EnergyAsMWh |  | cim | The rated energy storage capacity in megawatt-hours. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Energy Storage Capacity
|  | CIMProduction | CAESPlant | CAESPlant | ratedCapacityMW | ratedCapacityMW | ActivePower |  | cim | The CAES plant's gross rated generating capacity in MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Rated Capacity MW
|  | CIMProduction | CogenerationPlant | CogenerationPlant | cogenHPSendoutRating | cogenHPSendoutRating | Float |  | cim | The high pressure steam sendout, in klb/hour | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cogen HPSendout Rating
|  | CIMProduction | CogenerationPlant | CogenerationPlant | cogenHPSteamRating | cogenHPSteamRating | Float |  | cim | The high pressure steam rating, in psi | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cogen HPSteam Rating
|  | CIMProduction | CogenerationPlant | CogenerationPlant | cogenLPSendoutRating | cogenLPSendoutRating | Float |  | cim | The low pressure steam sendout, in klb/hour | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cogen LPSendout Rating
|  | CIMProduction | CogenerationPlant | CogenerationPlant | cogenLPSteamRating | cogenLPSteamRating | Float |  | cim | The low pressure steam rating, in psi | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cogen LPSteam Rating
|  | CIMProduction | CogenerationPlant | CogenerationPlant | cogenPlantMWRating | cogenPlantMWRating | ActivePower |  | cim | The rated output MW of the cogeneration plant | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cogen Plant MWRating
|  | CIMProduction | CombinedCyclePlant | CombinedCyclePlant | blockLoadTransfer | blockLoadTransfer | Boolean | FALSE | etx | Block load transfer. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Block Load Transfer
|  | CIMProduction | CombinedCyclePlant | CombinedCyclePlant | combCyclePlantRating | combCyclePlantRating | ActivePower |  | cim | The combined cycle plant's output rating, in MW | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Comb Cycle Plant Rating
|  | CIMProduction | CombinedCyclePlant | CombinedCyclePlant | commercialOperationsDate | commercialOperationsDate | Date |  | etx | Date commercial operations started. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Commercial Operations Date
|  | CIMProduction | CombinedCyclePlant | CombinedCyclePlant | GstTpspiMax | GstTpspiMax | Float |  | etx | GstTpspiMax | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | GstTpspiMax
|  | CIMProduction | CombinedCyclePlant | CombinedCyclePlant | GstTpspiMin | GstTpspiMin | Float |  | etx | GstTpspiMin | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | GstTpspiMin
|  | CIMProduction | CombinedCyclePlant | CombinedCyclePlant | GtMax | GtMax | Float |  | etx | GtMax | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | GtMax
|  | CIMProduction | CombinedCyclePlant | CombinedCyclePlant | GtMin | GtMin | Float |  | etx | GtMin | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | GtMin
|  | CIMProduction | CombinedCyclePlant | CombinedCyclePlant | LogicalResourceNodeName | LogicalResourceNodeName | String12 |  | etx | Logical resource node name. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Logical Resource Node Name
|  | CIMProduction | CombinedCyclePlant | CombinedCyclePlant | qualificationStatus | qualificationStatus | Boolean | FALSE | etx | Qualification status. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Qualification Status
|  | CIMProduction | CombinedCyclePlant | CombinedCyclePlant | resourceCategory | resourceCategory | String50 |  | etx | Type of resource. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Type of Resource
|  | CIMProduction | CombinedCyclePlant | CombinedCyclePlant | wfrmcr | wfrmcr | Boolean | FALSE | etx | wfrmcr. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | wfrmcr
|  | CIMProduction | EmissionAccount | EmissionAccount | emissionType | emissionType | EnumEmissionType |  | cim | The type of emission, for example sulfur dioxide (SO2). The y1AxisUnits of the curve contains the unit of measure (e.g. kg) and the emissionType is the type of emission (e.g. sulfer dioxide). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emission Type
|  | CIMProduction | EmissionAccount | EmissionAccount | emissionValueSource | emissionValueSource | EnumEmissionValueSource |  | cim | The source of the emission value: Measured or Calculated. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emission Value Source
|  | CIMProduction | EmissionCurve | EmissionCurve | emissionContent | emissionContent | Emission |  | cim | The emission content per quantity of fuel burned. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emission Content
|  | CIMProduction | EmissionCurve | EmissionCurve | emissionType | emissionType | EnumEmissionType |  | cim | The type of emission, which also gives the production rate measurement unit. The y1AxisUnits of the curve contains the unit of measure (e.g. kg) and the emissionType is the type of emission (e.g. sulfer dioxide). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emission Type
|  | CIMProduction | EmissionCurve | EmissionCurve | netGrossMWFlag | netGrossMWFlag | Boolean | FALSE | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net Gross MW Flag
|  | CIMProduction | FossilFuel | FossilFuel | fossilFuelType | fossilFuelType | EnumFuelType |  | cim | The type of fossil fuel, such as coal, oil, or gas. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fossil Fuel Type
|  | CIMProduction | FossilFuel | FossilFuel | fuelCost | fuelCost | CostPerHeatUnit |  | cim | The cost in terms of heat value for the given type of fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Cost
|  | CIMProduction | FossilFuel | FossilFuel | fuelDispatchCost | fuelDispatchCost | CostPerHeatUnit |  | cim | The cost of fuel used for economic dispatching which includes: fuel cost, transportation cost, and incremental maintenance cost. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Dispatch Cost
|  | CIMProduction | FossilFuel | FossilFuel | fuelEffFactor | fuelEffFactor | PU |  | cim | The efficiency factor for the fuel (per unit) in terms of the effective MBtu absorbed. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Efficiency Factor
|  | CIMProduction | FossilFuel | FossilFuel | fuelHandlingCosgt | fuelHandlingCosgt | CostPerHeatUnit |  | cim | Handling and processing cost associated with this fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Handling Cost
|  | CIMProduction | FossilFuel | FossilFuel | fuelHeatContent | fuelHeatContent | Float |  | cim | The amount of heat (Btu) per weight (or volume) of the given type of fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Heat Content
|  | CIMProduction | FossilFuel | FossilFuel | fuelMixture | fuelMixture | PerCent |  | cim | The amount in percent of the given type of fuel , when multiple fuels are being consumed. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Mixture
|  | CIMProduction | FossilFuel | FossilFuel | fuelSulfur | fuelSulfur | PU |  | cim | The fuel's fraction of pollution credit per unit of heat content (MBtu). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Sulfur
|  | CIMProduction | FossilFuel | FossilFuel | highMWBreakpoint | highMWBreakpoint | ActivePower |  | cim | The MW output level of the unit at which the given type of fuel is switched on. This fuel (e.g., oil) is sometimes used to supplement the base fuel (e.g., coal) at high MW output levels. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | High MW Breakpoint
|  | CIMProduction | FossilFuel | FossilFuel | lowMWBreakpoint | lowMWBreakpoint | ActivePower |  | cim | The MW output level of the unit at which the given type of fuel is switched off. This fuel (e.g., oil) is sometimes used to stabilize the base fuel (e.g., coal) at low MW output levels. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Low MW Breakpoint
|  | CIMProduction | FuelAllocationSchedule | FuelAllocationSchedule | fuelAllocationEndDate | fuelAllocationEndDate | AbsoluteDateTime |  | cim | The end time and date of the fuel allocation schedule. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Allocation End Date
|  | CIMProduction | FuelAllocationSchedule | FuelAllocationSchedule | fuelAllocationStartDate | fuelAllocationStartDate | AbsoluteDateTime |  | cim | The start time and date of the fuel allocation schedule. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Allocation Start Date
|  | CIMProduction | FuelAllocationSchedule | FuelAllocationSchedule | fuelType | fuelType | EnumFuelType |  | cim | The type of fuel, which also indicates the corresponding measurement unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Type
|  | CIMProduction | FuelAllocationSchedule | FuelAllocationSchedule | maxFuelAllocation | maxFuelAllocation | Float |  | cim | The maximum amount fuel that is allocated for consumption for the scheduled time period. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Fuel Allocation
|  | CIMProduction | FuelAllocationSchedule | FuelAllocationSchedule | minFuelAllocation | minFuelAllocation | Float |  | cim | The minimum amount fuel that is allocated for consumption for the scheduled time period, e.g., based on a 'take-or-pay' contract. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Fuel Allocation
|  | CIMProduction | GeneratingUnit | GeneratingUnit | allocSpinResMW | allocSpinResMW | ActivePower |  | cim | The planned unused capacity (spinning reserve) which can be used to support emergency load. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Alloc Spin Res MW
|  | CIMProduction | GeneratingUnit | GeneratingUnit | autoCntrlMarginMW | autoCntrlMarginMW | ActivePower |  | cim | The planned unused capacity which can be used to support automatic control overruns, in MW. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Auto Control Margin MW
|  | CIMProduction | GeneratingUnit | GeneratingUnit | baseMW | baseMW | ActivePower |  | cim | For dispatchable units, this value represents the economic MW basepoint, for units that are not dispatchable, this value represents the fixed generation value. The value must be between the operating low and high limits. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Base MW
|  | CIMProduction | GeneratingUnit | GeneratingUnit | blackStart | blackStart | Bool | FALSE | etx | TRUE - Unit is qualified to black start. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Black Start
|  | CIMProduction | GeneratingUnit | GeneratingUnit | blockLoadTransfer | blockLoadTransfer | Boolean | FALSE | etx | Block load transfer. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Block Load Transfer
|  | CIMProduction | GeneratingUnit | GeneratingUnit | coldStartTime | coldStartTime | Float |  | etx | Cold start time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Cold start time
|  | CIMProduction | GeneratingUnit | GeneratingUnit | commercialOperationsDate | commercialOperationsDate | Date |  | etx | Commericial operations date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Commercial Operations Date
|  | CIMProduction | GeneratingUnit | GeneratingUnit | controlDeadband | controlDeadband | ActivePower |  | cim | Unit control error deadband. When a unit's desired MW change is less than this deadband, then no control pulses will be sent to the unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Control Deadband
|  | CIMProduction | GeneratingUnit | GeneratingUnit | ControlPulseHigh | controlPulseHigh | Seconds | 0.5 | cim | Pulse high limit which is the largest control pulse that the unit can respond to. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Control Pulse High
|  | CIMProduction | GeneratingUnit | GeneratingUnit | ControlPulseLow | controlPulseLow | Seconds | 0.5 | cim | Pulse low limit which is the smallest control pulse that the unit can respond to. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Control Pulse Low
|  | CIMProduction | GeneratingUnit | GeneratingUnit | controlResponseRate | controlResponseRate | PowerROCPerSec | 2 | cim | MW change for a control pulse of one second in the most responsive loading level of the unit. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Control Response Rate
|  | CIMProduction | GeneratingUnit | GeneratingUnit | dispReserveFlag | dispReserveFlag | Boolean | FALSE | cim | Display Reserve Flag | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Disp Reserve Flag
|  | CIMProduction | GeneratingUnit | GeneratingUnit | Efficiency | efficiency | PU | 1 | cim | The efficiency of the unit in converting mechanical energy, from the prime mover, into electrical energy. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE | 1.2 | 0.001 | Efficiency
|  | CIMProduction | GeneratingUnit | GeneratingUnit | energyMinMW | energyMinMW | HeatPerHour |  | cim | Energy Minimum MW. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Energy Min MW
|  | CIMProduction | GeneratingUnit | GeneratingUnit | fastStartFlag | fastStartFlag | Boolean | FALSE | cim | Fast Start Flag. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Fast Start Flag
|  | CIMProduction | GeneratingUnit | GeneratingUnit | freqBias | freqBias | Float |  | etx | Unit Regulating Frequency Bias as MW per 0.1 Hz. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Frequency Bias
|  | CIMProduction | GeneratingUnit | GeneratingUnit | freqDevDeadband | freqDevDeadband | Float |  | etx | Frequency deviation deadband for Feed-Forward correction. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Frequencey Deviation Deadband
|  | CIMProduction | GeneratingUnit | GeneratingUnit | frequencyDeadBandHz | frequencyDeadBandHz | Float |  | etx | Allowable deviation of the unit frequency. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Deadband HZ
|  | CIMProduction | GeneratingUnit | GeneratingUnit | fuelPriority | fuelPriority | Priority |  | cim | Fuel Priority. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fuel Priority
|  | CIMProduction | GeneratingUnit | GeneratingUnit | genControlMode | genControlMode | EnumGeneratorControlMode |  | cim | Select the unit control mode as Setpoint (S) or Pulse (P). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Generator Control Mode
|  | CIMProduction | GeneratingUnit | GeneratingUnit | genControlSource | genControlSource | EnumGeneratorControlSource |  | cim | The source of controls for a generating unit, i.e., Unavailable, Off-AGC, On-AGC, Plant Control. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Gen Control Source
|  | CIMProduction | GeneratingUnit | GeneratingUnit | OperatingMode | genOperatingMode | EnumGeneratorOperatingMode | 0 | cim | Operating mode for secondary control, e.g.: Off, Manual, Fixed, LFC, AGC, EDC, RPN, MRN, or REG. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Generator Operating Mode
|  | CIMProduction | GeneratingUnit | GeneratingUnit | GovernorMPL | governorMPL | PU | 1 | cim | Governor motor position limit. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Governor MPL
|  | CIMProduction | GeneratingUnit | GeneratingUnit | GovernorSCD | governorSCD | PerCent | 5 | cim | Governor Speed Changer Droop. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Governor Speed Changer Droop
|  | CIMProduction | GeneratingUnit | GeneratingUnit | highControlLimit | highControlLimit | ActivePower |  | cim | High limit for secondary (AGC) control. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | High Control Limit
|  | CIMProduction | GeneratingUnit | GeneratingUnit | highReasonabilityLimit | highReasonabilityLimit | ActivePower |  | etx | High reasonability limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | High Reasonability Limit
|  | CIMProduction | GeneratingUnit | GeneratingUnit | highRsnbltyRampRateLimit | highReasonabilityRampRateLimit | ActivePower |  | etx | High reasonability ramp rate limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | High Reasonability Ramp Rate Limit
|  | CIMProduction | GeneratingUnit | GeneratingUnit | hotintTime | hotintTime | Float |  | etx | Hot-to-intermediate time (Seasonal). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Hot-to-intermediate time (Seasonal)
|  | CIMProduction | GeneratingUnit | GeneratingUnit | hotStartTime | hotStartTime | Float |  | etx | Hot start time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Hot start time
|  | CIMProduction | GeneratingUnit | GeneratingUnit | initialMW | initialMW | ActivePower |  | cim | Default generation for use when the operating type is fixed. An entry is required because the unit may later be placed in a fixed operating type mode even though that may not be the initial selection. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Initial MW
|  | CIMProduction | GeneratingUnit | GeneratingUnit | intColdTime | intColdTime | Float |  | etx | Intermediate-to-cold time (Seasonal). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Intermediate-to-cold time (Seasonal)
|  | CIMProduction | GeneratingUnit | GeneratingUnit | intStartTime | intStartTime | Float |  | etx | Intermediate start time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Intermediate start time
|  | CIMProduction | GeneratingUnit | GeneratingUnit | longPF | longPF | ParticipationFactor |  | cim | Additional information is not available. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Long PF
|  | CIMProduction | GeneratingUnit | GeneratingUnit | lowControlLimit | lowControlLimit | ActivePower |  | cim | Low limit for secondary (AGC) control. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Low Control Limit
|  | CIMProduction | GeneratingUnit | GeneratingUnit | lowerRampRate | lowerRampRate | PowerROCPerMin |  | cim | Lower Ramp Rate. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Lower Ramp Rate
|  | CIMProduction | GeneratingUnit | GeneratingUnit | lowReasonabilityLimit | lowReasonabilityLimit | ActivePower |  | etx | Low reasonability limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Low Reasonability Limit
|  | CIMProduction | GeneratingUnit | GeneratingUnit | lowRsnbltyRampRateLimit | lowReasonabilityRampRateLimit | ActivePower |  | etx | Low reasonability ramp rate limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Low Reasonability Ramp Rate Limit
|  | CIMProduction | GeneratingUnit | GeneratingUnit | maxCapacityLimit | maxCapacityLimit | Integer |  | etx | MAXIMUM POSSIBLE CAPACITY. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Capacity Limit
|  | CIMProduction | GeneratingUnit | GeneratingUnit | maxDailyStarts | maxDailyStarts | Float |  | etx | Maximum daily starts (seasonal parameter). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum daily starts (seasonal parameter)
|  | CIMProduction | GeneratingUnit | GeneratingUnit | maxDownRampRate | maxDownRampRate | Float |  | etx | DEFAULT MAXIMUM RAMP RATE IN DOWN DIRECTION. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Down Ramp Rate
|  | CIMProduction | GeneratingUnit | GeneratingUnit | maxAllowableSpinngReserve | maximumAllowableSpinngReserve | ActivePower |  | cim | Maximum allowable spinning reserve. Spinning reserve will never be considered greater than this value regardless of the current operating point. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Allowable Spinning Reserve
|  | CIMProduction | GeneratingUnit | GeneratingUnit | maximumCurrentCapacity | maximumCurrentCapacity | Float |  | etx | (MW) DEFAULT CURRENT MAX CAPACITY. OPERATOR ENTERABLE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Current Capacity
|  | CIMProduction | GeneratingUnit | GeneratingUnit | maximumCurrentCapacityRef | maximumCurrentCapacityRef | Float |  | etx | (MW) Reference value for Advisory ECO maximum. Entered in modeling. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Current Capacity Ref
|  | CIMProduction | GeneratingUnit | GeneratingUnit | MaximumEconomicMW | maximumEconomicMW | ActivePower |  | cim | Maximum high economic MW limit, that should not exceed the maximum operating MW limit. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 9999 | 0 | Maximum Economic MW
|  | CIMProduction | GeneratingUnit | GeneratingUnit | maximumEconomicMWRef | maximumEconomicMWRef | Float |  | etx | Maximum economic dispatch reference value. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Economic MW Ref
|  | CIMProduction | GeneratingUnit | GeneratingUnit | MaximumOperatingMW | maximumOperatingMW | ActivePower |  | cim | This is the maximum operating MW limit the dispatcher can enter for this unit. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Operating MW
|  | CIMProduction | GeneratingUnit | GeneratingUnit | maxONTime | maxONTime | Float |  | etx | Maximum On-Line time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum On-Line time
|  | CIMProduction | GeneratingUnit | GeneratingUnit | maxResponseReserveLimit | maxResponseReserveLimit | Float |  | etx | Maximum responsive reserve limit MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Response Reserve Limit
|  | CIMProduction | GeneratingUnit | GeneratingUnit | maxSpinReserveContribution | maxSpinReserveContribution | Float |  | etx | Maximum Spinning Reserve Contribution. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Spin Reserve Contribution
|  | CIMProduction | GeneratingUnit | GeneratingUnit | maxUpRampRate | maxUpRampRate | Float |  | etx | DEFAULT MAXIMUM RAMP RATE IN UP DIRECTION. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Up Ramp Rate
|  | CIMProduction | GeneratingUnit | GeneratingUnit | maxWeeklyEnergy | maxWeeklyEnergy | Float |  | etx | Maximum weekly energy (seasonal parameter). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum weekly energy (seasonal parameter)
|  | CIMProduction | GeneratingUnit | GeneratingUnit | maxWeeklyStarts | maxWeeklyStarts | Float |  | etx | Maximum weekly starts (seasonal parameter). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum weekly starts (seasonal parameter)
|  | CIMProduction | GeneratingUnit | GeneratingUnit | minCapacityLimit | minCapacityLimit | Integer |  | etx | THE LOWEST CONTINUOUS ECONOMICAL CAPACITY LIMIT. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Capacity Limit
|  | CIMProduction | GeneratingUnit | GeneratingUnit | MinimumEconomicMW | minimumEconomicMW | ActivePower | 0 | cim | Low economic MW limit that must be greater than or equal to the minimum operating MW limit. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 999 | 0 | Minimum Economic MW
|  | CIMProduction | GeneratingUnit | GeneratingUnit | minimumOffTime | minimumOffTime | Seconds |  | cim | Minimum time interval between unit shutdown and startup. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Off Time
|  | CIMProduction | GeneratingUnit | GeneratingUnit | MinimumOperatingMW | minimumOperatingMW | ActivePower | 0 | cim | This is the minimum operating MW limit the dispatcher can enter for this unit. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Operating MW
|  | CIMProduction | GeneratingUnit | GeneratingUnit | minOFFTime | minOFFTime | Float |  | etx | Minimum Off-Line time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Off-Line time
|  | CIMProduction | GeneratingUnit | GeneratingUnit | minONTime | minONTime | Float |  | etx | Minimum On-Line time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum On-Line time
|  | CIMProduction | GeneratingUnit | GeneratingUnit | minResponseReserveLimit | minResponseReserveLimit | Float |  | etx | Minimum responsive reserve limit MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Response Reserve Limit
|  | CIMProduction | GeneratingUnit | GeneratingUnit | modelDetail | modelDetail | Classification | 3 | cim | Detail level of the generator model data. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Model Detail
|  | CIMProduction | GeneratingUnit | GeneratingUnit | normalPF | normalPF | ParticipationFactor | 1 | cim | Economic participation factor based on the slope of the unit incremental cost curve at the current operating point of the unit. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Normal PF
|  | CIMProduction | GeneratingUnit | GeneratingUnit | onlineThresholdDeadbandPct | onlineThresholdDeadbandPercent | Float |  | etx | Unit online threshold deadband percentage. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Online Threshold Deadband Percent
|  | CIMProduction | GeneratingUnit | GeneratingUnit | PenaltyFactor | penaltyFactor | PenaltyFactor | 1 | cim | The unit's penalty factor as calculated by the Network Sensitivity function. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Penalty Factor
|  | CIMProduction | GeneratingUnit | GeneratingUnit | PrimaryFuelType | PrimaryFuelType | EnumERCOTFuelType |  | etx | Primary fuel type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Primary Fuel Type
|  | CIMProduction | GeneratingUnit | GeneratingUnit | qualificationStatus | qualificationStatus | Boolean | FALSE | etx | Qualification status. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Qualification Status
|  | CIMProduction | GeneratingUnit | GeneratingUnit | raiseRampRate | raiseRampRate | PowerROCPerMin |  | cim | Raise Ramp Rate | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Raise Ramp Rate
|  | CIMProduction | GeneratingUnit | GeneratingUnit | ratedGrossMaxMW | ratedGrossMaxMW | ActivePower |  | cim | The unit's gross rated maximum capacity (Book Value). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Rated Gross Max MW
|  | CIMProduction | GeneratingUnit | GeneratingUnit | ratedGrossMinMW | ratedGrossMinMW | ActivePower |  | cim | The gross rated minimum generation level which the unit can safely operate at while delivering power to the transmission grid. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Rated Gross Min MW
|  | CIMProduction | GeneratingUnit | GeneratingUnit | ratedNetMaxMW | ratedNetMaxMW | ActivePower |  | cim | The net rated maximum capacity determined by subtracting the auxiliary power used to operate the internal plant machinery from the rated gross maximum capacity. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Rated Net Max MW
|  | CIMProduction | GeneratingUnit | GeneratingUnit | reliabilityMustRun | reliabilityMustRun | Boolean | FALSE | etx | TRUE - Unit is qualified to reliability must run. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reliability Must Run
|  | CIMProduction | GeneratingUnit | GeneratingUnit | reserveDiscountFactor | reserveDiscountFactor | Float |  | etx | Reserve Discount Factor. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reserve Discount Factor
|  | CIMProduction | GeneratingUnit | GeneratingUnit | resourceCategory | resourceCategory | String50 |  | etx | Type of resource. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Type of Resource
|  | CIMProduction | GeneratingUnit | GeneratingUnit | seasonalMaxSustainableRating | seasonalMaxSustainableRating | ActivePower |  | etx | Seasonal maximum sustainable rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Max Sustainable Rating
|  | CIMProduction | GeneratingUnit | GeneratingUnit | seasonalMinEmergencyRating | seasonalMinEmergencyRating | ActivePower |  | etx | Seasonal minimum emergency rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Min Emergency Rating
|  | CIMProduction | GeneratingUnit | GeneratingUnit | seasonalMinSustainableRating | seasonalMinSustainableRating | ActivePower |  | etx | Seasonal minimum sustainable rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Min Sustainable Rating
|  | CIMProduction | GeneratingUnit | GeneratingUnit | SecondaryFuelType | SecondaryFuelType | EnumERCOTFuelType |  | etx | Secondary fuel type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Secondary Fuel Type
|  | CIMProduction | GeneratingUnit | GeneratingUnit | shortPF | shortPF | ParticipationFactor |  | cim | Short Participation Factor | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Short PF
|  | CIMProduction | GeneratingUnit | GeneratingUnit | spinningReserveMax | spinningReserveMax | Float |  | etx | Max spinning reserve from this unit. Usuallly derived from response rate. Applicable only to non-peakers. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Spinning Reserve Max
|  | CIMProduction | GeneratingUnit | GeneratingUnit | spinReserveRamp | spinReserveRamp | PowerROCPerMin |  | cim | Spin Reserve Ramp | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Spin Reserve Ramp
|  | CIMProduction | GeneratingUnit | GeneratingUnit | startupTime | startupTime | Seconds |  | cim | Time it takes to get the unit on-line, from the time that the prime mover mechanical power is applied. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Startup Time
|  | CIMProduction | GeneratingUnit | GeneratingUnit | StepChange | stepChange | ActivePower | 5 | cim | Unit allowable step change which specifies the maximum stored energy in the boiler. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Step Change
|  | CIMProduction | GeneratingUnit | GeneratingUnit | synCondenserCapable | synCondenserCapable | Boolean | FALSE | etx | Flag indicating whether the Resource is Synchronous Condenser capable. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Synchronous Condeser Capable?
|  | CIMProduction | GeneratingUnit | GeneratingUnit | tieLinePF | tieLinePF | ParticipationFactor | 1 | cim | Unit frequency and tie-line regulation participation factor. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tie Line PF
|  | CIMProduction | GeneratingUnit | GeneratingUnit | wfrmcr | wfrmcr | Boolean | FALSE | etx | wfrmcr. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | wfrmcr
|  | CIMProduction | GenUnitOpCostCurve | GenUnitOpCostCurve | netGrossMWFlag | netGrossMWFlag | Boolean | FALSE | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net Gross MW Flag
|  | CIMProduction | HeatInputCurve | HeatInputCurve | auxPowerMult | auxPowerMult | PU |  | cim | Power output - auxiliary power multiplier adjustment factor in per unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Aux Power Mult
|  | CIMProduction | HeatInputCurve | HeatInputCurve | auxPowerOffset | auxPowerOffset | ActivePower |  | cim | Power output - auxiliary power offset adjustment factor in MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Aux Power Offset
|  | CIMProduction | HeatInputCurve | HeatInputCurve | heatInputEff | heatInputEff | PU |  | cim | Heat input - efficiency multiplier adjustment factor in per unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Heat Input Efficiency
|  | CIMProduction | HeatInputCurve | HeatInputCurve | heatInputOffset | heatInputOffset | HeatPerHour |  | cim | Heat input - offset adjustment factor in MBtu/hr. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Heat Input Offset
|  | CIMProduction | HeatInputCurve | HeatInputCurve | netGrossMWFlag | netGrossMWFlag | Boolean | FALSE | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net Gross MW Flag
|  | CIMProduction | HeatRateCurve | HeatRateCurve | baseHeat | baseHeat | Float |  | etx | (MBTU/HR) The amount of heat required at first MW point to maintain synchronization. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Base Heat
|  | CIMProduction | HeatRateCurve | HeatRateCurve | netGrossMWFlag | netGrossMWFlag | Boolean | FALSE | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net Gross MW Flag
|  | CIMProduction | HydroGeneratingUnit | HydroGeneratingUnit | HydroUnitWaterCost | hydroUnitWaterCost | Float |  | cim | The equivalent cost of water that drives the hydro turbine, expressed as (dollars/cubic meter). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Hydro Unit Water Cost
|  | CIMProduction | HydroPowerPlant | HydroPowerPlant | dischargeTravelDelay | dischargeTravelDelay | Seconds |  | cim | Water travel delay from tailbay to next downstream hydro power station. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Discharge Travel Delay
|  | CIMProduction | HydroPowerPlant | HydroPowerPlant | hydroPlantType | hydroPlantType | EnumHydroPlantType |  | cim | The type of hydro power plant, e.g.: Run-of-River, Pumped Storage, Major Storage, Minor Storage. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Hydro Plant Type
|  | CIMProduction | HydroPowerPlant | HydroPowerPlant | penstockType | penstockType | EnumPenstockType |  | cim | Type and configuration of hydro plant penstock(s). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Penstock Type
|  | CIMProduction | HydroPowerPlant | HydroPowerPlant | plantDischargeCapacity | plantDischargeCapacity | Float |  | cim | Total plant discharge capacity in cubic meters per second. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Plant Discharge Capacity
|  | CIMProduction | HydroPowerPlant | HydroPowerPlant | plantMWGenRating | plantMWGenRating | ActivePower |  | cim | The hydro plant's generating rating in MW for rated head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Plant MW Gen Rating
|  | CIMProduction | HydroPowerPlant | HydroPowerPlant | plantMWPumpRating | plantMWPumpRating | ActivePower |  | cim | The hydro plant's pumping rating in MW for rated head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Plant MW Pump Rating
|  | CIMProduction | HydroPowerPlant | HydroPowerPlant | plantRatedHead | plantRatedHead | Float |  | cim | The plant's rated gross head in meters. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Plant Rated Head
|  | CIMProduction | HydroPowerPlant | HydroPowerPlant | surgeTankCode | surgeTankCode | EnumSurgeTankCode |  | cim | A code describing the type (or absence) of surge tank that is associated with the hydro power plant. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Surge Tank Code
|  | CIMProduction | HydroPowerPlant | HydroPowerPlant | surgeTankCrestLevel | surgeTankCrestLevel | WaterLevel |  | cim | The level at which the surge tank spills. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Surge Tank Crest Level
|  | CIMProduction | HydroPump | HydroPump | pumpDischAtMaxHead | pumpDischAtMaxHead | Float |  | cim | The pumping discharge (m3/sec) under maximum head conditions, usually at full gate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pump Discharge at Max Head
|  | CIMProduction | HydroPump | HydroPump | pumpDischAtMinHead | pumpDischAtMinHead | Float |  | cim | The pumping discharge (m3/sec) under minimum head conditions, usually at full gate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pump Discharge at Min Head
|  | CIMProduction | HydroPump | HydroPump | pumpPowerAtMaxHead | pumpPowerAtMaxHead | ActivePower |  | cim | The pumping power (MW) under maximum head conditions, usually at full gate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pump Power at Max Head
|  | CIMProduction | HydroPump | HydroPump | pumpPowerAtMinHead | pumpPowerAtMinHead | ActivePower |  | cim | The pumping power (MW) under minimum head conditions, usually at full gate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pump Power at Min Head
|  | CIMProduction | IncrementalHeatRateCurve | IncrementalHeatRateCurve | netGrossMWFlag | netGrossMWFlag | Boolean | FALSE | cim | Flag is set to YES when output is expressed in net MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net Gross MW Flag
|  | CIMProduction | Reservoir | Reservoir | activeStorageCapacity | activeStorageCapacity | Volume |  | cim | Storage volume (in Mm3) between the full supply level and the normal minimum operating level. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Active Storage Volume
|  | CIMProduction | Reservoir | Reservoir | energyStorageRating | energyStorageRating | Float |  | cim | The reservoir's energy storage rating in MWh for given head conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Energy Storage Rating
|  | CIMProduction | Reservoir | Reservoir | fullSupplyLevel | fullSupplyLevel | WaterLevel |  | cim | Full supply level, above which water will spill. This can be the spillway crest level or the top of closed gates. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Full Supply Level
|  | CIMProduction | Reservoir | Reservoir | grossCapacity | grossCapacity | Volume |  | cim | Total capacity of reservoir. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gross Capacity
|  | CIMProduction | Reservoir | Reservoir | normalMinOperateLevel | normalMinOperateLevel | WaterLevel |  | cim | Normal minimum operating level below which the penstocks will draw air. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Normal Min Operate Level
|  | CIMProduction | Reservoir | Reservoir | riverOutletWorks | riverOutletWorks | String100 |  | cim | River outlet works for riparian right releases or other purposes. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | River Outlet Works
|  | CIMProduction | Reservoir | Reservoir | spillTravelDelay | spillTravelDelay | Seconds |  | cim | The spillway water travel delay to the next downstream reservoir. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Spill Travel Delay
|  | CIMProduction | Reservoir | Reservoir | spillwayCapacity | spillwayCapacity | Float |  | cim | The flow capacity of the spillway in cubic meters per second. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Spillway Capacity
|  | CIMProduction | Reservoir | Reservoir | spillwayCrestLength | spillwayCrestLength | Float |  | cim | The length of the spillway crest in meters. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Spillway Crest Length
|  | CIMProduction | Reservoir | Reservoir | spillwayCrestLevel | spillwayCrestLevel | WaterLevel |  | cim | Spillway crest level above which water will spill. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Spillway Crest Level
|  | CIMProduction | Reservoir | Reservoir | spillWayGateType | spillWayGateType | EnumSpillwayGateType |  | cim | Type of spillway gate, including parameters. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Spillway Gate Type
|  | CIMProduction | ShutdownCurve | ShutdownCurve | shutdownCost | shutdownCost | Money |  | cim | Fixed shutdown cost. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Shutdown Cost
|  | CIMProduction | ShutdownCurve | ShutdownCurve | shutdownDate | shutdownDate | AbsoluteDateTime |  | cim | The date and time of the most recent generating unit shutdown. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Shutdown Date
|  | CIMProduction | StartIgnFuelCurve | StartIgnFuelCurve | ignitionFuelType | ignitionFuelType | EnumFuelType |  | cim | Type of ignition fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Ignition Fuel Type
|  | CIMProduction | StartMainFuelCurve | StartMainFuelCurve | mainFuelType | mainFuelType | EnumFuelType |  | cim | Type of main fuel. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Main Fuel Type
|  | CIMProduction | StartRampCurve | StartRampCurve | hotStandbyRamp | hotStandbyRamp | PowerROCPerMin |  | cim | The startup ramp rate in gross MW/minute for a unit that is on hot standby. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Hot Standby Ramp
|  | CIMProduction | StartupModel | StartupModel | fixedMaintCost | fixedMaintCost | CostPerHour |  | cim | Fixed Maintenance Cost. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Fixed Maintenance Cost
|  | CIMProduction | StartupModel | StartupModel | hotStandbyHeat | hotStandbyHeat | HeatPerHour |  | cim | The amount of heat input per hour required for hot standby operation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Hot Standby Heat
|  | CIMProduction | StartupModel | StartupModel | incrementalMaintCost | incrementalMaintCost | CostPerEnergyUnit |  | cim | Incremental Maintenance Cost | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Incremental Maintenance Cost
|  | CIMProduction | StartupModel | StartupModel | minimumDownTime | minimumDownTime | Hours |  | cim | The minimum number of hours the unit must be down before restart. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Down Time
|  | CIMProduction | StartupModel | StartupModel | minimumRunTime | minimumRunTime | Hours |  | cim | The minimum number of hours the unit must be operating before being allowed to shut down. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Run Time
|  | CIMProduction | StartupModel | StartupModel | riskFactorCost | riskFactorCost | Money |  | cim | The opportunity cost associated with the return in dollars. This represents the restart's 'share' of the unit depreciation and risk of an event which would damage the unit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Risk Factor Cost
|  | CIMProduction | StartupModel | StartupModel | startupCost | startupCost | Money |  | cim | Total miscellaneous start up costs. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Startup Cost
|  | CIMProduction | StartupModel | StartupModel | startupDate | startupDate | AbsoluteDateTime |  | cim | The date and time of the most recent generating unit startup. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Startup Date
|  | CIMProduction | StartupModel | StartupModel | startupPriority | startupPriority | Priority |  | cim | Startup priority within control area where lower numbers indicate higher priorities. More than one unit in an area may be assigned the same priority. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Startup Priority
|  | CIMProduction | StartupModel | StartupModel | stbyAuxPowerMW | stbyAuxPowerMW | ActivePower |  | cim | The unit's auxiliary power consumption to maintain standby mode. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Standby Aux Power MW
|  | CIMProduction | TargetLevelSchedule | TargetLevelSchedule | highLevelLimit | highLevelLimit | WaterLevel |  | cim | High target level limit, above which the reservoir operation will be penalized. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | High Level Limit
|  | CIMProduction | TargetLevelSchedule | TargetLevelSchedule | lowLevelLimit | lowLevelLimit | WaterLevel |  | cim | Low target level limit, below which the reservoir operation will be penalized. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Low Level Limit
|  | CIMProduction | ThermalGeneratingUnit | ThermalGeneratingUnit | boilerColdStartEnergy | boilerColdStartEnergy | Float |  | etx | Boiler cold start engergy (MBTU). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Boiler Cold Start Energy
|  | CIMProduction | ThermalGeneratingUnit | ThermalGeneratingUnit | boilerEfficiency | boilerEfficiency | Float |  | etx | (%) BOILER EFFICIENCY FACTOR. THE HEAT RATE CURVE WILL BE DIVIDED BY THIS FACTOR TO ACCOUNT FOR A DIRTY BOILER OR ANY OTHER CAUSE FOR LOSS OF EFFICIENCY OF THE HEAT CYCLE. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Boiler Efficiency
|  | CIMProduction | ThermalGeneratingUnit | ThermalGeneratingUnit | oMCost | oMCost | CostPerHeatUnit |  | cim | Operating and maintenance cost for the thermal unit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Operating-Maintenance Cost
|  | CIMProduction | ThermalGeneratingUnit | ThermalGeneratingUnit | turbineColdStartEnergy | turbineColdStartEnergy | Float |  | etx | Turbine cold start energy MBTU (used by UC only). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Turbine Cold Start Energy
|  | CIMProtection | CurrentRelay | CurrentRelay | currentLimit1 | currentLimit1 | CurrentFlow |  | cim | Current limit #1 for inverse time pickup. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Current Limit1
|  | CIMProtection | CurrentRelay | CurrentRelay | currentLimit2 | currentLimit2 | CurrentFlow |  | cim | Current limit #2 for inverse time pickup. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Current Limit2
|  | CIMProtection | CurrentRelay | CurrentRelay | currentLimit3 | currentLimit3 | CurrentFlow |  | cim | Current limit #3 for inverse time pickup. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Current Limit3
|  | CIMProtection | CurrentRelay | CurrentRelay | instantTrip | instantTrip | CurrentFlow |  | etx | Instant trip current. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Instant Trip
|  | CIMProtection | CurrentRelay | CurrentRelay | inverseTimeFlag | inverseTimeFlag | Boolean | FALSE | cim | True/False flag that indicates whether or not the current relay has inverse time characteristic. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Inverse Time Flag
|  | CIMProtection | CurrentRelay | CurrentRelay | isDirectional | isDirectional | Boolean |  | etx | Is directional? | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Is Directional
|  | CIMProtection | CurrentRelay | CurrentRelay | isMvaSetting | isMvaSetting | Boolean |  | etx | Is MVA Setting? | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Is MVA Setting
|  | CIMProtection | CurrentRelay | CurrentRelay | lockoutTime | lockoutTime | Seconds |  | etx | Relay lockout time delay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Lockout Time
|  | CIMProtection | CurrentRelay | CurrentRelay | mvaLimit1 | mvaLimit1 | ApparentPower |  | etx | MVA limit 1. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | mvaLimit1
|  | CIMProtection | CurrentRelay | CurrentRelay | nominalMva | nominalMva | ApparentPower |  | etx | Nominal MVA. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | nominalMva
|  | CIMProtection | CurrentRelay | CurrentRelay | pickup | pickup | CurrentFlow |  | etx | Pickup time. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pickup Time
|  | CIMProtection | CurrentRelay | CurrentRelay | pickupMva | pickupMva | ApparentPower |  | etx | Pickup MVA. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | pickupMva
|  | CIMProtection | CurrentRelay | CurrentRelay | resetTime | resetTime | Seconds |  | etx | Relay (disk) reset time delay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reset Time
|  | CIMProtection | CurrentRelay | CurrentRelay | timeDelay1 | timeDelay1 | Seconds |  | cim | Inverse time delay #1 for current limit #1. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time Delay1
|  | CIMProtection | CurrentRelay | CurrentRelay | timeDelay2 | timeDelay2 | Seconds |  | cim | Inverse time delay #2 for current limit #2. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time Delay2
|  | CIMProtection | CurrentRelay | CurrentRelay | timeDelay3 | timeDelay3 | Seconds |  | cim | Inverse time delay #3 for current limit #3. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time Delay3
|  | CIMProtection | ProtectedSwitch | ProtectedSwitch | protectLockoutAfterAction | protectLockoutAfterAction | Boolean |  | etx | Protect lockout after action. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | protectLockoutAfterAction
DD-1.21.1-001 OTS | DELETE | CIMProtection | ProtectedSwitch | ProtectedSwitch | protectLockoutAfterAction | protectLockoutAfterAction | Boolean |  | etx | Protect lockout after action. | [10 empty] | protectLockoutAfterAction
|  | CIMProtection | ProtectedSwitch | ProtectedSwitch | protectOverAction | protectOverAction | EnumSwitchState |  | etx | Protect over action. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | protectOverAction
DD-1.21.1-001 OTS | DELETE | CIMProtection | ProtectedSwitch | ProtectedSwitch | protectOverAction | protectOverAction | EnumSwitchState |  | etx | Protect over action. | [10 empty] | protectOverAction
|  | CIMProtection | ProtectedSwitch | ProtectedSwitch | protectUnderAction | protectUnderAction | EnumSwitchState |  | etx | Protect under action. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Protect Under Action
DD-1.21.1-001 OTS | DELETE | CIMProtection | ProtectedSwitch | ProtectedSwitch | protectUnderAction | protectUnderAction | EnumSwitchState |  | etx | Protect under action. | [10 empty] | Protect Under Action
|  | CIMProtection | ProtectedSwitch | ProtectedSwitch | switchOperationOver | switchOperationOver | Boolean | FALSE | etx | Over Limit Violation Switch Operation (Open/Close). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch Operation Over
DD-1.21.1-001 OTS | DELETE | CIMProtection | ProtectedSwitch | ProtectedSwitch | switchOperationOver | switchOperationOver | Boolean | FALSE | etx | Over Limit Violation Switch Operation (Open/Close). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch Operation Over
|  | CIMProtection | ProtectedSwitch | ProtectedSwitch | switchOperationUnder | switchOperationUnder | Boolean | FALSE | etx | Under Limit Violation Switch Operation (Open/Close). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch Operation Under
DD-1.21.1-001 OTS | DELETE | CIMProtection | ProtectedSwitch | ProtectedSwitch | switchOperationUnder | switchOperationUnder | Boolean | FALSE | etx | Under Limit Violation Switch Operation (Open/Close). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch Operation Under
|  | CIMProtection | ProtectedSwitch | ProtectedSwitch | tripLockout | tripLockout | Boolean | FALSE | etx | Lockout after trip. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Trip Lockout
DD-1.21.1-001 OTS | DELETE | CIMProtection | ProtectedSwitch | ProtectedSwitch | tripLockout | tripLockout | Boolean | FALSE | etx | Lockout after trip. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Trip Lockout
|  | CIMProtection | ProtectionEquipment | ProtectionEquipment | highLimit | highLimit | Float |  | cim | The maximum allowable value. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | High Limit
|  | CIMProtection | ProtectionEquipment | ProtectionEquipment | lockoutTimeHigh | lockoutTimeHigh | Seconds |  | etx | Lockout time high (in seconds). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | lockoutTimeHigh
|  | CIMProtection | ProtectionEquipment | ProtectionEquipment | lockoutTimeLow | lockoutTimeLow | Seconds |  | etx | Lockout time low (in seconds). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | lockoutTimeLow
|  | CIMProtection | ProtectionEquipment | ProtectionEquipment | lowLimit | lowLimit | Float |  | cim | The minimum allowable value. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Low Limit
|  | CIMProtection | ProtectionEquipment | ProtectionEquipment | powerDirectionFlag | powerDirectionFlag | Boolean | FALSE | cim | Direction same as positive active power flow value. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Power Direction Flag
|  | CIMProtection | ProtectionEquipment | ProtectionEquipment | relayDelayTime | relayDelayTime | Seconds | 0 | cim | The time delay in seconds from detection of abnormal conditions to relay operation | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Relay Delay Time
|  | CIMProtection | ProtectionEquipment | ProtectionEquipment | relayDelayTimeHigh | relayDelayTimeHigh | Seconds |  | etx | Relay delay time high (in seconds). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | relayDelayTimeHigh
|  | CIMProtection | ProtectionEquipment | ProtectionEquipment | relayDelayTimeLow | relayDelayTimeLow | Seconds |  | etx | Relay delay time low (in seconds). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | relayDelayTimeLow
|  | CIMProtection | RecloseSequence | RecloseSequence | recloseDelay | recloseDelay | Seconds |  | cim | Indicates the time lapse before the reclose step will execute a reclose. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reclose Delay
|  | CIMProtection | RecloseSequence | RecloseSequence | recloseStep | recloseStep | Integer |  | cim | Indicates the ordinal position of the reclose step relative to other steps in the sequence. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reclose Step
|  | CIMProtection | SynchrocheckRelay | SynchrocheckRelay | maxAngleDiff | maxAngleDiff | AngleRadians |  | cim | The maximum allowable voltage vector phase angle difference across the open device. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Angle Diff
|  | CIMProtection | SynchrocheckRelay | SynchrocheckRelay | maxAngleDiffDelay | maxAngleDiffDelay | Seconds |  | etx | Trip delay at maximum angle difference. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Angle Difference Delay
|  | CIMProtection | SynchrocheckRelay | SynchrocheckRelay | maxFreqDiff | maxFreqDiff | Frequency |  | cim | The maximum allowable frequency difference across the open device. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Freq Diff
|  | CIMProtection | SynchrocheckRelay | SynchrocheckRelay | maxFreqDiffDelay | maxFreqDiffDelay | Seconds |  | etx | Trip delay at maximum frequency difference. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Frequency Difference Delay
|  | CIMProtection | SynchrocheckRelay | SynchrocheckRelay | maxVoltDiff | maxVoltDiff | Voltage |  | cim | The maximum allowable difference voltage across the open device. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Volt Diff
|  | CIMProtection | SynchrocheckRelay | SynchrocheckRelay | minAngleDiffDelay | minAngleDiffDelay | Seconds |  | etx | Trip delay at minimum angle difference. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Angle Difference Delay
|  | CIMProtection | SynchrocheckRelay | SynchrocheckRelay | minFreqDiffDelay | minFreqDiffDelay | Seconds |  | etx | Trip delay at minimum frequency difference. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Frequency Difference Delay
|  | CIMSCADA | RemoteControl | RemoteControl | actuatorMaximum | actuatorMaximum | Float |  | cim | Actuator Maximum | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Actuator Maximum
|  | CIMSCADA | RemoteControl | RemoteControl | actuatorMinimum | actuatorMinimum | Float |  | cim | Actuator Minimum | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Actuator Minimum
|  | CIMSCADA | RemoteControl | RemoteControl | remoteControlled | remoteControlled | Boolean | FALSE | cim | Remote Controlled | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Remote Controlled
|  | CIMSCADA | RemoteSource | RemoteSource | deadband | deadband | Float |  | cim | The smallest change in value to be reported. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband
|  | CIMSCADA | RemoteSource | RemoteSource | scanInterval | scanInterval | Seconds |  | cim | The time interval between scans. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | scanInterval
|  | CIMSCADA | RemoteSource | RemoteSource | sensorMaximum | sensorMaximum | Float |  | cim | The maximum value the telemetry item can return. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Sensor Maximum
|  | CIMSCADA | RemoteSource | RemoteSource | sensorMinimum | sensorMinimum | Float |  | cim | The minimum value the telemetry item can return. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Sensor Minimum
|  | CIMSCADA | RemoteUnit | RemoteUnit | remoteUnitType | remoteUnitType | EnumRemoteUnitType |  | cim | A remote unit can be a RTU, IED, substation control system, control center etc. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Remote Unit Type
|  | CIMTopology | ConnectivityNode | ConnectivityNode | height | height | Integer | 0 | spc | height | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | height
|  | CIMTopology | ConnectivityNode | ConnectivityNode | PSSEBusName | PSSEBusName | String12 |  | etx | Store the PSS™E bus name that will be associated with the most favored Connectivity Node in Connectivity Node to Bus Processing Option 1. | FALSE | FALSE | TRUE | FALSE |  | TRUE |  | FALSE |  |  | PSS/E Bus Name
|  | CIMTopology | ConnectivityNode | ConnectivityNode | PSSEBusNumber | PSSEBusNumber | Integer |  | etx | The PSS/E bus number associated with this point in the network. This attribute should only be used to model ficticious PSS/E busbars that are not associated with physical busbar sections. | FALSE | FALSE | TRUE | FALSE |  | TRUE |  | FALSE | 99997 | 1 | PSS/E Bus Number
|  | CIMTopology | ConnectivityNode | ConnectivityNode | SlackBusPriority | SlackBusPriority | Integer |  | etx | Swing Bus Definition. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Slack Bus Priority
|  | CIMTopology | ConnectivityNode | ConnectivityNode | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
|  | CIMTopology | ConnectivityNode | ConnectivityNode | width | width | Integer | 0 | spc | width | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | width
|  | CIMTopology | ConnectivityNode | ConnectivityNode | xval | xval | Integer | 0 | spc | x co-ordinate | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | x co-ordinate
|  | CIMTopology | ConnectivityNode | ConnectivityNode | yval | yval | Integer | 0 | spc | y co-ordinate | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | y co-ordinate
|  | CIMTopology | TopologicalNode | TopologicalNode | energized | energized | Boolean | FALSE | cim | True if node energized. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Energized
|  | CIMTopology | TopologicalNode | TopologicalNode | loadCarrying | loadCarrying | Boolean | FALSE | cim | True if node is load carrying. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Carrying
|  | CIMTopology | TopologicalNode | TopologicalNode | netInjectionMVar | netInjectionMVar | ReactivePower |  | cim | Net injection MVAr | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net injection MVAr
|  | CIMTopology | TopologicalNode | TopologicalNode | netInjectionMW | netInjectionMW | ActivePower |  | cim | Net injection MW | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Net Injection MW
|  | CIMTopology | TopologicalNode | TopologicalNode | observabilityFlag | observabilityFlag | Boolean | FALSE | cim | The observability status of the node. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Observability Flag
|  | CIMTopology | TopologicalNode | TopologicalNode | phaseAngle | phaseAngle | AngleRadians |  | cim | Phase angle of node. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phase Angle
|  | CIMTopology | TopologicalNode | TopologicalNode | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number Alternate Areas and Zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
|  | CIMTopology | TopologicalNode | TopologicalNode | voltage | voltage | Voltage |  | cim | Voltage of node. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Voltage
|  | CIMWires | ACLineSegment | ACLineSegment | emergencyMaxShadowPrice | emergencyMaxShadowPrice | DoubleFloat | 99999 | etx | States the Emergency Max Shadow price for a ACLineSegment. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emergency Max Shadow Price
|  | CIMWires | ACLineSegment | ACLineSegment | fifteenMinuteMaxShadowPrice | fifteenMinuteMaxShadowPrice | DoubleFloat | 99999 | etx | States the 15 minute rating Max Shadow price for a ACLineSegment. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | 15 minute rating Max Shadow Price
|  | CIMWires | ACLineSegment | ACLineSegment | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a ACLineSegment. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
|  | CIMWires | Breaker | Breaker | ampRating | ampRating | CurrentFlow |  | cim | Fault interrupting rating in amperes. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Current Flow
|  | CIMWires | Breaker | Breaker | InTransitTime | InTransitTime | Seconds | 0 | cim | The transition time from open to close, in seconds. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | In Transit Time
|  | CIMWires | CompositeSwitch | CompositeSwitch | compositeSwitchType | compositeSwitchType | CompositeSwitchType |  | cim | An alphanumeric code that can be used as a reference to extar information such as the description of the interlocking scheme if any. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Composite Switch Type
|  | CIMWires | Conductor | Conductor | b0ch | b0ch | Susceptance |  | cim | Zero sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 5 | 0 | b0ch
|  | CIMWires | Conductor | Conductor | bch | bch | Susceptance |  | cim | Positive sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 50 | 0 | bch
|  | CIMWires | Conductor | Conductor | g0ch | g0ch | Conductance |  | cim | Zero sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | g0ch
|  | CIMWires | Conductor | Conductor | gch | gch | Conductance |  | cim | Positive sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | gch
|  | CIMWires | Conductor | Conductor | length | length | LongLength |  | cim | Segment length for calculating line section capabilities (long length units). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Length
|  | CIMWires | Conductor | Conductor | r | r | Resistance |  | cim | Positive sequence series resistance of the entire line section. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 500 | -500 | r
|  | CIMWires | Conductor | Conductor | r0 | r0 | Resistance |  | cim | Zero sequence series resistance of the entire line section. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 500 | -500 | r0
|  | CIMWires | Conductor | Conductor | x | x | Reactance |  | cim | Positive sequence series reactance of the entire line section. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 1000 | -1000 | x
|  | CIMWires | Conductor | Conductor | x0 | x0 | Reactance |  | cim | Zero sequence series reactance of the entire line section. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 1000 | -1000 | x0
|  | CIMWires | ConductorType | ConductorType | sheathReactance | sheathReactance | Reactance |  | cim | Reactance of the sheath for cable conductors. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Sheath Reactance
|  | CIMWires | ConductorType | ConductorType | sheathResistance | sheathResistance | Resistance |  | cim | Resistance of the sheath for cable conductors. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Sheath Resistance
|  | CIMWires | DCLineSegment | DCLineSegment | dcSegmentInductance | dcSegmentInductance | Inductance |  | cim | Inductance of the DC line segment, in millihenries. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | DC Segment Inductance
|  | CIMWires | DCLineSegment | DCLineSegment | dcSegmentResistance | dcSegmentResistance | Resistance |  | cim | Resistance of the DC line segment, in ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | DC Segment Resistance
|  | CIMWires | EnergyConsumer | EnergyConsumer | conformingLoadFlag | conformingLoadFlag | Boolean | TRUE | cim | Flag is set to YES if the load is conforming, i.e., tracks the area load to which the energy consumer belongs. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Conforming Load Flag
|  | CIMWires | EnergyConsumer | EnergyConsumer | customerCount | customerCount | Counter |  | cim | Number of individual customers represented by this Demand. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Customer Count
|  | CIMWires | EnergyConsumer | EnergyConsumer | maxMVAR | maxMVAR | Float |  | etx | Maximum Reactive POWER LOAD. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MVAR
|  | CIMWires | EnergyConsumer | EnergyConsumer | maxMW | maxMW | Float |  | etx | Maximum REAL POWER LOAD. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MW
|  | CIMWires | EnergyConsumer | EnergyConsumer | minMVAR | minMVAR | Float |  | etx | MINIMUM Reative POWER LOAD. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum MVAR
|  | CIMWires | EnergyConsumer | EnergyConsumer | minMW | minMW | Float |  | etx | MINIMUM REAL POWER LOAD. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum MW
|  | CIMWires | EnergyConsumer | EnergyConsumer | pFexp | pFexp | Exponent |  | cim | Exponent of per unit frequency effecting real power. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Real Power Frequency Exponent
|  | CIMWires | EnergyConsumer | EnergyConsumer | pfixed | pfixed | ActivePower |  | cim | Real component of the load that is a fixed quantity, MW. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Fixed Real Power
|  | CIMWires | EnergyConsumer | EnergyConsumer | pfixedPct | pfixedPct | PerCent |  | cim | Fixed MW as per cent of load area fixed MW. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Fixed Real Power Percent
|  | CIMWires | EnergyConsumer | EnergyConsumer | pnom | pnom | ActivePower |  | cim | Nominal value for real power, MW. Nominal real power is adjusted according to the load profile selected for the consumer. It equates to one per unit in the load profile. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Nominal Real Power
|  | CIMWires | EnergyConsumer | EnergyConsumer | pnomPct | pnomPct | PerCent |  | cim | Nominal MW as per cent of load group nominal MW. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Nominal Real Power Percent
|  | CIMWires | EnergyConsumer | EnergyConsumer | powerFactor | powerFactor | PowerFactor |  | cim | Power factor for nominal portion of load. Defined as MW/MVA. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Power Factor
|  | CIMWires | EnergyConsumer | EnergyConsumer | pVexp | pVexp | Exponent |  | cim | Exponent of per unit voltage effecting real power. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Real Power Voltage Exponent
|  | CIMWires | EnergyConsumer | EnergyConsumer | qFexp | qFexp | Exponent |  | cim | Exponent of per unit frequency effecting reactive power | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reactive Power Frequency Exponent
|  | CIMWires | EnergyConsumer | EnergyConsumer | qfixed | qfixed | ReactivePower |  | cim | Reactive component of the load that is a fixed quantity, MVAr. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Fixed Reactive Power
|  | CIMWires | EnergyConsumer | EnergyConsumer | qfixedPct | qfixedPct | PerCent |  | cim | Fixed MVAr as per cent of load area fixed MVAr. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Fixed Reactive Power Percent
|  | CIMWires | EnergyConsumer | EnergyConsumer | qnom | qnom | ReactivePower |  | cim | Nominal value for reactive power, MVAr. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Nominal Reactive Power
|  | CIMWires | EnergyConsumer | EnergyConsumer | qnomPct | qnomPct | PerCent |  | cim | Nominal MVAr as per cent of load group nominal MVAr. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Nominal Reactive Power Percent
|  | CIMWires | EnergyConsumer | EnergyConsumer | qVexp | qVexp | Exponent |  | cim | Exponent of per unit voltage effecting reactive power. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reactive Power Voltage Exponent
|  | CIMWires | EquivalentSource | EquivalentSource | activePower | activePower | ActivePower |  | cim | High voltage source load. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Active Power
|  | CIMWires | EquivalentSource | EquivalentSource | nominalVoltage | nominalVoltage | Voltage |  | cim | Phase-to-phase nominal voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Nominal Voltage
|  | CIMWires | EquivalentSource | EquivalentSource | r | r | Resistance |  | cim | Positive sequence Thevenin resistance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Resistance
|  | CIMWires | EquivalentSource | EquivalentSource | r0 | r0 | Resistance |  | cim | Zero sequence Thevenin resistance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zero Sequence Resistance
|  | CIMWires | EquivalentSource | EquivalentSource | rn | rn | Resistance |  | cim | Negative sequence Thevenin resistance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Negative Sequence Resistance
|  | CIMWires | EquivalentSource | EquivalentSource | voltageAngle | voltageAngle | AngleRadians |  | cim | Phase angle of a-phase open circuit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Voltage Angle
|  | CIMWires | EquivalentSource | EquivalentSource | voltageMagnitude | voltageMagnitude | Voltage |  | cim | Phase-to-phase open circuit voltage magnitude. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Voltage Magnitude
|  | CIMWires | EquivalentSource | EquivalentSource | x | x | Reactance |  | cim | Positive sequence Thevenin reactance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reactance
|  | CIMWires | EquivalentSource | EquivalentSource | x0 | x0 | Reactance |  | cim | Zero sequence Thevenin reactance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zero Sequence Reactance
|  | CIMWires | EquivalentSource | EquivalentSource | xn | xn | Reactance |  | cim | Negative sequence Thevenin reactance in Ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Negative Sequence Reactance
|  | CIMWires | FrequencyConverter | FrequencyConverter | frequency | frequency | Frequency |  | cim | Frequency on the AC side. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Frequency
|  | CIMWires | FrequencyConverter | FrequencyConverter | maximumKV | maximumKV | Voltage |  | cim | The maximum voltage on the DC side at which the frequency converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum kV
|  | CIMWires | FrequencyConverter | FrequencyConverter | maximumMW | maximumMW | ActivePower |  | cim | The maximum power on the DC side at which the frequence converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MW
|  | CIMWires | FrequencyConverter | FrequencyConverter | minimumKV | minimumKV | Voltage |  | cim | The minimum voltage on the DC side at which the frequency converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum kV
|  | CIMWires | FrequencyConverter | FrequencyConverter | minimumMW | minimumMW | ActivePower |  | cim | The minimum power on the DC side at which the frequence converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum MW
|  | CIMWires | FrequencyConverter | FrequencyConverter | operatingMode | operatingMode | OperatingMode |  | cim | Operating mode for the frequency converter. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Operating Mode
|  | CIMWires | Fuse | Fuse | ampRating | ampRating | CurrentFlow |  | cim | Fault interrupting rating in amperes. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Amp Rating
|  | CIMWires | Line | Line | emergencyMaxShadowPrice | emergencyMaxShadowPrice | DoubleFloat | 99999 | etx | States the Emergency Max Shadow price for a Line. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emergency Max Shadow Price
|  | CIMWires | Line | Line | fifteenMinuteMaxShadowPrice | fifteenMinuteMaxShadowPrice | DoubleFloat | 99999 | etx | States the 15 minute rating Max Shadow price for a Line. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | 15 minute rating Max Shadow Price
|  | CIMWires | Line | Line | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a Line. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
|  | CIMWires | LoadBreakSwitch | LoadBreakSwitch | ampRating | ampRating | CurrentFlow |  | cim | Current carrying capacity, expressed in amperes, of a wire or cable under stated thermal conditions | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | amp Rating
|  | CIMWires | MVArCapabilityCurve | MVArCapabilityCurve | coolantTemperature | coolantTemperature | Temperature |  | cim | The machine's coolant temperature in degrees Celsius (e.g., ambient air or stator circulating water). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Coolant Temperature
|  | CIMWires | MVArCapabilityCurve | MVArCapabilityCurve | hydrogenPressure | hydrogenPressure | Pressure |  | cim | The hydrogen coolant pressure. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Hydrogen Pressure
|  | CIMWires | PowerTransformer | PowerTransformer | bmagSat | bmagSat | PerCent |  | cim | Core shunt magnetizing susceptance in the saturation region, in per cent. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Magnetizing Susceptance Saturation
|  | CIMWires | PowerTransformer | PowerTransformer | emergencyMaxShadowPrice | emergencyMaxShadowPrice | DoubleFloat | 99999 | etx | States the Emergency Max Shadow price for a Line. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emergency Max Shadow Price
|  | CIMWires | PowerTransformer | PowerTransformer | fifteenMinuteMaxShadowPrice | fifteenMinuteMaxShadowPrice | DoubleFloat | 99999 | etx | States the 15 minute rating Max Shadow price for a Transformer. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | 15 minute rating Max Shadow Price
|  | CIMWires | PowerTransformer | PowerTransformer | magBaseKV | magBaseKV | Voltage |  | cim | The reference voltage at which the magnetizing saturation measurements were made. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Magnetizing Saturation Voltage
|  | CIMWires | PowerTransformer | PowerTransformer | magSatFlux | magSatFlux | PerCent |  | cim | Core magnetizing saturation curve knee flux level. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Magnetizing Saturation Flux
|  | CIMWires | PowerTransformer | PowerTransformer | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a Power Transformer. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
|  | CIMWires | PowerTransformer | PowerTransformer | phases | phases | PhaseCode |  | cim | Describes the phases carried by a power transformer. Possible values { ABCN , ABC, ABN, ACN, BCN, AB, AC, BC, AN, BN, CN, A, B, C, N }. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phases
|  | CIMWires | PowerTransformer | PowerTransformer | transfCoolingType | transfCoolingType | EnumTransformerCoolingType |  | cim | Type of transformer cooling. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Transformer Cooling Type
|  | CIMWires | PowerTransformer | PowerTransformer | transformerType | transformerType | EnumTransformerType |  | cim | Transformer Type. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Transformer Type
|  | CIMWires | PowerTransformer | PowerTransformer | voltageSensitivity | voltageSensitivity | PerCent |  | etx | SENSITIVITY OF VOLTAGE TO THE TRANSFORMER tap ratio. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Voltage Sensitivity
|  | CIMWires | RectifierInverter | RectifierInverter | bridges | bridges | Counter |  | cim | Number of bridges. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Bridges
|  | CIMWires | RectifierInverter | RectifierInverter | commutatingReactance | commutatingReactance | Reactance |  | cim | Commutating reactance in ohms at AC bus frequency. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Commutating Reactance
|  | CIMWires | RectifierInverter | RectifierInverter | commutatingResistance | commutatingResistance | Resistance |  | cim | Commutating resistance in ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Commutating Resistance
|  | CIMWires | RectifierInverter | RectifierInverter | compoundResistance | compoundResistance | Resistance |  | cim | Compounding resistance in ohms. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Compounding Resistance
|  | CIMWires | RectifierInverter | RectifierInverter | frequency | frequency | Frequency |  | cim | Frequency on the AC side. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Frequency
|  | CIMWires | RectifierInverter | RectifierInverter | maximumKV | maximumKV | Voltage |  | cim | The maximum voltage on the DC side at which the frequency converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum kV
|  | CIMWires | RectifierInverter | RectifierInverter | maximumMW | maximumMW | ActivePower |  | cim | The maximum power on the DC side at which the frequence converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MW
|  | CIMWires | RectifierInverter | RectifierInverter | minCompoundVoltage | minCompoundVoltage | Voltage |  | cim | Minimum compounded DC voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Compound Voltage
|  | CIMWires | RectifierInverter | RectifierInverter | minimumKV | minimumKV | Voltage |  | cim | The minimum voltage on the DC side at which the frequency converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum kV
|  | CIMWires | RectifierInverter | RectifierInverter | minimumMW | minimumMW | ActivePower |  | cim | The minimum power on the DC side at which the frequence converter should operate. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum MW
|  | CIMWires | RectifierInverter | RectifierInverter | operatingMode | operatingMode | OperatingMode |  | cim | Operating mode for the frequency converter. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Operating Mode
|  | CIMWires | RectifierInverter | RectifierInverter | ratedKV | ratedKV | Voltage |  | cim | Rectifier/inverter primary base voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Rated kV
|  | CIMWires | RegulatingCondEq | RegulatingCondEq | avrEnabled | avrEnabled | Boolean | FALSE | etx | T = Automatic voltage regulation enabled. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Automatic Voltage Regulation Enabled
|  | CIMWires | RegulatingCondEq | RegulatingCondEq | loadBasedRegulationEnabled | loadBasedRegulationEnabled | Boolean | FALSE | etx | T = Load based voltage regulation enabled. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Load Based Regulation Enabled
|  | CIMWires | RegulationSchedule | RegulationSchedule | lineDropCompensation | lineDropCompensation | Boolean | FALSE | cim | Flag to indicate that line drop compensation is to be applied. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Line Drop Compensation
|  | CIMWires | RegulationSchedule | RegulationSchedule | lineDropR | lineDropR | Resistance |  | cim | Line drop resistance. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Line Drop Resistance
|  | CIMWires | RegulationSchedule | RegulationSchedule | lineDropX | lineDropX | Reactance |  | cim | Line drop reactance. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Line Drop Reactance
|  | CIMWires | SeriesCompensator | SeriesCompensator | emergencyMaxShadowPrice | emergencyMaxShadowPrice | DoubleFloat | 99999 | etx | States the Emergency Max Shadow price for a SeriesCompensator. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emergency Max Shadow Price
|  | CIMWires | SeriesCompensator | SeriesCompensator | fifteenMinuteMaxShadowPrice | fifteenMinuteMaxShadowPrice | DoubleFloat | 99999 | etx | States the 15 minute Max Shadow price for a SeriesCompensator. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | 15 minute rating Max Shadow Price
|  | CIMWires | SeriesCompensator | SeriesCompensator | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a SeriesCompensator. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
|  | CIMWires | SeriesCompensator | SeriesCompensator | r | r | Resistance |  | cim | Positive sequence resistance of the capacitor bank. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Resistance
|  | CIMWires | SeriesCompensator | SeriesCompensator | x | x | Reactance |  | cim | Positive sequence reactance of the capacitor bank. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reactance
|  | CIMWires | ShuntCompensator | ShuntCompensator | aVRDelay | aVRDelay | Seconds |  | cim | Time delay in seconds required for the device to be connected or disconnected by automatic voltage regulation (AVR). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Automatic Voltage Regulation Delay
|  | CIMWires | ShuntCompensator | ShuntCompensator | impedance | impedance | Impedance |  | cim | The positive sequence impedance of the capacitor. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Impedance
|  | CIMWires | ShuntCompensator | ShuntCompensator | maximumkV | maximumkV | Voltage |  | cim | The maximum voltage at which the capacitor bank should operate. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum kV
|  | CIMWires | ShuntCompensator | ShuntCompensator | maximumSections | maximumSections | Counter |  | cim | For a capacitor bank, the maximum number of sections that may be switched in. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Sections
|  | CIMWires | ShuntCompensator | ShuntCompensator | minimumkV | minimumkV | Voltage |  | cim | The minimum voltage at which the capacitor bank should operate. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum kV
|  | CIMWires | ShuntCompensator | ShuntCompensator | mVArPerSection | mVArPerSection | ReactivePower |  | cim | For a capacitor bank, the size in MVAr of each switchable section at the Nominal kV. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | mVAr Per Section
|  | CIMWires | ShuntCompensator | ShuntCompensator | nominalkV | nominalkV | Voltage |  | cim | The nominal voltage at which the nominal MVAr was measured. This should normally be within 10% of the voltage at which the capacitor is connected to the network. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Nominal kV
|  | CIMWires | ShuntCompensator | ShuntCompensator | nominalMVAr | nominalMVAr | ReactivePower |  | cim | Nominal MVAr output of the capacitor bank at the nominal kV. This number should be positive. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Nominal MVAr
|  | CIMWires | ShuntCompensator | ShuntCompensator | normalSections | normalSections | Counter |  | cim | For a capacitor bank, the normal number of sections switched in. This number should correspond to the Nominal MVAr. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Normal Sections
|  | CIMWires | ShuntCompensator | ShuntCompensator | switchingPriority | switchingPriority | Integer |  | etx | Switching priority number. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Switching Priority
|  | CIMWires | ShuntCompensator | ShuntCompensator | switchOnCount | switchOnCount | Counter |  | cim | The switch on count since the capacitor count was last reset or initialized. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch On Count
|  | CIMWires | ShuntCompensator | ShuntCompensator | switchOnDate | switchOnDate | AbsoluteDateTime |  | cim | The date and time when the capacitor bank was last switched on. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch On Date
|  | CIMWires | ShuntCompensator | ShuntCompensator | voltSensitivity | voltSensitivity | PUkVPerMVAr |  | cim | Voltage sensitivity required for the device to regulate the bus voltage, in per unit voltage/MVAr. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Voltage Sensitivity
|  | CIMWires | ShuntCompensator | ShuntCompensator | yPerSection | yPerSection | Admittance |  | cim | For a capacitor bank, the admittance of each switchable section. Calculated using the MVAr per section and corrected for network voltage. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Y Per Section
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | b | b | ReactivePower |  | etx | SVC Shunt Admittance. The StaticVarCompensator class has been extended to include a 'charging' attribute. The units are assumed to be in MVAR, as required by the CPSM Profile. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | b
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | CapacitiveRating | capacitiveRating | Reactance |  | cim | Maximum available capacitive reactive power. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Capacitive Rating
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | fixedMVAr | fixedMVAr | Float |  | etx | Fixed MVAr. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 0 |  | Fixed MVAR
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | highVoltageChangeThreshold | highVoltageChangeThreshold | Float |  | etx | The upper bound of the voltage threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | High Voltage Change Threshold
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | InductiveRating | inductiveRating | Reactance |  | cim | Maximum available inductive reactive power. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Inductive Rating
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | lowVoltageChangeThreshold | lowVoltageChangeThreshold | Float |  | etx | The lower bound of the voltage threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Low Voltage Change Threshold
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | maximumkV | maximumkV | Voltage |  | etx | SVC Voltage Regulation. The maximum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Maximum kV
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | maxTimeSteadyState | maxTimeSteadyState | Float |  | etx | The maximum duration allowed to exceed Q range in steady_state. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Max Time Steady State
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | minimumkV | minimumkV | Voltage |  | etx | SVC Voltage Regulation. The minimum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Minimum kV
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | postContingencyMVARMax | postContingencyMVARMax | Float |  | etx | Post_contingency maximum MVAR limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Post Contingency MVAR Maximum
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | postContingencyMVARMin | postContingencyMVARMin | Float |  | etx | Post_contingency minimum MVAR limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Post Contingency MVAR Minimum
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | rampDelay | rampDelay | Float |  | etx | The desired time delay before ramp (Seconds). Entered by the database model builder. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Ramp Delay
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | rampDurationThreshold | rampDurationThreshold | Float |  | etx | The threshold ramp duration. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Ramp Duration Threshold
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | slope | slope | VoltagePerReactivePower |  | cim | The characteristics slope of an SVC defines how the reactive power output changes in proportion to the difference between the regulated bus voltage and the voltage setpoint. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | SVC Percentage Slope
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | steadyStateMVARMax | steadyStateMVARMax | Float |  | etx | Steady_state maximum MVAR limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Steady State MVAR Maximum
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | steadyStateMVARMin | steadyStateMVARMin | Float |  | etx | Steady_state minimum MVAR limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Steady State MVAR Minimum
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | sVCControlMode | sVCControlMode | EnumSVCControlMode |  | cim | SVC control mode | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | SVC Control Mode
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | voltageDeviation | voltageDeviation | Float |  | etx | SVC DEVIATION (+/-) FROM TARGET. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Voltage Deviation
|  | CIMWires | StaticVarCompensator | StaticVarCompensator | voltageSetPoint | voltageSetPoint | Voltage |  | cim | The reactive power output of the SVC is proportional to the difference between the voltage at the regulated bus and the voltage setpoint. When the regulated bus voltage is equal to the voltage setpoint, the reactive power output is zero. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 1100 | 0 | SVC Setpoint Voltage
|  | CIMWires | Switch | Switch | enableManualSwitching | enableManualSwitching | Boolean | FALSE | etx | T = Enables manual switching capability for the device. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Enable Manual Switching
|  | CIMWires | Switch | Switch | initiallyOpen | initiallyOpen | Boolean | FALSE | etx | T = The initial breaker state for the online switching device model is open. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Initially Open
|  | CIMWires | Switch | Switch | normalOpen | normalOpen | Boolean | FALSE | cim | The attribute is used in cases when no Measurement for the status value is present. If the Switch has a status measurment the Measurement.normalValue is expected to match with the Switch.normalOpen. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Normal Open
DD-1.21.1-001 OTS | ADD | CIMWires |  | Switch |  | protectLockoutAfterAction | Boolean |  | etx | Protect lockout after action. | [10 empty] | protectLockoutAfterAction
DD-1.21.1-001 OTS | ADD | CIMWires | ProtectedSwitch | Switch | protectLockoutAfterAction | protectOverAction | EnumSwitchState |  | etx | Protect over action. | [10 empty] | protectOverAction
DD-1.21.1-001 OTS | ADD | CIMWires | ProtectedSwitch | Switch | protectOverAction | protectUnderAction | EnumSwitchState |  | etx | Protect under action. | [10 empty] | Protect Under Action
|  | CIMWires | Switch | Switch | switchedBySchedule | switchedBySchedule | Boolean | FALSE | etx | T = The switch will follow a switching schedule to change state in the network applications. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Switched By Schedule
|  | CIMWires | Switch | Switch | switchOnCount | switchOnCount | Counter |  | cim | The switch on count since the switch was last reset or initialized. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch On Count
|  | CIMWires | Switch | Switch | switchOnDate | switchOnDate | AbsoluteDateTime |  | cim | The date and time when the switch was last switched on. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch On Date
DD-1.21.1-001 OTS | ADD | CIMWires |  | Switch |  | switchOperationOver | Boolean | FALSE | etx | Over Limit Violation Switch Operation (Open/Close). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch Operation Over
DD-1.21.1-001 OTS | ADD | CIMWires |  | Switch |  | switchOperationUnder | Boolean | FALSE | etx | Under Limit Violation Switch Operation (Open/Close). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Switch Operation Under
|  | CIMWires | Switch | Switch | triggerNetworkSequence | triggerNetworkSequence | Boolean | FALSE | etx | T = The switch will trigger the real?time network application sequence when the switch changes state in SCADA. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Trigger Network Sequence
DD-1.21.1-001 OTS | ADD | CIMWires |  | Switch |  | tripLockout | Boolean | FALSE | etx | Lockout after trip. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Trip Lockout
|  | CIMWires | Switch | Switch | ZBR | ZBR | Boolean | FALSE | etx | Mark Switching devices that should be converted to Zero Impedance Branches in Connectivity Node to Bus Processing Option 1. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | Zero Impedance Branch?
|  | CIMWires | SynchronousMachine | SynchronousMachine | aVRToManualLag | aVRToManualLag | Seconds |  | cim | Time delay, in seconds, required when switching from AVR to manual for a lagging MVAr violation. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | AVR to Manual Lag
|  | CIMWires | SynchronousMachine | SynchronousMachine | aVRToManualLead | aVRToManualLead | Seconds |  | cim | Time delay, in seconds, required when switching from Automatic Voltage Regulation to Manual for a leading MVAr violation. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | AVR to Manual Lead
|  | CIMWires | SynchronousMachine | SynchronousMachine | baseMVAr | baseMVAr | ReactivePower |  | cim | Default base MVAr value. This value represents the initial MVAr that can be used by any application function. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Base MVAr
|  | CIMWires | SynchronousMachine | SynchronousMachine | condenserMW | condenserMW | ActivePower |  | cim | Condensor MW | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Condenser MW
|  | CIMWires | SynchronousMachine | SynchronousMachine | coolantCondition | coolantCondition | Float |  | cim | Temperature or pressure of coolant medium. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Coolant Condition
|  | CIMWires | SynchronousMachine | SynchronousMachine | coolantType | coolantType | EnumCoolantType |  | cim | Method of cooling the machine, e.g., air, hydrogen gas, water. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Coolant Type
|  | CIMWires | SynchronousMachine | SynchronousMachine | damping | damping | Damping |  | cim | Damping torque coefficient, a proportionality constant that, when multiplied by the angular velocity of the rotor poles with respect to the magnetic field (frequency), results in the damping torque. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Damping
|  | CIMWires | SynchronousMachine | SynchronousMachine | inertia | inertia | Inertia | 5 | cim | The energy stored in the rotor when operating at rated speed. This value is used in the accelerating power reference frame for operator training simulator solutions. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Inertia
|  | CIMWires | SynchronousMachine | SynchronousMachine | manualToAVR | manualToAVR | Seconds |  | cim | Time delay, in seconds, required when switching from Manual to Automatic Voltage Regulation. This value is used in the accelerating power reference frame for powerflow solutions. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Manual to AVR
|  | CIMWires | SynchronousMachine | SynchronousMachine | maximumKV | maximumKV | Voltage |  | cim | Maximum kV limit for the unit. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 1100 | 0 | Maximum KV
|  | CIMWires | SynchronousMachine | SynchronousMachine | maximumMVAr | maximumMVAr | ReactivePower |  | cim | Maximum MVAr limit. This is the maximum (nameplate) limit for the unit. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MVAr
|  | CIMWires | SynchronousMachine | SynchronousMachine | minimumKV | minimumKV | Voltage |  | cim | Minimum kV limit for the unit. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 1100 | 0 | Minimum KV
|  | CIMWires | SynchronousMachine | SynchronousMachine | minimumMVAr | minimumMVAr | ReactivePower |  | cim | Minimum MVAr limit for the unit. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum MVAr
|  | CIMWires | SynchronousMachine | SynchronousMachine | operatingMode | operatingMode | EnumSynchronousMachineOperatingMode |  | cim | Current mode of operation, i.e., generator or condenser. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Operating Mode
|  | CIMWires | SynchronousMachine | SynchronousMachine | r | r | Resistance |  | cim | Positive sequence resistance of the synchronous machine. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | r
|  | CIMWires | SynchronousMachine | SynchronousMachine | r0 | r0 | Resistance |  | cim | Zero sequence resistance of the synchronous machine. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | r0
|  | CIMWires | SynchronousMachine | SynchronousMachine | ratedMVA | ratedMVA | ApparentPower |  | cim | Nameplate MVA rating for the unit. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Rated MVA
|  | CIMWires | SynchronousMachine | SynchronousMachine | Reduce | Reduce | Boolean | FALSE | etx | Attribute will be used to mark generators on low voltage systems that should be reduced and attached directly to the Transmission Level. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | Reduce?
|  | CIMWires | SynchronousMachine | SynchronousMachine | referencePriority | referencePriority | Integer |  | etx | Priority of unit for reference bus selection. 0 = don t care (default) 1 = highest priority. 2 is less than 1 and so on. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reference Priority
|  | CIMWires | SynchronousMachine | SynchronousMachine | type | type | EnumSynchronousMachineType |  | cim | Modes that this synchronous machine can operate in, i.e., as a generator, condenser, or both. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Type
|  | CIMWires | SynchronousMachine | SynchronousMachine | varManual | varManual | Boolean | FALSE | etx | Manually entered MVAR overrides capability curve. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | var Manual
|  | CIMWires | SynchronousMachine | SynchronousMachine | x | x | Reactance | 0.12 | cim | Positive sequence reactance of the synchronous machine. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 500 | 0.001 | x
|  | CIMWires | SynchronousMachine | SynchronousMachine | x0 | x0 | Reactance | 0.05 | cim | Zero sequence reactance of the synchronous machine. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 500 | 0.001 | x0
|  | CIMWires | SynchronousMachine | SynchronousMachine | xDirectSubtrans | xDirectSubtrans | Reactance |  | cim | Direct-axis subtransient reactance, also known as X'd. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | X Direct Subtrans
|  | CIMWires | SynchronousMachine | SynchronousMachine | xDirectSync | xDirectSync | Reactance |  | cim | Direct-axis synchronous reactance. The quotient of a sustained value of that AC component of armature voltage that is produced by the total direct-axis flux due to direct-axis armature current and the value of the AC component of this current, the machine running at rated speed. (Xd) | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | X Direct Sync
|  | CIMWires | SynchronousMachine | SynchronousMachine | xDirectTrans | xDirectTrans | Reactance |  | cim | Direct-axis transient reactance, also known as X'd. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | X Direct Trans
|  | CIMWires | SynchronousMachine | SynchronousMachine | xQuadSubtrans | xQuadSubtrans | Reactance |  | cim | Quadrature-axis subtransient reactance, also known as X'q. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | X Quad Subtrans
|  | CIMWires | SynchronousMachine | SynchronousMachine | xQuadSync | xQuadSync | Reactance |  | cim | Quadrature-axis synchronous reactance (Xq) , the ratio of the component of reactive armature voltage, due to the quadrature-axis component of armature current, to this component of current, under steady state conditions and at rated frequency. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | X Quad Sync
|  | CIMWires | SynchronousMachine | SynchronousMachine | xQuadTrans | xQuadTrans | Reactance |  | cim | Quadrature-axis transient reactance, also known as X'q. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | X Quad Trans
|  | CIMWires | SynchronousMachine | SynchronousMachine | xSubtrans | xSubtrans | Reactance |  | etx | Subtransient reactance, also known as X''. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | x Direct Subtrans
|  | CIMWires | SynchronousMachine | SynchronousMachine | xTrans | xTrans | Reactance |  | etx | Transient reactance, also known as X''. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | x Direct Trans
|  | CIMWires | TapChanger | TapChanger | avrEnabled | avrEnabled | Boolean | FALSE | etx | T =Automatic Voltage Regulation is enabled. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | AVR Enabled
|  | CIMWires | TapChanger | TapChanger | awrEnabled | awrEnabled | Boolean | FALSE | etx | T = automatic MW control is enabled. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | AWR Enabled
|  | CIMWires | TapChanger | TapChanger | coupledToTransformer | coupledToTransformer | Boolean | FALSE | etx | T = indicates that the phase shifter is coupled to a transformer winding. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Coupled To Transformer
|  | CIMWires | TapChanger | TapChanger | flowSensitivity | flowSensitivity | Float |  | etx | The sensitivity of the regulated MW flow to angle changes, in MW per degree. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Flow Sensitivity
|  | CIMWires | TapChanger | TapChanger | highStep | highStep | TapStep | 0 | cim | Highest possible tap step position, advance from neutral. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 99 | 0 | High Step
|  | CIMWires | TapChanger | TapChanger | InitialDelay | initialDelay | Seconds | 10 | cim | For an LTC, the delay for initial tap changer operation (first step change). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Initial Delay
|  | CIMWires | TapChanger | TapChanger | loadBasedRegulationEnabled | loadBasedRegulationEnabled | Boolean | FALSE | etx | T = Load-Based Voltage Regulation is enabled. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Load-Based Regulation Enabled
|  | CIMWires | TapChanger | TapChanger | lowStep | lowStep | TapStep | 0 | cim | Lowest possible tap step position, retard from neutral. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 99 | -99 | Low Step
|  | CIMWires | TapChanger | TapChanger | maximumkV | maximumkV | Voltage |  | etx | The maximum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum kV
|  | CIMWires | TapChanger | TapChanger | minimumkV | minimumkV | Voltage |  | etx | The minimum voltage regulation for TapChangers. Note that this is a fixed parameter which is not a function of time (i.e., not a regulation schedule). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum kV
|  | CIMWires | TapChanger | TapChanger | neutralAngle | neutralAngle | AngleDegrees |  | etx | The CIM currently has no way of defining the angle associated with the neutral position of a TapChanger belonging to a phase shifter. Thus a neutralAngle attribute (measured in degrees) has been added to the TapChanger class. This attribute only appears in XML when the parent PowerTransformer is a phase shifter, i.e., when PowerTransformer.transformerType = 'phaseControl' or 'voltageAndPhaseControl'. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Neutral Angle
|  | CIMWires | TapChanger | TapChanger | neutralKV | neutralKV | Voltage |  | cim | Voltage at which the winding operates at the neutral tap setting. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 1100 | 0 | Neutral KV
|  | CIMWires | TapChanger | TapChanger | neutralStep | neutralStep | TapStep | 0 | cim | The neutral tap step position for this winding. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 99 | -99 | Neutral Step
|  | CIMWires | TapChanger | TapChanger | normalStep | normalStep | TapStep | 0 | cim | The tap step position used in 'normal' network operation for this winding. For a 'Fixed' tap changer indicates the current physical tap setting. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 99 | -99 | Normal Step
|  | CIMWires | TapChanger | TapChanger | parMaxMW | parMaxMW | ActivePower |  | etx | PAR maximum MW value (MW). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | PAR Maximum MW
|  | CIMWires | TapChanger | TapChanger | parMinMW | parMinMW | ActivePower |  | etx | PAR minimum MW value (MW). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | PAR Minimum MW
|  | CIMWires | TapChanger | TapChanger | parOptimization | parOptimization | Boolean | FALSE | etx | PAR optimization flag. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | PAR Optimization
|  | CIMWires | TapChanger | TapChanger | parRampRate | parRampRate | ActivePower |  | etx | PAR optimiation ramp rate (MW per minute). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | PAR Ramp Rate
|  | CIMWires | TapChanger | TapChanger | stepPhaseShiftIncrement | stepPhaseShiftIncrement | AngleDegrees |  | cim | Phase shift, in degrees, per step position. A positive value indicates a positive phase shift from the winding where the tap is located to the other winding (for a two-winding transformer), or to the ANDquot;TANDquot; point (for a three-winding transformer). | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Step Phase Shift Increment
|  | CIMWires | TapChanger | TapChanger | stepVoltageIncrement | stepVoltageIncrement | PerCent |  | cim | Tap step increment, in per cent of nominal voltage, per step position. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Step Voltage Increment
|  | CIMWires | TapChanger | TapChanger | SubsequentDelay | subsequentDelay | Seconds | 5 | cim | For an LTC, the delay for subsequent tap changer operation (second and later step changes). | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Subsequent Delay
|  | CIMWires | TapChanger | TapChanger | TculControlMode | tculControlMode | EnumTransformerControlMode |  | cim | For an LTC, the tap changer control mode, e.g.: Off, Local, Volt, MVAr. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | LTC Control Mode
|  | CIMWires | TransformerWinding | TransformerWinding | b | b | Susceptance |  | cim | Magnetizing branch susceptance (B mag). | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 100 | -100 | b
|  | CIMWires | TransformerWinding | TransformerWinding | bmagSat | bmagSat | Susceptance |  | etx | Shunt magnetizing susceptance in saturation region. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | bmag Sat
|  | CIMWires | TransformerWinding | TransformerWinding | connectionType | connectionType | EnumWindingConnection | 1 | cim | The type of connection of the winding (e.g. Delta, Wye, zigzag). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Connection Type
|  | CIMWires | TransformerWinding | TransformerWinding | emergencyMVA | emergencyMVA | ApparentPower | 99999 | cim | The MVA that the winding can carry under emergency conditions. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Emergency Rating
|  | CIMWires | TransformerWinding | TransformerWinding | g | g | Conductance | 0 | cim | Magnetizing branch conductance (G mag). | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999 | 0 | g
|  | CIMWires | TransformerWinding | TransformerWinding | gmagSat | gmagSat | Conductance |  | etx | Shunt magnetizing conductance in saturation region. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | gmag Sat
|  | CIMWires | TransformerWinding | TransformerWinding | grounded | grounded | Boolean | TRUE | cim | Set if the winding is grounded. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Grounded
|  | CIMWires | TransformerWinding | TransformerWinding | insulationKV | insulationKV | Voltage |  | cim | Basic insulation level voltage rating. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Insulation kV
|  | CIMWires | TransformerWinding | TransformerWinding | kneeSat | kneeSat | Float |  | etx | Agnetization curve saturation knee flux level (pu volts/pu hz) | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | knee Sat
|  | CIMWires | TransformerWinding | TransformerWinding | r | r | Resistance |  | cim | Positive sequence series resistance of the winding. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 500 | 0 | r
|  | CIMWires | TransformerWinding | TransformerWinding | r0 | r0 | Resistance |  | cim | Zero sequence series resistance of the winding. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 5000 | -5000 | r0
|  | CIMWires | TransformerWinding | TransformerWinding | ratedKV | ratedKV | Voltage |  | cim | The rated voltage (phase-to-ground) of the winding, usually the same as the neutral voltage. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 1100 | 0.1 | Rated KV
|  | CIMWires | TransformerWinding | TransformerWinding | ratedMVA | ratedMVA | ApparentPower | 99999 | cim | The normal rating, in MVA, for the winding. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  | 0 | Normal Rating
|  | CIMWires | TransformerWinding | TransformerWinding | rground | rground | Resistance | 0 | cim | Ground resistance path through connected grounding transformer. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE | 10 | 0 | rground
|  | CIMWires | TransformerWinding | TransformerWinding | shortTermMVA | shortTermMVA | ApparentPower | 99999 | cim | MVA that the winding can carry for a short period of time. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Short Term Rating
|  | CIMWires | TransformerWinding | TransformerWinding | windingType | windingType | EnumWindingType |  | cim | The type of winding, i.e., Primary, Secondary, Tertiary, Quaternary. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Winding Type
|  | CIMWires | TransformerWinding | TransformerWinding | x | x | Reactance |  | cim | Positive sequence series reactance of the winding. | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 1000 | -1000 | x
|  | CIMWires | TransformerWinding | TransformerWinding | x0 | x0 | Reactance |  | cim | Zero sequence series reactance of the winding. | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 10000 | -10000 | x0
|  | CIMWires | TransformerWinding | TransformerWinding | xground | xground | Reactance | 0 | cim | Ground reactance path through connected grounding transformer. | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 9999 | 0 | x ground
|  | CIMWires | WindingTest | WindingTest | excitingCurrent | excitingCurrent | ExcitingCurrent |  | cim | The exciting current % ('to' winding open-circuited) from the test report. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Exciting Current
|  | CIMWires | WindingTest | WindingTest | fromTapStep | fromTapStep | TapStep |  | cim | The tap step number for the 'from' winding of the test pair. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | From Tap Step
|  | CIMWires | WindingTest | WindingTest | leakageImpedance | leakageImpedance | Impedance |  | cim | The leakage impedance measured at the 'from' winding with the 'to' winding short-circuited and all other windings open-circuited. Leakage impedance is expressed in units based on the MVA and kV ratings of the 'from' winding. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Leakage Impedance
|  | CIMWires | WindingTest | WindingTest | loadLoss | loadLoss | LoadLoss |  | cim | The load loss kW ('to' winding short-circuited) from the test report. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Loss
|  | CIMWires | WindingTest | WindingTest | noLoadLoss | noLoadLoss | NoLoadLoss |  | cim | The no load loss kW 'to' winding open-circuited) from the test report. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | No Load Loss
|  | CIMWires | WindingTest | WindingTest | phaseShift | phaseShift | AngleDegrees |  | cim | The phase shift measured at the open-circuited 'to' winding, with the 'from' winding set to the 'from' winding's rated voltage and all other windings open-circuited. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phase Shift
|  | CIMWires | WindingTest | WindingTest | toTapStep | toTapStep | TapStep |  | cim | The tap step number for the 'to' winding of the test pair. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | To Tap Step
|  | CIMWires | WindingTest | WindingTest | voltage | voltage | Voltage |  | cim | The voltage measured at the open-circuited 'to' winding, with the 'from' winding set to the 'from' winding's rated voltage and all other windings open-circuited. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Voltage
|  | CIMWires | WireArrangement | WireArrangement | mountingPointX | mountingPointX | Integer |  | cim | Mounting point where wire One is mounted. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Mounting Point X
|  | CIMWires | WireArrangement | WireArrangement | mountingPointY | mountingPointY | Integer |  | cim | Mounting point where wire Two is mounted. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Mounting Point Y
|  | CIMWires | WireType | WireType | ampRating | ampRating | CurrentFlow |  | cim | Current carrying capacity, expressed in amperes, of a wire or cable under stated thermal conditions. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Amp Rating
|  | CIMWires | WireType | WireType | gMR | gMR | ShortLength |  | cim | Geometric Mean Radius. If we replace the conductor by a thin walled tube of radius GMR, then its reactance is identical to the reactance of the actual conductor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Geometric Mean Radius
|  | CIMWires | WireType | WireType | phaseConductorCount | phaseConductorCount | Counter |  | cim | Number of conductor strands in the (symmetrical) bundle (1-12). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Phase Conductor Count
|  | CIMWires | WireType | WireType | phaseConductorSpacing | phaseConductorSpacing | ShortLength |  | cim | Distance between conductor strands in a (symmetrical) bundle (short length units). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Short Conductor Spacing
|  | CIMWires | WireType | WireType | radius | radius | ShortLength |  | cim | The radius of the conductor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Radius
|  | CIMWires | WireType | WireType | resistance | resistance | Resistance |  | cim | The resistance per unit length of the conductor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Resistance
|  | EnergyScheduling | AreaReserveSpec | AreaReserveSpec | lowerRegMarginReqt | lowerRegMarginReqt | ActivePower | 20 | cim | Lower regulating margin requirement in MW, the amount of generation that can be dropped by control in 10 minutes | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Lower Reg Margin Reqt
|  | EnergyScheduling | AreaReserveSpec | AreaReserveSpec | opReserveReqt | opReserveReqt | ActivePower | 500 | cim | Operating reserve requirement in MW, where operating reserve is the generating capability that is fully available within 30 minutes. Operating reserve is composed of primary reserve (t less than 10 min) and secondary reserve (10 less than t less than 30 min). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Op Reserve Reqt
|  | EnergyScheduling | AreaReserveSpec | AreaReserveSpec | primaryReserveReqt | primaryReserveReqt | ActivePower | 40 | cim | Primary reserve requirement in MW, where primary reserve is generating capability that is fully available within 10 minutes. Primary reserve is composed of spinning reserve and quick-start reserve. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Primary Reserve Reqt
|  | EnergyScheduling | AreaReserveSpec | AreaReserveSpec | raiseRegMarginReqt | raiseRegMarginReqt | ActivePower | 20 | cim | Raise regulating margin requirement in MW, the amount of generation that can be picked up by control in 10 minutes | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Raise Reg Margin Reqt
|  | EnergyScheduling | AreaReserveSpec | AreaReserveSpec | spinningReserveReqt | spinningReserveReqt | ActivePower | 200 | cim | Spinning reserve requirement in MW, spinning reserve is generating capability that is presently synchronized to the network and is fully available within 10 minutes | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  | 0 | Spinning Reserve Reqt
|  | EnergyScheduling | EnergyTransaction | EnergyTransaction | congestChargeMax | congestChargeMax | Money |  | cim | Maximum congestion charges in monetary units. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Congestion Charge Maximum
|  | EnergyScheduling | EnergyTransaction | EnergyTransaction | deliveryPointMW | deliveryPointMW | ActivePower |  | cim | Delivery point typically expressed in MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Delivery Point MW
|  | EnergyScheduling | EnergyTransaction | EnergyTransaction | energyMin | energyMin | ActivePower |  | cim | Transaction minimum MW if dispatchable. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Energy Min
|  | EnergyScheduling | EnergyTransaction | EnergyTransaction | firmInterchangeFlag | firmInterchangeFlag | Boolean | FALSE | cim | Firm interchange flag indicates whether or not this energy transaction can be changed without potential financial consequences. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Firm Interchange Flag
|  | EnergyScheduling | EnergyTransaction | EnergyTransaction | reason | reason | String100 |  | cim | Additional information is not available. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reason
|  | EnergyScheduling | EnergyTransaction | EnergyTransaction | receiptPointMW | receiptPointMW | ActivePower |  | cim | Receipt point typically expressed in MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Receipt Point MW
|  | EnergyScheduling | HostControlArea | HostControlArea | AreaControlMode | areaControlMode | EnumAreaControlModel | 0 | cim | The area's present control mode: (CF = constant frequency) or (CTL = constant tie-line) or (TLB = tie-line bias) or (OFF = off control) | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Area Control Mode
|  | EnergyScheduling | HostControlArea | HostControlArea | assistEmergencyPriorityLevel | assistEmergencyPriorityLevel | Integer |  | etx | Assist Threshold. When the ACE is in emergency region, then all the units up to this Pritority level will have the desired priority level =1. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Assist Emergency Priority Level
|  | EnergyScheduling | HostControlArea | HostControlArea | assistPriorityLevel | assistPriorityLevel | Integer |  | etx | Assist Threshold. When the ACE is in assist region, then all the units up to this Priority level will have the desired priority level =1. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Assist Priority Level
|  | EnergyScheduling | HostControlArea | HostControlArea | balanceRampEnd | balanceRampEnd | Float |  | etx | Number of minutes into the period to end the balancing energy schedule ramp. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Balance Ramp End
|  | EnergyScheduling | HostControlArea | HostControlArea | balanceRampStart | balanceRampStart | Float |  | etx | Number of minutes before the end of the period to start the balancing energy schedule ramp. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Balance Ramp Start
|  | EnergyScheduling | HostControlArea | HostControlArea | costCO2 | costCO2 | Float |  | etx | Cost of CO2 in objective (Cost/UnitsCO2). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cost CO2
|  | EnergyScheduling | HostControlArea | HostControlArea | costNOX | costNOX | Float |  | etx | Cost of NOX in objective (Cost/UnitsCO2). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cost NOX
|  | EnergyScheduling | HostControlArea | HostControlArea | costSO2 | costSO2 | Float |  | etx | Cost of SO2 in objective (Cost/UnitsCO2). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cost SO2
|  | EnergyScheduling | HostControlArea | HostControlArea | cycleTimeMultiplier | cycleTimeMultiplier | Integer |  | etx | AGC CONTROL CYCLE MULTIPLIER (AGC ONLY). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | cycle Time Multiplier
|  | EnergyScheduling | HostControlArea | HostControlArea | deadbandAlarmACE | deadbandAlarmACE | Float |  | etx | ACE ALARM DEADBAND (EG: 2 MW). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Alarm ACE
|  | EnergyScheduling | HostControlArea | HostControlArea | deadbandAutoInadvertent | deadbandAutoInadvertent | Integer |  | etx | DEADBAND FOR AUTOMATIC INADVERTENT (PEAK AND OFFPEAK) IN MWHR IF INADVERTENT VALUE IS WITHIN THIS DEADBAND AUTO PAYBACK IS DISABLED | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Auto Inadvertent
|  | EnergyScheduling | HostControlArea | HostControlArea | deadbandFreqWarningAlarm | deadbandFrequencyWarningAlarm | Float |  | etx | DEADBAND ON WARNING ALARM THRESHOLD ON FREQUENCY (E.G. 0.05 HZ) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Frequency Warning Alarm
|  | EnergyScheduling | HostControlArea | HostControlArea | deadbandIntegratedSCEAlarm | deadbandIntegratedSCEAlarm | Float |  | etx | INTEGRATED SCE ALARM DEADBAND. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Integrated SCE Alarm
|  | EnergyScheduling | HostControlArea | HostControlArea | deadbandMultiplerNotTracking | deadbandMultiplerNotTracking | Float |  | etx | NOT TRACKING DEADBAND MULTIPLIER (EG: 2) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Multiplier Not Tracking
|  | EnergyScheduling | HostControlArea | HostControlArea | deadbandNormalResponseACE | deadbandNormalResponseACE | Integer |  | etx | ACE DEADBAND; ACE LIMIT FOR NORMAL RESPONSE (EG: 5 MW) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Normal Response ACE
|  | EnergyScheduling | HostControlArea | HostControlArea | deadbandPercentOpRsrvAlarm | deadbandPercentOpReserveAlarm | Integer |  | etx | OPERATING RESERVE ALARM DEADBAND (PERCENT OF OPER RESERVE REQUIREMENT) (EG: 5% ) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Percent Op Reserve Alarm
|  | EnergyScheduling | HostControlArea | HostControlArea | deadbandPercentRegRsrvAlarm | deadbandPercentRegReserveAlarm | Integer |  | etx | REGULATING RESERVE ALARM DEADBAND (PERCENT OF REG RESERVE REQUIREMENT) (EG: 5% ) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Percent Reg Reserve Alarm
|  | EnergyScheduling | HostControlArea | HostControlArea | deadbandPercentSpinRsrvAlarm | deadbandPercentSpinReserveAlarm | Integer |  | etx | SPINNING RESERVE ALARM DEADBAND (PERCENT OF ALARM LIMIT) (AGC ONLY) (EG: 5% ). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Percent Spin Reserve Alarm
|  | EnergyScheduling | HostControlArea | HostControlArea | deadbandPercentTieLimitAlarm | deadbandPercentTieLimitAlarm | Float |  | etx | TIE LINE FLOW LIMIT ALARMS DEADBAND (% OF LIMIT) (EG: 1%) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Percent Tie Limit Alarm
|  | EnergyScheduling | HostControlArea | HostControlArea | deadbandPercentTimeError | deadbandPercentTimeError | Integer |  | etx | TIME ERROR DEADBAND (PERCENT OF ALARM LIMIT) (EG:5%). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Percent Time Error
|  | EnergyScheduling | HostControlArea | HostControlArea | deadbandVariableMaximum | deadbandVariableMaximum | Float |  | etx | High limit for the deadband variable (scalar). Used in the variable frequency bias calculation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Variable Maximum
|  | EnergyScheduling | HostControlArea | HostControlArea | deadbandVariableMinimum | deadbandVariableMinimum | Float |  | etx | Low limit for the deadband variable (scalar). Used in the variable frequency bias calculation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Deadband Variable Minimum
|  | EnergyScheduling | HostControlArea | HostControlArea | defaultLoadRelief | defaultLoadRelief | Float |  | etx | The percentage of the breakpoint's control area load MW value to use as the default for the breakpoint's load relief value if that value is null. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Default Load Relief
|  | EnergyScheduling | HostControlArea | HostControlArea | deltaTime | deltaTime | Integer |  | etx | TIME DIFFERENCE BETWEEN EMS TIME ZONE AND REPORTING TIME ZONE. WHEN DELTA-TIME IS ADDED TO THE TIME IN THE EMS TIME ZONE, THE RESULT SHOULD BE THE CURRENT TIME IN THE REPORTING TIME ZONE. (Units?) | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Delta Time
|  | EnergyScheduling | HostControlArea | HostControlArea | deployFreqThreshold | deployFreqThreshold | Float |  | etx | Deploy frequency threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Deploy Frequency Threshold
|  | EnergyScheduling | HostControlArea | HostControlArea | filterTimeConstantJointACE | filterTimeConstantJointACE | Float |  | etx | Joint AGC ACE request filter time constant. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Filter Time Constant Joint ACE
|  | EnergyScheduling | HostControlArea | HostControlArea | forGeneration | forGeneration | Bool | FALSE | etx | HostControlArea belongs to Generation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | for Generation
|  | EnergyScheduling | HostControlArea | HostControlArea | forNetwork | forNetwork | Bool | FALSE | etx | HostControlArea Belongs to Network. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | for Network
|  | EnergyScheduling | HostControlArea | HostControlArea | frequencyAlarmThreshold | frequencyAlarmThreshold | Float |  | etx | WARNING ALARM THRESHOLD ON FREQUENCY (E.G. 0.2 HZ) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Alarm Threshold
|  | EnergyScheduling | HostControlArea | HostControlArea | frequencyBiasFactor | frequencyBiasFactor | Float |  | etx | AREA LOAD BIAS -LOAD FREQUENCY SENSITIVITY- (MW/0.1HZ) (EG: 0.2% AREA CAP). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Bias Factor
|  | EnergyScheduling | HostControlArea | HostControlArea | frequencyBiasFactorManual | frequencyBiasFactorManual | Float |  | etx | Manually entered frequency bias in MW/0.1 Hz. Equal to FBIAS_OPA if manual entry of frequency bias is selected, otherwise it contains the most recent manually entered value of frequency bias. Modifiable online. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Bias Factor Manual
|  | EnergyScheduling | HostControlArea | HostControlArea | frequencyNominalMaximum | frequencyNominalMaximum | Float |  | etx | SCHEDULED AREA FREQUENCY MAXIMUM (IN HZ; DEFAULT VALUE - 62 HZ). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Nominal Maximum
|  | EnergyScheduling | HostControlArea | HostControlArea | frequencyNominalMinimum | frequencyNominalMinimum | Float |  | etx | SCHEDULED AREA FREQUENCY MINIMUM (IN HZ; DEFAULT VALUE - 58 HZ). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Nominal Minimum
|  | EnergyScheduling | HostControlArea | HostControlArea | frequencyTrip | frequencyTrip | Float |  | etx | FREQUENCY OFFSET TO TRIP AGC OFF AND CREATE AGC CONTROL ALARM (E.G. 0.45 HZ) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Frequency Trip
|  | EnergyScheduling | HostControlArea | HostControlArea | gainAssist | gainAssist | Float |  | etx | ASSIST GAIN ON ACE (EG: 3.0) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gain Assist
|  | EnergyScheduling | HostControlArea | HostControlArea | gainEmergency | gainEmergency | Float |  | etx | EMERGENCY GAIN ON ACE. (EG: 10.0) (AGC ONLY) | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | gainEmergency
|  | EnergyScheduling | HostControlArea | HostControlArea | gainEmergencyIntegral | gainEmergencyIntegral | Float |  | etx | EMERGENCY GAIN ON INTEGRAL ACE. (EG: 0.6) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gain Emergency Integral
|  | EnergyScheduling | HostControlArea | HostControlArea | gainIntegralAssist | gainIntegralAssist | Float |  | etx | ASSIST GAIN ON INTEGRAL ACE. (EG: 0.4) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gain Integral Assist
|  | EnergyScheduling | HostControlArea | HostControlArea | gainJointAGCPersistFeeback | gainJointAGCPersistancyFeeback | Float |  | etx | Joint agc persistency feedback gain. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gain Joint AGC Persistancy Feeback
|  | EnergyScheduling | HostControlArea | HostControlArea | gainNominal | gainNominal | Float |  | etx | NOMINAL GAIN ON ACE (NORMAL REGULATING RESPONSE) (EG: 1.4) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gain Nominal
|  | EnergyScheduling | HostControlArea | HostControlArea | gainNominalIntegral | gainNominalIntegral | Float |  | etx | NOMINAL GAIN ON INTEGRAL ACE. (EG: 0.1) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Gain Nominal Integral
|  | EnergyScheduling | HostControlArea | HostControlArea | governorResponseDeadband | governorResponseDeadband | Float |  | etx | Expected governor response frequency deviation deadband. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Governor Response Deadband
|  | EnergyScheduling | HostControlArea | HostControlArea | internal | internal | Boolean | FALSE | etx | The MMS applications require that one of the HostControlAreas defined in the model be designated as the 'main' company. ERCOT may also opt for the decomposition of the model into areas, which requires an indication of which HostControlAreas are 'internal'. Note that the main designation is not necessarily synonymous with the internal designation since it is possible to have multiple internal HostControlAreas but only one main HostControlArea. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | internal
|  | EnergyScheduling | HostControlArea | HostControlArea | jointAGCStallMW | jointAGCStallMW | Float |  | etx | Joint agc regulation MW amount that'll be issued at detected stall of ACE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Joint AGC Stall MW
|  | EnergyScheduling | HostControlArea | HostControlArea | lamdaDeadband | lamdaDeadband | Float |  | etx | LAMBDA DEADBAND TO BE USED FOR PAYBACK OF INADVERTENT ACCUMULATION IN | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Lamda Deadband
|  | EnergyScheduling | HostControlArea | HostControlArea | limitAssistResponseACE | limitAssistResponseACE | Integer |  | etx | ACE LIMIT FOR ASSIST RESPONSE (EG: 20 MW) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Limit Assist Response ACE
|  | EnergyScheduling | HostControlArea | HostControlArea | limitEmergencyResponseACE | limitEmergencyResponseACE | Integer |  | etx | ACE LIMIT FOR EMERGENCY ASSIST RESPONSE (EG: 40 MW) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Limit Emergency Response ACE
|  | EnergyScheduling | HostControlArea | HostControlArea | limitNonWindupIntegralACE | limitNonWindupIntegralACE | Integer |  | etx | NON-WINDUP LIMIT ON INTEGRAL OF ACE (MW-HR). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Limit Non-Windup Integral ACE
|  | EnergyScheduling | HostControlArea | HostControlArea | loadReliefFirstMW | loadReliefFirstMW | Float |  | etx | The control area load MW value for the first breakpoint in the load relief table. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Relief First MW
|  | EnergyScheduling | HostControlArea | HostControlArea | loadReliefLastMW | loadReliefLastMW | Float |  | etx | The control area load MW value for the last breakpoint in the load relief table. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Load Relief Last MW
|  | EnergyScheduling | HostControlArea | HostControlArea | main | main | Boolean | FALSE | etx | The MMS applications require that one of the HostControlAreas defined in the model be designated as the 'main' company. ERCOT may also opt for the decomposition of the model into areas, which requires an indication of which HostControlAreas are 'internal'. Note that the main designation is not necessarily synonymous with the internal designation since it is possible to have multiple internal HostControlAreas but only one main HostControlArea. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | main
|  | EnergyScheduling | HostControlArea | HostControlArea | maxAutoInadvertentPayback | maximumAutoInadvertentPayback | Float |  | etx | MAXIMUM VALUE OF AUTOMATIC INADVERTENT PAYBACK PERMITTED PER CYCLE IN MW/AGC-CYCLE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Auto Inadvertent Payback
|  | EnergyScheduling | HostControlArea | HostControlArea | maximumInterchangeLossModel | maximumInterchangeLossModel | Float |  | etx | MAXIMUM INTERCHANGE FOR BOUNDARY DEFINITION FOR BINS FOR LOSS MODELLING.USED IN GENMODEL. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Interchange Loss Model
|  | EnergyScheduling | HostControlArea | HostControlArea | maximumInterchangeSchedule | maximumInterchangeSchedule | Float |  | etx | MAX. INTERCHANGE SCHEDULE MW ALLOWED BEFORE ALARM IS ISSUED (AGC ONLY) (EG: 2000 MW) | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Interchange Schedule
|  | EnergyScheduling | HostControlArea | HostControlArea | maxInterruptableLoadReserve | maximumInterruptableLoadReserve | Float |  | etx | Maximum interruptable load contribution to spinning or operating reserve. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Interruptable Load Reserve
|  | EnergyScheduling | HostControlArea | HostControlArea | maximumJointACE | maximumJointACE | Float |  | etx | Maximum value of ACE before the request percentage is applied. The request percentage is only applied to the incremental value of ACE above this threshold. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Joint ACE
|  | EnergyScheduling | HostControlArea | HostControlArea | maximumLoadLossModel | maximumLoadLossModel | Float |  | etx | MAXIMUM LOAD FOR BOUNDARY DEFINITION FOR BINS FOR LOSS MODELLING.USED IN GENMODEL. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Load Loss Model
|  | EnergyScheduling | HostControlArea | HostControlArea | maximumMiscReserve | maximumMiscReserve | Integer |  | etx | Maximum miscellaneous reserve contribution. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Misc Reserve
|  | EnergyScheduling | HostControlArea | HostControlArea | maximumObligationExportMW | maximumObligationExportMW | Float |  | etx | Maximum obligation Mw (Export) value used in the Target MW calculation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Obligation Export MW
|  | EnergyScheduling | HostControlArea | HostControlArea | maximumObligationImportMW | maximumObligationImportMW | Float |  | etx | Maximum obligation Mw (Import) value used in the Target MW calculation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Obligation Import MW
|  | EnergyScheduling | HostControlArea | HostControlArea | maximumTripACE | maximumTripACE | Integer |  | etx | VALUE OF ACE ABOVE WHICH AGC WILL PAUSE. VALUE MUST BE GREATER THAN OR EQUAL TO ACEALM_OPA, OR LESS THAN ZERO | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Trip ACE
|  | EnergyScheduling | HostControlArea | HostControlArea | minimumInterchangeLossModel | minimumInterchangeLossModel | Float |  | etx | MINIMUM INTERCHANGE FOR BOUNDARY DEFINITION FOR BINS FOR LOSS MODELLING.USED IN GENMODEL. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Interchange Loss Model
|  | EnergyScheduling | HostControlArea | HostControlArea | minimumJointACE | minimumJointACE | Float |  | etx | Minimum value of ACE before the request percentage is applied. The request percentage is only applied to the incremental value of ACE above this threshold. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Joint ACE
|  | EnergyScheduling | HostControlArea | HostControlArea | minimumLoadLossModel | minimumLoadLossModel | Float |  | etx | MINIMUM LOAD FOR BOUNDARY DEFINITION FOR THE BINS FOR LOSS MODELLING USED IN SETTING UP BOUNDARIES IN GENMODEL. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Load Loss Model
|  | EnergyScheduling | HostControlArea | HostControlArea | minimumPermissiveACE | minimumPermissiveACE | Integer |  | etx | MINIMUM ACE LEVEL FOR PERMISSIVE CONTROL (MW) (EG: 35 MW). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Permissive ACE
|  | EnergyScheduling | HostControlArea | HostControlArea | minimumResponseRateAlarm | minimumResponseRateAlarm | Float |  | etx | MIN RESPONSE RATE ALARM LEVEL (MW/MIN) (EG: 0.10% AREA CAP) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Response Rate Alarm
|  | EnergyScheduling | HostControlArea | HostControlArea | minutesFutureAdvisoryED | minutesFutureAdvisoryED | Float |  | etx | The number of minutes in the future to evaluate the load and transaction schedules at for the Advisory ED. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minutes Future Advisory ED
|  | EnergyScheduling | HostControlArea | HostControlArea | minutesOperatingReserve | minutesOperatingReserve | Float |  | etx | Time period (in minutes) in which a unit's output can change to contribute to operating reserves. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minutes Operating Reserve
|  | EnergyScheduling | HostControlArea | HostControlArea | minutesPendingFreqSchedule | minutesPendingFrequencySchedule | Float |  | etx | MINUTES FOR SENDING PENDING FREQUENCY SCHEDULE MESSAGE. (EG: 5 MIN). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minutes Pending Frequency Schedule
|  | EnergyScheduling | HostControlArea | HostControlArea | minutesRegulatingReserve | minutesRegulatingReserve | Float |  | etx | Time period (in minutes) in which a unit's output can change to contribute to regulating reserves. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minutes Regulating Reserve
|  | EnergyScheduling | HostControlArea | HostControlArea | minutesSpinningReserve | minutesSpinningReserve | Integer |  | etx | Time period (in minutes) in which a unit's output can change to contribute to spinning reserves. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minutes Spinning Reserve
|  | EnergyScheduling | HostControlArea | HostControlArea | percentCapOpRsrvReqDefault | percentCapOpReserveReqDefault | Float |  | etx | AREA REGULATING RESERVE REQUIREMENT (MW) (EG: 3% AREA CAP) (AGC ONLY) INITIAL DEFAULT VALUE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Cap Op Reserve Req Default
|  | EnergyScheduling | HostControlArea | HostControlArea | percentCapOpRsrvRequirement | percentCapOpReserveRequirement | Integer |  | etx | AREA OPERATING RESERVE REQUIREMENT (MW) (EG 8% AREA CAP) (AGC ONLY) INITIAL DEFAULT VALUE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Cap Op Reserve Requirement
|  | EnergyScheduling | HostControlArea | HostControlArea | percentCapSpinRsrvReqDefault | percentCapSpinReserveReqDefault | Float |  | etx | AN EXCESSIVE ALARM WILL BE ISSUED IF THE INTEGRATED SCE EXCEEDS THIS THRESHOLD. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Cap Spin Reserve Req Default
|  | EnergyScheduling | HostControlArea | HostControlArea | percentCapSpinRsrvReq | percentCapSpinReserveRequirement | Float |  | etx | SPINNING RESERVE REQUIREMENT (MW) (EG: 5% AREA CAP) (AGC ONLY) INITIAL DEFAULT VALUE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Cap Spin Reserve Requirement
|  | EnergyScheduling | HostControlArea | HostControlArea | percentFrequencyBias | percentFrequencyBias | PerCent |  | etx | Percentage of frequency bias. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Frequency Bias
|  | EnergyScheduling | HostControlArea | HostControlArea | percentIntegrationMissing | percentIntegrationMissing | Float |  | etx | percent threshold of missing samples in a regulation integration interval, if more than this percent samples are missing, quality (TRINBAD) for the interval’s integration will be declared 'bad' . | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Integration Missing
|  | EnergyScheduling | HostControlArea | HostControlArea | percentJointAGCRequest | percentJointAGCRequest | Float |  | etx | Percentage of area ACE that requester area is asking from other area. This is enterable on the joint AGC display for requester area. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Joint AGC Request
|  | EnergyScheduling | HostControlArea | HostControlArea | percentMWStepChangeAlarm | percentMWStepChangeAlarm | Float |  | etx | UNIT MW STEP CHANGE ALARM LEVEL (% OF UNIT CAPACITY) (EG:10%)(AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent MW Step Change Alarm
|  | EnergyScheduling | HostControlArea | HostControlArea | percentObjectCO2 | percentObjectCO2 | Float |  | etx | Weighting factor for CO2 in Emissions Reduction Objective. Has range from 0 to 100%. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | percentObjectiveCO2
|  | EnergyScheduling | HostControlArea | HostControlArea | percentObjectiveFuel | percentObjectiveFuel | Float |  | etx | Weighting factor for fuel in Emissions Reduction Objective. Has range from 0 to 100%. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Percent Objective Fuel
|  | EnergyScheduling | HostControlArea | HostControlArea | percentObjectiveNOX | percentObjectiveNOX | Float |  | etx | Weighting factor for NOX in Emissions Reduction Objective. Has range from 0 to 100%. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Percent Objective NOX
|  | EnergyScheduling | HostControlArea | HostControlArea | percentObjectiveSO2 | percentObjectiveSO2 | Float |  | etx | Weighting factor for SO2 in Emissions Reduction Objective. Has range from 0 to 100%. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Percent Objective SO2
|  | EnergyScheduling | HostControlArea | HostControlArea | percentUnitNotTrackingAlarm | percentUnitNotTrackingAlarm | Float |  | etx | UNIT NOT TRACKING ALARM LEVEL (PERCENT OF EQUIVALENT MSR) (AGC ONLY) (EG: 20% ). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Percent Unit Not Tracking Alarm
|  | EnergyScheduling | HostControlArea | HostControlArea | rampDurationToStop | rampDurationToStop | Float |  | etx | RSG Ramp duration to stop time. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Ramp Duration To Stop
|  | EnergyScheduling | HostControlArea | HostControlArea | rampDurationToTarget | rampDurationToTarget | Float |  | etx | RSG Ramp duration to target in Minutes. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Ramp Duration To Target
|  | EnergyScheduling | HostControlArea | HostControlArea | scedFailureThreshold | scedFailureThreshold | Integer |  | etx | SCED failure threshold in seconds. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | SCED Failure Threshold
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsAGCCycle | secondsAGCCycle | Integer |  | etx | AGC CYCLE PERIOD IN SECONDS (EG: 4 SEC) (AGC ONLY) MUST BE AN INTEGER MULTIPLE OF THE CORRESPONDING SCADA SCAN PERIOD. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds AGC Cycle
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsAGCOff | secondsAGCOff | Float |  | etx | AGC WILL START CYCLING THIS MANY SECONDS AFTER INITIALIZATION. (EG: 0 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds AGC Off
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsAlarmResponse | secondsAlarmResponse | Float |  | etx | NOM TIME TO REPEAT ALARM INSUFFICIENT AREA RESPONSE CAPABILITY (SEC) (EG: 600 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Alarm Response
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsControlEcoDispatch | secondsControlEcoDispatch | Float |  | etx | NOMINAL CONTROL ED RATE (SEC) (EG: 300 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Control Eco Dispatch
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsDeadbandDynamicACE | secondsDeadbandDynamicACE | Integer |  | etx | DYNAMIC ACE DEADBAND TIME CONSTANT (AGC ONLY) (EG: 4 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Deadband Dynamic ACE
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsDeadbandTimeError | secondsDeadbandTimeError | Float |  | etx | The auto time error correction deadband (SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Deadband Time Error
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsEmergencyDisableJoint | secondsEmergencyDisableJoint | Float |  | etx | Number of seconds ACE can be in emergency region before joint AGC is disabled for all TIEs. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Emergency Disable Joint
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsEvaluateLossModel | secondsEvaluateLossModel | Float |  | etx | IT IS THE NOMINAL TIME BETWEEN RE-EVALUATIONS OF PENALTY FACTORS FROM HISTORICAL LOSS MODEL IF RTNET HAS NOT EXECUTED. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Evaluate Loss Model
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsJointAGCStall | secondsJointAGCStall | Float |  | etx | Joint agc ACE stall check time threshold (in seconds). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Joint AGC Stall
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsMaximumTimeCorrection | secondsMaximumTimeCorrection | Float |  | etx | The maximum amount of auto time error correction allowed (SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Maximum Time Correction
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsMinimumEcoDispatch | secondsMinimumEcoDispatch | Float |  | etx | MINIMUM TIME PERIOD ALLOWED BETWEEN ECONOMIC DISPATCH EXECUTIONS.(AGC) (EG: 10 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Minimum Eco Dispatch
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsMinStudyEcoDispatch | secondsMinimumStudyEcoDispatch | Float |  | etx | MINIMUM TIME BETWEEN STUDY ED EXECUTIONS (SEC) (EG: 20 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Minimum Study Eco Dispatch
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsPauseThenSuspend | secondsPauseThenSuspend | Integer |  | etx | NOMINAL TIME FOR AGC PAUSE BEFORE SUSPEND IF NECESSARY (EG: 20 SEC). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Pause Then Suspend
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsPrediction | secondsPrediction | Float |  | etx | PREDICTED TIME IN SEC FROM TNOW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Prediction
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsProductionCosting | secondsProductionCosting | Float |  | etx | nominal value for the periodicity of the production costing module in seconds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Production Costing
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsRegulationAllocation | secondsRegulationAllocation | Float |  | etx | Regulation Allocation limit period (in sec). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Reulation Allocation
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsReserveCalculations | secondsReserveCalculations | Integer |  | etx | NOMINAL TIME TO PERFORM RESERVE CALCULATIONS (SEC) (AGC ONLY) (EG: 20 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Reserve Calculations
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsStudyEcoDispatch | secondsStudyEcoDispatch | Float |  | etx | NOMINAL STUDY ED RATE (SEC) (EG: 600 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Study Eco Dispatch
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsTimeErrorAlarm | secondsTimeErrorAlarm | Float |  | etx | TIME ERROR ALARM LIMIT IN SECONDS (EG: 2 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Time Error Alarm
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsUnitNotTrackingTest | secondsUnitNotTrackingTest | Float |  | etx | NOM TIME TO RUN UNIT NOT TRACKING TEST (SEC) (AGC ONLY) (EG: 120 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Unit Not Tracking Test
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsZeroAssist | secondsZeroAssist | Float |  | etx | THRESHOLD TIME FOR ASSIST REGION IN SECONDS SINCE LAST ZERO CROSSING. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Zero Assist
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsZeroEmergency | secondsZeroEmergency | Float |  | etx | THRESHOLD TIME FOR EMERGENCY REGION IN SECONDS SINCE LAST ZERO CROSSING. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Zero Emergency
|  | EnergyScheduling | HostControlArea | HostControlArea | secondsZeroNormal | secondsZeroNormal | Float |  | etx | THRESHOLD TIME FOR NORMAL REGION IN SECONDS SINCE LAST ZERO CROSSING. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Seconds Zero Normal
|  | EnergyScheduling | HostControlArea | HostControlArea | tauFilterLoad | tauFilterLoad | Float |  | etx | TIME CONSTANT FOR FILTERING LOAD (SECS). (EG: 40 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tau Filter Load
|  | EnergyScheduling | HostControlArea | HostControlArea | tauFrequency | tauFrequency | Float |  | etx | AREA FREQUENCY TIME CONSTANT (SECS) (EG: 10 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tau Frequency
|  | EnergyScheduling | HostControlArea | HostControlArea | tauLongTerm | tauLongTerm | Float |  | etx | UNIT LONG TERM ACCOUNT (PULSE CALIBRATION) TIME CONSTANT (SEC) (AGC) (EG: CORRESP TO 1 DAY = 24*3600 = 86400 SEC). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tau Long Term
|  | EnergyScheduling | HostControlArea | HostControlArea | tauRegulating | tauRegulating | Float |  | etx | REGULATING (AREA CONTROL) TIME CONSTANT (SEC) (E.G. 30 SEC) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tau Regulating
|  | EnergyScheduling | HostControlArea | HostControlArea | tauShortTerm | tauShortTerm | Float |  | etx | UNIT SHORT TERM ACCOUNT (NOT TRACKING TEST) TIME CONSTANT (SEC) (AGC) (EG: 300 SEC). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tau Short Term
|  | EnergyScheduling | HostControlArea | HostControlArea | timeErrorBias | timeErrorBias | Float |  | etx | (HZ/SEC) ACE EQUATION VARIABLE LITTLE B: AUTOMATIC TIME ERROR CORRECTION BIAS VALUE. * ENTER ABSOLUTE VALUE: NEGATION DONE IN THE CODE. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Time Error Bias
|  | EnergyScheduling | HostControlArea | HostControlArea | triggerControlEcoDispatchMW | triggerControlEcoDispatchMW | Float |  | etx | MW CHANGE TO TRIGGER CONTROL ED EXECUTION (EG: 25MW) (AGC ONLY) | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Trigger Control Eco Dispatch MW
|  | EnergyScheduling | HostControlArea | HostControlArea | triggerStudyEcoDispatchMW | triggerStudyEcoDispatchMW | Float |  | etx | MW CHANGE TO TRIGGER STUDY ED EXECUTION (EG: 50MW) (AGC ONLY). | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Trigger Study Eco Dispatch MW
|  | EnergyScheduling | HostControlArea | HostControlArea | variableFrequencyBiasMaximum | variableFrequencyBiasMaximum | Float |  | etx | Variable frequency bias high limit in MW/0.1 Hz. Must be greater or equal to VFBMIN_OPA. Enterable offline. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Variable Frequency Bias Maximum
|  | EnergyScheduling | HostControlArea | HostControlArea | variableFrequencyBiasMinimum | variableFrequencyBiasMinimum | Float |  | etx | Variable frequency bias low limit in MW/0.1 Hz. Must be less or equal to VFBMAX_OPA. Enterable offline. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Variable Frequency Bias Minimum
|  | ETX | Address | Address | City | City | String500 |  | etx | City | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | City
|  | ETX | Address | Address | County | County | String500 |  | etx | County | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | County
|  | ETX | Address | Address | PostalCode | PostalCode | String500 |  | etx | Postal Code | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Postal Code
|  | ETX | Address | Address | State | State | String500 |  | etx | State | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | State
|  | ETX | Address | Address | Street1 | Street1 | String500 |  | etx | Street | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Street 1
|  | ETX | Address | Address | Street2 | Street2 | String500 |  | etx | Street continued | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Street 2
|  | ETX | AggregateHub | AggregateHub | hubCalculationMethod | hubCalculationMethod | EnumHubCalcType |  | etx | Hub calculation method. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Hub Calculation Method
|  | ETX | AncillaryQualification | AncillaryQualification | blackStart | blackStart | Boolean | FALSE | etx | Black start.. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Black Start
|  | ETX | AncillaryQualification | AncillaryQualification | blackStartEffectiveDate | blackStartEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (black start)
|  | ETX | AncillaryQualification | AncillaryQualification | blackStartEndDate | blackStartEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (black start)
|  | ETX | AncillaryQualification | AncillaryQualification | ccEffectiveDate | ccEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (condensor capable)
|  | ETX | AncillaryQualification | AncillaryQualification | ccEndDate | ccEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (condensor capabile)
|  | ETX | AncillaryQualification | AncillaryQualification | condensorCapable | condensorCapable | Boolean | FALSE | etx | Condensor capable. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Condensor Capable
|  | ETX | AncillaryQualification | AncillaryQualification | dynamicSched | dynamicSched | Boolean | FALSE | etx | Dynamic scheduled. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Dynamic Scheduled
|  | ETX | AncillaryQualification | AncillaryQualification | dynamicSchedEffectiveDate | dynamicSchedEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (dynamic sched)
|  | ETX | AncillaryQualification | AncillaryQualification | dynamicSchedEndDate | dynamicSchedEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (dynamic sched)
|  | ETX | AncillaryQualification | AncillaryQualification | emergencyQse | emergencyQse | Boolean | FALSE | etx | Emergency qse. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Emergency Qse
|  | ETX | AncillaryQualification | AncillaryQualification | emergencyQseEffectiveDate | emergencyQseEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (emergency qse)
|  | ETX | AncillaryQualification | AncillaryQualification | emergencyQseEndDate | emergencyQseEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (emergency qse)
|  | ETX | AncillaryQualification | AncillaryQualification | nonSpin | nonSpin | Boolean | FALSE | etx | Non spin. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Non Spin
|  | ETX | AncillaryQualification | AncillaryQualification | nonSpinEffectiveDate | nonSpinEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (non-spin)
|  | ETX | AncillaryQualification | AncillaryQualification | nonSpinEndDate | nonSpinEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (non-spin)
|  | ETX | AncillaryQualification | AncillaryQualification | regDown | regDown | Boolean | FALSE | etx | Regulation down ancillary service. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reg Down
|  | ETX | AncillaryQualification | AncillaryQualification | regDownEffectiveDate | regDownEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (down)
|  | ETX | AncillaryQualification | AncillaryQualification | regDownEndDate | regDownEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (down)
|  | ETX | AncillaryQualification | AncillaryQualification | regUp | regUp | Boolean | FALSE | etx | Regulation up ancillary service. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reg Up
|  | ETX | AncillaryQualification | AncillaryQualification | regUpEffectiveDate | regUpEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (up)
|  | ETX | AncillaryQualification | AncillaryQualification | regUpEndDate | regUpEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (up)
|  | ETX | AncillaryQualification | AncillaryQualification | rmr | rmr | Boolean | FALSE | etx | RMR. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | RMR
|  | ETX | AncillaryQualification | AncillaryQualification | rmrEffectiveDate | rmrEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (rmr)
|  | ETX | AncillaryQualification | AncillaryQualification | rmrEndDate | rmrEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (rmr)
|  | ETX | AncillaryQualification | AncillaryQualification | rrs | rrs | Boolean | FALSE | etx | Responsive reserve service. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Responsive Reserve Service
|  | ETX | AncillaryQualification | AncillaryQualification | rrsUpEffectiveDate | rrsUpEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (rrs)
|  | ETX | AncillaryQualification | AncillaryQualification | rrsUpEndDate | rrsUpEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (rrs)
|  | ETX | AncillaryQualification | AncillaryQualification | ufr | ufr | Boolean | FALSE | etx | ufr. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | ufr
|  | ETX | AncillaryQualification | AncillaryQualification | ufrEffectiveDate | ufrEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (ufr)
|  | ETX | AncillaryQualification | AncillaryQualification | ufrEndDate | ufrEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (ufr)
|  | ETX | AncillaryQualification | AncillaryQualification | virtualQse | virtualQse | Boolean | FALSE | etx | Virtual Qse. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Virtual Qse
|  | ETX | AncillaryQualification | AncillaryQualification | virtualQseEffectiveDate | virtualQseEffectiveDate | Date |  | etx | Effective date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Effective date (virtual qse)
|  | ETX | AncillaryQualification | AncillaryQualification | virtualQseEndDate | virtualQseEndDate | Date |  | etx | End date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End date (virtual qse)
|  | ETX | Configuration | Configuration | coldStartTime | coldStartTime | Float |  | etx | Cold start time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Cold start time
|  | ETX | Configuration | Configuration | highReasonabilityLimit | highReasonabilityLimit | ActivePower |  | etx | High reasonability limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | High Reasonability Limit
|  | ETX | Configuration | Configuration | highRsnbltyRampRateLimit | highReasonabilityRampRateLimit | ActivePower |  | etx | High reasonability ramp rate limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | High Reasonability Ramp Rate Limit
|  | ETX | Configuration | Configuration | hotintTime | hotintTime | Float |  | etx | Hot-to-intermediate time (Seasonal). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Hot-to-intermediate time - Seasonal
|  | ETX | Configuration | Configuration | hotStartTime | hotStartTime | Float |  | etx | Hot start time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Hot start time
|  | ETX | Configuration | Configuration | intColdTime | intColdTime | Float |  | etx | Intermediate-to-cold time (Seasonal). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Intermediate-to-cold time - Seasonal
|  | ETX | Configuration | Configuration | intStartTime | intStartTime | Float |  | etx | Intermediate start time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Intermediate start time
|  | ETX | Configuration | Configuration | lowReasonabilityLimit | lowReasonabilityLimit | ActivePower |  | etx | Low reasonability limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Low Reasonability Limit
|  | ETX | Configuration | Configuration | lowRsnbltyRampRateLimit | lowReasonabilityRampRateLimit | ActivePower |  | etx | Low reasonability ramp rate limit. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Low Reasonability Ramp Rate Limit
|  | ETX | Configuration | Configuration | maxDailyStarts | maxDailyStarts | Float |  | etx | Maximum daily starts (seasonal parameter). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum daily starts - Seasonal
|  | ETX | Configuration | Configuration | maxONTime | maxONTime | Float |  | etx | Maximum On-Line time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum On-Line time
|  | ETX | Configuration | Configuration | maxWeeklyEnergy | maxWeeklyEnergy | Float |  | etx | Maximum weekly energy (seasonal parameter). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum weekly energy - Seasonal
|  | ETX | Configuration | Configuration | maxWeeklyStarts | maxWeeklyStarts | Float |  | etx | Maximum weekly starts (seasonal parameter). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum weekly starts - Seasonal
|  | ETX | Configuration | Configuration | minOFFTime | minOFFTime | Float |  | etx | Minimum Off-Line time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Off-Line time
|  | ETX | Configuration | Configuration | minONTime | minONTime | Float |  | etx | Minimum On-Line time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum On-Line time
|  | ETX | Configuration | Configuration | primaryConfiguration | primaryConfiguration | Boolean | FALSE | etx | Primary configuration? | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Primary Configuration
|  | ETX | Configuration | Configuration | qualificationStatus | qualificationStatus | Boolean | FALSE | etx | Qualification status. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Qualification Status
|  | ETX | Configuration | Configuration | seasonalMaxEmergencyRating | seasonalMaxEmergencyRating | ActivePower |  | etx | Seasonal maximum emergency rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Max Emergency Rating
|  | ETX | Configuration | Configuration | seasonalMaxSustainableRating | seasonalMaxSustainableRating | ActivePower |  | etx | Seasonal maximum sustainable rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Max Sustainable Rating
|  | ETX | Configuration | Configuration | seasonalMinEmergencyRating | seasonalMinEmergencyRating | ActivePower |  | etx | Seasonal minimum emergency rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Min Emergency Rating
|  | ETX | Configuration | Configuration | seasonalMinSustainableRating | seasonalMinSustainableRating | ActivePower |  | etx | Seasonal minimum sustainable rating. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Seasonal Min Sustainable Rating
|  | ETX | Configuration | Configuration | ShutdownFlag | ShutdownFlag | Boolean | FALSE | etx | Whether Combined Cycle Plant can be shut-down in this Logical Configuration? | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Shutdown Flag
|  | ETX | Configuration | Configuration | StartupFlag | StartupFlag | Boolean | FALSE | etx | Whether Combined Cycle Plant can be started in this Logical Configuration? | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Startup Flag
|  | ETX | ConfigurationMember | ConfigurationMember | primary | primary | Boolean | FALSE | etx | primary configuration. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Primary Configuration?
|  | ETX | ConfigurationMember | ConfigurationMember | steam | steam | Boolean | FALSE | etx | Steam plant. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Steam Plant?
|  | ETX | Contact | Contact | EmailAddress | EmailAddress | String500 |  | etx | Email Address | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Email Address
|  | ETX | Contact | Contact | FirstName | FirstName | String500 |  | etx | First Name. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | First Name
|  | ETX | Contact | Contact | LastName | LastName | String500 |  | etx | Last Name | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Last Name
|  | ETX | Contact | Contact | PrimaryPhone | PrimaryPhone | String20 | (999) 999-9999 x____ | etx | Primary Phone number for contact. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Primary Phone
|  | ETX | Contact | Contact | SecondaryPhone | SecondaryPhone | String20 | (999) 999-9999 x____ | etx | Secondary Phone number for contact. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Secondary Phone
|  | ETX | ControllableLoadResource | ControllableLoadResource | maxDeploymentTime | maxDeploymentTime | Float |  | etx | Maximum deployment time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Deployment Time
|  | ETX | ControllableLoadResource | ControllableLoadResource | maxWeeklyEnergy | maxWeeklyEnergy | Float |  | etx | Maximum weekly Energy. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Weekly Energy
|  | ETX | ControllableLoadResource | ControllableLoadResource | minNoticeTime | minNoticeTime | Float |  | etx | Minimum Notice time (seconds). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Notice time (seconds)
|  | ETX | ControllableLoadResource | ControllableLoadResource | rampRateSlopeDownLimit | rampRateSlopeDownLimit | Float |  | etx | Reasonability Limit for DOWN Ramp Rate. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Reasonability Limit for DOWN Ramp Rate
|  | ETX | ControllableLoadResource | ControllableLoadResource | rampRateSlopeUpLimit | rampRateSlopeUpLimit | Float |  | etx | Reasonability Limit for UP Ramp Rate. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Reasonability Limit for UP Ramp Rate
|  | ETX | DCTie | DCTie | DCTieLZName | DCTieLZName | String12 |  | etx | DC Tie Zone name for DC tie. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | DC Tie Zone name for DC tie
|  | ETX | ElectricalBus | ElectricalBus | DisplayLMP | DisplayLMP | Boolean | TRUE | etx | Display LMP? | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Display LMP
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | blockLoadTransfer | blockLoadTransfer | Boolean | FALSE | etx | Block load transfer. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Block Load Transfer
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | commercialOperationsDate | commercialOperationsDate | Date |  | etx | Date commercial operations started. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Commercial Operations Date
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | loadFreqBias | loadFreqBias | Float |  | etx | Regulating Frequency Bias as MW per 0.1 Hz. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | loadFreqBias
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | loadFreqDevDeadband | loadFreqDevDeadband | Float |  | etx | Frequency deviation deadband for Feed-Forward correction (in Hz). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | loadFreqDevDeadband
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | loadId | loadId | String14 |  | etx | A 14 character load ID used in ERCOT LFC. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | loadId
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | loadSubStationId | loadSubStationId | String8 |  | etx | ID of load's substation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | loadSubStationId
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | maxDailyDeployment | maxDailyDeployment | Float |  | etx | Maximum daily deployments. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Daily Deployments
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | maxInterruptionTime | maxInterruptionTime | Float |  | etx | Maximum interruption time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Interruption Time
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | MaxPowerConsumption | MaxPowerConsumption | Float |  | etx | Maximum power consumption for resource. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Power Consumption
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | maxWeeklyDeployment | maxWeeklyDeployment | Float |  | etx | Maximum weekly deployments. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Weekly Deployments
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | minInterruptionTime | minInterruptionTime | Float |  | etx | Minimum interruption time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Interruption Time
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | MinPowerConsumption | MinPowerConsumption | Float |  | etx | Minimum power consumption for resource. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Power Consumption
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | minRestorationTime | minRestorationTime | Float |  | etx | Minimum restoration time. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Restoration Time
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | qualificationStatus | qualificationStatus | Boolean | FALSE | etx | Qualification status. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Qualification Status
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | RelayType | RelayType | EnumRelayType |  | etx | Type of relay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Relay Type
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | resourceCategory | resourceCategory | String50 |  | etx | Type of resource. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Type of Resource
|  | ETX | EnergyConsumerResource | EnergyConsumerResource | wfrmcr | wfrmcr | Boolean | FALSE | etx | wfrmcr. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | wfrmcr
|  | ETX | EPSMeter | EPSMeter | AcceptedStatus | AcceptedStatus | Bool | FALSE | etx | EPS meter location has been accepted by settlements. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Accepted Status
|  | ETX | EPSMeter | EPSMeter | RID | RID | String100 |  | etx | Resource number for EPS meter Identifier. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Resource ID
|  | ETX | EPSMeter | EPSMeter | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
|  | ETX | ERCOTVersion | ERCOTVersion | ContactEmail | ContactEmail | String30 | jmoseley@ercot.com | etx | Contact Email. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Contact Email
|  | ETX | ERCOTVersion | ERCOTVersion | ContactPhoneNumber | ContactPhoneNumber | String14 | (512)248-6362 | etx | Contact Phone Number. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Contact Phone Number
|  | ETX | ERCOTVersion | ERCOTVersion | date | date | String30 | 2008-08-11 | etx | Date. | FALSE | TRUE | TRUE | TRUE |  | FALSE |  | TRUE |  |  | date
|  | ETX | ERCOTVersion | ERCOTVersion | ModelAdmin | ModelAdmin | String30 | John Moseley | etx | Model Administrator. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Model Administrator
|  | ETX | ERCOTVersion | ERCOTVersion | version | version | String30 | ERCOT 1.20 | etx | Version. | FALSE | TRUE | TRUE | TRUE |  | FALSE |  | TRUE |  |  | version
|  | ETX | FlowgateElement | FlowgateElement | biddable | biddable | Boolean | FALSE | etx | Biddable. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Biddable
|  | ETX | FlowgateElement | FlowgateElement | endDate | endDate | Date |  | etx | End Date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | End Date
|  | ETX | FlowgateElement | FlowgateElement | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a BranchGroup. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
|  | ETX | FlowgateElement | FlowgateElement | monitored | monitored | Boolean | FALSE | etx | Monitored. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Monitored
|  | ETX | FlowgateElement | FlowgateElement | positiveFlowIn | positiveFlowIn | Boolean | TRUE | etx | Determines metered direction of EPS meter. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Positive Flow In
|  | ETX | FlowgateElement | FlowgateElement | principleElement | principleElement | Boolean | FALSE | etx | Principle element? | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Principle Element
|  | ETX | FlowgateElement | FlowgateElement | rating | rating | DoubleFloat |  | etx | Rating. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Rating
|  | ETX | FlowgateElement | FlowgateElement | startDate | startDate | Date |  | etx | Start Date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Start Date
|  | ETX | FlowgateGroup | FlowgateGroup | defaultLimit | defaultLimit | DoubleFloat |  | etx | Default limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Default Limit
|  | ETX | FlowgateGroup | FlowgateGroup | infB | infB | Float |  | etx | Impact Normalization Factor for Base Case. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 1 | 0 | infB
|  | ETX | FlowgateGroup | FlowgateGroup | infC | infC | Float |  | etx | Impact Normalization Factor for Contingency. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 1 | 0 | infC
|  | ETX | FlowgateGroup | FlowgateGroup | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a BranchGroup. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
|  | ETX | FlowgateGroup | FlowgateGroup | rating | rating | Float |  | etx | Flowgate Group Rating. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | rating
|  | ETX | FlowgateGroup | FlowgateGroup | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
|  | ETX | FlowgateGroup | FlowgateGroup | thermalLimit | thermalLimit | Boolean | FALSE | etx | Is thermal limit? | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Thermal Limit
|  | ETX | IccpQualityConversion | IccpQualityConversion | ICalculated | ICalculated | Boolean | FALSE | etx | I... calculated. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ICalculated
|  | ETX | IccpQualityConversion | IccpQualityConversion | IEstimated | IEstimated | Boolean | FALSE | etx | I... estimated. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | IEstimated
|  | ETX | IccpQualityConversion | IccpQualityConversion | IHeld | IHeld | Boolean | FALSE | etx | I... held. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | IHeld
|  | ETX | IccpQualityConversion | IccpQualityConversion | IManual | IManual | Boolean | FALSE | etx | I... manual. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | IManual
|  | ETX | IccpQualityConversion | IccpQualityConversion | INotValid | INotValid | Boolean | FALSE | etx | I... not valid. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | INotValid
|  | ETX | IccpQualityConversion | IccpQualityConversion | ISuspect | ISuspect | Boolean | FALSE | etx | I... suspect. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ISuspect
|  | ETX | IccpQualityConversion | IccpQualityConversion | ITelemetered | ITelemetered | Boolean | FALSE | etx | I... telemetered. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ITelemetered
|  | ETX | IccpQualityConversion | IccpQualityConversion | IValid | IValid | Boolean | FALSE | etx | I... valid. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | IValid
|  | ETX | IccpQualityConversion | IccpQualityConversion | OCalculated | OCalculated | Boolean | FALSE | etx | O... calculated. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OCalculated
|  | ETX | IccpQualityConversion | IccpQualityConversion | OEstimated | OEstimated | Boolean | FALSE | etx | O... estimated. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OEstimated
|  | ETX | IccpQualityConversion | IccpQualityConversion | OHeld | OHeld | Boolean | FALSE | etx | O... held. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OHeld
|  | ETX | IccpQualityConversion | IccpQualityConversion | OManual | OManual | Boolean | FALSE | etx | O... manual. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OManual
|  | ETX | IccpQualityConversion | IccpQualityConversion | ONotValid | ONotValid | Boolean | FALSE | etx | O... not valid. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ONotValid
|  | ETX | IccpQualityConversion | IccpQualityConversion | OSuspect | OSuspect | Boolean | FALSE | etx | O... suspect. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OSuspect
|  | ETX | IccpQualityConversion | IccpQualityConversion | OTelemetered | OTelemetered | Boolean | FALSE | etx | O... telemetered. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OTelemetered
|  | ETX | IccpQualityConversion | IccpQualityConversion | OValid | OValid | Boolean | FALSE | etx | O... valid. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | OValid
|  | ETX | LoadResource | LoadResource | maxWeeklyEnergy | maxWeeklyEnergy | Float |  | etx | Maximum weekly Energy. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Weekly Energy
|  | ETX | LoadResource | LoadResource | minNoticeTime | minNoticeTime | Float |  | etx | Minimum Notice time (seconds). | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Notice time (seconds)
|  | ETX | ModelBuild | ModelBuild | ModelBuilder | ModelBuilder | String30 |  | etx | Model Builder. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Model Builder
|  | ETX | ModelBuild | ModelBuild | ModelBuildTime | ModelBuildTime | String30 |  | etx | Model Build Time. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Model Build Time
|  | ETX | ModelBuild | ModelBuild | ModelDescription | ModelDescription | String100 |  | etx | Model Description. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Model Description
|  | ETX | ModelBuild | ModelBuild | ModelProfile | ModelProfile | String30 |  | etx | Model Profile. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Model Profile
|  | ETX | ModelBuild | ModelBuild | ValidDateRange | ValidDateRange | String30 |  | etx | Valid Date. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Valid Date Range
|  | ETX | Operatorship | Operatorship | operatePercent | operatePercent | Float |  | etx | Operator share percentage. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Operate Percent
|  | ETX | Ownership | Ownership | ownPercent | ownPercent | Float |  | etx | Owner share percentage. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Own Percent
|  | ETX | Ownership | Ownership | penaltyFactor | penaltyFactor | Float |  | etx | User entered penalty factor for loss calculations. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Penalty Factor
|  | ETX | Ownership | Ownership | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
|  | ETX | PricingVector | PricingVector | positiveFlowIn | positiveFlowIn | Boolean | TRUE | etx | Determines metered direction of EPS meter. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Positive Flow In
|  | ETX | PricingVector | PricingVector | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
|  | ETX | PrivateAreaNetwork | PrivateAreaNetwork | networkType | networkType | EnumPANType |  | etx | Type of Private Use Network. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Type of Private Use Network
|  | ETX | SettlementLoadZone | SettlementLoadZone | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number Alternate Areas and Zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
|  | ETX | SettlementNOIELoadZone | SettlementNOIELoadZone | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number Alternate Areas and Zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
|  | ETX | SupportLoadData | SupportLoadData | p | p | DoubleFloat |  | etx | motor p. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | motor p
|  | ETX | SupportLoadData | SupportLoadData | percentageFlag | percentageFlag | Boolean |  | etx | percentage flag | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | percentage flag
|  | ETX | SupportLoadData | SupportLoadData | q | q | DoubleFloat |  | etx | motor q. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | motor q
|  | ETX | SupportLoadData | SupportLoadData | r | r | DoubleFloat |  | etx | motor r. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | motor r
|  | ETX | SupportLoadData | SupportLoadData | rating | rating | DoubleFloat |  | etx | motor rating. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | motor rating
|  | ETX | SupportLoadData | SupportLoadData | ratiotransformer | ratiotransformer | DoubleFloat |  | etx | ratio transformer. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | ratio transformer
|  | ETX | SupportLoadData | SupportLoadData | rtransformer | rtransformer | Float |  | etx | stepup transformer r. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | stepup transformer r
|  | ETX | SupportLoadData | SupportLoadData | varhighlimit | varhighlimit | Float |  | etx | motor var high limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | motor var high limit
|  | ETX | SupportLoadData | SupportLoadData | varlowlimit | varlowlimit | Float |  | etx | motor var low limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | motor var low limit
|  | ETX | SupportLoadData | SupportLoadData | x | x | DoubleFloat |  | etx | motor x. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | motor x
|  | ETX | SupportLoadData | SupportLoadData | xtransformer | xtransformer | Float |  | etx | stepup transformer x. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | stepup transformer x
|  | ETX | TransformerKluge | TransformerKluge | PSSE3WinderID | PSSE3WinderID | String2 |  | etx | Attribute will be used to store the three winding transformer ID and Mark which transformers are to be grouped as three winding Transformers. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | PSS/E 3 Winding ID
|  | ETX | TransformerKluge | TransformerKluge | PSSE3Windername | PSSE3Windername | String12 |  | etx | Attribute will be used to store the three winding transformer name. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | PSS/E 3 Winding Name
|  | ETX | TransState | TransState | upTransition | upTransition | Boolean | FALSE | cim | Flag indicating whether this is an UP transition or DOWN transition. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Up Transition?
|  | ETX_ABB | LimitLogicType | LimitLogicType | postContLimitType | postContLimitType | EnumPostContLimitType |  | etx | Post Cont Limit Type | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Post-Cont Limit Type
|  | ETX_ABB | LimitLogicType | LimitLogicType | preContLimitType | preContLimitType | EnumPreContLimitType |  | etx | Pre-Cont Limit Type | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Pre-Cont Limit Type
|  | ETX_Areva | RampRateCurve | RampRateCurve | Emergency | Emergency | Boolean | FALSE | etx | Denote the type of ramp rate. | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Emergency
|  | ETX_Areva | RampRateCurve | RampRateCurve | rampRateCurveId | rampRateCurveId | String5 |  | etx | Ramp Rate Curve ID. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Ramp Rate Curve ID
|  | ETX_Areva | ResourceController | ResourceController | externalJointUnit | externalJointUnit | Boolean | FALSE | etx | external Joint Unit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | external Joint Unit
|  | ETX_Areva | ResourceController | ResourceController | frequencyBias | frequencyBias | Float |  | etx | Frequency bias. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Frequency Bias
|  | ETX_Areva | ResourceController | ResourceController | gross | gross | Boolean | FALSE | etx | Gross. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Gross
|  | ETX_Areva | ResourceController | ResourceController | jointUnit | jointUnit | Boolean | FALSE | etx | joint Unit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | joint Unit
|  | ETX_Areva | ResourceController | ResourceController | physical | physical | Boolean | FALSE | etx | physical. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | physical
|  | ETX_Areva | TieCorridor | TieCorridor | maxInflowLimit | maxInflowLimit | Float |  | etx | Maximum MW inflow alarm limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MW Inflow Alarm Limit
|  | ETX_Areva | TieCorridor | TieCorridor | maxOutflowLimit | maxOutflowLimit | Float |  | etx | Maximum MW outflow alarm limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MW Outflow Alarm Limit
|  | ETX_Areva | TieCorridor | TieCorridor | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
|  | ETX_Areva | TieCorridor | TieCorridor | tieId | tieId | String14 |  | etx | ID of Tie/ | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Tie ID
|  | ETX_Areva | TieCorridor | TieCorridor | tieIsInternal | tieIsInternal | Boolean | FALSE | etx | True if Tie is internal. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Tie Is Internal?
|  | ETX_Areva | TieEnd | TieEnd | participationFactorJointAGC | participationFactorJointAGC | Float |  | etx | Joint AGC participation factor. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Participation Factor Joint AGC
|  | ETX_Areva | TieEnd | TieEnd | percentChangeAlarm | percentChangeAlarm | Float |  | etx | TiePointEnd MW STEP CHANGE ALARM LEVEL (% OF maximuInMW of TiePointEnd) (EG: 10%) (AGC ONLY). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | percentChangeAlarm
|  | ETX_Areva | TieEnd | TieEnd | priorityJointAGC | priorityJointAGC | Integer |  | etx | Joint AGC priority level. Lowest numbered ties will be used first. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Priority Joint AGC
|  | ETX_Areva | TieEnd | TieEnd | tauJointAGCLoadFollowing | tauJointAGCLoadFollowing | Float |  | etx | Time constant for filtering joint AGC load following component (requester only).. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Tau Joint AGC Load Following
|  | ETX_Areva | TieLine | TieLine | isATransLine | isATransLine | Boolean | FALSE | etx | True for transmission line, false for transformer. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Is a Transmission Line?
|  | ETX_Areva | TieLine | TieLine | measAtNearEnd | measAtNearEnd | Boolean | FALSE | etx | TRUE - USE THE MEASUREMENT AT THE NEAR END OF THE LINE FALSE - USE THE MEASUREMENT AT THE FAR END OF THE LINE. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Measurement at Near End?
|  | ETX_Areva | TieLine | TieLine | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
|  | ETXContingency | ContingencyElement | ContingencyElement | cbFault | cbFault | Boolean | FALSE | etx | Indicates TRUE if this CB is included in post contingency and related to CB fault due to the dynamic redefinition logic. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | CB Fault
|  | ETXContingency | ContingencyElement | ContingencyElement | status | status | Boolean | TRUE | etx | The status of contingency element, i.e. Open/Close for Switch, Removed or not for other conducting equipment. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Status
|  | ETXContingency | ContingencyGroup | ContingencyGroup | maintainSubSystems | maintainSubSystems | Boolean | TRUE | etx | This field sets whether the subsystems for the contingencies in this CTGGroup are maintained even though the group is inactive. When Maintain Subsystems set ON, and Study is set OFF, CA maintains the contingency local subsystems for base case changes. If Maintain Subsystems is set OFF and Study is set OFF, the subsystems are deleted. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maintain Sub Systems
|  | ETXContingency | ContingencyGroup | ContingencyGroup | study | study | Boolean | TRUE | etx | T=activate the contigencies in the group. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Study
|  | ETXLoadModel | EnergyConsumerAltConnection | EnergyConsumerAltConnection | percentTransfer | percentTransfer | Float |  | etx | Percentage of load transferred from parent load to target load. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Percent Transfer
|  | ETXLoadModel | LoadType | LoadType | expPFrequency | expPFrequency | Float |  | etx | Load watts are proportional to (V**WVEXP)*(F**WFEXP). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | exp P Frequency
|  | ETXLoadModel | LoadType | LoadType | expPVoltage | expPVoltage | Float |  | etx | Exp P Voltage. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | exp P Voltage
|  | ETXLoadModel | LoadType | LoadType | expQFrequency | expQFrequency | Float |  | etx | Load vars are proportional to (V**RVEXP)*(F**RFEXP). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | exp Q Frequency
|  | ETXLoadModel | LoadType | LoadType | expQVoltage | expQVoltage | Float |  | etx | Exp Q Voltage. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | exp Q Voltage
|  | ETXLoadModel | LoadType | LoadType | initialTime | initialTime | Integer |  | etx | The initial time on the cooling characteristic in seconds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Initial Time
|  | ETXLoadModel | LoadType | LoadType | maxScaling | maxScaling | Float |  | etx | The maximum value that the load could be scaled by upon its reconection. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum Scaling
|  | ETXMonitoring | BranchGroup | BranchGroup | maximumActivePower | maximumActivePower | Float |  | etx | Maximum active power. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Active Power
DD-1.21.1-001 | DELETE | ETXMonitoring | BranchGroup | BranchGroup | maximumMVAr | maximumMVAr | Float |  | etx | Maximum MVAr | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Maximum MVAr
DD-1.21.1-001 | DELETE | ETXMonitoring | BranchGroup | BranchGroup | maximumMW | maximumMW | Float |  | etx | Maximum MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Maximum MW
|  | ETXMonitoring | BranchGroup | BranchGroup | maximumReactivePower | maximumReactivePower | Float |  | etx | Maximum reactive power | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Maximum Reactive Power
|  | ETXMonitoring | BranchGroup | BranchGroup | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a BranchGroup. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
|  | ETXMonitoring | BranchGroup | BranchGroup | minimumActivePower | minimumActivePower | Float |  | etx | Minimum active power. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Minimum Active Power
DD-1.21.1-001 | DELETE | ETXMonitoring | BranchGroup | BranchGroup | minimumMVAr | minimumMVAr | Float |  | etx | Minimum MVAr. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Minimum MVAr
DD-1.21.1-001 | DELETE | ETXMonitoring | BranchGroup | BranchGroup | minimumMW | minimumMW | Float |  | etx | Minimum MW. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Minimum MW
|  | ETXMonitoring | BranchGroup | BranchGroup | minimumReactivePower | minimumReactivePower | Float |  | etx | Minimum reactive power. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Minimum Reactive Power
|  | ETXMonitoring | BranchGroup | BranchGroup | monitorActivePower | monitorActivePower | Boolean | FALSE | etx | Monitor active power. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Monitor Active Power
|  | ETXMonitoring | BranchGroup | BranchGroup | monitorReactivePower | monitorReactivePower | Boolean | FALSE | etx | Monitor reactive power. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Monitor Reactive Power
|  | ETXMonitoring | BranchGroup | BranchGroup | teid | teid | Integer |  | etx | Transmission Element ID. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE | 999999999 | 0 | Transmission Element ID
|  | ETXMonitoring | BranchGroupTerminal | BranchGroupTerminal | positiveFlowIn | positiveFlowIn | Boolean | FALSE | etx | Positive Flow In. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Positive Flow In
|  | ETXMonitoring | Monitored | Monitored | eligible | eligible | Boolean | FALSE | etx | Eligible. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Eligible
|  | ETXMonitoring | MonitoredGroup | MonitoredGroup | active | active | Boolean | FALSE | etx | Active. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Active
|  | ETXMonitoring | VoltageLimit | VoltageLimit | value | value | Float |  | etx | The value to supervise against. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value
|  | ETXNetwork | AccuracyClass | AccuracyClass | adConverterError | adConverterError | Float |  | etx | A to D converter error. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | ADConverterError
|  | ETXNetwork | AccuracyClass | AccuracyClass | addEntered | addEntered | Boolean | FALSE | etx | T = add the value in the Standard Deviation (per Unit) field to the calculated standard deviation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Add Entered
|  | ETXNetwork | AccuracyClass | AccuracyClass | base | base | Float |  | etx | Base value. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Base
|  | ETXNetwork | AccuracyClass | AccuracyClass | breakPoint | breakPoint | Float |  | etx | Break point for uncertainty model. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Break Point
|  | ETXNetwork | AccuracyClass | AccuracyClass | currentTransformerError | currentTransformerError | Float |  | etx | Current transformer error. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Current Transformer Error
|  | ETXNetwork | AccuracyClass | AccuracyClass | defaultAccuracy | defaultAccuracy | Boolean | FALSE | etx | T = it is a defaulted accuracy record or manually inserted accuracy record. Manually inserted accuracy record could be assigned to SCADA analog observation or other modeled loads (LDs) and units (UNs). The defaulted accuracy record is inserted by the NETV. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Default Accuracy
|  | ETXNetwork | AccuracyClass | AccuracyClass | standardDeviation | standardDeviation | Float |  | etx | Standard deviation for uncertainty model. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Standard Deviation
|  | ETXNetwork | AccuracyClass | AccuracyClass | transducerMaxError | transducerMaxError | Float |  | etx | Transducer maximum error. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Transducer Maximum Error
|  | ETXNetwork | AccuracyClass | AccuracyClass | useEntered | useEntered | Boolean | FALSE | etx | T = use the value in the Standard Deviation (per Unit) field as the standard deviation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Use Entered
|  | ETXNetwork | AccuracyClass | AccuracyClass | voltageTransformerError | voltageTransformerError | Float |  | etx | Voltage tranformer error. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Voltage Transformer Error
|  | ETXPlanning | ConnectivityNodeGroup | ConnectivityNodeGroup | PSSEBusName | PSSEBusName | String12 |  | etx | Store the PSS™E bus name that will be associated with the grouping of Connectivity Nodes in Option 2. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE |  |  | PSS/E Bus Name
|  | ETXPlanning | ConnectivityNodeGroup | ConnectivityNodeGroup | PSSEBusNumber | PSSEBusNumber | Integer |  | etx | Attribute will be used to store the PSS™E bus number that will be associated with the grouping of Connectivity Nodes in Option 2. | FALSE | FALSE | TRUE | FALSE |  | TRUE |  | TRUE |  |  | PSS/E Bus Number
|  | ETXPlanning | PlanningArea | PlanningArea | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number areas. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
|  | ETXPlanning | PlanningZone | PlanningZone | psseid | psseid | ShortInt |  | etx | Attribute will give IMM modelers control over the PSS®E ID that the Topology Processor uses to properly number zones. | FALSE | FALSE | FALSE | FALSE |  | TRUE |  | FALSE | 9999 | 0 | PSS®E ID
|  | ETXRASE | Gate | Gate | changeThreshold | changeThreshold | Boolean | FALSE | etx | Use change limit for voltages. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Change Threshold
|  | ETXRASE | Gate | Gate | emergencyThreshold | emergencyThreshold | Boolean | FALSE | etx | Use the branch emergency limit as threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Emergency Threshold
|  | ETXRASE | Gate | Gate | gatetype | gatetype | EnumGateType |  | etx | Gate Type. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Gate Type
|  | ETXRASE | Gate | Gate | level | level | Integer | 0 | etx | Level of the gate. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Level
|  | ETXRASE | Gate | Gate | limitPercentage | limitPercentage | Float |  | etx | Percentage of the limit. 90% should enter 90. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE | 100 | 0 | Limit Percentage
|  | ETXRASE | Gate | Gate | loadshedThreshold | loadshedThreshold | Boolean | FALSE | etx | Use the branch loadshed limit as threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Loadshed Threshold
|  | ETXRASE | Gate | Gate | lowerThreshold | lowerThreshold | Boolean | FALSE | etx | Use lower limit (for FlowSummation and voltage). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Lower Threshold
|  | ETXRASE | Gate | Gate | normalThreshold | normalThreshold | Boolean | FALSE | etx | Use the branch normal limit as threshold. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Normal Threshold
|  | ETXRASE | Gate | Gate | thresholdValue | thresholdValue | Float |  | etx | Threshold value for gate type of (GE,GT,LE,LT,NE,EQ) with single gate input | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Threshold Value
|  | ETXRASE | Gate | Gate | upperThreshold | upperThreshold | Boolean | FALSE | etx | Use upper limit (for FlowSummation and voltage). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Upper Threshold
|  | ETXRASE | Gate | Gate | useLimitThreshold | useLimitThreshold | Boolean | FALSE | etx | Use the branch limit as threashold value, otherwise use Gate::thresholdValue. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Use Limit Threshold
|  | ETXRASE | GateInputPin | GateInputPin | flowMVA | flowMVA | Boolean | FALSE | etx | If true the input is a MVA. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Flow MVA
|  | ETXRASE | GateInputPin | GateInputPin | flowMVAR | flowMVAR | Boolean | FALSE | etx | If true the input is a MVAR. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Flow MVAR
|  | ETXRASE | GateInputPin | GateInputPin | flowMW | flowMW | Boolean | FALSE | etx | If true, the input is a MW. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Flow MW
|  | ETXRASE | GateInputPin | GateInputPin | negate | negate | Boolean | FALSE | etx | If true, input is negated first and then input to the gate. only applicable to logical gates. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Negate
|  | ETXRASE | GateInputPin | GateInputPin | useAbsoluteValue | useAbsoluteValue | Boolean | FALSE | etx | Use absolute value of input (only applies to analog inputs). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Use Absolute Value
|  | ETXRASE | PinFlow | PinFlow | eitherEnd | eitherEnd | Boolean | FALSE | etx | True if doing status input on a branch and want to check if either end is out. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Either End
|  | ETXRASE | PinFlow | PinFlow | inputIsFlow | inputIsFlow | Boolean | FALSE | etx | If true, the input is a flow, otherwise it is branch status. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Input Is Flow
|  | ETXRASE | PinFlow | PinFlow | intoBus | intoBus | Boolean | FALSE | etx | Flow into the bus is positive. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Into Bus
|  | ETXRASE | PinFlow | PinFlow | outOfBus | outOfBus | Boolean | FALSE | etx | Flow out of the bus is positive. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Out of Bus
|  | ETXRASE | ProtActACLineSegment | ProtActACLineSegment | inService | inService | Boolean | FALSE | etx | If true the ACLineSegment is put in-service, otherwise out-of-service. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | In Service
|  | ETXRASE | ProtActAnalog | ProtActAnalog | actionValue | actionValue | Float |  | etx | The value to reduce to or by. Used if no value from SCADA. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Action Value
|  | ETXRASE | ProtActAnalog | ProtActAnalog | actionValueFromSCADA | actionValueFromSCADA | Boolean | FALSE | etx | True, the action value is obtained from SCADA otherwise from actionValue attribute. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Action Value From SCADA
|  | ETXRASE | ProtActAnalog | ProtActAnalog | isReduceTo | isReduceTo | Boolean | FALSE | etx | If true, action is a 'reduce to' otherwise it is a 'reduce by'. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Is Reduce To
|  | ETXRASE | ProtActSeriesCompensator | ProtActSeriesCompensator | inService | inService | Boolean | FALSE | etx | If true the SeriesCompensator is put in-service, otherwise out-of-service. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | In Service
|  | ETXRASE | ProtActSwitch | ProtActSwitch | closeAction | closeAction | Boolean | FALSE | etx | If true close the switch, otherwise open switch. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Close Action
|  | ETXRASE | ProtActTransformerWinding | ProtActTransformerWinding | inService | inService | Boolean | FALSE | etx | If true the Transformer is put in-service, otherwise out-of-service. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | In Service
|  | ETXRASE | ProtectiveAction | ProtectiveAction | enableArming | enableArming | Boolean | FALSE | etx | Enable arming. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Enable Arming
|  | ETXRASE | RemedialActionScheme | RemedialActionScheme | active | active | Boolean | FALSE | etx | User specified active. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Active
|  | ETXRASE | RemedialActionScheme | RemedialActionScheme | isRAP | isRAP | Boolean | FALSE | etx | This is a remedial action plan (RAP). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Is RAP
|  | ETXRASE | RemedialActionScheme | RemedialActionScheme | isRAS | isRAS | Boolean | FALSE | etx | This is a remedial action scheme (RAS). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Is RAS
|  | ETXRating | DynamicElement | DynamicElement | line | line | Boolean | FALSE | etx | True if the dynamic element is a line. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Line?
|  | ETXRating | DynamicElement | DynamicElement | transformer | transformer | Boolean | FALSE | etx | True if the dynamic element is a transformer. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Transformer?
|  | ETXRating | DynamicElement | DynamicElement | zeroImpBranch | zeroImpBranch | Boolean | FALSE | etx | True if the dynamic element is a zero impedance branch. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Zero Impedance Branch?
|  | ETXRating | OwnerShareLimits | OwnerShareLimits | highReasonabilityLimit | highReasonabilityLimit | ActivePower |  | etx | highReasonabilityLimit split based on the ownership percentage. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | High Reasonability Limit
|  | ETXRating | OwnerShareLimits | OwnerShareLimits | lowReasonabilityLimit | lowReasonabilityLimit | ActivePower |  | etx | lowReasonabilityLimit split based on the ownership percentage. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Low Reasonability Limit
|  | ETXRating | OwnerShareLimits | OwnerShareLimits | maxWeeklyEnergy | maxWeeklyEnergy | Float |  | etx | Maximum weekly energy (seasonal parameter) split based on the ownership percentage. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Maximum weekly energy (seasonal parameter)
|  | ETXRating | Rating | Rating | activateValue | activateValue | Float |  | etx | Temperature. It is used to pick the actual rating to supervise againist. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Activate Value
|  | ETXRating | Rating | Rating | ratingType | ratingType | EnumRatingType |  | etx | Rating type: static (planning) or dynamic (temperature). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Rating Type
|  | ETXRating | Rating | Rating | TempPoint | TempPoint | Integer |  | etx | Temperature Point index. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Temperature Point index
|  | ETXRating | WeatherStationAlt | WeatherStationAlt | DynamicAdder | DynamicAdder | Integer | 0 | etx | Dynamic adder. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Dynamic Adder
|  | ETXSCADA | AlternateLimit | AlternateLimit | highLimit | highLimit | Float |  | etx | High Limit: The threshold above which the analog is considered in violation of the limit. When the low limit is null, only the high limit is checked for violation. The High Limit must be greater then the Low Limit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | High Limit
|  | ETXSCADA | AlternateLimit | AlternateLimit | lowLimit | lowLimit | Float |  | etx | Low Limit: The threshold below which the analog is considered in violation of the limit. When the high limit is null, only the low limit is checked for violation. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | Low Limit
|  | ETXSCADA | Calculation | Calculation | type | type | String30 |  | etx | Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Type
|  | ETXSCADA | Calculation | Calculation | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temp Attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
|  | ETXSCADA | CalculationArgument | CalculationArgument | referenceFlag | referenceFlag | Boolean |  | etx | The Boolean flag to indicate this arguement is a reference. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reference Flag
|  | ETXSCADA | CalculationArgument | CalculationArgument | referenceName | referenceName | String4 |  | etx | If this is a Reference, name for the reference. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Reference Name
|  | ETXSCADA | CalculationArgument | CalculationArgument | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temporary attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
DD-1.21.1-001 | ADD | ETXSCADA | ConstantArgument | ConstantArgument | scalarValue | scalarValue | Float |  | etx | The scalar constant I/O parameter for a SCADA calculation. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | The scalar constant I/O parameter for a SCADA calculation.
|  | ETXSCADA | ConstantValue | ConstantValue | value | value | Float |  | etx | The value of the SCADA constant argument. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Value
|  | ETXSCADA | Function | Function | subRoutine | subRoutine | String100 |  | etx | Function subroutine. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Subroutine
|  | ETXSCADA | FunctionArgument | FunctionArgument | analogFlag | analogFlag | Boolean | FALSE | etx | Flag indicating this is input is an analog. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Analog Flag
|  | ETXSCADA | FunctionArgument | FunctionArgument | constantFlag | constantFlag | Boolean | FALSE | etx | Flag indicating this is input is a constant. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Constant Flag
|  | ETXSCADA | FunctionArgument | FunctionArgument | openFlag | openFlag | Boolean | FALSE | etx | Flag indicating any number of this type of argument can be included. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Open Flag
|  | ETXSCADA | FunctionArgument | FunctionArgument | pointFlag | pointFlag | Boolean | FALSE | etx | Flag indicating this is input is a constant. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Point Flag
|  | ETXSCADA | FunctionArgument | FunctionArgument | readFlag | readFlag | Boolean | FALSE | etx | Flag indicating this is an input to the function. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Read Flag
|  | ETXSCADA | FunctionArgument | FunctionArgument | realFlag | realFlag | Boolean | FALSE | etx | Flag indicating this is input is a real (constant, analog, or count). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Real Flag
|  | ETXSCADA | FunctionArgument | FunctionArgument | triggerFlag | triggerFlag | Boolean | FALSE | etx | Flag indicating the function runs when this argument changes. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Trigger Flag
|  | ETXSCADA | FunctionArgument | FunctionArgument | writeFlag | writeFlag | Boolean | FALSE | etx | Flag indicating this is an output from the function. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Write Flag
|  | ETXSCADA | MeasurementArgument | MeasurementArgument | triggerFlag | triggerFlag | Boolean | FALSE | etx | This reference record is an input to a calculation and triggers that calculation when referenced Measurement record changes. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | trigger Flag
|  | ETXSCADA | MeasurementGroup | MeasurementGroup | bufferPeriod | bufferPeriod | ShortInt |  | etx | Number of seconds to wait for a cluster of exceptions to be reported. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | buffer Period
|  | ETXSCADA | MeasurementGroup | MeasurementGroup | gracePeriod | gracePeriod | ShortInt |  | etx | Number of seconds to wait before declaring an expected scan 'late'. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | grace Period
|  | ETXSCADA | MeasurementGroup | MeasurementGroup | integrityPeriod | integrityPeriod | ShortInt |  | etx | Number of seconds between integrity scans. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | integrity Period
|  | ETXSCADA | MeasurementGroup | MeasurementGroup | scanPeriod | scanPeriod | ShortInt |  | etx | Number of seconds between scans. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | scan Period
|  | ETXSCADA | MeasurementGroup | MeasurementGroup | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temp Attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | abnormalForAlarm | abnormalForAlarm | Boolean | FALSE | etx | This flag is used to cause alarm messages for abnormals to have their date/time displayed in black in the Alarm displays instead of red (assuming the HABITAT FG element set). | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Abnormal For Alarm
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | abnormalForSCADA | abnormalForSCADA | Boolean | FALSE | etx | Setting this flag to true does not affect Alarm displays, but forces the record to appear Normal on SCADA displays. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Abnormal For SCADA
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | audibleTone | audibleTone | Boolean | FALSE | etx | A flag indicating that notifications of alarm conditions via audible tones and horns will be suppressed. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Audible Tone
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | farNodeNormallyEarthed | farNodeNormallyEarthed | Boolean | FALSE | etx | T = The far node of the location is normally earthed; if connected to an energized portion of the network, it is considered to be in an abnormal state. Without the normally open or normally grounded flags set, SCADA topology assumes the node is normally . | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | far Node Normally Earthed
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | farNodeNormallyOpen | farNodeNormallyOpen | Boolean | FALSE | etx | T = The far node of the location is normally open; if closed or grounded, it is considered to be in an abnormal state. Without the normally open or normally grounded flags set, SCADA topology assumes the node is normally closed (connected to at least two... | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | far Node Normally Open
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | farStation | farStation | String8 |  | etx | The 'far' station identifer for the location (as opposed to the local substation under which the device is modeled). Only used for device records which link substations, typically lines. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | far Station
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | inhibitAbnormalForAlarm | inhibitAbnormalForAlarm | Boolean | FALSE | etx | Permanently Inhibit the flag of abnormalForAlarm. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Abnormal For Alarm
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | inhibitAbnormalForSCADA | inhibitAbnormalForSCADA | Boolean | FALSE | etx | Permanently Inhibit the flag of abnormalForSCADA. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Abnormal For SCADA
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | inhibitAudibleTone | inhibitAudibleTone | Boolean | FALSE | etx | Permanently Inhibit the flag of audibleTone. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Audible Tone
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | inhibitLoggingAndAlarmList | inhibitLoggingAndAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of loggingAndAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Logging and Alarm List
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | inhibitUnackAlarmList | inhibitUnacknowledgedAlarmList | Boolean | FALSE | etx | Permanently Inhibit the flag of unacknowledgedAlarmList. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Inhibit Unacknowledged Alarm List
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | initiallyInhibit | initiallyInhibit | Boolean | FALSE | etx | A flag indicating that when the system first comes online, alarm indications for this SCADA entry will initially be inhibited. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Initially Inhibit
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | loggingAndAlarmList | loggingAndAlarmList | Boolean | FALSE | etx | A flag indicating that SCADA will issue neither an alarm nor an event. Therefore, entries will appear in the neither the alarm list nor the event logs. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Logging and Alarm List
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | nearNodeNormallyEarthed | nearNodeNormallyEarthed | Boolean | FALSE | etx | T = The near node of the location is normally earthed; if connected to an energized portion of the network, it is considered to be in an abnormal state. Without the normally open or normally grounded flags set, SCADA topology assumes the node is normally. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | near Node Normally Earthed
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | nearNodeNormallyOpen | nearNodeNormallyOpen | Boolean | FALSE | etx | T = The near node of the location is normally open; if closed or grounded, it is considered to be in an abnormal state. Without the normally open or normally grounded flags set, SCADA topology assumes the node is normally closed (connected to at least two... | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | near Node Normally Open
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | normallyDead | normallyDead | Boolean | FALSE | etx | A flag indicating whether the location is normally dead. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Normally Dead
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | overrideDefaultnhibitDef | overrideDefaultInhibitDefinition | Boolean | FALSE | etx | A flag indicating that that the Operator Inhibit Definition overrides the Global Default Inhibit. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Override Default Inhibit Definition
|  | ETXSCADA | MeasurementLocation | MeasurementLocation | unacknowledgedAlarmList | unacknowledgedAlarmList | Boolean | FALSE | etx | A flag ndicating that SCADA will issue an event to the event log, but will not issue unacknowledged alarm indications to the alarm list. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Unacknowledged Alarm List
|  | ETXSCADA | ModelVersion | ModelVersion | date | date | AbsoluteDateTime |  | etx | Date upon which CIM XML file was produced. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | date
|  | ETXSCADA | ModelVersion | ModelVersion | information | information | String100 |  | etx | Supplemental information, perhaps identifying the sources of the model or model changes. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | information
|  | ETXSCADA | ModelVersion | ModelVersion | version | version | String30 |  | etx | Identifier by which various CIM XML files can be bound together. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | TRUE |  |  | version
|  | ETXSCADA | SetPointLock | SetPointLock | assignedToAnalog | assignedToAnalog | Boolean | FALSE | etx | Assigned to Analog. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | assigned To Analog
|  | ETXSCADA | Site | Site | zonalAttribute | zonalAttribute | Boolean | FALSE | etx | Temp Attribute to support dual SCADA feeds. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Zonal Attribute
|  | MarketOperations | Contingency | Contingency | ActionType | ActionType | String100 |  | etx | Action Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Action Type
|  | MarketOperations | Contingency | Contingency | activeMode | activeMode | EnumContingencyActiveMode |  | etx | Contingency active mode. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Active Mode
|  | MarketOperations | Contingency | Contingency | DeviceName | DeviceName | String100 |  | etx | Device Name. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Device Name
|  | MarketOperations | Contingency | Contingency | DeviceType | DeviceType | String100 |  | etx | Device Type. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Device Type
|  | MarketOperations | Contingency | Contingency | enableCascading | enableCascading | Boolean | FALSE | etx | TRUE if Cascading contigency analysis needs to performed, default is FALSE. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Enable Cascading
|  | MarketOperations | Contingency | Contingency | enableRedefinition | enableRedefinition | Boolean | FALSE | etx | T=enable F=disable dynamic redefinition. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Enable Redefinition
|  | MarketOperations | Contingency | Contingency | enableSPS | enableSPS | Boolean | FALSE | etx | T=enable F=disable SPS functions. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Enable SPS
|  | MarketOperations | Contingency | Contingency | endDate | endDate | AbsoluteDateTime | 2100-01-01 | etx | Final Date this Contingency is in use. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | End Date
|  | MarketOperations | Contingency | Contingency | generationLoss | generationLoss | Float |  | etx | The amount (in MW) of generation you expect the contingency to lose. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Generation Loss
|  | MarketOperations | Contingency | Contingency | generatorParticipationFactor | generatorParticipationFactor | EnumGeneratorParticipationFactor |  | etx | Short/Long. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Generator Participation Factor
|  | MarketOperations | Contingency | Contingency | loadLoss | loadLoss | Float |  | etx | The amount (in MW) of load you expect the contingency to lose. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Load Loss
|  | MarketOperations | Contingency | Contingency | MaxShadowPrice | MaxShadowPrice | DoubleFloat | 99999 | etx | States the Max Shadow price for a Contingency. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Max Shadow Price
|  | MarketOperations | Contingency | Contingency | probabilityOfOccurance | probabilityOfOccurance | Float |  | etx | A number between 0 and 1. Contingencies with a probability less than 0.5 are considered 'low probability' contingencies. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE | 1 | 0 | Probability of Occurance
|  | MarketOperations | Contingency | Contingency | processType | processType | EnumContingencyProcessType |  | etx | Contingency process type. | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Process Type
|  | MarketOperations | Contingency | Contingency | refactor | refactor | Boolean | FALSE | etx | Set to TRUE to force a partial refactorization method when updating the matrices for the contingency solution. The default is FALSE, in this case the software will automatically determine whether a factor update or partial refactorization is more efficient for the contingency being processed, and use the most efficient method. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Refactor
|  | MarketOperations | Contingency | Contingency | responseTime | responseTime | Integer |  | etx | the time frame of response in seconds for the components associated with this contingency. | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | FALSE |  |  | Response Time
|  | MarketOperations | Contingency | Contingency | RunFlag | RunFlag | Boolean | TRUE | etx | Run Flag. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Run Flag
|  | MarketOperations | Contingency | Contingency | startDate | startDate | AbsoluteDateTime | 2001-01-01 | etx | Starting Date this Contingency is expected to be in use. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Start Date
|  | Protection | FrequencyRelay | FrequencyRelay | overFrequencyDelay | overFrequencyDelay | Seconds |  | etx | Over frequency trip delay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Frequency Trip Delay
|  | Protection | FrequencyRelay | FrequencyRelay | overFrequencyLimit | overFrequencyLimit | Voltage |  | etx | Over frequency limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Frequency Limit
|  | Protection | FrequencyRelay | FrequencyRelay | overFrequencyLockoutTime | overFrequencyLockoutTime | Seconds |  | etx | Lockout time when trip at over frequency. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Frequency Lockout Time
|  | Protection | FrequencyRelay | FrequencyRelay | underFrequencyDelay | underFrequencyDelay | Seconds |  | etx | Under frequency trip delay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Under Frequency Trip Delay
|  | Protection | FrequencyRelay | FrequencyRelay | underFrequencyLimit | underFrequencyLimit | Voltage |  | etx | Under frequency limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Under Frequency Limit
|  | Protection | FrequencyRelay | FrequencyRelay | underFrequencyLockoutTime | underFrequencyLockoutTime | Seconds |  | etx | Lockout time when trip at under frequency. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Under Frequency Lockout Time
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | freq1 | freq1 | Float |  | etx | First point in under frequency relay characteristic - decrease load by ls1 factor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Freq 1
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | freq2 | freq2 | Float |  | etx | Second point in under frequency relay characteristic - decrease load by ls2 factor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Freq 2
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | freq3 | freq3 | Float |  | etx | Third point in under frequency relay characteristic - decrease load by ls3 factor. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Freq 1
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | i | i | Integer |  | etx | Pointer to company/station. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | i
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | id | id | String30 |  | etx | Company/station that this frequency relay model belongs to. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | id
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | Is1 | Is1 | Float |  | etx | Load deration factor when frequency less than freq1. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Is 1
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | Is2 | Is2 | Float |  | etx | Load deration factor when frequency less than freq2. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Is 2
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | Is3 | Is3 | Float |  | etx | Load deration factor when frequency less than freq3. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Is 3
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | isle1 | isle1 | Integer |  | etx | Subscript of first island to trip in region one. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Isle 1
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | isle2 | isle2 | Integer |  | etx | Subscript of first island to trip in region two. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Isle 2
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | isle3 | isle3 | Integer |  | etx | Subscript of first island to trip in region three. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Isle 3
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | reset1 | reset1 | Boolean | FALSE | etx | Relay has been requested for reset from trip in region one. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reset 1
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | reset2 | reset2 | Boolean | FALSE | etx | Relay has been requested for reset from trip in region two. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reset 2
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | reset3 | reset3 | Boolean | FALSE | etx | Relay has been requested for reset from trip in region three. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Reset 3
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | tripped1 | tripped1 | Boolean | FALSE | etx | Relay has tripped in region one. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tripped 1
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | tripped2 | tripped2 | Boolean | FALSE | etx | Relay has tripped in region two. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tripped 2
|  | Protection | GenericUnderfrequencyRelay | GenericUnderfrequencyRelay | tripped3 | tripped3 | Boolean | FALSE | etx | Relay has tripped in region three. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tripped 3
|  | Protection | VoltageRelay | VoltageRelay | overVoltageDelay | overVoltageDelay | Seconds |  | etx | Over Voltage Trip Delay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Voltage Trip Delay
|  | Protection | VoltageRelay | VoltageRelay | overVoltageLimit | overVoltageLimit | Voltage |  | etx | Over Voltage Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Voltage Limit
|  | Protection | VoltageRelay | VoltageRelay | overVoltageLockoutTime | overVoltageLockoutTime | Seconds |  | etx | Lockout Time when Trip at Over Voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Over Voltage Lockout Time
|  | Protection | VoltageRelay | VoltageRelay | underVoltageDelay | underVoltageDelay | Seconds |  | etx | Under Voltage Trip Delay. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Under Voltage Trip Delay
|  | Protection | VoltageRelay | VoltageRelay | underVoltageLimit | underVoltageLimit | Voltage |  | etx | Under Voltage Limit. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Under Voltage Limit
|  | Protection | VoltageRelay | VoltageRelay | underVoltageLockoutTime | underVoltageLockoutTime | Seconds |  | etx | Lockout Time when Trip at Under Voltage. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Under Voltage Lockout Time
|  | RDF_Import | sysRdfContainer | sysRdfContainer | TypeName | TypeName | String28 |  | spc | Specifies the type this container applies to. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Type Name
|  | Reservation | TiePoint | TiePoint | tiePointMWRating | tiePointMWRating | ActivePower |  | cim | The MW rating of the tie point. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | FALSE |  |  | Tie Point MW Rating
|  | Reservation | TransmissionPath | TransmissionPath | availTransferCapability | availTransferCapability | ActivePower |  | cim | The available transmission capability of a transmission path for the reference direction. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Available Transfer Capability
|  | Reservation | TransmissionPath | TransmissionPath | parallelPathFlag | parallelPathFlag | Boolean | FALSE | cim | Flag which indicates if the transmission path is also a designated interconnection 'parallel path'. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Parallel Path Flag
|  | Reservation | TransmissionPath | TransmissionPath | totalTransferCapability | totalTransferCapability | ActivePower |  | cim | The total transmission capability of a transmission path in the reference direction. | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TRUE |  |  | Total Transfer Capability
|  |  | ProtectedSwitch |  | protectUnderAction

## Associations
issue | Notes | Package | ClassA | Association | ClassB | ClassARoleName (RDF RoleA) | ClassARoleName (RDF RoleB) | Cardinality RoleA | Cardinality RoleB | Association Type | Name Space | CPSM Nerc | ABB / MMS | Areva / EMS | ABB / OS | Nexant / CRR | PTI / Planning | Lodestar / Settlement data | NMMS Label
|  | CIMMeas | AccumulatorLimit | MemberOf | AccumulatorLimitSet | Limits | LimitSet | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | AccumulatorLimitSet
|  | CIMMeas | AccumulatorLimitSet | Limits | Accumulator | LimitSets | Measurements | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Limits (Accumulator)
|  | CIMMeas | AccumulatorValue | MemberOf | Accumulator | Contain_MeasurementValues | MemberOf_Measurement | 0..n | 1 | ParentChild | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Accumulator
DD-1.21.1-001 | INSERT | CIMWires | ACLineSegment | ACLineSegmentPartOfDCTie | DCTie | ACLineSegment | DCTie | 1..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ACLineSegmentPartOfDCTie
DD-1.21.1-003 | DELETE | CIMWires | ACLineSegment | ACLineSegmentPartOfDCTie | DCTie | ACLineSegment | DCTie | 1..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ACLineSegmentPartOfDCTie
DD-1.21.1-003 | INSERT | CIMWires | TieCorridor | TieCorridorPartOfDCTie | DCTie | TieCorridor | DCTie | 1..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TieCorridorPartOfDCTie
|  | CIMWires | ACLineSegment | BelongsFrom | SubLoadArea | depACLineSegment | FromLoadZone | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs From (LoadZone)
|  | CIMWires | ACLineSegment | BelongsTo | SubLoadArea | ACLineSegment | ToLoadZone | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (LoadZone)
|  | ETX | AggregateHub | HasA | SettlementHUB | AggregateHub | SettlementHUB | 0..n | 0..n | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (SettlementHub)
|  | CIMProduction | AirCompressor | DrivenBy | CombustionTurbine | Drives_AirCompressor | DrivenBy_CombustionTurbine | 0..1 | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Driven By (CombustionTurbine)
|  | CIMProduction | AirCompressor | MemberOf | CAESPlant | Contain_AirCompressor | MemberOf_CAESPlant | 1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | CAESPlant
|  | ETXSCADA | AlternateLimit | BelongTo | AlternateLimitSet | AlternateLimit | AlternateLimitSet | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belong To (AlternateLimitSet)
|  | ETXSCADA | AlternateLimit | BelongTo | LimitAlarmCategory | AnalogLimit | LimitAlarmCategory | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belong To (LimitAlarmCategory)
|  | ETXSCADA | AlternateLimit | Contain | AnalogLimit | AlternateLimit | AnalogLimit | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Contain (AnalogLimit)
|  | CIMMeas | AnalogLimit | BelongTo | LimitAlarmCategory | AnalogLimit | LimitAlarmCategory | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belong To (LimitAlarmCategory)
|  | CIMMeas | AnalogLimit | HasNameOf | AnalogLimitName | AnalogLimit | AnalogLimitName | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has Name Of (AnalogLimitName)
|  | CIMMeas | AnalogLimit | MemberOf | AnalogLimitSet | Limits | LimitSet | 0..n | 1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | AnalogLimitSet
|  | CIMMeas | AnalogLimitSet | Limits | Analog | LimitSets | Measurements | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | Analog
|  | CIMMeas | AnalogValue | BelongTo | AnalogAlarmCategory | AnalogValue | AnalogAlarmCategory | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belong To (AnalogAlarmCategory)
|  | CIMMeas | AnalogValue | Contain | AnalogLimit | AnalogValue | AnalogLimit | 0..n | 0..n | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Contain (AnalogLimit)
|  | CIMMeas | AnalogValue | Has | AccuracyClass | AnalogValue | AccuracyClass | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (AccuracyClass)
|  | CIMMeas | AnalogValue | HasNameOf | AnalogName | AnalogValue | AnalogName | 0..n | 0..1 | Attributive | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has Name Of (AnalogName)
|  | CIMMeas | AnalogValue | IncludedIn | ExceptionListDisplay | AnalogValue | ExceptionListDisplay | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Included In (ExceptionListDisplay)
|  | CIMMeas | AnalogValue | MemberOf | Analog | Contain_MeasurementValues | MemberOf_Measurement | 0..n | 1 | ParentChild | cim | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | Analog
|  | ETX | AncillaryQualification | MemberOf | CombinedCyclePlant | AncillaryQualification | CombinedCyclePlant | 0..1 | 0..1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | CombinedCyclePlant
|  | ETX | AncillaryQualification | MemberOf | EnergyConsumerResource | AncillaryQualification | EnergyConsumerResource | 0..1 | 0..1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | EnergyConsumerResource
|  | ETX | AncillaryQualification | MemberOf | GeneratingUnit | AncillaryQualification | GeneratingUnit | 0..1 | 0..1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | GeneratingUnit
|  | ETXMonitoring | AngleDifference | MonitorNodeA | ConnectivityNode | AngleDifference | ConnectivityNodeA | 0..n | 1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Monitor Node A (ConnectivityNode)
|  | ETXMonitoring | AngleDifference | MonitorNodeB | ConnectivityNode | AngleDifference | ConnectivityNodeB | 0..n | 1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Monitor Node B (ConnectivityNode)
|  | ETXMonitoring | AngleDifferenceLimitSet | HasA | AngleDifference | AngleDifferenceLimitSet | AngleDifference | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (AngleDifference)
|  | CIMLoadModel | AreaLossCurve | HasA | LoadArea | AreaLossCurves | LoadArea | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | LoadArea
|  | CIMCore | BasePower | MemberOf | BaseVoltage | BasePower | BaseVoltage | 0..1 | 0..1 | ParentChild | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | BaseVoltage
|  | CIMCore | Bay | MemberOf | Substation | Contains_Bays | MemberOf_Substation | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Substation
|  | CIMCore | Bay | MemberOf | VoltageLevel | Contains_Bays | MemberOf_VoltageLevel | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | FALSE | FALSE |  | FALSE |  | VoltageLevel
|  | ETXMonitoring | BranchGroup | References | Terminal | BranchGroup | Terminals | 0..n | 0..n | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | References (Terminals)
|  | ETXMonitoring | BranchGroup | ReferencesInverse | Terminal | BranchGroup | InvTerminal | 0..n | 0..n | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | References Inverse (Terminal)
|  | ETXMonitoring | BranchGroupTerminal | MemberOf | BranchGroup | BranchGroupTerminal | BranchGroup | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | BranchGroup
|  | ETXMonitoring | BranchGroupTerminal | References | Terminal | BranchGroupTerminal | Terminal | 0..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | References (Terminal)
|  | ETXSCADA | Calculation | MemberOf | MeasurementLocation | Calculation | MeasurementLocation | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | MeasurementLocation
|  | ETXSCADA | Calculation | SourceOf | MeasurementValue | Calculation | MeasurementValue | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Source Of (MeasurementValue)
|  | ETXSCADA | Calculation | TriggeredBy | CalculationTriggerTimer | Calculation | CalculationTriggerTimer | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Triggered By (CalculationTriggerTimer)
|  | ETXSCADA | Calculation | Uses | Function | Calculation | Function | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Uses (Function)
|  | ETXSCADA | CalculationArgument | AssignedTo | FunctionArgument | CalculationArgument | FunctionArgument | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Assigned To (FunctionArgument)
|  | ETXSCADA | CalculationArgument | MemberOf | Calculation | CalculationArgument | Calculation | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Contained By (Calculation)
|  | CIMOutage | ClearanceTag | AssignedTo | ConductingEquipment | ClearanceTags | ConductingEquipment | 0..n | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Assigned To (ConductingEquipment)
|  | CIMProduction | CombinedCyclePlant | References | ResourceController | CombinedCyclePlant | ResourceController | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | References (ResourceController)
|  | CIMGenerationDynamics | CombustionTurbine | Uses | HeatRecoveryBoiler | CombustionTurbines | HeatRecoveryBoiler | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | May Have (HeatRecoveryBoiler)
|  | CIMMeas | Command | ControlledBy | Discrete | ControlledBy_Control | MeasuredBy_Measurement | 0..1 | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Controlled By (Command)
|  | CIMWires | CompositeSwitch | MemberOf | Substation | Contains_CompositeSwitches | MemberOf_Substation | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Substation
|  | CIMCore | ConductingEquipment | ProtectedBy | ProtectionEquipment | ConductingEquipments | ProtectionEquipments | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Protected By (ProtectionEquipment)
|  | CIMCore | ConductingEquipment | UsesA | BaseVoltage | ConductingEquipments | BaseVoltage | 0..n | 0..1 | Reference | cim | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | BaseVoltage
|  | CIMWires | Conductor | AssignsLosses | SubControlArea | Conductor | SubControlArea | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Assigns Losses (SubControlArea)
|  | CIMWires | Conductor | MemberOf | ConductorType | Conductors | ConductorType | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Conductor
|  | ETX | Configuration | HasA | LogicalConfiguration | Configuration | LogicalConfiguration | 1..n | 0..1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | LogicalConfiguration
|  | ETX | ConfigurationMember | HasA | ThermalGeneratingUnit | ConfigurationMember | ThermalGeneratingUnit | 0..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (ThermalGeneratingUnit)
|  | ETX | ConfigurationMember | IsMemberOf | Configuration | ConfigurationMember | Configuration | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Configuration
|  | CIMLoadModel | ConformLoad | AssignedTo | ConformLoadGroup | EnergyConsumers | LoadGroup | 0..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | Assigned To (ConformLoadGroup)
|  | CIMLoadModel | ConformLoadSchedule | MemberOf | ConformLoadGroup | ConformLoadSchedules | ConformLoadGroup | 0..n | 1 | ParentChild | cim | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | ConformLoadGroup
|  | CIMTopology | ConnectivityNode | BelongsTo | ConnectivityNodeGroup | ConnectivityNode | ConnectivityNodeGroup | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | ConnectivityNodeGroup
|  | CIMTopology | ConnectivityNode | MemberOf | EquipmentContainer | ConnectivityNodes | MemberOf_EquipmentContainer | 0..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | EquipmentContainer
|  | CIMTopology | ConnectivityNode | MemberOf | TopologicalNode | ConnectivityNodes | TopologicalNode | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TopologicalNode
DD-1.21.1-001 | UPDATE | CIMTopology | ConnectivityNode | MemberOf | TopologicalNode | ConnectivityNodes | TopologicalNode | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TopologicalNode
|  | ETXPlanning | ConnectivityNodeGroup | BelongsTo | PlanningArea | ConnectivityNodeGroup | PlanningArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | PlanningArea
|  | ETXPlanning | ConnectivityNodeGroup | BelongsTo | PlanningZone | ConnectivityNodeGroup | PlanningZone | 1..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | PlanningZone
DD-1.21.1-001 | UPDATE | ETXPlanning | ConnectivityNodeGroup | BelongsTo | PlanningZone | ConnectivityNodeGroup | PlanningZone | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | PlanningZone
DD-1.21.1-003 | DELETE | ETXSCADA | ConstantArgument | Has | PermissionArea | ConstantArgument | PermissionArea | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (PermissionArea)
DD-1.21.1-001 | UPDATE | ETXSCADA | ConstantArgument | Has | PermissionArea | ConstantArgument | PermissionArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (PermissionArea)
DD-1.21.1-003 | UPDATE | ETXSCADA | ConstantArgument | MappedTo | ConstantValue | ConstantArgument | ConstantValue | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Mapped To (ConstantValue)
|  | ETXContingency | ContingencyElement | HasA | Equipment | ContingencyElement | Equipment | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (Equipment)
|  | ETXContingency | ContingencyElement | MemberOf | Contingency | ContingencyElement | MemberOf_Contingency | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Contingency
|  | ETXContingency | ContingencyGroupMember | HasA | Contingency | ContingencyGroupMember | Contingency | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (Contingency)
|  | ETXContingency | ContingencyGroupMember | IsMemberOf | ContingencyGroup | ContingencyGroupMember | ContingencyGroup | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | ContingencyGroup
|  | CIMMeas | Control | ControlledBy | RemoteControl | Control | RemoteControl | 1 | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Controlled By (RemoteControl)
|  | CIMMeas | Control | Controls | RegulatingCondEq | Controls | ControlledBy_RegulatingCondEq | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Controls (RegulatingCondEq)
|  | CIMMeas | Control | Controls | Unit | Controls | Unit | 0..n | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Controls (Unit)
DD-1.21.1-001 | UPDATE | CIMMeas | Control | Controls | Unit | Controls | Unit | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Controls (Unit)
|  | CIMMeas | Control | UsesA | ControlType | Control | ControlType | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Uses A (ControlType)
|  | CIMGenerationDynamics | CTTEMPMWCurve | MemberOf | CombustionTurbine | CTTempMWCurve | CombustionTurbine | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | CombustionTurbine
|  | CIMCore | CurveData | HasA | Curve | CurveScheduleDatas | CurveSchedule | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | CurveSchedule
|  | CIMMeas | Discrete | AliasedBy | ValueAliasSet | Discrete | ValueAliasSet | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Aliased By (ValueAliasSet)
|  | CIMMeas | DiscreteValue | BelongTo | DiscreteAlarmCategory | DiscreteValue | DiscreteAlarmCategory | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belong To (DiscreteAlarmCategory)
|  | CIMMeas | DiscreteValue | Has | ConversionTable | DiscreteValue | ConversionTable | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (ConversionTable)
|  | CIMMeas | DiscreteValue | HasNameOf | DiscreteName | DiscreteValue | DiscreteName | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has Name Of (DiscreteName)
|  | CIMMeas | DiscreteValue | HasTypeOf | DiscreteType | DiscreteValue | DiscreteType | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has Type Of (DiscreteType)
|  | CIMMeas | DiscreteValue | IncludedIn | ExceptionListDisplay | DiscreteValue | ExceptionListDisplay | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Included In (ExceptionListDisplay)
|  | CIMMeas | DiscreteValue | MemberOf | Discrete | Contain_MeasurementValues | MemberOf_Measurement | 0..n | 1 | ParentChild | cim | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | Contains (Discrete)
|  | Common | Domain | MemberOf | sysOrphan | Domain_MemberOf | MemberOf_sysOrphan | 0..n | 0..1 | ParentChild | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | sysOrphan
|  | ETX | ElectricalBus | MemberOf | ConnectivityNode | ElectricalBus_HasA | ConnectivityNode | 0..1 | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | ConnectivityNode
|  | CIMProduction | EmissionAccount | MemberOf | ThermalGeneratingUnit | EmmissionAccounts | ThermalGeneratingUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
|  | CIMProduction | EmissionCurve | MemberOf | ThermalGeneratingUnit | EmissionCurves | ThermalGeneratingUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
|  | CIMWires | EnergyConsumer | AssignedTo | LoadArea | EnergyConsumers | LoadArea | 0..n | 0..1 | Reference | cim | TRUE | TRUE | FALSE | FALSE |  | FALSE |  | LoadArea
|  | CIMWires | EnergyConsumer | BelongsTo | PlanningArea | EnergyConsumer | PlanningArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (PlanningArea)
|  | CIMWires | EnergyConsumer | BelongsTo | PlanningZone | EnergyConsumer | PlanningZone | 1..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (PlanningZone)
DD-1.21.1-001 | UPDATE | CIMWires | EnergyConsumer | BelongsTo | PlanningZone | EnergyConsumer | PlanningZone | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (PlanningZone)
|  | CIMWires | EnergyConsumer | BelongsTo | SubLoadArea | LoadZone | EnergyConsumer | 0..n | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Belongs To (LoadZone)
|  | CIMWires | EnergyConsumer | HasA | AccuracyClass | EnergyConsumer | AccuracyClass | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (AccuracyClass)
|  | CIMWires | EnergyConsumer | HasA | LoadType | EnergyConsumer | LoadType | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | LoadType
|  | CIMWires | EnergyConsumer | MemberOf | PowerCutZone | EnergyConsumers | PowerCutZone | 1..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | PowerCutZone
|  | CIMWires | EnergyConsumer | MemberOf | SubLoadArea | EnergyConsumers | LoadZone | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | LoadZone
|  | CIMWires | EnergyConsumer | PartOf | DCTie | EnergyConsumer | DCTie | 1 | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Part Of (DCTie)
|  | CIMWires | EnergyConsumer | PartOf | PrivateAreaNetwork | EnergyConsumer | PrivateAreaNetwork | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Part Of (PrivateAreaNetwork)
|  | ETXLoadModel | EnergyConsumerAltConnection | TransferFrom | EnergyConsumer | TransferTo | TransferFrom_EnergyConsumer | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | EnergyConsumer
|  | ETXLoadModel | EnergyConsumerAltConnection | TransferTo | EnergyConsumer | TransferFrom | TransferTo_EnergyConsumer | 0..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Transfer To (EnergyConsumer)
|  | ETX | EnergyConsumerResource | HasA | EnergyConsumer | LR_HasA | HasA_EnergyConsumer | 0..n | 1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (EnergyConsumer)
|  | ETX | EnergyConsumerResource | HasA | ResourceNode | LoadResource | HasA_ResourceNode | 0..n | 0..1 | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (ResourceNode)
|  | ETX | EnergyConsumerResource | OperatedBy | Operatorship | EnergyConsumerResource | Operatorship | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Energy Consumer Operatorship
|  | ETX | EnergyConsumerResource | OwnedBy | Ownership | EnergyConsumerResource | Ownership | 0..n | 0..n | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Energy Consumer Ownership
|  | ETX | EnergyConsumerResource | References | HostControlArea | EnergyConsumerResource | HostControlArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (HostControlArea)
|  | ETX | EPSMeter | HasA | Configuration | EPSMeter_HasA | Configuration | 0..n | 0..n | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (Configuration)
|  | ETX | EPSMeter | HasA | GeneratingUnit | EPSMeter_HasA | GeneratingUnit | 0..n | 0..n | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (GeneratingUnit)
|  | ETX | EPSMeter | HasA | MeterConfiguration | EPSMeter_HasA | MeterConfiguration | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | MeterConfiguration
|  | ETX | EPSMeter | HasA | PricingVector | EPSMeter_HasA | HasA_PricingVector | 1 | 1..n | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (PricingVector)
|  | CIMCore | Equipment | AssociatesDAM | LimitLogicType | Equipment | DAM_LLT | 0..1 | 0..n | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Associates DAM (LimitLogicType)
|  | CIMCore | Equipment | AssociatesRUC | LimitLogicType | Equipment | RUC_LLT | 0..1 | 0..n | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Associates RUC (LimitLogicType)
|  | CIMCore | Equipment | HasTypeOf | EquipmentType | GenericEquipment | EquipmentType | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has Type Of (EquipmentType)
|  | CIMCore | Equipment | MemberOf | EquipmentContainer | Contains_Equipments | MemberOf_EquipmentContainer | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | EquipmentContainer
|  | ETX | FlowgateElement | HasA | ConductingEquipment | FlowgateElement | ConductingEquipment | 0..1 | 0..1 | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (ConductingEquipment)
|  | ETX | FlowgateElement | HasA | Terminal | FlowgateElement | Terminal | 0..1 | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (Terminal)
|  | ETX | FlowgateElement | MemberOf | FlowgateGroup | FlowgateElement | FlowgateGroup | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | FlowgateGroup
|  | CIMProduction | FossilFuel | Fuels | ThermalGeneratingUnit | FossilFuels | ThermalGeneratingUnit | 0..n | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Fuels (FossilFuel)
|  | CIMProduction | FuelAllocationSchedule | MemberOf | ThermalGeneratingUnit | FuelAllocationSchedules | ThermalGeneratingUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
|  | CIMProduction | FuelAllocationSchedule | Requires | FossilFuel | FuelAllocationSchedule | FossilFuel | 0..n | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Requires (FossilFuel)
|  | ETXSCADA | FunctionArgument | MemberOf | Function | FunctionArgument | Function | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Function
|  | ETXRASE | Gate | MemberOf | TriggerCondition | Gate | MemberOf_TriggerCondition | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (TriggerCondition)
|  | ETXRASE | GateInputPin | MemberOf | Gate | GateInputPin | MemberOf_Gate | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Gate
|  | CIMProduction | GeneratingUnit | HasA | GenerationType | GeneratingUnit | GenerationType | 0..n | 0..1 | Attributive | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (GenerationType)
DD-1.21.1-001 | UPDATE | CIMProduction | GeneratingUnit | HasA | ResourceNode | GeneratingUnit_HasA | HasA_ResourceNode | 0..n | 0..1 | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (ResourceNode)
|  | CIMProduction | GeneratingUnit | MemberOf | SubLoadArea | GeneratingUnit | SubLoadArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Member Of (SubLoadArea)
|  | CIMProduction | GeneratingUnit | operatesDuringStartStop | ProtectedSwitch | GeneratingUnit | ProtectedSwitch | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | operatesDuringStartStop (ProtectedSwitch)
DD-1.21.1-001 OTS | DELETE | CIMProduction | GeneratingUnit | operatesDuringStartStop | ProtectedSwitch | GeneratingUnit | ProtectedSwitch | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | operatesDuringStartStop (ProtectedSwitch)
|  | CIMProduction | GeneratingUnit | PartOf | DCTie | GeneratingUnit | DCTie | 1 | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Part Of (DCTie)
|  | CIMProduction | GeneratingUnit | PartOf | PrivateAreaNetwork | GeneratingUnit | PrivateAreaNetwork | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Part Of (PrivateAreaNetwork)
|  | CIMProduction | GenUnitOpCostCurve | MemberOf | GeneratingUnit | GenUnitOpCostCurves | GeneratingUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | GeneratingUnit
|  | CIMProduction | GenUnitOpSchedule | ScheduleFor | GeneratingUnit | GenUnitOpSchedule | GeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | GeneratingUnit
|  | CIMProduction | GrossToNetMWCurve | MemberOf | GeneratingUnit | GrossToNetMWCurves | GeneratingUnit | 0..n | 0..1 | ParentChild | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | GeneratingUnit
|  | CIMWires | HeatExchanger | MemberOf | PowerTransformer | HeatExchanger | PowerTransformer | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | PowerTransformer
|  | CIMProduction | HeatInputCurve | MemberOf | ThermalGeneratingUnit | HeatInputCurve | ThermalGeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
|  | CIMProduction | HeatRateCurve | MemberOf | ThermalGeneratingUnit | HeatRateCurve | ThermalGeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
|  | ETX | HUBBus | HasA | ConnectivityNodeGroup | HasAHUBBus | HasAConnectivityNodes | 0..1 | 1..n | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (ConnectivityNodeGroup)
|  | ETX | HUBBus | MemberOf | SettlementHUB | HubBus | SettlementHub | 1..n | 1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | SettlementHub
|  | CIMProduction | HydroGenEfficiencyCurve | HasA | HydroGeneratingUnit | HydroGeneratingEfficiencyCurves | HydroGeneratingUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroGeneratingUnit
DD-1.21.1-003 | UPDATE | CIMProduction | HydroGeneratingUnit | MemberOf | HydroPowerPlant | Contain_HydroGeneratingUnit | MemberOf_HydroPowerPlant | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroPowerPlant
|  | CIMProduction | HydroPump | DrivenBy | SynchronousMachine | Drives_HydroPump | DrivenBy_SynchronousMachine | 0..1 | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroPump
|  | CIMProduction | HydroPump | MemberOf | HydroPowerPlant | Contain_HydroPumps | MemberOf_HydroPowerPlant | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroPowerPlant
|  | CIMProduction | HydroPumpOpSchedule | HasA | HydroPump | HydroPumpOpSchedule | HydroPump | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroPump
|  | ETX | IccpQualityConversion | MemberOf | IccpQualityConversionSet | IccpQualityConversion | IccpQualityConversionSet | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | IccpQualityConversionSet
|  | ETX | IccpQualityConversionSet | References | Ownership | IccpQualityConversionSet | Ownership | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (Ownership)
|  | CIMCore | IdentifiedObject | BelongsTo | ModelingAuthoritySet | IdentifiedObjects | ModelingAuthoritySet | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Belongs To (ModelingAuthoritySet)
|  | CIMProduction | IncrementalHeatRateCurve | MemberOf | ThermalGeneratingUnit | IncrementalHeatRateCurve | ThermalGeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
|  | CIMProduction | InflowForecast | HasA | Reservoir | InflowForecast | Reservoir | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Reservoir
|  | CIMCore | IrregularTimePoint | MemberOf | IrregularIntervalSchedule | TimePoints | IntervalSchedule | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | IrregularIntervalSchedule
|  | CIMProduction | LevelVsVolumeCurve | HasA | Reservoir | LevelVsVolumeCurve | Reservoir | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Reservoir
|  | CIMMeas | LimitSet | HasA | Season | LimitSets | Season | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (Season)
|  | CIMWires | Line | MemberOf | SubGeographicalRegion | Lines | Region | 0..n | 0..1 | ParentChild | cim | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | SubGeographicalRegion
|  | CIMLoadModel | LoadDemandModel | BasedOn | DayType | LoadDemandModels | DayType | 0..n | 0..1 | Attributive | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Based On (DayType)
|  | CIMLoadModel | LoadDemandModel | BasedOn | Season | LoadDemandModels | BasisFor | 0..n | 0..1 | Attributive | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Based On (Season)
|  | CIMLoadModel | LoadDemandModel | MemberOf | EnergyConsumer | LoadDemandModels | EnergyConsumer | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | EnergyConsumer
|  | CIMLoadModel | LoadGroup | MemberOf | SubLoadArea | LoadGroups | SubLoadArea | 0..n | 1 | ParentChild | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | SubLoadArea
DD-1.21.1-001 | UPDATE | ETX | LogicalConfiguration | HasA | CombinedCyclePlant | LogicalConfiguration | CombinedCyclePlant | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | CombinedCyclePlant
|  | CIMMeas | Measurement | MeasuredBy | Terminal | Measurements | Terminal | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Terminal
|  | CIMMeas | Measurement | MemberOf | PowerSystemResource | Contains_Measurements | MemberOf_PSR | 0..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | PowerSystemResource
|  | CIMMeas | Measurement | OperatedBy | Operatorship | Measurement | Operatorship | 0..n | 0..n | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Operated By (Operatorship)
|  | CIMMeas | Measurement | OwnedBy | Ownership | Measurement | Ownership | 0..n | 0..n | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Owned By (Ownership)
|  | CIMMeas | Measurement | UsesA | LimitSet | Measurements | LimitSets | 0..n | 0..n | Reference | cim | TRUE | TRUE | FALSE | FALSE |  | FALSE |  | LimitSet
|  | CIMMeas | Measurement | UsesA | MeasurementType | Measurements | MeasurementType | 0..n | 0..1 | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | MeasurementType
|  | CIMMeas | Measurement | UsesA | Unit | Measurements | Unit | 0..n | 0..1 | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Unit
|  | ETXSCADA | MeasurementArgument | MappedTo | MeasurementValue | MeasurementArgument | MeasurementValue | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Mapped To (MeasurementValue)
|  | ETXSCADA | MeasurementGroup | Contains | MeasurementLocation | MeasurementGroup | MeasurementLocation | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Contains (MeasurementLocation)
|  | ETXSCADA | MeasurementLocation | Has | PermissionArea | MeasurementLocation | PermissionArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (PermissionArea)
DD-1.21.1.003 | UPDATE | ETXSCADA | MeasurementLocation | HasTypeOf | DeviceTypeName | MeasurementLocation | DeviceTypeName | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | HasTypeOf (DeviceTypeName)
|  | ETXSCADA | MeasurementLocation | Has | VoltageLevel | MeasurementLocation | VoltageLevel | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (VoltageLevel)
DD-1.21.1-001 | DELETE | ETXSCADA | MeasurementLocation | Has | VoltageLevel | MeasurementLocation | VoltageLevel | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (VoltageLevel)
DD-1.21.1-004 phone call | UPDATE | ETXSCADA | MeasurementLocation | MemberOf | PowerSystemResource | MeasurementLocation | MemberOf_PSR | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | PowerSystemResource
|  | CIMMeas | MeasurementValue | BelongTo | Site | MeasurementValue | Site | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belong To (Site)
|  | CIMMeas | MeasurementValue | CalculatedBy | Calculation | MeasurementValue | Calculation | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Calculated By (Calculation)
|  | CIMMeas | MeasurementValue | GroupedBy | MeasurementGroup | MeasurementValue | MemberOf_MeasurementGroup | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Grouped By (MeasurementGroup)
|  | CIMMeas | MeasurementValue | Has | PermissionArea | MeasurementValue | PermissionArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (PermissionArea)
DD-1.21.1-001 | DELETE | CIMMeas | MeasurementValue | Has | PermissionArea | MeasurementValue | PermissionArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (PermissionArea)
|  | CIMMeas | MeasurementValue | Has | SitePermission | MeasurementValue | SitePermission | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has (SitePermission)
|  | CIMMeas | MeasurementValue | HasA | MeasurementValueSource | MeasurementValues | MeasurementValueSource | 0..n | 0..1 | Reference | cim | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | MeasurementValueSource
|  | CIMMeas | MeasurementValue | HasSecondary | Site | MeasurementValue | SecondarySite | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has Secondary (Site)
|  | CIMMeas | MeasurementValue | LinksTo | RemoteSource | MeasurementValue | RemoteSource | 1 | 0..1 | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Links To (RemoteSource)
|  | CIMMeas | MeasurementValue | References | IccpQualityConversionSet | MeasurementValue | IccpQualityConversionSet | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (IccpQualityConversionSet)
|  | CIMMeas | MeasurementValueQuality | MemberOf | MeasurementValue | MeasurementValueQuality | MeasurementValue | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | MeasurementValue
|  | CIMMeas | MeasurementValueSource | MemberOf | Company | MeasurementValueSource | Company | 0..n | 1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Company
|  | CIMCore | ModelingAuthoritySet | MemberOf | ModelingAuthority | ModelingAuthoritySets | ModelingAuthority | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Maintained By (ModelingAuthority)
|  | ETXMonitoring | Monitored | MemberOf | MonitoredGroup | Monitored | MonitoredGroup | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | MonitoredGroup
DD-1.21.1-001 | UPDATE | CIMWires | MVArCapabilityCurve | HasA | SynchronousMachine | MVArCapabilityCurves | SynchronousMachines | 0..n | 1 | ParentChild | cim | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | SynchronousMachine
|  | CIMLoadModel | NonConformLoad | AssignedTo | NonConformLoadGroup | EnergyConsumers | LoadGroup | 0..n | 0..1 | Reference | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Assigned To (NonConformLoadGroup)
|  | CIMLoadModel | NonConformLoadSchedule | MemberOf | NonConformLoadGroup | NonConformLoadSchedules | NonConformLoadGroup | 0..n | 1 | ParentChild | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | NonConformLoadGroup
|  | ETX | Operatorship | HasAPrimary | Contact | Operator_HasAPrimary | Contact | 0..1 | 1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A Primary (Contact)
DD-1.21.1-001 | UPDATE | ETX | Operatorship | HasAPrimary | Contact | Operator_HasAPrimary | Contact | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A Primary (Contact)
|  | ETX | Operatorship | HasASecondary | Contact | Operator_HasASecondary | Contact | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A Secondary (Contact)
|  | ETX | Operatorship | MemberOf | Company | Operatorship_OperatesPartOf | Company | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Company
|  | CIMOutage | OutageSchedule | MemberOf | PowerSystemResource | OutageSchedule | PSR | 0..1 | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | PowerSystemResource
|  | CIMOutage | OutageSchedule | OperatedBy | SwitchingOperation | OutageSchedule | SwitchingOperations | 0..1 | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Operated By (SwitchingOperation)
|  | ETXRating | OwnerShareLimits | HasA | RampRateCurve | OwnerShareLimits | RampRateCurve | 0..n | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (RampRateCurve)
|  | ETXRating | OwnerShareLimits | LimitsBy | Operatorship | OwnerShareLimits | Operatorship | 0..1 | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Limits By (Operatorship)
|  | ETXRating | OwnerShareLimits | LimitsBy | Ownership | OwnerShareLimits | Ownership | 1 | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Limits By (Ownership)
DD-1.21.1-001 | UPDATE | ETXRating | OwnerShareLimits | LimitsBy | Ownership | OwnerShareLimits | Ownership | 0..1 | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Limits By (Ownership)
|  | ETXRating | OwnerShareLimits | MemberOf | EnergyConsumerResource | OwnerShareLimits | EnergyConsumerResource | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | EnergyConsumerResource
|  | ETXRating | OwnerShareLimits | MemberOf | GeneratingUnit | OwnerShareLimits | GeneratingUnit | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | GeneratingUnit
|  | ETXRating | OwnerShareRating | MemberOf | Equipment | OwnerShareRating | Equipment | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Equipment
|  | ETXRating | OwnerShareRating | OwnedBy | DynamicElement | OwnerShareRating | DynamicElement | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Owned By (DynamicElement)
DD-1.21.1-001 | UPDATE | ETXRating | OwnerShareRating | OwnedBy | DynamicElement | OwnerShareRating | DynamicElement | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Owned By (DynamicElement)
|  | ETXRating | OwnerShareRating | RatedBy | Ownership | OwnerShareRating | Ownership | 0..1 | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Rated By (Ownership)
DD-1.21.1-001 | UPDATE | ETXRating | OwnerShareRating | RatedBy | Ownership | OwnerShareRating | Ownership | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Rated By (Ownership)
|  | ETXRating | OwnerShareRating | Reference | WeatherStation | OwnerShareRating | WeatherStation | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reference (WeatherStation)
|  | ETXRating | OwnerShareRating | Reference | WeatherStationAlt | OwnerShareRating | WeatherStationAlt | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reference (WeatherStationAlt)
|  | ETX | Ownership | HasAPrimary | Contact | Owner_HasAPrimary | Contact | 0..1 | 1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A Primary (Contact)
DD-1.21.1-001 | UPDATE | ETX | Ownership | HasAPrimary | Contact | Owner_HasAPrimary | Contact | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A Primary (Contact)
|  | ETX | Ownership | HasASecondary | Contact | Owner_HasASecondary | Contact | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A Secondary (Contact)
|  | ETX | Ownership | MemberOf | Company | Owner_OwnsPartOfCompany | Company | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Company
|  | CIMProduction | PenstockLossCurve | HasA | HydroGeneratingUnit | PenstockLossCurve | HydroGeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroGeneratingUnit
DD-1.21.1-001 | INSERT | CIMWires | PhaseShifterImpedanceCurve | HasA | TapChanger | PhaseShifterImpedanceCurve | TapChanger | 0..1 | 0..1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (PhaseShifterImpedanceCurve)
|  | ETX_Areva | PhysicalTiePoint | AssociatedWith | Terminal | PhysicalTiePoint | Terminal | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Associated With (Terminal)
|  | ETXRASE | PinBranchGroup | BelongsTo | BranchGroup | PinBranchGroup | BranchGroup | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (BranchGroup)
|  | ETXRASE | PinFlow | HasA | Terminal | PinFlow | Terminal | 0..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (Terminal)
|  | ETXRASE | PinGate | HasA | Gate | PinGate | Gate | 0..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (Gate)
|  | ETXRASE | PinSwitch | HasA | Switch | PinSwitch | Switch | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (Switch)
|  | ETXRASE | PinTriggerCondition | HasA | TriggerCondition | PinTriggerCondition | TriggerCondition | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (TriggerCondition)
|  | ETXRASE | PinVoltage | HasA | ConnectivityNode | ConnectivityNode | PinVoltage | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (ConnectivityNode)
DD-1.21.1-003 | UPDATE | ETXPlanning | PlanningBay | BelongsTo | VoltageLevel | PlanningBay | VoltageLevel | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | VoltageLevel
|  | ETXPlanning | PlanningZone | BelongsTo | PlanningZoneGroup | PlanningZone | PlanningZoneGroup | 1..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | PlanningZoneGroup
|  | CIMCore | PowerSystemResource | MemberOf | Company | Operates_PSRs | OperatedBy_Companies | 0..n | 0..1 | ParentChild | cim | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | Company
|  | CIMCore | PowerSystemResource | OperatedBy | Operatorship | PowerSystemResource | Operatorship | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Operated By (Operatorship)
DD-1.21.1-002 | UPDATE | CIMCore | PowerSystemResource | OperatedBy | Operatorship | PowerSystemResource | Operatorship | 0..n | 0..n | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Operated By (Operatorship)
|  | CIMCore | PowerSystemResource | OwnedBy | Ownership | PowerSystemResource | Ownership | 0..n | 0..n | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Own Percent (Ownership)
|  | CIMWires | PowerTransformer | HasAMaster | PowerTransformer | PowerTransformer | PowerTransformer | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A Master (PowerTransformer)
|  | ETX | PricingVector | HasA | Terminal | HasA_PricingVector | Terminal | 0..1 | 1 | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (Terminal)
DD-1.21.1-001 | UPDATE | ETX | PricingVector | HasA | Terminal | HasA_PricingVector | Terminal | 0..n | 1 | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Has A (Terminal)
DD-1.21.1-001 | UPDATE | ETX | PricingVector | MemberOf | ElectricalBus | PricingLocation | ElectricalBus | 0..n | 1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | ElectricalBus
|  | ETX | PrivateAreaNetwork | HasA | ResourceNode | PrivateAreaNetwork_HasA | HasA_ResourceNode | 0..1 | 0..n | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (ResourceNode)
|  | ETXRASE | PrivateProtectiveActions | ActionsOfTrigger | StageTrigger | PrivateProtectiveActions | StageTrigger | 1 | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Actions Of Trigger (StageTrigger)
|  | ETXRASE | ProtActACLineSegment | Reference | ACLineSegment | ProtActACLineSegment | ACLineSegment | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reference (ACLineSegment)
|  | ETXRASE | ProtActAnalog | ReduceBy | AnalogValue | ProtActAnalog | AnalogValue | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reduce By (AnalogValue)
|  | ETXRASE | ProtActEnergyConsumer | References | EnergyConsumer | ProtActEnergyConsumer | EnergyConsumer | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (EnergyConsumer)
|  | ETXRASE | ProtActSeriesCompensator | Reference | SeriesCompensator | ProtActSeriesCompensator | SeriesCompensator | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reference (SeriesCompensator)
|  | ETXRASE | ProtActStationReduction | References | Substation | ProtActStationReduction | Substation | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (Substation)
|  | ETXRASE | ProtActSwitch | Reference | Switch | ProtActSwitch | Switch | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (Switch)
|  | ETXRASE | ProtActSynchronousMachine | References | SynchronousMachine | ProtActSynchronousMachine | SynchronousMachine | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (SynchronousMachine)
|  | ETXRASE | ProtActTransformerWinding | Reference | TransformerWinding | ProtActTransformerWinding | TransformerWinding | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reference (TransformerWinding)
|  | CIMWires | ProtectedSwitch | operatesDuringStartStop | GeneratingUnit | ProtectedSwitch | GeneratingUnit | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | operatesDuringStartStop (GeneratingUnit)
DD-1.21.1-001 OTS | DELETE | CIMWires | ProtectedSwitch | operatesDuringStartStop | GeneratingUnit | ProtectedSwitch | GeneratingUnit | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | operatesDuringStartStop (GeneratingUnit)
|  | CIMProtection | ProtectionEquipment | HasA | Unit | ProtectionEquipments | Unit | 0..n | 1 | Attributive | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (Unit)
|  | CIMProtection | ProtectionEquipment | Operates | ProtectedSwitch | OperatedBy_ProtectionEquipments | Operates_Breakers | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Operates (Breaker)
DD-1.21.1-001 OTS | DELETE | CIMProtection | ProtectionEquipment | Operates | ProtectedSwitch | OperatedBy_ProtectionEquipments | Operates_Breakers | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Operates (Breaker)
DD-1.21.1-001 OTS | INSERT | CIMProtection | ProtectionEquipment | Operates | Switch | OperatedBy_ProtectionEquipments | Operates_Switches | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Operates (Switch)
|  | CIMProtection | ProtectionEquipment | sensedBus | BusbarSection | ProtectionEquipment | BusbarSection | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | sensedBus (BusbarSection)
|  | ETXRASE | ProtectiveAction | ArmedBy | DiscreteValue | ProtectiveAction | DiscreteValue | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Armed By (DiscreteValue)
|  | ETXRASE | ProtectiveAction | Contains | ProtectiveActions | ProtectiveAction | ProtectiveActions | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | ProtectiveActions
|  | ETXRASE | ProtectiveActionShared | Has | SharedProtectiveActions | ProtectiveActionShared | SharedProtectiveActions | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (SharedProtectiveActions)
|  | ETX | PseudoTerminal | For | CombinedCyclePlant | PseudoTerminal | CombinedCyclePlant | 0..1 | 0..1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | CombinedCyclePlant
|  | ETX | PseudoTerminal | For | GenericEquipment | PseudoTerminal | GenericEquipment | 0..1 | 0..1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | GenericEquipment
|  | ETX | PseudoTerminal | For | OwnerShareLimits | PseudoTerminal | OwnerShareLimits | 0..1 | 0..1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | OwnerShareLimits
|  | CIMCore | PSRType | HasA | PowerSystemResource | PSRType | PowerSystemResource | 0..1 | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (PSRType)
|  | ETX_Areva | RampRateCurve | MemberOf | Configuration | RampRateCurve | Configuration | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Configuration
|  | ETX_Areva | RampRateCurve | MemberOf | EnergyConsumerResource | RampRateCurve | EnergyConsumerResource | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Member Of (EnergyConsumerResource)
|  | ETX_Areva | RampRateCurve | MemberOf | GeneratingUnit | RampRateCurve | GeneratingUnit | 0..n | 0..1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Member Of (GeneratingUnit)
|  | ETXRating | Rating | IsMonitored | MonitoredRating | Rating | MonitoredRating | 1 | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Is Monitored (MonitoredRating)
|  | ETXRating | Rating | MemberOf | OwnerShareRating | Rating | OwnerShareRating | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Member Of (OwnerShareRating)
|  | ETXRating | Rating | Uses | Unit | Rating | Unit | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Uses (Unit)
|  | CIMProtection | RecloseSequence | MemberOf | ProtectedSwitch | RecloseSequences | Breaker | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ProtectedSwitch
DD-1.21.1-001 OTS | DELETE | CIMProtection | RecloseSequence | MemberOf | ProtectedSwitch | RecloseSequences | Breaker | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ProtectedSwitch
DD-1.21.1-001 OTS | INSERT | CIMProtection | RecloseSequence | MemberOf | Switch | RecloseSequences | Breaker | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Switch
|  | CIMCore | RegularTimePoint | MemberOf | RegularIntervalSchedule | TimePoints | IntervalSchedule | 0..n | 1 | ParentChild | cim | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | RegularIntervalSchedule
|  | CIMWires | RegulatingCondEq | HasA | RegulationSchedule | RegulatingCondEqs | RegulationSchedule | 0..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | RegulationSchedule
|  | CIMWires | RegulatingCondEq | RegulatedBy | LoadBasedRegulationCurve | RegulatingCondEq | LoadBasedRegulationCurve | 0..1 | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Regulated By (LoadBasedRegulationSchedule)
DD-1.21.1-001 | UPDATE | CIMWires | RegulatingCondEq | RegulatedBy | LoadBasedRegulationCurve | RegulatingCondEq | LoadBasedRegulationCurve | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Regulated By (LoadBasedRegulationSchedule)
|  | CIMWires | RegulatingCondEq | Regulates | Terminal | RegulatingCondEquipment | Terminal | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Regulates (Terminal)
|  | CIMWires | RegulatingCondEq | UsesA | Measurement | RegulatingCondEqs | Measurement | 0..n | 0..1 | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Uses A (Measurement)
|  | CIMWires | RegulationSchedule | HasA | DayType | RegulationSchedule | DayType | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (DayType)
|  | CIMWires | RegulationSchedule | HasA | Season | RegulationSchedule | Season | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (Season)
|  | ETXRASE | RemedialActionScheme | BelongsTo | Contingency | RemedialActionScheme | Contigency | 0..n | 1..n | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (Contingency)
DD-1.21.1-001 | UPDATE | ETXRASE | RemedialActionScheme | BelongsTo | Contingency | RemedialActionScheme | Contigency | 0..n | 0..n | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (Contingency)
|  | CIMSCADA | RemotePoint | MemberOf | RemoteUnit | Contains_RemotePoints | MemberOf_RemoteUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | RemoteUnit
|  | CIMSCADA | RemoteUnit | AttachedTo | CommunicationLink | Contain_RemoteUnits | MemberOf_CommunicationLinks | 0..n | 1..n | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Attached To (CommunicationLink)
|  | CIMProduction | Reservoir | ProvidesWaterTo | HydroPowerPlant | Reservoir | HydroPowerPlants | 0..1 | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Provides Water To (HydroPowerPlants
|  | CIMProduction | Reservoir | SpillsTo | Reservoir | SpillsInto | SpillsFrom | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Spills To (Reservoir)
|  | ETX_Areva | ResourceController | MemberOf | Substation | ResourceController | Substation | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Substation
|  | ETX | ResourceNode | MemberOf | ElectricalBus | ResourceNode | ElectricalBus | 0..1 | 1 | ParentChild | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | ElectricalBus
|  | CIMLoadModel | SeasonDayTypeSchedule | BasedOn | DayType | SeasonDayTypeSchedules | DayType | 0..n | 0..1 | Attributive | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Based On (DayType)
|  | CIMLoadModel | SeasonDayTypeSchedule | BasedOn | Season | SeasonDayTypeSchedules | Season | 0..n | 0..1 | Attributive | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Based On (Season)
|  | CIMMeas | SetPoint | Contain | AnalogValue | Setpoint | AnalogValue | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Contain (AnalogValue)
|  | CIMMeas | SetPoint | ControlledBy | Analog | ControlledBy_Control | MeasuredBy_Measurement | 0..1 | 0..1 | ParentChild | cim | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Analog
|  | CIMMeas | SetPoint | HasNameOf | SetPointName | SetPoint | SetPointName | 0..n | 1 | Attributive | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has Name Of (SetPointName)
|  | ETXSCADA | SetPointLock | AssignedTo | AnalogValue | SetPointLock | AnalogValue | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Assigned To (AnalogValue)
|  | ETXSCADA | SetPointLock | AssignedTo | DiscreteValue | SetPointLock | DiscreteValue | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Assigned To (DiscreteValue)
|  | ETXSCADA | SetPointLock | LockedBy | SetPoint | SetPointLock | SetPoint | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Locked By (SetPoint)
|  | ETX | SettlementLoadZone | Contains | Substation | SettlementLoadZone | Substation | 0..1 | 1..n | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Contains (Substation)
|  | ETX | SettlementNOIELoadZone | Contains | EnergyConsumer | SettlementNOIELoadZone | EnergyConsumer | 0..1 | 0..n | Reference | etx | FALSE | TRUE | FALSE | FALSE |  | FALSE |  | Contains (EnergyConsumer)
|  | CIMWires | ShuntCompensator | SwitchedBy | Switch | ShuntCompensator | Switch | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Switched By (Switch)
|  | CIMProduction | ShutdownCurve | MemberOf | ThermalGeneratingUnit | ShutdownCurve | ThermalGeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
|  | ETXRASE | Stage | MemberOf | RemedialActionScheme | Stage | RemedialActionScheme | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has (RemedialActionScheme)
|  | ETXRASE | StageTrigger | MemberOf | Stage | StageTrigger | Stage | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (Stage)
|  | ETXRASE | StageTrigger | TriggeredBy | TriggerCondition | StageTrigger | TriggerCondition | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Triggered By (TriggerCondition)
|  | CIMProduction | StartIgnFuelCurve | MemberOf | StartupModel | StartIgnFuelCurve | StartupModel | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | StartupModel
|  | CIMProduction | StartMainFuelCurve | MemberOf | StartupModel | StartMainFuelCurve | StartupModel | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | StartupModel
|  | CIMProduction | StartRampCurve | MemberOf | StartupModel | StartRampCurve | StartupModel | 0..1 | 1 | ParentChild | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | StartupModel
|  | CIMProduction | StartupModel | MemberOf | ThermalGeneratingUnit | StartupModel | ThermalGeneratingUnit | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ThermalGeneratingUnit
|  | CIMLoadModel | StationSupply | Follows | SynchronousMachine | StationSupply | SynchronousMachine | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Follows (SynchronousMachine)
|  | ETXNetwork | StationSupplyWRCurve | HasA | StationSupply | StationSupplyWRCurve | StationSupply | 0..1 | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | StationSupply
|  | CIMProduction | SteamSendoutSchedule | MemberOf | CogenerationPlant | SteamSendoutSchedule | CogenerationPlant | 0..1 | 0..1 | ParentChild | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | CogenerationPlant
|  | CIMGenerationDynamics | SteamSupply | Supplies | SteamTurbine | SteamSupplys | SteamTurbines | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Supplies
|  | CIMMeas | StringMeasurementValue | MemberOf | StringMeasurement | Contains_MeasurementValues | MemberOf_Measurement | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | StringMeasurement
|  | CIMCore | SubControlArea | Contains | GeneratingUnit | SubControlArea | GeneratingUnits | 0..1 | 0..n | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | GeneratingUnit
|  | CIMCore | SubGeographicalRegion | MemberOf | GeographicalRegion | Regions | Region | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | GeographicalRegion
|  | CIMCore | SubGeographicalRegion | References | HostControlArea | SubGeographicalRegion | HostControlArea | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (HostControlArea)
|  | CIMLoadModel | SubLoadArea | MemberOf | LoadArea | SubLoadAreas | LoadArea | 0..n | 1 | ParentChild | cim | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | LoadArea
|  | CIMCore | Substation | Has | PermissionArea | Substation | PermissionArea | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has (PermissionArea)
|  | CIMCore | Substation | MemberOf | SubControlArea | Contain_Substations | MemberOf_SubControlArea | 0..n | 0..1 | ParentChild | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | SubControlArea
|  | CIMCore | Substation | MemberOf | SubGeographicalRegion | Substations | Region | 0..n | 0..1 | ParentChild | cim | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | SubGeographicalRegion
|  | CIMCore | Substation | MemberOf | SubLoadArea | Substation | LoadZone | 0..n | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | LoadZone
|  | CIMCore | Substation | References | HostControlArea | Substation | HostControlArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | References (HostControlArea)
|  | ETX | SupportLoadData | BelongTo | ConformLoad | SupportLoadData | ConformLoad | 0..1 | 1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ConformLoad
|  | CIMWires | Switch | HasA | EnergyConsumerResource | Switch | LR | 0..1 | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HasA (LoadResource)
|  | CIMWires | Switch | MemberOf | CompositeSwitch | Switches | CompositeSwitch | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | CompositeSwitch
|  | CIMWires | Switch | OperatedBy | SwitchingOperation | Switches | SwitchingOperations | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Operated By (SwitchingOperation)
DD-1.21.1-001 OTS | INSERT | CIMWires | Switch | operatedDuringStartStop | GeneratingUnit | Switch | GeneratingUnit | 0..n | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | operatedDuringStartStop (GeneratingUnit)
|  | ETX_ABB | SwitchSchedule | HasA | DayType | SwitchSchedule | DayType | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (DayType)
|  | ETX_ABB | SwitchSchedule | HasA | Season | SwitchSchedule | Season | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (Season)
|  | ETX_ABB | SwitchSchedule | MemberOf | Switch | SwitchSchedules | Switch | 0..n | 1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Switch
|  | CIMWires | SynchronousMachine | BelongsTo | SubLoadArea | LoadZone | SynchronousMachine | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Belongs To (LoadZone)
|  | CIMWires | SynchronousMachine | Drives | PrimeMover | Drives_SynchronousMachine | DrivenBy_PrimeMover | 0..n | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Drives (SynchronousMachine)
|  | CIMWires | SynchronousMachine | HasA | AccuracyClass | SynchronousMachine | AccuracyClass | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (AccuracyClass)
|  | CIMWires | SynchronousMachine | HasDefault | MVArCapabilityCurve | InitiallyUsedBySynchronousMachine | InitiallyUsesMVArCapabilityCurve | 1..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | Has Default (MVArCapabilityCurve)
|  | CIMWires | SynchronousMachine | MemberOf | GeneratingUnit | Contains_SynchronousMachines | MemberOf_GeneratingUnit | 0..1 | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | GeneratingUnit
|  | ETX_ABB | SyncMachineSchedule | HasA | DayType | SyncMachineSchedule | DayType | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (DayType)
|  | ETX_ABB | SyncMachineSchedule | HasA | Season | SyncMachineSchedule | Season | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (Season)
|  | ETX_ABB | SyncMachineSchedule | MemberOf | SynchronousMachine | SyncMachineSchedules | SynchronousMachines | 0..n | 1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | SynchronousMachine
|  | RDF_Import | sysOrphan | MemberOf | sysOrphans | sysOrphan_MemberOf | MemberOf_sysOrphans | 0..n | 0..1 | ParentChild | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | sysOrphans
|  | RDF_Import | sysOrphan | OwnedBy | Ownership | sysOrphan | Ownership | 0..n | 0..n | Reference | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Owned By (Ownership)
|  | RDF_Import | sysRdfContainer | HasA | Domain | sysRdfContainer_HasA | HasA_Domain | 0..1 | 0..1 | Reference | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Orphan Root
|  | RDF_Import | sysRdfContainer | MemberOf | sysRdfContainers | sysRdfContainer_MemberOf | MemberOf_sysRdfContainers | 0..n | 0..1 | ParentChild | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | sysRdfContainers
|  | Engineering_sysTreeCategory | sysTreeCategory | MemberOf | RootType | sysTreeCategory_MemberOf | MemberOf_RootType | 0..n | 0..n | ParentChild | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | RootType
|  | Engineering_sysTreeCategory | sysTreeCategory | OwnedBy | Ownership | sysTreeCategory | Ownership | 0..n | 0..n | Reference | spc | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | OwnedBy (Ownership)
|  | CIMProduction | TailbayLossCurve | HasA | HydroGeneratingUnit | TailbayLossCurve | HydroGeneratingUnit | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | HydroGeneratingUnit
|  | CIMWires | TapChanger | HasA | PhaseShifterImpedanceCurve | TapChanger | PhaseShifterImpedanceCurve | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (PhaseShifterImpedanceCurve)
DD-1.21.1-001 | DELETE | CIMWires | TapChanger | HasA | PhaseShifterImpedanceCurve | TapChanger | PhaseShifterImpedanceCurve | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has A (PhaseShifterImpedanceCurve)
|  | CIMWires | TapChanger | HasA | RegulationSchedule | TapChangers | RegulationSchedule | 0..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | RegulationSchedule
|  | CIMWires | TapChanger | HasA | TapRatioCurve | TapChanger | TapRatioCurve | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (TapRatioCurve)
|  | CIMWires | TapChanger | HasA | TransformerWinding | TapChangers | TransformerWinding | 0..n | 1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | TransformerWinding
|  | CIMWires | TapChanger | HasAMaster | TapChanger | TapChanger | TapChanger | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A Master (TapChanger)
|  | CIMWires | TapChanger | RegulatedBy | LoadBasedRegulationCurve | TapChanger | LoadBasedRegulationCurve | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Regulated By (LoadBasedRegulationCurve)
|  | CIMWires | TapChanger | Regulates | Measurement | TapChangers | Measurement | 0..n | 0..1 | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Regulates (Measurement)
|  | CIMWires | TapChanger | Regulates | Terminal | TapChanger | Terminal | 0..n | 0..1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Regulates (Terminal)
|  | ETX_ABB | TapSchedule | HasA | DayType | TapSchedule | DayType | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (DayType)
|  | ETX_ABB | TapSchedule | HasA | Season | TapSchedule | Season | 0..n | 0..1 | Attributive | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (Season)
|  | ETX_ABB | TapSchedule | MemberOf | TapChanger | TapSchedules | TapChanger | 0..n | 1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TapChanger
|  | CIMProduction | TargetLevelSchedule | HasA | Reservoir | TargetLevelSchedule | Reservoir | 0..1 | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Reservoir
|  | CIMCore | Terminal | ConnectedTo | ConnectivityNode | Terminals | ConnectivityNode | 0..n | 0..1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | ConnectivityNode
|  | CIMCore | Terminal | ExternalConnectionFor | ConductingEquipment | Terminals | ConductingEquipment | 0..n | 1..1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | ConductingEquipment
DD-1.21.1-001 | UPDATE | CIMCore | Terminal | ExternalConnectionFor | ConductingEquipment | Terminals | ConductingEquipment | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | ConductingEquipment
|  | CIMProduction | ThermalGeneratingUnit | MemberOf | CAESPlant | Contain_ThermalGeneratingUnit | MemberOf_CAESPlant | 0..1 | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Member Of (CAESPlant)
|  | CIMProduction | ThermalGeneratingUnit | MemberOf | CogenerationPlant | Contain_ThermalGeneratingUnits | MemberOf_CogenerationPlant | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Member Of (CogenerationPlant)
|  | CIMProduction | ThermalGeneratingUnit | MemberOf | CombinedCyclePlant | Contain_ThermalGeneratingUnits | MemberOf_CombinedCyclePlant | 0..n | 0..1 | Reference | cim | TRUE | FALSE | TRUE | FALSE |  | FALSE |  | Member Of (CombinedCyclePlant)
|  | ETX_Areva | TieCorridor | ConnectsFrom | HostControlArea | TieCorridor_Out | From_HostControlArea | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Connects From (HostControlArea)
|  | ETX_Areva | TieCorridor | ConnectsFrom | SubLoadArea | TieCorridor_Out | From_SubLoadArea | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Connects From (SubLoadArea)
|  | ETX_Areva | TieCorridor | ConnectsTo | HostControlArea | TieCorridor_In | To_HostControlArea | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | HostControlArea
|  | ETX_Areva | TieCorridor | ConnectsTo | SubLoadArea | TieCorridor_In | To_SubLoadArea | 0..n | 0..1 | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Connects To (SubLoadArea
|  | ETX_Areva | TieEnd | MemberOf | PhysicalTiePoint | TieEnd | PhysicalTiePoint | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | PhysicalTiePoint
DD-1.21.1-003 | UPDATE | ETX_Areva | TieLine | BelongsTo | TieCorridor | TieLine | TieCorridor | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TieCorridor
|  | ETX_Areva | TieLine | HasA | Terminal | TieLine | Terminal | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Terminal
|  | ETX_Areva | TieLine | Reference | Substation | TieLine | Substation | 0..n | 0..1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Reference (Substation)
|  | CIMTopology | TopologicalNode | MemberOf | TopologicalIsland | TopologicalNodes | TopologicalIsland | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | TopologicalIsland
|  | ETXNetwork | TransformerImpedanceCurve | HasA | TransformerWinding | TransformerImpedanceCurve | TransformerWinding | 0..n | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TransformerWinding
DD-1.21.1-001 | UPDATE | ETXNetwork | TransformerImpedanceCurve | HasA | TransformerWinding | TransformerImpedanceCurve | TransformerWinding | 0..1 | 0..1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | TransformerWinding
|  | ETX | TransformerKluge | HasA | PowerTransformer | TransformerKluge | PowerTransformer | 0..1 | 0..n | Reference | etx | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Has A (PowerTransformer)
|  | CIMWires | TransformerWinding | FromTest | WindingTest | From_TransferWinding | From_WindingTests | 1 | 0..n | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | From (TransformerWinding)
|  | CIMWires | TransformerWinding | HasA | PowerTransformer | Contains_TransformerWindings | MemberOf_PowerTransformer | 0..n | 1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | PowerTransformer
|  | CIMWires | TransformerWinding | To | WindingTest | To_TransformerWindings | To_WindingTest | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | To (WindingTest)
|  | Reservation | TransmissionPath | HasPOD | ServicePoint | HasAPOD_ | DeliveryPointFor | 0..n | 1..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | POD ServicePoint
|  | Reservation | TransmissionPath | HasPOR | ServicePoint | HasAPOR_ | PointOfReceiptFor | 0..n | 1..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | POR ServicePoint
|  | ETX | TransState | FromConfig | Configuration | TransState_FromConfig | FromConfig_Configuration | 1..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | From Config (Configuration)
DD-1.21.1-001 | UPDATE | ETX | TransState | FromConfig | Configuration | TransState_FromConfig | FromConfig_Configuration | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | From Config (Configuration)
dup req | UPDATE | ETX | TransState | FromConfig | Configuration | TransState_FromConfig | FromConfig_Configuration | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | From Config (Configuration)
|  | ETX | TransState | ToConfig | Configuration | TransState_ToConfig | ToConfig_Configuration | 1..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | To Config (Configuration)
DD-1.21.1-001 | UPDATE | ETX | TransState | ToConfig | Configuration | TransState_ToConfig | ToConfig_Configuration | 0..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | To Config (Configuration)
dup req | UPDATE | ETX | TransState | ToConfig | Configuration | TransState_ToConfig | ToConfig_Configuration | 0..n | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | To Config (Configuration)
|  | ETXRASE | TriggerCondition | HasResulting | Gate | TriggerCondition | ResultingGate | 0..1 | 1 | Reference | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has Resulting (Gate)
|  | ETXRASE | TriggerCondition | MemberOf | RemedialActionScheme | TriggerCondition | RemedialActionScheme | 0..n | 1 | ParentChild | etx | FALSE | TRUE | TRUE | FALSE |  | FALSE |  | Has (TriggerCondition)
|  | CIMMeas | ValueAliasSet | Controls | Command | ValueAliasSet | Controls | 0..1 | 0..n | Reference | cim | TRUE | FALSE | FALSE | FALSE |  | FALSE |  | Controls (Command)
|  | CIMMeas | ValueToAlias | MemberOf | ValueAliasSet | Values | ValueAliasSet | 0..n | 1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ValueAliasSet
|  | ETXMonitoring | VLSBusBarMonitored | IsMonitored | BusbarSection | VLSBusBarMonitored | BusbarSection | 0..1 | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Is Monitored (BusbarSection)
|  | ETXMonitoring | VLSBusBarMonitored | Uses | VoltageLimitSet | VLSBusBarMonitored | VoltageLimitSet | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Uses (VoltageLimitSet)
|  | CIMWires | VoltageControlZone | ControlledBy | BusbarSection | VoltageControlZone | BusbarSection | 0..1 | 1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Controlled By (BusbarSection)
|  | CIMWires | VoltageControlZone | RegulatedBy | RegulationSchedule | VoltageControlZones | RegulationSchedule | 0..n | 0..1 | Reference | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | Regulated By (RegulationSchedule)
|  | CIMCore | VoltageLevel | HasA | BaseVoltage | VoltageLevel | BaseVoltage | 0..n | 1 | Reference | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | BaseVoltage
|  | CIMCore | VoltageLevel | MemberOf | Substation | Contains_VoltageLevels | MemberOf_Substation | 0..n | 0..1 | ParentChild | cim | TRUE | TRUE | TRUE | FALSE |  | FALSE |  | Substation
|  | ETXMonitoring | VoltageLimit | HasA | VoltageLimitSet | VoltageLimit | VoltageLimitSet | 0..n | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Has A (VoltageLimitSet)
|  | ETXMonitoring | VoltageMonitored | IsMonitored | VoltageLevel | VoltageMonitored | VoltageLevel | 0..1 | 1 | ParentChild | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Is Monitored (VoltageLevel)
|  | ETXMonitoring | VoltageMonitored | Uses | VoltageLimitSet | VoltageMonitored | VoltageLimitSet | 0..n | 1 | Reference | etx | FALSE | FALSE | TRUE | FALSE |  | FALSE |  | Uses (VoltageLimitSet)
|  | CIMWires | WireArrangement | MemberOf | ConductorType | WireArrangements | ConductorType | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | ConductorType
|  | CIMWires | WireArrangement | MemberOf | WireType | WireArrangements | WireType | 0..n | 0..1 | ParentChild | cim | FALSE | FALSE | FALSE | FALSE |  | FALSE |  | WireType