ERCOT Operations Report

July 2009 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 7/6/2009 20:20 | 59.804 | 106 | Unit trip with 815 MW |
| 7/7/2009 11:59 | 59.889 | 4 | Unit trip with 603 MW |
| 7/8/2009 15:17 | 59.895 | 4 | Unit trip with 530 MW |
| 7/9/2009 23:02 | 59.87 | 246 | SCE change -300 MW in 3 minutes and offset calculation error |
| 7/13/2009 22:02 | 59.873 | 32 | Unit trip with 467 MW |
| 7/17/2009 4:03 | 59.881 | 64 | Unit trip with 460 MW |
| 7/20/2009 7:08 | 59.886 | 8 | Unit trip with 490 MW |
| 7/20/2009 16:14 | 59.883 | 8 | Unit trip with 470 MW |
| 7/30/2009 0:05 | 59.886 | 152 | SCE change -600 MW in 5minutes, out of up regulation |
| 7/30/2009 15:26 | 59.872 | 8 | Unit trip with 592 MW |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 7/2/09 16:58:06 | 7/2/09 17:08:44 | 0:10:38 | 337.9 | Unit Trip |
| 7/6/09 20:20:44 | 7/6/09 20:41:54 | 0:21:10 | 876.5 |  |
| 7/7/09 11:59:58 | 7/7/09 12:10:08 | 0:10:10 | 427.7 |  |
| 7/8/09 15:17:26 | 7/8/09 15:30:30 | 0:13:04 | 396.0 |  |
| 7/9/09 22:58:48 | 7/9/09 23:27:00 | 0:28:12 | 528.0 |  |
| 7/13/09 22:02:46 | 7/13/09 22:20:48 | 0:18:02 | 507.8 |  |
| 7/17/09 04:03:39 | 7/17/09 04:19:53 | 0:16:14 | 469.9 |  |
| 7/17/09 18:31:49 | 7/17/09 18:47:43 | 0:15:54 | 332.6 | Offset calculation error |
| 7/19/09 22:01:06 | 7/19/09 22:13:00 | 0:11:54 | 327.4 | Large SCE change (-1000 MW in 7minutes) |
| 7/20/09 07:08:20 | 7/20/09 07:17:54 | 0:09:34 | 443.5 |  |
| 7/20/09 10:06:08 | 7/20/09 10:31:56 | 0:25:48 | 327.4 | Slow unit response. |
| 7/20/09 16:14:08 | 7/20/09 16:27:36 | 0:13:28 | 459.3 |  |
| 7/30/09 00:00:40 | 7/30/09 00:24:06 | 0:23:26 | 443.5 |  |
| 7/30/09 15:26:25 | 7/30/09 15:43:53 | 0:17:28 | 517.4 |  |

Day-Ahead OOMC and RPRS Capacity Purchases

| Details | OOMC | RPRS S1 | RPRS S2 | RPRS S1+S2 | RMR | Total |
| --- | --- | --- | --- | --- | --- | --- |
| Houston | 2 | 35 | 72 | 107 | 0 | 109 |
| DFW | 24 | 4 | 62 | 66 | 0 | 90 |
| North | 12 | 34 | 38 | 72 | 0 | 84 |
| Western | 4 | 6 | 27 | 33 | 9 | 46 |
| South | 0 | 13 | 2 | 15 | 0 | 15 |
| San Antonio | 3 | 11 | 0 | 11 | 0 | 14 |
| E RIO | 2 | 7 | 0 | 7 | 0 | 9 |
| Austin | 0 | 5 | 1 | 6 | 0 | 6 |
| Bryan Area | 0 | 0 | 4 | 4 | 0 | 4 |
| Northeast | 2 | 0 | 1 | 1 | 0 | 3 |
| Laredo | 0 | 0 | 0 | 0 | 0 | 0 |
| Corpus | 0 | 0 | 0 | 0 | 0 | 0 |
| W RIO | 0 | 0 | 0 | 0 | 0 | 0 |
| Total | 49 | 115 | 207 | 322 | 9 | 380 |

| Historical Totals | Jul-09 | Jul-08 | Jun-09 |
| --- | --- | --- | --- |
| Austin | 5 | 13 | 5 |
| Bryan Area | 0 | 2 | 5 |
| Corpus | 0 | 1 | 15 |
| DFW | 28 | 14 | 51 |
| E RIO | 9 | 1 | 31 |
| Houston | 37 | 43 | 2 |
| Laredo | 0 | 87 | 14 |
| North | 46 | 50 | 37 |
| Northeast | 2 | 1 | 0 |
| San Antonio | 14 | 7 | 12 |
| South | 13 | 1 | 11 |
| W RIO | 0 | 0 | 1 |
| Western | 19 | 4 | 14 |
| Total | 173 | 224 | 198 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages  Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Dilley Switch - San Miguel Switch 138KV | Derby - Pearsall 69KV | 29 |
| Temple Pecan Creek - Tradinghouse and Temple Switch - Lake Creek 345KV | San Angelo Power Station - Shrew Tap 138KV | 19 |
| Aspermont - Spur 138KV | Jayton - Spur 69KV | 12 |
| Garfield - Onion and Hicross 138KV | Lytton Springs - Pilot Knob 138KV | 7 |
| Hill Country - Marion and Elm Creek 345KV | Marion - Skyline 345KV | 7 |
| Hill Country 345/138KV AT 3 | Hill Country 345/138KV AT 2 | 6 |
| San Miguel Switchyard 345/138Kv autotransformer "A" | San Miguel Switchyard 345/138Kv autotransformer "B" | 6 |
| Skyline - Marion and Elm Creek 345KV | Schertz - Parkway 138KV | 6 |
| Graham - Long Creek 345KV | San Angelo Power Station - Shrew 138KV | 5 |
| North Denton - West Denton 138KV | West Denton - Teasley 138KV | 5 |
| Abilene South - Eskota Switch 138KV | Merkel - Trent 69KV | 5 |
| Austrop - Daffin and Decker 138KV | Decker - Sprinkle 138KV | 5 |
| North Denton T1 138/69KV AT | North Denton T2 138/69KV AT | 4 |
| Odessa EHV Switch 345/138KV T2 | Odessa EHV Switch 345/138KV T1 | 4 |
| Garfield - Onion Creek - Hicross 138KV | Austrop - Decker 138KV | 2 |
| Nueces Bay - Whitepoint #1 138KV | Nueces Bay - Whitepoint #2 138KV | 2 |
| Valley SES - Payne Switch 138KV | Denison North - Denison Dam Tap 138KV | 2 |
| West Levee Switch T1 345/138KV AT | Compton Street - Industrial Blvd 138KV | 2 |
| Chambers - King Reit and Cedar Bayou - North Belt 345KV | Baytown - Haney 138KV | 2 |
| Morgan Creek SES - Quail Switch and Longshore Switch Station 345KV | Midland East - Stanton Switch 138KV | 2 |
| Morgan Creek SES - Quail Switch and Longshore Switch Station 345KV | Stanton East Switching Station - Big Spring West138KV | 2 |
| North Denton - West Denton 138KV | Pockrus - West Denton 138KV | 2 |
| Sandow Switch - Temple Switch 345KV | Hearne 138/69KV transformer | 2 |
| Skyline - Marion and Elm Creek 345KV | Hill Country - Marion 345KV | 2 |
| Cagnon 345/138KV transformer T3 | Cagnon T4 345/138KV | 1 |
| Enterprise - Trinidad SES & Martin Lake SES - Stryker Creek SES 345KV | Nacogdoches 345/138KV autotransformer | 1 |
| Hill Country 345/138KV AT 2 | Hill Country 345/138KV AT 3 | 1 |
| Jack County - Reno 138KV | Decatur - Decatur Tap 138KV | 1 |
| Wink - No Trees 138KV | Holt Switch - Emma Tap 69KV | 1 |
| Trinidad SES - Stryker SES and Mount Enterprise 345 KV | Stryker Creek SES - Stryker Cherokee POI | 1 |
| Austrop 345/138KV AT 2 | Austrop 345/138KV AT1 | 1 |
| Basecase | San Angelo Power Station - Shrew Tap 138KV | 1 |
| Bates - Pearsall 138KV | Derby - Pearsall 69KV | 1 |
| Cedar Hill Switch 345/138KV AT 2 | Sherry Switch - Park Row 138KV | 1 |
| Denton 138/69KV autotransformer #1 | Spencer - King 69KV | 1 |
| Elgin Switch - Sandow Switch 138KV | Sandow Switch - Salty 138KV | 1 |
| Garfield - Onion Creek - Hicross 138KV | Austrop - Daffin 138KV | 1 |
| Garfield - Onion Creek - Hicross 138KV | Daffin - Decker 138KV | 1 |
| Geronimo - Clear Springs 138KV | Marion - Cibolo 138KV | 1 |
| Heights Sub - Freeway Park 138KV | Greenbelt - Gaf Sub 138KV | 1 |
| Moss Switch - Holt Switch 138KV | Odessa North - North Cowden 69KV | 1 |
| Trinidad SES - Stryker Creek SES & Mount Enterprise 345KV | Lufkin Switch - Lufkin Chipper Mill 138KV | 1 |
| Watermill - West Levee - Sargent Rd 345KV | Norwood 345/138KV Auto #1 | 1 |
| West Levee Switch T2 345/138KV AT | West Levee Switch T1 345/138KV AT | 1 |
| Zorn autotransformer #2 345/138KV | Zorn autotransformer #1 345/138KV | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| West-North | 8 |
| North-Houston | 6 |
| North-South | 1 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 07/16/2009 | Transmission and Security Desk V4 R3 | 427 |
| 07/16/2009 | Shift Supervisor Desk V4 R3 | 426 |
| 07/16/2009 | Frequency Control Desk V4 R3 | 425 |
| 07/16/2009 | Day Ahead Desk V4 R3 | 424 |
| 07/16/2009 | Operating Period Desk V 3 R 4 | 423 |

## Blackout/Load Shed Incidences

None

EEA

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

07/17  07:15	Held Real-time Balancing deployments for interval ending 07:15 due to 07:30 Real-time Balancing Market failed to execute. Resumed with interval ending 07:45 deployments.

Communication

None

## ERCOT peak (Unofficial)

07/13 	   17:00 63,453 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2006 | 2007 | 2008 | 2009 |
| January | 4.79 | 4.55 | 3.30 | 4.11 |
| February | 4.81 | 3.75 | 3.59 | 3.49 |
| March | 4.95 | 2.70 | 3.29 | 3.24 |
| April | 5.59 | 3.00 | 2.45 | 2.66 |
| May | 3.59 | 3.22 | 3.01 | 2.90 |
| June | 2.65 | 4.46 | 2.81 | 2.89 |
| July | 2.62 | 4.29 | 2.55 | 2.83 |
| August | 2.09 | 3.11 | 3.66 | NA |
| September | 4.03 | 3.78 | 4.99 | NA |
| October | 3.63 | 3.08 | 2.79 | NA |
| November | 3.28 | 2.95 | 2.60 | NA |
| December | 3.44 | 3.74 | 4.54 | NA |
| Annual Average | 3.79 | 3.55 | 3.29 | 3.16 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 7/2/09 | 15:30 | 18:00 | Advisory issued for ARR below 3000 MW. |
| 7/3/09 | 16:16 | 18:40 | Advisory issued for ARR below 3000 MW. |
| 7/8/09 | 2:45 | 11:24 | Operating Condition Notice (OCN) issued due to projected reserve capacity shortage for HE 15:00 - 21:00. |
| 7/8/09 | 15:22 | 18:00 | Advisory issued due to ARR below 3000 MW. |
| 7/8/09 | 7:35 | 24:00 | OCN issued due to high pressure influencing much of Texas weather. ERCOT is expecting high electricity demand for the remainder of the week due to the heat advisory in effect for much of the state. ERCOT does not anticipate any electricity emergencies. |
| 7/8/09 | 11:24 | 18:00 | Watch issued due to projected reserve capacity shortage for HE 15:00 - 18:00. |
| 7/9/09 | 0:15 | 24:00 | OCN issued due to high pressure influencing much of Texas weather. ERCOT is expecting high electricity demand for the remainder of the week due to the heat advisory in effect for much of the state. ERCOT does not anticipate any electricity emergencies. |
| 7/10/09 | 0:15 | 24:00 | OCN issued due to high pressure influencing much of Texas weather. ERCOT is expecting high electricity demand for the remainder of the week due to the heat advisory in effect for much of the state. ERCOT does not anticipate any electricity emergencies. |
| 7/10/09 | 15:17 | 18:00 | Advisory issued due to ARR below 3000 MW. |
| 7/11/09 | 0:15 | 24:00 | OCN issued due to high pressure influencing much of Texas weather. ERCOT is expecting high electricity demand for the remainder of the week due to the heat advisory in effect for much of the state. ERCOT does not anticipate any electricity emergencies. |
| 7/12/09 | 0:15 | 24:00 | OCN issued due to high pressure influencing much of Texas weather. ERCOT is expecting high electricity demand for the remainder of the week due to the heat advisory in effect for much of the state. ERCOT does not anticipate any electricity emergencies. |
| 7/12/09 | 13:33 | 19:30 | OCN issued for a potential reserve capacity shortage for HE 15:00 - 20:00. |
| 7/12/09 | 13:40 | 20:30 | Advisory issued for ARR below 3000 MW |
| 7/13/09 | 0:15 | 24:00 | OCN issued due to high pressure influencing much of Texas weather. ERCOT is expecting high electricity demand for the remainder of the week due to the heat advisory in effect for much of the state. ERCOT does not anticipate any electricity emergencies. |
| 7/13/09 | 13:30 | 20:15 | Advisory issued for ARR below 3000 MW |
| 7/14/09 | 0:15 | 24:00 | OCN issued due to high pressure influencing much of Texas weather. ERCOT is expecting high electricity demand for the remainder of the week due to the heat advisory in effect for much of the state. ERCOT does not anticipate any electricity emergencies. |
| 7/14/09 | 15:20 | 18:30 | Advisory issued for ARR below 3000 MW |
| 7/15/09 | 0:15 | 24:00 | OCN issued due to high pressure influencing much of Texas weather. ERCOT is expecting high electricity demand for the remainder of the week due to the heat advisory in effect for much of the state. ERCOT does not anticipate any electricity emergencies. |
| 7/16/09 | 0:15 | 24:00 | OCN issued due to high pressure influencing much of Texas weather. ERCOT is expecting high electricity demand for the remainder of the week due to the heat advisory in effect for much of the state. ERCOT does not anticipate any electricity emergencies. |
| 7/16/09 | 12:45 | 18:00 | OCN issued due to projected reserve capacity shortage for HE 16:00 - 18:00. |
| 7/16/09 | 16:55 | 18:00 | Advisory issued for ARR below 3000 MW. |
| 7/17/09 | 0:15 | 24:00 | OCN issued due to high pressure influencing Central Texas weather. ERCOT is expecting high electricity demand for the remainder of the week due to the heat advisory in effect for much of the state. ERCOT does not anticipate any electricity emergencies. |
| 7/18/09 | 5:45 | 17:30 | OCN issued due to projected reserve capacity shortage for HE 1500 - HE 1900. |
| 7/19/09 | 15:40 | 17:30 | OCN issued due to projected reserve capacity shortage for HE 1700 - HE 1900. |
| 7/20/09 | 10:00 | 13:00 | OCN issued due to projected reserve capacity shortage for HE 1600 - HE 1800. |
| 7/25/09 | 16:39 | 19:45 | Advisory issued for ARR below 3000 MW. |
| 7/26/09 | 15:20 | 18:45 | Advisory issued for ARR below 3000 MW. |
| 7/28/09 | 14:56 | 19:15 | Advisory issued for ARR below 3000 MW. |
| 7/28/09 | 15:28 | 18:00 | OCN issued due to projected reserve capacity shortage for HE 17:00 - 19:00. |

Transmission Watch

07/08  11:24	ERCOT issued a transmission Watch issued due to contingency loss of Dilley Switch – San Miguel Switch overloads Pearsall Switch – Derby Sub.  ERCOT received emergency energy from CFE across the Laredo VFT.

07/10  18:00	ERCOT issued a transmission Watch issued due to forced outage and post contingency loss of Dilley Switch – San Miguel Switch overloads Pearsall Switch – Derby Sub.  ERCOT received emergency energy from CFE across the Laredo VFT.

07/15  16:16	Transmission Watch issued due to forced outage and for post contingent loss of Hill Country 345/138KV auto #3 overloads Hill Country auto #2.

.

07/17  14:20	ERCOT issued a transmission Watch issued due to forced outage and post contingency loss of Dilley Switch – San Miguel Switch overloads Pearsall Switch – Derby Sub.  ERCOT received emergency energy from CFE across the Laredo VFT.

07/26  12:43	ERCOT issued a transmission Watch issued due to forced outage and post contingency loss of Dilley Switch – San Miguel Switch overloads Pearsall Switch – Derby Sub.  ERCOT received emergency energy from CFE across the Laredo VFT.

Emergency Notice

07/17  13:30	Market Emergency Notice issued due to the procurement of the Ancillary Service Market did not meet the market time line requirement.  Market Emergency Notice issued for extending the procurement of the A/S Market due to communication issues.

Texas RE Event Analysis

07/17   13:30   Market Emergency Notice issued for Ancillary Services Market delay.

07/30   16:50   Loss of a QSE & TDSP’s primary control center.