# 2010 CSC Study

Version 1.0

Document Revisions

| Date | Version | Description | Author(s) |
| --- | --- | --- | --- |
| 07/16/2009 | 0.1 | First draft | Chris Ngai |
| 07/17/2009 | 0.2 | Formatted and added congestion data. | Isabel Flores |
| 07/20/2009 | 0.3 | Corrections to Section 3 & updated table of contents | Isabel Flores |
| 07/23/2009 | 0.4 | Revised scenarios to reflect case update; added scenario 12 | Isabel Flores |
| 07/30/2009 | 0.5 | Revised all scenarios to incorporate case corrections. | Isabel Flores |
| 07/31/2009 | 0.6 | Added 5 scenarios & corrected scenarios SN1-4Z and SN1-5Z. | Isabel Flores |
| 08/03/2009 | 0.7 | Updated scenarios FW1_WN1 & FW2_WN1. | Isabel Flores |
| 08/07/2009 | 0.8 | Added scenarios FW1_WN2-5Z, WN2_SN2-5Z & WN2_SN2-6Z Included ERCOT’s recommendation | Isabel Flores |
| 8/10/2009 | 0.9 | Added scenarios WN3_SN0-4Z; WN4_SN0-4Z; FW1_WN4_SN0-5Z | Isabel Flores |
| 8/11/2009 | 1.0 | Correction to Table 1b & updates to scenario matrix | Isabel Flores |

Table of Contents

2010 CSC Study	1

2010 CSC Analysis	1

1.	Background	1

2.	2010 Significant Changes to the ERCOT Grid	1

3.	Transfer Study	3

4.	Evaluation of Current Congestion Events	3

5.	Projection of Future Congestion	6

6.	Cluster Analysis	6

6.1.	Scenario 1	7

6.2.	Scenario 1a – Current 2009 CSCs	7

6.3.	Scenario WN1-4Z	7

6.4.	Scenario WN1-5Z – eliminated 8/10/2009	7

6.5.	Scenario WN1-6Z – eliminated 8/02/2009	7

6.6.	Scenario WN2-4Z	7

6.7.	Scenario WN2-5Z – eliminated 8/10/2009	7

6.8.	Scenario WN2-6Z – eliminated 8/04/2009	7

6.9.	Scenario WN3-4Z – eliminated 8/10/2009	7

6.10.	Scenario WN3-5Z – eliminated 8/10/2009	7

6.11.	Scenario WN3-6Z – eliminated 8/04/2009	7

6.12.	Scenario NH4L-4Z - eliminated 8/04/2009	7

6.13.	Scenario SN1-4Z - eliminated 8/04/2009	7

6.14.	Scenario SN1-5Z - eliminated 8/04/2009	7

6.15.	Scenario FW1-5Z	7

6.16.	Scenario FW2-5Z - eliminated	7

6.17.	Scenario FW1_WN1-5Z	7

6.18.	Scenario FW2_WN1-5Z - eliminated	7

6.19.	Scenario WN2_SN1_NH4L - eliminated	7

6.20.	Scenario WN2_SN2-5Z – eliminated 8/10/2009	7

6.21.	Scenario WN2_SN2-6Z – eliminated 8/10/2009	7

6.22.	Scenario FW1_WN2-5Z	7

6.23.	Scenario WN3_SN0-4Z	7

6.24.	Scenario WN4_SN0-4Z	7

6.25.	Scenario FW1_WN4_SN0-4Z	7

7.	ERCOT Recommendation	7

# 2010 CSC Analysis

# Background

Protocol Section 7.2.1 requires ERCOT Staff to conduct an annual analysis to determine the upcoming year’s Commercially Significant Constraints (CSCs).  This analysis may include a transfer study, an evaluation of past congestion costs, and a projection of congestion costs for the upcoming year; ERCOT’s analysis includes all of these features.

# 2010 Significant Changes to the ERCOT Grid

Per the May 2009 TPIT, these are the significant transmission projects scheduled to go in-service by the end of 2010:

- Hutto Switch and 345/138 kV autotransformer (June 2010)

- Sandow Switch - Sandow Third 138 kV line (May 2010)

- Sandow Switch Third 345/138 kV autotransformer (May 2010)

- Anderson to Westover Hills - New 138kV Transmission Line (June 2010)

- Sandow Switch - Elgin Switch 138 kV line (Oct 2010)

- Decker to Techridge 138kV Circuit Relocation (Nov 2010)

- Rothwood 345/138 kV substation (May 2010)

- Hutto - Salado new 345 (6/2010) #08TPIT0003

- Bowman - Jacksboro 345 reconductor (6/2010 -- a CREZ default project) #10TPIT0102

- Jacksboro - Willow Creek rebuild as DCKT 345 (2/2010 -- a CREZ default project) #09TPIT0124

- Willow Creek - Parker rebuild as DCKT 345 (12/2010 -- a CREZ default project) #10TPIT0101

- Loop Graham - Benbrook 345 into Parker (2/2010) #10TPIT0105

- Parker - Everman 345 (2/2010) also #10TPIT0105

- 138kV phase shifting transformer at Santa Anna (3/2010) #08-TPIT-0146

- San Miguel - Lobo 345kV line (4/2010) #09-TPIT-0003

- 138kV phase shifting transformer at Yellow Jacket (12/2009) #08-TPIT-0135

- 138kV phase shifting transformer at Big Lake (12/2009) #10-TPIT-0052

Generation projects scheduled to go in-service:

2010

| Unit Name | Expected in-service | In case? |
| --- | --- | --- |
| Oak Grove SES 2 | May-10 | yes |
| JK Spruce 2 | June-10 | yes |
| Formosa 11 | December-10 | no |
| Formosa 12 | December-10 | no |
| TECO Central Plant | February-10 | yes |
| Sandhill Peaking | July-10 | yes |

2009

| Unit Name | Expected in-service | In case? |
| --- | --- | --- |
| Sandow 5 | March-09 | yes |
| Oak Grove SES 1 | November-09 | yes |
| Lufkin | September-09 | yes |
| Mont Belvieu (Warvue_GT1) | April-09 | yes |
| PEARSALL | August-09 | yes |
| Bosque 5 | March-09 | yes |
| Cedar Bayor 4 | June-09 | yes |
| Nueces Bay Repowering | April-10 | yes |
| B M Davis Repowering | November-09 | yes |
| Dansby 3 | August-09 | no |
| Braunig Peaking | October-09 | yes |
| Winchester Peaking | June-09 | yes |

The generation reconnects of Horse Hollow and Callahan Divide from the West Zone to South Zone is included in the wind generation capacity provided below.

Wind generation capacity:

| Zone | 2009 | 2010 |
| --- | --- | --- |
| West | 8339.2 | 8339.2 – 959 = 7380 |
| North | 693.5 | 693.5 |
| South | 773 | 871 + 959 = 1830 |

Generation being suspended after September 2009:

| Name | MW | Bus |
| --- | --- | --- |
| Tradinghouse Unit 1 | 563 | 3403 |
| Morgan Creek Unit 5 | 137 | 1037 |
| Sweetwater Cogen Unit 1 | 30 | 1416 |
| Sweetwater CT1 | 72 | 1417 |
| Sweetwater CT2 | 68 | 1418 |
| Sweetwater CT3 | 61 | 1419 |
| North Lake 1 | 156 | 2381 |
| North Lake 2 | 181 | 2382 |
| North Lake 3 | 329 | 2383 |
| Decordova SES Unit 1 | 779 | 1889 |
| Lake Creek SES Unit 1 | 75 | 3416 |
| Lake Creek SES Unit 2 | 222 | 3417 |

# Transfer Study

The Steady State Working Group (SSWG) Data Set A 2010 summer peak base case was used for the transfer analysis.  A congestion management (CM) zone to CM zone transfer analysis was performed by mapping all generators to their respective 2009 CM zones.  New generation units were mapped to their assumed CM zone.

Transfer analysis was performed for the following zone to zone generation transfers:

- West to North

- South to North

- North to South

- North to Houston

- North to West

- West to South

The results of the transfer studies are provided as a separate attachment.

# Evaluation of Current Congestion Events

The tables (Table 1a-e) below contain estimated of scheduled net costs for inter-zonal congestion assigned to contingency and overloaded elements based on those identified when determining CSC limits during real-time operations for the period January through June, 2009.  “True” costs were calculated for each CSC as the product of 15-minute average flows, Shadow Price, and 0.25.

North to South (Table 1a)

| Contingency | Overloaded Element | Net Costs | “true” costs |
| --- | --- | --- | --- |
| Temple Pecan Creek - Trading house SES & Temple Switch – Lake Creek SES 345 kV | Waco Atco-Waco Woodway | $53,046,567 | $61,778,133 |
| Temple Pecan Creek - Trading house SES & Temple Switch – Lake Creek SES 345 kV | Goldwaithe - Evant | $ 2,808,480 | $ 3,863,234 |
| Temple Pecan Creek - Trading house SES & Temple Switch – Lake Creek SES 345 kV | Waco Atco-Cotton Belt | $ 173,144 | $ 183,152 |
| Lake Creek SES-Temple Switch 345kV | Temple Pecan Crk-Tradinghouse 345kV | $ 120,326 | $ 124,024 |
| Temple Pecan Creek - Trading house SES & Temple Switch – Lake Creek SES 345 kV | Temple-Temple Pecan Crk | $ 16,590 | $ 16,940 |

South to North (Table 1b)

| Contingency | Overloaded Element | Net Cost | “true” costs |
| --- | --- | --- | --- |
| Austrop – Sandow 345 kV & Sandow Auto #2 | Austrop – Sandow SW 345kV | ($7,675,044) | $2,488,928 |

West to North (Table 1c)

| Contingency | Overloaded Element | Net Cost | “true” costs |
| --- | --- | --- | --- |
| Stability Limit |  | $2,227,059 | $22,035,422 |
| Graham-Long Creek | Murray - Paint Creek 138kV | $ 957,333 | $ 6,059,873 |

Note: Out of 2,403 binding intervals for the West to North CSC 2,032 have been due to the Stability Limit.

North to West (Table 1d)

| Contingency | Overloaded Element | Net Cost | “true” costs |
| --- | --- | --- | --- |
| DCKT Long Creek – Sweetwater Cogen & Abilene Mulberry Creek 345 kV | Murray – Paint Creek 138kV | $ 986,176 | $2,610,732 |

North to Houston (Table 1e)

| Contingency | Overloaded Element | Net Cost | “true” costs |
| --- | --- | --- | --- |
| Roans Prairie-King & Singleton-Tomball345kV | Singleton-TH Wharton345kV | $1,376,793 | $5,664,149 |
| TH Wharton-Jewett & Obrien - Gibbons Creek 345kV | Voltage (VSAT) | $1,104,756 | $2,407,736 |
| DCKT Gibbons Creek – O’Brien & Singleton – TH Wharton 345kV | Peters – Flewellen 138kV | $ 793,935 | $1,591,909 |
| TH Wharton-Singleton & Jewett-Singleton 345kV | Peters – Flewellen 138kV | $ 456,052 | $1,236,495 |
| Singleton – O'brien 345kV | Voltage (VSAT) | $ 239,267 | $ 499,587 |
| O’Brien – Singleton 345kV | Jewett-Singleton 345kV | $ 49,113 | $ 166,408 |
| O’Brien-THWharton345kV | Singleton-TH Wharton345kV | $ 19,693 | $ 45,586 |
| Gibbons Creek – Singleton 345kV | Jewett-Singleton 345kV | $ 2,935 | $ 13,889 |

Recurring Congestion - days

Table 2 shows recurring congestion in days for the January through June, 2009 timeframe these are the top congested contingency and overloaded element pairs observed during real-time:

| Contingency | Overloaded Element | Total |
| --- | --- | --- |
| Aspermont - Spur 138KV | Jayton - Spur 69 kV | 61 |
| San Miguel - Dilley Switch 138KV | Derby – Pearsall 69KV | 50 |
| Abilene South - Eskota 138KV | Trent - Merkel 69KV | 43 |
| Comanche Peak SES - Decordova SES & Wolf Hollow - Rocky Creek 345KV | Concord 345/138KV autotransformer | 39 |
| Santa Anna - Ballinger 138KV | Ballinger - Humble 69KV | 34 |
| Oasis - PH Robinson 345KV | Garrott - Midtown 138KV | 26 |
| Basecase | Menard – San Angelo Power Station 138 kV | 25 |
| Dilley Switch - North Laredo 138KV | North Laredo - Asherton 138KV | 25 |
| Aspermont - Spur 138KV | Spur 138/69KV autotransformer | 21 |
| Menard - Gillespie 138KV | Menard 138/69KV autotransformer | 19 |
| Aspermont - Spur 138KV | Matador – Paducah 69KV | 18 |
| Abilene South - Eskota Switch 138KV | Eskota Switch 138/69KV autotransformer | 17 |

Table 2: Counts provided are for the number of days these pairs appeared as congested.

For local congestion incurred during the period February through June, 2009, these are the top congested contingency and overload element pairs thus far:

| Contingency | Overloaded Element | Cost |
| --- | --- | --- |
| Base-case; Graham SES-Long Creek 345kV Sandow Switch-Austrop 345kV | SAPS - Menard 138kV | $ 12,006,612 |
| Ballinger - Santa Anna 138kV | Ballinger - Humble 69kV | $ 8,513,994 |
| Valley Import |  | $ 5,101,300 |
|  | Capacity Shortage | $ 4,158,447 |
| Comanche Peak SES - DeCordova SES & Wolf Hollow - Rocky Creek 345kV | Concord 345/138kV Autotransformer | $ 3,968,846 |
| Menard - Gillespie 138kV | Menard Auto | $ 3,620,392 |
| Watermill - DeSoto Switch - Cedar Hill Switch 345kV | Watermill - DeSoto | $ 3,549,488 |
| Comanche Peak SES - DeCordova SES & Wolf Hollow - Rocky Creek 345kV | Venus Switch - Comanche Peak 345kV | $ 3,515,768 |
| Skyline to Marion & Elm Creek 345 | Marion - Hill Country 345kV | $ 3,159,056 |
| Ballinger - San Angelo Red Creek 138kV | Miles - Rowena 69kV | $ 3,074,447 |
| Temple Pecan Creek - Tradinghouse & Temple Switch - Long Creek SES | San Angelo Power Station -Shrew Tap | $ 2,923,976 |
| Watermill - West Levee SW & Sargent Road | Watermill - DeSoto | $ 1,832,359 |
| Area Security - Valley |  | $ 1,718,466 |
| Comanche Peak SES-DeCordova SES & Wolf Hollow-Rocky Creek 345kV | Comanche Peak SES - Parker Switch 345KV | $ 1,652,826 |
| Comanche Peak SES-DeCordova SES-Wolf Hollow 345kV | Parker Switch - Benbrook Switch 345KV | $ 1,160,067 |
| Lon Hill - Coleto Creek 345kV | Warburton - Victoria 138kV | $ 1,098,875 |
| Lytton S/HC Tap | Austrop outage | $ 948,231 |
| Watermill Swithch - DeSoto Switch-Cedar Hill Switch | West Levee Auto #5 | $ 914,588 |
| Austrop - Lost Pines 345kV | Winchester - Fayetteville 138kV | $ 895,574 |
| Oklaunion - Fisher Road - Bowman 345kV | Vernon - Grayback 69kV | $ 891,532 |
| Roanoke Switch - West Denton & Lewisville Switch 345kV | West Denton - Airport 138kV | $ 872,109 |
| Austrop 345/138kV Autotransformer T1/T2 | Austrop 345/138kV Autotransformer T2/T1 | $ 861,714 |
| Tradinghouse - Venus Switch 345kV | Rogers Hill - Elm Mott 138kV | $ 839,174 |

Table 3: Dollars shown are estimates and not Settlement quality.  Local congestion costs have totaled an estimated $100 million for January through June; the element pairs shown above represent 67% of the total estimated costs.

# Projection of Future Congestion

The projected 2010 congestion study provided as a separate attachment uses the same case developed for the CSC analysis which is the 2010 Data Set A Summer peak case and updates made to include inadvertent deletions.  The updates made include: the Long Creek bus tie, Lake Creek to Rattlesnake line, Willow Creek to Parker line, and use of the Permian Basin Units 5 and 6, which typically run during the summer.  The elements in this report are sorted based on congestion cost.

# Cluster Analysis

All clustering analyses were performed using the 2010 Data Set A Summer peak case.  A summary of the scenarios follows.  In most scenarios Horse Hollow and Callahan Divide clustered in the South zone; exceptions occurred when a central zone was created.  All of the scenarios provided in this version of the analysis have been updated to incorporate corrections made to the 2010 Data Set A Summer peak case.  The updates include: adding the Long Creek bus tie, Lake Creek to Rattlesnake line, and Willow Creek to Parker line.  The case has been posted on the Planning and Operations Information site:  http://planning.ercot.com/planning/tcrsc/csccmzd/

In reviewing the remaining scenarios, ERCOT was asked to look at the impact of the Salado to Hutto 345kV line; our study indicated that the loss of this line would not cause additional overloads using the 2010 DSA summer peak case.

| Scenario | W_N & N_W | N_S & S_N | N_H | Zones | Notes |
| --- | --- | --- | --- | --- | --- |
| 1 | Sweetwater-Long Creek/ Abilene Mulberry Creek-Long Creek 345-kV dckt | Lake Creek-Temple/ Tradinghouse-Temple Pecan Creek 345-kV dckt | Singleton-Obrien/ Singleton-TH Wharton 345-kV dckt | 4 | Pre-contingency |
| 1a | same as 1 | same as 1 | same as 1 | 4 | Post-contingency |
| WN1-4Z | Graham-Long Creek/ Graham-Cook Field Road 345-kV double circuit | same as 1 | same as 1 | 4 |  |
| WN1-5Z | Graham-Long Creek/ Graham-Cook Field Road 345-kV double circuit | same as 1 | same as 1 | 5 | Eliminated on 8/10/2009 by CMWG. |
| WN1-6Z | Graham-Long Creek/ Graham-Cook Field Road 345-kV double circuit | same as 1 | same as 1 | 6 | Eliminated on 8/04/2009 by CMWG. Refer to version 0.7 for diagram. |
| WN2-4Z | W-N & N-W: stability limit interface | same as 1 | same as 1 | 4 |  |
| WN2-5Z | W-N & N-W: stability limit interface | same as 1 | same as 1 | 5 | Eliminated on 8/10/2009 by CMWG. |
| WN2-6Z | W-N & N-W: stability limit interface | same as 1 | same as 1 | 6 | Eliminated on 8/04/2009 by CMWG. Refer to version 0.7 for diagram. |
| WN3-4Z | Graham-Parker 345-kV double circuit | same as 1 | same as 1 | 4 | Eliminated on 8/10/2009 by CMWG. |
| WN3-5Z | Graham-Parker 1 & 2 345-kV double circuit | same as 1 | same as 1 | 5 | Eliminated on 8/10/2009 by CMWG. |
| WN3-6Z | Graham-Parker 345-kV double circuit | same as 1 | same as 1 | 6 | Eliminated on 8/04/2009 by CMWG. Refer to version 0.7 for diagram. |
| NH4L-4Z | same as 1 | same as 1 | Singleton-Obrien Singleton-TH Wharton Singleton-Tombal Roans-Kuykendahl | 4 | Eliminated on 8/04/2009 by CMWG. |
| SN1-4Z | same as 1 | N_S: no change S_N: Sandow-Temple Switch DCKT | same as 1 | 4 | Eliminated on 8/04/2009 by CMWG. Refer to version 0.7 for diagram. |
| SN1-5Z | same as 1 | N_S: no change S_N: Sandow-Temple Switch DCKT | same as 1 | 5 | Eliminated on 8/04/2009 by CMWG. Refer to version 0.7 for diagram. |
| FW1-5Z | same as 1 | same as 1 | same as 1 | 5 | W-FW: China-Radium & Bitter Creek-Mulberry Creek Withdrawn by Direct Energy. |
| FW2-5Z | same as 1 | same as 1 | same as 1 | 5 | W-FW: China-Radium & McElmur -Potter Eliminated on 8/04/2009 by CMWG. Refer to version 0.7 for diagram. |
| FW1_WN1-5Z | Graham-Long Creek/ Graham-Cook Field Road 345-kV double circuit | same as 1 | same as 1 | 5 | W-FW: China-Radium & Bitter Creek-Mulberry Creek Withdrawn by Direct Energy. |
| FW2_WN1-5Z | Graham-Long Creek/ Graham-Cook Field Road 345-kV double circuit | same as 1 | same as 1 | 4 | W-FW: China-Radium & McElmur -Potter Eliminated on 8/04/2009 by CMWG. Refer to version 0.7 for diagram. |
| WN2_SN1_NH4L | N_W & W_N: Stability limit interface | N_S: no change S_N: Sandow-Temple Switch DCKT | Singleton-Obrien Singleton-TH Wharton Singleton-Tombal Roans-Kuykendahl | 4 | Eliminated on 8/04/2009 by CMWG. Refer to version 0.7 for diagram. |
| WN2_SN2-5Z | W_N & N_W: Stability Interface | S_N: Sandow – Austrop N_S: same as 1 | same as 1 | 5 | Eliminated on 8/10/2009 by CMWG. |
| WN2_SN2-6Z | W_N & N_W: Stability Interface | S_N: Sandow – Austrop N_S: same as 1 | same as 1 | 6 | Eliminated on 8/10/09 by CMWG. |
| FW1_WN2-5Z | W_N & N_W: Stability Interface | same as 1 | same as 1 | 5 | W-FW: China-Radium & Bitter Creek-Mulberry Creek Withdrawn by Direct Energy. |
| WN3_SN0-4Z | Graham-Parker 1 & 2 345Kv dckt | N_S: same S_N: remove | same | 4 | ERCOT recommendation |
| WN4_SN0-4Z | W_N & N_W: Graham-Long Creek/ Graham-Cook Field Road 345-kV double circuit; Bowman-Jacksboro | N_S: same S_N: remove | same | 4 | Eliminated on 8/10/09 by CMWG. |
| WN2_SN0-4Z | W-N & N_W: Graham-Long Creek/ Graham-Cook Field Road 345-kV double circuit; Jacksboro-Bowman; Graham-Tonkawa; Bowman-Graham; Comanche Switch-Red Creek | N_S: same S_N: remove | same as 1 | 4 |  |
| FW1_WN4_SN0-5Z | W_N & N_W: Graham-Long Creek/ Graham-Cook Field Road 345-kV double circuit; Bowman-Jacksboro | N_S: same S_N: remove | same | 5 | W-FW: China-Radium & Bitter Creek-Mulberry Creek Withdrawn by Direct Energy. |

## Scenario 1

Scenario 1 was clustered using the pre-contingency 2010 DSA SUM1 base case.  The 2009 CSCs were used and the model was clustered into four zones.

## Scenario 1a – Current 2009 CSCs

Scenario 1a was clustered using the post-contingency with the Fisher to Bowman 345kV line 2010 DSA SUM1 base case.  The 2009 CSCs were used and the model was clustered into four zones.

## Scenario WN1-4Z

Scenario WN1-4Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 4 zone scenario with the 2009 CSCs for N_S, S_N, and N_H; the N_W and the W_N CSCs were modeled as the Long Creek to Graham and Cook Field to Graham 345kV lines.

## Scenario WN1-5Z – eliminated 8/10/2009

Scenario WN1-5Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 5 zone scenario with the 2009 CSCs for N_S, S_N, and N_H; the N_W and the W_N CSCs were modeled as the Long Creek to Graham and Cook Field to Graham 345kV lines.

## Scenario WN1-6Z – eliminated 8/02/2009

Scenario WN1-6Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 6 zone scenario with the 2009 CSCs for N_S, S_N, and N_H; the N_W and the W_N CSCs were modeled as the Long Creek to Graham and Cook Field to Graham 345kV lines.

## Scenario WN2-4Z

Scenario WN2-4Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 4 zone scenario with the 2009 CSCs for N_S, S_N, and N_H; the N_W CSC is excluded and the W_N CSC was modeled as the Stability interface.  The Stability Limit monitored lines are:

- Graham – Cook Field

- Jacksboro – Bowman

- Graham – Tonkawa

- Bowman – Graham

- Comanche Switch – Red Creek

- Graham – Long Creek

## Scenario WN2-5Z – eliminated 8/10/2009

Scenario WN2-5Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 5 zone scenario with the 2009 CSCs for N_S, S_N, and N_H; the N_W CSC is excluded and the W_N CSC was modeled as the Stability interface.

## Scenario WN2-6Z – eliminated 8/04/2009

Scenario WN2-6Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 6 zone scenario with the 2009 CSCs for N_S, S_N, and N_H; the N_W CSC is excluded and the W_N CSC was modeled as the Stability interface.

## Scenario WN3-4Z – eliminated 8/10/2009

Scenario WN3-4Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 4 zone scenario with the 2009 CSCs for N_S, S_N, and N_H; the N_W and the W_N CSCs were modeled as the Graham to Parker double circuit

## Scenario WN3-5Z – eliminated 8/10/2009

Scenario WN3-5Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 5 zone scenario with the 2009 CSCs for N_S, S_N, and N_H; the N_W and the W_N CSCs were modeled as the Graham to Parker double circuit

## Scenario WN3-6Z – eliminated 8/04/2009

Scenario WN3-6Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 6 zone scenario with the 2009 CSCs for N_S, S_N, and N_H; the N_W and the W_N CSCs were modeled as the Graham to Parker double circuit

## Scenario NH4L-4Z - eliminated 8/04/2009

Scenario NH4L-4Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 4 zone scenario with the 2009 CSCs for N_S, S_N, N_W, W_N, and with N_H clustered using the four lines that go into Houston.

## Scenario SN1-4Z - eliminated 8/04/2009

Scenario SN1-4Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 4 zone scenario with the 2009 CSCs for N_S, N_W, W_N, and N_H; the S_N CSC was defined as the Sandow-Temple Switch 345kV double circuit.

## Scenario SN1-5Z - eliminated 8/04/2009

Scenario SN1-5Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 5 zone scenario with the 2009 CSCs for N_S, N_W, W_N, and N_H; the S_N CSC was defined as the Sandow-Temple Switch 345kV double circuit.

## Scenario FW1-5Z - withdrawn

Scenario FW1-5Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 5 zone scenario with the 2009 CSCs for N_S, S_N, W_N, N_W, and N_H; the F_W CSC was defined as China Radium and Bitter Creek-Mulberry Creek.

## Scenario FW2-5Z - eliminated

Scenario FW2-5Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 5 zone scenario with the 2009 CSCs for N_S, S_N, N_W, W_N, and N_H; the F_W CSC was defined as China Radium and McElmur-Potter.

## Scenario FW1_WN1-5Z - withdrawn

Scenario FW1_WN1-5Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 5 zone scenario with the 2009 CSCs for N_S, S_N and N_H; the W_N CSC is Long Creek to Graham and Cook Field to Graham 345kV lines and the F_W CSC was defined as China Radium and Bitter Creek-Mulberry Creek.

## Scenario FW2_WN1-5Z - eliminated

Scenario FW2_WN1-5Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 5 zone scenario with the 2009 CSCs for N_S, S_N and N_H; the W_N CSC is Long Creek to Graham and Cook Field to Graham 345kV lines and the F_W CSC was defined as China Radium and McElmur-Potter.

## Scenario WN2_SN1_NH4L - eliminated

Scenario WN2_SN1_NH4L was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 4 zone scenario with the 2009 CSC for N_S only; N_W and W_N were defined as the stability limit interface; N_H was defined with the 4 lines that import into Houston; the S_N CSC was defined as the Sandow-Temple Switch 345kV double circuit.

## Scenario WN2_SN2-5Z – eliminated 8/10/2009

Scenario WN2_SN2-5Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 5 zone scenario with the 2009 CSC for N_S and N_H; N_W and W_N were defined as the stability limit interface; the S_N CSC was defined as the Sandow-Austrop 345kV double circuit.

## Scenario WN2_SN2-6Z – eliminated 8/10/2009

Scenario WN2_SN2-6Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 6 zone scenario with the 2009 CSC for N_S and N_H; N_W and W_N were defined as the stability limit interface; the S_N CSC was defined as the Sandow-Austrop 345kV double circuit.

## Scenario FW1_WN2-5Z - withdrawn

Scenario FW1_WN1-5Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 5 zone scenario with the 2009 CSCs for N_S, S_N and N_H; the W_N CSC is Stability interface lines and the F_W CSC was defined as China Radium and Bitter Creek-Mulberry Creek.

## Scenario WN3_SN0-4Z

Scenario WN3_SN0-4Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 4 zone scenario with the 2009 CSCs for N_S, and N_H; the W_N and N_W CSCs are Graham to Parker 345kV double circuit; the S_N CSC was removed.

## Scenario WN4_SN0-4Z – eliminated 8/10/2009

Scenario WN4_SN0-4Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 4 zone scenario with the 2009 CSCs for N_S and N_H; the W_N and N_W CSCs are Graham-Long Creek, Graham-Cook Field Road 345-kV double circuit and Bowman-Jacksboro 345kV; the S_N CSC was removed.

## Scenario FW1_WN4_SN0-4Z - withdrawn

Scenario WN4_SN0-4Z was clustered using the pre-contingency 2010 DSA SUM1 base case.  This is a 4 zone scenario with the 2009 CSCs for N_S and N_H; the W_N and N_W CSCs are Graham-Long Creek, Graham-Cook Field Road 345-kV double circuit and Bowman-Jacksboro 345kV; the S_N CSC was removed; F_W CSC is China-Radium & Bitter Creek-Mulberry Creek.

# ERCOT Recommendation

To see if there were any significant differences between the proposed CSCs, ERCOT performed an additional shift-factor analysis using an EMS snapshot of a real-time peak case taken on July 13, 2009 with a load of 63,300MWs.  This snapshot was chosen because it had the most equipment and generation in-service.  Two calculations were done using Power World.  In the first table, average generation shift-factors were calculated with the weighting based on the difference between the high sustainable limit (HSL) and the low sustainable limits (LSL).  The second table has average generation shift-factors with the weighting based on the difference between current operating points and the LSLs.

| Weighted based on the difference between Generator's Maximum output and Minimum output: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Scenario | W_N | N_W | N_S | S_N | N_H | W_N Stability | N_W Stability | F_W |
| 1 | 0.3104 | 0.32109 | 0.34255 | 0.33632 | 0.3046 |  |  |  |
| 1a | 0.335007 | 0.3485 | 0.346 | 0.3395 | 0.304627 |  |  |  |
| WN1-4Z | 0.2968 | 0.30416 | 0.34255 | 0.33632 | 0.3046 |  |  |  |
| WN1-5Z | 0.28997 | 0.3103 | 0.321405 | 0.28007 | 0.307238 |  |  |  |
| WN1-6Z | 0.29416 | 0.30497 | 0.317824 | 0.02799 | 0.302753 |  |  |  |
| WN2-4Z |  |  | 0.34255 | 0.33632 | 0.3046 | 0.65417 | 0.6767 |  |
| WN2-5Z |  |  | 0.321405 | 0.28007 | 0.307238 | 0.65117 | 0.697382 |  |
| WN2-6Z |  |  | 0.317824 | 0.27985 | 0.302753 | 0.65122 | 0.679584 |  |
| WN3-4Z | 0.28504 | 0.29527 | 0.34255 | 0.33632 | 0.3046 |  |  |  |
| WN3-5Z | 0.271805 | 0.29055 | 0.321405 | 0.28007 | 0.307238 |  |  |  |
| WN3-6Z | 0.285119 | 0.298 | 0.317824 | 0.27985 | 0.302753 |  |  |  |
| NH4L-4Z | 0.3104 | 0.32109 | 0.34255 | 0.33632 | 0.61107 |  |  |  |
| SN1-4Z | 0.3104 | 0.32109 | 0.34255 | 0.31625 | 0.3046 |  |  |  |
| SN1-5Z | 0.30286 | 0.32732 | 0.32141 | 0.26492 | 0.35792 |  |  |  |
| FW1_5Z | 0.3337 | 0.29674 | 0.34255 | 0.33632 | 0.3046 |  |  | 0.2486 |
| FW2_5Z | 0.3337 | 0.29674 | 0.34255 | 0.33632 | 0.3046 |  |  | 0.00972 |
| FW1_WN1_5Z | 0.2901 |  | 0.34255 | 0.33632 | 0.3046 |  |  | 0.2486 |
| FW2_WN1_5Z | 0.2901 |  | 0.34255 | 0.33632 | 0.3046 |  |  | 0.00972 |
| WN2_SN1_NH4L |  |  | 0.34255 | 0.31625 | 0.61107 | 0.65417 | 0.6767 |  |

Weighted based on the difference between Generator's Real-Time Operating Point and Minimum output:

| Scenario | W_N | N_W | N_S | S_N | N_H | W_N Stability | N_W Stability | F_W |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 0.3699 | 0.3711 | 0.416244 | 0.4255 | 0.3585 |  |  |  |
| 1a | 0.4115 | 0.4035 | 0.42034 | 0.427 | 0.352538 |  |  |  |
| WN1-4Z | 0.3529 | 0.36772 | 0.416244 | 0.4255 | 0.3585 |  |  |  |
| WN1-5Z | 0.3739 | 0.37354 | 0.379015 | 0.40269 | 0.357953 |  |  |  |
| WN1-6Z | 0.35067 | 0.36605 | 0.372729 | 0.40474 | 0.356558 |  |  |  |
| WN2-4Z |  |  | 0.416244 | 0.4255 | 0.3585 | 0.80327 | 0.81059 |  |
| WN2-5Z |  |  | 0.379015 | 0.40269 | 0.357953 | 0.83812 | 0.833009 |  |
| WN2-6Z |  |  | 0.372729 | 0.40474 | 0.356558 | 0.80153 | 0.81097 |  |
| WN3-4Z | 0.36159 | 0.35479 | 0.416244 | 0.4255 | 0.3585 |  |  |  |
| WN3-5Z | 0.357196 | 0.34772 | 0.379015 | 0.40269 | 0.357953 |  |  |  |
| WN3-6Z | 0.364874 | 0.35841 | 0.372729 | 0.40474 | 0.356558 |  |  |  |
| NH4L-4Z | 0.3699 | 0.3711 | 0.416244 | 0.4255 | 0.719133 |  |  |  |
| SN1-4Z | 0.3699 | 0.3711 | 0.416244 | 0.40206 | 0.3585 |  |  |  |
| SN1-5Z | 0.39071 | 0.37685 | 0.37302 | 0.38103 | 0.35753 |  |  |  |
| FW1_5Z | 0.3425 | 0.3573 | 0.416244 | 0.4255 | 0.3585 |  |  | 0.3336 |
| FW2_5Z | 0.3425 | 0.3573 | 0.416244 | 0.4255 | 0.3585 |  |  | 0.00148 |
| FW1_WN1_5Z | 0.20747 |  | 0.416244 | 0.4255 | 0.3585 |  |  | 0.3336 |
| FW2_WN1_5Z | 0.20747 |  | 0.416244 | 0.4255 | 0.3585 |  |  | 0.0148 |
| WN2_SN1_NH4L |  |  | 0.416244 | 0.40206 | 0.719133 | 0.80327 | 0.81059 |  |

ERCOT recommends four zones and the following CSCs for 2010:

W_N:	Graham – Parker 345kV double circuit

N_W:	Graham – Parker 345kV double circuit

N_S:	Lake Creek-Temple/Tradinghouse-Temple Pecan Creek 345-kV double circuit S_N:	Remove

N_H:	Singleton-Obrien/ Singleton-TH Wharton 345-kV double circuit

This recommendation is the cluster shown in scenario WN3_SN0-4Z.

Planning studies indicate that the stability limit may continue to be of concern in 2010; therefore, ERCOT will also recommend that the stability limit interface be designated as a Closely Related Element (CRE).  ERCOT believes that it effectively managed the stability limit with the Graham-Parker 345kV double circuit (Graham-Parker-Benbrook 345kV) as the CSC in the past.

While the shift-factor analysis performed shows that the stability interface may be more effective than all other scenarios studied, operating experience demonstrates that the stability limit can be controlled effectively using zonal methods if it is a CRE.  If the stability limit interface were to be designated as the CSC then ERCOT would be posting the day-ahead thermal constraint as the limit instead of the stability limit.