| OGRR Number | 217 | OGRR Title | Relay Misoperation Report Format Change |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Action |  | Tabled |
| Date of Decision |  | May 20, 2009 |  |  |
| Guide Section Requiring Revision |  | 6.1.2, Relay Misoperation Report |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Revision Description |  | This Operating Guide Revision Request (OGRR) changes the format for reporting yearly relay misoperations from a report format to a data format. |  |  |
| Overall Market Benefit |  | The new report format will help to improve the reliability of transmission protection systems. |  |  |
| Overall Market Impact |  | None. |  |  |
| Consumer Impact |  | None. |  |  |
| Procedural History |  | - On 1/6/09, OGRR217 was posted. - On 2/9/09, the Operations Working Group (OWG) considered OGRR217. - On 3/26/09, the Operating Guide Revisions Task Force (OGRTF) comments were posted. - On 3/27/09, the OWG again considered OGRR217. - On 4/23/09, the OWG again considered OGRR217. - On 5/20/09, the OWG again considered OGRR217. |  |  |
| OWG Decision |  | On 2/9/09, the OWG was in consensus to table OGRR217. On 3/27/09, the OWG was in consensus to table OGRR217. On 4/23/09, the OWG was in consensus to table OGRR217 for one (1) month. On 5/20/09, the OWG was in consensus to table OGRR217. |  |  |
| Summary of OWG Discussion |  | On 2/9/09, there was discussion regarding the proposed changes to the report and the possibility that some necessary information would not be captured in the new report. Clarification from the sponsor of OGRR217 would need to be provided at the next OGRTF meeting. On 3/27/09, there was discussion regarding the need to expand the proposed narrative section of the report as it is currently limited to 250 characters. On 4/23/09, there was discussion regarding the need to expand the proposed narrative section to accommodate up to 1000 characters. OWG was in consensus to table OGRR217 until this issue can be addressed by the sponsor. On 5/20/09, it was noted that the sponsor of OGRR217 is currently performing testing on the changes requested by OWG. The sponsor will provide the results of the test to OWG when complete. |  |  |

Quantitative Impacts and Benefits

| Assumptions | 1 | The new format will help to improve the reliability of transmission protection systems. |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | The new report format will help to improve the reliability of transmission protection systems. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| OGRTF 032609 | Recommended approval of OGRR217 as submitted. |

| Original Sponsor |  |
| --- | --- |
| Name | Glenn Hargrave on behalf of the System Protection Working Group (SPWG) |
| Company | CPS Energy |
| Market Segment | Municipally Owned Utilities |

Proposed Guide Language Revision

### 6.1.2	Relay Misoperation Report

Relay misoperations shall be reported in a data format of either Microsoft Excel© or a comma delimited text for import into a Microsoft© database for compilation.  The submitted file shall include headers for each field.  The field headers and data format shall match that described in the table below.

| Field Name | Type | Size or Format | Description |
| --- | --- | --- | --- |
| Misop_Date | Date | mm/dd/yyyy | The date that misoperation occurred |
| Misop_Time | Time | hh:nn:ss | The time at which misoperation occurred in 24-hour format – this could be time marked by the relay if it is synchronized with GPS clock, time noted by each facility owner’s or operator’s operations control center. |
| Time_Zone | Text | 50 | Define the standard time of the misoperation time noted (i.e. GMT, CT, EST, etc.) |
| Utility | Text | 25 | Name of the facility owner |
| Voltage | Text | 10 | Transmission voltage (345 kV, 138 kV, 69 kV, etc.) |
| Protected_Equipment | Text | 25 | The transmission element (line, autotransformer, bus, etc.) protected by the protection scheme |
| Substation | Text | 50 | Name of the substation where the misoperated element or equipment located |
| Protection_Scheme | Text | 25 | Type of protection scheme applied (i.e. Differential, DCB, SPS, Step distance, etc.) |
| Equipment_Name | Text | 50 | Specific description of the protected transmission |
| CB_Number | Text | 50 | equipment Unique circuit breaker number assigned or used by the facility owner that effected the actual isolation. |
| Fault_Type | Text | 50 | Type of fault occurred (L-L, L-G, L-L-G, 3L-G, etc. If the misoperation occurred for a non-fault condition, note this field with ‘N/A’) |
| Communication_Method | Text | 50 | Type of communication method used for the protection scheme (i.e. Pilot wire, fiber, power-line carrier, etc.) |
| Manufacturer | Text | 50 | Relay Manufacturer’s name |
| Relay_Type | Text | 50 | Relay Type or style name (i.e. SEL-321, REL-512, CO-9, etc.) |
| Relay_Style | Text | 50 | Relay model number |
| Misop_Category | Text | 50 | Relay events constitute as reportable protective relay system misoperation as detailed in ERCOT Operating Guide 7, Section 7.2.3 |
| Misop_Description | Text | 255 | Description of the protective element/scheme failure that caused the misoperation. |
| Investigation_Results | Text | 255 | Description of the analysis results from the misoperation review and any deficiencies identified |
| Corrective_Action | Text | 255 | An action plan to correct any deficiencies identified in the investigation results or any additional action plan to avoid similar operations in the future. |
| Target_Date | Date | mm/dd/yyyy | Target date to implement the corrective action plan at the terminal(s) where the misoperation(s) occurred. This could also be the date that the corrective action plan was implemented. |
| Recommendation | Text | 255 | System wide corrective action plan or long term solution to avoid similar misoperations (i.e. design changes, equipment replacements, etc.) |
| Report_By | Text | 25 | Individual who completed the report |
| Phone | Text | 50 | Business phone number of the individual who completed the report |
| Report_Date | Date | mm/dd/yyyy | The date at which the report was completed (i.e. when corrective action was implemented) |