## Slide 1: 2010 CSC & Zone Selection: WN2-4Z
WMS Meeting
August 19, 2009

## Slide 2: Recommendation of WN2-4Z
WN2-4Z has the following CSCs & 4 Congestion Zones:
  N-S and S-N: Lake Creek-Temple/Tradinghouse-Temple Pecan Creek 345-kV (same as 2009)
  N-H: Singleton-Obrien/Singleton-TH Wharton 345-kV (same as 2009)
  W-N and N-W: Graham–Cook Field, Jacksboro–Bowman, Graham–Tonkawa, Bowman–Graham, Comanche Switch–Red Creek, Graham–Long Creek (6 lines used to monitor W-N Stability Limit)
The CSCs for N to S, S to N, and N to H are all the same as in 2009.
This recommendation differs from WN2_S0-4Z in that it retains a S to N CSC. WN2_S0-4Z proposes to eliminate the S to N CSC.
Without designating a 2010 S-N CSC, Luminant is concerned that there may be a material amount of unintended uplift of Local Congestion to resolve Sandow – Temple area constraints that could be competitively resolved with Zonal Balancing.
Utilizing a S-N CSC made up of the same lines as the N-S CSC will allow a set of relevant S-N CREs for 2010.

## Slide 3: Change in Most Prevalent CRE
In 2009 there were 15 S to N CREs and the prevalent constraint of those CREs was:
Contingency | Overloaded Element | “True” Cost
Austrop-Sandow Switch 345kV and Sandow Auto #2 | Austrop-Sandow Switch 345kV | $2,488,928
The next most prevalent constraint was a contingency on Sandow – Temple 345 kV overloading the second Sandow – Temple 345 kV circuit.
However, power flow studies reveal that the operation of the new Sandow 5 unit at Sandow plant will change this going forward and will likely make the Sandow-Temple 345 kV the most prevalent CRE.

## Slide 4: Sandow-Temple Becomes Most Binding in 2010
Luminant Energy performed PowerWorld S-N transfer studies to better understand the evolution of constraints from 2009 to 2010
During some cases when the S-N CSC bound during the past 12 months, Sandow 4 was on outage
  The studies above show that in this situation, the Austrop – Sandow constraint is more limiting, consistent with historically observed outcomes
For 2010, with one or both units at Sandow online:
  The Sandow – Temple constraint is the most binding as shown in the ERCOT studies on the prior page & and in Luminant’s studies below

## Slide 5
Note: The above table is a summary of ERCOT’s S-N transfer study results, that has been summarized to only show the constraints consisting of both the contingency & limiting element pair that are from the list of 11 S-N CREs from slide 4
  ERCOT’s Study Also Shows the Shift

## Slide 6: The Importance of a S to N CSC
A S to N CSC allows congestion to be effectively managed using zonal balancing techniques.
Applying the new CRE test, 13 of the CREs used in 2009 can be used again in 2010.
The Austrop – Sandow 345 kV lines would not qualify as CREs under the new test.
That only makes sense. Austrop-Sandow 345 kV lines should be managed using local congestion techniques since it is not a good CRE because of fails due to boundary generation limits.
But, the other CREs are all relevant and should be used for zonal congestion management.
In particular, the Sandow-Temple 345 kV lines will likely become more prevalent due to the addition of Sandow Unit 5 and should be managed using competitive rather than command and control techniques.

## Slide 7: Conclusion
Lack of a S to N CSC would prevent ERCOT from managing congestion on the Sandow-Temple 345 kV with zonal balancing techniques.
Power flow analysis reveals that Sandow-Temple 345 kV will become the more prevalent S to N constraint in 2010.

## Slide 8: Appendix: 2010 Relevant CREs
10 out of 11 of the active constraint pairs during the past 12 months will meet the new CRE requirements of PRR815.
13 out of the 15 2009 S-N CREs will still meet the PRR815 criteria
Red indicates 2009 S-N CREs not usable in 2010
  Adamsville – Evant 138 kV line
  Austrop – Sandow 345 kV line #1
  Austrop – Sandow 345 kV line #2
  Cottonwood – Waco Atco 138 kV line
  Evant – Goldthwaite 138 kV line
  Goldthwaite – Brownwood Sw. 138 kV line
  Lake Creek – Tradinghouse 345 kV line #1
  Lake Creek – Tradinghouse 345 kV line #2
  Rogers – Temple Sw. 138 kV line
  Sandow – Temple 345 kV line #1
  Sandow – Temple 345 kV line #2
  Temple Pecan Creek – Lake Creek 138 kV line
  Temple Sw. – Temple Pecan Creek 138 kV line
  Temple Sw. – Temple Pecan Creek 345 kV line
  Waco Atco – Waco Woodway

## Slide 9: Appendix: 2010 Relevant CREs