## Slide 1: 2010 CSC & Zone Selection: 6 Lines W-N & 4 Zones (WN2_SN0-4Z)
Shams Siddiqi, Ph.D.
Crescent Power, Inc.
(512) 263-0653
shams@crescentpower.net
August 19, 2009
Notes: <number>

## Slide 2: Recommendation: WN2_SN0-4Z
August 19, 2009
<number>
WN2_SN0-4Z has following CSCs & 4 Congestion Zones:
  N-S: Lake Creek-Temple/Tradinghouse-Temple Pecan Creek 345-kV (same as 2009)
  N-H: Singleton-Obrien/Singleton-TH Wharton 345-kV (same as 2009)
  W-N and N-W: Graham–Cook Field, Jacksboro–Bowman, Graham–Tonkawa, Bowman–Graham, Comanche Switch–Red Creek, Graham–Long Creek (6 lines used to monitor W-N Stability Limit)
Given all information currently available, these CSCs are the most efficient to manage known and expected commercially significant inter-zonal congestion in 2010
Any other choice of W-N CSC will introduce some amount of inefficiency whenever the Stability Limit is binding (which is the vast majority of the time) as well as send the wrong price signals to some Resources
The 4 Congestion Zones represent a continuity of the current zonal market with minimal load and resources switching zones

## Slide 3: Considerations for CSC Selection
August 19, 2009
<number>
Candidate CSCs are determined:
  using transfer analysis between Study Zones
  through an evaluation of the actual annual Congestion costs from the prior year
  based on ERCOT’s operational experience
CSCs should be selected such that:
  there is a sufficiently competitive market to resolve Congestion on the transmission path to be considered for CSC designation
  Candidate CSC is an adequate indicator to be used to operationally manage and measure inter-zonal transfers; and
  deployment of zonal balancing will be effective for managing the post-contingency flow on the limiting element

## Slide 4: Evaluation of Congestion Costs
August 19, 2009
<number>
Based on ERCOT evaluation: Current N-S & N-H CSCs are appropriate (so, no change proposed)
History of W-N congestion:
Note: Out of 2,403 binding intervals for the West to North CSC, 2,032 have been due to the Stability Limit.
History of S-N congestion:
Contingency | Overloaded Element | “True” Cost
Stability Limit |  | $22,035,422
Graham-Long Creek | Murray-Paint Creek 138kV | $6,059,873
Contingency | Overloaded Element | “True” Cost
Temple Switch-Sandow Switch 345kV | Austrop-Sandow Switch 345kV | $2,488,928

## Slide 5: Implications of W-N Congestion
August 19, 2009
<number>
The West to North Stability Limit is by far the most important and most often binding constraint
The following lines that ERCOT monitors for the Stability Limit are the obvious choice to define the W-N CSC: Graham–Cook Field, Jacksboro–Bowman, Graham–Tonkawa, Bowman–Graham, Comanche Switch–Red Creek, Graham–Long Creek
Selecting Graham-Parker or pre-contingency Sweetwater-Long Creek/Abilene Mulberry Creek-Long Creek as the W-N CSC would result in inefficiencies in managing the Stability Limit and send the wrong price signals to certain Resources
All other constraints in the West (apart from candidate CREs to this CSC) are scattered throughout the West and are on lower voltage lines
Thus, given the lack of significant congestion on any element further West in ERCOT’s evaluation results, there is no clear justification for another CSC further West of this W-N CSC

## Slide 6: Map of W-N Congestion
August 19, 2009
<number>
West – North Stability Interface
Bowman – Jacksboro
Bowman – Graham
Tonkawa – Graham
Long Creek – Graham
Cook Field – Graham
Red Creek - Comanche
2009 W-N CSC
800 MW Wind Capacity
608 MW @ Graham
Graham-Parker

## Slide 7: Concerns with 2009 W-N CSC
August 19, 2009
<number>
From the table below, Generation at Mesquite and Cook Field increase flows on the West–North Stability Interface (i.e. large positive Shift Factors relative to Norwood bus)
Under 2009 W-N CSC definition, these generators would get the wrong price signal and not be backed down whenever the Stability Limit is binding
Clearly indicates the need to change the current West – North CSC definition

## Slide 8: Implications of S-N Congestion
August 19, 2009
<number>
The only significant congestion South to North occurred as the contingency of the Sandow-Temple Switch 345kV overloading the Austrop-Sandow Switch 345kV
With S-N CSC defined as the N-S CSC in reverse and with both elements above as CREs, there was a lack of TCRs to hedge congestion risk S-N and there was significant boundary generation
CMWG also examined Austrop-Sandow as a CSC but rejected it due to insufficient competition when both N-S and Austrop-Sandow constraints bind
The congestion cost related to Austrop-Sandow was relatively small and there was no other significant congestion from South to North
As such, ERCOT recommended the elimination of the S-N CSC and we agree with that recommendation

## Slide 9: Proposed 6-line W-N CSC & 4 Zones
August 19, 2009
<number>
Under WN2_SN0-4Z, the CSCs are:
  N-S: Lake Creek-Temple/Tradinghouse-Temple Pecan Creek 345-kV (same as 2009)
  N-H: Singleton-Obrien/Singleton-TH Wharton 345-kV (same as 2009)
  W-N and N-W: Graham–Cook Field, Jacksboro–Bowman, Graham–Tonkawa, Bowman–Graham, Comanche Switch–Red Creek, Graham–Long Creek
There was also no compelling reason to increase the number of Congestion Zones from the current four – thus, consistent with ERCOT’s recommendation, the proposal is to have 4 Congestion Zones in 2010
Few Resources switch zones except some Resources currently in the North that appropriatelymove to the West

## Slide 10: 4 Zones under WN2_SN0-4Z
August 19, 2009
<number>

## Slide 11: Benefits of Proposed CSCs & Zones
August 19, 2009
<number>
Given all information currently available, the CSCs of WN2_SN0-4Z are the most efficient to manage known and expected commercially significant inter-zonal congestion in 2010
Any other choice of W-N CSC will introduce some amount of inefficiency whenever the Stability Limit is binding (which is the vast majority of the time) as well as send the wrong price signals to some Resources
The 4 Congestion Zones represent a continuity of the current zonal market in what is likely to be the final year of the zonal market with minimal load and resources switching zones