| CMGRR Number | 009 | CMGRR Title | Clarification of the Standards for Competitive Meters |
| --- | --- | --- | --- |
| Timeline | Normal | Action | Approved |
| Date of Decision | September 3, 2009 |
| Competitive Metering Guide (CMG) Sections Requiring Revision | 12.11, Diagnostic Checks 12.13, Event Logging 12.14, Error Reset 12.17, Interval Data Recorder (IDR) Functionality |
| Effective Date | October 1, 2009 |
| Priority and Rank Assigned | Not applicable. |
| Revision Description | This Competitive Metering Guide Revision Request (CMGRR) updates the CMG to provide clarification of the standards for competitive meters. |
| Overall Market Benefit | Increased clarity of the CMG. |
| Overall Market Impact | None. |
| Consumer Impact | None. |
| Procedural History | On 4/8/09, CMGRR009 was posted. On 6/3/09, Retail Metering Working Group (RMWG) considered CMGRR009. On 7/8/09, an Impact Analysis was posted. On 7/13/09, the CEO Revision Request Review was posted. On 7/29/09, RMWG considered the RMWG Recommendation Report and Impact Analysis for CMGRR009. On 8/12/09, RMS considered CMGRR009. On 9/3/09, TAC considered CMGRR009. |
| RMWG Recommendation | On 6/3/09, there was consensus at RMWG to recommend approval of CMGRR009 as submitted. 7/29/09, there was consensus at RMWG to endorse and forward the RMWG Recommendation Report and Impact Analysis for CMGRR009 to RMS. |
| Summary of RMWG Discussion | On 6/3/09, it was noted that no comments had been received for CMGRR009. On 7/29/09, there was no discussion. |
| RMS Recommendation | On 8/12/09, RMS unanimously voted to recommend approval of CMGRR009 as recommended by RMWG in the 7/29/09 RMWG Recommendation Report. All Market Segments were present for the vote. |
| Summary of RMS Discussion | On 8/12/09, there was no discussion. |
| TAC Decision | On 9/3/09, TAC unanimously voted to approve CMGRR009 as recommended by RMS in the 8/12/09 RMS Recommendation Report. All Market Segments were present for the vote. |
| Summary of TAC Discussion | On 9/3/09, there was no discussion. |

Quantitative Impacts and Benefits

| Assumptions | 1 | None. |
| --- | --- | --- |
|  | 2 |  |
|  | 3 |  |
|  | 4 |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Increased clarity of the CMG. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | None. |
|  | 2 |  |
|  | 3 |  |
|  | 4 |  |
| Other Comments | 1 | None. |
|  | 2 |  |
|  | 3 |  |
|  | 4 |  |

| Comments Received |
| --- |
| Comment Author | Comment Summary |
| None. |  |

| Original Sponsor |
| --- |
| Name | Terry Bates on behalf of RMWG |
| Company | Oncor |
| Market Segment | Investor Owned Utility (IOU) |

Proposed Guide Language Revision

## Diagnostic Checks

Upon failure of a diagnostic check, the meter shall store a status flag (indicator) that can be retrieved from the display or remotely, if applicable.  As a minimum, the following diagnostic checks shall be performed during a self-test:

(1)	Check the backup battery usage or voltage;

(2)	Verify the program integrity; and,

(3)	Verify the memory integrity.

## Event Logging

(1)	When interrogated, meters shall be capable of flagging and reporting the following events:

(a)	Hardware errors;

(b)	Firmware errors;

(c)	RAM and ROM errors;

(d)	Pulse Overflow errors;

(e)	Low battery condition;

(f)	AC power up;

(g)	AC power down;

(h)	Configuration changed;

(i)	Clock set/change;

(j)	Test mode activation; and,

(k)	Inactive potential.

(2)	Definitions:

(a)	Hardware Errors: Various hardware malfunctions (i.e. modem card/chip, measurement chip, CPU, etc.), whether fatal or not.

(b)	Firmware Errors: Firmware has a checksum error, watchdog time out error, or other problem with the firmware, whether fatal or not.

(c)	RAM and ROM Errors: Bad spots in memory identified via checksum or other means.

(d)	Pulse Overflow Errors: The maximum size value for the number of pulses per interval in load profile has been exceeded.  This does not apply to meters that store/report data in engineering units.

(e)	Low Battery Condition: Low battery has been sensed during initial power up, daily self checks, after power outages, or any other means to check for a low battery condition.

(f)	AC Power Up: When the meter electronics are powered up either via auxiliary power or connected to system power.

(g)	AC Power Down: When the meter electronics loses power either by auxiliary power or connected to system power.

(h)	Configuration Changed: Meter has been reprogrammed, or any meter programming where a settlement metering parameter is changed.

(i)	Clock Set/Change: The meter real time clock has been set/changed by external sources.

(j)	Test Mode Activation: Meter going into and out of “test mode.”

(k)	Inactive Potential: System phase voltage has been lost on any phase.

## Error Reset

Fatal error  or warning conditions shall only be reset upon an explicit command invoked via the meter programmer or upon some other explicit action.

## Interval Data Recorder (IDR) Functionality

Meters with an Interval Data Recorder (IDR) shall have the following interval data recording functions:

(1)	Recording of interval data for a minimum of two (2) channels;

(2)	Programmable intervals of five, fifteen, thirty, and sixty minutes;

(3)	Storage of interval data for a minimum of forty-five (45) days per channel, fifteen (15) minute interval data, in addition to allowances for event recording (power outages, resets, time sets, etc.);

(4)	Capacity to count and store at least 4,000 counts for the programmed interval for meters that store pulse data;

(5)	“Wraparound” memory that stores new interval data by writing over the oldest interval data; and,

(6)	Capability to continually record interval data while the meter is communicating via its communication ports.