## Sheet1
2010 CRE Test Results Summary
Threshold |  |  |  | PTDF>0.05 & PTDF:line rating > 0.0002 OR PTDF>0.2 | For Dec side: Gen wtd avg PTDF< 2* CRE PTDF | For Inc side: Gen wtd avg PTDF< 2* CRE PTDF | Impact errors of all Boundary Generation Resouces<=.3*line rating | Percentage error of deployment <50%
| Rating Type | Rating | Pass/Fail | PTDF (7.2.3.1.1) | Generation Concentration (7.2.3.1.2) | Generation Concentration (7.2.3.1.2) | Boundary Generation Resources (7.2.3.1.3) | CRE Correlation to CSC (7.2.3.1.4)
North to South
L: 3436 WACO_W1_ 3591 WACOWOOD C: 3405THOUSE-3412Temp_Pec C: 3409LAKE_CRK1-3414Temp_SS | min | 199 | PASS | 0.068181 | 1.2704 | 1.1742 | 0.29603 | 0.0098953
| avg | 247.95 | PASS | 0.068181 | 1.2704 | 1.1697 | 0.23759 | 0.0098953
| max | 268 | PASS | 0.068181 | 1.2704 | 1.1697 | 0.21981 | 0.0098953
L: 3650 ELGIN_SS 13430 SAND_TXU C: SANDOW__5-L_AUSTRO5_1Y C: L_AUSTRO5_1Y-SAND_TXU_59 | min | 199 | FAIL | -0.056842 | -1.5264 | -1.1917 | 0.47875 | 0.17397
| avg | 247.95 | FAIL | -0.056842 | -1.5264 | -1.1917 | 0.38423 | 0.17397
| max | 268 | FAIL | -0.056842 | -1.5264 | -1.1917 | 0.35549 | 0.17397
L: 3591 WACOWOOD 3592 WACOATCO C: 3405THOUSE-3412TEMP_PEC C: 3409LAKE_CRK1-3414TEMP_SS | min | 214 | PASS | 0.068181 | 1.2704 | 1.1742 | 0.27161 | 0.009897
| avg | 214 | PASS | 0.068181 | 1.2704 | 1.1742 | 0.27161 | 0.009897
| max | 214 | PASS | 0.068181 | 1.2704 | 1.1742 | 0.27161 | 0.009897
L: 3409 LAKE_CRK 3414 TEMP_SS_ C: 3405 THOUSE__3412 TEMP_PEC | min | 994 | PASS | 0.32983 | 1.2047 | 1.1536 | 0.27527 | 0.0064189
| avg | 1239.6 | PASS | 0.32983 | 1.1645 | 1.1497 | 0.22073 | 0.0064189
| max | 1340 | PASS | 0.32983 | 1.1558 | 1.1476 | 0.20419 | 0.0064189
L: 3402 LAKE_CRK 3405 THOUSE__ C: THOUSE__5-LAKE_CRK1_5 C: THOUSE__5-AEP_PEC__59 | min | 956 | FAIL | -0.2771 | -1.1554 | -1.8668 | 1.0889 | 0.33867
| avg | 1086.15 | FAIL | -0.2771 | -1.1401 | -1.7962 | 0.95841 | 0.33867
| max | 1195 | FAIL | -0.2771 | -1.1379 | -1.743 | 0.87111 | 0.33867
L: 3668 RNDROCK1 3670 RNDRCKNE C: SANDOW__5-L_AUSTRO5_1Y C: L_AUSTRO5_1Y-SAND_TXU_59 | min | 199 | FAIL | -0.10072 | -1.3939 | -1.2166 | 0.88553 | 0.1014
| avg | 247.95 | FAIL | -0.10072 | -1.3939 | -1.2166 | 0.71071 | 0.1014
| max | 268 | FAIL | -0.10072 | -1.3939 | -1.2166 | 0.65754 | 0.1014
L: 3409 LAKE_CRK 3414 TEMP_SS_ C: THOUSE__5-LAKE_CRK1_5 C: THOUSE__5-AEP_PEC__59 | min | 994 | PASS | 0.32523 | 1.1953 | 1.1545 | 0.27115 | 0.011308
| avg | 1239.6 | PASS | 0.32523 | 1.1569 | 1.1506 | 0.21743 | 0.011308
| max | 1340 | PASS | 0.32523 | 1.1487 | 1.1485 | 0.20114 | 0.011308
L: 3405 THOUSE__ TEMP_PEC C: 3409 LAKE_CRK 3414 TEMP_SS_ | min | 994 | 2010 CSC | 0.31305 | 1.2316 | 1.1515 | 0.27441 | 0.013629
| avg | 1239.6 | 2010 CSC | 0.31305 | 1.1861 | 1.1474 | 0.22004 | 0.013629
| max | 1340 | 2010 CSC | 0.31305 | 1.1764 | 1.1453 | 0.20356 | 0.013629
L: 173 CRAWFORD 177 BOSQUE C: THOUSE__5-AEP_PEC__5 C: LAKE_CRK1_5-AEP_SS__59 | min | 156 | FAIL | -0.052495 | -1.2753 | -2.1395 | 0.34027 | 0.045033
| avg | 226.45 | FAIL | -0.052495 | -1.2753 | -2.1395 | 0.23441 | 0.045033
| max | 284 | FAIL | -0.052495 | -1.2753 | -1.8998 | 0.18691 | 0.045033
L: 3592 WACOATCO 13591 COTTONB_ C: 3405THOUSE-3412Temp_Pec C: 3409LAKE_CRK1-3414Temp_SS | min | 199 | PASS | 0.068181 | 1.2704 | 1.1742 | 0.28827 | 0.0098929
| avg | 247.95 | PASS | 0.068181 | 1.2704 | 1.1697 | 0.23136 | 0.0098929
| max | 268 | PASS | 0.068181 | 1.2704 | 1.1697 | 0.21405 | 0.0098929
L:3415 TEMP_SS - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | min | 480 | FAIL | -0.17534 | -1.347 | -1.3043 | 0.31249 | 0.0090579
| avg | 532.85 | PASS | -0.17534 | -1.347 | -1.2857 | 0.2815 | 0.0090579
| max | 581 | PASS | -0.17534 | -1.347 | -1.2857 | 0.25817 | 0.0090579
L:3593 SPGVALLY - 13591 COTTONB_ C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ | min | 199 | PASS | -0.068181 | -1.2984 | -1.2704 | 0.28764 | 0.0098928
| avg | 247.95 | PASS | -0.068181 | -1.2984 | -1.2704 | 0.23086 | 0.0098928
| max | 268 | PASS | -0.068181 | -1.2984 | -1.2704 | 0.21359 | 0.0098928
L:3412 TEMP_PEC - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | min | 750 | PASS | 0.16345 | 1.2934 | 1.1654 | 0.19873 | 0.013151
| avg | 750 | PASS | 0.16345 | 1.2934 | 1.1654 | 0.19873 | 0.013151
| max | 750 | PASS | 0.16345 | 1.2934 | 1.1654 | 0.19873 | 0.013151
L:3593 SPGVALLY - 3594 MCGREG_T C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ | min | 199 | PASS | 0.068181 | 1.2704 | 1.1742 | 0.28697 | 0.0098954
| avg | 247.95 | PASS | 0.068181 | 1.2704 | 1.1697 | 0.23031 | 0.0098954
| max | 268 | PASS | 0.068181 | 1.2704 | 1.1697 | 0.21308 | 0.0098954
L:165 WINDSORS - 173 CRAWFORD C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ | min | 156 | FAIL | -0.052495 | -1.2753 | -2.1395 | 0.33896 | 0.045033
| avg | 226.45 | FAIL | -0.052495 | -1.2753 | -2.1395 | 0.23351 | 0.045033
| max | 284 | FAIL | -0.052495 | -1.2753 | -1.8998 | 0.18619 | 0.045033
L:3668 RNDROCK1 - 3670 RNDRCKNE C:7334 L_MCNEIL - 7336 L_GILLCR | min | 199 | FAIL | -0.062372 | -1.9603 | -1.2034 | 0.5677 | 0.1355
| avg | 247.95 | FAIL | -0.062372 | -1.9603 | -1.2034 | 0.45562 | 0.1355
| max | 268 | FAIL | -0.062372 | -1.9603 | -1.2034 | 0.42154 | 0.1355
L:3666 HUTTOSS1 - 3670 RNDRCKNE C:3429 SANDOW__ - 7040 L_AUSTRO C:7040 L_AUSTRO - 13429 SAND_TXU_ | min | 198 | FAIL | 0.10072 | 1.2166 | 1.3939 | 0.89988 | 0.1014
| avg | 247.6 | FAIL | 0.10072 | 1.2166 | 1.3939 | 0.71961 | 0.1014
| max | 268 | FAIL | 0.10072 | 1.2166 | 1.3939 | 0.66483 | 0.1014
L:3668 RNDRock1 - 3670 RNDRCKNE C:7328 L_AUSTRO - 9040 AUSTROP 1 C:7328 L_AUSTRO - 9040 AUSTROP 2 | min | 199 | FAIL | 0.049147 | 1.1984 | 2.2341 | 0.46255 | 0.14811
| avg | 247.5 | FAIL | 0.049147 | 1.1984 | 2.2341 | 0.37123 | 0.14811
| max | 268 | FAIL | 0.049147 | 1.1984 | 2.2341 | 0.34346 | 0.14811
L:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | min | 994 | 2010 CSC | 0.30438 | 1.2001 | 1.1493 | 0.24866 | 0.0067503
| avg | 1239.6 | 2010 CSC | 0.30438 | 1.16 | 1.1482 | 0.1994 | 0.0067503
| max | 1340 | 2010 CSC | 0.30438 | 1.1515 | 1.1467 | 0.18446 | 0.0067503
L:3407 ELM_MOTT - 3575 WACONCST C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ | min | 302 | FAIL | 0.033857 | 2.7012 | 1.1396 | 0.15905 | 0.13072
| avg | 378.15 | FAIL | 0.033857 | 2.6711 | 1.1396 | 0.12702 | 0.13072
| max | 408 | FAIL | 0.033857 | 2.6521 | 1.1396 | 0.11773 | 0.13072
L:3668 RNDROCK1 - 3670 RNDRCKNE C:7334 L_MCNEIL - 7336 L_GILLCR | min | 198 | FAIL | 0.062372 | 1.2034 | 1.9603 | 0.58044 | 0.1355
| avg | 247.6 | FAIL | 0.062372 | 1.2034 | 1.9603 | 0.46416 | 0.1355
| max | 268 | FAIL | 0.062372 | 1.2034 | 1.9603 | 0.42883 | 0.1355
South to North
L: 3436 WACO_W1_ 3591 WACOWOOD C: THOUSE__5-AEP_PEC__5 C: LAKE_CRK1_5-AEP_SS__59 | min | 199 | PASS | -0.071266 | -0.48853 | -0.24703 | 0.29603 | 0.0087833
| avg | 247.95 | PASS | -0.071266 | -0.48853 | -0.24703 | 0.23759 | 0.0087833
| max | 268 | PASS | -0.071266 | -0.48853 | -0.24703 | 0.21981 | 0.0087833
L: 3650 ELGIN_SS 13430 SAND_TXU C: SANDOW__5-L_AUSTRO5_1Y C: L_AUSTRO5_1Y-SAND_TXU_59 | min | 199 | FAIL | 0.049093 | 0.89797 | 0.43527 | 0.47875 | 0.20251
| avg | 247.95 | FAIL | 0.049093 | 0.89797 | 0.43527 | 0.38423 | 0.20251
| max | 268 | FAIL | 0.049093 | 0.89797 | 0.43527 | 0.35549 | 0.20251
L: 3591 WACOWOOD 3592 WACOATCO C: THOUSE__5-AEP_PEC__5 C: LAKE_CRK1_5-AEP_SS__59 | min | 214 | PASS | -0.071266 | -0.48853 | -0.24703 | 0.27161 | 0.0087847
| avg | 214 | PASS | -0.071266 | -0.48853 | -0.24703 | 0.27161 | 0.0087847
| max | 214 | PASS | -0.071266 | -0.48853 | -0.24703 | 0.27161 | 0.0087847
L: 3409 LAKE_CRK 3414 TEMP_SS_ C: 3405 THOUSE__3412 TEMP_PEC | min | 994 | 2010 CSC | -0.34454 | -0.4867 | -0.15938 | 0.27527 | 0.0051585
| avg | 1239.6 | 2010 CSC | -0.34454 | -0.48502 | -0.15105 | 0.22073 | 0.0051585
| max | 1340 | 2010 CSC | -0.34454 | -0.48502 | -0.14905 | 0.20419 | 0.0051585
L: 3402 LAKE_CRK 3405 THOUSE__ C: THOUSE__5-LAKE_CRK1_5 C: THOUSE__5-AEP_PEC__59 | min | 994 | FAIL | 0.32102 | 0.65195 | 0.6112 | 1.0473 | 0.24606
| avg | 1239.6 | FAIL | 0.32102 | 0.65195 | 0.54443 | 0.83977 | 0.24606
| max | 1340 | FAIL | 0.32102 | 0.62983 | 0.50257 | 0.77685 | 0.24606
L: 3668 RNDROCK1 3670 RNDRCKNE C: SANDOW__5-L_AUSTRO5_1Y C: L_AUSTRO5_1Y-SAND_TXU_59 | min | 199 | FAIL | 0.094364 | 1.0988 | 0.4683 | 0.88553 | 0.11195
| avg | 247.95 | FAIL | 0.094364 | 0.66133 | 0.4683 | 0.71071 | 0.11195
| max | 268 | FAIL | 0.094364 | 0.66133 | 0.4683 | 0.65754 | 0.11195
L: 3409 LAKE_CRK 3414 TEMP_SS_ C: THOUSE__5-LAKE_CRK1_5 C: THOUSE__5-AEP_PEC__59 | min | 994 | 2010 CSC | -0.33921 | -0.49086 | -0.15964 | 0.27115 | 0.009111
| avg | 1239.6 | 2010 CSC | -0.33921 | -0.48917 | -0.15145 | 0.21743 | 0.009111
| max | 1340 | 2010 CSC | -0.33921 | -0.48917 | -0.14948 | 0.20114 | 0.009111
L: 3405 THOUSE__ TEMP_PEC C: 3409 LAKE_CRK 3414 TEMP_SS_ | min | 994 | 2010 CSC | -0.32845 | -0.47489 | -0.15926 | 0.27441 | 0.014029
| avg | 1239.6 | 2010 CSC | -0.32845 | -0.47326 | -0.15025 | 0.22004 | 0.014029
| max | 1340 | 2010 CSC | -0.32845 | -0.47326 | -0.1481 | 0.20356 | 0.014029
L: 173 CRAWFORD 177 BOSQUE C: THOUSE__5-AEP_PEC__5 C: LAKE_CRK1_5-AEP_SS__59 | min | 156 | FAIL | 0.05598 | 0.59501 | 1.0147 | 0.34027 | 0.045508
| avg | 226.45 | PASS | 0.05598 | 0.5834 | 1.0147 | 0.23441 | 0.045508
| max | 284 | FAIL | 0.05598 | 0.5834 | 0.7899 | 0.18691 | 0.045508
L: 3592 WACOATCO 13591 COTTONB_ C: THOUSE__5-AEP_PEC__5 C: LAKE_CRK1_5-AEP_SS__59 | min | 199 | PASS | -0.071266 | -0.48853 | -0.24703 | 0.28827 | 0.00878
| avg | 247.95 | PASS | -0.071266 | -0.48853 | -0.24703 | 0.23136 | 0.00878
| max | 268 | PASS | -0.071266 | -0.48853 | -0.24703 | 0.21405 | 0.00878
L:3415 TEMP_SS - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | min | 480 | FAIL | 0.18423 | 0.40003 | 0.47978 | 0.31249 | 0.010298
| avg | 532.85 | PASS | 0.18423 | 0.40003 | 0.47978 | 0.2815 | 0.010298
| max | 581 | PASS | 0.18423 | 0.40003 | 0.47913 | 0.25817 | 0.010298
L:3593 SPGVALLY - 13591 COTTONB_ C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ | min | 199 | PASS | 0.071266 | 0.53598 | 0.48853 | 0.28764 | 0.0087801
| avg | 247.95 | PASS | 0.071266 | 0.53598 | 0.48853 | 0.23086 | 0.0087801
| max | 268 | PASS | 0.071266 | 0.53598 | 0.48853 | 0.21359 | 0.0087801
L:3412 TEMP_PEC - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | min | 750 | PASS | -0.17145 | -0.47511 | -0.17863 | 0.19873 | 0.013484
| avg | 750 | PASS | -0.17145 | -0.47511 | -0.17863 | 0.19873 | 0.013484
| max | 750 | PASS | -0.17145 | -0.47511 | -0.17863 | 0.19873 | 0.013484
L:3593 SPGVALLY - 3594 MCGREG_T C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ | min | 199 | PASS | -0.071266 | -0.48854 | -0.24703 | 0.28697 | 0.0087824
| avg | 247.95 | PASS | -0.071266 | -0.48854 | -0.24703 | 0.23031 | 0.0087824
| max | 268 | PASS | -0.071266 | -0.48854 | -0.24703 | 0.21308 | 0.0087824
L:165 WINDSORS - 173 CRAWFORD C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ | min | 156 | FAIL | 0.05598 | 0.59501 | 1.0147 | 0.33896 | 0.045508
| avg | 226.45 | PASS | 0.05598 | 0.5834 | 1.0147 | 0.23351 | 0.045508
| max | 284 | FAIL | 0.05598 | 0.5834 | 0.7899 | 0.18619 | 0.045508
L:3668 RNDROCK1 - 3670 RNDRCKNE C:7334 L_MCNEIL - 7336 L_GILLCR | min | 199 | FAIL | 0.056829 | 1.1808 | 0.5158 | 0.5677 | 0.14218
| avg | 247.95 | FAIL | 0.056829 | 1.1808 | 0.5158 | 0.45562 | 0.14218
| max | 268 | FAIL | 0.056829 | 1.1808 | 0.5158 | 0.42154 | 0.14218
L:3666 HUTTOSS1 - 3670 RNDRCKNE C:3429 SANDOW__ - 7040 L_AUSTRO C:7040 L_AUSTRO - 13429 SAND_TXU_ | min | 198 | FAIL | -0.094364 | -1.488 | -0.52021 | 0.89988 | 0.11195
| avg | 247.6 | FAIL | -0.094364 | -1.488 | -0.52021 | 0.71961 | 0.11195
| max | 268 | FAIL | -0.094364 | -1.488 | -0.52021 | 0.66483 | 0.11195
L:3666 HUTTOSS1 - 3670 RNDRCKNE C:7328 L_AUSTRO - 9040 AUSTROP 1 C:7328 L_AUSTRO - 9040 AUSTROP 2 | min | 199 | FAIL | -0.04417 | -1.2782 | -1.5141 | 0.46255 | 0.15733
| avg | 247.95 | FAIL | -0.04417 | -1.2782 | -1.5141 | 0.37123 | 0.15733
| max | 268 | FAIL | -0.04417 | -1.2782 | -1.5141 | 0.34346 | 0.15733
L:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | min | 994 | 2010 CSC | -0.31775 | -0.48856 | -0.15463 | 0.24866 | 0.0051827
| avg | 1239.6 | 2010 CSC | -0.31775 | -0.48687 | -0.14841 | 0.1994 | 0.0051827
| max | 1340 | 2010 CSC | -0.31775 | -0.48687 | -0.14699 | 0.18446 | 0.0051827
L:3407 ELM_MOTT - 3575 WACONCST C:3405 THOUSE__ - 3412 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ | min | 302 | FAIL | -0.037382 | -1.4547 | -0.33327 | 0.15905 | 0.11444
| avg | 378.15 | FAIL | -0.037382 | -1.4275 | -0.29953 | 0.12702 | 0.11444
| max | 408 | FAIL | -0.037382 | -1.4103 | -0.29953 | 0.11773 | 0.11444
L:3666 RNDROCK1 - 3670 RNDRCKNE C:7334 L_MCNEIL - 7336 L_GILLCR | min | 198 | FAIL | -0.056829 | -1.3933 | -1.1808 | 0.58044 | 0.14218
| avg | 247.6 | FAIL | -0.056829 | -1.3933 | -1.1808 | 0.46416 | 0.14218
| max | 268 | FAIL | -0.056829 | -1.3933 | -1.1808 | 0.42883 | 0.14218
West to North
L: Longcreek - Cookfield 345kV [1439-1442] C: Fisher Road - Oklaunion 345kV [1425-6100] | min | 994 | Pass | 0.21684 | 1.3238 | 0.95873 | 0.14555 | 0.037436
| avg | 1240 | Pass | 0.21684 | 1.2804 | 0.95863 | 0.11667 | 0.037436
| max | 1340 | Pass | 0.21684 | 1.2635 | 0.95863 | 0.10796 | 0.037436
L: Willow Creek - Parker 345 [1421-1436] C: Jacksboro SS - Krum 345kV [1429-1730] | min | 994 | Fail | 0.19366 | 1.9635 | 1.1713 | 0.91608 | 0.19328
| avg | 1240 | Fail | 0.19366 | 1.8676 | 1.1712 | 0.73434 | 0.19328
| max | 1340 | Fail | 0.19366 | 1.7303 | 1.1712 | 0.67954 | 0.19328
L: Parker - Benbrook 345 [1436-1869 C:Lewisville Jones Street - Lakepointe 138kV [1972-37010] & Lakepointe - Lewisville TT [37010-37080] | min | 956 | Fail | 0.089499 | 1.2713 | 1.1806 | 0.3981 | 0.21249
| avg | 1086 | Fail | 0.089499 | 1.2568 | 1.1806 | 0.35044 | 0.21249
| max | 1195 | Fail | 0.089499 | 1.2568 | 1.1806 | 0.31848 | 0.21249
L:Leon Switch - Flatcreek 138kV [1624-1642] C:Comanchee SS Auto [1440-1441] | min | 78 | Fail | 0.031918 | 0 | 1.3834 | 0.46743 | 0.13534
| avg | 97 | Fail | 0.031918 | 0 | 1.3834 | 0.37587 | 0.13534
| max | 105 | Fail | 0.031918 | 0 | 1.3834 | 0.34723 | 0.13534
L:Murray BEC POD - Graham 138kV [1371-1431] C:Graham - Longcreek / Longcreek - Cookfield 345 kV [1430-1435 / 1439-1442] | min | 173 | Fail | 0.056915 | 2.1292 | 1.0819 | 0.26113 | 0.075169
| avg | 215 | Pass | 0.056915 | 1.9442 | 1.0421 | 0.21012 | 0.075169
| max | 233 | Pass | 0.056915 | 1.8703 | 1.0421 | 0.19389 | 0.075169
L: Graham - Longcreek 345kV [1430-1435] C: Graham - Cookfield 345kV [1430-1442] | min |  | 2010 CSC
| avg |  | 2010 CSC
| max |  | 2010 CSC
L: Willow Creek - Parker 345kV [1421-1436] C:Graham - Parker 345 (Ckt1) 345 kV [1430-1436] | min | 994 | Fail | 0.18741 | 1.849 | 1.1766 | 0.9126 | 0.19907
| avg | 1240 | Fail | 0.18741 | 1.7682 | 1.1765 | 0.73155 | 0.19907
| max | 1340 | Fail | 0.18741 | 1.6515 | 1.1765 | 0.67696 | 0.19907
L: Willow Creek - Parker 345kV [1421-1436] C:Graham - Parker 345 (Ckt2) 345 kV [1430-1436] | min | 994 | Fail | 0.18741 | 1.849 | 1.1766 | 0.9126 | 0.19907
| avg | 1240 | Fail | 0.18741 | 1.7682 | 1.1765 | 0.73155 | 0.19907
| max | 1340 | Fail | 0.18741 | 1.6515 | 1.1765 | 0.67696 | 0.19907
L: MURRY_P8 to PAIP4B [1371 - 6169] C: COOKFIELD / LONGCREEK - GRAHAM8 [1430 - 1435] and [1430 - 1442] | min | 155 | Pass | -0.05784 | -1.0676 | -1.0878 | 0.23336 | 0.089225
| avg | 155 | Pass | -0.05784 | -1.0676 | -1.0878 | 0.23336 | 0.089225
| max | 155 | Pass | -0.05784 | -1.0676 | -1.0878 | 0.23336 | 0.089225
L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:COOKFIELD / LONGCREEK - GRAHAM8 [1430 - 1442] and [1430 - 1435] | min | 994 | 2010 CSC | 0.27941 | 0.62726 | 0.063548 | 0.20552 | 0.067559
| avg | 1235.45 | 2010 CSC | 0.27941 | 0.46397 | 0.050466 | 0.16536 | 0.067559
| max | 1340 | 2010 CSC | 0.27941 | 0.43301 | 0.047656 | 0.15246 | 0.067559
L: MURRY_P8 - GRHAMSES 138kV [1371 - 1431] C:SWEETWATER / MULBERRY - LONGCREEK8 [1420 - 1439] & [1435 - 6230] | min | 173 | Fail | 0.052967 | 2.2836 | 0.94639 | 0.44336 | 0.043408
| avg | 215.4 | Fail | 0.052967 | 2.0835 | 0.79141 | 0.35609 | 0.043408
| max | 223 | Fail | 0.052967 | 2.0835 | 0.79141 | 0.34395 | 0.043408
L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | min | 994 | 2010 CSC | 0.26584 | 1.4499 | 0.43663 | 0.52401 | 0.22375
| avg | 1235.45 | 2010 CSC | 0.26584 | 1.4241 | 0.55385 | 0.4216 | 0.22375
| max | 1340 | 2010 CSC | 0.26584 | 1.4152 | 0.55385 | 0.3887 | 0.22375
L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:GRAHAM - LONGCREEK / LONGCREEK - COOKFIELD8 | min | 994 | 2010 CSC | 0.27941 | 0.62726 | 0.063548 | 0.20552 | 0.067559
| avg | 1235.45 | 2010 CSC | 0.27941 | 0.46397 | 0.050466 | 0.16536 | 0.067559
| max | 1340 | 2010 CSC | 0.27941 | 0.43301 | 0.047656 | 0.15246 | 0.067559
L: LONCREK2 - COKFIELD 345kV [ 1439 - 1442] C: GRHAMSES - LONGCREK 345kV [1430 - 1435] | min | 994 | PASS | 0.2859 | 1.3598 | 0.52363 | 0.20458 | 0.01913
| avg | 1235.45 | PASS | 0.2859 | 1.3042 | 0.58955 | 0.1646 | 0.01913
| max | 1340 | PASS | 0.2859 | 1.2836 | 0.58955 | 0.15176 | 0.01913
L: GRHAMSES - COKFIELD 345kV [1430 - 1442] C: GRHAMSES - LONGCREK 345kV [1430 - 1435] | min | 994 | 2010 CSC | -0.30057 | -0.5212 | -1.004 | 0.17131 | 0.052402
| avg | 1235.45 | 2010 CSC | -0.30057 | -0.58779 | -0.92703 | 0.13783 | 0.052402
| max | 1340 | 2010 CSC | -0.30057 | -0.58779 | -0.8585 | 0.12707 | 0.052402
L: GRHAMSES - LONGCREK 345kV [1430 - 1435] C: LONCREK2 - COKFIELD 345kV [1439 - 1442] | min | 994 | 2010 CSC | -0.29026 | -0.4575 | -1.0374 | 0.20956 | 0.022389
| avg | 1235.45 | 2010 CSC | -0.29026 | -0.56383 | -0.95791 | 0.1686 | 0.022389
| max | 1340 | 2010 CSC | -0.29026 | -0.56383 | -0.8871 | 0.15545 | 0.022389
L: COMCHESS - COMANCHE 138 kV [1441 -1650] C: COMCHESS - COMCHPKW 345kV [1440 - 1900] | min | 173 | PASS | 0.06101 | 1.3243 | 0.87047 | 0.21926 | 0.12631
| avg | 215.35 | PASS | 0.06101 | 1.3243 | 0.87047 | 0.17614 | 0.12631
| max | 233 | PASS | 0.06101 | 1.3243 | 0.87047 | 0.1628 | 0.12631
L: LINGLVLL - FLATCRK_ 138 kV [1640 - 1642] C: COMCHESS - SARC7A 345kV [1440 - 6444] | min | 343 | Fail | -0.039859 | -0.94102 | -1.2562 | 0.21522 | 0.12854
| avg | 401.4 | Fail | -0.039859 | -0.89812 | -1.2083 | 0.18391 | 0.12854
| max | 416 | Fail | -0.039859 | -0.86259 | -1.2083 | 0.17745 | 0.12854
L:1427 FISHERRD - 1448 WCHTFLLS C:1422 BOWMAN_5 - 1425 FISHRDSS | min | 260 | FAIL | 0.055699 | 4.625 | 0.94993 | 0.14235 | 0.30037
| avg | 260 | FAIL | 0.055699 | 4.625 | 0.94993 | 0.14235 | 0.30037
| max | 260 | FAIL | 0.055699 | 4.625 | 0.94993 | 0.14235 | 0.30037
L: 1426 FISHRDSS - 1427 FISHERRD C: 1422 BOWMAN5 - 1425 FISHRDSS | min | 287 | FAIL | 0.055699 | 4.625 | 0.94993 | 0.12822 | 0.30037
| avg | 287 | FAIL | 0.055699 | 4.625 | 0.94993 | 0.12822 | 0.30037
| max | 287 | FAIL | 0.055699 | 4.625 | 0.94993 | 0.12822 | 0.30037
L: 1371 MURRY_P8 - 1431 GRHAMSES C: 1430 GRHAMES - 1435 LONGCREK C: 1430 GRHAMES - 1442 COKFIELD | min | 173 | FAIL | 0.05784 | 2.0952 | 1.0676 | 0.20898 | 0.089233
| avg | 215.35 | PASS | 0.05784 | 1.9131 | 1.032 | 0.16789 | 0.089233
| max | 233 | PASS | 0.05784 | 1.8404 | 1.032 | 0.15517 | 0.089233
L: 1422 BOWMAN5 - 1425 FISHRDSS C: 1430 GRHAMES - 1435 LONGCREK C: 1439 LONCREK2 - 1442 COKFIELD | min | 956 | PASS | -0.20342 | -0.97013 | -0.88939 | 0.13163 | 0.13935
| avg | 1079.45 | FAIL | -0.20342 | -0.97005 | -0.88825 | 0.11657 | 0.13935
| max | 1195 | FAIL | -0.20342 | -0.97005 | -0.87198 | 0.1053 | 0.13935
L: 1430 GRHAMES - 1442 COKFIELD C: 1425 FISHRDSS - 6100 OKLA7A | min | 994 | 2010 CSC | -0.23151 | -0.96134 | -0.96145 | 0.11409 | 0.095553
| avg | 1239.6 | 2010 CSC | -0.23151 | -0.96125 | -0.88765 | 0.091486 | 0.095553
| max | 1340 | 2010 CSC | -0.23151 | -0.96125 | -0.82191 | 0.084632 | 0.095553
L: 1430 GRHAMES - 1435 LONGCREK C: 1048 TONKAWA - 1430 GRHAMSES | min | 994 | 2010 CSC | -0.23968 | -0.96134 | -1.0516 | 0.14968 | 0.016223
| avg | 1239.6 | 2010 CSC | -0.23968 | -0.96125 | -0.97034 | 0.12002 | 0.016223
| max | 1340 | 2010 CSC | -0.23968 | -0.96125 | -0.89816 | 0.11103 | 0.016223
L: 1596 GRAHAMSW - 1601 GRAHAME_ C: 37980 TNWICKET- 38000 TNPYOTE C: 38000 TNPYOTE_ - 38020 TNWORSHA C: 38020 TNWORSHA - 38040 TNH20__ | min | 233 | FAIL | -0.031296 | -7.5073 | -3.5359 | 0.64743 | 0.11211
| avg | 290.5 | FAIL | -0.031296 | -5.8449 | -3.5359 | 0.51928 | 0.11211
| max | 314 | FAIL | -0.031296 | -5.428 | -3.5359 | 0.48041 | 0.11211
L: 1431 GRHAMSES - 1601 GRAHAME C: 1440 COMCHESS - 6444 SARC7A | min | 199 | FAIL | 0.036737 | 3.2115 | 2.8271 | 0.74759 | 0.092627
| avg | 221.5 | FAIL | 0.036737 | 3.2115 | 2.8271 | 0.67165 | 0.092627
| max | 239 | FAIL | 0.036737 | 2.55 | 2.8271 | 0.62247 | 0.092627
North to West
L: Longcreek - Cookfield 345kV [1439-1442] C: Fisher Road - Oklaunion 345kV [1425-6100] | min | 994 | PASS | -0.21324 | -0.34181 | -1.0797 | 0.14555 | 0.019675
| avg | 1240 | PASS | -0.21324 | -0.29765 | -1.0649 | 0.11667 | 0.019675
| max | 1340 | PASS | -0.21324 | -0.27836 | -1.0617 | 0.10796 | 0.019675
L: Willow Creek - Parker 345 [1421-1436] C: Jacksboro SS - Krum 345kV [1429-1730] | min | 994 | FAIL | -0.20614 | -0.91156 | -1.1469 | 0.91608 | 0.12496
| avg | 1240 | FAIL | -0.20614 | -0.8215 | -1.1435 | 0.73434 | 0.12496
| max | 1340 | FAIL | -0.20614 | -0.69254 | -1.1432 | 0.67954 | 0.12496
L: Parker - Benbrook 345 [1436-1869 C:Lewisville Jones Street - Lakepointe 138kV [1972-37010] & Lakepointe - Lewisville TT [37010-37080] | min | 956 | FAIL | -0.092823 | -0.25972 | -1.3816 | 0.3981 | 0.1731
| avg | 1086 | FAIL | -0.092823 | -0.24573 | -1.3718 | 0.35044 | 0.1731
| max | 1195 | FAIL | -0.092823 | -0.24573 | -1.3644 | 0.31848 | 0.1731
L:Leon Switch - Flatcreek 138kV [1624-1642] C:Comanchee SS Auto [1440-1441] | min | 78 | FAIL | -0.032048 | 0 | -2.3607 | 0.46743 | 0.1344
| avg | 97 | FAIL | -0.032048 | 0 | -2.3607 | 0.37587 | 0.1344
| max | 105 | FAIL | -0.032048 | 0 | -2.3607 | 0.34723 | 0.1344
L:Murray BEC POD - Graham 138kV [1371-1431] C:Graham - Longcreek / Longcreek - Cookfield 345 kV [1430-1435 / 1439-1442] | min | 173 | PASS | -0.054453 | -1.215 | -1.9314 | 0.26113 | 0.033107
| avg | 215 | PASS | -0.054453 | -1.0216 | -1.7807 | 0.21012 | 0.033107
| max | 233 | PASS | -0.054453 | -0.94443 | -1.7807 | 0.19389 | 0.033107
L: Graham - Longcreek 345kV [1430-1435] C: Graham - Cookfield 345kV [1430-1442] | min |  | 2010 CSC
| avg |  | 2010 CSC
| max |  | 2010 CSC
L: Willow Creek - Parker 345kV [1421-1436] C:Graham - Parker 345 (Ckt1) 345 kV [1430-1436] | min | 994 | FAIL | -0.19846 | -0.80561 | -1.2029 | 0.9126 | 0.1361
| avg | 1240 | FAIL | -0.19846 | -0.72927 | -1.1983 | 0.73155 | 0.1361
| max | 1340 | FAIL | -0.19846 | -0.61906 | -1.1966 | 0.67696 | 0.1361
L: Willow Creek - Parker 345kV [1421-1436] C:Graham - Parker 345 (Ckt2) 345 kV [1430-1436] | min | 994 | FAIL | -0.19846 | -0.80561 | -1.2029 | 0.9126 | 0.1361
| avg | 1240 | FAIL | -0.19846 | -0.72927 | -1.1983 | 0.73155 | 0.1361
| max | 1340 | FAIL | -0.19846 | -0.61906 | -1.1966 | 0.67696 | 0.1361
L: MURRY_P8 to PAIP4B [1371 - 6169] C: COOKFIELD / LONGCREEK - GRAHAM8 [1430 - 1435] and [1430 - 1442] | min | 155 | FAIL | 0.054454 | 2.1759 | 0.14493 | 0.23336 | 0.033106
| avg | 155 | FAIL | 0.054454 | 2.1759 | 0.14493 | 0.23336 | 0.033106 | Newly added
| max | 155 | FAIL | 0.054454 | 2.1759 | 0.14493 | 0.23336 | 0.033106
L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:COOKFIELD / LONGCREEK - GRAHAM8 [1430 - 1442] and [1430 - 1435] | min | 994 | 2010 CSC | -0.29899 | -0.1939 | -1.063 | 0.20552 | 0.074237
| avg | 1235.45 | 2010 CSC | -0.29899 | -0.15944 | -1.0508 | 0.16536 | 0.074237
| max | 1340 | 2010 CSC | -0.29899 | -0.1529 | -1.0481 | 0.15246 | 0.074237
L: MURRY_P8 - GRHAMSES 138kV [1371 - 1431] C:SWEETWATER / MULBERRY - LONGCREEK8 [1420 - 1439] & [1435 - 6230] | min | 173 | FAIL | -0.053826 | -1.2366 | -1.9419 | 0.44336 | 0.055845
| avg | 215.4 | FAIL | -0.053826 | -1.0396 | -1.7894 | 0.35609 | 0.055845
| max | 223 | FAIL | -0.053826 | -1.0396 | -1.7894 | 0.34395 | 0.055845
L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:SWEET WATER - LONGCREEK / BITTER CREEK - MULBERRY8 | min | 994 | 2010 CSC | -0.32598 | -0.17975 | -0.63346 | 0.52401 | 0.18366
| avg | 1235.45 | 2010 CSC | -0.32598 | -0.15876 | -0.49413 | 0.4216 | 0.18366
| max | 1340 | 2010 CSC | -0.32598 | -0.1515 | -0.49413 | 0.3887 | 0.18366
L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:GRAHAM - LONGCREEK / LONGCREEK - COOKFIELD8 | min | 994 | 2010 CSC | -0.29899 | -0.1939 | -1.063 | 0.20552 | 0.074237
| avg | 1235.45 | 2010 CSC | -0.29899 | -0.15944 | -1.0508 | 0.16536 | 0.074237
| max | 1340 | 2010 CSC | -0.29899 | -0.1529 | -1.0481 | 0.15246 | 0.074237
L: LONCREK2 - COKFIELD 345kV [ 1439 - 1442] C: GRHAMSES - LONGCREK 345kV [1430 - 1435] | min | 994 | PASS | -0.29026 | -0.33498 | -0.59693 | 0.20458 | 0.031091
| avg | 1235.45 | PASS | -0.29026 | -0.28024 | -0.50643 | 0.1646 | 0.031091
| max | 1340 | PASS | -0.29026 | -0.25996 | -0.50643 | 0.15176 | 0.031091
L: GRHAMSES - COKFIELD 345kV [1430 - 1442] C: GRHAMSES - LONGCREK 345kV [1430 - 1435] | min | 994 | 2010 CSC | 0.29026 | 0.59693 | 0.035271 | 0.17131 | 0.019453
| avg | 1235.45 | 2010 CSC | 0.29026 | 0.50643 | 0.044411 | 0.13783 | 0.019453
| max | 1340 | 2010 CSC | 0.29026 | 0.50643 | 0.11537 | 0.12707 | 0.019453
L: GRHAMSES - LONGCREK 345kV [1430 - 1435] C: LONCREK2 - COKFIELD 345kV [1439 - 1442] | min | 994 | 2010 CSC | 0.28965 | 0.70438 | 0.035267 | 0.20956 | 0.018141
| avg | 1235.45 | 2010 CSC | 0.28965 | 0.55506 | 0.04441 | 0.1686 | 0.018141
| max | 1340 | 2010 CSC | 0.28965 | 0.55506 | 0.11537 | 0.15545 | 0.018141
L: COMCHESS - COMANCHE 138 kV [1441 -1650] C: COMCHESS - COMCHPKW 345kV [1440 - 1900] | min | 173 | PASS | -0.06049 | -0.31994 | -1.8937 | 0.21926 | 0.12167
| avg | 215.35 | PASS | -0.06049 | -0.31994 | -1.8937 | 0.17614 | 0.12167
| max | 233 | PASS | -0.06049 | -0.31994 | -1.8937 | 0.1628 | 0.12167
L: LINGLVLL - FLATCRK_ 138 kV [1640 - 1642] C: COMCHESS - SARC7A 345kV [1440 - 6444] | min | 343 | FAIL | 0.037748 | 2.0394 | 0.28071 | 0.21522 | 0.133
| avg | 401.42 | FAIL | 0.037748 | 1.9941 | 0.23064 | 0.1839 | 0.133
| max | 416 | FAIL | 0.037748 | 1.9566 | 0.23064 | 0.17745 | 0.133
L:1427 FISHERRD - 1448 WCHTFLLS C:1422 BOWMAN_5 - 1425 FISHRDSS | min | 260 | FAIL | -0.04016 | -5.4059 | -1.562 | 0.14235 | 0.34188
| avg | 260 | FAIL | -0.04016 | -5.4059 | -1.562 | 0.14235 | 0.34188
| max | 260 | FAIL | -0.04016 | -5.4059 | -1.562 | 0.14235 | 0.34188
L: 1426 FISHRDSS - 1427 FISHERRD C: 1422 BOWMAN5 - 1425 FISHRDSS | min | 287 | FAIL | -0.04016 | -5.4059 | -1.562 | 0.12822 | 0.34189
| avg | 287 | FAIL | -0.04016 | -5.4059 | -1.562 | 0.12822 | 0.34189
| max | 287 | FAIL | -0.04016 | -5.4059 | -1.562 | 0.12822 | 0.34189
L: 1371 MURRY_P8 - 1431 GRHAMSES C: 1430 GRHAMES - 1435 LONGCREK C: 1430 GRHAMES - 1442 COKFIELD | min | 173 | PASS | -0.054453 | -1.215 | -1.9314 | 0.20898 | 0.033107
| avg | 215.35 | PASS | -0.054453 | -1.0216 | -1.7807 | 0.16789 | 0.033107
| max | 233 | PASS | -0.054453 | -0.94443 | -1.7807 | 0.15517 | 0.033107
L: 1422 BOWMAN5 - 1425 FISHRDSS C: 1430 GRHAMES - 1435 LONGCREK C: 1439 LONCREK2 - 1442 COKFIELD | min | 956 | FAIL | 0.17693 | 1.1296 | 0.083804 | 0.13163 | 0.14003
| avg | 1079.45 | FAIL | 0.17693 | 1.1296 | 0.081527 | 0.11657 | 0.14003
| max | 1195 | FAIL | 0.17693 | 1.1018 | 0.08097 | 0.1053 | 0.14003
L: 1430 GRHAMES - 1442 COKFIELD C: 1425 FISHRDSS - 6100 OKLA7A | min | 994 | 2010 CSC | 0.21324 | 1.0989 | 0.087965 | 0.11409 | 0.068474
| avg | 1239.6 | 2010 CSC | 0.21324 | 1.0666 | 0.085208 | 0.091486 | 0.068474
| max | 1340 | 2010 CSC | 0.21324 | 1.0631 | 0.083244 | 0.084632 | 0.068474
L: 1430 GRHAMES - 1435 LONGCREK C: 1048 TONKAWA - 1430 GRHAMSES | min | 994 | 2010 CSC | 0.24239 | 1.074 | 0.080747 | 0.14968 | 0.024508
| avg | 1239.6 | 2010 CSC | 0.24239 | 1.0596 | 0.0782 | 0.12002 | 0.024508
| max | 1340 | 2010 CSC | 0.24239 | 1.0566 | 0.076387 | 0.11103 | 0.024508
L: 1596 GRAHAMSW - 1601 GRAHAME_ C: 37980 TNWICKET- 38000 TNPYOTE C: 38000 TNPYOTE_ - 38020 TNWORSHA C: 38020 TNWORSHA - 38040 TNH20__ | min | 233 | FAIL | 0.032186 | 8.2719 | 1.7591 | 0.64743 | 0.10842
| avg | 290.5 | FAIL | 0.032186 | 6.6555 | 1.4621 | 0.51928 | 0.10842
| max | 314 | FAIL | 0.032186 | 6.2501 | 1.4121 | 0.48041 | 0.10842
L: 1431 GRHAMSES - 1601 GRAHAME C: 1440 COMCHESS - 6444 SARC7A | min | 199 | FAIL | -0.03769 | -2.1543 | -3.7315 | 0.74759 | 0.089751
| avg | 221.5 | FAIL | -0.03769 | -2.1543 | -3.7315 | 0.67165 | 0.089751
| max | 239 | FAIL | -0.03769 | -1.4387 | -3.7315 | 0.62247 | 0.089751
North to Houston
L: H_O_C - Knight 138kV [47150-47331] C:Bellaire - Garrot 138kV [47015-47320] & H_O_C - Garrot 138kV [47155-47660] | min | 247 | Fail | 0.01171 | 7.3152 | 8.1724 | 0.74146 | 1.6398
| avg | 378 | Fail | 0.01171 | 7.3152 | 7.6006 | 0.4845 | 1.6398
| max | 461 | Fail | 0.01171 | 7.3152 | 7.085 | 0.39727 | 1.6398
L:Singleton - TH Wharton 345kV [44645-45500] C:Singleton - Tomball 345kV [44645-46500] & Roans - King 345kV [40600-45872] | min |  | 2010 CSC
| avg |  | 2010 CSC
| max |  | 2010 CSC
L: Garrot - Midtown 138kV [47660-47705] C:Singleton - Tomball 345kV [44645-46500] & Roans - King 345kV [40600-45972] | min | 247 | Fail | 0.032416 | 2.429 | 5.717 | 1.2832 | 1.0057
| avg | 247 | Fail | 0.032416 | 2.429 | 5.717 | 1.2832 | 1.0057
| max | 247 | Fail | 0.032416 | 2.429 | 5.717 | 1.2832 | 1.0057
L: Midtown - Midtown Reit 138kV [47705-47707] C:Singleton - Tomball 345kV [44645-46500] & Roans - King 345kV [40600-45972] | min | 251 | Fail | 0.032416 | 2.429 | 5.717 | 1.2627 | 1.0057
| avg | 251 | Fail | 0.032416 | 2.429 | 5.717 | 1.2627 | 1.0057
| max | 251 | Fail | 0.032416 | 2.429 | 5.717 | 1.2627 | 1.0057
L: Midtown Reit - Polk 138kV [47707-47730] C:Singleton - Tomball 345kV [44645-46500] & Roans - King 345kV [40600-45972] | min | 251 | Fail | 0.032416 | 2.429 | 5.717 | 1.2627 | 1.0057
| avg | 251 | Fail | 0.032416 | 2.429 | 5.717 | 1.2627 | 1.0057
| max | 251 | Fail | 0.032416 | 2.429 | 5.717 | 1.2627 | 1.0057
L: Obrien - Singleton 345kV [44500-44645] C:Singleton - Tomball 345kV [44645-46500] & Roans - King 345kV [40600-45972] | min |  | 2010 CSC
| avg |  | 2010 CSC
| max |  | 2010 CSC
L: Singleton - Tomball 345kV [44645-46500] C:Singleton - TH Wharton [44645-45500] & Singleton - Obrien [44500-44645] | min | 1505 | PASS | 0.32042 | 1.1366 | 1.0294 | 0.11277 | 0.061447
| avg | 1749 | PASS | 0.32042 | 1.1366 | 1.0277 | 0.097035 | 0.061447
| max | 1793 | PASS | 0.32042 | 1.1245 | 1.0274 | 0.094653 | 0.061447
L:Jewett - Singleton [3391-44645] C:Gibbons Creek - Singleton 345kV Double Circuit [44645-967] | min | 1005 | Fail | 0.31976 | 1.1451 | 1.0302 | 0.45045 | 0.048552
| avg | 1165 | Fail | 0.31976 | 1.1451 | 1.0301 | 0.38859 | 0.048552
| max | 1195 | Fail | 0.31976 | 1.1451 | 1.0301 | 0.37883 | 0.048552
L:Gibbons Creek - Singleton 345kV [44645-967] C:Gibbons Creek - Singleton 345kV [44645-967] | min | 2080 | Fail | 0.29925 | 1.5996 | 1.0256 | 0.39733 | 0.10955
| avg | 2080 | Fail | 0.29925 | 1.5996 | 1.0256 | 0.39733 | 0.10955
| max | 2080 | Fail | 0.29925 | 1.5996 | 1.0256 | 0.39733 | 0.10955
L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 99 C: 967 GIBN_CRE 345 44645 SNGLTN_3 345 75 | min | 2080 | Fail | 0.29925 | 1.5996 | 1.0256 | 0.39733 | 0.10955
| avg | 2080 | Fail | 0.29925 | 1.5996 | 1.0256 | 0.39733 | 0.10955
| max | 2080 | Fail | 0.29925 | 1.5996 | 1.0256 | 0.39733 | 0.10955
L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 75 C: 967 GIBN_CRE 345 44645 SNGLTN_3 345 99 C: 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99 | min | 2080 | Fail | 0.2847 | 1.6226 | 1.0296 | 0.39693 | 0.11886
| avg | 2080 | Fail | 0.2847 | 1.6226 | 1.0296 | 0.39693 | 0.11886
| max | 2080 | Fail | 0.2847 | 1.6226 | 1.0296 | 0.39693 | 0.11886
L: 3390 JEWETT_S 345 44645 SNGLTN_3 345 1 C: GIBN_CREK - SNGLTN_75 (967-44645) & GIBN_CREK - SNGLTN_99 (967-44645) | min | 1005 | Fail | 0.31294 | 1.0626 | 1.0329 | 0.38375 | 0.083245
| avg | 1165 | Fail | 0.31294 | 1.0574 | 1.0329 | 0.33104 | 0.083245
| max | 1195 | Fail | 0.31294 | 1.0574 | 1.0329 | 0.32273 | 0.083245
L: 975 JKCREEK1 345 3400 TWIN_OAK 345 1 C: JEWETT - SNGLTN_74 (3390-44645) & JEWETT - SNGLTN_98 (3391-44645) [3390 - 44645 CKT 1] & [3391 - 44645 CKT 1] | min | 1376 | Fail | -0.27669 | -0.71179 | -0.35962 | 0.40981 | 0.042561
| avg | 1376 | Fail | -0.27669 | -0.71179 | -0.35962 | 0.40981 | 0.042561
| max | 1376 | Fail | -0.27669 | -0.71179 | -0.35962 | 0.40981 | 0.042561
L: 40600 ROANS___ 345 45972 KUYDAL75 345 75 C: SNGLTN - T_H_W__98 (44645-45500) & SNGLTN - OBRIEN_99 (44645-44500) | min | 1541 | PASS | 0.2768 | 1.1287 | 1.056 | 0.090745 | 0.090814
| avg | 1758.9 | PASS | 0.2768 | 1.1287 | 1.0515 | 0.079503 | 0.090814
| max | 1793 | PASS | 0.2768 | 1.1173 | 1.0509 | 0.077991 | 0.090814
L: 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99 C: SNGLTN - TOMBAL_74 (44645-46500) & SNGLTN - ROANS_75 (44645-40600) | min | 1004 | 2010 CSC | -0.28955 | -0.99751 | -0.32929 | 0.38652 | 0.023506
| avg | 1377.39 | 2010 CSC | -0.28955 | -1.0058 | -0.39459 | 0.28174 | 0.023506
| max | 1562 | 2010 CSC | -0.28955 | -1.0109 | -0.40971 | 0.24844 | 0.023506
L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 75 C: JEWETT_S5-T_H_W___345B & JEWETT_N5-TOMBAL__345B [3390 - 44645] & [3391 - 44645] | min | 2080 | PASS | 0.30597 | 0.73754 | 1.0265 | 0.21373 | 0.062135
| avg | 2080 | PASS | 0.30597 | 0.73754 | 1.0265 | 0.21373 | 0.062135
| max | 2080 | PASS | 0.30597 | 0.73754 | 1.0265 | 0.21373 | 0.062135
L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 99 C: JEWETT_S5-T_H_W___345B & JEWETT_N5-TOMBAL__345B [3390 - 44645] & [3391 - 44645] | min | 2080 | PASS | 0.30597 | 0.73754 | 1.0265 | 0.21373 | 0.062135
| avg | 2080 | PASS | 0.30597 | 0.73754 | 1.0265 | 0.21373 | 0.062135
| max | 2080 | PASS | 0.30597 | 0.73754 | 1.0265 | 0.21373 | 0.062135
L:46290 ROTHWOOD74 - 40900 KING___345 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A |  | 1710 | Fail | 0.18729 | 1.11 | 1.1237 | 0.051373 | 0.1606
L:46500 TOMBAL__ - 45971 KYUDAL74 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A |  | 1710 | PASS | 0.2026 | 1.1171 | 1.0941 | 0.057131 | 0.13391
L:45972 KUYDAL75 - 40900 KING___345 C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A |  | 1710 | PASS | 0.2768 | 1.1287 | 1.0528 | 0.080787 | 0.090814