## test results
CRE test for: |  | 3390 JEWETT_S 345 44645 SNGLTN_3 345 1 | [5 empty] | FAIL
Line Rating: |  | 1005
Direcction |  | North | → | Houston |  | N-H
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3390 JEWETT_S 345 44645 SNGLTN_3 345 1
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.14157
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.037794
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.12566
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.16892
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3390 JEWETT_S 345 44645 SNGLTN_3 345 1
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.13752
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.040139
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.12595
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.17137
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3390 JEWETT_S 345 44645 SNGLTN_3 345 1
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.18171
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.015621
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.31294 | PASS
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.16374
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.13112
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.29703
PTDF tests
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.31294 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.31294 | 0.18171
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.33254
[6 empty] | Concentration |  | 1.0626 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.32323
[6 empty] | Concentration |  | 1.0329 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 385.6644
| Percent of line rating => | [6 empty] | 38.37% | FAIL
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 1.0991
[7 empty] | B1(N-S) | 0.028633 | 0.22835 | 0.19972 | 0.028633
[7 empty] | B2 (N-W) | 0.008963 | 0.026133 | 0.01717 | 0.008963
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B4 (S-W) | -0.019317 | -0.19929 | -0.17997 | -0.019317
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.025584 | 0.11854 | 0.14412 | -0.025584
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0089987 | 0.31747 | 0.32647 | -0.0089987
[7 empty] | test | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B1 | 8.324%
Deployment Error Percent | [6 empty] | B2 | 2.606%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0%
[7 empty] | B4 | -5.616%
[7 empty] | B5 | -7.438%
[7 empty] | B6 | -2.616%
[7 empty] | Max Abs Error | 8.324% | PASS

## Generation_sensitivity
Generator Sensitivities
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: 3390 JEWETT_S 345 44645 SNGLTN_3 345 1 C: GIBN_CREK - SNGLTN_75 (967-44645) & GIBN_CREK - SNGLTN_99 (967-44645) | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: 3390 JEWETT_S 345 44645 SNGLTN_3 345 1 C: GIBN_CREK - SNGLTN_75 (967-44645) & GIBN_CREK - SNGLTN_99 (967-44645)
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.11682 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 29.7881
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.11682 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 17.4056
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.12046 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.8069
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.12046 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.8069
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.11682 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 17.8728
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.11728 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 17.5923
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.11728 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 9.3826
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13264 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 9.6829
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13264 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 15.7845
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13264 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 27.1918
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13264 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 13.5296
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13264 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 12.7337
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.13353 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.6023
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.13353 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.6023
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.13392 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 22.4981
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.13392 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 12.0525
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.1347 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.4247
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.1347 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.4247
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.1347 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 5.1188
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.13593 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 39.1478
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.13593 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 19.9817
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.13593 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 19.9817
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.13737 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 15.454
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.14132 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 5.6528
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14131 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 11.1639
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14131 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 14.9794
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14131 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 20.632
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14131 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 10.7399
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.13855 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 8.3129
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.13855 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 8.7285
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.14142 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 2.8285
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.14142 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 3.5356
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.14142 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 5.7984
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.14382 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 66.5882
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 8.2119
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 8.0874
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.3363
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.3363
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.3363
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12442 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 14.1841
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.12442 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 64.0773
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 8.3742
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.7549
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.7549
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.5011
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.5011
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 8.2473
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12653 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 8.8573
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12653 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 9.2875
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12653 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 8.9079
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 19.0098
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 27.881
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.127 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 12.573
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.127 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 7.747
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.12698 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 17.9043
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.127 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 3.175
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.127 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.8039
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.127 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.8039
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.12698 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 15.2377
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.12594 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 3.2493
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.12572 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 12.6346
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.12632 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 15.1584
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.1257 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 7.2903
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 26.9594
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.12727 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 19.0907
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12509 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.82556
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12509 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 4.2904
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.12727 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 12.8544
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.12635 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 15.1618
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.13324 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 48.7655
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.1326 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 32.0887
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.13008 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 52.0308
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.13008 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 30.6991
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.13084 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 21.5884
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.13517 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 27.5741
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.13517 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 27.1686
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.13517 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 32.7104
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13337 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.6674
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13337 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.6674
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13337 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.6674
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13337 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 2.2673
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.13338 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 16.0054
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.12894 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 7.7366
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.1411 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 10.5823
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.1411 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 11.2314
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.1411 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 12.4731
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 22.5683
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 22.0041
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 27.6462
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 22.0041
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 22.1452
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 27.9283
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.14078 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 23.9321
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.14078 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 73.204
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14098 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 52.1611
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14119 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 78.7857
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14119 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 81.7507
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14119 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 114.0839
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.13718 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 15.3642
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.13718 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 13.718
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.13718 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 51.854
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.1355 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 29.4452
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.1355 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 27.7785
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.1355 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 36.9116
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.13577 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 104.5444
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.13434 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 9.4035
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.13434 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 9.2692
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.13434 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 9.2692
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.13434 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 9.1348
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.13519 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 156.4171
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.13519 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 156.5523
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.13695 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 30.6759
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.13695 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 30.9498
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.13807 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 29.8786
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.13807 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 29.8371
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.13695 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 29.0326
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.13695 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 28.8956
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.13767 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 54.3785
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.13787 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 59.9739
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.13767 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 59.8851
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.1402 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 19.3472
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14061 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 16.5914
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14061 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 16.1696
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14061 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 78.1764
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.14162 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 54.9478
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.14162 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 72.9333
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.14489 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 113.7363
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.14489 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 115.1852
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.14489 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 113.0119
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.14421 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 26.246
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.14421 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 69.7972
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.13962 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 31.2747
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.14551 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 7.2757
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.14542 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 6.1076
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.1551 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 95.3877
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.1551 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 91.0449
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.11667 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 62.6502
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.11667 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 91.8169
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.1128 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 8.4599
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.1128 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 25.0414
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.036384 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 20.7025
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.043073 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -9.0023
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.043073 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -9.3038
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.042851 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -17.4404
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.043073 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.9814
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.043073 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -2.0244
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.043073 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.9814
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.043073 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.9814
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.042929 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -18.2019
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.042929 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -18.2448
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.042896 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -2.488
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.042896 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -3.8177
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.042896 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.8874
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.042896 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.8874
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.042896 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -1.8445
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.042896 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -1.9303
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.042907 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -17.6777
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.042907 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -17.1628
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.045301 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -24.7343
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.045301 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -33.9757
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.043113 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -2.6299
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.043113 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -4.0957
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.043113 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -6.5101
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.044256 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -6.8597
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.044256 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -7.5235
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.044256 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -6.8597
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.074986 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -1.6497
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.074986 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.82485
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.074986 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.82485
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.074216 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -3.5401
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.074216 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -2.7683
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.074216 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -3.4139
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.074216 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -3.5624
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.062922 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.75506
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.062922 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.69214
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.044415 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.066
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.044415 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.066
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.044415 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -1.0215
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.05202 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -20.5999
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.12356 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -164.7001
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.12356 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -164.0824
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.068973 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -2.621
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.068973 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -1.3312
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.068973 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -1.0346
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.068973 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -3.2417
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11755 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 8.8165
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.12788 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 19.1824
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.12465 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 21.1289
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.090961 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 13.6441
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.12693 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 7.9967
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.13148 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 85.4213
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.14062 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.625
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.14062 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.625
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.005582 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 2.3556
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.012005 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -1.5847
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.012005 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -1.6087
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.012005 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -3.8776
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.01409 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -2.2262
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.01409 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -2.2544
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.01409 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -2.4657
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.033303 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -19.449
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.033303 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -19.8153
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.033454 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -14.4856
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.031703 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -7.0983
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.031703 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -7.1332
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.031703 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -7.1205
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.031703 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -7.1871
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.001614 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.012912
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.001614 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.012912
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.015219 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.27394
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.015219 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.27394
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.015219 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.22828
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.013449 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.18425
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.004171 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.075078
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.004171 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.075078
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000971 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.033985
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000971 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.033014
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000971 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.033985
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.006007 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.1682
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.006007 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.1742
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.12448 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 4.3569
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.12448 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 3.7345
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.029849 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.4925
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.029849 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.4925
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.029849 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.4925
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.029849 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.4925
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.025354 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.15212
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.035885 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.086124
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.035885 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.086124
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.035885 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.10048
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.037448 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.14979
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.038701 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.092882
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.038701 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.092882
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -6.1368
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -5.7611
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -5.8446
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -6.1368
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -7.598
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -8.2659
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.011395 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -1.7377
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.011395 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -1.7036
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.011395 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -2.6505
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.036866 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -5.235
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.036866 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -5.3456
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.036866 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -5.5668
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.036866 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -10.6911
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.000942 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.031086
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.000942 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.02355
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.062922 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.75506
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.074259 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -5.4209
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -6.5684
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -6.7347
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -2.192
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.54799
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -6.5684
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -6.6515
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -6.5185
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -2.0786
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -3.8246
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.065692 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -41.3203
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.072768 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -10.4786
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.072768 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -13.6804
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.048045 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.57654
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.013878 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.083268
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.070856 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -23.8076
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.070518 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -23.553
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.070518 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -23.9761
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.070268 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -2.6702
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.070437 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.7609
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.070437 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.7609
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.070313 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -2.6719
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.069529 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -2.0163
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.070838 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -10.5053
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.070838 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -10.5265
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.070838 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -10.8382
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -11.4416
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -11.0795
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -7.2415
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -10.5002
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -10.645
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -9.1967
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.067638 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -9.909
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.067638 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -10.0037
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.067638 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -11.7014
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.068414 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -14.1617
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.068414 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -14.8253
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.068414 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -16.5562
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.068419 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -9.8523
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.068419 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -9.8523
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.068419 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -11.6996
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.001799 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -0.55769
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.001799 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -0.74299
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.000381 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -0.016002
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.000381 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.016764
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.000381 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.016764
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.000381 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -0.017907
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.19845
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.1863
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.1863
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.19035
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00405 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -0.6237
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00405 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -0.5994
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.1944
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.1944
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.7961
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.7961
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 11.6611
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 10.0526
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 10.0526
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 14.4507
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 26.1597
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 17.8544
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 16.6357
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 17.088
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 18.4701
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 26.3859
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12783 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 26.7163
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12783 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 16.1704
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12783 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 31.8294
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12783 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 25.1823
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 25.3464
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 15.4486
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.12469 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 18.5793
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 22.7749
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 22.7749
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.12646 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 28.4542
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.12738 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 15.9224
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.12738 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 15.9224
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 19.7366
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 19.8776
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 43.5616
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 20.1596
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 20.3005
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 43.7026
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.13893 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 27.2305
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.13893 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 15.4213
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.14044 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 22.9005
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 23.3272
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 23.3272
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 58.8869
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 23.0427
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 22.9005
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 23.185
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 58.1758
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.14146 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.14146 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.14553 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 21.539
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.14553 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 18.9194
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.14553 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 21.1024
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.14553 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 58.0681
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.15359 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 23.1457
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.15359 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 23.1918
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.15359 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 27.2465
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.1533 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 23.2249
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.1533 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 23.3476
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.1533 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 27.2108
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.036384 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 21.1391
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.1476 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 126.1954
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.1476 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 126.1954
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.13723 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 4.3915
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.13495 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 6.4776
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.13495 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 6.2077
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.13716 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 1.6459
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.13716 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 6.995
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.13716 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 2.3317
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.13716 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 3.0175
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.13716 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 3.4289
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.13495 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 14.1696
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.12716 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 10.6818
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.11743 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 9.3943
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.11736 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 17.6047
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.11736 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 17.6047
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16705 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -11.827
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16705 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -11.1421
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16705 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -8.8535
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -25.5918
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -25.6419
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -25.4414
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -16.0366
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -40.7597
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.16705 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -6.6819
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.16702 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -16.7522
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.16702 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -15.5163
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.16702 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -17.1531
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.16702 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -17.0361
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.16702 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -5.3447
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.16702 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -5.0107
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.14969 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -16.615
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.14969 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -16.615
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.14969 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -17.8125
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.14969 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -16.3905
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.1476 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 22.479
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.1476 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 22.5823
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.17759 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -24.1525
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.16126 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -5.3217
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.17764 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -7.461
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.17764 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -7.461
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.17764 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -6.7505
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.17764 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -6.7505
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.14687 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -10.4277
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.14687 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -1.4687
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.16027 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -26.1247
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.16027 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -26.1247
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.16027 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -39.2671
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.17365 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -11.2873
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.17365 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -10.4191
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.17365 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -11.2873
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.17365 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -11.2873
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.17622 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -26.2563
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.17622 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -11.4717
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -15.732
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -15.1442
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -15.0405
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -9.4219
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -2.1091
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.18086 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -134.3775
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.17955 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -131.9722
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.18125 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -31.175
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.18125 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -31.175
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.18125 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -31.175
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18849 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -32.6089
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.17785 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -30.7682
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.17785 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -24.0099
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.18217 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -29.6576
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.18217 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -29.4026
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.18217 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -28.9471
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.18217 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -49.0407
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -11.2833
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -11.1423
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -14.5625
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -12.9758
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -28.6375
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -27.5671
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -27.6373
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -27.5496
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -47.2028
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.18079 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.90396
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.18079 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -3.7966
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.23939 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -36.9141
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.23939 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -37.345
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.23939 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -37.345
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.23939 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -90.9686
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.1825 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -72.6354
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -8.0417
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -8.0417
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -8.0417
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -9.6151
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -9.6151
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -9.4403
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.16117 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 133.2876
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.16117 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 131.9982
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.15976 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -7.3649
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -9.4471
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -9.4471
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -13.0519
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -9.1985
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -9.1985
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -12.679
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.17633 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -31.739
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.17633 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -27.9656
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.17633 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -27.6835
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.17581 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -6.1532
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.17091 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -78.4454
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -11.7522
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -11.933
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -12.6562
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -11.3906
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -11.2098
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -18.8035
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -10.6674
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18849 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -29.4046
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18849 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -29.0276
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18849 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -29.0276
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.18849 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -30.5355
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.1811 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -28.433
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.17681 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -12.5537
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.17681 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -12.7305
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.17681 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -6.8957
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.17681 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -5.3044
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.17509 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -13.6567
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.17509 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -14.0069
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -2.856
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.1762 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -29.0723
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.17617 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -29.7726
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.17629 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -37.5491
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.17631 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -40.1998
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.17615 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -2.1138
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.17615 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -3.1707
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.16925 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -8.4623
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -18.6266
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -18.6266
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -9.6715
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -9.4924
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -9.6715
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -10.2088
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -9.6715
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -9.6715
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -10.3879
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -10.3879
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.1803 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -2.1635
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -10.2517
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -10.8009
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -10.2517
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -10.2517
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -10.8009
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -10.2517
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.1287 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -8.4941
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.16182 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -26.0525
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.16182 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -26.8616
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.16182 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -40.1306
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.16182 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -88.3521
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.16182 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -104.0483
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.16019 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -104.283
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.16019 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -90.3466
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.16019 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -96.1134
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.16182 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -2.1036
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.18082 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -2.1699
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -6.1156
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -6.2416
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -5.8818
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -8.2561
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -3.1837
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -3.6694
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -3.5795
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -6.2955
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -3.2377
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -15.3611
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -26.6211
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -8.8865
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -10.2338
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -6.4499
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -14.4764
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -12.3265
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -12.6131
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -7.1665
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -2.58
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -13.4731
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -10.0332
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -9.0299
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -10.3198
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -9.2878
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -14.4764
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -13.9031
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -14.7631
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -10.8932
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -11.4665
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -11.4665
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -24.5096
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.35887
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.11443 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 8.7541
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11755 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 9.4043
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.11755 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 4.7022
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.11806 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 9.4446
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.11744 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 9.3955
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.11485 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 9.1881
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.114 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 9.5763
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.11806 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 9.4446
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -3.8279
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12648 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 15.177
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12648 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 29.4687
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12648 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 21.526
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -7.4543
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -6.1784
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -7.5215
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -3.8615
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -3.3578
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.1288 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 7.7278
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.031239 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.10048 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.11992 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.57561
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 4.7901
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 13.7315
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 17.2442
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 15.2005
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 13.4122
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 10.2827
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.12572 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 18.8574
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 14.1144
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 18.7564
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 23.3357
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 26.9114
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.068973 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.017325 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.051649 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -2.328
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -3.6251
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -6.1527
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.5032
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -2.8365
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -2.629
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -1.3145
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.5032
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -2.4906
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -2.9749
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -1.522
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -3.0531
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.1743
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.54799
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.1743
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -3.0531
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -3.0531
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -10.2391
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.4592
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -3.8051
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.4592
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072415 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.86898
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.0768 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -1.152
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.0768 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -1.7664
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.082016 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -3.9368
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.077701 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.62161
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.070808 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -12.7454
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.070856 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -12.7541
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.070518 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -12.6932
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.070518 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -12.6932
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.051644 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -5.1644
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.051644 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -5.1644
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.7948
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.7948
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.7948
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -1.1486
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.7948
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.7948
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.7948
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -1.0769
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.051644 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.051644 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -25.822
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.051644 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -25.822
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.051644 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.062156 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.000942 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.058409 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.065456 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L: 3390 JEWETT_S 345 44645 SNGLTN_3 345 1 C: GIBN_CREK - SNGLTN_75 (967-44645) & GIBN_CREK - SNGLTN_99 (967-44645) | [7 empty] | 385.6644
Number of Bus | Name of Bus | ID | Max MW | L: 3390 JEWETT_S 345 44645 SNGLTN_3 345 1 C: GIBN_CREK - SNGLTN_75 (967-44645) & GIBN_CREK - SNGLTN_99 (967-44645) | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.11682 | north | -0.024753 | 0.15461 | -0.0088406 | 0.28573 | 0.0088406 | west | Y | 0.024753 | 4.0578
239 | BOSQUESW | 1 | 149 | 0.11682 | north | -0.024753 | 0.15461 | -0.0088406 | 0.28573 | 0.0088406 | west | Y | 0.024753 | 2.371
244 | WHITNYDM | 1 | 15 | 0.12046 | north | -0.021111 | 0.15825 | -0.0051986 | 0.28937 | 0.0051986 | west | Y | 0.021111 | 0.23869
245 | WHITNYDM | 2 | 15 | 0.12046 | north | -0.021111 | 0.15825 | -0.0051986 | 0.28937 | 0.0051986 | west | Y | 0.021111 | 0.23869
247 | BOSQUESW | 2 | 153 | 0.11682 | north | -0.024753 | 0.15461 | -0.0088406 | 0.28573 | 0.0088406 | west | Y | 0.024753 | 2.4347
251 | BOSQUESW | 2 | 150 | 0.11728 | north | -0.024287 | 0.15508 | -0.0083746 | 0.2862 | 0.0083746 | west | Y | 0.024287 | 2.3869
253 | BOSQUESW | 2 | 80 | 0.11728 | north | -0.024287 | 0.15508 | -0.0083746 | 0.2862 | 0.0083746 | west | Y | 0.024287 | 1.273
332 | RWMILLER | 1 | 73 | 0.13264 | north | -0.0089264 | 0.17044 | 0.0069864 | 0.30156 | 0.0069864 | west | Y | 0.0089264 | 0.14162
333 | RWMILLER | 2 | 119 | 0.13264 | north | -0.0089264 | 0.17044 | 0.0069864 | 0.30156 | 0.0069864 | west | Y | 0.0089264 | 0.23086
334 | RWMILLER | 3 | 205 | 0.13264 | north | -0.0089264 | 0.17044 | 0.0069864 | 0.30156 | 0.0069864 | west | Y | 0.0089264 | 0.39769
335 | RWMILLER | 4 | 102 | 0.13264 | north | -0.0089264 | 0.17044 | 0.0069864 | 0.30156 | 0.0069864 | west | Y | 0.0089264 | 0.19788
336 | RWMILLER | 5 | 96 | 0.13264 | north | -0.0089264 | 0.17044 | 0.0069864 | 0.30156 | 0.0069864 | west | Y | 0.0089264 | 0.18624
344 | MRSSHPRD | 1 | 12 | 0.13353 | north | -0.0080444 | 0.17132 | 0.0078684 | 0.30244 | 0.0078684 | west | Y | 0.0080444 | 0.0021116
345 | MRSSHPRD | 2 | 12 | 0.13353 | north | -0.0080444 | 0.17132 | 0.0078684 | 0.30244 | 0.0078684 | west | Y | 0.0080444 | 0.0021116
366 | JNSNCNTY | 1 | 168 | 0.13392 | north | -0.0076524 | 0.17171 | 0.0082604 | 0.30283 | 0.0076524 | North | N | 0.0076524 | 0
367 | JNSNCNTY | 2 | 90 | 0.13392 | north | -0.0076524 | 0.17171 | 0.0082604 | 0.30283 | 0.0076524 | North | N | 0.0076524 | 0
503 | NTHTEXAS | 1 | 18 | 0.1347 | north | -0.0068644 | 0.1725 | 0.0090484 | 0.30362 | 0.0068644 | North | N | 0.0068644 | 0
504 | NTHTEXAS | 2 | 18 | 0.1347 | north | -0.0068644 | 0.1725 | 0.0090484 | 0.30362 | 0.0068644 | North | N | 0.0068644 | 0
505 | NTHTEXAS | 3 | 38 | 0.1347 | north | -0.0068644 | 0.1725 | 0.0090484 | 0.30362 | 0.0068644 | North | N | 0.0068644 | 0
580 | JCKCNTY8 | 1 | 288 | 0.13593 | north | -0.0056394 | 0.17372 | 0.010273 | 0.30485 | 0.0056394 | North | N | 0.0056394 | 0
581 | JCKCNTY8 | 2 | 147 | 0.13593 | north | -0.0056394 | 0.17372 | 0.010273 | 0.30485 | 0.0056394 | North | N | 0.0056394 | 0
582 | JCKCNTY8 | 3 | 147 | 0.13593 | north | -0.0056394 | 0.17372 | 0.010273 | 0.30485 | 0.0056394 | North | N | 0.0056394 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.13737 | north | -0.0042004 | 0.17516 | 0.011712 | 0.30629 | 0.0042004 | North | N | 0.0042004 | 0
837 | NEWMAN_G | 1 | 40 | 0.14132 | north | -0.00024838 | 0.17911 | 0.015664 | 0.31024 | 0.00024838 | North | N | 0.00024838 | 0
842 | OLINGER_ | 1 | 79 | 0.14131 | north | -0.00025438 | 0.17911 | 0.015658 | 0.31023 | 0.00025438 | North | N | 0.00025438 | 0
843 | OLINGER_ | 1 | 106 | 0.14131 | north | -0.00025438 | 0.17911 | 0.015658 | 0.31023 | 0.00025438 | North | N | 0.00025438 | 0
844 | OLINGER_ | 1 | 146 | 0.14131 | north | -0.00025438 | 0.17911 | 0.015658 | 0.31023 | 0.00025438 | North | N | 0.00025438 | 0
845 | OLINGER_ | 1 | 76 | 0.14131 | north | -0.00025438 | 0.17911 | 0.015658 | 0.31023 | 0.00025438 | North | N | 0.00025438 | 0
923 | SPENCER_ | 1 | 60 | 0.13855 | north | -0.0030214 | 0.17634 | 0.012891 | 0.30746 | 0.0030214 | North | N | 0.0030214 | 0
924 | SPENCER_ | 1 | 63 | 0.13855 | north | -0.0030214 | 0.17634 | 0.012891 | 0.30746 | 0.0030214 | North | N | 0.0030214 | 0
948 | STEAM1 | 1 | 20 | 0.14142 | north | -0.00014438 | 0.17922 | 0.015768 | 0.31034 | 0.00014438 | North | N | 0.00014438 | 0
949 | STEAM2 | 1 | 25 | 0.14142 | north | -0.00014438 | 0.17922 | 0.015768 | 0.31034 | 0.00014438 | North | N | 0.00014438 | 0
950 | STEAM3 | 1 | 41 | 0.14142 | north | -0.00014438 | 0.17922 | 0.015768 | 0.31034 | 0.00014438 | North | N | 0.00014438 | 0
990 | GIBN_CRE | 1 | 463 | 0.14382 | north | 0.0022496 | 0.18161 | 0.018162 | 0.31274 | 0.0022496 | North | N | 0.0022496 | 0
1002 | PBCTAGE_ | A | 66 | 0.12442 | west | -0.017147 | 0.16222 | -0.0012346 | 0.29334 | 0.0012346 | west | N | 0.0012346 | 0
1003 | PBCTBGE_ | B | 65 | 0.12442 | west | -0.017147 | 0.16222 | -0.0012346 | 0.29334 | 0.0012346 | west | N | 0.0012346 | 0
1004 | PBCTCGE_ | C | 67 | 0.12442 | west | -0.017147 | 0.16222 | -0.0012346 | 0.29334 | 0.0012346 | west | N | 0.0012346 | 0
1005 | PBCTDGE_ | D | 67 | 0.12442 | west | -0.017147 | 0.16222 | -0.0012346 | 0.29334 | 0.0012346 | west | N | 0.0012346 | 0
1006 | PBCTEGE_ | E | 67 | 0.12442 | west | -0.017147 | 0.16222 | -0.0012346 | 0.29334 | 0.0012346 | west | N | 0.0012346 | 0
1007 | PB5GEN_6 | MB | 114 | 0.12442 | west | -0.017147 | 0.16222 | -0.0012346 | 0.29334 | 0.0012346 | west | N | 0.0012346 | 0
1008 | PB6GEN_7 | MB | 515 | 0.12442 | west | -0.017147 | 0.16222 | -0.0012346 | 0.29334 | 0.0012346 | west | N | 0.0012346 | 0
1039 | MRGNAG_1 | A | 66 | 0.12688 | west | -0.014687 | 0.16468 | 0.0012254 | 0.2958 | 0.0012254 | west | N | 0.0012254 | 0
1040 | MRGNBG_2 | B | 69 | 0.12688 | west | -0.014687 | 0.16468 | 0.0012254 | 0.2958 | 0.0012254 | west | N | 0.0012254 | 0
1041 | MRGNCG_3 | C | 69 | 0.12688 | west | -0.014687 | 0.16468 | 0.0012254 | 0.2958 | 0.0012254 | west | N | 0.0012254 | 0
1042 | MRGNDG_4 | D | 67 | 0.12688 | west | -0.014687 | 0.16468 | 0.0012254 | 0.2958 | 0.0012254 | west | N | 0.0012254 | 0
1043 | MRGNEG_5 | E | 67 | 0.12688 | west | -0.014687 | 0.16468 | 0.0012254 | 0.2958 | 0.0012254 | west | N | 0.0012254 | 0
1044 | MRGNFG_6 | F | 65 | 0.12688 | west | -0.014687 | 0.16468 | 0.0012254 | 0.2958 | 0.0012254 | west | N | 0.0012254 | 0
1045 | CALENG1G | 1 | 70 | 0.12653 | west | -0.015036 | 0.16433 | 0.00087641 | 0.29545 | 0.00087641 | west | N | 0.00087641 | 0
1046 | CALENG2G | 2 | 73.4 | 0.12653 | west | -0.015036 | 0.16433 | 0.00087641 | 0.29545 | 0.00087641 | west | N | 0.00087641 | 0
1047 | CALENG3G | 3 | 70.4 | 0.12653 | west | -0.015036 | 0.16433 | 0.00087641 | 0.29545 | 0.00087641 | west | N | 0.00087641 | 0
1058 | LONGSHOR | 1 | 150 | 0.12673 | west | -0.014837 | 0.16453 | 0.0010754 | 0.29565 | 0.0010754 | west | N | 0.0010754 | 0
1058 | LONGSHOR | 2 | 220 | 0.12673 | west | -0.014837 | 0.16453 | 0.0010754 | 0.29565 | 0.0010754 | west | N | 0.0010754 | 0
1061 | CIELOGEN | 1 | 99 | 0.127 | west | -0.014569 | 0.16479 | 0.0013434 | 0.29592 | 0.0013434 | west | N | 0.0013434 | 0
1062 | CIELOGEN | 1 | 61 | 0.127 | west | -0.014569 | 0.16479 | 0.0013434 | 0.29592 | 0.0013434 | west | N | 0.0013434 | 0
1068 | SCURRYCW | 1 | 141 | 0.12698 | west | -0.014588 | 0.16477 | 0.0013244 | 0.2959 | 0.0013244 | west | N | 0.0013244 | 0
1069 | KINDERMG | 1 | 25 | 0.127 | west | -0.014569 | 0.16479 | 0.0013434 | 0.29592 | 0.0013434 | west | N | 0.0013434 | 0
1070 | KINDERMG | 1 | 45.7 | 0.127 | west | -0.014569 | 0.16479 | 0.0013434 | 0.29592 | 0.0013434 | west | N | 0.0013434 | 0
1071 | KINDERMG | 1 | 45.7 | 0.127 | west | -0.014569 | 0.16479 | 0.0013434 | 0.29592 | 0.0013434 | west | N | 0.0013434 | 0
1073 | SCURRYCW | 2 | 120 | 0.12698 | west | -0.014588 | 0.16477 | 0.0013244 | 0.2959 | 0.0013244 | west | N | 0.0013244 | 0
1320 | BSP 1 | 1 | 25.8 | 0.12594 | west | -0.015627 | 0.16374 | 0.00028541 | 0.29486 | 0.00028541 | west | N | 0.00028541 | 0
1326 | STANTONW | 1 | 100.5 | 0.12572 | west | -0.015852 | 0.16351 | 6.0414e-05 | 0.29463 | 6.0414e-05 | west | N | 6.0414e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.12632 | west | -0.015249 | 0.16411 | 0.00066341 | 0.29524 | 0.00066341 | west | N | 0.00066341 | 0
1328 | OCOTILLO | 1 | 58 | 0.1257 | west | -0.015874 | 0.16349 | 3.8414e-05 | 0.29461 | 3.8414e-05 | west | N | 3.8414e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.12586 | west | -0.015708 | 0.16365 | 0.00020441 | 0.29478 | 0.00020441 | west | N | 0.00020441 | 0
1343 | TRENTIPP | 1 | 150 | 0.12727 | west | -0.014298 | 0.16506 | 0.0016144 | 0.29619 | 0.0016144 | west | N | 0.0016144 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.12509 | west | -0.016484 | 0.16288 | -0.00057159 | 0.294 | 0.00057159 | west | N | 0.00057159 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.12509 | west | -0.016484 | 0.16288 | -0.00057159 | 0.294 | 0.00057159 | west | N | 0.00057159 | 0
1354 | AEPWIND_ | 1 | 101 | 0.12727 | west | -0.014298 | 0.16506 | 0.0016144 | 0.29619 | 0.0016144 | west | N | 0.0016144 | 0
1360 | GUNSIGHT | 1 | 120 | 0.12635 | west | -0.015221 | 0.16414 | 0.00069141 | 0.29526 | 0.00069141 | west | N | 0.00069141 | 0
1432 | GRHAMSES | 2 | 366 | 0.13324 | north | -0.0083304 | 0.17103 | 0.0075824 | 0.30216 | 0.0075824 | west | Y | 0.0083304 | 0.27376
1433 | GRHAMSES | 1 | 242 | 0.1326 | north | -0.0089714 | 0.17039 | 0.0069414 | 0.30151 | 0.0069414 | west | Y | 0.0089714 | 0.49125
1437 | MESQUITW | 1 | 400 | 0.13008 | west | -0.011492 | 0.16787 | 0.0044204 | 0.29899 | 0.0044204 | west | N | 0.0044204 | 0
1438 | MESQUITW | 1 | 236 | 0.13008 | west | -0.011488 | 0.16787 | 0.0044244 | 0.299 | 0.0044244 | west | N | 0.0044244 | 0
1442 | COKFIELD | 1 | 165 | 0.13084 | west | -0.01073 | 0.16863 | 0.0051824 | 0.29976 | 0.0051824 | west | N | 0.0051824 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.13517 | north | -0.0064024 | 0.17296 | 0.0095104 | 0.30408 | 0.0064024 | North | N | 0.0064024 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.13517 | north | -0.0064024 | 0.17296 | 0.0095104 | 0.30408 | 0.0064024 | North | N | 0.0064024 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.13517 | north | -0.0064024 | 0.17296 | 0.0095104 | 0.30408 | 0.0064024 | North | N | 0.0064024 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.13337 | west | -0.0082004 | 0.17116 | 0.0077124 | 0.30229 | 0.0077124 | west | N | 0.0077124 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.13337 | west | -0.0082004 | 0.17116 | 0.0077124 | 0.30229 | 0.0077124 | west | N | 0.0077124 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.13337 | west | -0.0082004 | 0.17116 | 0.0077124 | 0.30229 | 0.0077124 | west | N | 0.0077124 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.13337 | west | -0.0082004 | 0.17116 | 0.0077124 | 0.30229 | 0.0077124 | west | N | 0.0077124 | 0
1600 | BARTNWND | 1 | 120 | 0.13338 | north | -0.0081914 | 0.17117 | 0.0077214 | 0.30229 | 0.0077214 | west | Y | 0.0081914 | 0.056396
1643 | SLSTR1PP | 1 | 60 | 0.12894 | north | -0.012625 | 0.16674 | 0.0032874 | 0.29786 | 0.0032874 | west | Y | 0.012625 | 0.56028
1675 | PEC_1G | 1 | 75 | 0.1411 | north | -0.00047138 | 0.17889 | 0.015441 | 0.31001 | 0.00047138 | North | N | 0.00047138 | 0
1676 | PEC_2G | 2 | 79.6 | 0.1411 | north | -0.00047138 | 0.17889 | 0.015441 | 0.31001 | 0.00047138 | North | N | 0.00047138 | 0
1677 | PEC_3G | 3 | 88.4 | 0.1411 | north | -0.00047138 | 0.17889 | 0.015441 | 0.31001 | 0.00047138 | North | N | 0.00047138 | 0
1678 | LAMARPWR | 1 | 160 | 0.14105 | north | -0.00051738 | 0.17885 | 0.015395 | 0.30997 | 0.00051738 | North | N | 0.00051738 | 0
1679 | LAMARPWR | 2 | 156 | 0.14105 | north | -0.00051738 | 0.17885 | 0.015395 | 0.30997 | 0.00051738 | North | N | 0.00051738 | 0
1680 | LAMARPWR | 3 | 196 | 0.14105 | north | -0.00051738 | 0.17885 | 0.015395 | 0.30997 | 0.00051738 | North | N | 0.00051738 | 0
1681 | LAMARPWR | 4 | 156 | 0.14105 | north | -0.00051738 | 0.17885 | 0.015395 | 0.30997 | 0.00051738 | North | N | 0.00051738 | 0
1682 | LAMARPWR | 5 | 157 | 0.14105 | north | -0.00051738 | 0.17885 | 0.015395 | 0.30997 | 0.00051738 | North | N | 0.00051738 | 0
1683 | LAMARPWR | 6 | 198 | 0.14105 | north | -0.00051738 | 0.17885 | 0.015395 | 0.30997 | 0.00051738 | North | N | 0.00051738 | 0
1687 | VALLEY_1 | 1 | 170 | 0.14078 | north | -0.00079238 | 0.17857 | 0.01512 | 0.30969 | 0.00079238 | North | N | 0.00079238 | 0
1688 | VALLEY_2 | 2 | 520 | 0.14078 | north | -0.00079238 | 0.17857 | 0.01512 | 0.30969 | 0.00079238 | North | N | 0.00079238 | 0
1689 | VALLEY_3 | 3 | 370 | 0.14098 | north | -0.00059338 | 0.17877 | 0.015319 | 0.30989 | 0.00059338 | North | N | 0.00059338 | 0
1701 | MOSES_1G | 1 | 558 | 0.14119 | north | -0.00037638 | 0.17899 | 0.015536 | 0.31011 | 0.00037638 | North | N | 0.00037638 | 0
1702 | MOSES_2G | 2 | 579 | 0.14119 | north | -0.00037638 | 0.17899 | 0.015536 | 0.31011 | 0.00037638 | North | N | 0.00037638 | 0
1703 | MOSES_3G | 3 | 808 | 0.14119 | north | -0.00037638 | 0.17899 | 0.015536 | 0.31011 | 0.00037638 | North | N | 0.00037638 | 0
1861 | EAGLEMNT | MB | 112 | 0.13718 | north | -0.0043894 | 0.17497 | 0.011523 | 0.3061 | 0.0043894 | North | N | 0.0043894 | 0
1862 | EAGLEMNT | MB | 100 | 0.13718 | north | -0.0043894 | 0.17497 | 0.011523 | 0.3061 | 0.0043894 | North | N | 0.0043894 | 0
1863 | EAGLEMNT | MB | 378 | 0.13718 | north | -0.0043894 | 0.17497 | 0.011523 | 0.3061 | 0.0043894 | North | N | 0.0043894 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.1355 | north | -0.0060644 | 0.1733 | 0.0098484 | 0.30442 | 0.0060644 | North | N | 0.0060644 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.1355 | north | -0.0060644 | 0.1733 | 0.0098484 | 0.30442 | 0.0060644 | North | N | 0.0060644 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.1355 | north | -0.0060644 | 0.1733 | 0.0098484 | 0.30442 | 0.0060644 | North | N | 0.0060644 | 0
1889 | DECRDOVA | MB | 770 | 0.13577 | north | -0.0057974 | 0.17357 | 0.010115 | 0.30469 | 0.0057974 | North | N | 0.0057974 | 0
1892 | DECRDOVA | A | 70 | 0.13434 | north | -0.0072334 | 0.17213 | 0.0086794 | 0.30325 | 0.0072334 | North | N | 0.0072334 | 0
1893 | DECRDOVA | B | 69 | 0.13434 | north | -0.0072334 | 0.17213 | 0.0086794 | 0.30325 | 0.0072334 | North | N | 0.0072334 | 0
1894 | DECRDOVA | C | 69 | 0.13434 | north | -0.0072334 | 0.17213 | 0.0086794 | 0.30325 | 0.0072334 | North | N | 0.0072334 | 0
1895 | DECRDOVA | D | 68 | 0.13434 | north | -0.0072334 | 0.17213 | 0.0086794 | 0.30325 | 0.0072334 | North | N | 0.0072334 | 0
1898 | COMCHEPK | 1 | 1157 | 0.13519 | north | -0.0063774 | 0.17299 | 0.0095354 | 0.30411 | 0.0063774 | North | N | 0.0063774 | 0
1899 | COMCHEPK | 2 | 1158 | 0.13519 | north | -0.0063774 | 0.17299 | 0.0095354 | 0.30411 | 0.0063774 | North | N | 0.0063774 | 0
1937 | MDLTHELP | 5 | 224 | 0.13695 | north | -0.0046234 | 0.17474 | 0.011289 | 0.30586 | 0.0046234 | North | N | 0.0046234 | 0
1938 | MDLTHELP | 6 | 226 | 0.13695 | north | -0.0046234 | 0.17474 | 0.011289 | 0.30586 | 0.0046234 | North | N | 0.0046234 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.13807 | north | -0.0034984 | 0.17586 | 0.012414 | 0.30699 | 0.0034984 | North | N | 0.0034984 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.13807 | north | -0.0034984 | 0.17586 | 0.012414 | 0.30699 | 0.0034984 | North | N | 0.0034984 | 0
1943 | MDLTHELP | 3 | 212 | 0.13695 | north | -0.0046234 | 0.17474 | 0.011289 | 0.30586 | 0.0046234 | North | N | 0.0046234 | 0
1944 | MDLTHELP | 4 | 211 | 0.13695 | north | -0.0046234 | 0.17474 | 0.011289 | 0.30586 | 0.0046234 | North | N | 0.0046234 | 0
1947 | HANDLEY_ | 3 | 395 | 0.13767 | north | -0.0039024 | 0.17546 | 0.01201 | 0.30658 | 0.0039024 | North | N | 0.0039024 | 0
1948 | HANDLEY_ | 4 | 435 | 0.13787 | north | -0.0036984 | 0.17566 | 0.012214 | 0.30679 | 0.0036984 | North | N | 0.0036984 | 0
1949 | HANDLEY_ | 5 | 435 | 0.13767 | north | -0.0039024 | 0.17546 | 0.01201 | 0.30658 | 0.0039024 | North | N | 0.0039024 | 0
2371 | COLLIN_1 | MB | 138 | 0.1402 | north | -0.0013724 | 0.17799 | 0.01454 | 0.30911 | 0.0013724 | North | N | 0.0013724 | 0
2413 | MTCK6_G | 6 | 118 | 0.14061 | north | -0.00096438 | 0.1784 | 0.014948 | 0.30952 | 0.00096438 | North | N | 0.00096438 | 0
2414 | MTCK7_G | 7 | 115 | 0.14061 | north | -0.00096438 | 0.1784 | 0.014948 | 0.30952 | 0.00096438 | North | N | 0.00096438 | 0
2417 | MTCK8_G | 8 | 556 | 0.14061 | north | -0.00096438 | 0.1784 | 0.014948 | 0.30952 | 0.00096438 | North | N | 0.00096438 | 0
2451 | LKHB1_G | 1 | 388 | 0.14162 | north | 4.862e-05 | 0.17941 | 0.015961 | 0.31053 | 4.862e-05 | North | N | 4.862e-05 | 0
2452 | LKHB2_G | 2 | 515 | 0.14162 | north | 4.862e-05 | 0.17941 | 0.015961 | 0.31053 | 4.862e-05 | North | N | 4.862e-05 | 0
3097 | MARTLAKE | 1 | 785 | 0.14489 | north | 0.0033176 | 0.18268 | 0.01923 | 0.3138 | 0.0033176 | North | N | 0.0033176 | 0
3098 | MARTLAKE | 2 | 795 | 0.14489 | north | 0.0033176 | 0.18268 | 0.01923 | 0.3138 | 0.0033176 | North | N | 0.0033176 | 0
3099 | MARTLAKE | 3 | 780 | 0.14489 | north | 0.0033176 | 0.18268 | 0.01923 | 0.3138 | 0.0033176 | North | N | 0.0033176 | 0
3107 | STRYKER_ | 1 | 182 | 0.14421 | north | 0.0026396 | 0.182 | 0.018552 | 0.31313 | 0.0026396 | North | N | 0.0026396 | 0
3108 | STRYKER_ | 2 | 484 | 0.14421 | north | 0.0026396 | 0.182 | 0.018552 | 0.31313 | 0.0026396 | North | N | 0.0026396 | 0
3126 | TRINIDAD | 1 | 224 | 0.13962 | north | -0.0019504 | 0.17741 | 0.013962 | 0.30854 | 0.0019504 | North | N | 0.0019504 | 0
3309 | ASPN_G | 1 | 50 | 0.14551 | north | 0.0039446 | 0.18331 | 0.019857 | 0.31443 | 0.0039446 | North | N | 0.0039446 | 0
3348 | CHAMPION | MB | 42 | 0.14542 | north | 0.0038506 | 0.18321 | 0.019763 | 0.31434 | 0.0038506 | North | N | 0.0038506 | 0
3381 | BBRN_1G | 1 | 615 | 0.1551 | north | 0.013533 | 0.1929 | 0.029445 | 0.32402 | 0.013533 | North | N | 0.013533 | 0
3382 | BBRN_2G | 2 | 587 | 0.1551 | north | 0.013533 | 0.1929 | 0.029445 | 0.32402 | 0.013533 | North | N | 0.013533 | 0
3403 | THOUSE_1 | MB | 537 | 0.11667 | north | -0.024902 | 0.15446 | -0.0089896 | 0.28558 | 0.0089896 | west | Y | 0.024902 | 8.5452
3404 | THOUSE_2 | 2 | 787 | 0.11667 | north | -0.024902 | 0.15446 | -0.0089896 | 0.28558 | 0.0089896 | west | Y | 0.024902 | 12.5234
3416 | LAKE_CRK | MB | 75 | 0.1128 | north | -0.02877 | 0.15059 | -0.012858 | 0.28172 | 0.012858 | west | Y | 0.02877 | 1.1935
3417 | LAKE_CRK | MB | 222 | 0.1128 | north | -0.02877 | 0.15059 | -0.012858 | 0.28172 | 0.012858 | west | Y | 0.02877 | 3.5326
3432 | SANDOW_4 | 4 | 569 | 0.036384 | south | -0.10519 | 0.074178 | -0.089273 | 0.2053 | 0.074178 | south | N | 0.074178 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.043073 | south | -0.18464 | -0.0052794 | -0.16873 | 0.12584 | 0.0052794 | south | N | 0.0052794 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.043073 | south | -0.18464 | -0.0052794 | -0.16873 | 0.12584 | 0.0052794 | south | N | 0.0052794 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.042851 | south | -0.18442 | -0.0050574 | -0.16851 | 0.12607 | 0.0050574 | south | N | 0.0050574 | 0
5031 | BRA_VHBC | 1 | 46 | -0.043073 | south | -0.18464 | -0.0052794 | -0.16873 | 0.12584 | 0.0052794 | south | N | 0.0052794 | 0
5032 | BRA_VHBC | 2 | 47 | -0.043073 | south | -0.18464 | -0.0052794 | -0.16873 | 0.12584 | 0.0052794 | south | N | 0.0052794 | 0
5033 | BRA_VHBC | 3 | 46 | -0.043073 | south | -0.18464 | -0.0052794 | -0.16873 | 0.12584 | 0.0052794 | south | N | 0.0052794 | 0
5034 | BRA_VHBC | 4 | 46 | -0.043073 | south | -0.18464 | -0.0052794 | -0.16873 | 0.12584 | 0.0052794 | south | N | 0.0052794 | 0
5111 | CALAVER_ | 1 | 424 | -0.042929 | south | -0.1845 | -0.0051354 | -0.16859 | 0.12599 | 0.0051354 | south | N | 0.0051354 | 0
5112 | CALAVER_ | 2 | 425 | -0.042929 | south | -0.1845 | -0.0051354 | -0.16859 | 0.12599 | 0.0051354 | south | N | 0.0051354 | 0
5264 | LEON_LCP | 3 | 58 | -0.042896 | south | -0.18447 | -0.0051024 | -0.16855 | 0.12602 | 0.0051024 | south | N | 0.0051024 | 0
5265 | LEON_LCP | 4 | 89 | -0.042896 | south | -0.18447 | -0.0051024 | -0.16855 | 0.12602 | 0.0051024 | south | N | 0.0051024 | 0
5266 | LEON_LCP | 1 | 44 | -0.042896 | south | -0.18447 | -0.0051024 | -0.16855 | 0.12602 | 0.0051024 | south | N | 0.0051024 | 0
5267 | LEON_LCP | 2 | 44 | -0.042896 | south | -0.18447 | -0.0051024 | -0.16855 | 0.12602 | 0.0051024 | south | N | 0.0051024 | 0
5268 | LEON_LCP | 3 | 43 | -0.042896 | south | -0.18447 | -0.0051024 | -0.16855 | 0.12602 | 0.0051024 | south | N | 0.0051024 | 0
5269 | LEON_LCP | 4 | 45 | -0.042896 | south | -0.18447 | -0.0051024 | -0.16855 | 0.12602 | 0.0051024 | south | N | 0.0051024 | 0
5396 | CALAVER_ | 1 | 412 | -0.042907 | south | -0.18448 | -0.0051134 | -0.16856 | 0.12601 | 0.0051134 | south | N | 0.0051134 | 0
5397 | CALAVER_ | 2 | 400 | -0.042907 | south | -0.18448 | -0.0051134 | -0.16856 | 0.12601 | 0.0051134 | south | N | 0.0051134 | 0
5401 | CALAVER_ | 1 | 546 | -0.045301 | south | -0.18687 | -0.0075074 | -0.17096 | 0.12362 | 0.0075074 | south | N | 0.0075074 | 0
5402 | CALAVER_ | 2 | 750 | -0.045301 | south | -0.18687 | -0.0075074 | -0.17096 | 0.12362 | 0.0075074 | south | N | 0.0075074 | 0
5436 | TUTTL_WB | MB | 61 | -0.043113 | south | -0.18468 | -0.0053194 | -0.16877 | 0.1258 | 0.0053194 | south | N | 0.0053194 | 0
5438 | TUTTL_WB | MB | 95 | -0.043113 | south | -0.18468 | -0.0053194 | -0.16877 | 0.1258 | 0.0053194 | south | N | 0.0053194 | 0
5439 | TUTTL_WB | MB | 151 | -0.043113 | south | -0.18468 | -0.0053194 | -0.16877 | 0.1258 | 0.0053194 | south | N | 0.0053194 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.044256 | south | -0.18583 | -0.0064624 | -0.16991 | 0.12466 | 0.0064624 | south | N | 0.0064624 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.044256 | south | -0.18583 | -0.0064624 | -0.16991 | 0.12466 | 0.0064624 | south | N | 0.0064624 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.044256 | south | -0.18583 | -0.0064624 | -0.16991 | 0.12466 | 0.0064624 | south | N | 0.0064624 | 0
5503 | RAYBURNG | 1 | 22 | -0.074986 | south | -0.21656 | -0.037192 | -0.20064 | 0.093931 | 0.037192 | south | N | 0.037192 | 0
5505 | RAYBURNG | 1 | 11 | -0.074986 | south | -0.21656 | -0.037192 | -0.20064 | 0.093931 | 0.037192 | south | N | 0.037192 | 0
5506 | RAYBURNG | 1 | 11 | -0.074986 | south | -0.21656 | -0.037192 | -0.20064 | 0.093931 | 0.037192 | south | N | 0.037192 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.074216 | south | -0.21579 | -0.036422 | -0.19987 | 0.094701 | 0.036422 | south | N | 0.036422 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.074216 | south | -0.21579 | -0.036422 | -0.19987 | 0.094701 | 0.036422 | south | N | 0.036422 | 0
5511 | RAYBURNC | 1 | 46 | -0.074216 | south | -0.21579 | -0.036422 | -0.19987 | 0.094701 | 0.036422 | south | N | 0.036422 | 0
5512 | RAYBURNC | 1 | 48 | -0.074216 | south | -0.21579 | -0.036422 | -0.19987 | 0.094701 | 0.036422 | south | N | 0.036422 | 0
5728 | FALCONHY | 2 | 12 | -0.062922 | south | -0.20449 | -0.025128 | -0.18858 | 0.10599 | 0.025128 | south | N | 0.025128 | 0
5729 | FALCONHY | 3 | 11 | -0.062922 | south | -0.20449 | -0.025128 | -0.18858 | 0.10599 | 0.025128 | south | N | 0.025128 | 0
5890 | PEARSALL | 1 | 24 | -0.044415 | south | -0.18598 | -0.0066214 | -0.17007 | 0.1245 | 0.0066214 | south | N | 0.0066214 | 0
5891 | PEARSALL | 1 | 24 | -0.044415 | south | -0.18598 | -0.0066214 | -0.17007 | 0.1245 | 0.0066214 | south | N | 0.0066214 | 0
5892 | PEARSALL | 1 | 23 | -0.044415 | south | -0.18598 | -0.0066214 | -0.17007 | 0.1245 | 0.0066214 | south | N | 0.0066214 | 0
5903 | SANMIGUE | 1 | 396 | -0.05202 | south | -0.19359 | -0.014226 | -0.17768 | 0.1169 | 0.014226 | south | N | 0.014226 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.12356 | houston | -0.26513 | -0.085762 | -0.24921 | 0.045361 | 0.045361 | houston | N | 0.045361 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.12356 | houston | -0.26513 | -0.085762 | -0.24921 | 0.045361 | 0.045361 | houston | N | 0.045361 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | -0.14157 | 0.037794 | -0.12566 | 0.16892 | 0.037794 | south | Y | 0.14157 | 62.2655
5932 | SI_RAY9 | 9 | 38 | -0.068973 | south | -0.21054 | -0.031179 | -0.19463 | 0.099944 | 0.031179 | south | N | 0.031179 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.068973 | south | -0.21054 | -0.031179 | -0.19463 | 0.099944 | 0.031179 | south | N | 0.031179 | 0
5934 | SI_RAY5 | 5 | 15 | -0.068973 | south | -0.21054 | -0.031179 | -0.19463 | 0.099944 | 0.031179 | south | N | 0.031179 | 0
5935 | SI_RAY10 | 10 | 47 | -0.068973 | south | -0.21054 | -0.031179 | -0.19463 | 0.099944 | 0.031179 | south | N | 0.031179 | 0
6016 | SWMESA | 1 | 75 | 0.11755 | west | -0.024015 | 0.15535 | -0.0081026 | 0.28647 | 0.0081026 | west | N | 0.0081026 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | -0.14157 | 0.037794 | -0.12566 | 0.16892 | 0.037794 | south | Y | 0.12566 | 19.3299
6144 | MCADOO1A | 1 | 150 | 0.12788 | west | -0.013686 | 0.16568 | 0.0022264 | 0.2968 | 0.0022264 | west | N | 0.0022264 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.12465 | west | -0.016915 | 0.16245 | -0.0010026 | 0.29357 | 0.0010026 | west | N | 0.0010026 | 0
6476 | LANGFORD | 1 | 150 | 0.090961 | west | -0.050608 | 0.12875 | -0.034696 | 0.25988 | 0.034696 | west | N | 0.034696 | 0
6637 | SNYDERW1 | 1 | 63 | 0.12693 | west | -0.014638 | 0.16472 | 0.0012744 | 0.29585 | 0.0012744 | west | N | 0.0012744 | 0
6752 | OKLA0A | 1 | 649.7 | 0.13148 | west | -0.010091 | 0.16927 | 0.0058214 | 0.30039 | 0.0058214 | west | N | 0.0058214 | 0
6948 | DENISNDM | 1 | 40 | 0.14062 | north | -0.00094538 | 0.17842 | 0.014967 | 0.30954 | 0.00094538 | North | N | 0.00094538 | 0
6948 | DENISNDM | 2 | 40 | 0.14062 | north | -0.00094538 | 0.17842 | 0.014967 | 0.30954 | 0.00094538 | North | N | 0.00094538 | 0
7000 | L_FERGUS | 1 | 422 | 0.005582 | south | -0.13599 | 0.043376 | -0.12007 | 0.1745 | 0.043376 | south | N | 0.043376 | 0
7004 | L_SIMGID | 1 | 132 | -0.012005 | south | -0.15357 | 0.025789 | -0.13766 | 0.15691 | 0.025789 | south | N | 0.025789 | 0
7005 | L_SIMGID | 2 | 134 | -0.012005 | south | -0.15357 | 0.025789 | -0.13766 | 0.15691 | 0.025789 | south | N | 0.025789 | 0
7006 | L_SIMGID | 3 | 323 | -0.012005 | south | -0.15357 | 0.025789 | -0.13766 | 0.15691 | 0.025789 | south | N | 0.025789 | 0
7007 | L_LOSTPI | 1 | 158 | -0.01409 | south | -0.15566 | 0.023704 | -0.13975 | 0.15483 | 0.023704 | south | N | 0.023704 | 0
7008 | L_LOSTPI | 2 | 160 | -0.01409 | south | -0.15566 | 0.023704 | -0.13975 | 0.15483 | 0.023704 | south | N | 0.023704 | 0
7009 | L_LOSTPI | 3 | 175 | -0.01409 | south | -0.15566 | 0.023704 | -0.13975 | 0.15483 | 0.023704 | south | N | 0.023704 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.033303 | south | -0.17487 | 0.0044906 | -0.15896 | 0.13561 | 0.0044906 | south | N | 0.0044906 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.033303 | south | -0.17487 | 0.0044906 | -0.15896 | 0.13561 | 0.0044906 | south | N | 0.0044906 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.033454 | south | -0.17502 | 0.0043396 | -0.15911 | 0.13546 | 0.0043396 | south | N | 0.0043396 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.031703 | south | -0.17327 | 0.0060906 | -0.15736 | 0.13721 | 0.0060906 | south | N | 0.0060906 | 0
7015 | L_HAYSEN | 2 | 225 | -0.031703 | south | -0.17327 | 0.0060906 | -0.15736 | 0.13721 | 0.0060906 | south | N | 0.0060906 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.031703 | south | -0.17327 | 0.0060906 | -0.15736 | 0.13721 | 0.0060906 | south | N | 0.0060906 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.031703 | south | -0.17327 | 0.0060906 | -0.15736 | 0.13721 | 0.0060906 | south | N | 0.0060906 | 0
7020 | L_AUSTPL | 1 | 8 | -0.001614 | south | -0.14318 | 0.03618 | -0.12727 | 0.1673 | 0.03618 | south | N | 0.03618 | 0
7020 | L_AUSTPL | 2 | 8 | -0.001614 | south | -0.14318 | 0.03618 | -0.12727 | 0.1673 | 0.03618 | south | N | 0.03618 | 0
7022 | L_BUCHAN | 1 | 18 | 0.015219 | south | -0.12635 | 0.053013 | -0.11044 | 0.18414 | 0.053013 | south | N | 0.053013 | 0
7023 | L_BUCHAN | 2 | 18 | 0.015219 | south | -0.12635 | 0.053013 | -0.11044 | 0.18414 | 0.053013 | south | N | 0.053013 | 0
7024 | L_BUCHAN | 3 | 15 | 0.015219 | south | -0.12635 | 0.053013 | -0.11044 | 0.18414 | 0.053013 | south | N | 0.053013 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.013449 | south | -0.12812 | 0.051243 | -0.11221 | 0.18237 | 0.051243 | south | N | 0.051243 | 0
7028 | L_MARBFA | 1 | 18 | 0.004171 | south | -0.1374 | 0.041965 | -0.12149 | 0.17309 | 0.041965 | south | N | 0.041965 | 0
7029 | L_MARBFA | 2 | 18 | 0.004171 | south | -0.1374 | 0.041965 | -0.12149 | 0.17309 | 0.041965 | south | N | 0.041965 | 0
7031 | L_MARSFO | 1 | 35 | 0.000971 | south | -0.1406 | 0.038765 | -0.12469 | 0.16989 | 0.038765 | south | N | 0.038765 | 0
7032 | L_MARSFO | 2 | 34 | 0.000971 | south | -0.1406 | 0.038765 | -0.12469 | 0.16989 | 0.038765 | south | N | 0.038765 | 0
7033 | L_MARSFO | 3 | 35 | 0.000971 | south | -0.1406 | 0.038765 | -0.12469 | 0.16989 | 0.038765 | south | N | 0.038765 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.006007 | south | -0.13556 | 0.043801 | -0.11965 | 0.17492 | 0.043801 | south | N | 0.043801 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.006007 | south | -0.13556 | 0.043801 | -0.11965 | 0.17492 | 0.043801 | south | N | 0.043801 | 0
7038 | L_DELAWA | 1 | 35 | 0.12448 | west | -0.017086 | 0.16228 | -0.0011736 | 0.2934 | 0.0011736 | west | N | 0.0011736 | 0
7038 | L_DELAWA | 2 | 30 | 0.12448 | west | -0.017086 | 0.16228 | -0.0011736 | 0.2934 | 0.0011736 | west | N | 0.0011736 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.029849 | south | -0.17142 | 0.0079446 | -0.15551 | 0.13907 | 0.0079446 | south | N | 0.0079446 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.029849 | south | -0.17142 | 0.0079446 | -0.15551 | 0.13907 | 0.0079446 | south | N | 0.0079446 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.029849 | south | -0.17142 | 0.0079446 | -0.15551 | 0.13907 | 0.0079446 | south | N | 0.0079446 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.029849 | south | -0.17142 | 0.0079446 | -0.15551 | 0.13907 | 0.0079446 | south | N | 0.0079446 | 0
7487 | L_CANYHY | 1 | 6 | -0.025354 | south | -0.16692 | 0.01244 | -0.15101 | 0.14356 | 0.01244 | south | N | 0.01244 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.035885 | south | -0.17745 | 0.0019086 | -0.16154 | 0.13303 | 0.0019086 | south | N | 0.0019086 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.035885 | south | -0.17745 | 0.0019086 | -0.16154 | 0.13303 | 0.0019086 | south | N | 0.0019086 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.035885 | south | -0.17745 | 0.0019086 | -0.16154 | 0.13303 | 0.0019086 | south | N | 0.0019086 | 0
7609 | L_SCHUMA | 1 | 4 | -0.037448 | south | -0.17902 | 0.00034557 | -0.1631 | 0.13147 | 0.00034557 | south | N | 0.00034557 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.038701 | south | -0.18027 | -0.00090743 | -0.16436 | 0.13022 | 0.00090743 | south | N | 0.00090743 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.038701 | south | -0.18027 | -0.00090743 | -0.16436 | 0.13022 | 0.00090743 | south | N | 0.00090743 | 0
7800 | L_GUADGE | 1 | 147 | -0.041747 | south | -0.18332 | -0.0039534 | -0.1674 | 0.12717 | 0.0039534 | south | N | 0.0039534 | 0
7801 | L_GUADGE | 2 | 138 | -0.041747 | south | -0.18332 | -0.0039534 | -0.1674 | 0.12717 | 0.0039534 | south | N | 0.0039534 | 0
7802 | L_GUADGE | 3 | 140 | -0.041747 | south | -0.18332 | -0.0039534 | -0.1674 | 0.12717 | 0.0039534 | south | N | 0.0039534 | 0
7803 | L_GUADGE | 4 | 147 | -0.041747 | south | -0.18332 | -0.0039534 | -0.1674 | 0.12717 | 0.0039534 | south | N | 0.0039534 | 0
7804 | L_GUADGE | 5 | 182 | -0.041747 | south | -0.18332 | -0.0039534 | -0.1674 | 0.12717 | 0.0039534 | south | N | 0.0039534 | 0
7805 | L_GUADGE | 6 | 198 | -0.041747 | south | -0.18332 | -0.0039534 | -0.1674 | 0.12717 | 0.0039534 | south | N | 0.0039534 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.011395 | south | -0.15296 | 0.026399 | -0.13705 | 0.15752 | 0.026399 | south | N | 0.026399 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.011395 | south | -0.15296 | 0.026399 | -0.13705 | 0.15752 | 0.026399 | south | N | 0.026399 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.011395 | south | -0.15296 | 0.026399 | -0.13705 | 0.15752 | 0.026399 | south | N | 0.026399 | 0
7810 | L_RIONOG | 1 | 142 | -0.036866 | south | -0.17844 | 0.00092757 | -0.16252 | 0.13205 | 0.00092757 | south | N | 0.00092757 | 0
7811 | L_RIONOG | 2 | 145 | -0.036866 | south | -0.17844 | 0.00092757 | -0.16252 | 0.13205 | 0.00092757 | south | N | 0.00092757 | 0
7812 | L_RIONOG | 3 | 151 | -0.036866 | south | -0.17844 | 0.00092757 | -0.16252 | 0.13205 | 0.00092757 | south | N | 0.00092757 | 0
7813 | L_RIONOG | 4 | 290 | -0.036866 | south | -0.17844 | 0.00092757 | -0.16252 | 0.13205 | 0.00092757 | south | N | 0.00092757 | 0
8032 | AMISTADH | 1 | 33 | 0.000942 | south | -0.14063 | 0.038736 | -0.12471 | 0.16986 | 0.038736 | south | N | 0.038736 | 0
8033 | AMISTADH | 2 | 25 | 0.000942 | south | -0.14063 | 0.038736 | -0.12471 | 0.16986 | 0.038736 | south | N | 0.038736 | 0
8048 | FALCONHY | 1 | 12 | -0.062922 | south | -0.20449 | -0.025128 | -0.18858 | 0.10599 | 0.025128 | south | N | 0.025128 | 0
8066 | DUP1V#1 | 1 | 73 | -0.074259 | south | -0.21583 | -0.036465 | -0.19992 | 0.094658 | 0.036465 | south | N | 0.036465 | 0
8134 | FOR69CG0 | 1 | 79 | -0.083144 | south | -0.22471 | -0.04535 | -0.2088 | 0.085773 | 0.04535 | south | N | 0.04535 | 0
8138 | FOR69CG0 | 2 | 81 | -0.083144 | south | -0.22471 | -0.04535 | -0.2088 | 0.085773 | 0.04535 | south | N | 0.04535 | 0
8139 | JOS #1 | MB | 255 | 0 | south | -0.14157 | 0.037794 | -0.12566 | 0.16892 | 0.037794 | south | N | 0.037794 | 0
8147 | UCAR #2 | 10 | 28 | -0.078284 | south | -0.21985 | -0.04049 | -0.20394 | 0.090633 | 0.04049 | south | N | 0.04049 | 0
8148 | UCAR #1 | 2 | 7 | -0.078284 | south | -0.21985 | -0.04049 | -0.20394 | 0.090633 | 0.04049 | south | N | 0.04049 | 0
8153 | FOR69CG0 | 3 | 79 | -0.083144 | south | -0.22471 | -0.04535 | -0.2088 | 0.085773 | 0.04535 | south | N | 0.04535 | 0
8154 | FOR69CG0 | 4 | 80 | -0.083144 | south | -0.22471 | -0.04535 | -0.2088 | 0.085773 | 0.04535 | south | N | 0.04535 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.083144 | south | -0.22471 | -0.04535 | -0.2088 | 0.085773 | 0.04535 | south | N | 0.04535 | 0
8156 | FOR69CG0 | 6 | 25 | -0.083144 | south | -0.22471 | -0.04535 | -0.2088 | 0.085773 | 0.04535 | south | N | 0.04535 | 0
8157 | FOR69CG0 | 7 | 46 | -0.083144 | south | -0.22471 | -0.04535 | -0.2088 | 0.085773 | 0.04535 | south | N | 0.04535 | 0
8161 | COLETOU1 | 1 | 629 | -0.065692 | south | -0.20726 | -0.027898 | -0.19135 | 0.10322 | 0.027898 | south | N | 0.027898 | 0
8173 | VICEC51A | 5 | 144 | -0.072768 | south | -0.21434 | -0.034974 | -0.19842 | 0.096149 | 0.034974 | south | N | 0.034974 | 0
8174 | VICEC61A | 6 | 188 | -0.072768 | south | -0.21434 | -0.034974 | -0.19842 | 0.096149 | 0.034974 | south | N | 0.034974 | 0
8189 | CUERO 2 | 1 | 12 | -0.048045 | south | -0.18961 | -0.010251 | -0.1737 | 0.12087 | 0.010251 | south | N | 0.010251 | 0
8262 | ELPS | 1 | 6 | -0.013878 | south | -0.15545 | 0.023916 | -0.13953 | 0.15504 | 0.023916 | south | N | 0.023916 | 0
8285 | LAR #1 | MB | 32 | 0 | south | -0.14157 | 0.037794 | -0.12566 | 0.16892 | 0.037794 | south | N | 0.037794 | 0
8287 | LAR #2 | MB | 32 | 0 | south | -0.14157 | 0.037794 | -0.12566 | 0.16892 | 0.037794 | south | N | 0.037794 | 0
8288 | LAR #3 | MB | 105 | 0 | south | -0.14157 | 0.037794 | -0.12566 | 0.16892 | 0.037794 | south | N | 0.037794 | 0
8388 | BATES0A | MB | 70 | 0 | south | -0.14157 | 0.037794 | -0.12566 | 0.16892 | 0.037794 | south | N | 0.037794 | 0
8393 | BATES0B | MB | 110 | 0 | south | -0.14157 | 0.037794 | -0.12566 | 0.16892 | 0.037794 | south | N | 0.037794 | 0
8442 | NBEC71A | 1 | 336 | -0.070856 | south | -0.21243 | -0.033062 | -0.19651 | 0.098061 | 0.033062 | south | N | 0.033062 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | -0.14157 | 0.037794 | -0.12566 | 0.16892 | 0.037794 | south | N | 0.037794 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | -0.14157 | 0.037794 | -0.12566 | 0.16892 | 0.037794 | south | N | 0.037794 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.070518 | south | -0.21209 | -0.032724 | -0.19617 | 0.098399 | 0.032724 | south | N | 0.032724 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.070518 | south | -0.21209 | -0.032724 | -0.19617 | 0.098399 | 0.032724 | south | N | 0.032724 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.070268 | south | -0.21184 | -0.032474 | -0.19592 | 0.098649 | 0.032474 | south | N | 0.032474 | 0
8506 | VAL #1 | 1 | 25 | -0.070437 | south | -0.21201 | -0.032643 | -0.19609 | 0.09848 | 0.032643 | south | N | 0.032643 | 0
8507 | VAL #2 | 2 | 25 | -0.070437 | south | -0.21201 | -0.032643 | -0.19609 | 0.09848 | 0.032643 | south | N | 0.032643 | 0
8511 | OXY_CC0A | 1 | 38 | -0.070313 | south | -0.21188 | -0.032519 | -0.19597 | 0.098604 | 0.032519 | south | N | 0.032519 | 0
8517 | CELANEBI | 1 | 29 | -0.069529 | south | -0.2111 | -0.031735 | -0.19519 | 0.099388 | 0.031735 | south | N | 0.031735 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.070838 | south | -0.21241 | -0.033044 | -0.19649 | 0.098079 | 0.033044 | south | N | 0.033044 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.070838 | south | -0.21241 | -0.033044 | -0.19649 | 0.098079 | 0.033044 | south | N | 0.033044 | 0
8562 | CNOPST1 | 3 | 153 | -0.070838 | south | -0.21241 | -0.033044 | -0.19649 | 0.098079 | 0.033044 | south | N | 0.033044 | 0
8926 | LGE_GT10 | 1 | 158 | -0.072415 | south | -0.21398 | -0.034621 | -0.19807 | 0.096502 | 0.034621 | south | N | 0.034621 | 0
8927 | LGE_GT20 | 2 | 153 | -0.072415 | south | -0.21398 | -0.034621 | -0.19807 | 0.096502 | 0.034621 | south | N | 0.034621 | 0
8928 | LGE_STG0 | 3 | 100 | -0.072415 | south | -0.21398 | -0.034621 | -0.19807 | 0.096502 | 0.034621 | south | N | 0.034621 | 0
8930 | ICPGN10A | 1 | 145 | -0.072415 | south | -0.21398 | -0.034621 | -0.19807 | 0.096502 | 0.034621 | south | N | 0.034621 | 0
8931 | ICPGN20A | 2 | 147 | -0.072415 | south | -0.21398 | -0.034621 | -0.19807 | 0.096502 | 0.034621 | south | N | 0.034621 | 0
8932 | ICPGN30A | 3 | 127 | -0.072415 | south | -0.21398 | -0.034621 | -0.19807 | 0.096502 | 0.034621 | south | N | 0.034621 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.067638 | south | -0.20921 | -0.029844 | -0.19329 | 0.10128 | 0.029844 | south | N | 0.029844 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.067638 | south | -0.20921 | -0.029844 | -0.19329 | 0.10128 | 0.029844 | south | N | 0.029844 | 0
8935 | FGNTS201 | 3 | 173 | -0.067638 | south | -0.20921 | -0.029844 | -0.19329 | 0.10128 | 0.029844 | south | N | 0.029844 | 0
8936 | MVGN#1 | 1 | 207 | -0.068414 | south | -0.20998 | -0.03062 | -0.19407 | 0.1005 | 0.03062 | south | N | 0.03062 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.068414 | south | -0.20998 | -0.03062 | -0.19407 | 0.1005 | 0.03062 | south | N | 0.03062 | 0
8938 | MVGN#3 | 3 | 242 | -0.068414 | south | -0.20998 | -0.03062 | -0.19407 | 0.1005 | 0.03062 | south | N | 0.03062 | 0
8981 | HECN1 | 1 | 144 | -0.068419 | south | -0.20999 | -0.030625 | -0.19408 | 0.1005 | 0.030625 | south | N | 0.030625 | 0
8982 | HECN2 | 2 | 144 | -0.068419 | south | -0.20999 | -0.030625 | -0.19408 | 0.1005 | 0.030625 | south | N | 0.030625 | 0
8983 | HECN3 | 3 | 171 | -0.068419 | south | -0.20999 | -0.030625 | -0.19408 | 0.1005 | 0.030625 | south | N | 0.030625 | 0
9000 | DECKR_G1 | 1 | 310 | -0.001799 | south | -0.14337 | 0.035995 | -0.12746 | 0.16712 | 0.035995 | south | N | 0.035995 | 0
9001 | DECKR_G2 | 2 | 413 | -0.001799 | south | -0.14337 | 0.035995 | -0.12746 | 0.16712 | 0.035995 | south | N | 0.035995 | 0
9002 | DECKR_G3 | 3 | 42 | -0.000381 | south | -0.14195 | 0.037413 | -0.12604 | 0.16854 | 0.037413 | south | N | 0.037413 | 0
9003 | DECKR_G4 | 4 | 44 | -0.000381 | south | -0.14195 | 0.037413 | -0.12604 | 0.16854 | 0.037413 | south | N | 0.037413 | 0
9004 | DECKR_G5 | 5 | 44 | -0.000381 | south | -0.14195 | 0.037413 | -0.12604 | 0.16854 | 0.037413 | south | N | 0.037413 | 0
9005 | DECKR_G6 | 6 | 47 | -0.000381 | south | -0.14195 | 0.037413 | -0.12604 | 0.16854 | 0.037413 | south | N | 0.037413 | 0
9016 | SANDH_G1 | 1 | 49 | -0.00405 | south | -0.14562 | 0.033744 | -0.12971 | 0.16487 | 0.033744 | south | N | 0.033744 | 0
9017 | SANDH_G2 | 2 | 46 | -0.00405 | south | -0.14562 | 0.033744 | -0.12971 | 0.16487 | 0.033744 | south | N | 0.033744 | 0
9018 | SANDH_G3 | 3 | 46 | -0.00405 | south | -0.14562 | 0.033744 | -0.12971 | 0.16487 | 0.033744 | south | N | 0.033744 | 0
9019 | SANDH_G4 | 4 | 47 | -0.00405 | south | -0.14562 | 0.033744 | -0.12971 | 0.16487 | 0.033744 | south | N | 0.033744 | 0
9020 | SANDHG5A | 5A | 154 | -0.00405 | south | -0.14562 | 0.033744 | -0.12971 | 0.16487 | 0.033744 | south | N | 0.033744 | 0
9021 | SANDHG5C | 5C | 148 | -0.00405 | south | -0.14562 | 0.033744 | -0.12971 | 0.16487 | 0.033744 | south | N | 0.033744 | 0
9022 | SANDH_G6 | 6 | 48 | -0.00405 | south | -0.14562 | 0.033744 | -0.12971 | 0.16487 | 0.033744 | south | N | 0.033744 | 0
9023 | SANDH_G7 | 7 | 48 | -0.00405 | south | -0.14562 | 0.033744 | -0.12971 | 0.16487 | 0.033744 | south | N | 0.033744 | 0
11001 | NAV1CT | 1 | 70 | 0.12566 | west | -0.015911 | 0.16345 | 1.4135e-06 | 0.29457 | 1.4135e-06 | west | N | 1.4135e-06 | 0
11009 | NAV2CT | 1 | 70 | 0.12566 | west | -0.015911 | 0.16345 | 1.4135e-06 | 0.29457 | 1.4135e-06 | west | N | 1.4135e-06 | 0
11011 | NAV3ST | 1 | 92.8 | 0.12566 | west | -0.015911 | 0.16345 | 1.4135e-06 | 0.29457 | 1.4135e-06 | west | N | 1.4135e-06 | 0
11012 | NAV4CT | 1 | 80 | 0.12566 | west | -0.015911 | 0.16345 | 1.4135e-06 | 0.29457 | 1.4135e-06 | west | N | 1.4135e-06 | 0
11013 | NAV5CT | 1 | 80 | 0.12566 | west | -0.015911 | 0.16345 | 1.4135e-06 | 0.29457 | 1.4135e-06 | west | N | 1.4135e-06 | 0
11014 | NAV6ST | 1 | 115 | 0.12566 | west | -0.015911 | 0.16345 | 1.4135e-06 | 0.29457 | 1.4135e-06 | west | N | 1.4135e-06 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.12565 | west | -0.015922 | 0.16344 | -9.5865e-06 | 0.29456 | 9.5865e-06 | west | N | 9.5865e-06 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.12565 | west | -0.015922 | 0.16344 | -9.5865e-06 | 0.29456 | 9.5865e-06 | west | N | 9.5865e-06 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.12565 | west | -0.015922 | 0.16344 | -9.5865e-06 | 0.29456 | 9.5865e-06 | west | N | 9.5865e-06 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.12565 | west | -0.015922 | 0.16344 | -9.5865e-06 | 0.29456 | 9.5865e-06 | west | N | 9.5865e-06 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.12565 | west | -0.015922 | 0.16344 | -9.5865e-06 | 0.29456 | 9.5865e-06 | west | N | 9.5865e-06 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.12565 | west | -0.015922 | 0.16344 | -9.5865e-06 | 0.29456 | 9.5865e-06 | west | N | 9.5865e-06 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.12783 | west | -0.01374 | 0.16562 | 0.0021724 | 0.29675 | 0.0021724 | west | N | 0.0021724 | 0
11057 | CHAMPION | 1 | 126.5 | 0.12783 | west | -0.01374 | 0.16562 | 0.0021724 | 0.29675 | 0.0021724 | west | N | 0.0021724 | 0
11058 | PYRON_1G | 1 | 249 | 0.12783 | west | -0.01374 | 0.16562 | 0.0021724 | 0.29675 | 0.0021724 | west | N | 0.0021724 | 0
11059 | INADALE_ | 1 | 197 | 0.12783 | west | -0.01374 | 0.16562 | 0.0021724 | 0.29675 | 0.0021724 | west | N | 0.0021724 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.12673 | west | -0.014837 | 0.16453 | 0.0010754 | 0.29565 | 0.0010754 | west | N | 0.0010754 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.12673 | west | -0.014837 | 0.16453 | 0.0010754 | 0.29565 | 0.0010754 | west | N | 0.0010754 | 0
11147 | NOTREES_ | 1 | 149 | 0.12469 | west | -0.016876 | 0.16249 | -0.00096359 | 0.29361 | 0.00096359 | west | N | 0.00096359 | 0
11309 | BULLCREK | 1 | 180 | 0.12653 | west | -0.015042 | 0.16432 | 0.00087041 | 0.29544 | 0.00087041 | west | N | 0.00087041 | 0
11310 | BULLCREK | 1 | 180 | 0.12653 | west | -0.015042 | 0.16432 | 0.00087041 | 0.29544 | 0.00087041 | west | N | 0.00087041 | 0
11320 | COYOTE_1 | 1 | 225 | 0.12646 | west | -0.015106 | 0.16426 | 0.00080641 | 0.29538 | 0.00080641 | west | N | 0.00080641 | 0
11415 | LORAINE_ | 1 | 125 | 0.12738 | west | -0.01419 | 0.16517 | 0.0017224 | 0.2963 | 0.0017224 | west | N | 0.0017224 | 0
11416 | LORAINE_ | 1 | 125 | 0.12738 | west | -0.01419 | 0.16517 | 0.0017224 | 0.2963 | 0.0017224 | west | N | 0.0017224 | 0
11691 | KMICHICT | 1 | 140 | 0.14098 | north | -0.00059338 | 0.17877 | 0.015319 | 0.30989 | 0.00059338 | North | N | 0.00059338 | 0
11692 | KMICHICT | 2 | 141 | 0.14098 | north | -0.00059338 | 0.17877 | 0.015319 | 0.30989 | 0.00059338 | North | N | 0.00059338 | 0
11693 | KMICHIST | 3 | 309 | 0.14098 | north | -0.00059338 | 0.17877 | 0.015319 | 0.30989 | 0.00059338 | North | N | 0.00059338 | 0
11694 | KMICHICT | 4 | 143 | 0.14098 | north | -0.00059338 | 0.17877 | 0.015319 | 0.30989 | 0.00059338 | North | N | 0.00059338 | 0
11695 | KMICHICT | 5 | 144 | 0.14098 | north | -0.00059338 | 0.17877 | 0.015319 | 0.30989 | 0.00059338 | North | N | 0.00059338 | 0
11696 | KMICHIST | 6 | 310 | 0.14098 | north | -0.00059338 | 0.17877 | 0.015319 | 0.30989 | 0.00059338 | North | N | 0.00059338 | 0
12322 | ENNSTRAC | 1 | 196 | 0.13893 | north | -0.0026384 | 0.17672 | 0.013274 | 0.30785 | 0.0026384 | North | N | 0.0026384 | 0
12323 | ENNSTRAC | 2 | 111 | 0.13893 | north | -0.0026384 | 0.17672 | 0.013274 | 0.30785 | 0.0026384 | North | N | 0.0026384 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.14044 | north | -0.0011254 | 0.17824 | 0.014787 | 0.30936 | 0.0011254 | North | N | 0.0011254 | 0
12411 | FPLEFR1A | 1 | 161 | 0.14224 | north | 0.00066962 | 0.18003 | 0.016582 | 0.31116 | 0.00066962 | North | N | 0.00066962 | 0
12412 | FPLEFR1B | 2 | 164 | 0.14224 | north | 0.00066962 | 0.18003 | 0.016582 | 0.31116 | 0.00066962 | North | N | 0.00066962 | 0
12413 | FPLEFR1C | 3 | 164 | 0.14224 | north | 0.00066962 | 0.18003 | 0.016582 | 0.31116 | 0.00066962 | North | N | 0.00066962 | 0
12414 | FPLEFR1S | 4 | 414 | 0.14224 | north | 0.00066962 | 0.18003 | 0.016582 | 0.31116 | 0.00066962 | North | N | 0.00066962 | 0
12421 | FPLEFR2A | 1 | 162 | 0.14224 | north | 0.00066962 | 0.18003 | 0.016582 | 0.31116 | 0.00066962 | North | N | 0.00066962 | 0
12422 | FPLEFR2B | 2 | 161 | 0.14224 | north | 0.00066962 | 0.18003 | 0.016582 | 0.31116 | 0.00066962 | North | N | 0.00066962 | 0
12423 | FPLEFR2C | 3 | 163 | 0.14224 | north | 0.00066962 | 0.18003 | 0.016582 | 0.31116 | 0.00066962 | North | N | 0.00066962 | 0
12424 | FPLEFR2S | 4 | 409 | 0.14224 | north | 0.00066962 | 0.18003 | 0.016582 | 0.31116 | 0.00066962 | North | N | 0.00066962 | 0
12440 | PARKD_1S | 1 | 0 | 0.14146 | north | -0.00010938 | 0.17925 | 0.015803 | 0.31038 | 0.00010938 | North | N | 0.00010938 | 0
12449 | PARKD_2S | 1 | 0 | 0.14146 | north | -0.00010938 | 0.17925 | 0.015803 | 0.31038 | 0.00010938 | North | N | 0.00010938 | 0
13116 | TGATEWAY | 1 | 148 | 0.14553 | north | 0.0039646 | 0.18333 | 0.019877 | 0.31445 | 0.0039646 | North | N | 0.0039646 | 0
13117 | TGATEWAY | 2 | 130 | 0.14553 | north | 0.0039646 | 0.18333 | 0.019877 | 0.31445 | 0.0039646 | North | N | 0.0039646 | 0
13118 | TGATEWAY | 3 | 145 | 0.14553 | north | 0.0039646 | 0.18333 | 0.019877 | 0.31445 | 0.0039646 | North | N | 0.0039646 | 0
13119 | TGATEWAY | 4 | 399 | 0.14553 | north | 0.0039646 | 0.18333 | 0.019877 | 0.31445 | 0.0039646 | North | N | 0.0039646 | 0
13131 | CALFREST | 1 | 150.7 | 0.15359 | north | 0.012019 | 0.19138 | 0.027931 | 0.3225 | 0.012019 | North | N | 0.012019 | 0
13132 | CALFREST | 2 | 151 | 0.15359 | north | 0.012019 | 0.19138 | 0.027931 | 0.3225 | 0.012019 | North | N | 0.012019 | 0
13133 | CALFREST | 3 | 177.4 | 0.15359 | north | 0.012019 | 0.19138 | 0.027931 | 0.3225 | 0.012019 | North | N | 0.012019 | 0
13134 | CALFREST | 4 | 151.5 | 0.1533 | north | 0.011731 | 0.19109 | 0.027643 | 0.32222 | 0.011731 | North | N | 0.011731 | 0
13135 | CALFREST | 5 | 152.3 | 0.1533 | north | 0.011731 | 0.19109 | 0.027643 | 0.32222 | 0.011731 | North | N | 0.011731 | 0
13136 | CALFREST | 6 | 177.5 | 0.1533 | north | 0.011731 | 0.19109 | 0.027643 | 0.32222 | 0.011731 | North | N | 0.011731 | 0
13432 | SANDOW_5 | 5 | 581 | 0.036384 | south | -0.10519 | 0.074178 | -0.089273 | 0.2053 | 0.074178 | south | N | 0.074178 | 0
13691 | OAKGROVE | 1 | 855 | 0.1476 | north | 0.0060276 | 0.18539 | 0.02194 | 0.31651 | 0.0060276 | North | N | 0.0060276 | 0
13692 | OAKGROVE | 2 | 855 | 0.1476 | north | 0.0060276 | 0.18539 | 0.02194 | 0.31651 | 0.0060276 | North | N | 0.0060276 | 0
32798 | BRYN_TAM | 1 | 32 | 0.13723 | north | -0.0043364 | 0.17503 | 0.011576 | 0.30615 | 0.0043364 | North | N | 0.0043364 | 0
32883 | BRYN_DNS | 1 | 48 | 0.13495 | north | -0.0066204 | 0.17274 | 0.0092924 | 0.30387 | 0.0066204 | North | N | 0.0066204 | 0
32884 | BRYN_DNS | 1 | 46 | 0.13495 | north | -0.0066204 | 0.17274 | 0.0092924 | 0.30387 | 0.0066204 | North | N | 0.0066204 | 0
32886 | BRYN_ATK | MB | 12 | 0.13716 | north | -0.0044124 | 0.17495 | 0.0115 | 0.30607 | 0.0044124 | North | N | 0.0044124 | 0
32887 | BRYN_ATK | MB | 51 | 0.13716 | north | -0.0044124 | 0.17495 | 0.0115 | 0.30607 | 0.0044124 | North | N | 0.0044124 | 0
32888 | BRYN_ATK | 1 | 17 | 0.13716 | north | -0.0044124 | 0.17495 | 0.0115 | 0.30607 | 0.0044124 | North | N | 0.0044124 | 0
32890 | BRYN_ATK | MB | 22 | 0.13716 | north | -0.0044124 | 0.17495 | 0.0115 | 0.30607 | 0.0044124 | North | N | 0.0044124 | 0
32891 | BRYN_ATK | MB | 25 | 0.13716 | north | -0.0044124 | 0.17495 | 0.0115 | 0.30607 | 0.0044124 | North | N | 0.0044124 | 0
32892 | BRYN_DNS | 1 | 105 | 0.13495 | north | -0.0066204 | 0.17274 | 0.0092924 | 0.30387 | 0.0066204 | North | N | 0.0066204 | 0
36998 | RDCNYNG1 | 1 | 84 | 0.12716 | west | -0.014405 | 0.16496 | 0.0015074 | 0.29608 | 0.0015074 | west | N | 0.0015074 | 0
38332 | WDWRDU2 | 1 | 80 | 0.11743 | west | -0.02414 | 0.15522 | -0.0082276 | 0.28635 | 0.0082276 | west | N | 0.0082276 | 0
38437 | TNSRBNMS | 1 | 150 | 0.11736 | west | -0.024204 | 0.15516 | -0.0082916 | 0.28628 | 0.0082916 | west | N | 0.0082916 | 0
38438 | TNSRBNMS | 1 | 150 | 0.11736 | west | -0.024204 | 0.15516 | -0.0082916 | 0.28628 | 0.0082916 | west | N | 0.0082916 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.16705 | houston | -0.30862 | -0.12925 | -0.2927 | 0.0018688 | 0.0018688 | houston | N | 0.0018688 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.16705 | houston | -0.30862 | -0.12925 | -0.2927 | 0.0018688 | 0.0018688 | houston | N | 0.0018688 | 0
38600 | TNBP_CGN | 5 | 53 | -0.16705 | houston | -0.30862 | -0.12925 | -0.2927 | 0.0018688 | 0.0018688 | houston | N | 0.0018688 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.16705 | houston | -0.30862 | -0.12925 | -0.2927 | 0.0018688 | 0.0018688 | houston | N | 0.0018688 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.16705 | houston | -0.30862 | -0.12925 | -0.2927 | 0.0018688 | 0.0018688 | houston | N | 0.0018688 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.16705 | houston | -0.30862 | -0.12925 | -0.2927 | 0.0018688 | 0.0018688 | houston | N | 0.0018688 | 0
38614 | TNBPAMCG | 4 | 96 | -0.16705 | houston | -0.30862 | -0.12925 | -0.2927 | 0.0018688 | 0.0018688 | houston | N | 0.0018688 | 0
38615 | TNBPAMCG | 1 | 244 | -0.16705 | houston | -0.30862 | -0.12925 | -0.2927 | 0.0018688 | 0.0018688 | houston | N | 0.0018688 | 0
38690 | TNBP_CGN | 3 | 40 | -0.16705 | houston | -0.30862 | -0.12925 | -0.2927 | 0.0018688 | 0.0018688 | houston | N | 0.0018688 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.16702 | houston | -0.30859 | -0.12923 | -0.29268 | 0.0018958 | 0.0018958 | houston | N | 0.0018958 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.16702 | houston | -0.30859 | -0.12923 | -0.29268 | 0.0018958 | 0.0018958 | houston | N | 0.0018958 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.16702 | houston | -0.30859 | -0.12923 | -0.29268 | 0.0018958 | 0.0018958 | houston | N | 0.0018958 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.16702 | houston | -0.30859 | -0.12923 | -0.29268 | 0.0018958 | 0.0018958 | houston | N | 0.0018958 | 0
39470 | TNDOWCGN | 1 | 32 | -0.16702 | houston | -0.30859 | -0.12923 | -0.29268 | 0.0018948 | 0.0018948 | houston | N | 0.0018948 | 0
39480 | TNDOWCGN | 1 | 30 | -0.16702 | houston | -0.30859 | -0.12923 | -0.29268 | 0.0018948 | 0.0018948 | houston | N | 0.0018948 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.14969 | houston | -0.29125 | -0.11189 | -0.27534 | 0.019232 | 0.019232 | houston | N | 0.019232 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.14969 | houston | -0.29125 | -0.11189 | -0.27534 | 0.019232 | 0.019232 | houston | N | 0.019232 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.14969 | houston | -0.29125 | -0.11189 | -0.27534 | 0.019232 | 0.019232 | houston | N | 0.019232 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.14969 | houston | -0.29125 | -0.11189 | -0.27534 | 0.019232 | 0.019232 | houston | N | 0.019232 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.1476 | north | 0.0060276 | 0.18539 | 0.02194 | 0.31651 | 0.0060276 | North | N | 0.0060276 | 0
39970 | TNTNPONE | 1 | 153 | 0.1476 | north | 0.0060276 | 0.18539 | 0.02194 | 0.31651 | 0.0060276 | North | N | 0.0060276 | 0
48500 | APD_GT1_ | 1 | 136 | -0.17759 | houston | -0.31916 | -0.1398 | -0.30325 | -0.0086752 | 0.0086752 | houston | N | 0.0086752 | 0
48510 | AK_GT1__ | 1 | 33 | -0.16126 | houston | -0.30283 | -0.12347 | -0.28692 | 0.0076518 | 0.0076518 | houston | N | 0.0076518 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.17764 | houston | -0.31921 | -0.13985 | -0.3033 | -0.0087272 | 0.0087272 | houston | N | 0.0087272 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.17764 | houston | -0.31921 | -0.13985 | -0.3033 | -0.0087272 | 0.0087272 | houston | N | 0.0087272 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.17764 | houston | -0.31921 | -0.13985 | -0.3033 | -0.0087272 | 0.0087272 | houston | N | 0.0087272 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.17764 | houston | -0.31921 | -0.13985 | -0.3033 | -0.0087272 | 0.0087272 | houston | N | 0.0087272 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.14687 | houston | -0.28844 | -0.10908 | -0.27253 | 0.022048 | 0.022048 | houston | N | 0.022048 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.14687 | houston | -0.28844 | -0.10908 | -0.27253 | 0.022048 | 0.022048 | houston | N | 0.022048 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.16027 | houston | -0.30184 | -0.12248 | -0.28593 | 0.0086428 | 0.0086428 | houston | N | 0.0086428 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.16027 | houston | -0.30184 | -0.12248 | -0.28593 | 0.0086428 | 0.0086428 | houston | N | 0.0086428 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.16027 | houston | -0.30184 | -0.12248 | -0.28593 | 0.0086428 | 0.0086428 | houston | N | 0.0086428 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.17365 | houston | -0.31522 | -0.13586 | -0.29931 | -0.0047342 | 0.0047342 | houston | N | 0.0047342 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.17365 | houston | -0.31522 | -0.13586 | -0.29931 | -0.0047342 | 0.0047342 | houston | N | 0.0047342 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.17365 | houston | -0.31522 | -0.13586 | -0.29931 | -0.0047342 | 0.0047342 | houston | N | 0.0047342 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.17365 | houston | -0.31522 | -0.13586 | -0.29931 | -0.0047342 | 0.0047342 | houston | N | 0.0047342 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.17622 | houston | -0.31779 | -0.13842 | -0.30187 | -0.0073002 | 0.0073002 | houston | N | 0.0073002 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.17622 | houston | -0.31779 | -0.13842 | -0.30187 | -0.0073002 | 0.0073002 | houston | N | 0.0073002 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.17288 | houston | -0.31445 | -0.13509 | -0.29854 | -0.0039622 | 0.0039622 | houston | N | 0.0039622 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.17288 | houston | -0.31445 | -0.13509 | -0.29854 | -0.0039622 | 0.0039622 | houston | N | 0.0039622 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.17288 | houston | -0.31445 | -0.13509 | -0.29854 | -0.0039622 | 0.0039622 | houston | N | 0.0039622 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.17288 | houston | -0.31445 | -0.13509 | -0.29854 | -0.0039622 | 0.0039622 | houston | N | 0.0039622 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.17288 | houston | -0.31445 | -0.13509 | -0.29854 | -0.0039622 | 0.0039622 | houston | N | 0.0039622 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.18086 | houston | -0.32243 | -0.14306 | -0.30651 | -0.011941 | 0.011941 | houston | N | 0.011941 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.17955 | houston | -0.32112 | -0.14176 | -0.30521 | -0.010637 | 0.010637 | houston | N | 0.010637 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.18125 | houston | -0.32282 | -0.14346 | -0.30691 | -0.012333 | 0.012333 | houston | N | 0.012333 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.18125 | houston | -0.32282 | -0.14346 | -0.30691 | -0.012333 | 0.012333 | houston | N | 0.012333 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.18125 | houston | -0.32282 | -0.14346 | -0.30691 | -0.012333 | 0.012333 | houston | N | 0.012333 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.18849 | houston | -0.33006 | -0.1507 | -0.31415 | -0.019574 | 0.019574 | houston | N | 0.019574 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.17785 | houston | -0.31942 | -0.14006 | -0.30351 | -0.0089342 | 0.0089342 | houston | N | 0.0089342 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.17785 | houston | -0.31942 | -0.14006 | -0.30351 | -0.0089342 | 0.0089342 | houston | N | 0.0089342 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.18217 | houston | -0.32374 | -0.14438 | -0.30783 | -0.013255 | 0.013255 | houston | N | 0.013255 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.18217 | houston | -0.32374 | -0.14438 | -0.30783 | -0.013255 | 0.013255 | houston | N | 0.013255 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.18217 | houston | -0.32374 | -0.14438 | -0.30783 | -0.013255 | 0.013255 | houston | N | 0.013255 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.18217 | houston | -0.32374 | -0.14438 | -0.30783 | -0.013255 | 0.013255 | houston | N | 0.013255 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.1763 | houston | -0.31787 | -0.13851 | -0.30196 | -0.0073852 | 0.0073852 | houston | N | 0.0073852 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.1763 | houston | -0.31787 | -0.13851 | -0.30196 | -0.0073852 | 0.0073852 | houston | N | 0.0073852 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.1763 | houston | -0.31787 | -0.13851 | -0.30196 | -0.0073852 | 0.0073852 | houston | N | 0.0073852 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.1763 | houston | -0.31787 | -0.13851 | -0.30196 | -0.0073852 | 0.0073852 | houston | N | 0.0073852 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.17547 | houston | -0.31704 | -0.13768 | -0.30113 | -0.0065582 | 0.0065582 | houston | N | 0.0065582 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.17547 | houston | -0.31704 | -0.13768 | -0.30113 | -0.0065582 | 0.0065582 | houston | N | 0.0065582 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.17547 | houston | -0.31704 | -0.13768 | -0.30113 | -0.0065582 | 0.0065582 | houston | N | 0.0065582 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.17547 | houston | -0.31704 | -0.13768 | -0.30113 | -0.0065582 | 0.0065582 | houston | N | 0.0065582 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.17547 | houston | -0.31704 | -0.13768 | -0.30113 | -0.0065582 | 0.0065582 | houston | N | 0.0065582 | 0
48651 | EP_1_2 | 1 | 5 | -0.18079 | houston | -0.32236 | -0.143 | -0.30645 | -0.011875 | 0.011875 | houston | N | 0.011875 | 0
48651 | EP_1_2 | 2 | 21 | -0.18079 | houston | -0.32236 | -0.143 | -0.30645 | -0.011875 | 0.011875 | houston | N | 0.011875 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.23939 | north | -0.38096 | -0.2016 | -0.36505 | -0.070474 | 0.070474 | houston | Y | 0.38096 | 47.877
48672 | FTR_GT2_ | 2 | 156 | -0.23939 | north | -0.38096 | -0.2016 | -0.36505 | -0.070474 | 0.070474 | houston | Y | 0.38096 | 48.4359
48673 | FTR_GT3_ | 3 | 156 | -0.23939 | north | -0.38096 | -0.2016 | -0.36505 | -0.070474 | 0.070474 | houston | Y | 0.38096 | 48.4359
48674 | FTR_CN4_ | 4 | 380 | -0.23939 | north | -0.38096 | -0.2016 | -0.36505 | -0.070474 | 0.070474 | houston | Y | 0.38096 | 117.9848
48690 | GBY_GN5_ | 5 | 398 | -0.1825 | houston | -0.32407 | -0.14471 | -0.30816 | -0.013584 | 0.013584 | houston | N | 0.013584 | 0
48691 | GBY_7374 | A | 46 | -0.17482 | houston | -0.31639 | -0.13703 | -0.30048 | -0.0059032 | 0.0059032 | houston | N | 0.0059032 | 0
48691 | GBY_7374 | B | 46 | -0.17482 | houston | -0.31639 | -0.13703 | -0.30048 | -0.0059032 | 0.0059032 | houston | N | 0.0059032 | 0
48692 | GBY_8182 | C | 46 | -0.17482 | houston | -0.31639 | -0.13703 | -0.30048 | -0.0059032 | 0.0059032 | houston | N | 0.0059032 | 0
48692 | GBY_8182 | D | 55 | -0.17482 | houston | -0.31639 | -0.13703 | -0.30048 | -0.0059032 | 0.0059032 | houston | N | 0.0059032 | 0
48693 | GBY_8384 | E | 55 | -0.17482 | houston | -0.31639 | -0.13703 | -0.30048 | -0.0059032 | 0.0059032 | houston | N | 0.0059032 | 0
48693 | GBY_8384 | F | 54 | -0.17482 | houston | -0.31639 | -0.13703 | -0.30048 | -0.0059032 | 0.0059032 | houston | N | 0.0059032 | 0
48721 | LEG_1___ | 1 | 827 | 0.16117 | north | 0.019601 | 0.19896 | 0.035513 | 0.33009 | 0.019601 | North | N | 0.019601 | 0
48722 | LEG_2___ | 2 | 819 | 0.16117 | north | 0.019601 | 0.19896 | 0.035513 | 0.33009 | 0.019601 | North | N | 0.019601 | 0
48730 | MNS_GT | 1 | 46.1 | -0.15976 | houston | -0.30133 | -0.12197 | -0.28542 | 0.0091568 | 0.0091568 | houston | N | 0.0091568 | 0
48731 | CBE_GT1 | 1 | 76 | -0.1243 | houston | -0.26587 | -0.08651 | -0.24996 | 0.044613 | 0.044613 | houston | N | 0.044613 | 0
48732 | CBE_GT2 | 1 | 76 | -0.1243 | houston | -0.26587 | -0.08651 | -0.24996 | 0.044613 | 0.044613 | houston | N | 0.044613 | 0
48733 | CBE_ST12 | 1 | 105 | -0.1243 | houston | -0.26587 | -0.08651 | -0.24996 | 0.044613 | 0.044613 | houston | N | 0.044613 | 0
48734 | CBE_GT3 | 1 | 74 | -0.1243 | houston | -0.26587 | -0.08651 | -0.24996 | 0.044613 | 0.044613 | houston | N | 0.044613 | 0
48735 | CBE_GT4 | 1 | 74 | -0.1243 | houston | -0.26587 | -0.08651 | -0.24996 | 0.044613 | 0.044613 | houston | N | 0.044613 | 0
48736 | CBE_ST34 | 1 | 102 | -0.1243 | houston | -0.26587 | -0.08651 | -0.24996 | 0.044613 | 0.044613 | houston | N | 0.044613 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.17633 | houston | -0.3179 | -0.13853 | -0.30198 | -0.0074112 | 0.0074112 | houston | N | 0.0074112 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.17633 | houston | -0.3179 | -0.13853 | -0.30198 | -0.0074112 | 0.0074112 | houston | N | 0.0074112 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.17633 | houston | -0.3179 | -0.13853 | -0.30198 | -0.0074112 | 0.0074112 | houston | N | 0.0074112 | 0
48761 | PR_GT1__ | 1 | 35 | -0.17581 | houston | -0.31738 | -0.13801 | -0.30146 | -0.0068902 | 0.0068902 | houston | N | 0.0068902 | 0
48772 | PHR_GN2_ | MB | 459 | -0.17091 | houston | -0.31247 | -0.13311 | -0.29656 | -0.0019882 | 0.0019882 | houston | N | 0.0019882 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.1808 | houston | -0.32237 | -0.14301 | -0.30646 | -0.011886 | 0.011886 | houston | N | 0.011886 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.1808 | houston | -0.32237 | -0.14301 | -0.30646 | -0.011886 | 0.011886 | houston | N | 0.011886 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.1808 | houston | -0.32237 | -0.14301 | -0.30646 | -0.011886 | 0.011886 | houston | N | 0.011886 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.1808 | houston | -0.32237 | -0.14301 | -0.30646 | -0.011886 | 0.011886 | houston | N | 0.011886 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.1808 | houston | -0.32237 | -0.14301 | -0.30646 | -0.011886 | 0.011886 | houston | N | 0.011886 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.1808 | houston | -0.32237 | -0.14301 | -0.30646 | -0.011886 | 0.011886 | houston | N | 0.011886 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.1808 | houston | -0.32237 | -0.14301 | -0.30646 | -0.011886 | 0.011886 | houston | N | 0.011886 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.18849 | houston | -0.33006 | -0.1507 | -0.31415 | -0.019574 | 0.019574 | houston | N | 0.019574 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.18849 | houston | -0.33006 | -0.1507 | -0.31415 | -0.019574 | 0.019574 | houston | N | 0.019574 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.18849 | houston | -0.33006 | -0.1507 | -0.31415 | -0.019574 | 0.019574 | houston | N | 0.019574 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.18849 | houston | -0.33006 | -0.1507 | -0.31415 | -0.019574 | 0.019574 | houston | N | 0.019574 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.1811 | houston | -0.32267 | -0.14331 | -0.30676 | -0.012185 | 0.012185 | houston | N | 0.012185 | 0
48820 | SHELLG1_ | 1 | 71 | -0.17681 | houston | -0.31838 | -0.13902 | -0.30247 | -0.0078962 | 0.0078962 | houston | N | 0.0078962 | 0
48821 | SHELLG2 | 2 | 72 | -0.17681 | houston | -0.31838 | -0.13902 | -0.30247 | -0.0078962 | 0.0078962 | houston | N | 0.0078962 | 0
48822 | SHELLG3_ | 1 | 39 | -0.17681 | houston | -0.31838 | -0.13902 | -0.30247 | -0.0078962 | 0.0078962 | houston | N | 0.0078962 | 0
48822 | SHELLG3_ | 2 | 30 | -0.17681 | houston | -0.31838 | -0.13902 | -0.30247 | -0.0078962 | 0.0078962 | houston | N | 0.0078962 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.17509 | houston | -0.31666 | -0.13729 | -0.30074 | -0.0061692 | 0.0061692 | houston | N | 0.0061692 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.17509 | houston | -0.31666 | -0.13729 | -0.30074 | -0.0061692 | 0.0061692 | houston | N | 0.0061692 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.1763 | houston | -0.31787 | -0.1385 | -0.30195 | -0.0073792 | 0.0073792 | houston | N | 0.0073792 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.1762 | houston | -0.31777 | -0.1384 | -0.30185 | -0.0072792 | 0.0072792 | houston | N | 0.0072792 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.17617 | houston | -0.31774 | -0.13838 | -0.30183 | -0.0072522 | 0.0072522 | houston | N | 0.0072522 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.17629 | houston | -0.31786 | -0.13849 | -0.30194 | -0.0073702 | 0.0073702 | houston | N | 0.0073702 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.17631 | houston | -0.31788 | -0.13852 | -0.30197 | -0.0073982 | 0.0073982 | houston | N | 0.0073982 | 0
48855 | SRB_GT21 | B2 | 12 | -0.17615 | houston | -0.31772 | -0.13836 | -0.30181 | -0.0072332 | 0.0072332 | houston | N | 0.0072332 | 0
48855 | SRB_GT21 | MB | 18 | -0.17615 | houston | -0.31772 | -0.13836 | -0.30181 | -0.0072332 | 0.0072332 | houston | N | 0.0072332 | 0
48865 | TECO_GT1 | 1 | 50 | -0.16925 | houston | -0.31082 | -0.13145 | -0.2949 | -0.00032915 | 0.00032915 | houston | N | 0.00032915 | 0
48873 | THW_ST3_ | 3 | 104 | -0.1791 | houston | -0.32067 | -0.14131 | -0.30476 | -0.010185 | 0.010185 | houston | N | 0.010185 | 0
48874 | THW_ST4_ | 4 | 104 | -0.1791 | houston | -0.32067 | -0.14131 | -0.30476 | -0.010185 | 0.010185 | houston | N | 0.010185 | 0
48875 | THW_3132 | A | 54 | -0.1791 | houston | -0.32067 | -0.14131 | -0.30476 | -0.010185 | 0.010185 | houston | N | 0.010185 | 0
48875 | THW_3132 | B | 53 | -0.1791 | houston | -0.32067 | -0.14131 | -0.30476 | -0.010185 | 0.010185 | houston | N | 0.010185 | 0
48877 | THW_3334 | C | 54 | -0.1791 | houston | -0.32067 | -0.14131 | -0.30476 | -0.010185 | 0.010185 | houston | N | 0.010185 | 0
48877 | THW_3334 | D | 57 | -0.1791 | houston | -0.32067 | -0.14131 | -0.30476 | -0.010185 | 0.010185 | houston | N | 0.010185 | 0
48879 | THW_4142 | E | 54 | -0.1791 | houston | -0.32067 | -0.14131 | -0.30476 | -0.010185 | 0.010185 | houston | N | 0.010185 | 0
48879 | THW_4142 | F | 54 | -0.1791 | houston | -0.32067 | -0.14131 | -0.30476 | -0.010185 | 0.010185 | houston | N | 0.010185 | 0
48881 | THW_4344 | G | 58 | -0.1791 | houston | -0.32067 | -0.14131 | -0.30476 | -0.010185 | 0.010185 | houston | N | 0.010185 | 0
48881 | THW_4344 | H | 58 | -0.1791 | houston | -0.32067 | -0.14131 | -0.30476 | -0.010185 | 0.010185 | houston | N | 0.010185 | 0
48883 | THW_GT1_ | B2 | 12 | -0.1803 | houston | -0.32186 | -0.1425 | -0.30595 | -0.011378 | 0.011378 | houston | N | 0.011378 | 0
48885 | THW_5152 | A | 56 | -0.18307 | houston | -0.32464 | -0.14527 | -0.30872 | -0.014149 | 0.014149 | houston | N | 0.014149 | 0
48885 | THW_5152 | B | 59 | -0.18307 | houston | -0.32464 | -0.14527 | -0.30872 | -0.014149 | 0.014149 | houston | N | 0.014149 | 0
48886 | THW_5354 | C | 56 | -0.18307 | houston | -0.32464 | -0.14527 | -0.30872 | -0.014149 | 0.014149 | houston | N | 0.014149 | 0
48886 | THW_5354 | D | 56 | -0.18307 | houston | -0.32464 | -0.14527 | -0.30872 | -0.014149 | 0.014149 | houston | N | 0.014149 | 0
48887 | THW_5556 | E | 59 | -0.18307 | houston | -0.32464 | -0.14527 | -0.30872 | -0.014149 | 0.014149 | houston | N | 0.014149 | 0
48887 | THW_5556 | F | 56 | -0.18307 | houston | -0.32464 | -0.14527 | -0.30872 | -0.014149 | 0.014149 | houston | N | 0.014149 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.1287 | houston | -0.27027 | -0.090904 | -0.25435 | 0.040219 | 0.040219 | houston | N | 0.040219 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.16182 | houston | -0.30339 | -0.12402 | -0.28747 | 0.0070998 | 0.0070998 | houston | N | 0.0070998 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.16182 | houston | -0.30339 | -0.12402 | -0.28747 | 0.0070998 | 0.0070998 | houston | N | 0.0070998 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.16182 | houston | -0.30339 | -0.12402 | -0.28747 | 0.0070998 | 0.0070998 | houston | N | 0.0070998 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.16182 | houston | -0.30339 | -0.12402 | -0.28747 | 0.0070998 | 0.0070998 | houston | N | 0.0070998 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.16182 | houston | -0.30339 | -0.12402 | -0.28747 | 0.0070998 | 0.0070998 | houston | N | 0.0070998 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.16019 | houston | -0.30176 | -0.1224 | -0.28585 | 0.0087278 | 0.0087278 | houston | N | 0.0087278 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.16019 | houston | -0.30176 | -0.1224 | -0.28585 | 0.0087278 | 0.0087278 | houston | N | 0.0087278 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.16019 | houston | -0.30176 | -0.1224 | -0.28585 | 0.0087278 | 0.0087278 | houston | N | 0.0087278 | 0
48929 | WAPGT21_ | B1 | 13 | -0.16182 | houston | -0.30339 | -0.12402 | -0.28747 | 0.0070998 | 0.0070998 | houston | N | 0.0070998 | 0
48940 | WARVUE_G | G1 | 12 | -0.18082 | houston | -0.32239 | -0.14303 | -0.30648 | -0.011907 | 0.011907 | houston | N | 0.011907 | 0
49803 | EXN_15GT | 1 | 34 | -0.17987 | houston | -0.32144 | -0.14208 | -0.30553 | -0.010955 | 0.010955 | houston | N | 0.010955 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.17987 | houston | -0.32144 | -0.14208 | -0.30553 | -0.010955 | 0.010955 | houston | N | 0.010955 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.17987 | houston | -0.32144 | -0.14208 | -0.30553 | -0.010955 | 0.010955 | houston | N | 0.010955 | 0
49826 | EXN938GT | 5 | 45.9 | -0.17987 | houston | -0.32144 | -0.14208 | -0.30553 | -0.010955 | 0.010955 | houston | N | 0.010955 | 0
49828 | EXN941GT | 10 | 17.7 | -0.17987 | houston | -0.32144 | -0.14208 | -0.30553 | -0.010955 | 0.010955 | houston | N | 0.010955 | 0
49829 | EXN942GT | 11 | 20.4 | -0.17987 | houston | -0.32144 | -0.14208 | -0.30553 | -0.010955 | 0.010955 | houston | N | 0.010955 | 0
49830 | EXN943GT | 12 | 19.9 | -0.17987 | houston | -0.32144 | -0.14208 | -0.30553 | -0.010955 | 0.010955 | houston | N | 0.010955 | 0
49831 | EXN944GT | 13 | 35 | -0.17987 | houston | -0.32144 | -0.14208 | -0.30553 | -0.010955 | 0.010955 | houston | N | 0.010955 | 0
49832 | EXN945GT | 9 | 18 | -0.17987 | houston | -0.32144 | -0.14208 | -0.30553 | -0.010955 | 0.010955 | houston | N | 0.010955 | 0
49837 | EXN_GT | 4 | 85.4 | -0.17987 | houston | -0.32144 | -0.14208 | -0.30553 | -0.010955 | 0.010955 | houston | N | 0.010955 | 0
49838 | EXN_14GT | 14 | 148 | -0.17987 | houston | -0.32144 | -0.14208 | -0.30553 | -0.010955 | 0.010955 | houston | N | 0.010955 | 0
49851 | DOW17000 | 37 | 62 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49858 | DOW38100 | 31 | 71.4 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49859 | DOW38200 | 33 | 45 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49860 | DOW38300 | 32 | 101 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49862 | DOW39100 | 36 | 86 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49863 | DOW39200 | 35 | 88 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49865 | DOW41000 | 41 | 50 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49866 | DOW42000 | 42 | 18 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49869 | DOW49000 | 45 | 94 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49870 | DOW61000 | 61 | 70 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49871 | DOW62000 | 62 | 63 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49872 | DOW63000 | 63 | 72 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49873 | DOW64000 | 64 | 64.8 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49876 | DOW65000 | 65 | 101 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49877 | DOW66000 | 66 | 97 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49878 | DOW67000 | 67 | 103 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49882 | DOW81000 | 81 | 76 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49884 | DOW82000 | 82 | 80 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49885 | DOW83000 | 83 | 80 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
49886 | DOW84000 | 84 | 171 | -0.14333 | houston | -0.2849 | -0.10554 | -0.26899 | 0.025586 | 0.025586 | houston | N | 0.025586 | 0
58909 | PEARSALL | 1 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58909 | PEARSALL | 2 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58909 | PEARSALL | 3 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58909 | PEARSALL | 4 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58909 | PEARSALL | 5 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58909 | PEARSALL | 6 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58919 | PEARSALL | 1 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58919 | PEARSALL | 2 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58919 | PEARSALL | 3 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58919 | PEARSALL | 4 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58919 | PEARSALL | 5 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58919 | PEARSALL | 6 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58929 | PEARSALL | 1 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58929 | PEARSALL | 2 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58929 | PEARSALL | 3 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58929 | PEARSALL | 4 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58929 | PEARSALL | 5 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58929 | PEARSALL | 6 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58949 | PEARSALL | 1 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58949 | PEARSALL | 2 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58949 | PEARSALL | 3 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58949 | PEARSALL | 4 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58949 | PEARSALL | 5 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
58949 | PEARSALL | 6 | 8.4 | -0.042723 | south | -0.18429 | -0.0049294 | -0.16838 | 0.12619 | 0.0049294 | south | N | 0.0049294 | 0
60000 | DSKY2 | 1 | 76.5 | 0.11443 | west | -0.027136 | 0.15223 | -0.011224 | 0.28335 | 0.011224 | west | N | 0.011224 | 0
60003 | KING_NE1 | 1 | 80 | 0.11755 | west | -0.024015 | 0.15535 | -0.0081026 | 0.28647 | 0.0081026 | west | N | 0.0081026 | 0
60005 | KING_SE1 | 1 | 40 | 0.11755 | west | -0.024015 | 0.15535 | -0.0081026 | 0.28647 | 0.0081026 | west | N | 0.0081026 | 0
60007 | KING_SW1 | 1 | 80 | 0.11806 | west | -0.023512 | 0.15585 | -0.0075996 | 0.28697 | 0.0075996 | west | N | 0.0075996 | 0
60016 | WOODWRD1 | 1 | 80 | 0.11744 | west | -0.024125 | 0.15524 | -0.0082126 | 0.28636 | 0.0082126 | west | N | 0.0082126 | 0
60017 | ORNNWP1 | 1 | 80 | 0.11485 | west | -0.026718 | 0.15264 | -0.010806 | 0.28377 | 0.010806 | west | N | 0.010806 | 0
60018 | DSKY1 | 1 | 84 | 0.114 | west | -0.027566 | 0.1518 | -0.011654 | 0.28292 | 0.011654 | west | N | 0.011654 | 0
60019 | KING_NW1 | 1 | 80 | 0.11806 | west | -0.023512 | 0.15585 | -0.0075996 | 0.28697 | 0.0075996 | west | N | 0.0075996 | 0
60057 | CALLAHAN | 1 | 114 | -0.033578 | south | -0.17515 | 0.0042156 | -0.15923 | 0.13534 | 0.0042156 | south | N | 0.0042156 | 0
60058 | BUFF_GAP | 1 | 120 | 0.12648 | west | -0.015094 | 0.16427 | 0.00081841 | 0.29539 | 0.00081841 | west | N | 0.00081841 | 0
60060 | CIRELLO | 1 | 233 | 0.12648 | west | -0.015094 | 0.16427 | 0.00081841 | 0.29539 | 0.00081841 | west | N | 0.00081841 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.12648 | west | -0.015094 | 0.16427 | 0.00081841 | 0.29539 | 0.00081841 | west | N | 0.00081841 | 0
60066 | H_HOLLOW | 1 | 222 | -0.033578 | south | -0.17515 | 0.0042156 | -0.15923 | 0.13534 | 0.0042156 | south | N | 0.0042156 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.033578 | south | -0.17515 | 0.0042156 | -0.15923 | 0.13534 | 0.0042156 | south | N | 0.0042156 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.033578 | south | -0.17515 | 0.0042156 | -0.15923 | 0.13534 | 0.0042156 | south | N | 0.0042156 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.033578 | south | -0.17515 | 0.0042156 | -0.15923 | 0.13534 | 0.0042156 | south | N | 0.0042156 | 0
60074 | HORSH5 | 1 | 100 | -0.033578 | south | -0.17515 | 0.0042156 | -0.15923 | 0.13534 | 0.0042156 | south | N | 0.0042156 | 0
60081 | WHRLWIND | 1 | 60 | 0.1288 | west | -0.012773 | 0.16659 | 0.0031394 | 0.29771 | 0.0031394 | west | N | 0.0031394 | 0
60201 | RIO DRCS | F | 0 | 0.031239 | south | -0.11033 | 0.069033 | -0.094418 | 0.20016 | 0.069033 | south | N | 0.069033 | 0
60202 | FRIEND_R | F | 0 | 0.10048 | west | -0.041093 | 0.13827 | -0.025181 | 0.26939 | 0.025181 | west | N | 0.025181 | 0
60203 | PRES0A | BT | 4.8 | 0.11992 | west | -0.02165 | 0.15771 | -0.0057376 | 0.28884 | 0.0057376 | west | N | 0.0057376 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.12773 | west | -0.013834 | 0.16553 | 0.0020784 | 0.29665 | 0.0020784 | west | N | 0.0020784 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.12773 | west | -0.013834 | 0.16553 | 0.0020784 | 0.29665 | 0.0020784 | west | N | 0.0020784 | 0
71057 | L_SWEETW | W1 | 135 | 0.12773 | west | -0.013834 | 0.16553 | 0.0020784 | 0.29665 | 0.0020784 | west | N | 0.0020784 | 0
71059 | L_SWEETW | W1 | 119 | 0.12773 | west | -0.013834 | 0.16553 | 0.0020784 | 0.29665 | 0.0020784 | west | N | 0.0020784 | 0
71060 | L_SWEETW | W1 | 105 | 0.12773 | west | -0.013834 | 0.16553 | 0.0020784 | 0.29665 | 0.0020784 | west | N | 0.0020784 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.12773 | west | -0.013834 | 0.16553 | 0.0020784 | 0.29665 | 0.0020784 | west | N | 0.0020784 | 0
76031 | L_GASCCR | W1 | 150 | 0.12572 | west | -0.015853 | 0.16351 | 5.9414e-05 | 0.29463 | 5.9414e-05 | west | N | 5.9414e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.12546 | west | -0.016108 | 0.16325 | -0.00019559 | 0.29438 | 0.00019559 | west | N | 0.00019559 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.12546 | west | -0.016108 | 0.16325 | -0.00019559 | 0.29438 | 0.00019559 | west | N | 0.00019559 | 0
76096 | L_CAPRSI | W1 | 186 | 0.12546 | west | -0.016108 | 0.16325 | -0.00019559 | 0.29438 | 0.00019559 | west | N | 0.00019559 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.12546 | west | -0.016108 | 0.16325 | -0.00019559 | 0.29438 | 0.00019559 | west | N | 0.00019559 | 0
80003 | MILHWYS | F | 0 | -0.068973 | south | -0.21054 | -0.031179 | -0.19463 | 0.099944 | 0.031179 | south | N | 0.031179 | 0
80010 | EPLVT1 | F | 0 | -0.017325 | south | -0.15889 | 0.020469 | -0.14298 | 0.15159 | 0.020469 | south | N | 0.020469 | 0
80012 | LAR | F | 0 | -0.051649 | south | -0.19322 | -0.013855 | -0.17731 | 0.11727 | 0.013855 | south | N | 0.013855 | 0
80051 | FORPVCM0 | 8 | 28 | -0.083144 | south | -0.22471 | -0.04535 | -0.2088 | 0.085773 | 0.04535 | south | N | 0.04535 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.083144 | south | -0.22471 | -0.04535 | -0.2088 | 0.085773 | 0.04535 | south | N | 0.04535 | 0
80053 | FOR69CG0 | 10 | 74 | -0.083144 | south | -0.22471 | -0.04535 | -0.2088 | 0.085773 | 0.04535 | south | N | 0.04535 | 0
80080 | GWINDT11 | 1 | 94 | -0.069183 | south | -0.21075 | -0.031389 | -0.19484 | 0.099734 | 0.031389 | south | N | 0.031389 | 0
80080 | GWINDT11 | 2 | 41 | -0.069183 | south | -0.21075 | -0.031389 | -0.19484 | 0.099734 | 0.031389 | south | N | 0.031389 | 0
80080 | GWINDT11 | 3 | 38 | -0.069183 | south | -0.21075 | -0.031389 | -0.19484 | 0.099734 | 0.031389 | south | N | 0.031389 | 0
80080 | GWINDT11 | 4 | 19 | -0.069183 | south | -0.21075 | -0.031389 | -0.19484 | 0.099734 | 0.031389 | south | N | 0.031389 | 0
80081 | GWINDT21 | 1 | 94 | -0.069183 | south | -0.21075 | -0.031389 | -0.19484 | 0.099734 | 0.031389 | south | N | 0.031389 | 0
80081 | GWINDT21 | 2 | 36 | -0.069183 | south | -0.21075 | -0.031389 | -0.19484 | 0.099734 | 0.031389 | south | N | 0.031389 | 0
80081 | GWINDT21 | 3 | 43 | -0.069183 | south | -0.21075 | -0.031389 | -0.19484 | 0.099734 | 0.031389 | south | N | 0.031389 | 0
80081 | GWINDT21 | 4 | 22 | -0.069183 | south | -0.21075 | -0.031389 | -0.19484 | 0.099734 | 0.031389 | south | N | 0.031389 | 0
80137 | CSDR89 | 8 | 39 | -0.078284 | south | -0.21985 | -0.04049 | -0.20394 | 0.090633 | 0.04049 | south | N | 0.04049 | 0
80137 | CSDR89 | 9 | 15 | -0.078284 | south | -0.21985 | -0.04049 | -0.20394 | 0.090633 | 0.04049 | south | N | 0.04049 | 0
80138 | CSDR7 | 7 | 7 | -0.078284 | south | -0.21985 | -0.04049 | -0.20394 | 0.090633 | 0.04049 | south | N | 0.04049 | 0
80139 | CSDR56 | 5 | 15 | -0.078284 | south | -0.21985 | -0.04049 | -0.20394 | 0.090633 | 0.04049 | south | N | 0.04049 | 0
80139 | CSDR56 | 6 | 39 | -0.078284 | south | -0.21985 | -0.04049 | -0.20394 | 0.090633 | 0.04049 | south | N | 0.04049 | 0
80140 | CSDR11 | 11 | 39 | -0.078284 | south | -0.21985 | -0.04049 | -0.20394 | 0.090633 | 0.04049 | south | N | 0.04049 | 0
80180 | PNSCALT1 | 1 | 148 | -0.069183 | south | -0.21075 | -0.031389 | -0.19484 | 0.099734 | 0.031389 | south | N | 0.031389 | 0
80180 | PNSCALT1 | 2 | 50 | -0.069183 | south | -0.21075 | -0.031389 | -0.19484 | 0.099734 | 0.031389 | south | N | 0.031389 | 0
80181 | PNSCALT2 | 1 | 55 | -0.069183 | south | -0.21075 | -0.031389 | -0.19484 | 0.099734 | 0.031389 | south | N | 0.031389 | 0
80181 | PNSCALT2 | 2 | 50 | -0.069183 | south | -0.21075 | -0.031389 | -0.19484 | 0.099734 | 0.031389 | south | N | 0.031389 | 0
80223 | REYSHR G | 1 | 12 | -0.072415 | south | -0.21398 | -0.034621 | -0.19807 | 0.096502 | 0.034621 | south | N | 0.034621 | 0
80224 | VISTRONG | 1 | 15 | -0.0768 | south | -0.21837 | -0.039006 | -0.20246 | 0.092117 | 0.039006 | south | N | 0.039006 | 0
80225 | VISTRONG | 2 | 23 | -0.0768 | south | -0.21837 | -0.039006 | -0.20246 | 0.092117 | 0.039006 | south | N | 0.039006 | 0
80226 | ALCOA G | 1 | 48 | -0.082016 | south | -0.22359 | -0.044222 | -0.20767 | 0.086901 | 0.044222 | south | N | 0.044222 | 0
80227 | AIRCO G | 1 | 8 | -0.077701 | south | -0.21927 | -0.039907 | -0.20336 | 0.091216 | 0.039907 | south | N | 0.039907 | 0
80261 | NBEC81A | 1 | 180 | -0.070808 | south | -0.21238 | -0.033014 | -0.19646 | 0.098109 | 0.033014 | south | N | 0.033014 | 0
80262 | NBEC91A | 1 | 180 | -0.070856 | south | -0.21243 | -0.033062 | -0.19651 | 0.098061 | 0.033062 | south | N | 0.033062 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.070518 | south | -0.21209 | -0.032724 | -0.19617 | 0.098399 | 0.032724 | south | N | 0.032724 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.070518 | south | -0.21209 | -0.032724 | -0.19617 | 0.098399 | 0.032724 | south | N | 0.032724 | 0
80265 | LARECU40 | 4 | 100 | -0.051644 | south | -0.19321 | -0.01385 | -0.1773 | 0.11727 | 0.01385 | south | N | 0.01385 | 0
80266 | LARECU50 | 5 | 100 | -0.051644 | south | -0.19321 | -0.01385 | -0.1773 | 0.11727 | 0.01385 | south | N | 0.01385 | 0
80291 | PAPALOTE | 1 | 25 | -0.07179 | south | -0.21336 | -0.033996 | -0.19745 | 0.097127 | 0.033996 | south | N | 0.033996 | 0
80291 | PAPALOTE | 2 | 25 | -0.07179 | south | -0.21336 | -0.033996 | -0.19745 | 0.097127 | 0.033996 | south | N | 0.033996 | 0
80291 | PAPALOTE | 3 | 25 | -0.07179 | south | -0.21336 | -0.033996 | -0.19745 | 0.097127 | 0.033996 | south | N | 0.033996 | 0
80291 | PAPALOTE | 4 | 16 | -0.07179 | south | -0.21336 | -0.033996 | -0.19745 | 0.097127 | 0.033996 | south | N | 0.033996 | 0
80294 | PAPALOTE | 5 | 25 | -0.07179 | south | -0.21336 | -0.033996 | -0.19745 | 0.097127 | 0.033996 | south | N | 0.033996 | 0
80294 | PAPALOTE | 6 | 25 | -0.07179 | south | -0.21336 | -0.033996 | -0.19745 | 0.097127 | 0.033996 | south | N | 0.033996 | 0
80294 | PAPALOTE | 7 | 25 | -0.07179 | south | -0.21336 | -0.033996 | -0.19745 | 0.097127 | 0.033996 | south | N | 0.033996 | 0
80294 | PAPALOTE | 8 | 15 | -0.07179 | south | -0.21336 | -0.033996 | -0.19745 | 0.097127 | 0.033996 | south | N | 0.033996 | 0
86104 | CID-138 | EQ | 0 | -0.051644 | south | -0.19321 | -0.01385 | -0.1773 | 0.11727 | 0.01385 | south | N | 0.01385 | 0
86105 | CID-230 | EQ | 500 | -0.051644 | south | -0.19321 | -0.01385 | -0.1773 | 0.11727 | 0.01385 | south | N | 0.01385 | 0
86106 | CUF-230 | EQ | 500 | -0.051644 | south | -0.19321 | -0.01385 | -0.1773 | 0.11727 | 0.01385 | south | N | 0.01385 | 0
86107 | CUF-138 | EQ | 0 | -0.051644 | south | -0.19321 | -0.01385 | -0.1773 | 0.11727 | 0.01385 | south | N | 0.01385 | 0
88198 | BEEVILLE | F | 0 | -0.062156 | south | -0.20373 | -0.024362 | -0.18781 | 0.10676 | 0.024362 | south | N | 0.024362 | 0
88253 | HAMILTON | F | 0 | 0.000942 | south | -0.14063 | 0.038736 | -0.12471 | 0.16986 | 0.038736 | south | N | 0.038736 | 0
88299 | ZAPATA | F | 0 | -0.058409 | south | -0.19998 | -0.020615 | -0.18407 | 0.11051 | 0.020615 | south | N | 0.020615 | 0
88508 | FALFURRI | F | 0 | -0.065456 | south | -0.20703 | -0.027662 | -0.19111 | 0.10346 | 0.027662 | south | N | 0.027662 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: 3390 JEWETT_S 345 44645 SNGLTN_3 345 1 C: GIBN_CREK - SNGLTN_75 (967-44645) & GIBN_CREK - SNGLTN_99 (967-44645) | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.16117 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 133.2876 | 827 | 0.33254 | 275.0097 | 827 | 275.0097
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.16117 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 131.9982 | 819 | 0.33254 | 272.3494 | 1646 | 547.3591
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.1551 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 95.3877 | 615 | 0.32647 | 200.7796
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.1551 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 91.0449 | 587 | 0.32647 | 191.6384 |  |  | Weighted Shift Factors
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.15359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1457 | 150.7 | 0.32496 | 48.971 |  |  | North | 0.14157
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.15359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1918 | 151 | 0.32496 | 49.0685 |  |  | Houston | -0.17137
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.15359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.2465 | 177.4 | 0.32496 | 57.6474 |  |  |  | 0.31294
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.1533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2249 | 151.5 | 0.32467 | 49.1873
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.1533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3476 | 152.3 | 0.32467 | 49.4471 |  |  | Line Rating | 1005
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.1533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.2108 | 177.5 | 0.32467 | 57.6287 |  |  | Conc Gen | 1646
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.1476 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 126.1954 | 855 | 0.31897 | 272.7159 |  |  | Weighted Imp. | 547.3591
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.1476 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 126.1954 | 855 | 0.31897 | 272.7159 |  |  | PTDF | 0.33254
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.1476 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.479 | 152.3 | 0.31897 | 48.5785
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.1476 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.5823 | 153 | 0.31897 | 48.8018 |  |  | Concentration | 1.0626
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.14553 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.539 | 0 | 0.3169 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.14553 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.9194 | 0 | 0.3169 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.14553 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.1024 | 0 | 0.3169 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.14553 | north | 1 | N | N | Nnorth | Nnorth | 1 | 58.0681 | 0 | 0.3169 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.14551 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.2757 | 50 | 0.31688 | 15.8441
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.14542 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.31679 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.14489 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 113.7363 | 785 | 0.31626 | 248.2609
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.14489 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 115.1852 | 795 | 0.31626 | 251.4235
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.14489 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 113.0119 | 780 | 0.31626 | 246.6796
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.14421 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.246 | 182 | 0.31558 | 57.4352
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.14421 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 69.7972 | 484 | 0.31558 | 152.7397
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.14382 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 66.5882 | 463 | 0.31519 | 145.932
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9005 | 161 | 0.31361 | 50.4909
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3272 | 164 | 0.31361 | 51.4317
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3272 | 164 | 0.31361 | 51.4317
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 58.8869 | 414 | 0.31361 | 129.8337
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.0427 | 162 | 0.31361 | 50.8045
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9005 | 161 | 0.31361 | 50.4909
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.185 | 163 | 0.31361 | 51.1181
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 58.1758 | 409 | 0.31361 | 128.2656
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.14162 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 54.9478 | 388 | 0.31299 | 121.4389
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.14162 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 72.9333 | 515 | 0.31299 | 161.1883
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14146 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31283 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14146 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31283 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.14142 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.8285 | 20 | 0.31279 | 6.2559
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.14142 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.5356 | 25 | 0.31279 | 7.8198
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.14142 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.7984 | 41 | 0.31279 | 12.8246
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.14132 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.6528 | 40 | 0.31269 | 12.5076
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.14131 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.1639 | 79 | 0.31268 | 24.702
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.14131 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.9794 | 106 | 0.31268 | 33.1445
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.14131 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 20.632 | 146 | 0.31268 | 45.6519
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.14131 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.7399 | 76 | 0.31268 | 23.764
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.14119 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 78.7857 | 558 | 0.31256 | 174.4095
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.14119 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.7507 | 579 | 0.31256 | 180.9733
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.14119 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 114.0839 | 808 | 0.31256 | 252.55
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.1411 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.5823 | 0 | 0.31247 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.1411 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.2314 | 0 | 0.31247 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.1411 | north | 8 | N | N | Nnorth | Nnorth | 1 | 12.4731 | 0 | 0.31247 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.5683 | 160 | 0.31242 | 49.9873
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.0041 | 156 | 0.31242 | 48.7377
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.6462 | 196 | 0.31242 | 61.2345
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.0041 | 156 | 0.31242 | 48.7377
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1452 | 157 | 0.31242 | 49.0501
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.9283 | 198 | 0.31242 | 61.8593
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.14098 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 52.1611 | 370 | 0.31234 | 115.5676
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.7366 | 0 | 0.31234 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.8776 | 0 | 0.31234 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | 1 | 43.5616 | 0 | 0.31234 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.1596 | 0 | 0.31234 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.3005 | 0 | 0.31234 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | 1 | 43.7026 | 0 | 0.31234 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.14078 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 23.9321 | 170 | 0.31215 | 53.0648
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.14078 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 73.204 | 520 | 0.31215 | 162.3159
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.14062 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.625 | 0 | 0.31199 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.14062 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.625 | 0 | 0.31199 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.14061 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.5914 | 118 | 0.31197 | 36.8129
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.14061 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 16.1696 | 115 | 0.31197 | 35.877
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.14061 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 78.1764 | 556 | 0.31197 | 173.4575
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.14044 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31181 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.1402 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31157 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.13962 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.2747 | 224 | 0.31099 | 69.6613
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.13893 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.2305 | 196 | 0.3103 | 60.8188
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.13893 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.4213 | 111 | 0.3103 | 34.4433
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.13855 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.3129 | 60 | 0.30992 | 18.595
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.13855 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.7285 | 63 | 0.30992 | 19.5248
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.13807 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.8786 | 216.4 | 0.30944 | 66.9628
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.13807 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.8371 | 216.1 | 0.30944 | 66.87
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.13787 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 59.9739 | 435 | 0.30924 | 134.5194
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.13767 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 54.3785 | 395 | 0.30904 | 122.0692
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.13767 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 59.8851 | 435 | 0.30904 | 134.4306
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.13737 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.454 | 112.5 | 0.30874 | 34.733
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.13723 | north | 7 | N | N | Nnorth | Nnorth | 1 | 4.3915 | 0 | 0.3086 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.13718 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30855 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.13718 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30855 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.13718 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30855 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.13716 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30853 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.13716 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30853 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.13716 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.3317 | 17 | 0.30853 | 5.2449
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.13716 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30853 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.13716 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30853 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.13695 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.6759 | 224 | 0.30831 | 69.0625
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.13695 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.9498 | 226 | 0.30831 | 69.6792
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.13695 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.0326 | 212 | 0.30831 | 65.3628
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.13695 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.8956 | 211 | 0.30831 | 65.0544
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.13593 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 39.1478 | 288 | 0.3073 | 88.5021
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.13593 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9817 | 147 | 0.3073 | 45.1729
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.13593 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9817 | 147 | 0.3073 | 45.1729
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.13577 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30714 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.1355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.4452 | 217.3 | 0.30687 | 66.6837
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.1355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.7785 | 205 | 0.30687 | 62.9092
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.1355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 36.9116 | 272.4 | 0.30687 | 83.5925
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.13519 | north | 3 | N | N | Nnorth | Nnorth | 1 | 156.4171 | 0 | 0.30656 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.13519 | north | 3 | N | N | Nnorth | Nnorth | 1 | 156.5523 | 0 | 0.30656 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.13517 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.5741 | 204 | 0.30654 | 62.5333
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.13517 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.1686 | 201 | 0.30654 | 61.6137
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.13517 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.7104 | 242 | 0.30654 | 74.1817
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.13495 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.4776 | 48 | 0.30632 | 14.7033
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.13495 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.2077 | 46 | 0.30632 | 14.0906
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.13495 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.1696 | 105 | 0.30632 | 32.1634
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.1347 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.4247 | 18 | 0.30607 | 5.5093
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.1347 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.4247 | 18 | 0.30607 | 5.5093
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.1347 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.1188 | 38 | 0.30607 | 11.6308
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.13434 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.4035 | 70 | 0.3057 | 21.3993
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.13434 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.2692 | 69 | 0.3057 | 21.0936
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.13434 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.2692 | 69 | 0.3057 | 21.0936
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.13434 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.1348 | 68 | 0.3057 | 20.7879
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.13392 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.4981 | 168 | 0.30529 | 51.288
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.13392 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.0525 | 90 | 0.30529 | 27.4757
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13353 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6023 | 0 | 0.30489 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13353 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6023 | 0 | 0.30489 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.13338 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 16.0054 | 120 | 0.30475 | 36.5696
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13337 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6674 | 20 | 0.30474 | 6.0948
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.13337 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6674 | 20 | 0.30474 | 6.0948
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13337 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6674 | 20 | 0.30474 | 6.0948
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.13337 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2673 | 17 | 0.30474 | 5.1805
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.13324 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 48.7655 | 366 | 0.30461 | 111.4865
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.13264 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.6829 | 73 | 0.30401 | 22.1929
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.13264 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.7845 | 119 | 0.30401 | 36.1774
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.13264 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 27.1918 | 205 | 0.30401 | 62.3224
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.13264 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.5296 | 102 | 0.30401 | 31.0092
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.13264 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 12.7337 | 96 | 0.30401 | 29.1851
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1326 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 32.0887 | 242 | 0.30397 | 73.56
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.13148 | west | 4 | Y | N | Ywest | Nwest | 1 | 85.4213 | 649.7 | 0.30285 | 196.7596
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.13084 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.5884 | 165 | 0.30221 | 49.8643
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.13008 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.6991 | 236 | 0.30145 | 71.1422
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.13008 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.0308 | 400 | 0.30145 | 120.5784
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.12894 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.7366 | 60 | 0.30031 | 18.0188
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.1288 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7278 | 60 | 0.30016 | 18.0099
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12788 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.1824 | 150 | 0.29925 | 44.8878
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.12783 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.7163 | 209 | 0.2992 | 62.5324
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.12783 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.1704 | 126.5 | 0.2992 | 37.8485
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.12783 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.8294 | 249 | 0.2992 | 74.5003
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.12783 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.1823 | 197 | 0.2992 | 58.942
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7901 | 37.5 | 0.2991 | 11.2164
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.7315 | 107.5 | 0.2991 | 32.1537
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.2442 | 135 | 0.2991 | 40.379
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.2005 | 119 | 0.2991 | 35.5934
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.4122 | 105 | 0.2991 | 31.4059
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.2827 | 80.5 | 0.2991 | 24.0779
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12738 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9224 | 125 | 0.29875 | 37.3435
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12738 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9224 | 125 | 0.29875 | 37.3435
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.12727 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.0907 | 150 | 0.29864 | 44.796
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.12727 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.8544 | 101 | 0.29864 | 30.1626
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.12716 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6818 | 84 | 0.29853 | 25.0768
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.127 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.573 | 99 | 0.29837 | 29.5385
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.127 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.747 | 61 | 0.29837 | 18.2005
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.127 | west | 7 | N | N | Nwest | Nwest | 1 | 3.175 | 0 | 0.29837 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.127 | west | 7 | N | N | Nwest | Nwest | 1 | 5.8039 | 0 | 0.29837 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.127 | west | 7 | N | N | Nwest | Nwest | 1 | 5.8039 | 0 | 0.29837 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.12698 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.9043 | 141 | 0.29835 | 42.0673
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.12698 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.2377 | 120 | 0.29835 | 35.802
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.12693 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9967 | 63 | 0.2983 | 18.7929
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3742 | 66 | 0.29825 | 19.6846
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7549 | 69 | 0.29825 | 20.5793
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7549 | 69 | 0.29825 | 20.5793
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.5011 | 67 | 0.29825 | 19.9828
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.5011 | 67 | 0.29825 | 19.9828
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2473 | 65 | 0.29825 | 19.3863
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.0098 | 150 | 0.2981 | 44.7151
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.881 | 220 | 0.2981 | 65.5822
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.3464 | 200 | 0.2981 | 59.6202
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4486 | 121.9 | 0.2981 | 36.3385
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12653 | west | 8 | N | N | Nwest | Nwest | 1 | 8.8573 | 0 | 0.2979 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12653 | west | 8 | N | N | Nwest | Nwest | 1 | 9.2875 | 0 | 0.2979 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12653 | west | 8 | N | N | Nwest | Nwest | 1 | 8.9079 | 0 | 0.2979 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.7749 | 180 | 0.2979 | 53.6213
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.7749 | 180 | 0.2979 | 53.6213
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12648 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.177 | 120 | 0.29784 | 35.7413
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12648 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.4687 | 233 | 0.29784 | 69.3976
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12648 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.526 | 170.2 | 0.29784 | 50.693
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.12646 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.4542 | 225 | 0.29783 | 67.0122
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.12635 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1618 | 120 | 0.29772 | 35.726
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.12632 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1584 | 120 | 0.29769 | 35.7227
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.12594 | west | 8 | N | N | Nwest | Nwest | 1 | 3.2493 | 0 | 0.29731 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.9594 | 214.2 | 0.29723 | 63.6666
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12572 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6346 | 100.5 | 0.29709 | 29.8571
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.12572 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.8574 | 150 | 0.29708 | 44.5627
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.1257 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2903 | 58 | 0.29706 | 17.2297
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.7961 | 70 | 0.29703 | 20.7919
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.7961 | 70 | 0.29703 | 20.7919
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.6611 | 92.8 | 0.29703 | 27.5641
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.0526 | 80 | 0.29703 | 23.7622
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.0526 | 80 | 0.29703 | 23.7622
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.4507 | 115 | 0.29703 | 34.1581
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.1597 | 208.2 | 0.29702 | 61.8387
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.8544 | 142.1 | 0.29702 | 42.206
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.6357 | 132.4 | 0.29702 | 39.3249
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.088 | 136 | 0.29702 | 40.3942
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.4701 | 147 | 0.29702 | 43.6613
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.3859 | 210 | 0.29702 | 62.3733
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1144 | 112.5 | 0.29683 | 33.3934
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.7564 | 149.5 | 0.29683 | 44.3761
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.3357 | 186 | 0.29683 | 55.2104
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.9114 | 214.5 | 0.29683 | 63.67
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12509 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.82556 | 6.6 | 0.29645 | 1.9566
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12509 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2904 | 34.3 | 0.29645 | 10.1684
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.12469 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.5793 | 149 | 0.29606 | 44.1132
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.12465 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.1289 | 169.5 | 0.29602 | 50.1759
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.12448 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3569 | 35 | 0.29585 | 10.3548
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.12448 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7345 | 30 | 0.29585 | 8.8756
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2119 | 66 | 0.29579 | 19.5222
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.0874 | 65 | 0.29579 | 19.2264
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3363 | 67 | 0.29579 | 19.818
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3363 | 67 | 0.29579 | 19.818
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3363 | 67 | 0.29579 | 19.818
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.12442 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29579 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.12442 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29579 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.12046 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.8069 | 0 | 0.29183 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.12046 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.8069 | 0 | 0.29183 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.11992 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.57561 | 0 | 0.29129 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11806 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4446 | 80 | 0.28943 | 23.1541
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11806 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4446 | 80 | 0.28943 | 23.1541
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.11755 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8165 | 75 | 0.28892 | 21.6692
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11755 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4043 | 80 | 0.28892 | 23.1138
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.11755 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7022 | 40 | 0.28892 | 11.5569
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11744 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3955 | 80 | 0.28881 | 23.105
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.11743 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3943 | 80 | 0.2888 | 23.1038
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.11736 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.6047 | 150 | 0.28873 | 43.3101
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.11736 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.6047 | 150 | 0.28873 | 43.3101
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.11728 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.5923 | 150 | 0.28865 | 43.2976
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.11728 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3826 | 80 | 0.28865 | 23.0921
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.11682 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.7881 | 255 | 0.28818 | 73.4872
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.11682 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 17.4056 | 149 | 0.28818 | 42.9396
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.11682 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 17.8728 | 153 | 0.28818 | 44.0923
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.11667 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28804 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.11667 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 91.8169 | 787 | 0.28804 | 226.6843
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11485 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1881 | 80 | 0.28622 | 22.8976
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.11443 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7541 | 76.5 | 0.2858 | 21.8638
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.114 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5763 | 84 | 0.28537 | 23.9712
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.1128 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28417 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.1128 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28417 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.10048 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.27184 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.090961 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.6441 | 150 | 0.26233 | 39.3495
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.031239 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.20261 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17137 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.17137 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -3.3578 | 100 | 0.13779 | 13.7791
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.23939 | north | 1 | N | N | Nnorth | Nnorth | 1 | -36.9141 | 0 | -0.068022 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.23939 | north | 1 | N | N | Nnorth | Nnorth | 1 | -37.345 | 0 | -0.068022 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.23939 | north | 1 | N | N | Nnorth | Nnorth | 1 | -37.345 | 0 | -0.068022 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.23939 | north | 1 | N | N | Nnorth | Nnorth | 1 | -90.9686 | 0 | -0.068022 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.036384 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 20.7025 | 569 | -0.10519 | -59.8505
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.036384 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 21.1391 | 581 | -0.10519 | -61.1127
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.015219 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.27394 | 0 | -0.12635 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.015219 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.27394 | 0 | -0.12635 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.015219 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22828 | 0 | -0.12635 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.013449 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18425 | 0 | -0.12812 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.006007 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1682 | 0 | -0.13556 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.006007 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1742 | 0 | -0.13556 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.005582 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.3556 | 422 | -0.13599 | -57.3867
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.004171 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.075078 | 0 | -0.1374 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.004171 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.075078 | 0 | -0.1374 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.000971 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033985 | 0 | -0.1406 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.000971 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033014 | 0 | -0.1406 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.000971 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033985 | 0 | -0.1406 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.000942 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.031086 | 0 | -0.14063 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.000942 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.02355 | 0 | -0.14063 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.000942 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14063 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14157 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14157 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14157 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14157 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14157 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14157 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14157 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14157 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.000381 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016002 | 42 | -0.14195 | -5.9619
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.000381 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016764 | 44 | -0.14195 | -6.2458
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.000381 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016764 | 44 | -0.14195 | -6.2458
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.000381 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.017907 | 47 | -0.14195 | -6.6717
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.001614 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.012912 | 0 | -0.14318 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.001614 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.012912 | 0 | -0.14318 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.001799 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.55769 | 310 | -0.14337 | -44.4442
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.001799 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.74299 | 413 | -0.14337 | -59.2111
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.19845 | 49 | -0.14562 | -7.1353
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1863 | 46 | -0.14562 | -6.6985
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1863 | 46 | -0.14562 | -6.6985
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.19035 | 47 | -0.14562 | -6.8441
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.00405 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.6237 | 154 | -0.14562 | -22.4254
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.00405 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.5994 | 148 | -0.14562 | -21.5517
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1944 | 48 | -0.14562 | -6.9897
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1944 | 48 | -0.14562 | -6.9897
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.011395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.7377 | 152.5 | -0.15296 | -23.3271
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.011395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.7036 | 149.5 | -0.15296 | -22.8682
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.011395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6505 | 232.6 | -0.15296 | -35.5795
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.012005 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5847 | 132 | -0.15357 | -20.2718
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.012005 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.6087 | 134 | -0.15357 | -20.579
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.012005 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.8776 | 323 | -0.15357 | -49.6045
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.013878 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.083268 | 0 | -0.15545 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.01409 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2262 | 158 | -0.15566 | -24.5942
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.01409 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2544 | 160 | -0.15566 | -24.9055
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.01409 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.4657 | 175 | -0.15566 | -27.2404
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.017325 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.15889 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.025354 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15212 | 0 | -0.16692 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.029849 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4925 | 50 | -0.17142 | -8.5709
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.029849 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4925 | 50 | -0.17142 | -8.5709
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.029849 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4925 | 50 | -0.17142 | -8.5709
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.029849 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4925 | 50 | -0.17142 | -8.5709
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.031703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.0983 | 223.9 | -0.17327 | -38.7957
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.031703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1332 | 225 | -0.17327 | -38.9863
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.031703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1205 | 224.6 | -0.17327 | -38.917
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.031703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1871 | 226.7 | -0.17327 | -39.2808
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.033303 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -19.449 | 584 | -0.17487 | -102.1255
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.033303 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -19.8153 | 595 | -0.17487 | -104.0491
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.033454 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -14.4856 | 433 | -0.17502 | -75.7851
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8279 | 114 | -0.17515 | -19.9668
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.4543 | 222 | -0.17515 | -38.8827
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.1784 | 184 | -0.17515 | -32.2271
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.5215 | 224 | -0.17515 | -39.233
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8615 | 115 | -0.17515 | -20.1419
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.035885 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.086124 | 0 | -0.17745 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.035885 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.086124 | 0 | -0.17745 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.035885 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10048 | 0 | -0.17745 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.036866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.235 | 142 | -0.17844 | -25.3378
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.036866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3456 | 145 | -0.17844 | -25.8731
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.036866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.5668 | 151 | -0.17844 | -26.9437
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.036866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.6911 | 290 | -0.17844 | -51.7463
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.037448 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.14979 | 0 | -0.17902 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.038701 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.092882 | 0 | -0.18027 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.038701 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.092882 | 0 | -0.18027 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1368 | 147 | -0.18332 | -26.9475
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.7611 | 138 | -0.18332 | -25.2977
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8446 | 140 | -0.18332 | -25.6643
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1368 | 147 | -0.18332 | -26.9475
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.598 | 182 | -0.18332 | -33.3636
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.2659 | 198 | -0.18332 | -36.2966
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.042851 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -17.4404 | 407 | -0.18442 | -75.0591
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.042896 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.488 | 58 | -0.18447 | -10.699
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.042896 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.8177 | 89 | -0.18447 | -16.4174
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.042896 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8874 | 44 | -0.18447 | -8.1165
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.042896 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8874 | 44 | -0.18447 | -8.1165
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.042896 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8445 | 43 | -0.18447 | -7.932
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.042896 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9303 | 45 | -0.18447 | -8.3009
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.042907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -17.6777 | 412 | -0.18448 | -76.0043
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.042907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -17.1628 | 400 | -0.18448 | -73.7906
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.042929 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.2019 | 424 | -0.1845 | -78.2273
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.042929 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.2448 | 425 | -0.1845 | -78.4118
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.043073 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.0023 | 209 | -0.18464 | -38.5903
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.043073 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.3038 | 216 | -0.18464 | -39.8828
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.043073 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9814 | 46 | -0.18464 | -8.4935
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.043073 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.0244 | 47 | -0.18464 | -8.6782
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.043073 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9814 | 46 | -0.18464 | -8.4935
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.043073 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9814 | 46 | -0.18464 | -8.4935
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.043113 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18468 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.043113 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18468 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.043113 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18468 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.044256 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8597 | 155 | -0.18583 | -28.8029
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.044256 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.5235 | 170 | -0.18583 | -31.5903
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.044256 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8597 | 155 | -0.18583 | -28.8029
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.044415 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.066 | 24 | -0.18598 | -4.4636
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.044415 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.066 | 24 | -0.18598 | -4.4636
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.044415 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.0215 | 23 | -0.18598 | -4.2776
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.045301 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -24.7343 | 546 | -0.18687 | -102.0312
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.045301 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -33.9757 | 750 | -0.18687 | -140.1528
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.048045 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.57654 | 0 | -0.18961 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.051644 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.1644 | 100 | -0.19321 | -19.3213
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.051644 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.1644 | 100 | -0.19321 | -19.3213
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.051644 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19321 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.051644 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19321 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.051644 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19321 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.051644 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19321 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.051649 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19322 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.05202 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -20.5999 | 396 | -0.19359 | -76.6614
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.058409 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19998 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.062156 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20373 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.062922 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.75506 | 0 | -0.20449 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.062922 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.69214 | 0 | -0.20449 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.062922 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.75506 | 0 | -0.20449 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.065456 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20703 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.065692 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -41.3203 | 629 | -0.20726 | -130.3674
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.067638 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.909 | 146.5 | -0.20921 | -30.6489
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.067638 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.0037 | 147.9 | -0.20921 | -30.9418
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.067638 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7014 | 173 | -0.20921 | -36.1929
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.068414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.1617 | 207 | -0.20998 | -43.4666
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.068414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.8253 | 216.7 | -0.20998 | -45.5034
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.068414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.5562 | 242 | -0.20998 | -50.816
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.068419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.8523 | 144 | -0.20999 | -30.2383
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.068419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.8523 | 144 | -0.20999 | -30.2383
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.068419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.6996 | 171 | -0.20999 | -35.908
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.068973 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.21054 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.068973 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.621 | 38 | -0.21054 | -8.0006
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.068973 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3312 | 19.3 | -0.21054 | -4.0635
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.068973 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0346 | 15 | -0.21054 | -3.1581
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.068973 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.2417 | 47 | -0.21054 | -9.8955
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.5032 | 94 | -0.21075 | -19.8107
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8365 | 41 | -0.21075 | -8.6408
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.629 | 38 | -0.21075 | -8.0086
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.3145 | 19 | -0.21075 | -4.0043
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.5032 | 94 | -0.21075 | -19.8107
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4906 | 36 | -0.21075 | -7.5871
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9749 | 43 | -0.21075 | -9.0624
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.522 | 22 | -0.21075 | -4.6366
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.2391 | 148 | -0.21075 | -31.1914
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4592 | 50 | -0.21075 | -10.5376
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8051 | 55 | -0.21075 | -11.5914
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4592 | 50 | -0.21075 | -10.5376
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.069529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0163 | 0 | -0.2111 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.070268 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.6702 | 0 | -0.21184 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.070313 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.6719 | 0 | -0.21188 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.070437 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7609 | 0 | -0.21201 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.070437 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7609 | 0 | -0.21201 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.070518 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -23.553 | 334 | -0.21209 | -70.8372
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.070518 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -23.9761 | 340 | -0.21209 | -72.1097
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.070518 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6932 | 180 | -0.21209 | -38.1757
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.070518 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6932 | 180 | -0.21209 | -38.1757
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.070808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.7454 | 180 | -0.21238 | -38.2279
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.070838 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5053 | 0 | -0.21241 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.070838 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5265 | 0 | -0.21241 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.070838 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.8382 | 0 | -0.21241 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.070856 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8076 | 336 | -0.21243 | -71.3749
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.070856 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.7541 | 180 | -0.21243 | -38.2366
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7948 | 25 | -0.21336 | -5.334
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7948 | 25 | -0.21336 | -5.334
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7948 | 25 | -0.21336 | -5.334
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1486 | 16 | -0.21336 | -3.4138
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7948 | 25 | -0.21336 | -5.334
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7948 | 25 | -0.21336 | -5.334
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7948 | 25 | -0.21336 | -5.334
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0769 | 15 | -0.21336 | -3.2004
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.4416 | 0 | -0.21398 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.0795 | 0 | -0.21398 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.2415 | 0 | -0.21398 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5002 | 0 | -0.21398 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.645 | 0 | -0.21398 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.1967 | 0 | -0.21398 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.072415 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.86898 | 0 | -0.21398 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.072768 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.4786 | 144 | -0.21434 | -30.8646
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.072768 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6804 | 188 | -0.21434 | -40.2954
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.074216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5401 | 47.7 | -0.21579 | -10.293
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.074216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7683 | 37.3 | -0.21579 | -8.0488
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.074216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4139 | 46 | -0.21579 | -9.9261
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.074216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5624 | 48 | -0.21579 | -10.3577
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.074259 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4209 | 0 | -0.21583 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.074986 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.6497 | 22 | -0.21656 | -4.7642
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.074986 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.82485 | 11 | -0.21656 | -2.3821
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.074986 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.82485 | 11 | -0.21656 | -2.3821
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.0768 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.152 | 0 | -0.21837 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.0768 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7664 | 0 | -0.21837 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.077701 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.62161 | 0 | -0.21927 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.192 | 0 | -0.21985 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.54799 | 0 | -0.21985 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0531 | 0 | -0.21985 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1743 | 0 | -0.21985 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.54799 | 0 | -0.21985 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1743 | 0 | -0.21985 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0531 | 0 | -0.21985 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0531 | 0 | -0.21985 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.082016 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.9368 | 0 | -0.22359 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.5684 | 0 | -0.22471 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.7347 | 0 | -0.22471 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.5684 | 0 | -0.22471 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.6515 | 0 | -0.22471 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.5185 | 0 | -0.22471 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0786 | 0 | -0.22471 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8246 | 0 | -0.22471 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.328 | 0 | -0.22471 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.6251 | 0 | -0.22471 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.1527 | 0 | -0.22471 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.12356 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -164.7001 | 0 | -0.26513 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.12356 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -164.0824 | 0 | -0.26513 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.4471 | 76 | -0.26587 | -20.2064
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.4471 | 76 | -0.26587 | -20.2064
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -13.0519 | 105 | -0.26587 | -27.9167
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.1985 | 74 | -0.26587 | -19.6746
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.1985 | 74 | -0.26587 | -19.6746
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -12.679 | 102 | -0.26587 | -27.1191
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.1287 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.4941 | 66 | -0.27027 | -17.8376
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.8865 | 0 | -0.2849 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.2338 | 0 | -0.2849 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.4499 | 0 | -0.2849 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.4764 | 0 | -0.2849 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.3265 | 0 | -0.2849 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.6131 | 0 | -0.2849 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.1665 | 0 | -0.2849 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.58 | 0 | -0.2849 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.4731 | 0 | -0.2849 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.0332 | 0 | -0.2849 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.0299 | 0 | -0.2849 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.3198 | 0 | -0.2849 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.2878 | 0 | -0.2849 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.4764 | 0 | -0.2849 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.9031 | 0 | -0.2849 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.7631 | 0 | -0.2849 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.8932 | 0 | -0.2849 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.4665 | 0 | -0.2849 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.4665 | 0 | -0.2849 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.5096 | 0 | -0.2849 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.14687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.4277 | 0 | -0.28844 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.14687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4687 | 0 | -0.28844 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.14969 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.615 | 0 | -0.29125 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.14969 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.615 | 0 | -0.29125 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.14969 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.8125 | 0 | -0.29125 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.14969 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.3905 | 0 | -0.29125 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.15976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.3649 | 0 | -0.30133 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.16019 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -104.283 | 651 | -0.30176 | -196.4447
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.16019 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -90.3466 | 564 | -0.30176 | -170.1917
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.16019 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -96.1134 | 600 | -0.30176 | -181.055
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.16027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.1247 | 0 | -0.30184 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.16027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.1247 | 0 | -0.30184 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.16027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -39.2671 | 0 | -0.30184 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.16126 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3217 | 0 | -0.30283 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.16182 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -26.0525 | 161 | -0.30339 | -48.8452
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.16182 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -26.8616 | 166 | -0.30339 | -50.3621
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.16182 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -40.1306 | 248 | -0.30339 | -75.2398
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.16182 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -88.3521 | 546 | -0.30339 | -165.649
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.16182 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -104.0483 | 0 | -0.30339 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.16182 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1036 | 13 | -0.30339 | -3.944
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.16702 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.7522 | 0 | -0.30859 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.16702 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.5163 | 0 | -0.30859 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.16702 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.1531 | 0 | -0.30859 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.16702 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.0361 | 0 | -0.30859 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.16702 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3447 | 0 | -0.30859 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.16702 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0107 | 0 | -0.30859 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.16705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.827 | 0 | -0.30862 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.16705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.1421 | 0 | -0.30862 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.16705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.8535 | 0 | -0.30862 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.5918 | 0 | -0.30862 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.6419 | 0 | -0.30862 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.4414 | 0 | -0.30862 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.0366 | 0 | -0.30862 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -40.7597 | 0 | -0.30862 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.16705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6819 | 0 | -0.30862 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.16925 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.4623 | 50 | -0.31082 | -15.5408
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.17091 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.31247 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.732 | 0 | -0.31445 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.1442 | 0 | -0.31445 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.0405 | 0 | -0.31445 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.4219 | 0 | -0.31445 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1091 | 0 | -0.31445 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.17365 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2873 | 0 | -0.31522 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.17365 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.4191 | 0 | -0.31522 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.17365 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2873 | 0 | -0.31522 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.17365 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2873 | 0 | -0.31522 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.0417 | 46 | -0.31639 | -14.5539
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.0417 | 46 | -0.31639 | -14.5539
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.0417 | 46 | -0.31639 | -14.5539
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.6151 | 55 | -0.31639 | -17.4014
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.6151 | 55 | -0.31639 | -17.4014
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.4403 | 54 | -0.31639 | -17.085
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.17509 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.6567 | 0 | -0.31666 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.17509 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.0069 | 0 | -0.31666 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.6375 | 0 | -0.31704 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.5671 | 0 | -0.31704 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.6373 | 0 | -0.31704 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.5496 | 0 | -0.31704 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -47.2028 | 0 | -0.31704 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.17581 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1532 | 0 | -0.31738 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.17615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1138 | 12 | -0.31772 | -3.8126
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.17615 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.31772 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.17617 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -29.7726 | 169 | -0.31774 | -53.6978
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.1762 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -29.0723 | 165 | -0.31777 | -52.4313
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.17622 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.2563 | 0 | -0.31779 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.17622 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.4717 | 0 | -0.31779 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.17629 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -37.5491 | 213 | -0.31786 | -67.7034
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.856 | 0 | -0.31787 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.2833 | 0 | -0.31787 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.1423 | 0 | -0.31787 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.5625 | 0 | -0.31787 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.9758 | 0 | -0.31787 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.17631 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -40.1998 | 228 | -0.31788 | -72.4776
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.17633 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -31.739 | 0 | -0.3179 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.17633 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.9656 | 0 | -0.3179 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.17633 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.6835 | 0 | -0.3179 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.17681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.5537 | 0 | -0.31838 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.17681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.7305 | 0 | -0.31838 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.17681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8957 | 0 | -0.31838 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.17681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3044 | 0 | -0.31838 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.17759 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.1525 | 0 | -0.31916 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.17764 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.461 | 42 | -0.31921 | -13.407
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.17764 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.461 | 42 | -0.31921 | -13.407
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.17764 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.7505 | 38 | -0.31921 | -12.1301
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.17764 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.7505 | 38 | -0.31921 | -12.1301
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.17785 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.7682 | 0 | -0.31942 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.17785 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.0099 | 0 | -0.31942 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -18.6266 | 104 | -0.32067 | -33.3498
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -18.6266 | 104 | -0.32067 | -33.3498
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.6715 | 54 | -0.32067 | -17.3163
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.4924 | 53 | -0.32067 | -16.9956
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.6715 | 54 | -0.32067 | -17.3163
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.2088 | 57 | -0.32067 | -18.2783
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.6715 | 54 | -0.32067 | -17.3163
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.6715 | 54 | -0.32067 | -17.3163
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.3879 | 58 | -0.32067 | -18.5989
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.3879 | 58 | -0.32067 | -18.5989
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.17955 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -131.9722 | 735 | -0.32112 | -236.0257
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1156 | 0 | -0.32144 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2416 | 0 | -0.32144 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8818 | 0 | -0.32144 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2561 | 0 | -0.32144 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1837 | 0 | -0.32144 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6694 | 0 | -0.32144 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5795 | 0 | -0.32144 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2955 | 0 | -0.32144 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2377 | 0 | -0.32144 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.3611 | 0 | -0.32144 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.6211 | 0 | -0.32144 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.1803 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1635 | 12 | -0.32186 | -3.8624
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.18079 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90396 | 0 | -0.32236 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.18079 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7966 | 0 | -0.32236 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.7522 | 0 | -0.32237 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.933 | 0 | -0.32237 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.6562 | 0 | -0.32237 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.3906 | 0 | -0.32237 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.2098 | 0 | -0.32237 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -18.8035 | 0 | -0.32237 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6674 | 0 | -0.32237 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.18082 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -2.1699 | 12 | -0.32239 | -3.8687
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.18086 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -134.3775 | 743 | -0.32243 | -239.5635
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.1811 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.433 | 0 | -0.32267 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.18125 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -31.175 | 172 | -0.32282 | -55.5249
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.18125 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -31.175 | 172 | -0.32282 | -55.5249
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.18125 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -31.175 | 172 | -0.32282 | -55.5249
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.18217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -29.6576 | 0 | -0.32374 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.18217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -29.4026 | 0 | -0.32374 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.18217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -28.9471 | 0 | -0.32374 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.18217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -49.0407 | 0 | -0.32374 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.1825 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -72.6354 | 398 | -0.32407 | -128.98
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.2517 | 56 | -0.32464 | -18.1796
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.8009 | 59 | -0.32464 | -19.1535
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.2517 | 56 | -0.32464 | -18.1796
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.2517 | 56 | -0.32464 | -18.1796
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.8009 | 59 | -0.32464 | -19.1535
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.2517 | 56 | -0.32464 | -18.1796
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.18849 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -32.6089 | 0 | -0.33006 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.18849 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.4046 | 0 | -0.33006 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.18849 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.0276 | 0 | -0.33006 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.18849 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.0276 | 0 | -0.33006 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.18849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.5355 | 0 | -0.33006 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: 3390 JEWETT_S 345 44645 SNGLTN_3 345 1 C: GIBN_CREK - SNGLTN_75 (967-44645) & GIBN_CREK - SNGLTN_99 (967-44645) | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.18849 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -32.6089 | 0 | -0.33006 | 0 | 0 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.18849 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.4046 | 0 | -0.33006 | 0 | 0 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.18849 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.0276 | 0 | -0.33006 | 0 | 0 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.18849 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.0276 | 0 | -0.33006 | 0 | 0 | 0 | Weighted Shift Factors
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.18849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.5355 | 0 | -0.33006 | 0 | 0 | 0 | North | 0.14157
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.2517 | 56 | -0.32464 | -18.1796 | 56 | 18.1796 | Houston | -0.17137
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.8009 | 59 | -0.32464 | -19.1535 | 115 | 37.3331 |  | 0.31294
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.2517 | 56 | -0.32464 | -18.1796 | 171 | 55.5127
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.2517 | 56 | -0.32464 | -18.1796 | 227 | 73.6922 | Line Rating | 1005
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.8009 | 59 | -0.32464 | -19.1535 | 286 | 92.8457 | Conc Gen | 1999
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.18307 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -10.2517 | 56 | -0.32464 | -18.1796 | 342 | 111.0253 | Weighted Imp. | 646.1437
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.1825 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -72.6354 | 398 | -0.32407 | -128.98 | 740 | 240.0053 | PTDF | 0.32323
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.18217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -29.6576 | 0 | -0.32374 | 0 | 740 | 240.0053
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.18217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -29.4026 | 0 | -0.32374 | 0 | 740 | 240.0053 | Concentration | 1.0329
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.18217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -28.9471 | 0 | -0.32374 | 0 | 740 | 240.0053
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.18217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -49.0407 | 0 | -0.32374 | 0 | 740 | 240.0053
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.18125 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -31.175 | 172 | -0.32282 | -55.5249 | 912 | 295.5302
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.18125 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -31.175 | 172 | -0.32282 | -55.5249 | 1084 | 351.0552
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.18125 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -31.175 | 172 | -0.32282 | -55.5249 | 1256 | 406.5801
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.1811 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.433 | 0 | -0.32267 | 0 | 1256 | 406.5801
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.18086 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -134.3775 | 743 | -0.32243 | -239.5635 | 1999 | 646.1437
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.18082 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -2.1699 | 0 | -0.32239 | 0 | 1999 | 646.1437
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.7522 | 0 | -0.32237 | 0 | 1999 | 646.1437
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.933 | 0 | -0.32237 | 0 | 1999 | 646.1437
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.6562 | 0 | -0.32237 | 0 | 1999 | 646.1437
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.3906 | 0 | -0.32237 | 0 | 1999 | 646.1437
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.2098 | 0 | -0.32237 | 0 | 1999 | 646.1437
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -18.8035 | 0 | -0.32237 | 0 | 1999 | 646.1437
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.1808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6674 | 0 | -0.32237 | 0 | 1999 | 646.1437
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.18079 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90396 | 0 | -0.32236 | 0 | 1999 | 646.1437
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.18079 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7966 | 0 | -0.32236 | 0 | 1999 | 646.1437
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.1803 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1635 | 12 | -0.32186 | -3.8624
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1156 | 0 | -0.32144 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2416 | 0 | -0.32144 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8818 | 0 | -0.32144 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2561 | 0 | -0.32144 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1837 | 0 | -0.32144 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6694 | 0 | -0.32144 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5795 | 0 | -0.32144 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2955 | 0 | -0.32144 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2377 | 0 | -0.32144 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.3611 | 0 | -0.32144 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.17987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.6211 | 0 | -0.32144 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.17955 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -131.9722 | 735 | -0.32112 | -236.0257
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -18.6266 | 104 | -0.32067 | -33.3498
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -18.6266 | 104 | -0.32067 | -33.3498
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.6715 | 54 | -0.32067 | -17.3163
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.4924 | 53 | -0.32067 | -16.9956
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.6715 | 54 | -0.32067 | -17.3163
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.2088 | 57 | -0.32067 | -18.2783
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.6715 | 54 | -0.32067 | -17.3163
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.6715 | 54 | -0.32067 | -17.3163
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.3879 | 58 | -0.32067 | -18.5989
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.1791 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.3879 | 58 | -0.32067 | -18.5989
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.17785 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.7682 | 0 | -0.31942 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.17785 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.0099 | 0 | -0.31942 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.17764 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.461 | 42 | -0.31921 | -13.407
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.17764 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.461 | 42 | -0.31921 | -13.407
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.17764 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.7505 | 38 | -0.31921 | -12.1301
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.17764 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.7505 | 38 | -0.31921 | -12.1301
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.17759 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.1525 | 0 | -0.31916 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.17681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.5537 | 0 | -0.31838 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.17681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.7305 | 0 | -0.31838 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.17681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8957 | 0 | -0.31838 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.17681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3044 | 0 | -0.31838 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.17633 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -31.739 | 0 | -0.3179 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.17633 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.9656 | 0 | -0.3179 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.17633 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.6835 | 0 | -0.3179 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.17631 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -40.1998 | 228 | -0.31788 | -72.4776
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.2833 | 0 | -0.31787 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.1423 | 0 | -0.31787 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.5625 | 0 | -0.31787 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.9758 | 0 | -0.31787 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.1763 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.856 | 0 | -0.31787 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.17629 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -37.5491 | 213 | -0.31786 | -67.7034
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.17622 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.2563 | 0 | -0.31779 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.17622 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.4717 | 0 | -0.31779 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.1762 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -29.0723 | 165 | -0.31777 | -52.4313
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.17617 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -29.7726 | 169 | -0.31774 | -53.6978
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.17615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1138 | 12 | -0.31772 | -3.8126
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.17615 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.31772 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.17581 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1532 | 0 | -0.31738 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.6375 | 0 | -0.31704 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.5671 | 0 | -0.31704 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.6373 | 0 | -0.31704 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -27.5496 | 0 | -0.31704 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.17547 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -47.2028 | 0 | -0.31704 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.17509 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.6567 | 0 | -0.31666 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.17509 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.0069 | 0 | -0.31666 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.0417 | 46 | -0.31639 | -14.5539
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.0417 | 46 | -0.31639 | -14.5539
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.0417 | 46 | -0.31639 | -14.5539
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.6151 | 55 | -0.31639 | -17.4014
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.6151 | 55 | -0.31639 | -17.4014
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.17482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.4403 | 54 | -0.31639 | -17.085
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.17365 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2873 | 0 | -0.31522 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.17365 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.4191 | 0 | -0.31522 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.17365 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2873 | 0 | -0.31522 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.17365 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.2873 | 0 | -0.31522 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.732 | 0 | -0.31445 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.1442 | 0 | -0.31445 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -15.0405 | 0 | -0.31445 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.4219 | 0 | -0.31445 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.17288 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1091 | 0 | -0.31445 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.17091 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.31247 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.16925 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.4623 | 50 | -0.31082 | -15.5408
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.16705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.827 | 0 | -0.30862 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.16705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.1421 | 0 | -0.30862 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.16705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.8535 | 0 | -0.30862 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.5918 | 0 | -0.30862 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.6419 | 0 | -0.30862 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.4414 | 0 | -0.30862 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.0366 | 0 | -0.30862 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.16705 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -40.7597 | 0 | -0.30862 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.16705 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6819 | 0 | -0.30862 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.16702 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3447 | 0 | -0.30859 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.16702 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0107 | 0 | -0.30859 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.16702 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.7522 | 0 | -0.30859 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.16702 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.5163 | 0 | -0.30859 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.16702 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.1531 | 0 | -0.30859 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.16702 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.0361 | 0 | -0.30859 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.16182 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -26.0525 | 161 | -0.30339 | -48.8452
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.16182 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -26.8616 | 166 | -0.30339 | -50.3621
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.16182 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -40.1306 | 248 | -0.30339 | -75.2398
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.16182 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -88.3521 | 546 | -0.30339 | -165.649
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.16182 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -104.0483 | 0 | -0.30339 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.16182 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.1036 | 13 | -0.30339 | -3.944
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.16126 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3217 | 0 | -0.30283 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.16027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.1247 | 0 | -0.30184 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.16027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.1247 | 0 | -0.30184 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.16027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -39.2671 | 0 | -0.30184 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.16019 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -104.283 | 0 | -0.30176 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.16019 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -90.3466 | 0 | -0.30176 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.16019 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -96.1134 | 0 | -0.30176 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.15976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.3649 | 0 | -0.30133 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.14969 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.615 | 0 | -0.29125 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.14969 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.615 | 0 | -0.29125 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.14969 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -17.8125 | 0 | -0.29125 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.14969 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -16.3905 | 0 | -0.29125 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.14687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.4277 | 0 | -0.28844 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.14687 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4687 | 0 | -0.28844 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.8865 | 0 | -0.2849 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.2338 | 0 | -0.2849 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.4499 | 0 | -0.2849 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.4764 | 0 | -0.2849 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.3265 | 0 | -0.2849 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.6131 | 0 | -0.2849 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.1665 | 0 | -0.2849 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.58 | 0 | -0.2849 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.4731 | 0 | -0.2849 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.0332 | 0 | -0.2849 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.0299 | 0 | -0.2849 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.3198 | 0 | -0.2849 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.2878 | 0 | -0.2849 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.4764 | 0 | -0.2849 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.9031 | 0 | -0.2849 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.7631 | 0 | -0.2849 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.8932 | 0 | -0.2849 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.4665 | 0 | -0.2849 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.4665 | 0 | -0.2849 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.14333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.5096 | 0 | -0.2849 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.1287 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.4941 | 66 | -0.27027 | -17.8376
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.4471 | 76 | -0.26587 | -20.2064
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.4471 | 76 | -0.26587 | -20.2064
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -13.0519 | 105 | -0.26587 | -27.9167
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.1985 | 74 | -0.26587 | -19.6746
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.1985 | 74 | -0.26587 | -19.6746
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.1243 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -12.679 | 102 | -0.26587 | -27.1191
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.12356 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -164.7001 | 0 | -0.26513 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.12356 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -164.0824 | 0 | -0.26513 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.5684 | 0 | -0.22471 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.7347 | 0 | -0.22471 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.5684 | 0 | -0.22471 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.6515 | 0 | -0.22471 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.5185 | 0 | -0.22471 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0786 | 0 | -0.22471 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8246 | 0 | -0.22471 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.328 | 0 | -0.22471 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.6251 | 0 | -0.22471 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.083144 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.1527 | 0 | -0.22471 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.082016 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.9368 | 0 | -0.22359 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.192 | 0 | -0.21985 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.54799 | 0 | -0.21985 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0531 | 0 | -0.21985 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1743 | 0 | -0.21985 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.54799 | 0 | -0.21985 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1743 | 0 | -0.21985 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0531 | 0 | -0.21985 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.078284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0531 | 0 | -0.21985 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.077701 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.62161 | 0 | -0.21927 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.0768 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.152 | 0 | -0.21837 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.0768 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7664 | 0 | -0.21837 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.074986 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.6497 | 22 | -0.21656 | -4.7642
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.074986 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.82485 | 11 | -0.21656 | -2.3821
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.074986 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.82485 | 11 | -0.21656 | -2.3821
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.074259 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4209 | 0 | -0.21583 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.074216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5401 | 47.7 | -0.21579 | -10.293
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.074216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7683 | 37.3 | -0.21579 | -8.0488
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.074216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4139 | 46 | -0.21579 | -9.9261
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.074216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5624 | 48 | -0.21579 | -10.3577
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.072768 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.4786 | 144 | -0.21434 | -30.8646
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.072768 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6804 | 188 | -0.21434 | -40.2954
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.4416 | 0 | -0.21398 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.0795 | 0 | -0.21398 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.2415 | 0 | -0.21398 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5002 | 0 | -0.21398 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.645 | 0 | -0.21398 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.072415 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.1967 | 0 | -0.21398 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.072415 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.86898 | 0 | -0.21398 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7948 | 0 | -0.21336 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7948 | 0 | -0.21336 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7948 | 0 | -0.21336 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1486 | 0 | -0.21336 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7948 | 0 | -0.21336 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7948 | 0 | -0.21336 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7948 | 0 | -0.21336 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.07179 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0769 | 0 | -0.21336 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.070856 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8076 | 336 | -0.21243 | -71.3749
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.070856 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.7541 | 180 | -0.21243 | -38.2366
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.070838 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5053 | 0 | -0.21241 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.070838 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5265 | 0 | -0.21241 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.070838 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.8382 | 0 | -0.21241 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.070808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.7454 | 180 | -0.21238 | -38.2279
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.070518 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -23.553 | 334 | -0.21209 | -70.8372
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.070518 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -23.9761 | 340 | -0.21209 | -72.1097
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.070518 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6932 | 180 | -0.21209 | -38.1757
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.070518 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6932 | 180 | -0.21209 | -38.1757
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.070437 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7609 | 0 | -0.21201 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.070437 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7609 | 0 | -0.21201 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.070313 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.6719 | 0 | -0.21188 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.070268 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.6702 | 0 | -0.21184 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.069529 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0163 | 0 | -0.2111 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.5032 | 0 | -0.21075 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8365 | 0 | -0.21075 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.629 | 0 | -0.21075 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.3145 | 0 | -0.21075 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.5032 | 0 | -0.21075 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4906 | 0 | -0.21075 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9749 | 0 | -0.21075 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.522 | 0 | -0.21075 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.2391 | 0 | -0.21075 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4592 | 0 | -0.21075 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8051 | 0 | -0.21075 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.069183 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4592 | 0 | -0.21075 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.068973 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.621 | 38 | -0.21054 | -8.0006
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.068973 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3312 | 19.3 | -0.21054 | -4.0635
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.068973 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0346 | 15 | -0.21054 | -3.1581
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.068973 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.2417 | 47 | -0.21054 | -9.8955
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.068973 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.21054 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.068419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.8523 | 144 | -0.20999 | -30.2383
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.068419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.8523 | 144 | -0.20999 | -30.2383
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.068419 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.6996 | 171 | -0.20999 | -35.908
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.068414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.1617 | 207 | -0.20998 | -43.4666
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.068414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.8253 | 216.7 | -0.20998 | -45.5034
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.068414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.5562 | 242 | -0.20998 | -50.816
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.067638 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.909 | 146.5 | -0.20921 | -30.6489
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.067638 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.0037 | 147.9 | -0.20921 | -30.9418
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.067638 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7014 | 173 | -0.20921 | -36.1929
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.065692 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -41.3203 | 0 | -0.20726 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.065456 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20703 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.062922 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.75506 | 0 | -0.20449 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.062922 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.69214 | 0 | -0.20449 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.062922 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.75506 | 0 | -0.20449 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.062156 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20373 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.058409 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19998 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.05202 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -20.5999 | 0 | -0.19359 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.051649 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19322 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.051644 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.1644 | 100 | -0.19321 | -19.3213
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.051644 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.1644 | 100 | -0.19321 | -19.3213
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.051644 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19321 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.051644 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19321 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.051644 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19321 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.051644 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19321 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.048045 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.57654 | 0 | -0.18961 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.045301 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -24.7343 | 0 | -0.18687 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.045301 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -33.9757 | 0 | -0.18687 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.044415 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.066 | 24 | -0.18598 | -4.4636
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.044415 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.066 | 24 | -0.18598 | -4.4636
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.044415 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.0215 | 23 | -0.18598 | -4.2776
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.044256 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8597 | 155 | -0.18583 | -28.8029
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.044256 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.5235 | 170 | -0.18583 | -31.5903
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.044256 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8597 | 155 | -0.18583 | -28.8029
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.043113 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18468 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.043113 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18468 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.043113 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18468 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.043073 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.0023 | 209 | -0.18464 | -38.5903
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.043073 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.3038 | 216 | -0.18464 | -39.8828
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.043073 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9814 | 46 | -0.18464 | -8.4935
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.043073 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.0244 | 47 | -0.18464 | -8.6782
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.043073 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9814 | 46 | -0.18464 | -8.4935
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.043073 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9814 | 46 | -0.18464 | -8.4935
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.042929 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.2019 | 0 | -0.1845 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.042929 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.2448 | 0 | -0.1845 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.042907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -17.6777 | 412 | -0.18448 | -76.0043
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.042907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -17.1628 | 400 | -0.18448 | -73.7906
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.042896 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.488 | 58 | -0.18447 | -10.699
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.042896 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.8177 | 89 | -0.18447 | -16.4174
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.042896 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8874 | 44 | -0.18447 | -8.1165
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.042896 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8874 | 44 | -0.18447 | -8.1165
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.042896 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8445 | 43 | -0.18447 | -7.932
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.042896 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9303 | 45 | -0.18447 | -8.3009
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.042851 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -17.4404 | 407 | -0.18442 | -75.0591
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.042723 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.35887 | 8.4 | -0.18429 | -1.5481
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1368 | 147 | -0.18332 | -26.9475
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.7611 | 138 | -0.18332 | -25.2977
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8446 | 140 | -0.18332 | -25.6643
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1368 | 147 | -0.18332 | -26.9475
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.598 | 182 | -0.18332 | -33.3636
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.041747 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.2659 | 198 | -0.18332 | -36.2966
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.038701 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.092882 | 0 | -0.18027 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.038701 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.092882 | 0 | -0.18027 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.037448 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.14979 | 0 | -0.17902 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.036866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.235 | 142 | -0.17844 | -25.3378
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.036866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3456 | 145 | -0.17844 | -25.8731
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.036866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.5668 | 151 | -0.17844 | -26.9437
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.036866 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.6911 | 290 | -0.17844 | -51.7463
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.035885 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.086124 | 0 | -0.17745 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.035885 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.086124 | 0 | -0.17745 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.035885 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10048 | 0 | -0.17745 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8279 | 0 | -0.17515 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.4543 | 0 | -0.17515 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.1784 | 0 | -0.17515 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.5215 | 0 | -0.17515 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.8615 | 0 | -0.17515 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.033454 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -14.4856 | 0 | -0.17502 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.033303 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -19.449 | 0 | -0.17487 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.033303 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -19.8153 | 0 | -0.17487 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.031703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.0983 | 223.9 | -0.17327 | -38.7957
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.031703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1332 | 225 | -0.17327 | -38.9863
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.031703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1205 | 224.6 | -0.17327 | -38.917
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.031703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1871 | 226.7 | -0.17327 | -39.2808
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.029849 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4925 | 50 | -0.17142 | -8.5709
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.029849 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4925 | 50 | -0.17142 | -8.5709
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.029849 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4925 | 50 | -0.17142 | -8.5709
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.029849 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4925 | 50 | -0.17142 | -8.5709
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.025354 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15212 | 0 | -0.16692 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.017325 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.15889 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.01409 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2262 | 158 | -0.15566 | -24.5942
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.01409 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2544 | 160 | -0.15566 | -24.9055
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.01409 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.4657 | 175 | -0.15566 | -27.2404
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.013878 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.083268 | 0 | -0.15545 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.012005 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5847 | 132 | -0.15357 | -20.2718
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.012005 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.6087 | 134 | -0.15357 | -20.579
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.012005 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.8776 | 323 | -0.15357 | -49.6045
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.011395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.7377 | 152.5 | -0.15296 | -23.3271
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.011395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.7036 | 149.5 | -0.15296 | -22.8682
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.011395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6505 | 232.6 | -0.15296 | -35.5795
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.19845 | 49 | -0.14562 | -7.1353
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1863 | 46 | -0.14562 | -6.6985
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1863 | 46 | -0.14562 | -6.6985
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.19035 | 47 | -0.14562 | -6.8441
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.00405 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.6237 | 154 | -0.14562 | -22.4254
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.00405 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.5994 | 148 | -0.14562 | -21.5517
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1944 | 48 | -0.14562 | -6.9897
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.00405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1944 | 48 | -0.14562 | -6.9897
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.001799 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.55769 | 310 | -0.14337 | -44.4442
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.001799 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.74299 | 413 | -0.14337 | -59.2111
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.001614 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.012912 | 0 | -0.14318 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.001614 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.012912 | 0 | -0.14318 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.000381 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016002 | 42 | -0.14195 | -5.9619
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.000381 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016764 | 44 | -0.14195 | -6.2458
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.000381 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016764 | 44 | -0.14195 | -6.2458
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.000381 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.017907 | 47 | -0.14195 | -6.6717
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14157 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14157 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14157 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14157 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14157 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14157 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14157 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14157 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.000942 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.031086 | 0 | -0.14063 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.000942 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.02355 | 0 | -0.14063 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.000942 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14063 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.000971 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033985 | 0 | -0.1406 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.000971 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033014 | 0 | -0.1406 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.000971 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033985 | 0 | -0.1406 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.004171 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.075078 | 0 | -0.1374 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.004171 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.075078 | 0 | -0.1374 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.005582 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.3556 | 422 | -0.13599 | -57.3867
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.006007 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1682 | 0 | -0.13556 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.006007 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1742 | 0 | -0.13556 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.013449 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18425 | 0 | -0.12812 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.015219 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.27394 | 0 | -0.12635 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.015219 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.27394 | 0 | -0.12635 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.015219 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22828 | 0 | -0.12635 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.036384 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 20.7025 | 0 | -0.10519 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.036384 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 21.1391 | 0 | -0.10519 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.23939 | north | 1 | N | N | Nnorth | Nnorth | 1 | -36.9141 | 0 | -0.068022 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.23939 | north | 1 | N | N | Nnorth | Nnorth | 1 | -37.345 | 0 | -0.068022 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.23939 | north | 1 | N | N | Nnorth | Nnorth | 1 | -37.345 | 0 | -0.068022 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.23939 | north | 1 | N | N | Nnorth | Nnorth | 1 | -90.9686 | 0 | -0.068022 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.033578 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -3.3578 | 0 | 0.13779 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.17137 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.17137 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.031239 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.20261 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.090961 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.6441 | 0 | 0.26233 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.10048 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.27184 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.1128 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28417 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.1128 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28417 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.114 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5763 | 0 | 0.28537 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.11443 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7541 | 0 | 0.2858 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11485 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1881 | 0 | 0.28622 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.11667 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28804 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.11667 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 91.8169 | 787 | 0.28804 | 226.6843
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.11682 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.7881 | 255 | 0.28818 | 73.4872
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.11682 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 17.4056 | 149 | 0.28818 | 42.9396
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.11682 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 17.8728 | 153 | 0.28818 | 44.0923
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.11728 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.5923 | 150 | 0.28865 | 43.2976
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.11728 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3826 | 80 | 0.28865 | 23.0921
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.11736 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.6047 | 0 | 0.28873 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.11736 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.6047 | 0 | 0.28873 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.11743 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3943 | 0 | 0.2888 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11744 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3955 | 0 | 0.28881 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.11755 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8165 | 0 | 0.28892 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11755 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4043 | 0 | 0.28892 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.11755 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7022 | 0 | 0.28892 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11806 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4446 | 0 | 0.28943 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11806 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.4446 | 0 | 0.28943 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.11992 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.57561 | 0 | 0.29129 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.12046 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.8069 | 0 | 0.29183 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.12046 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.8069 | 0 | 0.29183 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2119 | 66 | 0.29579 | 19.5222
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.0874 | 65 | 0.29579 | 19.2264
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3363 | 67 | 0.29579 | 19.818
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3363 | 67 | 0.29579 | 19.818
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.12442 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3363 | 67 | 0.29579 | 19.818
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.12442 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29579 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.12442 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29579 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.12448 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3569 | 0 | 0.29585 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.12448 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7345 | 0 | 0.29585 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.12465 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.1289 | 0 | 0.29602 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.12469 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.5793 | 0 | 0.29606 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12509 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.82556 | 0 | 0.29645 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12509 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2904 | 0 | 0.29645 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1144 | 0 | 0.29683 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.7564 | 0 | 0.29683 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.3357 | 0 | 0.29683 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12546 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.9114 | 0 | 0.29683 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.1597 | 208.2 | 0.29702 | 61.8387
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.8544 | 142.1 | 0.29702 | 42.206
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.6357 | 132.4 | 0.29702 | 39.3249
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.088 | 136 | 0.29702 | 40.3942
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.4701 | 147 | 0.29702 | 43.6613
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.12565 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.3859 | 210 | 0.29702 | 62.3733
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.7961 | 70 | 0.29703 | 20.7919
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.7961 | 70 | 0.29703 | 20.7919
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.6611 | 92.8 | 0.29703 | 27.5641
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.0526 | 80 | 0.29703 | 23.7622
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.0526 | 80 | 0.29703 | 23.7622
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.12566 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.4507 | 115 | 0.29703 | 34.1581
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.1257 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2903 | 0 | 0.29706 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.12572 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.8574 | 0 | 0.29708 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12572 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6346 | 0 | 0.29709 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.12586 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.9594 | 0 | 0.29723 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.12594 | west | 8 | N | N | Nwest | Nwest | 1 | 3.2493 | 0 | 0.29731 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.12632 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1584 | 0 | 0.29769 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.12635 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1618 | 0 | 0.29772 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.12646 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.4542 | 0 | 0.29783 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12648 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.177 | 0 | 0.29784 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12648 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.4687 | 0 | 0.29784 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12648 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.526 | 0 | 0.29784 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.7749 | 0 | 0.2979 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12653 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.7749 | 0 | 0.2979 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12653 | west | 8 | N | N | Nwest | Nwest | 1 | 8.8573 | 0 | 0.2979 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12653 | west | 8 | N | N | Nwest | Nwest | 1 | 9.2875 | 0 | 0.2979 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12653 | west | 8 | N | N | Nwest | Nwest | 1 | 8.9079 | 0 | 0.2979 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.0098 | 0 | 0.2981 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.881 | 0 | 0.2981 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.3464 | 0 | 0.2981 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12673 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4486 | 0 | 0.2981 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3742 | 66 | 0.29825 | 19.6846
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7549 | 69 | 0.29825 | 20.5793
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7549 | 69 | 0.29825 | 20.5793
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.5011 | 67 | 0.29825 | 19.9828
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.5011 | 67 | 0.29825 | 19.9828
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.12688 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2473 | 65 | 0.29825 | 19.3863
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.12693 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9967 | 0 | 0.2983 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.12698 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.9043 | 0 | 0.29835 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.12698 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.2377 | 0 | 0.29835 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.127 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.573 | 0 | 0.29837 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.127 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.747 | 0 | 0.29837 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.127 | west | 7 | N | N | Nwest | Nwest | 1 | 3.175 | 0 | 0.29837 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.127 | west | 7 | N | N | Nwest | Nwest | 1 | 5.8039 | 0 | 0.29837 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.127 | west | 7 | N | N | Nwest | Nwest | 1 | 5.8039 | 0 | 0.29837 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.12716 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6818 | 0 | 0.29853 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.12727 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.0907 | 0 | 0.29864 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.12727 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.8544 | 0 | 0.29864 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12738 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9224 | 0 | 0.29875 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12738 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9224 | 0 | 0.29875 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.7901 | 0 | 0.2991 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.7315 | 0 | 0.2991 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.2442 | 0 | 0.2991 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.2005 | 0 | 0.2991 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.4122 | 0 | 0.2991 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.12773 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.2827 | 0 | 0.2991 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.12783 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.7163 | 0 | 0.2992 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.12783 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.1704 | 0 | 0.2992 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.12783 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.8294 | 0 | 0.2992 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.12783 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.1823 | 0 | 0.2992 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12788 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.1824 | 0 | 0.29925 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.1288 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7278 | 0 | 0.30016 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.12894 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.7366 | 0 | 0.30031 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.13008 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.0308 | 0 | 0.30145 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.13008 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.6991 | 0 | 0.30145 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.13084 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.5884 | 0 | 0.30221 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.13148 | west | 4 | Y | N | Ywest | Nwest | 1 | 85.4213 | 0 | 0.30285 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1326 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 32.0887 | 242 | 0.30397 | 73.56
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.13264 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.6829 | 73 | 0.30401 | 22.1929
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.13264 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.7845 | 119 | 0.30401 | 36.1774
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.13264 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 27.1918 | 205 | 0.30401 | 62.3224
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.13264 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.5296 | 102 | 0.30401 | 31.0092
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.13264 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 12.7337 | 96 | 0.30401 | 29.1851
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.13324 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 48.7655 | 366 | 0.30461 | 111.4865
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13337 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6674 | 20 | 0.30474 | 6.0948
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.13337 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6674 | 20 | 0.30474 | 6.0948
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13337 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.6674 | 20 | 0.30474 | 6.0948
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.13337 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2673 | 17 | 0.30474 | 5.1805
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.13338 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 16.0054 | 0 | 0.30475 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13353 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6023 | 0 | 0.30489 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13353 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6023 | 0 | 0.30489 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.13392 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.4981 | 168 | 0.30529 | 51.288
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.13392 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.0525 | 90 | 0.30529 | 27.4757
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.13434 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.4035 | 70 | 0.3057 | 21.3993
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.13434 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.2692 | 69 | 0.3057 | 21.0936
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.13434 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.2692 | 69 | 0.3057 | 21.0936
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.13434 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.1348 | 68 | 0.3057 | 20.7879
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.1347 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.4247 | 18 | 0.30607 | 5.5093
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.1347 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.4247 | 18 | 0.30607 | 5.5093
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.1347 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.1188 | 38 | 0.30607 | 11.6308
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.13495 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.4776 | 48 | 0.30632 | 14.7033
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.13495 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.2077 | 46 | 0.30632 | 14.0906
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.13495 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.1696 | 105 | 0.30632 | 32.1634
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.13517 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.5741 | 204 | 0.30654 | 62.5333
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.13517 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.1686 | 201 | 0.30654 | 61.6137
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.13517 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.7104 | 242 | 0.30654 | 74.1817
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.13519 | north | 3 | N | N | Nnorth | Nnorth | 1 | 156.4171 | 0 | 0.30656 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.13519 | north | 3 | N | N | Nnorth | Nnorth | 1 | 156.5523 | 0 | 0.30656 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.1355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.4452 | 217.3 | 0.30687 | 66.6837
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.1355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.7785 | 205 | 0.30687 | 62.9092
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.1355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 36.9116 | 272.4 | 0.30687 | 83.5925
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.13577 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30714 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.13593 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 39.1478 | 288 | 0.3073 | 88.5021
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.13593 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9817 | 147 | 0.3073 | 45.1729
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.13593 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9817 | 147 | 0.3073 | 45.1729
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.13695 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.6759 | 224 | 0.30831 | 69.0625
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.13695 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.9498 | 226 | 0.30831 | 69.6792
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.13695 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.0326 | 212 | 0.30831 | 65.3628
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.13695 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.8956 | 211 | 0.30831 | 65.0544
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.13716 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30853 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.13716 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30853 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.13716 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.3317 | 17 | 0.30853 | 5.2449
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.13716 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30853 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.13716 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30853 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.13718 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30855 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.13718 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30855 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.13718 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30855 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.13723 | north | 7 | N | N | Nnorth | Nnorth | 1 | 4.3915 | 0 | 0.3086 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.13737 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.454 | 0 | 0.30874 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.13767 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 54.3785 | 395 | 0.30904 | 122.0692
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.13767 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 59.8851 | 435 | 0.30904 | 134.4306
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.13787 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 59.9739 | 435 | 0.30924 | 134.5194
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.13807 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.8786 | 216.4 | 0.30944 | 66.9628
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.13807 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.8371 | 216.1 | 0.30944 | 66.87
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.13855 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.3129 | 60 | 0.30992 | 18.595
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.13855 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.7285 | 63 | 0.30992 | 19.5248
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.13893 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.2305 | 196 | 0.3103 | 60.8188
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.13893 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.4213 | 111 | 0.3103 | 34.4433
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.13962 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.2747 | 224 | 0.31099 | 69.6613
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.1402 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31157 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.14044 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31181 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.14061 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.5914 | 118 | 0.31197 | 36.8129
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.14061 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 16.1696 | 115 | 0.31197 | 35.877
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.14061 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 78.1764 | 556 | 0.31197 | 173.4575
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.14062 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.625 | 0 | 0.31199 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.14062 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.625 | 0 | 0.31199 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.14078 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 23.9321 | 170 | 0.31215 | 53.0648
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.14078 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 73.204 | 520 | 0.31215 | 162.3159
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.14098 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 52.1611 | 370 | 0.31234 | 115.5676
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.7366 | 0 | 0.31234 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.8776 | 0 | 0.31234 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | 1 | 43.5616 | 0 | 0.31234 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.1596 | 0 | 0.31234 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.3005 | 0 | 0.31234 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.14098 | north | 1 | N | N | Nnorth | Nnorth | 1 | 43.7026 | 0 | 0.31234 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.5683 | 160 | 0.31242 | 49.9873
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.0041 | 156 | 0.31242 | 48.7377
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.6462 | 196 | 0.31242 | 61.2345
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.0041 | 156 | 0.31242 | 48.7377
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1452 | 157 | 0.31242 | 49.0501
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.14105 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.9283 | 198 | 0.31242 | 61.8593
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.1411 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.5823 | 0 | 0.31247 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.1411 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.2314 | 0 | 0.31247 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.1411 | north | 8 | N | N | Nnorth | Nnorth | 1 | 12.4731 | 0 | 0.31247 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.14119 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 78.7857 | 0 | 0.31256 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.14119 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.7507 | 0 | 0.31256 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.14119 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 114.0839 | 0 | 0.31256 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.14131 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.1639 | 79 | 0.31268 | 24.702
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.14131 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.9794 | 106 | 0.31268 | 33.1445
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.14131 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 20.632 | 146 | 0.31268 | 45.6519
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.14131 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.7399 | 76 | 0.31268 | 23.764
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.14132 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.6528 | 40 | 0.31269 | 12.5076
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.14142 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.8285 | 20 | 0.31279 | 6.2559
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.14142 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.5356 | 25 | 0.31279 | 7.8198
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.14142 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.7984 | 41 | 0.31279 | 12.8246
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14146 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31283 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14146 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.31283 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.14162 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 54.9478 | 388 | 0.31299 | 121.4389
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.14162 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 72.9333 | 515 | 0.31299 | 161.1883
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9005 | 161 | 0.31361 | 50.4909
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3272 | 164 | 0.31361 | 51.4317
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3272 | 164 | 0.31361 | 51.4317
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 58.8869 | 414 | 0.31361 | 129.8337
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.0427 | 162 | 0.31361 | 50.8045
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9005 | 161 | 0.31361 | 50.4909
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.185 | 163 | 0.31361 | 51.1181
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.14224 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 58.1758 | 409 | 0.31361 | 128.2656
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.14382 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 66.5882 | 0 | 0.31519 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.14421 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.246 | 182 | 0.31558 | 57.4352
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.14421 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 69.7972 | 484 | 0.31558 | 152.7397
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.14489 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 113.7363 | 0 | 0.31626 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.14489 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 115.1852 | 0 | 0.31626 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.14489 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 113.0119 | 0 | 0.31626 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.14542 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.31679 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.14551 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.2757 | 0 | 0.31688 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.14553 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.539 | 0 | 0.3169 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.14553 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.9194 | 0 | 0.3169 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.14553 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.1024 | 0 | 0.3169 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.14553 | north | 1 | N | N | Nnorth | Nnorth | 1 | 58.0681 | 0 | 0.3169 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.1476 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 126.1954 | 0 | 0.31897 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.1476 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 126.1954 | 0 | 0.31897 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.1476 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.479 | 0 | 0.31897 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.1476 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.5823 | 0 | 0.31897 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.1533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2249 | 151.5 | 0.32467 | 49.1873
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.1533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3476 | 152.3 | 0.32467 | 49.4471
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.1533 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.2108 | 177.5 | 0.32467 | 57.6287
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.15359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1457 | 150.7 | 0.32496 | 48.971
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.15359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1918 | 151 | 0.32496 | 49.0685
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.15359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.2465 | 177.4 | 0.32496 | 57.6474
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.1551 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 95.3877 | 0 | 0.32647 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.1551 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 91.0449 | 0 | 0.32647 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.16117 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 133.2876 | 0 | 0.33254 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.16117 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 131.9982 | 0 | 0.33254 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
Average line rating
|  | Temp | Jewett-Singleton
|  | 20 | 1195
|  | 25 | 1195
|  | 30 | 1195
|  | 35 | 1195
|  | 40 | 1195
|  | 45 | 1195
|  | 50 | 1195
|  | 55 | 1195
|  | 60 | 1195
|  | 65 | 1195
|  | 70 | 1195
|  | 75 | 1195
|  | 80 | 1195
|  | 85 | 1195
|  | 90 | 1183
|  | 95 | 1149
|  | 100 | 1116
|  | 105 | 1080
|  | 110 | 1043
|  | 115 | 1005
|  | total | 23306
|  | avg | 1165.3