## test results
CRE test for: |  | Midtown Reit - Polk 138kV [47707-47730] | [5 empty] | FAIL
Line Rating: |  | 251
Direcction |  | North | → | Houston |  | N-H
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Midtown Reit - Polk 138kV [47707-47730]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.0045046
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.015408
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.0057635
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.016213
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Midtown Reit - Polk 138kV [47707-47730]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.0050169
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.015586
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.0057462
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.027912
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | Midtown Reit - Polk 138kV [47707-47730]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.011082
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.0012417
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.032416 | FAIL
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.0096616
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.031621
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.033675
PTDF tests
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.032416 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.032416 | -0.011082
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.078738
[6 empty] | Concentration |  | 2.429 | FAIL
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.18532
[6 empty] | Concentration |  | 5.717 | FAIL
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 316.9422
| Percent of line rating => | [6 empty] | 126.3% | FAIL
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 10.6106
[7 empty] | B1(N-S) | 0.34593 | 0.22835 | -0.11758 | 0.34593
[7 empty] | B2 (N-W) | 0.039308 | 0.026133 | -0.013175 | 0.039308
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B4 (S-W) | -0.3018 | -0.19929 | 0.10252 | -0.3018
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.21698 | 0.11854 | 0.33552 | -0.21698
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.039847 | 0.31747 | 0.35732 | -0.039847
[7 empty] | test | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B1 | 100.6%
Deployment Error Percent | [6 empty] | B2 | 11.43%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0%
[7 empty] | B4 | -87.74%
[7 empty] | B5 | -63.08%
[7 empty] | B6 | -11.58%
[7 empty] | Max Abs Error | 100.6% | FAIL

## Generation_sensitivity
Generator Sensitivities
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: Midtown Reit - Polk 138kV [47707-47730] C:Singleton - Tomball 345kV [44645-46500] & Roans - King 345kV [40600-45972] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: Midtown Reit - Polk 138kV [47707-47730] C:Singleton - Tomball 345kV [44645-46500] & Roans - King 345kV [40600-45972]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.006728 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 1.7156
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.006728 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 1.0025
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.006356 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.09534
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.006356 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.09534
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.006728 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 1.0294
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.006615 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 0.99225
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.006615 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 0.5292
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005381 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 0.39281
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005381 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 0.64034
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005381 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 1.1031
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005381 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 0.54886
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.005381 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 0.51658
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.005305 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.06366
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.005305 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.06366
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.005329 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 0.89527
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.005329 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 0.47961
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.005237 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.094266
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.005237 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.094266
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.005237 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 0.19901
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.005148 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 1.4826
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.005148 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 0.75676
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.005148 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 0.75676
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.005042 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 0.56722
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.004749 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.18996
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.00475 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 0.37525
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.00475 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 0.5035
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.00475 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 0.6935
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.00475 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 0.361
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.004961 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 0.29766
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.004961 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 0.31254
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.00474 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.0948
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.00474 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.1185
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.00474 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.19434
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.000872 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 0.40374
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 0.38524
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 0.3794
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 0.39108
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 0.39108
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 0.39108
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005837 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 0.66542
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005837 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 3.0061
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 0.37561
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 0.39268
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 0.39268
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 0.3813
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 0.3813
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 0.36991
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.005712 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 0.39984
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.005712 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 0.41926
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.005712 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 0.40212
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 0.855
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 1.254
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.005684 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 0.56272
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.005684 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 0.34672
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.005685 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 0.80158
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.005684 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 0.1421
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.005684 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 0.25976
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.005684 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 0.25976
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.005685 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 0.6822
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.005747 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 0.14827
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.00576 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 0.57888
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.005724 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 0.68688
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.005762 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 0.3342
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.005752 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 1.2321
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.005669 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 0.85035
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.005798 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.038267
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.005798 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 0.19887
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.005669 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 0.57257
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.005723 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 0.68676
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.00531 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 1.9435
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.005354 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 1.2957
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.0055 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 2.2
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.0055 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 1.298
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.005454 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 0.89991
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.005193 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 1.0594
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.005193 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 1.0438
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.005193 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 1.2567
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.005302 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.10604
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.005302 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.10604
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.005302 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.10604
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.005302 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.090134
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.005315 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 0.6378
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.00562 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 0.3372
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.004765 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 0.35737
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.004765 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 0.37929
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.004765 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 0.42123
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 0.7632
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.74412
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 0.93492
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.74412
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 0.74889
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 0.94446
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.004791 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 0.81447
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.004791 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 2.4913
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004776 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 1.7671
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.004758 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 2.655
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.004758 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 2.7549
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.004758 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 3.8445
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.005069 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 0.56773
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.005069 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 0.5069
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.005069 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 1.9161
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.005196 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 1.1291
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.005196 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 1.0652
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.005196 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 1.4154
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.005179 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 3.9878
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.005281 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 0.36967
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.005281 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.36439
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.005281 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.36439
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.005281 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 0.35911
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.005215 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 6.0338
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.005215 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 6.039
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.005141 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 1.1516
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.005141 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 1.1619
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.005063 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 1.0956
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.005063 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 1.0941
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.005141 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 1.0899
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.005141 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 1.0848
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.005051 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 1.9951
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.005035 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 2.1902
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.005051 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 2.1972
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.004839 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 0.66778
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.004819 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 0.56864
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.004819 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 0.55419
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.004819 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 2.6794
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.00473 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 1.8352
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.00473 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 2.436
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.004449 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 3.4925
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.004449 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 3.537
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.004449 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 3.4702
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.004378 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 0.7968
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.004378 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 2.119
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.004668 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 1.0456
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.004382 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 0.2191
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.004386 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.18421
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.003944 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 2.4256
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.003944 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 2.3151
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.006858 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 3.6827
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.006858 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 5.3972
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.006945 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 0.52087
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.006945 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 1.5418
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.01085 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 6.1737
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015733 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 3.2882
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015733 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 3.3983
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.015708 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 6.3932
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015733 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.72372
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015733 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 0.73945
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015733 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.72372
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.015733 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.72372
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.015708 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 6.6602
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.015708 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 6.6759
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.015724 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 0.91199
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.015724 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 1.3994
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.015724 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.69186
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.015724 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.69186
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.015724 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 0.67613
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.015724 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 0.70758
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.015716 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 6.475
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.015716 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 6.2864
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.015876 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 8.6683
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.015876 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 11.907
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.015715 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 0.95861
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.015715 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 1.4929
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.015715 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 2.373
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.015802 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 2.4493
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.015802 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 2.6863
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.015802 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 2.4493
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.01873 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.41206
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.01873 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.20603
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.01873 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.20603
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.018703 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 0.89213
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.018703 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.69762
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.018703 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 0.86034
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.018703 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 0.89774
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.017207 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.20648
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.017207 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.18928
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.015955 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.38292
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.015955 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.38292
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.015955 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.36696
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.016379 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 6.4861
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.02051 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 27.3398
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.02051 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 27.2373
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.017626 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.66979
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.017626 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.34018
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.017626 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.26439
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.017626 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 0.82842
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.006246 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 0.46845
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.005632 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 0.8448
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.005823 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 0.987
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.007817 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 1.1725
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.005688 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 0.35834
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.005415 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 3.5181
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.004803 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.19212
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.004803 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.19212
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.012708 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 5.3628
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.013334 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 1.7601
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.013334 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 1.7868
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.013334 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 4.3069
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.013597 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 2.1483
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.013597 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 2.1755
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.013597 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 2.3795
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.014454 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 8.4411
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.014454 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 8.6001
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.014469 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 6.2651
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.01491 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 3.3383
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.01491 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 3.3548
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.01491 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 3.3488
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.01491 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 3.3801
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.013027 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.10422
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.013027 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.10422
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.012155 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.21879
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.012155 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.21879
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.012155 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.18232
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.012257 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.16792
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.012771 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.22988
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.012771 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.22988
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.012913 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.45195
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.012913 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.43904
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.012913 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.45195
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.01268 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.35504
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.01268 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.36772
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.005834 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 0.20419
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.005834 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 0.17502
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.013908 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.6954
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.013908 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.6954
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.013908 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.6954
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.013908 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.6954
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.014518 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.087108
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.015218 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.036523
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.015218 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.036523
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.015218 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.04261
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.015319 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.061276
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.01543 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.037032
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.01543 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.037032
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 2.2914
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 2.1511
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 2.1823
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 2.2914
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 2.837
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 3.0864
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.013559 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 2.0677
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.013559 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 2.0271
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.013559 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 3.1538
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.015259 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 2.1668
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.015259 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 2.2126
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.015259 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 2.3041
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.015259 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 4.4251
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.013223 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.43636
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.013223 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.33058
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.017207 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.20648
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.018744 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 1.3683
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 1.5445
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 1.5836
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.53348
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.13337
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 1.5445
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 1.564
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 1.5327
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.48875
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.8993
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.017727 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 11.1503
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.018624 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 2.6819
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.018624 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 3.5013
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.016227 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.19472
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.014116 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.084696
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.017793 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 5.9784
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.017764 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 5.9332
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.017764 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 6.0398
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.017761 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.67492
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.01777 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.44425
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.01777 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.44425
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.017755 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.67469
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.017677 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.51263
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.017792 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 2.6386
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.017792 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 2.6439
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.017792 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 2.7222
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 2.8318
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 2.7422
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 1.7923
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 2.5988
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 2.6347
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 2.2762
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.017533 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 2.5686
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.017533 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 2.5931
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.017533 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 3.0332
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.017586 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 3.6403
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.017586 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 3.8109
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.017586 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 4.2558
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.017587 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 2.5325
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.017587 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 2.5325
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.017587 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 3.0074
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.013024 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 4.0374
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.013024 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 5.3789
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.012926 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.54289
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.012926 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.56874
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.012926 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.56874
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.012926 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.60752
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.64469
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.60522
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.60522
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.61838
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013157 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 2.0262
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013157 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 1.9472
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.63154
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.63154
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 0.40348
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 0.40348
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 0.5349
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 0.46112
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 0.46112
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 0.66286
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 1.2001
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 0.81906
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 0.76315
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 0.7839
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 0.84731
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 1.2104
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 1.1775
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 0.7127
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 1.4029
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 1.1099
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 1.14
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 0.69483
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.005821 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 0.86733
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.005712 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 1.0282
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.005712 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 1.0282
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.005716 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 1.2861
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.005661 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 0.70762
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.005661 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 0.70762
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 0.66864
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 0.67342
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 1.4758
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 0.68297
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 0.68774
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 1.4806
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.004883 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 0.95707
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.004883 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 0.54201
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.004821 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.75332
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.76736
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.76736
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 1.9371
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 0.758
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.75332
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 0.76268
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 1.9137
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.004745 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.004745 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004415 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 0.65342
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004415 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 0.57395
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004415 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 0.64018
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.004415 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 1.7616
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 0.60642
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 0.60762
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 0.71386
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.004039 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 0.61191
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.004039 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 0.61514
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.004039 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 0.71692
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.01085 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 6.3038
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.002412 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 2.0623
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.002412 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 2.0623
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.001693 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.054176
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.001972 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.094656
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.001972 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.090712
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001717 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.020604
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001717 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.087567
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001717 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.029189
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001717 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.037774
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.001717 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.042925
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.001972 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 0.20706
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.005674 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 0.47662
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.006254 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 0.50032
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.006257 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 0.93855
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.006257 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 0.93855
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019842 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -1.4048
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019842 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -1.3235
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019842 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -1.0516
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -3.0398
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -3.0457
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -3.0219
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -1.9048
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -4.8414
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019842 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.79368
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.019743 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -1.9802
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.019743 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -1.8341
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.019743 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -2.0276
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.019743 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -2.0138
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.019746 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.63187
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.019746 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.59238
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.04153 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 4.6098
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.04153 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 4.6098
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.04153 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 4.9421
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.04153 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 4.5475
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.002412 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 0.36735
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.002412 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 0.36904
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.19062 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -25.925
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.016897 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.5576
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.052727 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -2.2145
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.052727 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -2.2145
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.052727 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -2.0036
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.052727 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -2.0036
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.029878 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 2.1213
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.029878 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.29878
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.025815 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 4.2078
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.025815 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 4.2078
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.025815 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 6.3247
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.037351 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.4278
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.037351 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -2.2411
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.037351 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.4278
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.037351 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.4278
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.050825 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -7.5729
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.050825 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -3.3087
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -2.7783
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -2.6745
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -2.6562
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -1.6639
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.37248
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.05657 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -42.0315
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.054679 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -40.1891
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.049928 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -8.5876
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.049928 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -8.5876
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.049928 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -8.5876
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.067475 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -11.6732
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.18407 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -31.8443
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.18407 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -24.8496
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.051 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -8.3028
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.051 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -8.2314
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.051 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -8.1039
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.051 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -13.7292
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.050486 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -3.2311
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.050486 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -3.1907
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.050486 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -4.1701
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.050486 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -3.7158
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -5.8486
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -5.63
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -5.6443
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -5.6264
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -9.6402
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.068263 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.34131
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.068263 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -1.4335
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.000505 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 0.077871
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.000505 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.07878
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.000505 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.07878
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.000505 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 0.1919
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.10788 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -42.937
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -8.3177
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -8.3177
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -8.3177
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -9.945
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -9.945
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -9.7642
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.003015 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 2.4934
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.003015 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 2.4693
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.020787 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.95828
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 2.1849
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 2.1849
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 3.0186
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 2.1274
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 2.1274
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 2.9324
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.051451 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -9.2612
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.051451 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -8.1601
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.051451 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -8.0778
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.074068 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -2.5924
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.024802 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -11.3841
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -5.8379
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -5.9277
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -6.287
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -5.6583
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -5.5685
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -9.3407
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -5.299
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.067475 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -10.5261
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.067475 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -10.3911
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.067475 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -10.3911
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.067475 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -10.9309
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.092994 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -14.6001
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.051877 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -3.6833
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.051877 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -3.7351
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.051877 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -2.0232
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.051877 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -1.5563
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.045779 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -3.5708
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.045779 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -3.6623
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.050351 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.81569
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.052246 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -8.6206
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.052712 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -8.9083
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.050168 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -10.6858
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.050747 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -11.5703
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.053124 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.63749
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.053124 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.95623
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.18912 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 9.4559
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.8588
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.8588
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4844
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -1.4569
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4844
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -1.5668
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4844
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4844
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.5943
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.5943
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.042233 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.5068
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.3254
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.3964
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.3254
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.3254
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.3964
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.3254
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.031697 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 2.092
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.067054 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 10.7957
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.067054 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 11.131
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.067054 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 16.6294
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.067054 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 36.6115
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.067054 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 43.1157
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.025358 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 16.5081
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.025358 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 14.3019
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.025358 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 15.2148
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.067054 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.8717
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.062677 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.75212
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -2.1167
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -2.1603
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -2.0358
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -2.8576
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -1.1019
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -1.27
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -1.2389
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -2.179
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -1.1206
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -5.3167
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -9.214
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 1.1521
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 1.3268
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.83623
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 1.8769
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 1.5981
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 1.6353
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.92915
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.33449
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 1.7468
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 1.3008
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 1.1707
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 1.338
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 1.2042
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 1.8769
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 1.8026
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 1.914
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 1.4123
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 1.4866
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 1.4866
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 3.1777
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.13306
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.006432 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 0.49205
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.006246 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 0.49968
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.006246 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 0.24984
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.006216 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 0.49728
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.006253 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 0.50024
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.006407 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 0.51256
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.006458 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 0.54247
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.006216 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 0.49728
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 1.72
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.005716 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 0.68592
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.005716 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 1.3318
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.005716 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 0.97286
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 3.3495
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 2.7762
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 3.3797
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 1.7351
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 1.5088
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.005578 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 0.33468
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.011262 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.007263 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.006105 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.029304
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 0.2115
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 0.6063
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 0.7614
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 0.67116
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 0.5922
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 0.45402
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.005761 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 0.86415
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.005776 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 0.6498
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.005776 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 0.86351
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.005776 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 1.0743
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.005776 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 1.239
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.017626 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.014324 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.01642 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.5474
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.85238
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 1.4467
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 1.6582
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.72324
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.67032
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.33516
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 1.6582
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.63504
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 0.75852
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.38808
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.74307
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.2858
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.13337
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.2858
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.74307
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.74307
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 2.6107
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.882
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 0.9702
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.882
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.017923 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.21508
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.018917 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.28375
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.018917 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.43509
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.019439 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.93307
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.01896 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.15168
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.01779 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 3.2022
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.017793 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 3.2027
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.017764 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 3.1975
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.017764 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 3.1975
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016419 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 1.6419
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016419 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 1.6419
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.4465
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.4465
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.4465
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.28576
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.4465
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.4465
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.4465
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.2679
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016419 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016419 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 8.2095
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016419 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 8.2095
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.016419 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.017305 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.013223 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.016895 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.017392 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L: Midtown Reit - Polk 138kV [47707-47730] C:Singleton - Tomball 345kV [44645-46500] & Roans - King 345kV [40600-45972] | [7 empty] | 316.9422
Number of Bus | Name of Bus | ID | Max MW | L: Midtown Reit - Polk 138kV [47707-47730] C:Singleton - Tomball 345kV [44645-46500] & Roans - King 345kV [40600-45972] | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.006728 | north | 0.0022234 | -0.0086798 | 0.00096448 | 0.022941 | 0.00096448 | west | Y | 0.0022234 | 0.32103
239 | BOSQUESW | 1 | 149 | 0.006728 | north | 0.0022234 | -0.0086798 | 0.00096448 | 0.022941 | 0.00096448 | west | Y | 0.0022234 | 0.18758
244 | WHITNYDM | 1 | 15 | 0.006356 | north | 0.0018514 | -0.0090518 | 0.00059248 | 0.022569 | 0.00059248 | west | Y | 0.0018514 | 0.018884
245 | WHITNYDM | 2 | 15 | 0.006356 | north | 0.0018514 | -0.0090518 | 0.00059248 | 0.022569 | 0.00059248 | west | Y | 0.0018514 | 0.018884
247 | BOSQUESW | 2 | 153 | 0.006728 | north | 0.0022234 | -0.0086798 | 0.00096448 | 0.022941 | 0.00096448 | west | Y | 0.0022234 | 0.19262
251 | BOSQUESW | 2 | 150 | 0.006615 | north | 0.0021104 | -0.0087928 | 0.00085148 | 0.022828 | 0.00085148 | west | Y | 0.0021104 | 0.18884
253 | BOSQUESW | 2 | 80 | 0.006615 | north | 0.0021104 | -0.0087928 | 0.00085148 | 0.022828 | 0.00085148 | west | Y | 0.0021104 | 0.10072
332 | RWMILLER | 1 | 73 | 0.005381 | north | 0.00087643 | -0.010027 | -0.00038252 | 0.021594 | 0.00038252 | west | Y | 0.00087643 | 0.036056
333 | RWMILLER | 2 | 119 | 0.005381 | north | 0.00087643 | -0.010027 | -0.00038252 | 0.021594 | 0.00038252 | west | Y | 0.00087643 | 0.058776
334 | RWMILLER | 3 | 205 | 0.005381 | north | 0.00087643 | -0.010027 | -0.00038252 | 0.021594 | 0.00038252 | west | Y | 0.00087643 | 0.10125
335 | RWMILLER | 4 | 102 | 0.005381 | north | 0.00087643 | -0.010027 | -0.00038252 | 0.021594 | 0.00038252 | west | Y | 0.00087643 | 0.050379
336 | RWMILLER | 5 | 96 | 0.005381 | north | 0.00087643 | -0.010027 | -0.00038252 | 0.021594 | 0.00038252 | west | Y | 0.00087643 | 0.047416
344 | MRSSHPRD | 1 | 12 | 0.005305 | north | 0.00080043 | -0.010103 | -0.00045852 | 0.021518 | 0.00045852 | west | Y | 0.00080043 | 0.004103
345 | MRSSHPRD | 2 | 12 | 0.005305 | north | 0.00080043 | -0.010103 | -0.00045852 | 0.021518 | 0.00045852 | west | Y | 0.00080043 | 0.004103
366 | JNSNCNTY | 1 | 168 | 0.005329 | north | 0.00082443 | -0.010079 | -0.00043452 | 0.021542 | 0.00043452 | west | Y | 0.00082443 | 0.065505
367 | JNSNCNTY | 2 | 90 | 0.005329 | north | 0.00082443 | -0.010079 | -0.00043452 | 0.021542 | 0.00043452 | west | Y | 0.00082443 | 0.035092
503 | NTHTEXAS | 1 | 18 | 0.005237 | north | 0.00073243 | -0.010171 | -0.00052652 | 0.02145 | 0.00052652 | west | Y | 0.00073243 | 0.0037064
504 | NTHTEXAS | 2 | 18 | 0.005237 | north | 0.00073243 | -0.010171 | -0.00052652 | 0.02145 | 0.00052652 | west | Y | 0.00073243 | 0.0037064
505 | NTHTEXAS | 3 | 38 | 0.005237 | north | 0.00073243 | -0.010171 | -0.00052652 | 0.02145 | 0.00052652 | west | Y | 0.00073243 | 0.0078247
580 | JCKCNTY8 | 1 | 288 | 0.005148 | north | 0.00064343 | -0.01026 | -0.00061552 | 0.021361 | 0.00061552 | west | Y | 0.00064343 | 0.0080388
581 | JCKCNTY8 | 2 | 147 | 0.005148 | north | 0.00064343 | -0.01026 | -0.00061552 | 0.021361 | 0.00061552 | west | Y | 0.00064343 | 0.0041032
582 | JCKCNTY8 | 3 | 147 | 0.005148 | north | 0.00064343 | -0.01026 | -0.00061552 | 0.021361 | 0.00061552 | west | Y | 0.00064343 | 0.0041032
728 | WOLFRIDG | 1 | 112.5 | 0.005042 | north | 0.00053743 | -0.010366 | -0.00072152 | 0.021255 | 0.00053743 | North | N | 0.00053743 | 0
837 | NEWMAN_G | 1 | 40 | 0.004749 | north | 0.00024443 | -0.010659 | -0.0010145 | 0.020962 | 0.00024443 | North | N | 0.00024443 | 0
842 | OLINGER_ | 1 | 79 | 0.00475 | north | 0.00024543 | -0.010658 | -0.0010135 | 0.020963 | 0.00024543 | North | N | 0.00024543 | 0
843 | OLINGER_ | 1 | 106 | 0.00475 | north | 0.00024543 | -0.010658 | -0.0010135 | 0.020963 | 0.00024543 | North | N | 0.00024543 | 0
844 | OLINGER_ | 1 | 146 | 0.00475 | north | 0.00024543 | -0.010658 | -0.0010135 | 0.020963 | 0.00024543 | North | N | 0.00024543 | 0
845 | OLINGER_ | 1 | 76 | 0.00475 | north | 0.00024543 | -0.010658 | -0.0010135 | 0.020963 | 0.00024543 | North | N | 0.00024543 | 0
923 | SPENCER_ | 1 | 60 | 0.004961 | north | 0.00045643 | -0.010447 | -0.00080252 | 0.021174 | 0.00045643 | North | N | 0.00045643 | 0
924 | SPENCER_ | 1 | 63 | 0.004961 | north | 0.00045643 | -0.010447 | -0.00080252 | 0.021174 | 0.00045643 | North | N | 0.00045643 | 0
948 | STEAM1 | 1 | 20 | 0.00474 | north | 0.00023543 | -0.010668 | -0.0010235 | 0.020953 | 0.00023543 | North | N | 0.00023543 | 0
949 | STEAM2 | 1 | 25 | 0.00474 | north | 0.00023543 | -0.010668 | -0.0010235 | 0.020953 | 0.00023543 | North | N | 0.00023543 | 0
950 | STEAM3 | 1 | 41 | 0.00474 | north | 0.00023543 | -0.010668 | -0.0010235 | 0.020953 | 0.00023543 | North | N | 0.00023543 | 0
990 | GIBN_CRE | 1 | 463 | 0.000872 | north | -0.0036326 | -0.014536 | -0.0048915 | 0.017085 | 0.0036326 | North | N | 0.0036326 | 0
1002 | PBCTAGE_ | A | 66 | 0.005837 | west | 0.0013324 | -0.0095708 | 7.3482e-05 | 0.02205 | 7.3482e-05 | west | N | 7.3482e-05 | 0
1003 | PBCTBGE_ | B | 65 | 0.005837 | west | 0.0013324 | -0.0095708 | 7.3482e-05 | 0.02205 | 7.3482e-05 | west | N | 7.3482e-05 | 0
1004 | PBCTCGE_ | C | 67 | 0.005837 | west | 0.0013324 | -0.0095708 | 7.3482e-05 | 0.02205 | 7.3482e-05 | west | N | 7.3482e-05 | 0
1005 | PBCTDGE_ | D | 67 | 0.005837 | west | 0.0013324 | -0.0095708 | 7.3482e-05 | 0.02205 | 7.3482e-05 | west | N | 7.3482e-05 | 0
1006 | PBCTEGE_ | E | 67 | 0.005837 | west | 0.0013324 | -0.0095708 | 7.3482e-05 | 0.02205 | 7.3482e-05 | west | N | 7.3482e-05 | 0
1007 | PB5GEN_6 | MB | 114 | 0.005837 | west | 0.0013324 | -0.0095708 | 7.3482e-05 | 0.02205 | 7.3482e-05 | west | N | 7.3482e-05 | 0
1008 | PB6GEN_7 | MB | 515 | 0.005837 | west | 0.0013324 | -0.0095708 | 7.3482e-05 | 0.02205 | 7.3482e-05 | west | N | 7.3482e-05 | 0
1039 | MRGNAG_1 | A | 66 | 0.005691 | west | 0.0011864 | -0.0097168 | -7.2518e-05 | 0.021904 | 7.2518e-05 | west | N | 7.2518e-05 | 0
1040 | MRGNBG_2 | B | 69 | 0.005691 | west | 0.0011864 | -0.0097168 | -7.2518e-05 | 0.021904 | 7.2518e-05 | west | N | 7.2518e-05 | 0
1041 | MRGNCG_3 | C | 69 | 0.005691 | west | 0.0011864 | -0.0097168 | -7.2518e-05 | 0.021904 | 7.2518e-05 | west | N | 7.2518e-05 | 0
1042 | MRGNDG_4 | D | 67 | 0.005691 | west | 0.0011864 | -0.0097168 | -7.2518e-05 | 0.021904 | 7.2518e-05 | west | N | 7.2518e-05 | 0
1043 | MRGNEG_5 | E | 67 | 0.005691 | west | 0.0011864 | -0.0097168 | -7.2518e-05 | 0.021904 | 7.2518e-05 | west | N | 7.2518e-05 | 0
1044 | MRGNFG_6 | F | 65 | 0.005691 | west | 0.0011864 | -0.0097168 | -7.2518e-05 | 0.021904 | 7.2518e-05 | west | N | 7.2518e-05 | 0
1045 | CALENG1G | 1 | 70 | 0.005712 | west | 0.0012074 | -0.0096958 | -5.1518e-05 | 0.021925 | 5.1518e-05 | west | N | 5.1518e-05 | 0
1046 | CALENG2G | 2 | 73.4 | 0.005712 | west | 0.0012074 | -0.0096958 | -5.1518e-05 | 0.021925 | 5.1518e-05 | west | N | 5.1518e-05 | 0
1047 | CALENG3G | 3 | 70.4 | 0.005712 | west | 0.0012074 | -0.0096958 | -5.1518e-05 | 0.021925 | 5.1518e-05 | west | N | 5.1518e-05 | 0
1058 | LONGSHOR | 1 | 150 | 0.0057 | west | 0.0011954 | -0.0097078 | -6.3518e-05 | 0.021913 | 6.3518e-05 | west | N | 6.3518e-05 | 0
1058 | LONGSHOR | 2 | 220 | 0.0057 | west | 0.0011954 | -0.0097078 | -6.3518e-05 | 0.021913 | 6.3518e-05 | west | N | 6.3518e-05 | 0
1061 | CIELOGEN | 1 | 99 | 0.005684 | west | 0.0011794 | -0.0097238 | -7.9518e-05 | 0.021897 | 7.9518e-05 | west | N | 7.9518e-05 | 0
1062 | CIELOGEN | 1 | 61 | 0.005684 | west | 0.0011794 | -0.0097238 | -7.9518e-05 | 0.021897 | 7.9518e-05 | west | N | 7.9518e-05 | 0
1068 | SCURRYCW | 1 | 141 | 0.005685 | west | 0.0011804 | -0.0097228 | -7.8518e-05 | 0.021898 | 7.8518e-05 | west | N | 7.8518e-05 | 0
1069 | KINDERMG | 1 | 25 | 0.005684 | west | 0.0011794 | -0.0097238 | -7.9518e-05 | 0.021897 | 7.9518e-05 | west | N | 7.9518e-05 | 0
1070 | KINDERMG | 1 | 45.7 | 0.005684 | west | 0.0011794 | -0.0097238 | -7.9518e-05 | 0.021897 | 7.9518e-05 | west | N | 7.9518e-05 | 0
1071 | KINDERMG | 1 | 45.7 | 0.005684 | west | 0.0011794 | -0.0097238 | -7.9518e-05 | 0.021897 | 7.9518e-05 | west | N | 7.9518e-05 | 0
1073 | SCURRYCW | 2 | 120 | 0.005685 | west | 0.0011804 | -0.0097228 | -7.8518e-05 | 0.021898 | 7.8518e-05 | west | N | 7.8518e-05 | 0
1320 | BSP 1 | 1 | 25.8 | 0.005747 | west | 0.0012424 | -0.0096608 | -1.6518e-05 | 0.02196 | 1.6518e-05 | west | N | 1.6518e-05 | 0
1326 | STANTONW | 1 | 100.5 | 0.00576 | west | 0.0012554 | -0.0096478 | -3.5178e-06 | 0.021973 | 3.5178e-06 | west | N | 3.5178e-06 | 0
1327 | WILDHRSE | 1 | 120 | 0.005724 | west | 0.0012194 | -0.0096838 | -3.9518e-05 | 0.021937 | 3.9518e-05 | west | N | 3.9518e-05 | 0
1328 | OCOTILLO | 1 | 58 | 0.005762 | west | 0.0012574 | -0.0096458 | -1.5178e-06 | 0.021975 | 1.5178e-06 | west | N | 1.5178e-06 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.005752 | west | 0.0012474 | -0.0096558 | -1.1518e-05 | 0.021965 | 1.1518e-05 | west | N | 1.1518e-05 | 0
1343 | TRENTIPP | 1 | 150 | 0.005669 | west | 0.0011644 | -0.0097388 | -9.4518e-05 | 0.021882 | 9.4518e-05 | west | N | 9.4518e-05 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.005798 | west | 0.0012934 | -0.0096098 | 3.4482e-05 | 0.022011 | 3.4482e-05 | west | N | 3.4482e-05 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.005798 | west | 0.0012934 | -0.0096098 | 3.4482e-05 | 0.022011 | 3.4482e-05 | west | N | 3.4482e-05 | 0
1354 | AEPWIND_ | 1 | 101 | 0.005669 | west | 0.0011644 | -0.0097388 | -9.4518e-05 | 0.021882 | 9.4518e-05 | west | N | 9.4518e-05 | 0
1360 | GUNSIGHT | 1 | 120 | 0.005723 | west | 0.0012184 | -0.0096848 | -4.0518e-05 | 0.021936 | 4.0518e-05 | west | N | 4.0518e-05 | 0
1432 | GRHAMSES | 2 | 366 | 0.00531 | north | 0.00080543 | -0.010098 | -0.00045352 | 0.021523 | 0.00045352 | west | Y | 0.00080543 | 0.1288
1433 | GRHAMSES | 1 | 242 | 0.005354 | north | 0.00084943 | -0.010054 | -0.00040952 | 0.021567 | 0.00040952 | west | Y | 0.00084943 | 0.10646
1437 | MESQUITW | 1 | 400 | 0.0055 | west | 0.00099543 | -0.0099078 | -0.00026352 | 0.021713 | 0.00026352 | west | N | 0.00026352 | 0
1438 | MESQUITW | 1 | 236 | 0.0055 | west | 0.00099543 | -0.0099078 | -0.00026352 | 0.021713 | 0.00026352 | west | N | 0.00026352 | 0
1442 | COKFIELD | 1 | 165 | 0.005454 | west | 0.00094943 | -0.0099538 | -0.00030952 | 0.021667 | 0.00030952 | west | N | 0.00030952 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.005193 | north | 0.00068843 | -0.010215 | -0.00057052 | 0.021406 | 0.00057052 | west | Y | 0.00068843 | 0.024054
1454 | WCPWRCO_ | 2 | 201 | 0.005193 | north | 0.00068843 | -0.010215 | -0.00057052 | 0.021406 | 0.00057052 | west | Y | 0.00068843 | 0.0237
1455 | WCPWRCO_ | 3 | 242 | 0.005193 | north | 0.00068843 | -0.010215 | -0.00057052 | 0.021406 | 0.00057052 | west | Y | 0.00068843 | 0.028535
1479 | WFCOGEN_ | 1 | 20 | 0.005302 | west | 0.00079743 | -0.010106 | -0.00046152 | 0.021515 | 0.00046152 | west | N | 0.00046152 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.005302 | west | 0.00079743 | -0.010106 | -0.00046152 | 0.021515 | 0.00046152 | west | N | 0.00046152 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.005302 | west | 0.00079743 | -0.010106 | -0.00046152 | 0.021515 | 0.00046152 | west | N | 0.00046152 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.005302 | west | 0.00079743 | -0.010106 | -0.00046152 | 0.021515 | 0.00046152 | west | N | 0.00046152 | 0
1600 | BARTNWND | 1 | 120 | 0.005315 | north | 0.00081043 | -0.010093 | -0.00044852 | 0.021528 | 0.00044852 | west | Y | 0.00081043 | 0.04343
1643 | SLSTR1PP | 1 | 60 | 0.00562 | north | 0.0011154 | -0.0097878 | -0.00014352 | 0.021833 | 0.00014352 | west | Y | 0.0011154 | 0.058315
1675 | PEC_1G | 1 | 75 | 0.004765 | north | 0.00026043 | -0.010643 | -0.00099852 | 0.020978 | 0.00026043 | North | N | 0.00026043 | 0
1676 | PEC_2G | 2 | 79.6 | 0.004765 | north | 0.00026043 | -0.010643 | -0.00099852 | 0.020978 | 0.00026043 | North | N | 0.00026043 | 0
1677 | PEC_3G | 3 | 88.4 | 0.004765 | north | 0.00026043 | -0.010643 | -0.00099852 | 0.020978 | 0.00026043 | North | N | 0.00026043 | 0
1678 | LAMARPWR | 1 | 160 | 0.00477 | north | 0.00026543 | -0.010638 | -0.00099352 | 0.020983 | 0.00026543 | North | N | 0.00026543 | 0
1679 | LAMARPWR | 2 | 156 | 0.00477 | north | 0.00026543 | -0.010638 | -0.00099352 | 0.020983 | 0.00026543 | North | N | 0.00026543 | 0
1680 | LAMARPWR | 3 | 196 | 0.00477 | north | 0.00026543 | -0.010638 | -0.00099352 | 0.020983 | 0.00026543 | North | N | 0.00026543 | 0
1681 | LAMARPWR | 4 | 156 | 0.00477 | north | 0.00026543 | -0.010638 | -0.00099352 | 0.020983 | 0.00026543 | North | N | 0.00026543 | 0
1682 | LAMARPWR | 5 | 157 | 0.00477 | north | 0.00026543 | -0.010638 | -0.00099352 | 0.020983 | 0.00026543 | North | N | 0.00026543 | 0
1683 | LAMARPWR | 6 | 198 | 0.00477 | north | 0.00026543 | -0.010638 | -0.00099352 | 0.020983 | 0.00026543 | North | N | 0.00026543 | 0
1687 | VALLEY_1 | 1 | 170 | 0.004791 | north | 0.00028643 | -0.010617 | -0.00097252 | 0.021004 | 0.00028643 | North | N | 0.00028643 | 0
1688 | VALLEY_2 | 2 | 520 | 0.004791 | north | 0.00028643 | -0.010617 | -0.00097252 | 0.021004 | 0.00028643 | North | N | 0.00028643 | 0
1689 | VALLEY_3 | 3 | 370 | 0.004776 | north | 0.00027143 | -0.010632 | -0.00098752 | 0.020989 | 0.00027143 | North | N | 0.00027143 | 0
1701 | MOSES_1G | 1 | 558 | 0.004758 | north | 0.00025343 | -0.01065 | -0.0010055 | 0.020971 | 0.00025343 | North | N | 0.00025343 | 0
1702 | MOSES_2G | 2 | 579 | 0.004758 | north | 0.00025343 | -0.01065 | -0.0010055 | 0.020971 | 0.00025343 | North | N | 0.00025343 | 0
1703 | MOSES_3G | 3 | 808 | 0.004758 | north | 0.00025343 | -0.01065 | -0.0010055 | 0.020971 | 0.00025343 | North | N | 0.00025343 | 0
1861 | EAGLEMNT | MB | 112 | 0.005069 | north | 0.00056443 | -0.010339 | -0.00069452 | 0.021282 | 0.00056443 | North | N | 0.00056443 | 0
1862 | EAGLEMNT | MB | 100 | 0.005069 | north | 0.00056443 | -0.010339 | -0.00069452 | 0.021282 | 0.00056443 | North | N | 0.00056443 | 0
1863 | EAGLEMNT | MB | 378 | 0.005069 | north | 0.00056443 | -0.010339 | -0.00069452 | 0.021282 | 0.00056443 | North | N | 0.00056443 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.005196 | north | 0.00069143 | -0.010212 | -0.00056752 | 0.021409 | 0.00056752 | west | Y | 0.00069143 | 0.026926
1878 | WLFHOLW_ | 2 | 205 | 0.005196 | north | 0.00069143 | -0.010212 | -0.00056752 | 0.021409 | 0.00056752 | west | Y | 0.00069143 | 0.025402
1879 | WLFHOLW_ | 3 | 272.4 | 0.005196 | north | 0.00069143 | -0.010212 | -0.00056752 | 0.021409 | 0.00056752 | west | Y | 0.00069143 | 0.033754
1889 | DECRDOVA | MB | 770 | 0.005179 | north | 0.00067443 | -0.010229 | -0.00058452 | 0.021392 | 0.00058452 | west | Y | 0.00067443 | 0.069233
1892 | DECRDOVA | A | 70 | 0.005281 | north | 0.00077643 | -0.010127 | -0.00048252 | 0.021494 | 0.00048252 | west | Y | 0.00077643 | 0.020574
1893 | DECRDOVA | B | 69 | 0.005281 | north | 0.00077643 | -0.010127 | -0.00048252 | 0.021494 | 0.00048252 | west | Y | 0.00077643 | 0.02028
1894 | DECRDOVA | C | 69 | 0.005281 | north | 0.00077643 | -0.010127 | -0.00048252 | 0.021494 | 0.00048252 | west | Y | 0.00077643 | 0.02028
1895 | DECRDOVA | D | 68 | 0.005281 | north | 0.00077643 | -0.010127 | -0.00048252 | 0.021494 | 0.00048252 | west | Y | 0.00077643 | 0.019986
1898 | COMCHEPK | 1 | 1157 | 0.005215 | north | 0.00071043 | -0.010193 | -0.00054852 | 0.021428 | 0.00054852 | west | Y | 0.00071043 | 0.18733
1899 | COMCHEPK | 2 | 1158 | 0.005215 | north | 0.00071043 | -0.010193 | -0.00054852 | 0.021428 | 0.00054852 | west | Y | 0.00071043 | 0.18749
1937 | MDLTHELP | 5 | 224 | 0.005141 | north | 0.00063643 | -0.010267 | -0.00062252 | 0.021354 | 0.00062252 | west | Y | 0.00063643 | 0.0031164
1938 | MDLTHELP | 6 | 226 | 0.005141 | north | 0.00063643 | -0.010267 | -0.00062252 | 0.021354 | 0.00062252 | west | Y | 0.00063643 | 0.0031442
1941 | MDLTHELP | 1 | 216.4 | 0.005063 | north | 0.00055843 | -0.010345 | -0.00070052 | 0.021276 | 0.00055843 | North | N | 0.00055843 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.005063 | north | 0.00055843 | -0.010345 | -0.00070052 | 0.021276 | 0.00055843 | North | N | 0.00055843 | 0
1943 | MDLTHELP | 3 | 212 | 0.005141 | north | 0.00063643 | -0.010267 | -0.00062252 | 0.021354 | 0.00062252 | west | Y | 0.00063643 | 0.0029495
1944 | MDLTHELP | 4 | 211 | 0.005141 | north | 0.00063643 | -0.010267 | -0.00062252 | 0.021354 | 0.00062252 | west | Y | 0.00063643 | 0.0029356
1947 | HANDLEY_ | 3 | 395 | 0.005051 | north | 0.00054643 | -0.010357 | -0.00071252 | 0.021264 | 0.00054643 | North | N | 0.00054643 | 0
1948 | HANDLEY_ | 4 | 435 | 0.005035 | north | 0.00053043 | -0.010373 | -0.00072852 | 0.021248 | 0.00053043 | North | N | 0.00053043 | 0
1949 | HANDLEY_ | 5 | 435 | 0.005051 | north | 0.00054643 | -0.010357 | -0.00071252 | 0.021264 | 0.00054643 | North | N | 0.00054643 | 0
2371 | COLLIN_1 | MB | 138 | 0.004839 | north | 0.00033443 | -0.010569 | -0.00092452 | 0.021052 | 0.00033443 | North | N | 0.00033443 | 0
2413 | MTCK6_G | 6 | 118 | 0.004819 | north | 0.00031443 | -0.010589 | -0.00094452 | 0.021032 | 0.00031443 | North | N | 0.00031443 | 0
2414 | MTCK7_G | 7 | 115 | 0.004819 | north | 0.00031443 | -0.010589 | -0.00094452 | 0.021032 | 0.00031443 | North | N | 0.00031443 | 0
2417 | MTCK8_G | 8 | 556 | 0.004819 | north | 0.00031443 | -0.010589 | -0.00094452 | 0.021032 | 0.00031443 | North | N | 0.00031443 | 0
2451 | LKHB1_G | 1 | 388 | 0.00473 | north | 0.00022543 | -0.010678 | -0.0010335 | 0.020943 | 0.00022543 | North | N | 0.00022543 | 0
2452 | LKHB2_G | 2 | 515 | 0.00473 | north | 0.00022543 | -0.010678 | -0.0010335 | 0.020943 | 0.00022543 | North | N | 0.00022543 | 0
3097 | MARTLAKE | 1 | 785 | 0.004449 | north | -5.557e-05 | -0.010959 | -0.0013145 | 0.020662 | 5.557e-05 | North | N | 5.557e-05 | 0
3098 | MARTLAKE | 2 | 795 | 0.004449 | north | -5.557e-05 | -0.010959 | -0.0013145 | 0.020662 | 5.557e-05 | North | N | 5.557e-05 | 0
3099 | MARTLAKE | 3 | 780 | 0.004449 | north | -5.557e-05 | -0.010959 | -0.0013145 | 0.020662 | 5.557e-05 | North | N | 5.557e-05 | 0
3107 | STRYKER_ | 1 | 182 | 0.004378 | north | -0.00012657 | -0.01103 | -0.0013855 | 0.020591 | 0.00012657 | North | N | 0.00012657 | 0
3108 | STRYKER_ | 2 | 484 | 0.004378 | north | -0.00012657 | -0.01103 | -0.0013855 | 0.020591 | 0.00012657 | North | N | 0.00012657 | 0
3126 | TRINIDAD | 1 | 224 | 0.004668 | north | 0.00016343 | -0.01074 | -0.0010955 | 0.020881 | 0.00016343 | North | N | 0.00016343 | 0
3309 | ASPN_G | 1 | 50 | 0.004382 | north | -0.00012257 | -0.011026 | -0.0013815 | 0.020595 | 0.00012257 | North | N | 0.00012257 | 0
3348 | CHAMPION | MB | 42 | 0.004386 | north | -0.00011857 | -0.011022 | -0.0013775 | 0.020599 | 0.00011857 | North | N | 0.00011857 | 0
3381 | BBRN_1G | 1 | 615 | 0.003944 | north | -0.00056057 | -0.011464 | -0.0018195 | 0.020157 | 0.00056057 | North | N | 0.00056057 | 0
3382 | BBRN_2G | 2 | 587 | 0.003944 | north | -0.00056057 | -0.011464 | -0.0018195 | 0.020157 | 0.00056057 | North | N | 0.00056057 | 0
3403 | THOUSE_1 | MB | 537 | 0.006858 | north | 0.0023534 | -0.0085498 | 0.0010945 | 0.023071 | 0.0010945 | west | Y | 0.0023534 | 0.67606
3404 | THOUSE_2 | 2 | 787 | 0.006858 | north | 0.0023534 | -0.0085498 | 0.0010945 | 0.023071 | 0.0010945 | west | Y | 0.0023534 | 0.99079
3416 | LAKE_CRK | MB | 75 | 0.006945 | north | 0.0024404 | -0.0084628 | 0.0011815 | 0.023158 | 0.0011815 | west | Y | 0.0024404 | 0.094421
3417 | LAKE_CRK | MB | 222 | 0.006945 | north | 0.0024404 | -0.0084628 | 0.0011815 | 0.023158 | 0.0011815 | west | Y | 0.0024404 | 0.27949
3432 | SANDOW_4 | 4 | 569 | 0.01085 | south | 0.0063454 | -0.0045578 | 0.0050865 | 0.027063 | 0.0045578 | south | N | 0.0045578 | 0
5026 | BRAUNIG_ | 1 | 209 | 0.015733 | south | 0.011228 | 0.0003252 | 0.0099695 | 0.031946 | 0.0003252 | south | N | 0.0003252 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.015733 | south | 0.011228 | 0.0003252 | 0.0099695 | 0.031946 | 0.0003252 | south | N | 0.0003252 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.015708 | south | 0.011203 | 0.0003002 | 0.0099445 | 0.031921 | 0.0003002 | south | N | 0.0003002 | 0
5031 | BRA_VHBC | 1 | 46 | 0.015733 | south | 0.011228 | 0.0003252 | 0.0099695 | 0.031946 | 0.0003252 | south | N | 0.0003252 | 0
5032 | BRA_VHBC | 2 | 47 | 0.015733 | south | 0.011228 | 0.0003252 | 0.0099695 | 0.031946 | 0.0003252 | south | N | 0.0003252 | 0
5033 | BRA_VHBC | 3 | 46 | 0.015733 | south | 0.011228 | 0.0003252 | 0.0099695 | 0.031946 | 0.0003252 | south | N | 0.0003252 | 0
5034 | BRA_VHBC | 4 | 46 | 0.015733 | south | 0.011228 | 0.0003252 | 0.0099695 | 0.031946 | 0.0003252 | south | N | 0.0003252 | 0
5111 | CALAVER_ | 1 | 424 | 0.015708 | south | 0.011203 | 0.0003002 | 0.0099445 | 0.031921 | 0.0003002 | south | N | 0.0003002 | 0
5112 | CALAVER_ | 2 | 425 | 0.015708 | south | 0.011203 | 0.0003002 | 0.0099445 | 0.031921 | 0.0003002 | south | N | 0.0003002 | 0
5264 | LEON_LCP | 3 | 58 | 0.015724 | south | 0.011219 | 0.0003162 | 0.0099605 | 0.031937 | 0.0003162 | south | N | 0.0003162 | 0
5265 | LEON_LCP | 4 | 89 | 0.015724 | south | 0.011219 | 0.0003162 | 0.0099605 | 0.031937 | 0.0003162 | south | N | 0.0003162 | 0
5266 | LEON_LCP | 1 | 44 | 0.015724 | south | 0.011219 | 0.0003162 | 0.0099605 | 0.031937 | 0.0003162 | south | N | 0.0003162 | 0
5267 | LEON_LCP | 2 | 44 | 0.015724 | south | 0.011219 | 0.0003162 | 0.0099605 | 0.031937 | 0.0003162 | south | N | 0.0003162 | 0
5268 | LEON_LCP | 3 | 43 | 0.015724 | south | 0.011219 | 0.0003162 | 0.0099605 | 0.031937 | 0.0003162 | south | N | 0.0003162 | 0
5269 | LEON_LCP | 4 | 45 | 0.015724 | south | 0.011219 | 0.0003162 | 0.0099605 | 0.031937 | 0.0003162 | south | N | 0.0003162 | 0
5396 | CALAVER_ | 1 | 412 | 0.015716 | south | 0.011211 | 0.0003082 | 0.0099525 | 0.031929 | 0.0003082 | south | N | 0.0003082 | 0
5397 | CALAVER_ | 2 | 400 | 0.015716 | south | 0.011211 | 0.0003082 | 0.0099525 | 0.031929 | 0.0003082 | south | N | 0.0003082 | 0
5401 | CALAVER_ | 1 | 546 | 0.015876 | south | 0.011371 | 0.0004682 | 0.010112 | 0.032089 | 0.0004682 | south | N | 0.0004682 | 0
5402 | CALAVER_ | 2 | 750 | 0.015876 | south | 0.011371 | 0.0004682 | 0.010112 | 0.032089 | 0.0004682 | south | N | 0.0004682 | 0
5436 | TUTTL_WB | MB | 61 | 0.015715 | south | 0.01121 | 0.0003072 | 0.0099515 | 0.031928 | 0.0003072 | south | N | 0.0003072 | 0
5438 | TUTTL_WB | MB | 95 | 0.015715 | south | 0.01121 | 0.0003072 | 0.0099515 | 0.031928 | 0.0003072 | south | N | 0.0003072 | 0
5439 | TUTTL_WB | MB | 151 | 0.015715 | south | 0.01121 | 0.0003072 | 0.0099515 | 0.031928 | 0.0003072 | south | N | 0.0003072 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.015802 | south | 0.011297 | 0.0003942 | 0.010038 | 0.032015 | 0.0003942 | south | N | 0.0003942 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.015802 | south | 0.011297 | 0.0003942 | 0.010038 | 0.032015 | 0.0003942 | south | N | 0.0003942 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.015802 | south | 0.011297 | 0.0003942 | 0.010038 | 0.032015 | 0.0003942 | south | N | 0.0003942 | 0
5503 | RAYBURNG | 1 | 22 | 0.01873 | south | 0.014225 | 0.0033222 | 0.012966 | 0.034943 | 0.0033222 | south | N | 0.0033222 | 0
5505 | RAYBURNG | 1 | 11 | 0.01873 | south | 0.014225 | 0.0033222 | 0.012966 | 0.034943 | 0.0033222 | south | N | 0.0033222 | 0
5506 | RAYBURNG | 1 | 11 | 0.01873 | south | 0.014225 | 0.0033222 | 0.012966 | 0.034943 | 0.0033222 | south | N | 0.0033222 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.018703 | south | 0.014198 | 0.0032952 | 0.012939 | 0.034916 | 0.0032952 | south | N | 0.0032952 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.018703 | south | 0.014198 | 0.0032952 | 0.012939 | 0.034916 | 0.0032952 | south | N | 0.0032952 | 0
5511 | RAYBURNC | 1 | 46 | 0.018703 | south | 0.014198 | 0.0032952 | 0.012939 | 0.034916 | 0.0032952 | south | N | 0.0032952 | 0
5512 | RAYBURNC | 1 | 48 | 0.018703 | south | 0.014198 | 0.0032952 | 0.012939 | 0.034916 | 0.0032952 | south | N | 0.0032952 | 0
5728 | FALCONHY | 2 | 12 | 0.017207 | south | 0.012702 | 0.0017992 | 0.011443 | 0.03342 | 0.0017992 | south | N | 0.0017992 | 0
5729 | FALCONHY | 3 | 11 | 0.017207 | south | 0.012702 | 0.0017992 | 0.011443 | 0.03342 | 0.0017992 | south | N | 0.0017992 | 0
5890 | PEARSALL | 1 | 24 | 0.015955 | south | 0.01145 | 0.0005472 | 0.010191 | 0.032168 | 0.0005472 | south | N | 0.0005472 | 0
5891 | PEARSALL | 1 | 24 | 0.015955 | south | 0.01145 | 0.0005472 | 0.010191 | 0.032168 | 0.0005472 | south | N | 0.0005472 | 0
5892 | PEARSALL | 1 | 23 | 0.015955 | south | 0.01145 | 0.0005472 | 0.010191 | 0.032168 | 0.0005472 | south | N | 0.0005472 | 0
5903 | SANMIGUE | 1 | 396 | 0.016379 | south | 0.011874 | 0.0009712 | 0.010615 | 0.032592 | 0.0009712 | south | N | 0.0009712 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.02051 | houston | 0.016005 | 0.0051022 | 0.014746 | 0.036723 | 0.0051022 | south | Y | 0.036723 | 42.1509
5912 | STP_GN2_ | 2 | 1328 | 0.02051 | houston | 0.016005 | 0.0051022 | 0.014746 | 0.036723 | 0.0051022 | south | Y | 0.036723 | 41.9928
5920 | WELSHDC1 | EQ | 600 | 0 | north | -0.0045046 | -0.015408 | -0.0057635 | 0.016213 | 0.0045046 | North | N | 0.0045046 | 0
5932 | SI_RAY9 | 9 | 38 | 0.017626 | south | 0.013121 | 0.0022182 | 0.011862 | 0.033839 | 0.0022182 | south | N | 0.0022182 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.017626 | south | 0.013121 | 0.0022182 | 0.011862 | 0.033839 | 0.0022182 | south | N | 0.0022182 | 0
5934 | SI_RAY5 | 5 | 15 | 0.017626 | south | 0.013121 | 0.0022182 | 0.011862 | 0.033839 | 0.0022182 | south | N | 0.0022182 | 0
5935 | SI_RAY10 | 10 | 47 | 0.017626 | south | 0.013121 | 0.0022182 | 0.011862 | 0.033839 | 0.0022182 | south | N | 0.0022182 | 0
6016 | SWMESA | 1 | 75 | 0.006246 | west | 0.0017414 | -0.0091618 | 0.00048248 | 0.022459 | 0.00048248 | west | N | 0.00048248 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | -0.0045046 | -0.015408 | -0.0057635 | 0.016213 | 0.0045046 | North | Y | 0.0057635 | 0.27697
6144 | MCADOO1A | 1 | 150 | 0.005632 | west | 0.0011274 | -0.0097758 | -0.00013152 | 0.021845 | 0.00013152 | west | N | 0.00013152 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.005823 | west | 0.0013184 | -0.0095848 | 5.9482e-05 | 0.022036 | 5.9482e-05 | west | N | 5.9482e-05 | 0
6476 | LANGFORD | 1 | 150 | 0.007817 | west | 0.0033124 | -0.0075908 | 0.0020535 | 0.02403 | 0.0020535 | west | N | 0.0020535 | 0
6637 | SNYDERW1 | 1 | 63 | 0.005688 | west | 0.0011834 | -0.0097198 | -7.5518e-05 | 0.021901 | 7.5518e-05 | west | N | 7.5518e-05 | 0
6752 | OKLA0A | 1 | 649.7 | 0.005415 | west | 0.00091043 | -0.0099928 | -0.00034852 | 0.021628 | 0.00034852 | west | N | 0.00034852 | 0
6948 | DENISNDM | 1 | 40 | 0.004803 | north | 0.00029843 | -0.010605 | -0.00096052 | 0.021016 | 0.00029843 | North | N | 0.00029843 | 0
6948 | DENISNDM | 2 | 40 | 0.004803 | north | 0.00029843 | -0.010605 | -0.00096052 | 0.021016 | 0.00029843 | North | N | 0.00029843 | 0
7000 | L_FERGUS | 1 | 422 | 0.012708 | south | 0.0082034 | -0.0026998 | 0.0069445 | 0.028921 | 0.0026998 | south | N | 0.0026998 | 0
7004 | L_SIMGID | 1 | 132 | 0.013334 | south | 0.0088294 | -0.0020738 | 0.0075705 | 0.029547 | 0.0020738 | south | N | 0.0020738 | 0
7005 | L_SIMGID | 2 | 134 | 0.013334 | south | 0.0088294 | -0.0020738 | 0.0075705 | 0.029547 | 0.0020738 | south | N | 0.0020738 | 0
7006 | L_SIMGID | 3 | 323 | 0.013334 | south | 0.0088294 | -0.0020738 | 0.0075705 | 0.029547 | 0.0020738 | south | N | 0.0020738 | 0
7007 | L_LOSTPI | 1 | 158 | 0.013597 | south | 0.0090924 | -0.0018108 | 0.0078335 | 0.02981 | 0.0018108 | south | N | 0.0018108 | 0
7008 | L_LOSTPI | 2 | 160 | 0.013597 | south | 0.0090924 | -0.0018108 | 0.0078335 | 0.02981 | 0.0018108 | south | N | 0.0018108 | 0
7009 | L_LOSTPI | 3 | 175 | 0.013597 | south | 0.0090924 | -0.0018108 | 0.0078335 | 0.02981 | 0.0018108 | south | N | 0.0018108 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.014454 | south | 0.0099494 | -0.0009538 | 0.0086905 | 0.030667 | 0.0009538 | south | N | 0.0009538 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.014454 | south | 0.0099494 | -0.0009538 | 0.0086905 | 0.030667 | 0.0009538 | south | N | 0.0009538 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.014469 | south | 0.0099644 | -0.0009388 | 0.0087055 | 0.030682 | 0.0009388 | south | N | 0.0009388 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.01491 | south | 0.010405 | -0.0004978 | 0.0091465 | 0.031123 | 0.0004978 | south | N | 0.0004978 | 0
7015 | L_HAYSEN | 2 | 225 | 0.01491 | south | 0.010405 | -0.0004978 | 0.0091465 | 0.031123 | 0.0004978 | south | N | 0.0004978 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.01491 | south | 0.010405 | -0.0004978 | 0.0091465 | 0.031123 | 0.0004978 | south | N | 0.0004978 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.01491 | south | 0.010405 | -0.0004978 | 0.0091465 | 0.031123 | 0.0004978 | south | N | 0.0004978 | 0
7020 | L_AUSTPL | 1 | 8 | 0.013027 | south | 0.0085224 | -0.0023808 | 0.0072635 | 0.02924 | 0.0023808 | south | N | 0.0023808 | 0
7020 | L_AUSTPL | 2 | 8 | 0.013027 | south | 0.0085224 | -0.0023808 | 0.0072635 | 0.02924 | 0.0023808 | south | N | 0.0023808 | 0
7022 | L_BUCHAN | 1 | 18 | 0.012155 | south | 0.0076504 | -0.0032528 | 0.0063915 | 0.028368 | 0.0032528 | south | N | 0.0032528 | 0
7023 | L_BUCHAN | 2 | 18 | 0.012155 | south | 0.0076504 | -0.0032528 | 0.0063915 | 0.028368 | 0.0032528 | south | N | 0.0032528 | 0
7024 | L_BUCHAN | 3 | 15 | 0.012155 | south | 0.0076504 | -0.0032528 | 0.0063915 | 0.028368 | 0.0032528 | south | N | 0.0032528 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.012257 | south | 0.0077524 | -0.0031508 | 0.0064935 | 0.02847 | 0.0031508 | south | N | 0.0031508 | 0
7028 | L_MARBFA | 1 | 18 | 0.012771 | south | 0.0082664 | -0.0026368 | 0.0070075 | 0.028984 | 0.0026368 | south | N | 0.0026368 | 0
7029 | L_MARBFA | 2 | 18 | 0.012771 | south | 0.0082664 | -0.0026368 | 0.0070075 | 0.028984 | 0.0026368 | south | N | 0.0026368 | 0
7031 | L_MARSFO | 1 | 35 | 0.012913 | south | 0.0084084 | -0.0024948 | 0.0071495 | 0.029126 | 0.0024948 | south | N | 0.0024948 | 0
7032 | L_MARSFO | 2 | 34 | 0.012913 | south | 0.0084084 | -0.0024948 | 0.0071495 | 0.029126 | 0.0024948 | south | N | 0.0024948 | 0
7033 | L_MARSFO | 3 | 35 | 0.012913 | south | 0.0084084 | -0.0024948 | 0.0071495 | 0.029126 | 0.0024948 | south | N | 0.0024948 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.01268 | south | 0.0081754 | -0.0027278 | 0.0069165 | 0.028893 | 0.0027278 | south | N | 0.0027278 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.01268 | south | 0.0081754 | -0.0027278 | 0.0069165 | 0.028893 | 0.0027278 | south | N | 0.0027278 | 0
7038 | L_DELAWA | 1 | 35 | 0.005834 | west | 0.0013294 | -0.0095738 | 7.0482e-05 | 0.022047 | 7.0482e-05 | west | N | 7.0482e-05 | 0
7038 | L_DELAWA | 2 | 30 | 0.005834 | west | 0.0013294 | -0.0095738 | 7.0482e-05 | 0.022047 | 7.0482e-05 | west | N | 7.0482e-05 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.013908 | south | 0.0094034 | -0.0014998 | 0.0081445 | 0.030121 | 0.0014998 | south | N | 0.0014998 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.013908 | south | 0.0094034 | -0.0014998 | 0.0081445 | 0.030121 | 0.0014998 | south | N | 0.0014998 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.013908 | south | 0.0094034 | -0.0014998 | 0.0081445 | 0.030121 | 0.0014998 | south | N | 0.0014998 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.013908 | south | 0.0094034 | -0.0014998 | 0.0081445 | 0.030121 | 0.0014998 | south | N | 0.0014998 | 0
7487 | L_CANYHY | 1 | 6 | 0.014518 | south | 0.010013 | -0.0008898 | 0.0087545 | 0.030731 | 0.0008898 | south | N | 0.0008898 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.015218 | south | 0.010713 | -0.0001898 | 0.0094545 | 0.031431 | 0.0001898 | south | N | 0.0001898 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.015218 | south | 0.010713 | -0.0001898 | 0.0094545 | 0.031431 | 0.0001898 | south | N | 0.0001898 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.015218 | south | 0.010713 | -0.0001898 | 0.0094545 | 0.031431 | 0.0001898 | south | N | 0.0001898 | 0
7609 | L_SCHUMA | 1 | 4 | 0.015319 | south | 0.010814 | -8.8796e-05 | 0.0095555 | 0.031532 | 8.8796e-05 | south | N | 8.8796e-05 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.01543 | south | 0.010925 | 2.2204e-05 | 0.0096665 | 0.031643 | 2.2204e-05 | south | N | 2.2204e-05 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.01543 | south | 0.010925 | 2.2204e-05 | 0.0096665 | 0.031643 | 2.2204e-05 | south | N | 2.2204e-05 | 0
7800 | L_GUADGE | 1 | 147 | 0.015588 | south | 0.011083 | 0.0001802 | 0.0098245 | 0.031801 | 0.0001802 | south | N | 0.0001802 | 0
7801 | L_GUADGE | 2 | 138 | 0.015588 | south | 0.011083 | 0.0001802 | 0.0098245 | 0.031801 | 0.0001802 | south | N | 0.0001802 | 0
7802 | L_GUADGE | 3 | 140 | 0.015588 | south | 0.011083 | 0.0001802 | 0.0098245 | 0.031801 | 0.0001802 | south | N | 0.0001802 | 0
7803 | L_GUADGE | 4 | 147 | 0.015588 | south | 0.011083 | 0.0001802 | 0.0098245 | 0.031801 | 0.0001802 | south | N | 0.0001802 | 0
7804 | L_GUADGE | 5 | 182 | 0.015588 | south | 0.011083 | 0.0001802 | 0.0098245 | 0.031801 | 0.0001802 | south | N | 0.0001802 | 0
7805 | L_GUADGE | 6 | 198 | 0.015588 | south | 0.011083 | 0.0001802 | 0.0098245 | 0.031801 | 0.0001802 | south | N | 0.0001802 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.013559 | south | 0.0090544 | -0.0018488 | 0.0077955 | 0.029772 | 0.0018488 | south | N | 0.0018488 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.013559 | south | 0.0090544 | -0.0018488 | 0.0077955 | 0.029772 | 0.0018488 | south | N | 0.0018488 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.013559 | south | 0.0090544 | -0.0018488 | 0.0077955 | 0.029772 | 0.0018488 | south | N | 0.0018488 | 0
7810 | L_RIONOG | 1 | 142 | 0.015259 | south | 0.010754 | -0.0001488 | 0.0094955 | 0.031472 | 0.0001488 | south | N | 0.0001488 | 0
7811 | L_RIONOG | 2 | 145 | 0.015259 | south | 0.010754 | -0.0001488 | 0.0094955 | 0.031472 | 0.0001488 | south | N | 0.0001488 | 0
7812 | L_RIONOG | 3 | 151 | 0.015259 | south | 0.010754 | -0.0001488 | 0.0094955 | 0.031472 | 0.0001488 | south | N | 0.0001488 | 0
7813 | L_RIONOG | 4 | 290 | 0.015259 | south | 0.010754 | -0.0001488 | 0.0094955 | 0.031472 | 0.0001488 | south | N | 0.0001488 | 0
8032 | AMISTADH | 1 | 33 | 0.013223 | south | 0.0087184 | -0.0021848 | 0.0074595 | 0.029436 | 0.0021848 | south | N | 0.0021848 | 0
8033 | AMISTADH | 2 | 25 | 0.013223 | south | 0.0087184 | -0.0021848 | 0.0074595 | 0.029436 | 0.0021848 | south | N | 0.0021848 | 0
8048 | FALCONHY | 1 | 12 | 0.017207 | south | 0.012702 | 0.0017992 | 0.011443 | 0.03342 | 0.0017992 | south | N | 0.0017992 | 0
8066 | DUP1V#1 | 1 | 73 | 0.018744 | south | 0.014239 | 0.0033362 | 0.01298 | 0.034957 | 0.0033362 | south | N | 0.0033362 | 0
8134 | FOR69CG0 | 1 | 79 | 0.01955 | south | 0.015045 | 0.0041422 | 0.013786 | 0.035763 | 0.0041422 | south | N | 0.0041422 | 0
8138 | FOR69CG0 | 2 | 81 | 0.01955 | south | 0.015045 | 0.0041422 | 0.013786 | 0.035763 | 0.0041422 | south | N | 0.0041422 | 0
8139 | JOS #1 | MB | 255 | 0 | south | -0.0045046 | -0.015408 | -0.0057635 | 0.016213 | 0.0045046 | North | Y | 0.015408 | 2.7803
8147 | UCAR #2 | 10 | 28 | 0.019053 | south | 0.014548 | 0.0036452 | 0.013289 | 0.035266 | 0.0036452 | south | N | 0.0036452 | 0
8148 | UCAR #1 | 2 | 7 | 0.019053 | south | 0.014548 | 0.0036452 | 0.013289 | 0.035266 | 0.0036452 | south | N | 0.0036452 | 0
8153 | FOR69CG0 | 3 | 79 | 0.01955 | south | 0.015045 | 0.0041422 | 0.013786 | 0.035763 | 0.0041422 | south | N | 0.0041422 | 0
8154 | FOR69CG0 | 4 | 80 | 0.01955 | south | 0.015045 | 0.0041422 | 0.013786 | 0.035763 | 0.0041422 | south | N | 0.0041422 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.01955 | south | 0.015045 | 0.0041422 | 0.013786 | 0.035763 | 0.0041422 | south | N | 0.0041422 | 0
8156 | FOR69CG0 | 6 | 25 | 0.01955 | south | 0.015045 | 0.0041422 | 0.013786 | 0.035763 | 0.0041422 | south | N | 0.0041422 | 0
8157 | FOR69CG0 | 7 | 46 | 0.01955 | south | 0.015045 | 0.0041422 | 0.013786 | 0.035763 | 0.0041422 | south | N | 0.0041422 | 0
8161 | COLETOU1 | 1 | 629 | 0.017727 | south | 0.013222 | 0.0023192 | 0.011963 | 0.03394 | 0.0023192 | south | N | 0.0023192 | 0
8173 | VICEC51A | 5 | 144 | 0.018624 | south | 0.014119 | 0.0032162 | 0.01286 | 0.034837 | 0.0032162 | south | N | 0.0032162 | 0
8174 | VICEC61A | 6 | 188 | 0.018624 | south | 0.014119 | 0.0032162 | 0.01286 | 0.034837 | 0.0032162 | south | N | 0.0032162 | 0
8189 | CUERO 2 | 1 | 12 | 0.016227 | south | 0.011722 | 0.0008192 | 0.010463 | 0.03244 | 0.0008192 | south | N | 0.0008192 | 0
8262 | ELPS | 1 | 6 | 0.014116 | south | 0.0096114 | -0.0012918 | 0.0083525 | 0.030329 | 0.0012918 | south | N | 0.0012918 | 0
8285 | LAR #1 | MB | 32 | 0 | south | -0.0045046 | -0.015408 | -0.0057635 | 0.016213 | 0.0045046 | North | Y | 0.015408 | 0.3489
8287 | LAR #2 | MB | 32 | 0 | south | -0.0045046 | -0.015408 | -0.0057635 | 0.016213 | 0.0045046 | North | Y | 0.015408 | 0.3489
8288 | LAR #3 | MB | 105 | 0 | south | -0.0045046 | -0.015408 | -0.0057635 | 0.016213 | 0.0045046 | North | Y | 0.015408 | 1.1448
8388 | BATES0A | MB | 70 | 0 | south | -0.0045046 | -0.015408 | -0.0057635 | 0.016213 | 0.0045046 | North | Y | 0.015408 | 0.76323
8393 | BATES0B | MB | 110 | 0 | south | -0.0045046 | -0.015408 | -0.0057635 | 0.016213 | 0.0045046 | North | Y | 0.015408 | 1.1994
8442 | NBEC71A | 1 | 336 | 0.017793 | south | 0.013288 | 0.0023852 | 0.012029 | 0.034006 | 0.0023852 | south | N | 0.0023852 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | -0.0045046 | -0.015408 | -0.0057635 | 0.016213 | 0.0045046 | North | Y | 0.015408 | 0.21806
8457 | COSW#2 | 2 | 14 | 0 | south | -0.0045046 | -0.015408 | -0.0057635 | 0.016213 | 0.0045046 | North | Y | 0.015408 | 0.15265
8459 | B_DAVIS1 | 1 | 334 | 0.017764 | south | 0.013259 | 0.0023562 | 0.012 | 0.033977 | 0.0023562 | south | N | 0.0023562 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.017764 | south | 0.013259 | 0.0023562 | 0.012 | 0.033977 | 0.0023562 | south | N | 0.0023562 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.017761 | south | 0.013256 | 0.0023532 | 0.011997 | 0.033974 | 0.0023532 | south | N | 0.0023532 | 0
8506 | VAL #1 | 1 | 25 | 0.01777 | south | 0.013265 | 0.0023622 | 0.012006 | 0.033983 | 0.0023622 | south | N | 0.0023622 | 0
8507 | VAL #2 | 2 | 25 | 0.01777 | south | 0.013265 | 0.0023622 | 0.012006 | 0.033983 | 0.0023622 | south | N | 0.0023622 | 0
8511 | OXY_CC0A | 1 | 38 | 0.017755 | south | 0.01325 | 0.0023472 | 0.011991 | 0.033968 | 0.0023472 | south | N | 0.0023472 | 0
8517 | CELANEBI | 1 | 29 | 0.017677 | south | 0.013172 | 0.0022692 | 0.011913 | 0.03389 | 0.0022692 | south | N | 0.0022692 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.017792 | south | 0.013287 | 0.0023842 | 0.012028 | 0.034005 | 0.0023842 | south | N | 0.0023842 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.017792 | south | 0.013287 | 0.0023842 | 0.012028 | 0.034005 | 0.0023842 | south | N | 0.0023842 | 0
8562 | CNOPST1 | 3 | 153 | 0.017792 | south | 0.013287 | 0.0023842 | 0.012028 | 0.034005 | 0.0023842 | south | N | 0.0023842 | 0
8926 | LGE_GT10 | 1 | 158 | 0.017923 | south | 0.013418 | 0.0025152 | 0.012159 | 0.034136 | 0.0025152 | south | N | 0.0025152 | 0
8927 | LGE_GT20 | 2 | 153 | 0.017923 | south | 0.013418 | 0.0025152 | 0.012159 | 0.034136 | 0.0025152 | south | N | 0.0025152 | 0
8928 | LGE_STG0 | 3 | 100 | 0.017923 | south | 0.013418 | 0.0025152 | 0.012159 | 0.034136 | 0.0025152 | south | N | 0.0025152 | 0
8930 | ICPGN10A | 1 | 145 | 0.017923 | south | 0.013418 | 0.0025152 | 0.012159 | 0.034136 | 0.0025152 | south | N | 0.0025152 | 0
8931 | ICPGN20A | 2 | 147 | 0.017923 | south | 0.013418 | 0.0025152 | 0.012159 | 0.034136 | 0.0025152 | south | N | 0.0025152 | 0
8932 | ICPGN30A | 3 | 127 | 0.017923 | south | 0.013418 | 0.0025152 | 0.012159 | 0.034136 | 0.0025152 | south | N | 0.0025152 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.017533 | south | 0.013028 | 0.0021252 | 0.011769 | 0.033746 | 0.0021252 | south | N | 0.0021252 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.017533 | south | 0.013028 | 0.0021252 | 0.011769 | 0.033746 | 0.0021252 | south | N | 0.0021252 | 0
8935 | FGNTS201 | 3 | 173 | 0.017533 | south | 0.013028 | 0.0021252 | 0.011769 | 0.033746 | 0.0021252 | south | N | 0.0021252 | 0
8936 | MVGN#1 | 1 | 207 | 0.017586 | south | 0.013081 | 0.0021782 | 0.011822 | 0.033799 | 0.0021782 | south | N | 0.0021782 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.017586 | south | 0.013081 | 0.0021782 | 0.011822 | 0.033799 | 0.0021782 | south | N | 0.0021782 | 0
8938 | MVGN#3 | 3 | 242 | 0.017586 | south | 0.013081 | 0.0021782 | 0.011822 | 0.033799 | 0.0021782 | south | N | 0.0021782 | 0
8981 | HECN1 | 1 | 144 | 0.017587 | south | 0.013082 | 0.0021792 | 0.011823 | 0.0338 | 0.0021792 | south | N | 0.0021792 | 0
8982 | HECN2 | 2 | 144 | 0.017587 | south | 0.013082 | 0.0021792 | 0.011823 | 0.0338 | 0.0021792 | south | N | 0.0021792 | 0
8983 | HECN3 | 3 | 171 | 0.017587 | south | 0.013082 | 0.0021792 | 0.011823 | 0.0338 | 0.0021792 | south | N | 0.0021792 | 0
9000 | DECKR_G1 | 1 | 310 | 0.013024 | south | 0.0085194 | -0.0023838 | 0.0072605 | 0.029237 | 0.0023838 | south | N | 0.0023838 | 0
9001 | DECKR_G2 | 2 | 413 | 0.013024 | south | 0.0085194 | -0.0023838 | 0.0072605 | 0.029237 | 0.0023838 | south | N | 0.0023838 | 0
9002 | DECKR_G3 | 3 | 42 | 0.012926 | south | 0.0084214 | -0.0024818 | 0.0071625 | 0.029139 | 0.0024818 | south | N | 0.0024818 | 0
9003 | DECKR_G4 | 4 | 44 | 0.012926 | south | 0.0084214 | -0.0024818 | 0.0071625 | 0.029139 | 0.0024818 | south | N | 0.0024818 | 0
9004 | DECKR_G5 | 5 | 44 | 0.012926 | south | 0.0084214 | -0.0024818 | 0.0071625 | 0.029139 | 0.0024818 | south | N | 0.0024818 | 0
9005 | DECKR_G6 | 6 | 47 | 0.012926 | south | 0.0084214 | -0.0024818 | 0.0071625 | 0.029139 | 0.0024818 | south | N | 0.0024818 | 0
9016 | SANDH_G1 | 1 | 49 | 0.013157 | south | 0.0086524 | -0.0022508 | 0.0073935 | 0.02937 | 0.0022508 | south | N | 0.0022508 | 0
9017 | SANDH_G2 | 2 | 46 | 0.013157 | south | 0.0086524 | -0.0022508 | 0.0073935 | 0.02937 | 0.0022508 | south | N | 0.0022508 | 0
9018 | SANDH_G3 | 3 | 46 | 0.013157 | south | 0.0086524 | -0.0022508 | 0.0073935 | 0.02937 | 0.0022508 | south | N | 0.0022508 | 0
9019 | SANDH_G4 | 4 | 47 | 0.013157 | south | 0.0086524 | -0.0022508 | 0.0073935 | 0.02937 | 0.0022508 | south | N | 0.0022508 | 0
9020 | SANDHG5A | 5A | 154 | 0.013157 | south | 0.0086524 | -0.0022508 | 0.0073935 | 0.02937 | 0.0022508 | south | N | 0.0022508 | 0
9021 | SANDHG5C | 5C | 148 | 0.013157 | south | 0.0086524 | -0.0022508 | 0.0073935 | 0.02937 | 0.0022508 | south | N | 0.0022508 | 0
9022 | SANDH_G6 | 6 | 48 | 0.013157 | south | 0.0086524 | -0.0022508 | 0.0073935 | 0.02937 | 0.0022508 | south | N | 0.0022508 | 0
9023 | SANDH_G7 | 7 | 48 | 0.013157 | south | 0.0086524 | -0.0022508 | 0.0073935 | 0.02937 | 0.0022508 | south | N | 0.0022508 | 0
11001 | NAV1CT | 1 | 70 | 0.005764 | west | 0.0012594 | -0.0096438 | 4.8218e-07 | 0.021977 | 4.8218e-07 | west | N | 4.8218e-07 | 0
11009 | NAV2CT | 1 | 70 | 0.005764 | west | 0.0012594 | -0.0096438 | 4.8218e-07 | 0.021977 | 4.8218e-07 | west | N | 4.8218e-07 | 0
11011 | NAV3ST | 1 | 92.8 | 0.005764 | west | 0.0012594 | -0.0096438 | 4.8218e-07 | 0.021977 | 4.8218e-07 | west | N | 4.8218e-07 | 0
11012 | NAV4CT | 1 | 80 | 0.005764 | west | 0.0012594 | -0.0096438 | 4.8218e-07 | 0.021977 | 4.8218e-07 | west | N | 4.8218e-07 | 0
11013 | NAV5CT | 1 | 80 | 0.005764 | west | 0.0012594 | -0.0096438 | 4.8218e-07 | 0.021977 | 4.8218e-07 | west | N | 4.8218e-07 | 0
11014 | NAV6ST | 1 | 115 | 0.005764 | west | 0.0012594 | -0.0096438 | 4.8218e-07 | 0.021977 | 4.8218e-07 | west | N | 4.8218e-07 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.005764 | west | 0.0012594 | -0.0096438 | 4.8218e-07 | 0.021977 | 4.8218e-07 | west | N | 4.8218e-07 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.005764 | west | 0.0012594 | -0.0096438 | 4.8218e-07 | 0.021977 | 4.8218e-07 | west | N | 4.8218e-07 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.005764 | west | 0.0012594 | -0.0096438 | 4.8218e-07 | 0.021977 | 4.8218e-07 | west | N | 4.8218e-07 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.005764 | west | 0.0012594 | -0.0096438 | 4.8218e-07 | 0.021977 | 4.8218e-07 | west | N | 4.8218e-07 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.005764 | west | 0.0012594 | -0.0096438 | 4.8218e-07 | 0.021977 | 4.8218e-07 | west | N | 4.8218e-07 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.005764 | west | 0.0012594 | -0.0096438 | 4.8218e-07 | 0.021977 | 4.8218e-07 | west | N | 4.8218e-07 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.005634 | west | 0.0011294 | -0.0097738 | -0.00012952 | 0.021847 | 0.00012952 | west | N | 0.00012952 | 0
11057 | CHAMPION | 1 | 126.5 | 0.005634 | west | 0.0011294 | -0.0097738 | -0.00012952 | 0.021847 | 0.00012952 | west | N | 0.00012952 | 0
11058 | PYRON_1G | 1 | 249 | 0.005634 | west | 0.0011294 | -0.0097738 | -0.00012952 | 0.021847 | 0.00012952 | west | N | 0.00012952 | 0
11059 | INADALE_ | 1 | 197 | 0.005634 | west | 0.0011294 | -0.0097738 | -0.00012952 | 0.021847 | 0.00012952 | west | N | 0.00012952 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.0057 | west | 0.0011954 | -0.0097078 | -6.3518e-05 | 0.021913 | 6.3518e-05 | west | N | 6.3518e-05 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.0057 | west | 0.0011954 | -0.0097078 | -6.3518e-05 | 0.021913 | 6.3518e-05 | west | N | 6.3518e-05 | 0
11147 | NOTREES_ | 1 | 149 | 0.005821 | west | 0.0013164 | -0.0095868 | 5.7482e-05 | 0.022034 | 5.7482e-05 | west | N | 5.7482e-05 | 0
11309 | BULLCREK | 1 | 180 | 0.005712 | west | 0.0012074 | -0.0096958 | -5.1518e-05 | 0.021925 | 5.1518e-05 | west | N | 5.1518e-05 | 0
11310 | BULLCREK | 1 | 180 | 0.005712 | west | 0.0012074 | -0.0096958 | -5.1518e-05 | 0.021925 | 5.1518e-05 | west | N | 5.1518e-05 | 0
11320 | COYOTE_1 | 1 | 225 | 0.005716 | west | 0.0012114 | -0.0096918 | -4.7518e-05 | 0.021929 | 4.7518e-05 | west | N | 4.7518e-05 | 0
11415 | LORAINE_ | 1 | 125 | 0.005661 | west | 0.0011564 | -0.0097468 | -0.00010252 | 0.021874 | 0.00010252 | west | N | 0.00010252 | 0
11416 | LORAINE_ | 1 | 125 | 0.005661 | west | 0.0011564 | -0.0097468 | -0.00010252 | 0.021874 | 0.00010252 | west | N | 0.00010252 | 0
11691 | KMICHICT | 1 | 140 | 0.004776 | north | 0.00027143 | -0.010632 | -0.00098752 | 0.020989 | 0.00027143 | North | N | 0.00027143 | 0
11692 | KMICHICT | 2 | 141 | 0.004776 | north | 0.00027143 | -0.010632 | -0.00098752 | 0.020989 | 0.00027143 | North | N | 0.00027143 | 0
11693 | KMICHIST | 3 | 309 | 0.004776 | north | 0.00027143 | -0.010632 | -0.00098752 | 0.020989 | 0.00027143 | North | N | 0.00027143 | 0
11694 | KMICHICT | 4 | 143 | 0.004776 | north | 0.00027143 | -0.010632 | -0.00098752 | 0.020989 | 0.00027143 | North | N | 0.00027143 | 0
11695 | KMICHICT | 5 | 144 | 0.004776 | north | 0.00027143 | -0.010632 | -0.00098752 | 0.020989 | 0.00027143 | North | N | 0.00027143 | 0
11696 | KMICHIST | 6 | 310 | 0.004776 | north | 0.00027143 | -0.010632 | -0.00098752 | 0.020989 | 0.00027143 | North | N | 0.00027143 | 0
12322 | ENNSTRAC | 1 | 196 | 0.004883 | north | 0.00037843 | -0.010525 | -0.00088052 | 0.021096 | 0.00037843 | North | N | 0.00037843 | 0
12323 | ENNSTRAC | 2 | 111 | 0.004883 | north | 0.00037843 | -0.010525 | -0.00088052 | 0.021096 | 0.00037843 | North | N | 0.00037843 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.004821 | north | 0.00031643 | -0.010587 | -0.00094252 | 0.021034 | 0.00031643 | North | N | 0.00031643 | 0
12411 | FPLEFR1A | 1 | 161 | 0.004679 | north | 0.00017443 | -0.010729 | -0.0010845 | 0.020892 | 0.00017443 | North | N | 0.00017443 | 0
12412 | FPLEFR1B | 2 | 164 | 0.004679 | north | 0.00017443 | -0.010729 | -0.0010845 | 0.020892 | 0.00017443 | North | N | 0.00017443 | 0
12413 | FPLEFR1C | 3 | 164 | 0.004679 | north | 0.00017443 | -0.010729 | -0.0010845 | 0.020892 | 0.00017443 | North | N | 0.00017443 | 0
12414 | FPLEFR1S | 4 | 414 | 0.004679 | north | 0.00017443 | -0.010729 | -0.0010845 | 0.020892 | 0.00017443 | North | N | 0.00017443 | 0
12421 | FPLEFR2A | 1 | 162 | 0.004679 | north | 0.00017443 | -0.010729 | -0.0010845 | 0.020892 | 0.00017443 | North | N | 0.00017443 | 0
12422 | FPLEFR2B | 2 | 161 | 0.004679 | north | 0.00017443 | -0.010729 | -0.0010845 | 0.020892 | 0.00017443 | North | N | 0.00017443 | 0
12423 | FPLEFR2C | 3 | 163 | 0.004679 | north | 0.00017443 | -0.010729 | -0.0010845 | 0.020892 | 0.00017443 | North | N | 0.00017443 | 0
12424 | FPLEFR2S | 4 | 409 | 0.004679 | north | 0.00017443 | -0.010729 | -0.0010845 | 0.020892 | 0.00017443 | North | N | 0.00017443 | 0
12440 | PARKD_1S | 1 | 0 | 0.004745 | north | 0.00024043 | -0.010663 | -0.0010185 | 0.020958 | 0.00024043 | North | N | 0.00024043 | 0
12449 | PARKD_2S | 1 | 0 | 0.004745 | north | 0.00024043 | -0.010663 | -0.0010185 | 0.020958 | 0.00024043 | North | N | 0.00024043 | 0
13116 | TGATEWAY | 1 | 148 | 0.004415 | north | -8.957e-05 | -0.010993 | -0.0013485 | 0.020628 | 8.957e-05 | North | N | 8.957e-05 | 0
13117 | TGATEWAY | 2 | 130 | 0.004415 | north | -8.957e-05 | -0.010993 | -0.0013485 | 0.020628 | 8.957e-05 | North | N | 8.957e-05 | 0
13118 | TGATEWAY | 3 | 145 | 0.004415 | north | -8.957e-05 | -0.010993 | -0.0013485 | 0.020628 | 8.957e-05 | North | N | 8.957e-05 | 0
13119 | TGATEWAY | 4 | 399 | 0.004415 | north | -8.957e-05 | -0.010993 | -0.0013485 | 0.020628 | 8.957e-05 | North | N | 8.957e-05 | 0
13131 | CALFREST | 1 | 150.7 | 0.004024 | north | -0.00048057 | -0.011384 | -0.0017395 | 0.020237 | 0.00048057 | North | N | 0.00048057 | 0
13132 | CALFREST | 2 | 151 | 0.004024 | north | -0.00048057 | -0.011384 | -0.0017395 | 0.020237 | 0.00048057 | North | N | 0.00048057 | 0
13133 | CALFREST | 3 | 177.4 | 0.004024 | north | -0.00048057 | -0.011384 | -0.0017395 | 0.020237 | 0.00048057 | North | N | 0.00048057 | 0
13134 | CALFREST | 4 | 151.5 | 0.004039 | north | -0.00046557 | -0.011369 | -0.0017245 | 0.020252 | 0.00046557 | North | N | 0.00046557 | 0
13135 | CALFREST | 5 | 152.3 | 0.004039 | north | -0.00046557 | -0.011369 | -0.0017245 | 0.020252 | 0.00046557 | North | N | 0.00046557 | 0
13136 | CALFREST | 6 | 177.5 | 0.004039 | north | -0.00046557 | -0.011369 | -0.0017245 | 0.020252 | 0.00046557 | North | N | 0.00046557 | 0
13432 | SANDOW_5 | 5 | 581 | 0.01085 | south | 0.0063454 | -0.0045578 | 0.0050865 | 0.027063 | 0.0045578 | south | N | 0.0045578 | 0
13691 | OAKGROVE | 1 | 855 | 0.002412 | north | -0.0020926 | -0.012996 | -0.0033515 | 0.018625 | 0.0020926 | North | N | 0.0020926 | 0
13692 | OAKGROVE | 2 | 855 | 0.002412 | north | -0.0020926 | -0.012996 | -0.0033515 | 0.018625 | 0.0020926 | North | N | 0.0020926 | 0
32798 | BRYN_TAM | 1 | 32 | 0.001693 | north | -0.0028116 | -0.013715 | -0.0040705 | 0.017906 | 0.0028116 | North | N | 0.0028116 | 0
32883 | BRYN_DNS | 1 | 48 | 0.001972 | north | -0.0025326 | -0.013436 | -0.0037915 | 0.018185 | 0.0025326 | North | N | 0.0025326 | 0
32884 | BRYN_DNS | 1 | 46 | 0.001972 | north | -0.0025326 | -0.013436 | -0.0037915 | 0.018185 | 0.0025326 | North | N | 0.0025326 | 0
32886 | BRYN_ATK | MB | 12 | 0.001717 | north | -0.0027876 | -0.013691 | -0.0040465 | 0.01793 | 0.0027876 | North | N | 0.0027876 | 0
32887 | BRYN_ATK | MB | 51 | 0.001717 | north | -0.0027876 | -0.013691 | -0.0040465 | 0.01793 | 0.0027876 | North | N | 0.0027876 | 0
32888 | BRYN_ATK | 1 | 17 | 0.001717 | north | -0.0027876 | -0.013691 | -0.0040465 | 0.01793 | 0.0027876 | North | N | 0.0027876 | 0
32890 | BRYN_ATK | MB | 22 | 0.001717 | north | -0.0027876 | -0.013691 | -0.0040465 | 0.01793 | 0.0027876 | North | N | 0.0027876 | 0
32891 | BRYN_ATK | MB | 25 | 0.001717 | north | -0.0027876 | -0.013691 | -0.0040465 | 0.01793 | 0.0027876 | North | N | 0.0027876 | 0
32892 | BRYN_DNS | 1 | 105 | 0.001972 | north | -0.0025326 | -0.013436 | -0.0037915 | 0.018185 | 0.0025326 | North | N | 0.0025326 | 0
36998 | RDCNYNG1 | 1 | 84 | 0.005674 | west | 0.0011694 | -0.0097338 | -8.9518e-05 | 0.021887 | 8.9518e-05 | west | N | 8.9518e-05 | 0
38332 | WDWRDU2 | 1 | 80 | 0.006254 | west | 0.0017494 | -0.0091538 | 0.00049048 | 0.022467 | 0.00049048 | west | N | 0.00049048 | 0
38437 | TNSRBNMS | 1 | 150 | 0.006257 | west | 0.0017524 | -0.0091508 | 0.00049348 | 0.02247 | 0.00049348 | west | N | 0.00049348 | 0
38438 | TNSRBNMS | 1 | 150 | 0.006257 | west | 0.0017524 | -0.0091508 | 0.00049348 | 0.02247 | 0.00049348 | west | N | 0.00049348 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.019842 | houston | -0.024347 | -0.03525 | -0.025606 | -0.0036287 | 0.0036287 | houston | N | 0.0036287 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.019842 | houston | -0.024347 | -0.03525 | -0.025606 | -0.0036287 | 0.0036287 | houston | N | 0.0036287 | 0
38600 | TNBP_CGN | 5 | 53 | -0.019842 | houston | -0.024347 | -0.03525 | -0.025606 | -0.0036287 | 0.0036287 | houston | N | 0.0036287 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.019842 | houston | -0.024347 | -0.03525 | -0.025606 | -0.0036287 | 0.0036287 | houston | N | 0.0036287 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.019842 | houston | -0.024347 | -0.03525 | -0.025606 | -0.0036287 | 0.0036287 | houston | N | 0.0036287 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.019842 | houston | -0.024347 | -0.03525 | -0.025606 | -0.0036287 | 0.0036287 | houston | N | 0.0036287 | 0
38614 | TNBPAMCG | 4 | 96 | -0.019842 | houston | -0.024347 | -0.03525 | -0.025606 | -0.0036287 | 0.0036287 | houston | N | 0.0036287 | 0
38615 | TNBPAMCG | 1 | 244 | -0.019842 | houston | -0.024347 | -0.03525 | -0.025606 | -0.0036287 | 0.0036287 | houston | N | 0.0036287 | 0
38690 | TNBP_CGN | 3 | 40 | -0.019842 | houston | -0.024347 | -0.03525 | -0.025606 | -0.0036287 | 0.0036287 | houston | N | 0.0036287 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.019743 | houston | -0.024248 | -0.035151 | -0.025507 | -0.0035297 | 0.0035297 | houston | N | 0.0035297 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.019743 | houston | -0.024248 | -0.035151 | -0.025507 | -0.0035297 | 0.0035297 | houston | N | 0.0035297 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.019743 | houston | -0.024248 | -0.035151 | -0.025507 | -0.0035297 | 0.0035297 | houston | N | 0.0035297 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.019743 | houston | -0.024248 | -0.035151 | -0.025507 | -0.0035297 | 0.0035297 | houston | N | 0.0035297 | 0
39470 | TNDOWCGN | 1 | 32 | -0.019746 | houston | -0.024251 | -0.035154 | -0.02551 | -0.0035327 | 0.0035327 | houston | N | 0.0035327 | 0
39480 | TNDOWCGN | 1 | 30 | -0.019746 | houston | -0.024251 | -0.035154 | -0.02551 | -0.0035327 | 0.0035327 | houston | N | 0.0035327 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.04153 | houston | 0.037025 | 0.026122 | 0.035766 | 0.057743 | 0.026122 | south | Y | 0.057743 | 3.5099
39770 | TNSCLP2_ | 1 | 111 | 0.04153 | houston | 0.037025 | 0.026122 | 0.035766 | 0.057743 | 0.026122 | south | Y | 0.057743 | 3.5099
39775 | TNSCLP4_ | 1 | 119 | 0.04153 | houston | 0.037025 | 0.026122 | 0.035766 | 0.057743 | 0.026122 | south | Y | 0.057743 | 3.7629
39790 | TNSCLP3_ | 1 | 109.5 | 0.04153 | houston | 0.037025 | 0.026122 | 0.035766 | 0.057743 | 0.026122 | south | Y | 0.057743 | 3.4625
39960 | TNTNPONE | 1 | 152.3 | 0.002412 | north | -0.0020926 | -0.012996 | -0.0033515 | 0.018625 | 0.0020926 | North | N | 0.0020926 | 0
39970 | TNTNPONE | 1 | 153 | 0.002412 | north | -0.0020926 | -0.012996 | -0.0033515 | 0.018625 | 0.0020926 | North | N | 0.0020926 | 0
48500 | APD_GT1_ | 1 | 136 | -0.19062 | houston | -0.19513 | -0.20603 | -0.19639 | -0.17441 | 0.17441 | houston | N | 0.17441 | 0
48510 | AK_GT1__ | 1 | 33 | 0.016897 | houston | 0.012392 | 0.0014892 | 0.011133 | 0.03311 | 0.0014892 | south | Y | 0.03311 | 1.0435
48511 | LPE_GT1_ | 1 | 42 | -0.052727 | houston | -0.057232 | -0.068135 | -0.058491 | -0.036514 | 0.036514 | houston | N | 0.036514 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.052727 | houston | -0.057232 | -0.068135 | -0.058491 | -0.036514 | 0.036514 | houston | N | 0.036514 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.052727 | houston | -0.057232 | -0.068135 | -0.058491 | -0.036514 | 0.036514 | houston | N | 0.036514 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.052727 | houston | -0.057232 | -0.068135 | -0.058491 | -0.036514 | 0.036514 | houston | N | 0.036514 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.029878 | houston | 0.025373 | 0.01447 | 0.024114 | 0.046091 | 0.01447 | south | Y | 0.046091 | 2.2451
48520 | BSF_GT1_ | 2 | 10 | 0.029878 | houston | 0.025373 | 0.01447 | 0.024114 | 0.046091 | 0.01447 | south | Y | 0.046091 | 0.31621
48521 | BVE_GT1_ | 1 | 163 | 0.025815 | houston | 0.02131 | 0.010407 | 0.020051 | 0.042028 | 0.010407 | south | Y | 0.042028 | 5.1542
48522 | BVE_GT2_ | 2 | 163 | 0.025815 | houston | 0.02131 | 0.010407 | 0.020051 | 0.042028 | 0.010407 | south | Y | 0.042028 | 5.1542
48523 | BVE_ST1_ | 3 | 245 | 0.025815 | houston | 0.02131 | 0.010407 | 0.020051 | 0.042028 | 0.010407 | south | Y | 0.042028 | 7.7472
48531 | BYU_GT1_ | 1 | 65 | -0.037351 | houston | -0.041856 | -0.052759 | -0.043115 | -0.021138 | 0.021138 | houston | N | 0.021138 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.037351 | houston | -0.041856 | -0.052759 | -0.043115 | -0.021138 | 0.021138 | houston | N | 0.021138 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.037351 | houston | -0.041856 | -0.052759 | -0.043115 | -0.021138 | 0.021138 | houston | N | 0.021138 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.037351 | houston | -0.041856 | -0.052759 | -0.043115 | -0.021138 | 0.021138 | houston | N | 0.021138 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.050825 | houston | -0.05533 | -0.066233 | -0.056589 | -0.034612 | 0.034612 | houston | N | 0.034612 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.050825 | houston | -0.05533 | -0.066233 | -0.056589 | -0.034612 | 0.034612 | houston | N | 0.034612 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.030531 | houston | -0.035036 | -0.045939 | -0.036295 | -0.014318 | 0.014318 | houston | N | 0.014318 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.030531 | houston | -0.035036 | -0.045939 | -0.036295 | -0.014318 | 0.014318 | houston | N | 0.014318 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.030531 | houston | -0.035036 | -0.045939 | -0.036295 | -0.014318 | 0.014318 | houston | N | 0.014318 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.030531 | houston | -0.035036 | -0.045939 | -0.036295 | -0.014318 | 0.014318 | houston | N | 0.014318 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.030531 | houston | -0.035036 | -0.045939 | -0.036295 | -0.014318 | 0.014318 | houston | N | 0.014318 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.05657 | houston | -0.061075 | -0.071978 | -0.062334 | -0.040357 | 0.040357 | houston | N | 0.040357 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.054679 | houston | -0.059184 | -0.070087 | -0.060443 | -0.038466 | 0.038466 | houston | N | 0.038466 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.049928 | houston | -0.054433 | -0.065336 | -0.055692 | -0.033715 | 0.033715 | houston | N | 0.033715 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.049928 | houston | -0.054433 | -0.065336 | -0.055692 | -0.033715 | 0.033715 | houston | N | 0.033715 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.049928 | houston | -0.054433 | -0.065336 | -0.055692 | -0.033715 | 0.033715 | houston | N | 0.033715 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.067475 | houston | -0.07198 | -0.082883 | -0.073239 | -0.051262 | 0.051262 | houston | N | 0.051262 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.18407 | houston | -0.18858 | -0.19948 | -0.18983 | -0.16786 | 0.16786 | houston | N | 0.16786 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.18407 | houston | -0.18858 | -0.19948 | -0.18983 | -0.16786 | 0.16786 | houston | N | 0.16786 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.051 | houston | -0.055505 | -0.066408 | -0.056764 | -0.034787 | 0.034787 | houston | N | 0.034787 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.051 | houston | -0.055505 | -0.066408 | -0.056764 | -0.034787 | 0.034787 | houston | N | 0.034787 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.051 | houston | -0.055505 | -0.066408 | -0.056764 | -0.034787 | 0.034787 | houston | N | 0.034787 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.051 | houston | -0.055505 | -0.066408 | -0.056764 | -0.034787 | 0.034787 | houston | N | 0.034787 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.050486 | houston | -0.054991 | -0.065894 | -0.05625 | -0.034273 | 0.034273 | houston | N | 0.034273 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.050486 | houston | -0.054991 | -0.065894 | -0.05625 | -0.034273 | 0.034273 | houston | N | 0.034273 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.050486 | houston | -0.054991 | -0.065894 | -0.05625 | -0.034273 | 0.034273 | houston | N | 0.034273 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.050486 | houston | -0.054991 | -0.065894 | -0.05625 | -0.034273 | 0.034273 | houston | N | 0.034273 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.035837 | houston | -0.040342 | -0.051245 | -0.041601 | -0.019624 | 0.019624 | houston | N | 0.019624 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.035837 | houston | -0.040342 | -0.051245 | -0.041601 | -0.019624 | 0.019624 | houston | N | 0.019624 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.035837 | houston | -0.040342 | -0.051245 | -0.041601 | -0.019624 | 0.019624 | houston | N | 0.019624 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.035837 | houston | -0.040342 | -0.051245 | -0.041601 | -0.019624 | 0.019624 | houston | N | 0.019624 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.035837 | houston | -0.040342 | -0.051245 | -0.041601 | -0.019624 | 0.019624 | houston | N | 0.019624 | 0
48651 | EP_1_2 | 1 | 5 | -0.068263 | houston | -0.072768 | -0.083671 | -0.074027 | -0.05205 | 0.05205 | houston | N | 0.05205 | 0
48651 | EP_1_2 | 2 | 21 | -0.068263 | houston | -0.072768 | -0.083671 | -0.074027 | -0.05205 | 0.05205 | houston | N | 0.05205 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.000505 | north | -0.0039996 | -0.014903 | -0.0052585 | 0.016718 | 0.0039996 | North | N | 0.0039996 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.000505 | north | -0.0039996 | -0.014903 | -0.0052585 | 0.016718 | 0.0039996 | North | N | 0.0039996 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.000505 | north | -0.0039996 | -0.014903 | -0.0052585 | 0.016718 | 0.0039996 | North | N | 0.0039996 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.000505 | north | -0.0039996 | -0.014903 | -0.0052585 | 0.016718 | 0.0039996 | North | N | 0.0039996 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.10788 | houston | -0.11239 | -0.12329 | -0.11365 | -0.091669 | 0.091669 | houston | N | 0.091669 | 0
48691 | GBY_7374 | A | 46 | -0.18082 | houston | -0.18532 | -0.19623 | -0.18658 | -0.16461 | 0.16461 | houston | N | 0.16461 | 0
48691 | GBY_7374 | B | 46 | -0.18082 | houston | -0.18532 | -0.19623 | -0.18658 | -0.16461 | 0.16461 | houston | N | 0.16461 | 0
48692 | GBY_8182 | C | 46 | -0.18082 | houston | -0.18532 | -0.19623 | -0.18658 | -0.16461 | 0.16461 | houston | N | 0.16461 | 0
48692 | GBY_8182 | D | 55 | -0.18082 | houston | -0.18532 | -0.19623 | -0.18658 | -0.16461 | 0.16461 | houston | N | 0.16461 | 0
48693 | GBY_8384 | E | 55 | -0.18082 | houston | -0.18532 | -0.19623 | -0.18658 | -0.16461 | 0.16461 | houston | N | 0.16461 | 0
48693 | GBY_8384 | F | 54 | -0.18082 | houston | -0.18532 | -0.19623 | -0.18658 | -0.16461 | 0.16461 | houston | N | 0.16461 | 0
48721 | LEG_1___ | 1 | 827 | 0.003015 | north | -0.0014896 | -0.012393 | -0.0027485 | 0.019228 | 0.0014896 | North | N | 0.0014896 | 0
48722 | LEG_2___ | 2 | 819 | 0.003015 | north | -0.0014896 | -0.012393 | -0.0027485 | 0.019228 | 0.0014896 | North | N | 0.0014896 | 0
48730 | MNS_GT | 1 | 46.1 | 0.020787 | houston | 0.016282 | 0.0053792 | 0.015023 | 0.037 | 0.0053792 | south | Y | 0.037 | 1.4577
48731 | CBE_GT1 | 1 | 76 | 0.028749 | houston | 0.024244 | 0.013341 | 0.022985 | 0.044962 | 0.013341 | south | Y | 0.044962 | 2.4032
48732 | CBE_GT2 | 1 | 76 | 0.028749 | houston | 0.024244 | 0.013341 | 0.022985 | 0.044962 | 0.013341 | south | Y | 0.044962 | 2.4032
48733 | CBE_ST12 | 1 | 105 | 0.028749 | houston | 0.024244 | 0.013341 | 0.022985 | 0.044962 | 0.013341 | south | Y | 0.044962 | 3.3202
48734 | CBE_GT3 | 1 | 74 | 0.028749 | houston | 0.024244 | 0.013341 | 0.022985 | 0.044962 | 0.013341 | south | Y | 0.044962 | 2.34
48735 | CBE_GT4 | 1 | 74 | 0.028749 | houston | 0.024244 | 0.013341 | 0.022985 | 0.044962 | 0.013341 | south | Y | 0.044962 | 2.34
48736 | CBE_ST34 | 1 | 102 | 0.028749 | houston | 0.024244 | 0.013341 | 0.022985 | 0.044962 | 0.013341 | south | Y | 0.044962 | 3.2254
48740 | PSG_GN2_ | 1 | 180 | -0.051451 | houston | -0.055956 | -0.066859 | -0.057215 | -0.035238 | 0.035238 | houston | N | 0.035238 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.051451 | houston | -0.055956 | -0.066859 | -0.057215 | -0.035238 | 0.035238 | houston | N | 0.035238 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.051451 | houston | -0.055956 | -0.066859 | -0.057215 | -0.035238 | 0.035238 | houston | N | 0.035238 | 0
48761 | PR_GT1__ | 1 | 35 | -0.074068 | houston | -0.078573 | -0.089476 | -0.079832 | -0.057855 | 0.057855 | houston | N | 0.057855 | 0
48772 | PHR_GN2_ | MB | 459 | -0.024802 | houston | -0.029307 | -0.04021 | -0.030566 | -0.0085887 | 0.0085887 | houston | N | 0.0085887 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.089814 | houston | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.089814 | houston | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.089814 | houston | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.089814 | houston | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.089814 | houston | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.089814 | houston | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.089814 | houston | -0.094319 | -0.10522 | -0.095578 | -0.073601 | 0.073601 | houston | N | 0.073601 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.067475 | houston | -0.07198 | -0.082883 | -0.073239 | -0.051262 | 0.051262 | houston | N | 0.051262 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.067475 | houston | -0.07198 | -0.082883 | -0.073239 | -0.051262 | 0.051262 | houston | N | 0.051262 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.067475 | houston | -0.07198 | -0.082883 | -0.073239 | -0.051262 | 0.051262 | houston | N | 0.051262 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.067475 | houston | -0.07198 | -0.082883 | -0.073239 | -0.051262 | 0.051262 | houston | N | 0.051262 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.092994 | houston | -0.097499 | -0.1084 | -0.098758 | -0.076781 | 0.076781 | houston | N | 0.076781 | 0
48820 | SHELLG1_ | 1 | 71 | -0.051877 | houston | -0.056382 | -0.067285 | -0.057641 | -0.035664 | 0.035664 | houston | N | 0.035664 | 0
48821 | SHELLG2 | 2 | 72 | -0.051877 | houston | -0.056382 | -0.067285 | -0.057641 | -0.035664 | 0.035664 | houston | N | 0.035664 | 0
48822 | SHELLG3_ | 1 | 39 | -0.051877 | houston | -0.056382 | -0.067285 | -0.057641 | -0.035664 | 0.035664 | houston | N | 0.035664 | 0
48822 | SHELLG3_ | 2 | 30 | -0.051877 | houston | -0.056382 | -0.067285 | -0.057641 | -0.035664 | 0.035664 | houston | N | 0.035664 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.045779 | houston | -0.050284 | -0.061187 | -0.051543 | -0.029566 | 0.029566 | houston | N | 0.029566 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.045779 | houston | -0.050284 | -0.061187 | -0.051543 | -0.029566 | 0.029566 | houston | N | 0.029566 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.050351 | houston | -0.054856 | -0.065759 | -0.056115 | -0.034138 | 0.034138 | houston | N | 0.034138 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.052246 | houston | -0.056751 | -0.067654 | -0.05801 | -0.036033 | 0.036033 | houston | N | 0.036033 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.052712 | houston | -0.057217 | -0.06812 | -0.058476 | -0.036499 | 0.036499 | houston | N | 0.036499 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.050168 | houston | -0.054673 | -0.065576 | -0.055932 | -0.033955 | 0.033955 | houston | N | 0.033955 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.050747 | houston | -0.055252 | -0.066155 | -0.056511 | -0.034534 | 0.034534 | houston | N | 0.034534 | 0
48855 | SRB_GT21 | B2 | 12 | -0.053124 | houston | -0.057629 | -0.068532 | -0.058888 | -0.036911 | 0.036911 | houston | N | 0.036911 | 0
48855 | SRB_GT21 | MB | 18 | -0.053124 | houston | -0.057629 | -0.068532 | -0.058888 | -0.036911 | 0.036911 | houston | N | 0.036911 | 0
48865 | TECO_GT1 | 1 | 50 | 0.18912 | houston | 0.18461 | 0.17371 | 0.18335 | 0.20533 | 0.17371 | south | Y | 0.20533 | 1.5811
48873 | THW_ST3_ | 3 | 104 | -0.027488 | houston | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48874 | THW_ST4_ | 4 | 104 | -0.027488 | houston | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48875 | THW_3132 | A | 54 | -0.027488 | houston | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48875 | THW_3132 | B | 53 | -0.027488 | houston | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48877 | THW_3334 | C | 54 | -0.027488 | houston | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48877 | THW_3334 | D | 57 | -0.027488 | houston | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48879 | THW_4142 | E | 54 | -0.027488 | houston | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48879 | THW_4142 | F | 54 | -0.027488 | houston | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48881 | THW_4344 | G | 58 | -0.027488 | houston | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48881 | THW_4344 | H | 58 | -0.027488 | houston | -0.031993 | -0.042896 | -0.033252 | -0.011275 | 0.011275 | houston | N | 0.011275 | 0
48883 | THW_GT1_ | B2 | 12 | -0.042233 | houston | -0.046738 | -0.057641 | -0.047997 | -0.02602 | 0.02602 | houston | N | 0.02602 | 0
48885 | THW_5152 | A | 56 | -0.023667 | houston | -0.028172 | -0.039075 | -0.029431 | -0.0074537 | 0.0074537 | houston | N | 0.0074537 | 0
48885 | THW_5152 | B | 59 | -0.023667 | houston | -0.028172 | -0.039075 | -0.029431 | -0.0074537 | 0.0074537 | houston | N | 0.0074537 | 0
48886 | THW_5354 | C | 56 | -0.023667 | houston | -0.028172 | -0.039075 | -0.029431 | -0.0074537 | 0.0074537 | houston | N | 0.0074537 | 0
48886 | THW_5354 | D | 56 | -0.023667 | houston | -0.028172 | -0.039075 | -0.029431 | -0.0074537 | 0.0074537 | houston | N | 0.0074537 | 0
48887 | THW_5556 | E | 59 | -0.023667 | houston | -0.028172 | -0.039075 | -0.029431 | -0.0074537 | 0.0074537 | houston | N | 0.0074537 | 0
48887 | THW_5556 | F | 56 | -0.023667 | houston | -0.028172 | -0.039075 | -0.029431 | -0.0074537 | 0.0074537 | houston | N | 0.0074537 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.031697 | houston | 0.027192 | 0.016289 | 0.025933 | 0.04791 | 0.016289 | south | Y | 0.04791 | 2.087
48921 | WAP_GN1_ | 1 | 161 | 0.067054 | houston | 0.062549 | 0.051646 | 0.06129 | 0.083267 | 0.051646 | south | Y | 0.083267 | 5.091
48922 | WAP_GN2_ | 2 | 166 | 0.067054 | houston | 0.062549 | 0.051646 | 0.06129 | 0.083267 | 0.051646 | south | Y | 0.083267 | 5.2491
48923 | WAP_GN3_ | 3 | 248 | 0.067054 | houston | 0.062549 | 0.051646 | 0.06129 | 0.083267 | 0.051646 | south | Y | 0.083267 | 7.842
48924 | WAP_GN4_ | 4 | 546 | 0.067054 | houston | 0.062549 | 0.051646 | 0.06129 | 0.083267 | 0.051646 | south | Y | 0.083267 | 17.2651
48925 | WAP_GN5_ | 5 | 643 | 0.067054 | houston | 0.062549 | 0.051646 | 0.06129 | 0.083267 | 0.051646 | south | Y | 0.083267 | 20.3324
48926 | WAP_GN6_ | 6 | 651 | 0.025358 | houston | 0.020853 | 0.0099502 | 0.019594 | 0.041571 | 0.0099502 | south | Y | 0.041571 | 20.5853
48927 | WAP_GN7_ | 7 | 564 | 0.025358 | houston | 0.020853 | 0.0099502 | 0.019594 | 0.041571 | 0.0099502 | south | Y | 0.041571 | 17.8343
48928 | WAP_GN8_ | 8 | 600 | 0.025358 | houston | 0.020853 | 0.0099502 | 0.019594 | 0.041571 | 0.0099502 | south | Y | 0.041571 | 18.9727
48929 | WAPGT21_ | B1 | 13 | 0.067054 | houston | 0.062549 | 0.051646 | 0.06129 | 0.083267 | 0.051646 | south | Y | 0.083267 | 0.41107
48940 | WARVUE_G | G1 | 12 | -0.062677 | houston | -0.067182 | -0.078085 | -0.068441 | -0.046464 | 0.046464 | houston | N | 0.046464 | 0
49803 | EXN_15GT | 1 | 34 | -0.062257 | houston | -0.066762 | -0.077665 | -0.068021 | -0.046044 | 0.046044 | houston | N | 0.046044 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.062257 | houston | -0.066762 | -0.077665 | -0.068021 | -0.046044 | 0.046044 | houston | N | 0.046044 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.062257 | houston | -0.066762 | -0.077665 | -0.068021 | -0.046044 | 0.046044 | houston | N | 0.046044 | 0
49826 | EXN938GT | 5 | 45.9 | -0.062257 | houston | -0.066762 | -0.077665 | -0.068021 | -0.046044 | 0.046044 | houston | N | 0.046044 | 0
49828 | EXN941GT | 10 | 17.7 | -0.062257 | houston | -0.066762 | -0.077665 | -0.068021 | -0.046044 | 0.046044 | houston | N | 0.046044 | 0
49829 | EXN942GT | 11 | 20.4 | -0.062257 | houston | -0.066762 | -0.077665 | -0.068021 | -0.046044 | 0.046044 | houston | N | 0.046044 | 0
49830 | EXN943GT | 12 | 19.9 | -0.062257 | houston | -0.066762 | -0.077665 | -0.068021 | -0.046044 | 0.046044 | houston | N | 0.046044 | 0
49831 | EXN944GT | 13 | 35 | -0.062257 | houston | -0.066762 | -0.077665 | -0.068021 | -0.046044 | 0.046044 | houston | N | 0.046044 | 0
49832 | EXN945GT | 9 | 18 | -0.062257 | houston | -0.066762 | -0.077665 | -0.068021 | -0.046044 | 0.046044 | houston | N | 0.046044 | 0
49837 | EXN_GT | 4 | 85.4 | -0.062257 | houston | -0.066762 | -0.077665 | -0.068021 | -0.046044 | 0.046044 | houston | N | 0.046044 | 0
49838 | EXN_14GT | 14 | 148 | -0.062257 | houston | -0.066762 | -0.077665 | -0.068021 | -0.046044 | 0.046044 | houston | N | 0.046044 | 0
49851 | DOW17000 | 37 | 62 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 1.9605
49858 | DOW38100 | 31 | 71.4 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 2.2577
49859 | DOW38200 | 33 | 45 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 1.4229
49860 | DOW38300 | 32 | 101 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 3.1937
49862 | DOW39100 | 36 | 86 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 2.7194
49863 | DOW39200 | 35 | 88 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 2.7827
49865 | DOW41000 | 41 | 50 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 1.5811
49866 | DOW42000 | 42 | 18 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 0.56918
49869 | DOW49000 | 45 | 94 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 2.9724
49870 | DOW61000 | 61 | 70 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 2.2135
49871 | DOW62000 | 62 | 63 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 1.9921
49872 | DOW63000 | 63 | 72 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 2.2767
49873 | DOW64000 | 64 | 64.8 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 2.049
49876 | DOW65000 | 65 | 101 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 3.1937
49877 | DOW66000 | 66 | 97 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 3.0672
49878 | DOW67000 | 67 | 103 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 3.257
49882 | DOW81000 | 81 | 76 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 2.4032
49884 | DOW82000 | 82 | 80 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 2.5297
49885 | DOW83000 | 83 | 80 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 2.5297
49886 | DOW84000 | 84 | 171 | 0.018583 | houston | 0.014078 | 0.0031752 | 0.012819 | 0.034796 | 0.0031752 | south | Y | 0.034796 | 5.4072
58909 | PEARSALL | 1 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58909 | PEARSALL | 2 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58909 | PEARSALL | 3 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58909 | PEARSALL | 4 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58909 | PEARSALL | 5 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58909 | PEARSALL | 6 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58919 | PEARSALL | 1 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58919 | PEARSALL | 2 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58919 | PEARSALL | 3 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58919 | PEARSALL | 4 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58919 | PEARSALL | 5 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58919 | PEARSALL | 6 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58929 | PEARSALL | 1 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58929 | PEARSALL | 2 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58929 | PEARSALL | 3 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58929 | PEARSALL | 4 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58929 | PEARSALL | 5 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58929 | PEARSALL | 6 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58949 | PEARSALL | 1 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58949 | PEARSALL | 2 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58949 | PEARSALL | 3 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58949 | PEARSALL | 4 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58949 | PEARSALL | 5 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
58949 | PEARSALL | 6 | 8.4 | 0.015841 | south | 0.011336 | 0.0004332 | 0.010077 | 0.032054 | 0.0004332 | south | N | 0.0004332 | 0
60000 | DSKY2 | 1 | 76.5 | 0.006432 | west | 0.0019274 | -0.0089758 | 0.00066848 | 0.022645 | 0.00066848 | west | N | 0.00066848 | 0
60003 | KING_NE1 | 1 | 80 | 0.006246 | west | 0.0017414 | -0.0091618 | 0.00048248 | 0.022459 | 0.00048248 | west | N | 0.00048248 | 0
60005 | KING_SE1 | 1 | 40 | 0.006246 | west | 0.0017414 | -0.0091618 | 0.00048248 | 0.022459 | 0.00048248 | west | N | 0.00048248 | 0
60007 | KING_SW1 | 1 | 80 | 0.006216 | west | 0.0017114 | -0.0091918 | 0.00045248 | 0.022429 | 0.00045248 | west | N | 0.00045248 | 0
60016 | WOODWRD1 | 1 | 80 | 0.006253 | west | 0.0017484 | -0.0091548 | 0.00048948 | 0.022466 | 0.00048948 | west | N | 0.00048948 | 0
60017 | ORNNWP1 | 1 | 80 | 0.006407 | west | 0.0019024 | -0.0090008 | 0.00064348 | 0.02262 | 0.00064348 | west | N | 0.00064348 | 0
60018 | DSKY1 | 1 | 84 | 0.006458 | west | 0.0019534 | -0.0089498 | 0.00069448 | 0.022671 | 0.00069448 | west | N | 0.00069448 | 0
60019 | KING_NW1 | 1 | 80 | 0.006216 | west | 0.0017114 | -0.0091918 | 0.00045248 | 0.022429 | 0.00045248 | west | N | 0.00045248 | 0
60057 | CALLAHAN | 1 | 114 | 0.015088 | south | 0.010583 | -0.0003198 | 0.0093245 | 0.031301 | 0.0003198 | south | N | 0.0003198 | 0
60058 | BUFF_GAP | 1 | 120 | 0.005716 | west | 0.0012114 | -0.0096918 | -4.7518e-05 | 0.021929 | 4.7518e-05 | west | N | 4.7518e-05 | 0
60060 | CIRELLO | 1 | 233 | 0.005716 | west | 0.0012114 | -0.0096918 | -4.7518e-05 | 0.021929 | 4.7518e-05 | west | N | 4.7518e-05 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.005716 | west | 0.0012114 | -0.0096918 | -4.7518e-05 | 0.021929 | 4.7518e-05 | west | N | 4.7518e-05 | 0
60066 | H_HOLLOW | 1 | 222 | 0.015088 | south | 0.010583 | -0.0003198 | 0.0093245 | 0.031301 | 0.0003198 | south | N | 0.0003198 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.015088 | south | 0.010583 | -0.0003198 | 0.0093245 | 0.031301 | 0.0003198 | south | N | 0.0003198 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.015088 | south | 0.010583 | -0.0003198 | 0.0093245 | 0.031301 | 0.0003198 | south | N | 0.0003198 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.015088 | south | 0.010583 | -0.0003198 | 0.0093245 | 0.031301 | 0.0003198 | south | N | 0.0003198 | 0
60074 | HORSH5 | 1 | 100 | 0.015088 | south | 0.010583 | -0.0003198 | 0.0093245 | 0.031301 | 0.0003198 | south | N | 0.0003198 | 0
60081 | WHRLWIND | 1 | 60 | 0.005578 | west | 0.0010734 | -0.0098298 | -0.00018552 | 0.021791 | 0.00018552 | west | N | 0.00018552 | 0
60201 | RIO DRCS | F | 0 | 0.011262 | south | 0.0067574 | -0.0041458 | 0.0054985 | 0.027475 | 0.0041458 | south | N | 0.0041458 | 0
60202 | FRIEND_R | F | 0 | 0.007263 | west | 0.0027584 | -0.0081448 | 0.0014995 | 0.023476 | 0.0014995 | west | N | 0.0014995 | 0
60203 | PRES0A | BT | 4.8 | 0.006105 | west | 0.0016004 | -0.0093028 | 0.00034148 | 0.022318 | 0.00034148 | west | N | 0.00034148 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.00564 | west | 0.0011354 | -0.0097678 | -0.00012352 | 0.021853 | 0.00012352 | west | N | 0.00012352 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.00564 | west | 0.0011354 | -0.0097678 | -0.00012352 | 0.021853 | 0.00012352 | west | N | 0.00012352 | 0
71057 | L_SWEETW | W1 | 135 | 0.00564 | west | 0.0011354 | -0.0097678 | -0.00012352 | 0.021853 | 0.00012352 | west | N | 0.00012352 | 0
71059 | L_SWEETW | W1 | 119 | 0.00564 | west | 0.0011354 | -0.0097678 | -0.00012352 | 0.021853 | 0.00012352 | west | N | 0.00012352 | 0
71060 | L_SWEETW | W1 | 105 | 0.00564 | west | 0.0011354 | -0.0097678 | -0.00012352 | 0.021853 | 0.00012352 | west | N | 0.00012352 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.00564 | west | 0.0011354 | -0.0097678 | -0.00012352 | 0.021853 | 0.00012352 | west | N | 0.00012352 | 0
76031 | L_GASCCR | W1 | 150 | 0.005761 | west | 0.0012564 | -0.0096468 | -2.5178e-06 | 0.021974 | 2.5178e-06 | west | N | 2.5178e-06 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.005776 | west | 0.0012714 | -0.0096318 | 1.2482e-05 | 0.021989 | 1.2482e-05 | west | N | 1.2482e-05 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.005776 | west | 0.0012714 | -0.0096318 | 1.2482e-05 | 0.021989 | 1.2482e-05 | west | N | 1.2482e-05 | 0
76096 | L_CAPRSI | W1 | 186 | 0.005776 | west | 0.0012714 | -0.0096318 | 1.2482e-05 | 0.021989 | 1.2482e-05 | west | N | 1.2482e-05 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.005776 | west | 0.0012714 | -0.0096318 | 1.2482e-05 | 0.021989 | 1.2482e-05 | west | N | 1.2482e-05 | 0
80003 | MILHWYS | F | 0 | 0.017626 | south | 0.013121 | 0.0022182 | 0.011862 | 0.033839 | 0.0022182 | south | N | 0.0022182 | 0
80010 | EPLVT1 | F | 0 | 0.014324 | south | 0.0098194 | -0.0010838 | 0.0085605 | 0.030537 | 0.0010838 | south | N | 0.0010838 | 0
80012 | LAR | F | 0 | 0.01642 | south | 0.011915 | 0.0010122 | 0.010656 | 0.032633 | 0.0010122 | south | N | 0.0010122 | 0
80051 | FORPVCM0 | 8 | 28 | 0.01955 | south | 0.015045 | 0.0041422 | 0.013786 | 0.035763 | 0.0041422 | south | N | 0.0041422 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.01955 | south | 0.015045 | 0.0041422 | 0.013786 | 0.035763 | 0.0041422 | south | N | 0.0041422 | 0
80053 | FOR69CG0 | 10 | 74 | 0.01955 | south | 0.015045 | 0.0041422 | 0.013786 | 0.035763 | 0.0041422 | south | N | 0.0041422 | 0
80080 | GWINDT11 | 1 | 94 | 0.01764 | south | 0.013135 | 0.0022322 | 0.011876 | 0.033853 | 0.0022322 | south | N | 0.0022322 | 0
80080 | GWINDT11 | 2 | 41 | 0.01764 | south | 0.013135 | 0.0022322 | 0.011876 | 0.033853 | 0.0022322 | south | N | 0.0022322 | 0
80080 | GWINDT11 | 3 | 38 | 0.01764 | south | 0.013135 | 0.0022322 | 0.011876 | 0.033853 | 0.0022322 | south | N | 0.0022322 | 0
80080 | GWINDT11 | 4 | 19 | 0.01764 | south | 0.013135 | 0.0022322 | 0.011876 | 0.033853 | 0.0022322 | south | N | 0.0022322 | 0
80081 | GWINDT21 | 1 | 94 | 0.01764 | south | 0.013135 | 0.0022322 | 0.011876 | 0.033853 | 0.0022322 | south | N | 0.0022322 | 0
80081 | GWINDT21 | 2 | 36 | 0.01764 | south | 0.013135 | 0.0022322 | 0.011876 | 0.033853 | 0.0022322 | south | N | 0.0022322 | 0
80081 | GWINDT21 | 3 | 43 | 0.01764 | south | 0.013135 | 0.0022322 | 0.011876 | 0.033853 | 0.0022322 | south | N | 0.0022322 | 0
80081 | GWINDT21 | 4 | 22 | 0.01764 | south | 0.013135 | 0.0022322 | 0.011876 | 0.033853 | 0.0022322 | south | N | 0.0022322 | 0
80137 | CSDR89 | 8 | 39 | 0.019053 | south | 0.014548 | 0.0036452 | 0.013289 | 0.035266 | 0.0036452 | south | N | 0.0036452 | 0
80137 | CSDR89 | 9 | 15 | 0.019053 | south | 0.014548 | 0.0036452 | 0.013289 | 0.035266 | 0.0036452 | south | N | 0.0036452 | 0
80138 | CSDR7 | 7 | 7 | 0.019053 | south | 0.014548 | 0.0036452 | 0.013289 | 0.035266 | 0.0036452 | south | N | 0.0036452 | 0
80139 | CSDR56 | 5 | 15 | 0.019053 | south | 0.014548 | 0.0036452 | 0.013289 | 0.035266 | 0.0036452 | south | N | 0.0036452 | 0
80139 | CSDR56 | 6 | 39 | 0.019053 | south | 0.014548 | 0.0036452 | 0.013289 | 0.035266 | 0.0036452 | south | N | 0.0036452 | 0
80140 | CSDR11 | 11 | 39 | 0.019053 | south | 0.014548 | 0.0036452 | 0.013289 | 0.035266 | 0.0036452 | south | N | 0.0036452 | 0
80180 | PNSCALT1 | 1 | 148 | 0.01764 | south | 0.013135 | 0.0022322 | 0.011876 | 0.033853 | 0.0022322 | south | N | 0.0022322 | 0
80180 | PNSCALT1 | 2 | 50 | 0.01764 | south | 0.013135 | 0.0022322 | 0.011876 | 0.033853 | 0.0022322 | south | N | 0.0022322 | 0
80181 | PNSCALT2 | 1 | 55 | 0.01764 | south | 0.013135 | 0.0022322 | 0.011876 | 0.033853 | 0.0022322 | south | N | 0.0022322 | 0
80181 | PNSCALT2 | 2 | 50 | 0.01764 | south | 0.013135 | 0.0022322 | 0.011876 | 0.033853 | 0.0022322 | south | N | 0.0022322 | 0
80223 | REYSHR G | 1 | 12 | 0.017923 | south | 0.013418 | 0.0025152 | 0.012159 | 0.034136 | 0.0025152 | south | N | 0.0025152 | 0
80224 | VISTRONG | 1 | 15 | 0.018917 | south | 0.014412 | 0.0035092 | 0.013153 | 0.03513 | 0.0035092 | south | N | 0.0035092 | 0
80225 | VISTRONG | 2 | 23 | 0.018917 | south | 0.014412 | 0.0035092 | 0.013153 | 0.03513 | 0.0035092 | south | N | 0.0035092 | 0
80226 | ALCOA G | 1 | 48 | 0.019439 | south | 0.014934 | 0.0040312 | 0.013675 | 0.035652 | 0.0040312 | south | N | 0.0040312 | 0
80227 | AIRCO G | 1 | 8 | 0.01896 | south | 0.014455 | 0.0035522 | 0.013196 | 0.035173 | 0.0035522 | south | N | 0.0035522 | 0
80261 | NBEC81A | 1 | 180 | 0.01779 | south | 0.013285 | 0.0023822 | 0.012026 | 0.034003 | 0.0023822 | south | N | 0.0023822 | 0
80262 | NBEC91A | 1 | 180 | 0.017793 | south | 0.013288 | 0.0023852 | 0.012029 | 0.034006 | 0.0023852 | south | N | 0.0023852 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.017764 | south | 0.013259 | 0.0023562 | 0.012 | 0.033977 | 0.0023562 | south | N | 0.0023562 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.017764 | south | 0.013259 | 0.0023562 | 0.012 | 0.033977 | 0.0023562 | south | N | 0.0023562 | 0
80265 | LARECU40 | 4 | 100 | 0.016419 | south | 0.011914 | 0.0010112 | 0.010655 | 0.032632 | 0.0010112 | south | N | 0.0010112 | 0
80266 | LARECU50 | 5 | 100 | 0.016419 | south | 0.011914 | 0.0010112 | 0.010655 | 0.032632 | 0.0010112 | south | N | 0.0010112 | 0
80291 | PAPALOTE | 1 | 25 | 0.01786 | south | 0.013355 | 0.0024522 | 0.012096 | 0.034073 | 0.0024522 | south | N | 0.0024522 | 0
80291 | PAPALOTE | 2 | 25 | 0.01786 | south | 0.013355 | 0.0024522 | 0.012096 | 0.034073 | 0.0024522 | south | N | 0.0024522 | 0
80291 | PAPALOTE | 3 | 25 | 0.01786 | south | 0.013355 | 0.0024522 | 0.012096 | 0.034073 | 0.0024522 | south | N | 0.0024522 | 0
80291 | PAPALOTE | 4 | 16 | 0.01786 | south | 0.013355 | 0.0024522 | 0.012096 | 0.034073 | 0.0024522 | south | N | 0.0024522 | 0
80294 | PAPALOTE | 5 | 25 | 0.01786 | south | 0.013355 | 0.0024522 | 0.012096 | 0.034073 | 0.0024522 | south | N | 0.0024522 | 0
80294 | PAPALOTE | 6 | 25 | 0.01786 | south | 0.013355 | 0.0024522 | 0.012096 | 0.034073 | 0.0024522 | south | N | 0.0024522 | 0
80294 | PAPALOTE | 7 | 25 | 0.01786 | south | 0.013355 | 0.0024522 | 0.012096 | 0.034073 | 0.0024522 | south | N | 0.0024522 | 0
80294 | PAPALOTE | 8 | 15 | 0.01786 | south | 0.013355 | 0.0024522 | 0.012096 | 0.034073 | 0.0024522 | south | N | 0.0024522 | 0
86104 | CID-138 | EQ | 0 | 0.016419 | south | 0.011914 | 0.0010112 | 0.010655 | 0.032632 | 0.0010112 | south | N | 0.0010112 | 0
86105 | CID-230 | EQ | 500 | 0.016419 | south | 0.011914 | 0.0010112 | 0.010655 | 0.032632 | 0.0010112 | south | N | 0.0010112 | 0
86106 | CUF-230 | EQ | 500 | 0.016419 | south | 0.011914 | 0.0010112 | 0.010655 | 0.032632 | 0.0010112 | south | N | 0.0010112 | 0
86107 | CUF-138 | EQ | 0 | 0.016419 | south | 0.011914 | 0.0010112 | 0.010655 | 0.032632 | 0.0010112 | south | N | 0.0010112 | 0
88198 | BEEVILLE | F | 0 | 0.017305 | south | 0.0128 | 0.0018972 | 0.011541 | 0.033518 | 0.0018972 | south | N | 0.0018972 | 0
88253 | HAMILTON | F | 0 | 0.013223 | south | 0.0087184 | -0.0021848 | 0.0074595 | 0.029436 | 0.0021848 | south | N | 0.0021848 | 0
88299 | ZAPATA | F | 0 | 0.016895 | south | 0.01239 | 0.0014872 | 0.011131 | 0.033108 | 0.0014872 | south | N | 0.0014872 | 0
88508 | FALFURRI | F | 0 | 0.017392 | south | 0.012887 | 0.0019842 | 0.011628 | 0.033605 | 0.0019842 | south | N | 0.0019842 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Midtown Reit - Polk 138kV [47707-47730] C:Singleton - Tomball 345kV [44645-46500] & Roans - King 345kV [40600-45972] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.18912 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 9.4559 | 50 | 0.18461 | 9.2307 | 50 | 9.2307
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.067054 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 10.7957 | 161 | 0.062549 | 10.0705 | 211 | 19.3011
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.067054 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 11.131 | 166 | 0.062549 | 10.3832 | 377 | 29.6843
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.067054 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 16.6294 | 248 | 0.062549 | 15.5123 |  |  | Weighted Shift Factors
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.067054 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 36.6115 | 546 | 0.062549 | 34.152 |  |  | North | 0.0045046
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.067054 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 43.1157 | 0 | 0.062549 | 0 |  |  | Houston | -0.027912
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.067054 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.8717 | 13 | 0.062549 | 0.81314 |  |  |  | 0.032416
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.04153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.6098 | 0 | 0.037025 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.04153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.6098 | 0 | 0.037025 | 0 |  |  | Line Rating | 251
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.04153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.9421 | 0 | 0.037025 | 0 |  |  | Conc Gen | 377
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.04153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.5475 | 0 | 0.037025 | 0 |  |  | Weighted Imp. | 29.6843
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.031697 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 2.092 | 66 | 0.027192 | 1.7947 |  |  | PTDF | 0.078738
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.029878 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.1213 | 0 | 0.025373 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.029878 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29878 | 0 | 0.025373 | 0 |  |  | Concentration | 2.429
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.1849 | 76 | 0.024244 | 1.8426
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.1849 | 76 | 0.024244 | 1.8426
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.0186 | 105 | 0.024244 | 2.5457
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.1274 | 74 | 0.024244 | 1.7941
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.1274 | 74 | 0.024244 | 1.7941
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.9324 | 102 | 0.024244 | 2.4729
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.025815 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.2078 | 0 | 0.02131 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.025815 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.2078 | 0 | 0.02131 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.025815 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 6.3247 | 0 | 0.02131 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 1.5088 | 100 | 0.043 | 4.3
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.025358 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 16.5081 | 651 | 0.020853 | 13.5756
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.025358 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 14.3019 | 564 | 0.020853 | 11.7613
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.025358 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 15.2148 | 600 | 0.020853 | 12.5121
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.011262 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.039174 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.020787 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95828 | 0 | 0.016282 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.02051 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 27.3398 | 0 | 0.016005 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.02051 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 27.2373 | 0 | 0.016005 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5445 | 0 | 0.015045 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5836 | 0 | 0.015045 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5445 | 0 | 0.015045 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.564 | 0 | 0.015045 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5327 | 0 | 0.015045 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.48875 | 0 | 0.015045 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.8993 | 0 | 0.015045 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.5474 | 0 | 0.015045 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.85238 | 0 | 0.015045 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.4467 | 0 | 0.015045 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.019439 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.93307 | 0 | 0.014934 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.53348 | 0 | 0.014548 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13337 | 0 | 0.014548 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.74307 | 0 | 0.014548 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.2858 | 0 | 0.014548 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13337 | 0 | 0.014548 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.2858 | 0 | 0.014548 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.74307 | 0 | 0.014548 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.74307 | 0 | 0.014548 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.01896 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15168 | 0 | 0.014455 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.018917 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.28375 | 0 | 0.014412 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.018917 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.43509 | 0 | 0.014412 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.018744 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.3683 | 0 | 0.014239 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.01873 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.41206 | 22 | 0.014225 | 0.31296
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.01873 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20603 | 11 | 0.014225 | 0.15648
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.01873 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20603 | 11 | 0.014225 | 0.15648
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.018703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.89213 | 47.7 | 0.014198 | 0.67727
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.018703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.69762 | 37.3 | 0.014198 | 0.5296
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.018703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.86034 | 46 | 0.014198 | 0.65313
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.018703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.89774 | 48 | 0.014198 | 0.68152
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.018624 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.6819 | 144 | 0.014119 | 2.0332
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.018624 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.5013 | 188 | 0.014119 | 2.6545
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1521 | 0 | 0.014078 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3268 | 0 | 0.014078 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.83623 | 0 | 0.014078 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8769 | 0 | 0.014078 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5981 | 0 | 0.014078 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6353 | 0 | 0.014078 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.92915 | 0 | 0.014078 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33449 | 0 | 0.014078 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.7468 | 0 | 0.014078 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3008 | 0 | 0.014078 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1707 | 0 | 0.014078 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.338 | 0 | 0.014078 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2042 | 0 | 0.014078 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8769 | 0 | 0.014078 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8026 | 0 | 0.014078 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.914 | 0 | 0.014078 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4123 | 0 | 0.014078 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4866 | 0 | 0.014078 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4866 | 0 | 0.014078 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1777 | 0 | 0.014078 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.007817 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1725 | 150 | 0.035729 | 5.3593
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.8318 | 0 | 0.013418 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.7422 | 0 | 0.013418 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -1 | 1.7923 | 0 | 0.013418 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.5988 | 0 | 0.013418 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6347 | 0 | 0.013418 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.2762 | 0 | 0.013418 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.017923 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.21508 | 0 | 0.013418 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4465 | 25 | 0.013355 | 0.33389
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4465 | 25 | 0.013355 | 0.33389
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4465 | 25 | 0.013355 | 0.33389
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.28576 | 16 | 0.013355 | 0.21369
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4465 | 25 | 0.013355 | 0.33389
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4465 | 25 | 0.013355 | 0.33389
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4465 | 25 | 0.013355 | 0.33389
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.2679 | 15 | 0.013355 | 0.20033
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.017793 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.9784 | 336 | 0.013288 | 4.4649
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.017793 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2027 | 180 | 0.013288 | 2.3919
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.017792 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6386 | 0 | 0.013287 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.017792 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6439 | 0 | 0.013287 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.017792 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.7222 | 0 | 0.013287 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.01779 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2022 | 180 | 0.013285 | 2.3914
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.01777 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.44425 | 0 | 0.013265 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.01777 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.44425 | 0 | 0.013265 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.017764 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.9332 | 334 | 0.013259 | 4.4286
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.017764 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.0398 | 340 | 0.013259 | 4.5082
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.017764 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1975 | 180 | 0.013259 | 2.3867
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.017764 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1975 | 180 | 0.013259 | 2.3867
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.017761 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.67492 | 0 | 0.013256 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.017755 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.67469 | 0 | 0.01325 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.017727 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.1503 | 629 | 0.013222 | 8.3169
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.017677 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.51263 | 0 | 0.013172 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.007263 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.035175 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.6582 | 94 | 0.013135 | 1.2347
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.72324 | 41 | 0.013135 | 0.53855
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.67032 | 38 | 0.013135 | 0.49915
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.33516 | 19 | 0.013135 | 0.24957
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.6582 | 94 | 0.013135 | 1.2347
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.63504 | 36 | 0.013135 | 0.47288
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.75852 | 43 | 0.013135 | 0.56482
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.38808 | 22 | 0.013135 | 0.28898
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.6107 | 148 | 0.013135 | 1.944
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.882 | 50 | 0.013135 | 0.65677
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.9702 | 55 | 0.013135 | 0.72245
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.882 | 50 | 0.013135 | 0.65677
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.017626 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.013121 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.017626 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.66979 | 38 | 0.013121 | 0.49861
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.017626 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34018 | 19.3 | 0.013121 | 0.25324
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.017626 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.26439 | 15 | 0.013121 | 0.19682
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.017626 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.82842 | 47 | 0.013121 | 0.61671
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.017587 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5325 | 144 | 0.013082 | 1.8839
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.017587 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5325 | 144 | 0.013082 | 1.8839
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.017587 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0074 | 171 | 0.013082 | 2.2371
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.017586 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.6403 | 207 | 0.013081 | 2.7079
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.017586 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8109 | 216.7 | 0.013081 | 2.8347
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.017586 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.2558 | 242 | 0.013081 | 3.1657
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.017533 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5686 | 146.5 | 0.013028 | 1.9087
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.017533 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5931 | 147.9 | 0.013028 | 1.9269
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.017533 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0332 | 173 | 0.013028 | 2.2539
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.017392 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012887 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.006945 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034857 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.006945 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034857 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.017305 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0128 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.006858 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.03477 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.006858 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.3972 | 787 | 0.03477 | 27.3639
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.017207 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20648 | 0 | 0.012702 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.017207 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18928 | 0 | 0.012702 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.017207 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20648 | 0 | 0.012702 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.006728 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7156 | 255 | 0.03464 | 8.8332
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.006728 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0025 | 149 | 0.03464 | 5.1613
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.006728 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0294 | 153 | 0.03464 | 5.2999
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.006615 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.99225 | 150 | 0.034527 | 5.179
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.006615 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.5292 | 80 | 0.034527 | 2.7622
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.016897 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5576 | 0 | 0.012392 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.016895 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.01239 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.006458 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.54247 | 84 | 0.03437 | 2.8871
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.006432 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49205 | 76.5 | 0.034344 | 2.6273
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006407 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51256 | 80 | 0.034319 | 2.7455
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.006356 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.09534 | 0 | 0.034268 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.006356 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.09534 | 0 | 0.034268 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.006257 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.93855 | 150 | 0.034169 | 5.1253
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.006257 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.93855 | 150 | 0.034169 | 5.1253
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.006254 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.50032 | 80 | 0.034166 | 2.7333
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006253 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.50024 | 80 | 0.034165 | 2.7332
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.006246 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.46845 | 75 | 0.034158 | 2.5618
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006246 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49968 | 80 | 0.034158 | 2.7326
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.006246 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.24984 | 40 | 0.034158 | 1.3663
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006216 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49728 | 80 | 0.034128 | 2.7302
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006216 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49728 | 80 | 0.034128 | 2.7302
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.006105 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.029304 | 0 | 0.034017 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.01642 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011915 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.016419 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6419 | 100 | 0.011914 | 1.1914
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.016419 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6419 | 100 | 0.011914 | 1.1914
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.016419 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011914 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.016419 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011914 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.016419 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011914 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.016419 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011914 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.016379 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.4861 | 396 | 0.011874 | 4.7023
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38524 | 66 | 0.033749 | 2.2274
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.3794 | 65 | 0.033749 | 2.1937
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39108 | 67 | 0.033749 | 2.2612
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39108 | 67 | 0.033749 | 2.2612
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39108 | 67 | 0.033749 | 2.2612
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.005837 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033749 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.005837 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033749 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.016227 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19472 | 0 | 0.011722 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.005834 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.20419 | 35 | 0.033746 | 1.1811
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.005834 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.17502 | 30 | 0.033746 | 1.0124
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.005823 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.987 | 169.5 | 0.033735 | 5.7181
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.005821 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.86733 | 149 | 0.033733 | 5.0262
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.005798 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.038267 | 6.6 | 0.03371 | 0.22249
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.005798 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.19887 | 34.3 | 0.03371 | 1.1562
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.005776 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6498 | 112.5 | 0.033688 | 3.7899
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.005776 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.86351 | 149.5 | 0.033688 | 5.0363
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.005776 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0743 | 186 | 0.033688 | 6.2659
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.005776 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.239 | 214.5 | 0.033688 | 7.2261
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2001 | 208.2 | 0.033676 | 7.0113
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.81906 | 142.1 | 0.033676 | 4.7853
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.76315 | 132.4 | 0.033676 | 4.4587
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.7839 | 136 | 0.033676 | 4.5799
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.84731 | 147 | 0.033676 | 4.9504
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2104 | 210 | 0.033676 | 7.0719
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.40348 | 70 | 0.033676 | 2.3573
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.40348 | 70 | 0.033676 | 2.3573
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.5349 | 92.8 | 0.033676 | 3.1251
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.46112 | 80 | 0.033676 | 2.6941
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.46112 | 80 | 0.033676 | 2.6941
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.66286 | 115 | 0.033676 | 3.8727
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.005762 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.3342 | 58 | 0.033674 | 1.9531
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.005761 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.86415 | 150 | 0.033673 | 5.0509
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.00576 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.57888 | 100.5 | 0.033672 | 3.384
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.005752 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2321 | 214.2 | 0.033664 | 7.2108
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.005747 | west | 8 | N | N | Nwest | Nwest | 1 | 0.14827 | 0 | 0.033659 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.005724 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68688 | 120 | 0.033636 | 4.0363
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.005723 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68676 | 120 | 0.033635 | 4.0362
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.005716 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68592 | 120 | 0.033628 | 4.0353
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.005716 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3318 | 233 | 0.033628 | 7.8353
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.005716 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.97286 | 170.2 | 0.033628 | 5.7235
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.005716 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2861 | 225 | 0.033628 | 7.5663
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.005712 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0282 | 180 | 0.033624 | 6.0523
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.005712 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0282 | 180 | 0.033624 | 6.0523
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.005712 | west | 8 | N | N | Nwest | Nwest | 1 | 0.39984 | 0 | 0.033624 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.005712 | west | 8 | N | N | Nwest | Nwest | 1 | 0.41926 | 0 | 0.033624 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.005712 | west | 8 | N | N | Nwest | Nwest | 1 | 0.40212 | 0 | 0.033624 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.855 | 150 | 0.033612 | 5.0418
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.254 | 220 | 0.033612 | 7.3946
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.14 | 200 | 0.033612 | 6.7224
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.69483 | 121.9 | 0.033612 | 4.0973
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.37561 | 66 | 0.033603 | 2.2178
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39268 | 69 | 0.033603 | 2.3186
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39268 | 69 | 0.033603 | 2.3186
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.3813 | 67 | 0.033603 | 2.2514
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.3813 | 67 | 0.033603 | 2.2514
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.36991 | 65 | 0.033603 | 2.1842
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.005688 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.35834 | 63 | 0.0336 | 2.1168
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.005685 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.80158 | 141 | 0.033597 | 4.7372
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.005685 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6822 | 120 | 0.033597 | 4.0316
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.005684 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.56272 | 99 | 0.033596 | 3.326
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.005684 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.34672 | 61 | 0.033596 | 2.0493
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.005684 | west | 7 | N | N | Nwest | Nwest | 1 | 0.1421 | 0 | 0.033596 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.005684 | west | 7 | N | N | Nwest | Nwest | 1 | 0.25976 | 0 | 0.033596 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.005684 | west | 7 | N | N | Nwest | Nwest | 1 | 0.25976 | 0 | 0.033596 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.005674 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.47662 | 84 | 0.033586 | 2.8212
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.005669 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.85035 | 150 | 0.033581 | 5.0371
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.005669 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.57257 | 101 | 0.033581 | 3.3917
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.005661 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.70762 | 125 | 0.033573 | 4.1966
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.005661 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.70762 | 125 | 0.033573 | 4.1966
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.2115 | 37.5 | 0.033552 | 1.2582
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6063 | 107.5 | 0.033552 | 3.6068
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.7614 | 135 | 0.033552 | 4.5295
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.67116 | 119 | 0.033552 | 3.9927
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.5922 | 105 | 0.033552 | 3.5229
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.45402 | 80.5 | 0.033552 | 2.7009
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1775 | 209 | 0.033546 | 7.0111
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.7127 | 126.5 | 0.033546 | 4.2436
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.4029 | 249 | 0.033546 | 8.3529
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1099 | 197 | 0.033546 | 6.6085
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.005632 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8448 | 150 | 0.033544 | 5.0316
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.00562 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.3372 | 60 | 0.033532 | 2.0119
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.005578 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.33468 | 60 | 0.03349 | 2.0094
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.015955 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.38292 | 24 | 0.01145 | 0.27481
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.015955 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.38292 | 24 | 0.01145 | 0.27481
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.015955 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.36696 | 23 | 0.01145 | 0.26336
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.0055 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2 | 400 | 0.033412 | 13.3648
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.0055 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.298 | 236 | 0.033412 | 7.8852
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.015876 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.6683 | 546 | 0.011371 | 6.2088
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.015876 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.907 | 750 | 0.011371 | 8.5286
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.005454 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.89991 | 165 | 0.033366 | 5.5054
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.005415 | west | 4 | Y | N | Ywest | Nwest | 1 | 3.5181 | 649.7 | 0.033327 | 21.6525
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.015802 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4493 | 155 | 0.011297 | 1.7511
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.015802 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.6863 | 170 | 0.011297 | 1.9206
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.015802 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4493 | 155 | 0.011297 | 1.7511
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.005381 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.39281 | 73 | 0.033293 | 2.4304
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.005381 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.64034 | 119 | 0.033293 | 3.9619
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.005381 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.1031 | 205 | 0.033293 | 6.825
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.005381 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.54886 | 102 | 0.033293 | 3.3959
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.005381 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.51658 | 96 | 0.033293 | 3.1961
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.005354 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.2957 | 242 | 0.033266 | 8.0503
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.015733 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.2882 | 209 | 0.011228 | 2.3467
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.015733 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.3983 | 216 | 0.011228 | 2.4253
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.015733 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72372 | 46 | 0.011228 | 0.51651
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.015733 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.73945 | 47 | 0.011228 | 0.52774
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.015733 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72372 | 46 | 0.011228 | 0.51651
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.015733 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72372 | 46 | 0.011228 | 0.51651
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.015724 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.91199 | 58 | 0.011219 | 0.65073
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.015724 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3994 | 89 | 0.011219 | 0.99853
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.015724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.69186 | 44 | 0.011219 | 0.49365
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.015724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.69186 | 44 | 0.011219 | 0.49365
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.015724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.67613 | 43 | 0.011219 | 0.48244
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.015724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.70758 | 45 | 0.011219 | 0.50487
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.005329 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.89527 | 168 | 0.033241 | 5.5845
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.005329 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.47961 | 90 | 0.033241 | 2.9917
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.015716 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.475 | 412 | 0.011211 | 4.6191
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.015716 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.2864 | 400 | 0.011211 | 4.4846
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.015715 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.01121 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.015715 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.01121 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.015715 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.01121 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.015708 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.6602 | 424 | 0.011203 | 4.7503
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.015708 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.6759 | 425 | 0.011203 | 4.7615
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.015708 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.3932 | 407 | 0.011203 | 4.5598
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.005315 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.6378 | 120 | 0.033227 | 3.9872
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.00531 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.9435 | 366 | 0.033222 | 12.1592
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.005305 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.06366 | 0 | 0.033217 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.005305 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.06366 | 0 | 0.033217 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.005302 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.10604 | 20 | 0.033214 | 0.66428
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.005302 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.10604 | 20 | 0.033214 | 0.66428
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.005302 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.10604 | 20 | 0.033214 | 0.66428
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.005302 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.090134 | 17 | 0.033214 | 0.56464
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.005281 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.36967 | 70 | 0.033193 | 2.3235
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.005281 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.36439 | 69 | 0.033193 | 2.2903
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.005281 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.36439 | 69 | 0.033193 | 2.2903
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.005281 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.35911 | 68 | 0.033193 | 2.2571
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.005237 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.094266 | 18 | 0.033149 | 0.59668
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.005237 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.094266 | 18 | 0.033149 | 0.59668
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.005237 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.19901 | 38 | 0.033149 | 1.2597
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.005215 | north | 3 | N | N | Nnorth | Nnorth | 1 | 6.0338 | 0 | 0.033127 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.005215 | north | 3 | N | N | Nnorth | Nnorth | 1 | 6.039 | 0 | 0.033127 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2914 | 147 | 0.011083 | 1.6293
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1511 | 138 | 0.011083 | 1.5295
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1823 | 140 | 0.011083 | 1.5517
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2914 | 147 | 0.011083 | 1.6293
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.837 | 182 | 0.011083 | 2.0172
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0864 | 198 | 0.011083 | 2.1945
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.005196 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1291 | 217.3 | 0.033108 | 7.1943
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.005196 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0652 | 205 | 0.033108 | 6.7871
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.005196 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.4154 | 272.4 | 0.033108 | 9.0186
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.005193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0594 | 204 | 0.033105 | 6.7534
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.005193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0438 | 201 | 0.033105 | 6.6541
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.005193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.2567 | 242 | 0.033105 | 8.0114
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.005179 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033091 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.005148 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.4826 | 288 | 0.03306 | 9.5212
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.005148 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.75676 | 147 | 0.03306 | 4.8598
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.005148 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.75676 | 147 | 0.03306 | 4.8598
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.005141 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1516 | 224 | 0.033053 | 7.4038
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.005141 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1619 | 226 | 0.033053 | 7.47
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.005141 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0899 | 212 | 0.033053 | 7.0072
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.005141 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0848 | 211 | 0.033053 | 6.9742
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.005069 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032981 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.005069 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032981 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.005069 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032981 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.005063 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0956 | 216.4 | 0.032975 | 7.1358
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.005063 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0941 | 216.1 | 0.032975 | 7.1259
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.005051 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.9951 | 395 | 0.032963 | 13.0203
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.005051 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.1972 | 435 | 0.032963 | 14.3389
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.005042 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.56722 | 112.5 | 0.032954 | 3.7073
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.01543 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037032 | 0 | 0.010925 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.01543 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037032 | 0 | 0.010925 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.005035 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.1902 | 435 | 0.032947 | 14.3319
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.004961 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.29766 | 60 | 0.032873 | 1.9724
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.004961 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.31254 | 63 | 0.032873 | 2.071
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.015319 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.061276 | 0 | 0.010814 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.004883 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.95707 | 196 | 0.032795 | 6.4278
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.004883 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.54201 | 111 | 0.032795 | 3.6402
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.015259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1668 | 142 | 0.010754 | 1.5271
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.015259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2126 | 145 | 0.010754 | 1.5594
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.015259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3041 | 151 | 0.010754 | 1.6239
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.015259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.4251 | 290 | 0.010754 | 3.1188
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.004839 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032751 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.015218 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.036523 | 0 | 0.010713 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.015218 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.036523 | 0 | 0.010713 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.015218 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.04261 | 0 | 0.010713 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.004821 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.032733 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.004819 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.56864 | 118 | 0.032731 | 3.8622
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.004819 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.55419 | 115 | 0.032731 | 3.7641
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.004819 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.6794 | 556 | 0.032731 | 18.1984
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.004803 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.19212 | 0 | 0.032715 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.004803 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.19212 | 0 | 0.032715 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.004791 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.81447 | 170 | 0.032703 | 5.5595
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.004791 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.4913 | 520 | 0.032703 | 17.0055
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.004776 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.7671 | 370 | 0.032688 | 12.0945
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.66864 | 0 | 0.032688 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.67342 | 0 | 0.032688 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4758 | 0 | 0.032688 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.68297 | 0 | 0.032688 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.68774 | 0 | 0.032688 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4806 | 0 | 0.032688 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7632 | 160 | 0.032682 | 5.2291
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74412 | 156 | 0.032682 | 5.0984
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.93492 | 196 | 0.032682 | 6.4056
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74412 | 156 | 0.032682 | 5.0984
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74889 | 157 | 0.032682 | 5.1311
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.94446 | 198 | 0.032682 | 6.471
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.004765 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.35737 | 0 | 0.032677 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.004765 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.37929 | 0 | 0.032677 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.004765 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.42123 | 0 | 0.032677 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.004758 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.655 | 558 | 0.03267 | 18.2298
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.004758 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.7549 | 579 | 0.03267 | 18.9159
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.004758 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.8445 | 808 | 0.03267 | 26.3973
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.00475 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.37525 | 79 | 0.032662 | 2.5803
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.00475 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.5035 | 106 | 0.032662 | 3.4622
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.00475 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.6935 | 146 | 0.032662 | 4.7686
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.00475 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.361 | 76 | 0.032662 | 2.4823
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.004749 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.18996 | 40 | 0.032661 | 1.3064
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004745 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.032657 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004745 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.032657 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.00474 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.0948 | 20 | 0.032652 | 0.65304
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.00474 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.1185 | 25 | 0.032652 | 0.8163
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.00474 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.19434 | 41 | 0.032652 | 1.3387
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.00473 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.8352 | 388 | 0.032642 | 12.665
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.00473 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.436 | 515 | 0.032642 | 16.8106
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.72 | 114 | 0.010583 | 1.2065
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3495 | 222 | 0.010583 | 2.3495
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.7762 | 184 | 0.010583 | 1.9474
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3797 | 224 | 0.010583 | 2.3707
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7351 | 115 | 0.010583 | 1.2171
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.75332 | 161 | 0.032591 | 5.2471
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76736 | 164 | 0.032591 | 5.3449
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76736 | 164 | 0.032591 | 5.3449
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9371 | 414 | 0.032591 | 13.4926
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.758 | 162 | 0.032591 | 5.2797
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.75332 | 161 | 0.032591 | 5.2471
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76268 | 163 | 0.032591 | 5.3123
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9137 | 409 | 0.032591 | 13.3297
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.004668 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.0456 | 224 | 0.03258 | 7.2979
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.01491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3383 | 223.9 | 0.010405 | 2.3298
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.01491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3548 | 225 | 0.010405 | 2.3412
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.01491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3488 | 224.6 | 0.010405 | 2.3371
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.01491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3801 | 226.7 | 0.010405 | 2.3589
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.004449 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.4925 | 785 | 0.032361 | 25.4033
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.004449 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.537 | 795 | 0.032361 | 25.7269
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.004449 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.4702 | 780 | 0.032361 | 25.2415
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.004415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.65342 | 0 | 0.032327 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.004415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.57395 | 0 | 0.032327 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.004415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.64018 | 0 | 0.032327 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.004415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.7616 | 0 | 0.032327 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.004386 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.032298 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.004382 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.2191 | 50 | 0.032294 | 1.6147
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.004378 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.7968 | 182 | 0.03229 | 5.8768
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.004378 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.119 | 484 | 0.03229 | 15.6283
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.014518 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.087108 | 0 | 0.010013 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.014469 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.2651 | 433 | 0.0099644 | 4.3146
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.014454 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.4411 | 584 | 0.0099494 | 5.8105
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.014454 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.6001 | 595 | 0.0099494 | 5.9199
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.004039 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.61191 | 151.5 | 0.031951 | 4.8406
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.004039 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.61514 | 152.3 | 0.031951 | 4.8661
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.004039 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.71692 | 177.5 | 0.031951 | 5.6713
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.60642 | 150.7 | 0.031936 | 4.8127
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.60762 | 151 | 0.031936 | 4.8223
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.71386 | 177.4 | 0.031936 | 5.6654
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.003944 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4256 | 615 | 0.031856 | 19.5914
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.003944 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.3151 | 587 | 0.031856 | 18.6994
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.014324 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0098194 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.014116 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.084696 | 0 | 0.0096114 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.013908 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6954 | 50 | 0.0094034 | 0.47017
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.013908 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6954 | 50 | 0.0094034 | 0.47017
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.013908 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6954 | 50 | 0.0094034 | 0.47017
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.013908 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6954 | 50 | 0.0094034 | 0.47017
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.013597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1483 | 158 | 0.0090924 | 1.4366
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.013597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1755 | 160 | 0.0090924 | 1.4548
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.013597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3795 | 175 | 0.0090924 | 1.5912
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.013559 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.0677 | 152.5 | 0.0090544 | 1.3808
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.013559 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.0271 | 149.5 | 0.0090544 | 1.3536
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.013559 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1538 | 232.6 | 0.0090544 | 2.1061
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.003015 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4934 | 827 | 0.030927 | 25.5765
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.003015 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4693 | 819 | 0.030927 | 25.3291
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.013334 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7601 | 132 | 0.0088294 | 1.1655
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.013334 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7868 | 134 | 0.0088294 | 1.1831
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.013334 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.3069 | 323 | 0.0088294 | 2.8519
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.013223 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.43636 | 0 | 0.0087184 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.013223 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.33058 | 0 | 0.0087184 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.013223 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0087184 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.64469 | 49 | 0.0086524 | 0.42397
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.60522 | 46 | 0.0086524 | 0.39801
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.60522 | 46 | 0.0086524 | 0.39801
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.61838 | 47 | 0.0086524 | 0.40666
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.013157 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.0262 | 154 | 0.0086524 | 1.3325
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.013157 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.9472 | 148 | 0.0086524 | 1.2806
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.63154 | 48 | 0.0086524 | 0.41532
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.63154 | 48 | 0.0086524 | 0.41532
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.013027 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10422 | 0 | 0.0085224 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.013027 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10422 | 0 | 0.0085224 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.013024 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.0374 | 310 | 0.0085194 | 2.641
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.013024 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.3789 | 413 | 0.0085194 | 3.5185
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.012926 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.54289 | 42 | 0.0084214 | 0.3537
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.012926 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.56874 | 44 | 0.0084214 | 0.37054
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.012926 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.56874 | 44 | 0.0084214 | 0.37054
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.012926 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.60752 | 47 | 0.0084214 | 0.39581
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.012913 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.45195 | 0 | 0.0084084 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.012913 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.43904 | 0 | 0.0084084 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.012913 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.45195 | 0 | 0.0084084 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.002412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.0623 | 855 | 0.030324 | 25.9269
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.002412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.0623 | 855 | 0.030324 | 25.9269
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.002412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.36735 | 152.3 | 0.030324 | 4.6183
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.002412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.36904 | 153 | 0.030324 | 4.6396
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.012771 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22988 | 0 | 0.0082664 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.012771 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22988 | 0 | 0.0082664 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.012708 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.3628 | 422 | 0.0082034 | 3.4618
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.01268 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.35504 | 0 | 0.0081754 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.01268 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.36772 | 0 | 0.0081754 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.001972 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.094656 | 48 | 0.029884 | 1.4344
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.001972 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.090712 | 46 | 0.029884 | 1.3747
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.001972 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.20706 | 105 | 0.029884 | 3.1378
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.012257 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.16792 | 0 | 0.0077524 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.012155 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.21879 | 0 | 0.0076504 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.012155 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.21879 | 0 | 0.0076504 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.012155 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18232 | 0 | 0.0076504 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.001717 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.001717 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.001717 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.029189 | 17 | 0.029629 | 0.50369
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.001717 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.001717 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.001693 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.054176 | 0 | 0.029605 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.000872 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.40374 | 463 | 0.028784 | 13.3269
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.000505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.077871 | 0 | 0.028417 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.000505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.07878 | 0 | 0.028417 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.000505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.07878 | 0 | 0.028417 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.000505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.1919 | 0 | 0.028417 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.01085 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.1737 | 569 | 0.0063454 | 3.6105
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.01085 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.3038 | 581 | 0.0063454 | 3.6867
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.027912 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.027912 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045046 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045046 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045046 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045046 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045046 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045046 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0045046 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0045046 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.019743 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9802 | 0 | -0.024248 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.019743 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8341 | 0 | -0.024248 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.019743 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0276 | 0 | -0.024248 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.019743 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0138 | 0 | -0.024248 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.019746 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63187 | 0 | -0.024251 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.019746 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59238 | 0 | -0.024251 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.019842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4048 | 0 | -0.024347 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.019842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3235 | 0 | -0.024347 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.019842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0516 | 0 | -0.024347 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0398 | 0 | -0.024347 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0457 | 0 | -0.024347 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0219 | 0 | -0.024347 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9048 | 0 | -0.024347 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8414 | 0 | -0.024347 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.019842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.79368 | 0 | -0.024347 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3254 | 56 | -0.028172 | -1.5776
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3964 | 59 | -0.028172 | -1.6621
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3254 | 56 | -0.028172 | -1.5776
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3254 | 56 | -0.028172 | -1.5776
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3964 | 59 | -0.028172 | -1.6621
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3254 | 56 | -0.028172 | -1.5776
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.024802 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.029307 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8588 | 104 | -0.031993 | -3.3272
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8588 | 104 | -0.031993 | -3.3272
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4844 | 54 | -0.031993 | -1.7276
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4569 | 53 | -0.031993 | -1.6956
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4844 | 54 | -0.031993 | -1.7276
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5668 | 57 | -0.031993 | -1.8236
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4844 | 54 | -0.031993 | -1.7276
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4844 | 54 | -0.031993 | -1.7276
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5943 | 58 | -0.031993 | -1.8556
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5943 | 58 | -0.031993 | -1.8556
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7783 | 0 | -0.035036 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6745 | 0 | -0.035036 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6562 | 0 | -0.035036 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6639 | 0 | -0.035036 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37248 | 0 | -0.035036 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.8486 | 0 | -0.040342 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.63 | 0 | -0.040342 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.6443 | 0 | -0.040342 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.6264 | 0 | -0.040342 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.6402 | 0 | -0.040342 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.037351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4278 | 0 | -0.041856 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.037351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2411 | 0 | -0.041856 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.037351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4278 | 0 | -0.041856 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.037351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4278 | 0 | -0.041856 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.042233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.5068 | 12 | -0.046738 | -0.56085
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.045779 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.5708 | 0 | -0.050284 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.045779 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6623 | 0 | -0.050284 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.049928 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5876 | 172 | -0.054433 | -9.3624
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.049928 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5876 | 172 | -0.054433 | -9.3624
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.049928 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5876 | 172 | -0.054433 | -9.3624
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.050168 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -10.6858 | 213 | -0.054673 | -11.6453
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.050351 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.81569 | 0 | -0.054856 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.050486 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2311 | 0 | -0.054991 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.050486 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1907 | 0 | -0.054991 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.050486 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1701 | 0 | -0.054991 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.050486 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7158 | 0 | -0.054991 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.050747 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.5703 | 228 | -0.055252 | -12.5974
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.050825 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5729 | 0 | -0.05533 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.050825 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3087 | 0 | -0.05533 | 0
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.3028 | 0 | -0.055505 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2314 | 0 | -0.055505 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.1039 | 0 | -0.055505 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.7292 | 0 | -0.055505 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.051451 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.2612 | 0 | -0.055956 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.051451 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.1601 | 0 | -0.055956 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.051451 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.0778 | 0 | -0.055956 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.051877 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6833 | 0 | -0.056382 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.051877 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7351 | 0 | -0.056382 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.051877 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0232 | 0 | -0.056382 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.051877 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5563 | 0 | -0.056382 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.052246 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.6206 | 165 | -0.056751 | -9.3638
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.052712 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.9083 | 169 | -0.057217 | -9.6696
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.052727 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2145 | 42 | -0.057232 | -2.4037
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.052727 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2145 | 42 | -0.057232 | -2.4037
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.052727 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.0036 | 38 | -0.057232 | -2.1748
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.052727 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.0036 | 38 | -0.057232 | -2.1748
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.053124 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.63749 | 12 | -0.057629 | -0.69154
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.053124 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.057629 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.054679 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -40.1891 | 735 | -0.059184 | -43.4999
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.05657 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -42.0315 | 743 | -0.061075 | -45.3784
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1167 | 0 | -0.066762 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1603 | 0 | -0.066762 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0358 | 0 | -0.066762 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8576 | 0 | -0.066762 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1019 | 0 | -0.066762 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.27 | 0 | -0.066762 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2389 | 0 | -0.066762 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.179 | 0 | -0.066762 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1206 | 0 | -0.066762 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3167 | 0 | -0.066762 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.214 | 0 | -0.066762 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.062677 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.75212 | 12 | -0.067182 | -0.80618
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.067475 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.6732 | 0 | -0.07198 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.067475 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.5261 | 0 | -0.07198 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.067475 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.3911 | 0 | -0.07198 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.067475 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.3911 | 0 | -0.07198 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.067475 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.9309 | 0 | -0.07198 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.068263 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34131 | 0 | -0.072768 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.068263 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4335 | 0 | -0.072768 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.074068 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5924 | 0 | -0.078573 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8379 | 0 | -0.094319 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9277 | 0 | -0.094319 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.287 | 0 | -0.094319 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6583 | 0 | -0.094319 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5685 | 0 | -0.094319 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3407 | 0 | -0.094319 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.299 | 0 | -0.094319 | 0
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.092994 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.6001 | 0 | -0.097499 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.10788 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -42.937 | 398 | -0.11239 | -44.7299
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3177 | 46 | -0.18532 | -8.5249
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3177 | 46 | -0.18532 | -8.5249
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3177 | 46 | -0.18532 | -8.5249
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.945 | 55 | -0.18532 | -10.1928
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.945 | 55 | -0.18532 | -10.1928
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.7642 | 54 | -0.18532 | -10.0075
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.18407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -31.8443 | 0 | -0.18858 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.18407 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.8496 | 0 | -0.18858 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.19062 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.925 | 0 | -0.19513 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Midtown Reit - Polk 138kV [47707-47730] C:Singleton - Tomball 345kV [44645-46500] & Roans - King 345kV [40600-45972] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.19062 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.925 | 0 | -0.19513 | 0 | 0 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.18407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -31.8443 | 0 | -0.18858 | 0 | 0 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.18407 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.8496 | 0 | -0.18858 | 0 | 0 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3177 | 46 | -0.18532 | -8.5249 | 46 | 8.5249 | Weighted Shift Factors
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3177 | 46 | -0.18532 | -8.5249 | 92 | 17.0498 | North | 0.0045046
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3177 | 46 | -0.18532 | -8.5249 | 138 | 25.5747 | Houston | -0.027912
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.945 | 55 | -0.18532 | -10.1928 | 193 | 35.7674 |  | 0.032416
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.945 | 55 | -0.18532 | -10.1928 | 248 | 45.9602
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.18082 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.7642 | 54 | -0.18532 | -10.0075 | 302 | 55.9677 | Line Rating | 251
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.10788 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -42.937 | 398 | -0.11239 | -44.7299 |  |  | Conc Gen | 302
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.092994 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.6001 | 0 | -0.097499 | 0 |  |  | Weighted Imp. | 55.9677
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8379 | 0 | -0.094319 | 0 |  |  | PTDF | 0.18532
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9277 | 0 | -0.094319 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.287 | 0 | -0.094319 | 0 |  |  | Concentration | 5.717
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6583 | 0 | -0.094319 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5685 | 0 | -0.094319 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3407 | 0 | -0.094319 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.089814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.299 | 0 | -0.094319 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.074068 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5924 | 0 | -0.078573 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.068263 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34131 | 0 | -0.072768 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.068263 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4335 | 0 | -0.072768 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.067475 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.6732 | 0 | -0.07198 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.067475 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.5261 | 0 | -0.07198 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.067475 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.3911 | 0 | -0.07198 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.067475 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.3911 | 0 | -0.07198 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.067475 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.9309 | 0 | -0.07198 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.062677 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.75212 | 0 | -0.067182 | 0
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1167 | 0 | -0.066762 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1603 | 0 | -0.066762 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0358 | 0 | -0.066762 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8576 | 0 | -0.066762 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1019 | 0 | -0.066762 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.27 | 0 | -0.066762 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2389 | 0 | -0.066762 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.179 | 0 | -0.066762 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1206 | 0 | -0.066762 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3167 | 0 | -0.066762 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.062257 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.214 | 0 | -0.066762 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.05657 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -42.0315 | 743 | -0.061075 | -45.3784
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.054679 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -40.1891 | 735 | -0.059184 | -43.4999
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.053124 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.63749 | 12 | -0.057629 | -0.69154
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.053124 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.057629 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.052727 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2145 | 42 | -0.057232 | -2.4037
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.052727 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2145 | 42 | -0.057232 | -2.4037
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.052727 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.0036 | 38 | -0.057232 | -2.1748
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.052727 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.0036 | 38 | -0.057232 | -2.1748
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.052712 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.9083 | 169 | -0.057217 | -9.6696
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.052246 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.6206 | 165 | -0.056751 | -9.3638
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.051877 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6833 | 0 | -0.056382 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.051877 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7351 | 0 | -0.056382 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.051877 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0232 | 0 | -0.056382 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.051877 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5563 | 0 | -0.056382 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.051451 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.2612 | 0 | -0.055956 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.051451 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.1601 | 0 | -0.055956 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.051451 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.0778 | 0 | -0.055956 | 0
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.3028 | 0 | -0.055505 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.2314 | 0 | -0.055505 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.1039 | 0 | -0.055505 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.051 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.7292 | 0 | -0.055505 | 0
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.050825 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5729 | 0 | -0.05533 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.050825 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3087 | 0 | -0.05533 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.050747 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.5703 | 228 | -0.055252 | -12.5974
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.050486 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2311 | 0 | -0.054991 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.050486 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1907 | 0 | -0.054991 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.050486 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1701 | 0 | -0.054991 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.050486 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7158 | 0 | -0.054991 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.050351 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.81569 | 0 | -0.054856 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.050168 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -10.6858 | 213 | -0.054673 | -11.6453
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.049928 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5876 | 172 | -0.054433 | -9.3624
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.049928 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5876 | 172 | -0.054433 | -9.3624
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.049928 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5876 | 172 | -0.054433 | -9.3624
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.045779 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.5708 | 0 | -0.050284 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.045779 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6623 | 0 | -0.050284 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.042233 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.5068 | 12 | -0.046738 | -0.56085
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.037351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4278 | 0 | -0.041856 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.037351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2411 | 0 | -0.041856 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.037351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4278 | 0 | -0.041856 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.037351 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4278 | 0 | -0.041856 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.8486 | 0 | -0.040342 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.63 | 0 | -0.040342 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.6443 | 0 | -0.040342 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.6264 | 0 | -0.040342 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.035837 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.6402 | 0 | -0.040342 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7783 | 0 | -0.035036 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6745 | 0 | -0.035036 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6562 | 0 | -0.035036 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6639 | 0 | -0.035036 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.030531 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37248 | 0 | -0.035036 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8588 | 104 | -0.031993 | -3.3272
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8588 | 104 | -0.031993 | -3.3272
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4844 | 54 | -0.031993 | -1.7276
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4569 | 53 | -0.031993 | -1.6956
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4844 | 54 | -0.031993 | -1.7276
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5668 | 57 | -0.031993 | -1.8236
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4844 | 54 | -0.031993 | -1.7276
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4844 | 54 | -0.031993 | -1.7276
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5943 | 58 | -0.031993 | -1.8556
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.027488 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5943 | 58 | -0.031993 | -1.8556
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.024802 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.029307 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3254 | 56 | -0.028172 | -1.5776
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3964 | 59 | -0.028172 | -1.6621
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3254 | 56 | -0.028172 | -1.5776
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3254 | 56 | -0.028172 | -1.5776
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3964 | 59 | -0.028172 | -1.6621
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.023667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3254 | 56 | -0.028172 | -1.5776
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.019842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4048 | 0 | -0.024347 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.019842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3235 | 0 | -0.024347 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.019842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0516 | 0 | -0.024347 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0398 | 0 | -0.024347 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0457 | 0 | -0.024347 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0219 | 0 | -0.024347 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9048 | 0 | -0.024347 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.019842 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8414 | 0 | -0.024347 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.019842 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.79368 | 0 | -0.024347 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.019746 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63187 | 0 | -0.024251 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.019746 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59238 | 0 | -0.024251 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.019743 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9802 | 0 | -0.024248 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.019743 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8341 | 0 | -0.024248 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.019743 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0276 | 0 | -0.024248 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.019743 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0138 | 0 | -0.024248 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045046 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045046 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045046 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045046 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045046 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0045046 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0045046 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0045046 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.027912 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.027912 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.01085 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.1737 | 0 | 0.0063454 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.01085 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.3038 | 0 | 0.0063454 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.000505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.077871 | 0 | 0.028417 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.000505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.07878 | 0 | 0.028417 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.000505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.07878 | 0 | 0.028417 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.000505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.1919 | 0 | 0.028417 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.000872 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.40374 | 0 | 0.028784 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.001693 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.054176 | 0 | 0.029605 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.001717 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.001717 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.001717 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.029189 | 17 | 0.029629 | 0.50369
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.001717 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.001717 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.029629 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.012155 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.21879 | 0 | 0.0076504 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.012155 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.21879 | 0 | 0.0076504 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.012155 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18232 | 0 | 0.0076504 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.012257 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.16792 | 0 | 0.0077524 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.001972 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.094656 | 48 | 0.029884 | 1.4344
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.001972 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.090712 | 46 | 0.029884 | 1.3747
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.001972 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.20706 | 105 | 0.029884 | 3.1378
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.01268 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.35504 | 0 | 0.0081754 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.01268 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.36772 | 0 | 0.0081754 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.012708 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.3628 | 422 | 0.0082034 | 3.4618
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.012771 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22988 | 0 | 0.0082664 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.012771 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22988 | 0 | 0.0082664 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.002412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.0623 | 0 | 0.030324 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.002412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.0623 | 0 | 0.030324 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.002412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.36735 | 0 | 0.030324 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.002412 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.36904 | 0 | 0.030324 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.012913 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.45195 | 0 | 0.0084084 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.012913 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.43904 | 0 | 0.0084084 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.012913 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.45195 | 0 | 0.0084084 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.012926 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.54289 | 42 | 0.0084214 | 0.3537
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.012926 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.56874 | 44 | 0.0084214 | 0.37054
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.012926 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.56874 | 44 | 0.0084214 | 0.37054
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.012926 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.60752 | 47 | 0.0084214 | 0.39581
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.013024 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.0374 | 310 | 0.0085194 | 2.641
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.013024 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.3789 | 413 | 0.0085194 | 3.5185
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.013027 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10422 | 0 | 0.0085224 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.013027 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10422 | 0 | 0.0085224 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.64469 | 49 | 0.0086524 | 0.42397
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.60522 | 46 | 0.0086524 | 0.39801
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.60522 | 46 | 0.0086524 | 0.39801
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.61838 | 47 | 0.0086524 | 0.40666
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.013157 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.0262 | 154 | 0.0086524 | 1.3325
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.013157 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.9472 | 148 | 0.0086524 | 1.2806
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.63154 | 48 | 0.0086524 | 0.41532
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.013157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.63154 | 48 | 0.0086524 | 0.41532
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.013223 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.43636 | 0 | 0.0087184 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.013223 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.33058 | 0 | 0.0087184 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.013223 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0087184 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.013334 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7601 | 132 | 0.0088294 | 1.1655
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.013334 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7868 | 134 | 0.0088294 | 1.1831
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.013334 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.3069 | 323 | 0.0088294 | 2.8519
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.003015 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4934 | 0 | 0.030927 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.003015 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4693 | 0 | 0.030927 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.013559 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.0677 | 152.5 | 0.0090544 | 1.3808
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.013559 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.0271 | 149.5 | 0.0090544 | 1.3536
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.013559 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1538 | 232.6 | 0.0090544 | 2.1061
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.013597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1483 | 158 | 0.0090924 | 1.4366
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.013597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1755 | 160 | 0.0090924 | 1.4548
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.013597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3795 | 175 | 0.0090924 | 1.5912
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.013908 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6954 | 50 | 0.0094034 | 0.47017
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.013908 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6954 | 50 | 0.0094034 | 0.47017
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.013908 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6954 | 50 | 0.0094034 | 0.47017
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.013908 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.6954 | 50 | 0.0094034 | 0.47017
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.014116 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.084696 | 0 | 0.0096114 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.014324 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0098194 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.003944 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4256 | 0 | 0.031856 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.003944 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.3151 | 0 | 0.031856 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.60642 | 150.7 | 0.031936 | 4.8127
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.60762 | 151 | 0.031936 | 4.8223
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.004024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.71386 | 177.4 | 0.031936 | 5.6654
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.004039 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.61191 | 151.5 | 0.031951 | 4.8406
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.004039 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.61514 | 152.3 | 0.031951 | 4.8661
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.004039 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.71692 | 177.5 | 0.031951 | 5.6713
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.014454 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.4411 | 0 | 0.0099494 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.014454 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.6001 | 0 | 0.0099494 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.014469 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.2651 | 0 | 0.0099644 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.014518 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.087108 | 0 | 0.010013 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.004378 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.7968 | 182 | 0.03229 | 5.8768
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.004378 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.119 | 484 | 0.03229 | 15.6283
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.004382 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.2191 | 0 | 0.032294 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.004386 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.032298 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.004415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.65342 | 0 | 0.032327 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.004415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.57395 | 0 | 0.032327 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.004415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.64018 | 0 | 0.032327 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.004415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.7616 | 0 | 0.032327 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.004449 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.4925 | 0 | 0.032361 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.004449 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.537 | 0 | 0.032361 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.004449 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.4702 | 0 | 0.032361 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.01491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3383 | 223.9 | 0.010405 | 2.3298
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.01491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3548 | 225 | 0.010405 | 2.3412
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.01491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3488 | 224.6 | 0.010405 | 2.3371
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.01491 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3801 | 226.7 | 0.010405 | 2.3589
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.004668 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.0456 | 224 | 0.03258 | 7.2979
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.75332 | 161 | 0.032591 | 5.2471
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76736 | 164 | 0.032591 | 5.3449
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76736 | 164 | 0.032591 | 5.3449
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9371 | 414 | 0.032591 | 13.4926
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.758 | 162 | 0.032591 | 5.2797
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.75332 | 161 | 0.032591 | 5.2471
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.76268 | 163 | 0.032591 | 5.3123
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.004679 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9137 | 409 | 0.032591 | 13.3297
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.72 | 0 | 0.010583 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3495 | 0 | 0.010583 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.7762 | 0 | 0.010583 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3797 | 0 | 0.010583 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7351 | 0 | 0.010583 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.00473 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.8352 | 388 | 0.032642 | 12.665
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.00473 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.436 | 515 | 0.032642 | 16.8106
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.00474 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.0948 | 20 | 0.032652 | 0.65304
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.00474 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.1185 | 25 | 0.032652 | 0.8163
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.00474 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.19434 | 41 | 0.032652 | 1.3387
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004745 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.032657 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.004745 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.032657 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.004749 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.18996 | 40 | 0.032661 | 1.3064
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.00475 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.37525 | 79 | 0.032662 | 2.5803
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.00475 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.5035 | 106 | 0.032662 | 3.4622
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.00475 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.6935 | 146 | 0.032662 | 4.7686
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.00475 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.361 | 76 | 0.032662 | 2.4823
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.004758 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.655 | 0 | 0.03267 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.004758 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.7549 | 0 | 0.03267 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.004758 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 3.8445 | 0 | 0.03267 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.004765 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.35737 | 0 | 0.032677 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.004765 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.37929 | 0 | 0.032677 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.004765 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.42123 | 0 | 0.032677 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7632 | 160 | 0.032682 | 5.2291
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74412 | 156 | 0.032682 | 5.0984
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.93492 | 196 | 0.032682 | 6.4056
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74412 | 156 | 0.032682 | 5.0984
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.74889 | 157 | 0.032682 | 5.1311
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.00477 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.94446 | 198 | 0.032682 | 6.471
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.004776 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.7671 | 370 | 0.032688 | 12.0945
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.66864 | 0 | 0.032688 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.67342 | 0 | 0.032688 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4758 | 0 | 0.032688 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.68297 | 0 | 0.032688 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.68774 | 0 | 0.032688 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.004776 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4806 | 0 | 0.032688 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.004791 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.81447 | 170 | 0.032703 | 5.5595
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.004791 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.4913 | 520 | 0.032703 | 17.0055
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.004803 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.19212 | 0 | 0.032715 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.004803 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.19212 | 0 | 0.032715 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.004819 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.56864 | 118 | 0.032731 | 3.8622
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.004819 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.55419 | 115 | 0.032731 | 3.7641
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.004819 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.6794 | 556 | 0.032731 | 18.1984
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.004821 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.032733 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.015218 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.036523 | 0 | 0.010713 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.015218 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.036523 | 0 | 0.010713 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.015218 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.04261 | 0 | 0.010713 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.004839 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032751 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.015259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1668 | 142 | 0.010754 | 1.5271
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.015259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2126 | 145 | 0.010754 | 1.5594
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.015259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.3041 | 151 | 0.010754 | 1.6239
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.015259 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.4251 | 290 | 0.010754 | 3.1188
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.004883 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.95707 | 196 | 0.032795 | 6.4278
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.004883 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.54201 | 111 | 0.032795 | 3.6402
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.015319 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.061276 | 0 | 0.010814 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.004961 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.29766 | 60 | 0.032873 | 1.9724
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.004961 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.31254 | 63 | 0.032873 | 2.071
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.005035 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.1902 | 435 | 0.032947 | 14.3319
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.01543 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037032 | 0 | 0.010925 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.01543 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.037032 | 0 | 0.010925 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.005042 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.56722 | 0 | 0.032954 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.005051 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.9951 | 395 | 0.032963 | 13.0203
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.005051 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.1972 | 435 | 0.032963 | 14.3389
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.005063 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0956 | 216.4 | 0.032975 | 7.1358
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.005063 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0941 | 216.1 | 0.032975 | 7.1259
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.005069 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032981 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.005069 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032981 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.005069 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.032981 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.005141 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1516 | 224 | 0.033053 | 7.4038
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.005141 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1619 | 226 | 0.033053 | 7.47
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.005141 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0899 | 212 | 0.033053 | 7.0072
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.005141 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0848 | 211 | 0.033053 | 6.9742
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.005148 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.4826 | 288 | 0.03306 | 9.5212
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.005148 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.75676 | 147 | 0.03306 | 4.8598
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.005148 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.75676 | 147 | 0.03306 | 4.8598
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.005179 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033091 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.005193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0594 | 204 | 0.033105 | 6.7534
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.005193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0438 | 201 | 0.033105 | 6.6541
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.005193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.2567 | 242 | 0.033105 | 8.0114
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.005196 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1291 | 217.3 | 0.033108 | 7.1943
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.005196 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0652 | 205 | 0.033108 | 6.7871
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.005196 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.4154 | 272.4 | 0.033108 | 9.0186
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2914 | 147 | 0.011083 | 1.6293
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1511 | 138 | 0.011083 | 1.5295
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1823 | 140 | 0.011083 | 1.5517
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2914 | 147 | 0.011083 | 1.6293
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.837 | 182 | 0.011083 | 2.0172
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.015588 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0864 | 198 | 0.011083 | 2.1945
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.005215 | north | 3 | N | N | Nnorth | Nnorth | 1 | 6.0338 | 0 | 0.033127 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.005215 | north | 3 | N | N | Nnorth | Nnorth | 1 | 6.039 | 0 | 0.033127 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.005237 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.094266 | 18 | 0.033149 | 0.59668
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.005237 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.094266 | 18 | 0.033149 | 0.59668
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.005237 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.19901 | 38 | 0.033149 | 1.2597
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.005281 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.36967 | 70 | 0.033193 | 2.3235
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.005281 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.36439 | 69 | 0.033193 | 2.2903
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.005281 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.36439 | 69 | 0.033193 | 2.2903
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.005281 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.35911 | 68 | 0.033193 | 2.2571
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.005302 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.10604 | 20 | 0.033214 | 0.66428
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.005302 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.10604 | 20 | 0.033214 | 0.66428
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.005302 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.10604 | 20 | 0.033214 | 0.66428
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.005302 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.090134 | 17 | 0.033214 | 0.56464
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.005305 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.06366 | 0 | 0.033217 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.005305 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.06366 | 0 | 0.033217 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.00531 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.9435 | 366 | 0.033222 | 12.1592
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.005315 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.6378 | 0 | 0.033227 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.015708 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.3932 | 407 | 0.011203 | 4.5598
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.015708 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.6602 | 0 | 0.011203 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.015708 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.6759 | 0 | 0.011203 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.015715 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.01121 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.015715 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.01121 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.015715 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.01121 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.015716 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.475 | 412 | 0.011211 | 4.6191
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.015716 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.2864 | 400 | 0.011211 | 4.4846
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.005329 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.89527 | 168 | 0.033241 | 5.5845
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.005329 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.47961 | 90 | 0.033241 | 2.9917
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.015724 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.91199 | 58 | 0.011219 | 0.65073
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.015724 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3994 | 89 | 0.011219 | 0.99853
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.015724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.69186 | 44 | 0.011219 | 0.49365
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.015724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.69186 | 44 | 0.011219 | 0.49365
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.015724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.67613 | 43 | 0.011219 | 0.48244
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.015724 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.70758 | 45 | 0.011219 | 0.50487
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.015733 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.2882 | 209 | 0.011228 | 2.3467
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.015733 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.3983 | 216 | 0.011228 | 2.4253
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.015733 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72372 | 46 | 0.011228 | 0.51651
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.015733 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.73945 | 47 | 0.011228 | 0.52774
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.015733 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72372 | 46 | 0.011228 | 0.51651
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.015733 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72372 | 46 | 0.011228 | 0.51651
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.005354 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.2957 | 242 | 0.033266 | 8.0503
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.005381 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.39281 | 73 | 0.033293 | 2.4304
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.005381 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.64034 | 119 | 0.033293 | 3.9619
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.005381 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.1031 | 205 | 0.033293 | 6.825
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.005381 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.54886 | 102 | 0.033293 | 3.3959
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.005381 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.51658 | 96 | 0.033293 | 3.1961
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.015802 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4493 | 155 | 0.011297 | 1.7511
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.015802 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.6863 | 170 | 0.011297 | 1.9206
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.015802 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.4493 | 155 | 0.011297 | 1.7511
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.005415 | west | 4 | Y | N | Ywest | Nwest | 1 | 3.5181 | 0 | 0.033327 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.015841 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.13306 | 8.4 | 0.011336 | 0.095226
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.005454 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.89991 | 0 | 0.033366 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.015876 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 8.6683 | 0 | 0.011371 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.015876 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.907 | 0 | 0.011371 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.0055 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.298 | 0 | 0.033412 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.0055 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2 | 0 | 0.033412 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.015955 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.38292 | 24 | 0.01145 | 0.27481
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.015955 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.38292 | 24 | 0.01145 | 0.27481
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.015955 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.36696 | 23 | 0.01145 | 0.26336
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.005578 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.33468 | 0 | 0.03349 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.00562 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.3372 | 0 | 0.033532 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.005632 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.8448 | 0 | 0.033544 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1775 | 0 | 0.033546 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.7127 | 0 | 0.033546 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.4029 | 0 | 0.033546 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.005634 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1099 | 0 | 0.033546 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.2115 | 0 | 0.033552 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6063 | 0 | 0.033552 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.7614 | 0 | 0.033552 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.67116 | 0 | 0.033552 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.5922 | 0 | 0.033552 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.00564 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.45402 | 0 | 0.033552 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.005661 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.70762 | 0 | 0.033573 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.005661 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.70762 | 0 | 0.033573 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.005669 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.85035 | 0 | 0.033581 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.005669 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.57257 | 0 | 0.033581 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.005674 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.47662 | 0 | 0.033586 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.005684 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.56272 | 0 | 0.033596 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.005684 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.34672 | 0 | 0.033596 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.005684 | west | 7 | N | N | Nwest | Nwest | 1 | 0.1421 | 0 | 0.033596 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.005684 | west | 7 | N | N | Nwest | Nwest | 1 | 0.25976 | 0 | 0.033596 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.005684 | west | 7 | N | N | Nwest | Nwest | 1 | 0.25976 | 0 | 0.033596 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.005685 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.80158 | 0 | 0.033597 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.005685 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6822 | 0 | 0.033597 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.005688 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.35834 | 0 | 0.0336 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.37561 | 66 | 0.033603 | 2.2178
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39268 | 69 | 0.033603 | 2.3186
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39268 | 69 | 0.033603 | 2.3186
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.3813 | 67 | 0.033603 | 2.2514
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.3813 | 67 | 0.033603 | 2.2514
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.005691 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.36991 | 65 | 0.033603 | 2.1842
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.855 | 0 | 0.033612 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.254 | 0 | 0.033612 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.14 | 0 | 0.033612 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.0057 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.69483 | 0 | 0.033612 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.005712 | west | 8 | N | N | Nwest | Nwest | 1 | 0.39984 | 0 | 0.033624 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.005712 | west | 8 | N | N | Nwest | Nwest | 1 | 0.41926 | 0 | 0.033624 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.005712 | west | 8 | N | N | Nwest | Nwest | 1 | 0.40212 | 0 | 0.033624 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.005712 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0282 | 0 | 0.033624 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.005712 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0282 | 0 | 0.033624 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.005716 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2861 | 0 | 0.033628 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.005716 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68592 | 0 | 0.033628 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.005716 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3318 | 0 | 0.033628 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.005716 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.97286 | 0 | 0.033628 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.005723 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68676 | 0 | 0.033635 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.005724 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68688 | 0 | 0.033636 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.005747 | west | 8 | N | N | Nwest | Nwest | 1 | 0.14827 | 0 | 0.033659 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.005752 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2321 | 0 | 0.033664 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.00576 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.57888 | 0 | 0.033672 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.005761 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.86415 | 0 | 0.033673 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.005762 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.3342 | 0 | 0.033674 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.40348 | 70 | 0.033676 | 2.3573
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.40348 | 70 | 0.033676 | 2.3573
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.5349 | 92.8 | 0.033676 | 3.1251
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.46112 | 80 | 0.033676 | 2.6941
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.46112 | 80 | 0.033676 | 2.6941
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.66286 | 115 | 0.033676 | 3.8727
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2001 | 208.2 | 0.033676 | 7.0113
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.81906 | 142.1 | 0.033676 | 4.7853
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.76315 | 132.4 | 0.033676 | 4.4587
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.7839 | 136 | 0.033676 | 4.5799
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.84731 | 147 | 0.033676 | 4.9504
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.005764 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2104 | 210 | 0.033676 | 7.0719
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.005776 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6498 | 0 | 0.033688 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.005776 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.86351 | 0 | 0.033688 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.005776 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0743 | 0 | 0.033688 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.005776 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.239 | 0 | 0.033688 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.005798 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.038267 | 0 | 0.03371 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.005798 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.19887 | 0 | 0.03371 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.005821 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.86733 | 0 | 0.033733 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.005823 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.987 | 0 | 0.033735 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.005834 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.20419 | 0 | 0.033746 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.005834 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.17502 | 0 | 0.033746 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.016227 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19472 | 0 | 0.011722 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38524 | 66 | 0.033749 | 2.2274
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.3794 | 65 | 0.033749 | 2.1937
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39108 | 67 | 0.033749 | 2.2612
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39108 | 67 | 0.033749 | 2.2612
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.005837 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39108 | 67 | 0.033749 | 2.2612
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.005837 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033749 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.005837 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.033749 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.016379 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 6.4861 | 0 | 0.011874 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.016419 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6419 | 100 | 0.011914 | 1.1914
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.016419 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6419 | 100 | 0.011914 | 1.1914
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.016419 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011914 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.016419 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011914 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.016419 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011914 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.016419 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011914 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.01642 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011915 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.006105 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.029304 | 0 | 0.034017 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006216 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49728 | 0 | 0.034128 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006216 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49728 | 0 | 0.034128 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.006246 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.46845 | 0 | 0.034158 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006246 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49968 | 0 | 0.034158 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.006246 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.24984 | 0 | 0.034158 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006253 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.50024 | 0 | 0.034165 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.006254 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.50032 | 0 | 0.034166 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.006257 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.93855 | 0 | 0.034169 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.006257 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.93855 | 0 | 0.034169 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.006356 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.09534 | 0 | 0.034268 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.006356 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.09534 | 0 | 0.034268 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.006407 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.51256 | 0 | 0.034319 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.006432 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.49205 | 0 | 0.034344 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.006458 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.54247 | 0 | 0.03437 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.016895 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.01239 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.016897 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5576 | 0 | 0.012392 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.006615 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.99225 | 150 | 0.034527 | 5.179
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.006615 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.5292 | 80 | 0.034527 | 2.7622
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.006728 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7156 | 255 | 0.03464 | 8.8332
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.006728 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0025 | 149 | 0.03464 | 5.1613
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.006728 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0294 | 153 | 0.03464 | 5.2999
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.017207 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20648 | 0 | 0.012702 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.017207 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18928 | 0 | 0.012702 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.017207 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.20648 | 0 | 0.012702 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.006858 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.03477 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.006858 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.3972 | 787 | 0.03477 | 27.3639
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.017305 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0128 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.006945 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034857 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.006945 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.034857 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.017392 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012887 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.017533 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5686 | 146.5 | 0.013028 | 1.9087
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.017533 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5931 | 147.9 | 0.013028 | 1.9269
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.017533 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0332 | 173 | 0.013028 | 2.2539
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.017586 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.6403 | 207 | 0.013081 | 2.7079
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.017586 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8109 | 216.7 | 0.013081 | 2.8347
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.017586 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.2558 | 242 | 0.013081 | 3.1657
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.017587 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5325 | 144 | 0.013082 | 1.8839
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.017587 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.5325 | 144 | 0.013082 | 1.8839
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.017587 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0074 | 171 | 0.013082 | 2.2371
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.017626 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.66979 | 38 | 0.013121 | 0.49861
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.017626 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34018 | 19.3 | 0.013121 | 0.25324
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.017626 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.26439 | 15 | 0.013121 | 0.19682
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.017626 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.82842 | 47 | 0.013121 | 0.61671
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.017626 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.013121 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.6582 | 0 | 0.013135 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.72324 | 0 | 0.013135 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.67032 | 0 | 0.013135 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.33516 | 0 | 0.013135 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.6582 | 0 | 0.013135 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.63504 | 0 | 0.013135 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.75852 | 0 | 0.013135 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.38808 | 0 | 0.013135 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.6107 | 0 | 0.013135 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.882 | 0 | 0.013135 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.9702 | 0 | 0.013135 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.01764 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.882 | 0 | 0.013135 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.007263 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.035175 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.017677 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.51263 | 0 | 0.013172 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.017727 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.1503 | 0 | 0.013222 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.017755 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.67469 | 0 | 0.01325 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.017761 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.67492 | 0 | 0.013256 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.017764 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.9332 | 334 | 0.013259 | 4.4286
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.017764 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.0398 | 340 | 0.013259 | 4.5082
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.017764 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1975 | 180 | 0.013259 | 2.3867
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.017764 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.1975 | 180 | 0.013259 | 2.3867
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.01777 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.44425 | 0 | 0.013265 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.01777 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.44425 | 0 | 0.013265 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.01779 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2022 | 180 | 0.013285 | 2.3914
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.017792 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6386 | 0 | 0.013287 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.017792 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6439 | 0 | 0.013287 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.017792 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.7222 | 0 | 0.013287 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.017793 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.9784 | 336 | 0.013288 | 4.4649
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.017793 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2027 | 180 | 0.013288 | 2.3919
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4465 | 0 | 0.013355 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4465 | 0 | 0.013355 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4465 | 0 | 0.013355 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.28576 | 0 | 0.013355 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4465 | 0 | 0.013355 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4465 | 0 | 0.013355 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4465 | 0 | 0.013355 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.01786 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.2679 | 0 | 0.013355 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.8318 | 0 | 0.013418 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.7422 | 0 | 0.013418 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -1 | 1.7923 | 0 | 0.013418 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.5988 | 0 | 0.013418 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6347 | 0 | 0.013418 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.017923 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.2762 | 0 | 0.013418 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.017923 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.21508 | 0 | 0.013418 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.007817 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1725 | 0 | 0.035729 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1521 | 0 | 0.014078 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3268 | 0 | 0.014078 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.83623 | 0 | 0.014078 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8769 | 0 | 0.014078 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5981 | 0 | 0.014078 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6353 | 0 | 0.014078 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.92915 | 0 | 0.014078 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33449 | 0 | 0.014078 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.7468 | 0 | 0.014078 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3008 | 0 | 0.014078 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1707 | 0 | 0.014078 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.338 | 0 | 0.014078 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2042 | 0 | 0.014078 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8769 | 0 | 0.014078 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8026 | 0 | 0.014078 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.914 | 0 | 0.014078 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4123 | 0 | 0.014078 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4866 | 0 | 0.014078 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4866 | 0 | 0.014078 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.018583 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1777 | 0 | 0.014078 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.018624 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.6819 | 144 | 0.014119 | 2.0332
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.018624 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.5013 | 188 | 0.014119 | 2.6545
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.018703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.89213 | 47.7 | 0.014198 | 0.67727
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.018703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.69762 | 37.3 | 0.014198 | 0.5296
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.018703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.86034 | 46 | 0.014198 | 0.65313
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.018703 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.89774 | 48 | 0.014198 | 0.68152
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.01873 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.41206 | 22 | 0.014225 | 0.31296
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.01873 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20603 | 11 | 0.014225 | 0.15648
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.01873 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20603 | 11 | 0.014225 | 0.15648
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.018744 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.3683 | 0 | 0.014239 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.018917 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.28375 | 0 | 0.014412 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.018917 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.43509 | 0 | 0.014412 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.01896 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15168 | 0 | 0.014455 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.53348 | 0 | 0.014548 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13337 | 0 | 0.014548 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.74307 | 0 | 0.014548 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.2858 | 0 | 0.014548 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13337 | 0 | 0.014548 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.2858 | 0 | 0.014548 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.74307 | 0 | 0.014548 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.019053 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.74307 | 0 | 0.014548 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.019439 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.93307 | 0 | 0.014934 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5445 | 0 | 0.015045 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5836 | 0 | 0.015045 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5445 | 0 | 0.015045 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.564 | 0 | 0.015045 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5327 | 0 | 0.015045 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.48875 | 0 | 0.015045 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.8993 | 0 | 0.015045 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.5474 | 0 | 0.015045 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.85238 | 0 | 0.015045 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.01955 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.4467 | 0 | 0.015045 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.02051 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 27.3398 | 0 | 0.016005 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.02051 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 27.2373 | 0 | 0.016005 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.020787 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95828 | 0 | 0.016282 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.011262 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.039174 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.025358 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 16.5081 | 0 | 0.020853 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.025358 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 14.3019 | 0 | 0.020853 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.025358 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 15.2148 | 0 | 0.020853 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.015088 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 1.5088 | 0 | 0.043 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.025815 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.2078 | 0 | 0.02131 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.025815 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.2078 | 0 | 0.02131 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.025815 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 6.3247 | 0 | 0.02131 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.1849 | 76 | 0.024244 | 1.8426
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.1849 | 76 | 0.024244 | 1.8426
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.0186 | 105 | 0.024244 | 2.5457
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.1274 | 74 | 0.024244 | 1.7941
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.1274 | 74 | 0.024244 | 1.7941
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.028749 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.9324 | 102 | 0.024244 | 2.4729
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.029878 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.1213 | 0 | 0.025373 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.029878 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29878 | 0 | 0.025373 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.031697 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 2.092 | 66 | 0.027192 | 1.7947
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.04153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.6098 | 0 | 0.037025 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.04153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.6098 | 0 | 0.037025 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.04153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.9421 | 0 | 0.037025 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.04153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.5475 | 0 | 0.037025 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.067054 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 10.7957 | 161 | 0.062549 | 10.0705
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.067054 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 11.131 | 166 | 0.062549 | 10.3832
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.067054 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 16.6294 | 248 | 0.062549 | 15.5123
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.067054 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 36.6115 | 546 | 0.062549 | 34.152
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.067054 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 43.1157 | 0 | 0.062549 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.067054 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.8717 | 13 | 0.062549 | 0.81314
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.18912 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 9.4559 | 50 | 0.18461 | 9.2307

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
Average line rating
| 20 | 251
| 25 | 251
| 30 | 251
| 35 | 251
| 40 | 251
| 45 | 251
| 50 | 251
| 55 | 251
| 60 | 251
| 65 | 251
| 70 | 251
| 75 | 251
| 80 | 251
| 85 | 251
| 90 | 251
| 95 | 251
| 100 | 251
| 105 | 251
| 110 | 251
| 115 | 251
| avg | 251