## test results
CRE test for: |  | 967 GIBN_CRE 345 44645 SNGLTN_3 345 99 | [5 empty] | FAIL
Line Rating: |  | 2080
Direcction |  | North | → | Houston |  | N-H
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 967 GIBN_CRE 345 44645 SNGLTN_3 345 99
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.14606
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.035657
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.10469
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.15104
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 967 GIBN_CRE 345 44645 SNGLTN_3 345 99
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.11982
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.038243
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.10495
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.15319
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 967 GIBN_CRE 345 44645 SNGLTN_3 345 99
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.1843
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.041116
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.29925 | FAIL
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.1406
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.11538
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.25788
PTDF tests
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.29925 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.29925 | 0.1843
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.47868
[6 empty] | Concentration |  | 1.5996 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.30691
[6 empty] | Concentration |  | 1.0256 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 826.4486
| Percent of line rating => | [6 empty] | 39.73% | FAIL
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 1.1494
[7 empty] | B1(N-S) | 0.016514 | 0.22835 | 0.21184 | 0.016514
[7 empty] | B2 (N-W) | -0.021126 | 0.026133 | 0.047259 | -0.021126
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B4 (S-W) | -0.037681 | -0.19929 | -0.16161 | -0.037681
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.014085 | 0.11854 | 0.13262 | -0.014085
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.021059 | 0.31747 | 0.29641 | 0.021059
[7 empty] | test | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B1 | 4.801%
Deployment Error Percent | [6 empty] | B2 | -6.142%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0%
[7 empty] | B4 | -10.96%
[7 empty] | B5 | -4.095%
[7 empty] | B6 | 6.123%
[7 empty] | Max Abs Error | 10.96% | PASS

## Generation_sensitivity
Generator Sensitivities
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 99 C: 967 GIBN_CRE 345 44645 SNGLTN_3 345 75 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 99 C: 967 GIBN_CRE 345 44645 SNGLTN_3 345 75
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.087047 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 22.197
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.087047 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 12.97
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.09441 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.4162
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.09441 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.4162
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.087047 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 13.3182
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.089545 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 13.4317
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.089545 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 7.1636
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11005 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 8.0336
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11005 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 13.096
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11005 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 22.5602
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11005 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 11.2251
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11005 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 10.5648
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.11139 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.3367
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.11139 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.3367
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.11045 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 18.5563
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.11045 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 9.9409
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.11237 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.0227
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.11237 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.0227
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.11237 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 4.2701
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.11386 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 32.7928
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.11386 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 16.738
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.11386 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 16.738
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.11567 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 13.0128
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.12061 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 4.8242
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.12055 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 9.5238
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.12055 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 12.7787
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.12055 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 17.6009
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.12055 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 9.1621
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.11701 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 7.0209
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.11701 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 7.3719
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.12069 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 2.4139
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.12069 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 3.0173
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.12069 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 4.9484
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.63771 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 295.2616
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 6.8389
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 6.7352
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 6.9425
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 6.9425
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 6.9425
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10362 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 11.8126
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10362 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 53.3638
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 6.9792
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 7.2964
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 7.2964
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 7.0849
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 7.0849
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 6.8734
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.10545 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 7.3813
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.10545 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 7.7398
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.10545 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 7.4235
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.10562 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 15.8429
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.10562 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 23.2362
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.10585 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 10.4788
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.10585 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 6.4566
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.10583 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 14.9219
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.10585 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 2.6462
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.10585 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 4.8372
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.10585 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 4.8372
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.10583 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 12.6995
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.10493 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 2.7071
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.10474 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 10.5261
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.10526 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 12.6308
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.10472 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 6.0737
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.10486 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 22.4617
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.10605 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 15.9072
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.10417 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.68754
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.10417 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 3.5731
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.10605 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 10.7108
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.10528 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 12.6336
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.11138 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 40.7647
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.1107 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 26.7889
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.10857 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 43.4272
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.10857 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 25.6228
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.10924 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 18.0254
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.11313 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 23.0795
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.11313 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 22.7401
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.11313 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 27.3787
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.11152 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.2305
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.11152 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.2305
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.11152 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.2305
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.11152 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 1.8959
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.11123 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 13.3475
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.10636 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 6.3818
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.12018 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 9.0131
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.12018 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 9.5659
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.12018 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 10.6235
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 19.2195
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 18.739
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 23.5439
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 18.739
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 18.8592
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 23.7842
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.11979 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 20.3635
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.11979 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 62.2882
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12003 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 44.4115
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.12029 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 67.1241
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.12029 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 69.6502
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.12029 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 97.1976
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.11504 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 12.8845
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.11504 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 11.504
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.11504 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 43.4851
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.11272 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 24.4938
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.11272 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 23.1074
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.11272 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 30.7047
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.11302 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 87.0254
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11142 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 7.7997
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11142 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 7.6883
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11142 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 7.6883
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11142 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 7.5768
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.11242 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 130.0734
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.11242 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 130.1858
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11281 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 25.2694
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11281 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 25.4951
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.1142 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 24.7131
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.1142 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 24.6788
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11281 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 23.9157
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11281 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 23.8029
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.11514 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 45.4795
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.11546 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 50.2268
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.11514 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 50.085
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.11907 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 16.4312
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.11973 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 14.1287
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.11973 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 13.7695
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.11973 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 66.5727
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.121 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 46.948
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.121 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 62.315
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.12344 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 96.9035
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.12344 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 98.138
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.12344 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 96.2863
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.12512 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 22.7717
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.12512 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 60.5576
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.12183 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 27.2906
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.12405 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 6.2024
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.12406 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 5.2104
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.12281 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 75.5294
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.12281 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 72.0906
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.083869 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 45.0377
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.083869 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 66.0049
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.08516 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 6.387
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.08516 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 18.9055
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.038449 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 21.8775
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.040822 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -8.5318
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.040822 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -8.8176
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.040631 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -16.5368
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.040822 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.8778
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.040822 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -1.9186
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.040822 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.8778
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.040822 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.8778
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.040695 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -17.2547
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.040695 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -17.2954
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.040675 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -2.3592
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.040675 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -3.6201
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.040675 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.7897
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.040675 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.7897
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.040675 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -1.749
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.040675 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -1.8304
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.040677 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -16.7589
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.040677 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -16.2708
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.042766 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -23.3502
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.042766 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -32.0745
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.040851 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -2.4919
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.040851 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -3.8808
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.040851 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -6.1685
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.041854 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -6.4874
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.041854 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -7.1152
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.041854 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -6.4874
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.068759 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -1.5127
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.068759 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.75635
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.068759 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.75635
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.068081 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -3.2475
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.068081 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -2.5394
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.068081 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -3.1317
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.068081 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -3.2679
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.058225 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.6987
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.058225 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.64048
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.042087 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.0101
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.042087 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.0101
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.042087 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.968
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.048656 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -19.2678
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.1113 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -148.3562
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.1113 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -147.7998
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.063504 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -2.4132
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.063504 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -1.2256
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.063504 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.95256
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.063504 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -2.9847
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.097677 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 7.3258
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.10661 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 15.991
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.10377 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 17.5883
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.074678 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 11.2017
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.10579 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 6.6645
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.10983 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 71.3579
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.1196 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 4.7839
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.1196 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 4.7839
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.001077 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 0.45449
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.013228 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -1.7461
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.013228 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -1.7726
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.013228 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -4.2726
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.015275 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -2.4135
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.015275 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -2.444
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.015275 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -2.6731
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.032131 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -18.7645
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.032131 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -19.1179
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.032264 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -13.9703
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.030817 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -6.8999
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.030817 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -6.9338
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.030817 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -6.9215
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.030817 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -6.9862
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.004604 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.036832
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.004604 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.036832
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.009162 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.16492
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.009162 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.16492
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.009162 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.13743
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.007727 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.10586
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -2.9e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.000522
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -2.9e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.000522
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.002538 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.08883
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.002538 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -0.086292
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.002538 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.08883
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.001444 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.040432
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.001444 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.041876
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.10367 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 3.6285
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.10367 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 3.1102
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.02899 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.4495
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.02899 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.4495
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.02899 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.4495
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.02899 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.4495
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.025314 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.15188
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.034492 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.082781
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.034492 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.082781
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.034492 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.096578
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.035876 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.1435
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.036933 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.088639
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.036933 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.088639
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -5.8263
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -5.4696
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -5.5489
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -5.8263
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -7.2136
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -7.8477
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.012948 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -1.9746
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.012948 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -1.9357
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.012948 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -3.0117
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.03535 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -5.0197
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.03535 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -5.1258
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.03535 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -5.3379
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.03535 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -10.2515
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.002962 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -0.097746
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.002962 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -0.07405
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.058225 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.6987
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.068116 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -4.9725
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -5.9959
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -6.1477
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -2.006
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.5015
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -5.9959
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -6.0718
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -5.9504
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -1.8975
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -3.4913
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.060621 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -38.1306
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.06681 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -9.6206
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.06681 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -12.5603
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.045118 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.54142
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.015751 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.094506
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.06515 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -21.8904
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.064854 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -21.6612
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.064854 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -22.0504
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.064636 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -2.4562
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.064783 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.6196
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.064783 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.6196
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.064675 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -2.4577
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.06399 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -1.8557
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.065134 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -9.6594
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.065134 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -9.6789
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.065134 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -9.9655
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -10.5094
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -10.1768
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -6.6515
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -9.6447
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -9.7777
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -8.4474
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.06234 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -9.1328
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.06234 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -9.2201
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.06234 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -10.7848
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.063016 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -13.0443
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.063016 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -13.6556
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.063016 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -15.2499
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.063021 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -9.075
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.063021 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -9.075
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.063021 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -10.7766
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.00473 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -1.4663
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.00473 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -1.9535
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.003457 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -0.14519
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.003457 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.15211
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.003457 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.15211
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.003457 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -0.16248
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.32756
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.30751
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.30751
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.3142
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006685 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -1.0295
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006685 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -0.98938
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.32088
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.32088
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 7.3283
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 7.3283
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 9.7152
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 8.3752
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 8.3752
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 12.0394
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 21.7944
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 14.875
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 13.8596
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 14.2365
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 15.388
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 21.9828
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.10658 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 22.2763
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.10658 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 13.483
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.10658 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 26.5397
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.10658 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 20.9972
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.10562 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 21.1238
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.10562 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 12.875
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.10385 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 15.4741
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.10544 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 18.9787
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.10544 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 18.9787
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.10538 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 23.711
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.10619 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 13.2731
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.10619 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 13.2731
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 16.8043
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 16.9244
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 37.0896
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 17.1644
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 17.2845
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 37.2096
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.11882 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 23.2895
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.11882 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 13.1895
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.11939 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 19.577
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 19.9417
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 19.9417
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 50.3407
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 19.6986
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 19.577
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 19.8201
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 49.7328
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.12091 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.12091 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.12346 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 18.2716
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.12346 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 16.0494
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.12346 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 17.9013
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.12346 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 49.2593
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.12301 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 18.5376
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.12301 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 18.5745
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.12301 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 21.822
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.12288 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 18.6171
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.12288 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 18.7154
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.12288 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 21.8121
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.038449 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 22.3389
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.29529 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 252.4695
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.29529 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 252.4695
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.54391 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 17.4052
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.51456 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 24.6988
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.51456 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 23.6697
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.54 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 6.48
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.54 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 27.5402
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.54 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 9.1801
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.54 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 11.8801
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.54 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 13.5001
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.51456 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 54.0287
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.10599 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 8.9029
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.09757 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 7.8056
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.097515 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 14.6273
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.097515 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 14.6273
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1494 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -10.5778
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1494 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -9.9652
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1494 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -7.9184
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -22.8887
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -22.9335
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -22.7542
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -14.3428
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -36.4546
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.1494 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -5.9762
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.14938 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -14.9828
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.14938 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -13.8774
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.14938 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -15.3413
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.14938 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -15.2368
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.14938 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -4.7802
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.14938 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -4.4814
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.13419 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -14.8948
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.13419 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -14.8948
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.13419 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -15.9683
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.13419 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -14.6935
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.29529 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 44.9721
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.29529 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 45.1788
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.15864 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -21.5756
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.14434 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -4.7631
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.15869 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -6.665
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.15869 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -6.665
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.15869 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -6.0302
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.15869 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -6.0302
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.13172 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -9.3521
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.13172 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -1.3172
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.14347 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -23.3851
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.14347 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -23.3851
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.14347 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -35.1494
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.15519 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -10.0874
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.15519 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -9.3114
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.15519 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -10.0874
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.15519 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -10.0874
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.15744 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -23.4584
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.15744 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -10.2493
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -14.0607
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -13.5353
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -13.4426
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -8.421
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -1.8851
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.16151 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -119.999
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.16036 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -117.8668
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.16185 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -27.8382
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.16185 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -27.8382
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.16185 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -27.8382
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.1682 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -29.0977
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.15887 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -27.4845
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.15887 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -21.4474
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.16266 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -26.4807
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.16266 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -26.253
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.16266 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -25.8464
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.16266 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -43.7875
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -10.0809
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -9.9549
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -13.0107
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -11.593
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -25.588
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -24.6316
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -24.6943
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -24.6159
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -42.1762
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.16145 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.80724
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.16145 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -3.3904
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.2128 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -32.8144
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.2128 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -33.1974
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.2128 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -33.1974
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.2128 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -80.8655
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.16295 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -64.8521
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -7.1858
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -7.1858
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -7.1858
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -8.5918
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -8.5918
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -8.4356
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.17439 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 144.2205
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.17439 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 142.8254
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.14302 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -6.5931
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -8.5074
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -8.5074
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -11.7537
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -8.2836
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -8.2836
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -11.4179
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.15754 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -28.3565
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.15754 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -24.9852
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.15754 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -24.7332
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.15708 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -5.4978
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.15278 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -70.1279
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -10.4948
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -10.6562
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -11.3021
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -10.1719
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -10.0104
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -16.7916
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -9.526
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.1682 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -26.2384
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.1682 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -25.902
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.1682 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -25.902
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.1682 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -27.2476
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.16172 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -25.39
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.15796 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -11.2152
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.15796 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -11.3732
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.15796 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -6.1605
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.15796 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -4.7388
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.15645 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -12.2029
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.15645 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -12.5158
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -2.5516
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.15742 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -25.9743
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.1574 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -26.5999
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.1575 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -33.5475
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.15752 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -35.9157
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.15738 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -1.8886
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.15738 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -2.8328
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.15133 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -7.5665
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -16.6365
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -16.6365
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -8.6382
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -8.4782
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -8.6382
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -9.1181
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -8.6382
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -8.6382
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -9.278
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -9.278
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.16101 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -1.9322
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -9.1527
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -9.643
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -9.1527
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -9.1527
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -9.643
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -9.1527
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.11579 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -7.6425
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.14482 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -23.3157
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.14482 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -24.0398
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.14482 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -35.9149
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.14482 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -79.0706
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.14482 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -93.118
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.14339 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -93.3488
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.14339 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -80.8737
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.14339 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -86.0358
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.14482 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -1.8826
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.16148 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -1.9377
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -5.4618
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -5.5743
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -5.253
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -7.3735
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -2.8434
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -3.2771
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -3.1968
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -5.6225
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -2.8916
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -13.7188
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -23.775
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -7.9745
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -9.1835
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -5.7879
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -12.9907
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -11.0614
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -11.3186
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -6.431
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -2.3152
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -12.0904
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -9.0035
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -8.1031
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -9.2607
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -8.3346
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -12.9907
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -12.4762
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -13.248
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -9.7752
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -10.2897
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -10.2897
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -21.9942
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.34124
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.094977 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 7.2657
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.097677 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 7.8142
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.097677 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 3.9071
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.098113 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 7.849
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.097583 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 7.8066
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.095341 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 7.6273
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.094607 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 7.947
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.098113 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 7.849
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -3.7107
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.10536 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 12.6426
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.10536 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 24.5477
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.10536 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 17.9314
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -7.2261
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -5.9892
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -7.2912
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -3.7433
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -3.255
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.10741 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 6.4445
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.023217 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.082912 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.099723 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.47867
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 3.9935
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 11.448
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 14.3766
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 12.6727
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 11.1818
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 8.5727
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.1047 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 15.705
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.10447 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 11.7531
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.10447 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 15.6186
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.10447 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 19.4318
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.10447 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 22.4092
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.063504 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.018726 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.048387 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -2.1251
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -3.3092
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -5.6165
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -5.9866
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -2.6112
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -2.4201
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -1.2101
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -5.9866
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -2.2927
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -2.7385
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -1.4011
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.7941
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.0746
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.5015
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.0746
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.7941
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.7941
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -9.4257
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.1843
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -3.5028
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.1843
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.066515 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.79818
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.070343 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -1.0551
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.070343 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -1.6179
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.07491 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -3.5957
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.071133 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.56906
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.065108 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -11.7194
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.06515 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -11.727
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.064854 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -11.6737
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.064854 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -11.6737
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.048383 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -4.8383
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.048383 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -4.8383
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6492
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6492
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6492
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -1.0555
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6492
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6492
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.6492
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.98952
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.048383 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.048383 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -24.1915
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.048383 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -24.1915
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.048383 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.057534 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.002962 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.054289 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.060431 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 99 C: 967 GIBN_CRE 345 44645 SNGLTN_3 345 75 | [7 empty] | 826.4486
Number of Bus | Name of Bus | ID | Max MW | L: 967 GIBN_CRE 345 44645 SNGLTN_3 345 99 C: 967 GIBN_CRE 345 44645 SNGLTN_3 345 75 | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.087047 | north | -0.059014 | 0.1227 | -0.017647 | 0.23809 | 0.017647 | west | Y | 0.059014 | 10.5488
239 | BOSQUESW | 1 | 149 | 0.087047 | north | -0.059014 | 0.1227 | -0.017647 | 0.23809 | 0.017647 | west | Y | 0.059014 | 6.1638
244 | WHITNYDM | 1 | 15 | 0.09441 | north | -0.051651 | 0.13007 | -0.010284 | 0.24545 | 0.010284 | west | Y | 0.051651 | 0.62052
245 | WHITNYDM | 2 | 15 | 0.09441 | north | -0.051651 | 0.13007 | -0.010284 | 0.24545 | 0.010284 | west | Y | 0.051651 | 0.62052
247 | BOSQUESW | 2 | 153 | 0.087047 | north | -0.059014 | 0.1227 | -0.017647 | 0.23809 | 0.017647 | west | Y | 0.059014 | 6.3293
251 | BOSQUESW | 2 | 150 | 0.089545 | north | -0.056516 | 0.1252 | -0.015149 | 0.24059 | 0.015149 | west | Y | 0.056516 | 6.2052
253 | BOSQUESW | 2 | 80 | 0.089545 | north | -0.056516 | 0.1252 | -0.015149 | 0.24059 | 0.015149 | west | Y | 0.056516 | 3.3094
332 | RWMILLER | 1 | 73 | 0.11005 | north | -0.036011 | 0.14571 | 0.0053563 | 0.26109 | 0.0053563 | west | Y | 0.036011 | 2.2378
333 | RWMILLER | 2 | 119 | 0.11005 | north | -0.036011 | 0.14571 | 0.0053563 | 0.26109 | 0.0053563 | west | Y | 0.036011 | 3.648
334 | RWMILLER | 3 | 205 | 0.11005 | north | -0.036011 | 0.14571 | 0.0053563 | 0.26109 | 0.0053563 | west | Y | 0.036011 | 6.2843
335 | RWMILLER | 4 | 102 | 0.11005 | north | -0.036011 | 0.14571 | 0.0053563 | 0.26109 | 0.0053563 | west | Y | 0.036011 | 3.1268
336 | RWMILLER | 5 | 96 | 0.11005 | north | -0.036011 | 0.14571 | 0.0053563 | 0.26109 | 0.0053563 | west | Y | 0.036011 | 2.9429
344 | MRSSHPRD | 1 | 12 | 0.11139 | north | -0.034671 | 0.14705 | 0.0066963 | 0.26243 | 0.0066963 | west | Y | 0.034671 | 0.3357
345 | MRSSHPRD | 2 | 12 | 0.11139 | north | -0.034671 | 0.14705 | 0.0066963 | 0.26243 | 0.0066963 | west | Y | 0.034671 | 0.3357
366 | JNSNCNTY | 1 | 168 | 0.11045 | north | -0.035607 | 0.14611 | 0.0057603 | 0.26149 | 0.0057603 | west | Y | 0.035607 | 5.0143
367 | JNSNCNTY | 2 | 90 | 0.11045 | north | -0.035607 | 0.14611 | 0.0057603 | 0.26149 | 0.0057603 | west | Y | 0.035607 | 2.6862
503 | NTHTEXAS | 1 | 18 | 0.11237 | north | -0.033691 | 0.14803 | 0.0076763 | 0.26341 | 0.0076763 | west | Y | 0.033691 | 0.46827
504 | NTHTEXAS | 2 | 18 | 0.11237 | north | -0.033691 | 0.14803 | 0.0076763 | 0.26341 | 0.0076763 | west | Y | 0.033691 | 0.46827
505 | NTHTEXAS | 3 | 38 | 0.11237 | north | -0.033691 | 0.14803 | 0.0076763 | 0.26341 | 0.0076763 | west | Y | 0.033691 | 0.98857
580 | JCKCNTY8 | 1 | 288 | 0.11386 | north | -0.032197 | 0.14952 | 0.0091703 | 0.2649 | 0.0091703 | west | Y | 0.032197 | 6.6318
581 | JCKCNTY8 | 2 | 147 | 0.11386 | north | -0.032197 | 0.14952 | 0.0091703 | 0.2649 | 0.0091703 | west | Y | 0.032197 | 3.385
582 | JCKCNTY8 | 3 | 147 | 0.11386 | north | -0.032197 | 0.14952 | 0.0091703 | 0.2649 | 0.0091703 | west | Y | 0.032197 | 3.385
728 | WOLFRIDG | 1 | 112.5 | 0.11567 | north | -0.030392 | 0.15133 | 0.010975 | 0.26671 | 0.010975 | west | Y | 0.030392 | 2.1844
837 | NEWMAN_G | 1 | 40 | 0.12061 | north | -0.025455 | 0.15626 | 0.015912 | 0.27165 | 0.015912 | west | Y | 0.025455 | 0.38172
842 | OLINGER_ | 1 | 79 | 0.12055 | north | -0.025507 | 0.15621 | 0.01586 | 0.27159 | 0.01586 | west | Y | 0.025507 | 0.76212
843 | OLINGER_ | 1 | 106 | 0.12055 | north | -0.025507 | 0.15621 | 0.01586 | 0.27159 | 0.01586 | west | Y | 0.025507 | 1.0226
844 | OLINGER_ | 1 | 146 | 0.12055 | north | -0.025507 | 0.15621 | 0.01586 | 0.27159 | 0.01586 | west | Y | 0.025507 | 1.4085
845 | OLINGER_ | 1 | 76 | 0.12055 | north | -0.025507 | 0.15621 | 0.01586 | 0.27159 | 0.01586 | west | Y | 0.025507 | 0.73318
923 | SPENCER_ | 1 | 60 | 0.11701 | north | -0.029046 | 0.15267 | 0.012321 | 0.26806 | 0.012321 | west | Y | 0.029046 | 1.0035
924 | SPENCER_ | 1 | 63 | 0.11701 | north | -0.029046 | 0.15267 | 0.012321 | 0.26806 | 0.012321 | west | Y | 0.029046 | 1.0537
948 | STEAM1 | 1 | 20 | 0.12069 | north | -0.025368 | 0.15635 | 0.015999 | 0.27173 | 0.015999 | west | Y | 0.025368 | 0.18738
949 | STEAM2 | 1 | 25 | 0.12069 | north | -0.025368 | 0.15635 | 0.015999 | 0.27173 | 0.015999 | west | Y | 0.025368 | 0.23423
950 | STEAM3 | 1 | 41 | 0.12069 | north | -0.025368 | 0.15635 | 0.015999 | 0.27173 | 0.015999 | west | Y | 0.025368 | 0.38413
990 | GIBN_CRE | 1 | 463 | 0.63771 | north | 0.49165 | 0.67337 | 0.53302 | 0.78875 | 0.49165 | North | N | 0.49165 | 0
1002 | PBCTAGE_ | A | 66 | 0.10362 | west | -0.042442 | 0.13928 | -0.0010747 | 0.25466 | 0.0010747 | west | N | 0.0010747 | 0
1003 | PBCTBGE_ | B | 65 | 0.10362 | west | -0.042442 | 0.13928 | -0.0010747 | 0.25466 | 0.0010747 | west | N | 0.0010747 | 0
1004 | PBCTCGE_ | C | 67 | 0.10362 | west | -0.042442 | 0.13928 | -0.0010747 | 0.25466 | 0.0010747 | west | N | 0.0010747 | 0
1005 | PBCTDGE_ | D | 67 | 0.10362 | west | -0.042442 | 0.13928 | -0.0010747 | 0.25466 | 0.0010747 | west | N | 0.0010747 | 0
1006 | PBCTEGE_ | E | 67 | 0.10362 | west | -0.042442 | 0.13928 | -0.0010747 | 0.25466 | 0.0010747 | west | N | 0.0010747 | 0
1007 | PB5GEN_6 | MB | 114 | 0.10362 | west | -0.042442 | 0.13928 | -0.0010747 | 0.25466 | 0.0010747 | west | N | 0.0010747 | 0
1008 | PB6GEN_7 | MB | 515 | 0.10362 | west | -0.042442 | 0.13928 | -0.0010747 | 0.25466 | 0.0010747 | west | N | 0.0010747 | 0
1039 | MRGNAG_1 | A | 66 | 0.10575 | west | -0.040316 | 0.1414 | 0.0010513 | 0.25679 | 0.0010513 | west | N | 0.0010513 | 0
1040 | MRGNBG_2 | B | 69 | 0.10575 | west | -0.040316 | 0.1414 | 0.0010513 | 0.25679 | 0.0010513 | west | N | 0.0010513 | 0
1041 | MRGNCG_3 | C | 69 | 0.10575 | west | -0.040316 | 0.1414 | 0.0010513 | 0.25679 | 0.0010513 | west | N | 0.0010513 | 0
1042 | MRGNDG_4 | D | 67 | 0.10575 | west | -0.040316 | 0.1414 | 0.0010513 | 0.25679 | 0.0010513 | west | N | 0.0010513 | 0
1043 | MRGNEG_5 | E | 67 | 0.10575 | west | -0.040316 | 0.1414 | 0.0010513 | 0.25679 | 0.0010513 | west | N | 0.0010513 | 0
1044 | MRGNFG_6 | F | 65 | 0.10575 | west | -0.040316 | 0.1414 | 0.0010513 | 0.25679 | 0.0010513 | west | N | 0.0010513 | 0
1045 | CALENG1G | 1 | 70 | 0.10545 | west | -0.040614 | 0.1411 | 0.00075332 | 0.25649 | 0.00075332 | west | N | 0.00075332 | 0
1046 | CALENG2G | 2 | 73.4 | 0.10545 | west | -0.040614 | 0.1411 | 0.00075332 | 0.25649 | 0.00075332 | west | N | 0.00075332 | 0
1047 | CALENG3G | 3 | 70.4 | 0.10545 | west | -0.040614 | 0.1411 | 0.00075332 | 0.25649 | 0.00075332 | west | N | 0.00075332 | 0
1058 | LONGSHOR | 1 | 150 | 0.10562 | west | -0.040442 | 0.14128 | 0.00092532 | 0.25666 | 0.00092532 | west | N | 0.00092532 | 0
1058 | LONGSHOR | 2 | 220 | 0.10562 | west | -0.040442 | 0.14128 | 0.00092532 | 0.25666 | 0.00092532 | west | N | 0.00092532 | 0
1061 | CIELOGEN | 1 | 99 | 0.10585 | west | -0.040215 | 0.1415 | 0.0011523 | 0.25689 | 0.0011523 | west | N | 0.0011523 | 0
1062 | CIELOGEN | 1 | 61 | 0.10585 | west | -0.040215 | 0.1415 | 0.0011523 | 0.25689 | 0.0011523 | west | N | 0.0011523 | 0
1068 | SCURRYCW | 1 | 141 | 0.10583 | west | -0.040232 | 0.14149 | 0.0011353 | 0.25687 | 0.0011353 | west | N | 0.0011353 | 0
1069 | KINDERMG | 1 | 25 | 0.10585 | west | -0.040215 | 0.1415 | 0.0011523 | 0.25689 | 0.0011523 | west | N | 0.0011523 | 0
1070 | KINDERMG | 1 | 45.7 | 0.10585 | west | -0.040215 | 0.1415 | 0.0011523 | 0.25689 | 0.0011523 | west | N | 0.0011523 | 0
1071 | KINDERMG | 1 | 45.7 | 0.10585 | west | -0.040215 | 0.1415 | 0.0011523 | 0.25689 | 0.0011523 | west | N | 0.0011523 | 0
1073 | SCURRYCW | 2 | 120 | 0.10583 | west | -0.040232 | 0.14149 | 0.0011353 | 0.25687 | 0.0011353 | west | N | 0.0011353 | 0
1320 | BSP 1 | 1 | 25.8 | 0.10493 | west | -0.041135 | 0.14058 | 0.00023232 | 0.25597 | 0.00023232 | west | N | 0.00023232 | 0
1326 | STANTONW | 1 | 100.5 | 0.10474 | west | -0.041324 | 0.14039 | 4.3316e-05 | 0.25578 | 4.3316e-05 | west | N | 4.3316e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.10526 | west | -0.040804 | 0.14091 | 0.00056332 | 0.2563 | 0.00056332 | west | N | 0.00056332 | 0
1328 | OCOTILLO | 1 | 58 | 0.10472 | west | -0.041342 | 0.14038 | 2.5316e-05 | 0.25576 | 2.5316e-05 | west | N | 2.5316e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.10486 | west | -0.041198 | 0.14052 | 0.00016932 | 0.2559 | 0.00016932 | west | N | 0.00016932 | 0
1343 | TRENTIPP | 1 | 150 | 0.10605 | west | -0.040013 | 0.14171 | 0.0013543 | 0.25709 | 0.0013543 | west | N | 0.0013543 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.10417 | west | -0.041888 | 0.13983 | -0.00052068 | 0.25521 | 0.00052068 | west | N | 0.00052068 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.10417 | west | -0.041888 | 0.13983 | -0.00052068 | 0.25521 | 0.00052068 | west | N | 0.00052068 | 0
1354 | AEPWIND_ | 1 | 101 | 0.10605 | west | -0.040013 | 0.14171 | 0.0013543 | 0.25709 | 0.0013543 | west | N | 0.0013543 | 0
1360 | GUNSIGHT | 1 | 120 | 0.10528 | west | -0.040781 | 0.14094 | 0.00058632 | 0.25632 | 0.00058632 | west | N | 0.00058632 | 0
1432 | GRHAMSES | 2 | 366 | 0.11138 | north | -0.034682 | 0.14704 | 0.0066853 | 0.26242 | 0.0066853 | west | Y | 0.034682 | 10.2469
1433 | GRHAMSES | 1 | 242 | 0.1107 | north | -0.035363 | 0.14636 | 0.0060043 | 0.26174 | 0.0060043 | west | Y | 0.035363 | 7.1049
1437 | MESQUITW | 1 | 400 | 0.10857 | west | -0.037493 | 0.14423 | 0.0038743 | 0.25961 | 0.0038743 | west | N | 0.0038743 | 0
1438 | MESQUITW | 1 | 236 | 0.10857 | west | -0.03749 | 0.14423 | 0.0038773 | 0.25961 | 0.0038773 | west | N | 0.0038773 | 0
1442 | COKFIELD | 1 | 165 | 0.10924 | west | -0.036816 | 0.1449 | 0.0045513 | 0.26029 | 0.0045513 | west | N | 0.0045513 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.11313 | north | -0.032926 | 0.14879 | 0.0084413 | 0.26418 | 0.0084413 | west | Y | 0.032926 | 4.995
1454 | WCPWRCO_ | 2 | 201 | 0.11313 | north | -0.032926 | 0.14879 | 0.0084413 | 0.26418 | 0.0084413 | west | Y | 0.032926 | 4.9215
1455 | WCPWRCO_ | 3 | 242 | 0.11313 | north | -0.032926 | 0.14879 | 0.0084413 | 0.26418 | 0.0084413 | west | Y | 0.032926 | 5.9254
1479 | WFCOGEN_ | 1 | 20 | 0.11152 | west | -0.034538 | 0.14718 | 0.0068293 | 0.26256 | 0.0068293 | west | N | 0.0068293 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.11152 | west | -0.034538 | 0.14718 | 0.0068293 | 0.26256 | 0.0068293 | west | N | 0.0068293 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.11152 | west | -0.034538 | 0.14718 | 0.0068293 | 0.26256 | 0.0068293 | west | N | 0.0068293 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.11152 | west | -0.034538 | 0.14718 | 0.0068293 | 0.26256 | 0.0068293 | west | N | 0.0068293 | 0
1600 | BARTNWND | 1 | 120 | 0.11123 | north | -0.034832 | 0.14689 | 0.0065353 | 0.26227 | 0.0065353 | west | Y | 0.034832 | 3.3957
1643 | SLSTR1PP | 1 | 60 | 0.10636 | north | -0.039698 | 0.14202 | 0.0016693 | 0.2574 | 0.0016693 | west | Y | 0.039698 | 2.2817
1675 | PEC_1G | 1 | 75 | 0.12018 | north | -0.025886 | 0.15583 | 0.015481 | 0.27122 | 0.015481 | west | Y | 0.025886 | 0.78038
1676 | PEC_2G | 2 | 79.6 | 0.12018 | north | -0.025886 | 0.15583 | 0.015481 | 0.27122 | 0.015481 | west | Y | 0.025886 | 0.82825
1677 | PEC_3G | 3 | 88.4 | 0.12018 | north | -0.025886 | 0.15583 | 0.015481 | 0.27122 | 0.015481 | west | Y | 0.025886 | 0.91981
1678 | LAMARPWR | 1 | 160 | 0.12012 | north | -0.025939 | 0.15578 | 0.015428 | 0.27116 | 0.015428 | west | Y | 0.025939 | 1.6818
1679 | LAMARPWR | 2 | 156 | 0.12012 | north | -0.025939 | 0.15578 | 0.015428 | 0.27116 | 0.015428 | west | Y | 0.025939 | 1.6397
1680 | LAMARPWR | 3 | 196 | 0.12012 | north | -0.025939 | 0.15578 | 0.015428 | 0.27116 | 0.015428 | west | Y | 0.025939 | 2.0602
1681 | LAMARPWR | 4 | 156 | 0.12012 | north | -0.025939 | 0.15578 | 0.015428 | 0.27116 | 0.015428 | west | Y | 0.025939 | 1.6397
1682 | LAMARPWR | 5 | 157 | 0.12012 | north | -0.025939 | 0.15578 | 0.015428 | 0.27116 | 0.015428 | west | Y | 0.025939 | 1.6502
1683 | LAMARPWR | 6 | 198 | 0.12012 | north | -0.025939 | 0.15578 | 0.015428 | 0.27116 | 0.015428 | west | Y | 0.025939 | 2.0812
1687 | VALLEY_1 | 1 | 170 | 0.11979 | north | -0.026276 | 0.15544 | 0.015091 | 0.27083 | 0.015091 | west | Y | 0.026276 | 1.9015
1688 | VALLEY_2 | 2 | 520 | 0.11979 | north | -0.026276 | 0.15544 | 0.015091 | 0.27083 | 0.015091 | west | Y | 0.026276 | 5.8163
1689 | VALLEY_3 | 3 | 370 | 0.12003 | north | -0.02603 | 0.15569 | 0.015337 | 0.27107 | 0.015337 | west | Y | 0.02603 | 3.9565
1701 | MOSES_1G | 1 | 558 | 0.12029 | north | -0.025767 | 0.15595 | 0.0156 | 0.27133 | 0.0156 | west | Y | 0.025767 | 5.6733
1702 | MOSES_2G | 2 | 579 | 0.12029 | north | -0.025767 | 0.15595 | 0.0156 | 0.27133 | 0.0156 | west | Y | 0.025767 | 5.8868
1703 | MOSES_3G | 3 | 808 | 0.12029 | north | -0.025767 | 0.15595 | 0.0156 | 0.27133 | 0.0156 | west | Y | 0.025767 | 8.215
1861 | EAGLEMNT | MB | 112 | 0.11504 | north | -0.031021 | 0.1507 | 0.010346 | 0.26608 | 0.010346 | west | Y | 0.031021 | 2.3156
1862 | EAGLEMNT | MB | 100 | 0.11504 | north | -0.031021 | 0.1507 | 0.010346 | 0.26608 | 0.010346 | west | Y | 0.031021 | 2.0675
1863 | EAGLEMNT | MB | 378 | 0.11504 | north | -0.031021 | 0.1507 | 0.010346 | 0.26608 | 0.010346 | west | Y | 0.031021 | 7.8152
1877 | WLFHOLW_ | 1 | 217.3 | 0.11272 | north | -0.033342 | 0.14838 | 0.0080253 | 0.26376 | 0.0080253 | west | Y | 0.033342 | 5.5014
1878 | WLFHOLW_ | 2 | 205 | 0.11272 | north | -0.033342 | 0.14838 | 0.0080253 | 0.26376 | 0.0080253 | west | Y | 0.033342 | 5.19
1879 | WLFHOLW_ | 3 | 272.4 | 0.11272 | north | -0.033342 | 0.14838 | 0.0080253 | 0.26376 | 0.0080253 | west | Y | 0.033342 | 6.8964
1889 | DECRDOVA | MB | 770 | 0.11302 | north | -0.033041 | 0.14868 | 0.0083263 | 0.26406 | 0.0083263 | west | Y | 0.033041 | 19.0306
1892 | DECRDOVA | A | 70 | 0.11142 | north | -0.034637 | 0.14708 | 0.0067303 | 0.26246 | 0.0067303 | west | Y | 0.034637 | 1.9535
1893 | DECRDOVA | B | 69 | 0.11142 | north | -0.034637 | 0.14708 | 0.0067303 | 0.26246 | 0.0067303 | west | Y | 0.034637 | 1.9256
1894 | DECRDOVA | C | 69 | 0.11142 | north | -0.034637 | 0.14708 | 0.0067303 | 0.26246 | 0.0067303 | west | Y | 0.034637 | 1.9256
1895 | DECRDOVA | D | 68 | 0.11142 | north | -0.034637 | 0.14708 | 0.0067303 | 0.26246 | 0.0067303 | west | Y | 0.034637 | 1.8977
1898 | COMCHEPK | 1 | 1157 | 0.11242 | north | -0.033638 | 0.14808 | 0.0077293 | 0.26346 | 0.0077293 | west | Y | 0.033638 | 29.9769
1899 | COMCHEPK | 2 | 1158 | 0.11242 | north | -0.033638 | 0.14808 | 0.0077293 | 0.26346 | 0.0077293 | west | Y | 0.033638 | 30.0028
1937 | MDLTHELP | 5 | 224 | 0.11281 | north | -0.033251 | 0.14847 | 0.0081163 | 0.26385 | 0.0081163 | west | Y | 0.033251 | 5.6303
1938 | MDLTHELP | 6 | 226 | 0.11281 | north | -0.033251 | 0.14847 | 0.0081163 | 0.26385 | 0.0081163 | west | Y | 0.033251 | 5.6805
1941 | MDLTHELP | 1 | 216.4 | 0.1142 | north | -0.03186 | 0.14986 | 0.0095073 | 0.26524 | 0.0095073 | west | Y | 0.03186 | 4.8372
1942 | MDLTHELP | 2 | 216.1 | 0.1142 | north | -0.03186 | 0.14986 | 0.0095073 | 0.26524 | 0.0095073 | west | Y | 0.03186 | 4.8305
1943 | MDLTHELP | 3 | 212 | 0.11281 | north | -0.033251 | 0.14847 | 0.0081163 | 0.26385 | 0.0081163 | west | Y | 0.033251 | 5.3286
1944 | MDLTHELP | 4 | 211 | 0.11281 | north | -0.033251 | 0.14847 | 0.0081163 | 0.26385 | 0.0081163 | west | Y | 0.033251 | 5.3035
1947 | HANDLEY_ | 3 | 395 | 0.11514 | north | -0.030923 | 0.1508 | 0.010444 | 0.26618 | 0.010444 | west | Y | 0.030923 | 8.0893
1948 | HANDLEY_ | 4 | 435 | 0.11546 | north | -0.030597 | 0.15112 | 0.01077 | 0.2665 | 0.01077 | west | Y | 0.030597 | 8.6248
1949 | HANDLEY_ | 5 | 435 | 0.11514 | north | -0.030923 | 0.1508 | 0.010444 | 0.26618 | 0.010444 | west | Y | 0.030923 | 8.9084
2371 | COLLIN_1 | MB | 138 | 0.11907 | north | -0.026994 | 0.15472 | 0.014373 | 0.27011 | 0.014373 | west | Y | 0.026994 | 1.7417
2413 | MTCK6_G | 6 | 118 | 0.11973 | north | -0.026326 | 0.15539 | 0.015041 | 0.27078 | 0.015041 | west | Y | 0.026326 | 1.3316
2414 | MTCK7_G | 7 | 115 | 0.11973 | north | -0.026326 | 0.15539 | 0.015041 | 0.27078 | 0.015041 | west | Y | 0.026326 | 1.2978
2417 | MTCK8_G | 8 | 556 | 0.11973 | north | -0.026326 | 0.15539 | 0.015041 | 0.27078 | 0.015041 | west | Y | 0.026326 | 6.2745
2451 | LKHB1_G | 1 | 388 | 0.121 | north | -0.025061 | 0.15666 | 0.016306 | 0.27204 | 0.016306 | west | Y | 0.025061 | 3.397
2452 | LKHB2_G | 2 | 515 | 0.121 | north | -0.025061 | 0.15666 | 0.016306 | 0.27204 | 0.016306 | west | Y | 0.025061 | 4.5089
3097 | MARTLAKE | 1 | 785 | 0.12344 | north | -0.022617 | 0.1591 | 0.01875 | 0.27448 | 0.01875 | west | Y | 0.022617 | 3.0357
3098 | MARTLAKE | 2 | 795 | 0.12344 | north | -0.022617 | 0.1591 | 0.01875 | 0.27448 | 0.01875 | west | Y | 0.022617 | 3.0744
3099 | MARTLAKE | 3 | 780 | 0.12344 | north | -0.022617 | 0.1591 | 0.01875 | 0.27448 | 0.01875 | west | Y | 0.022617 | 3.0164
3107 | STRYKER_ | 1 | 182 | 0.12512 | north | -0.020942 | 0.16078 | 0.020425 | 0.27616 | 0.020425 | west | Y | 0.020942 | 0.094116
3108 | STRYKER_ | 2 | 484 | 0.12512 | north | -0.020942 | 0.16078 | 0.020425 | 0.27616 | 0.020425 | west | Y | 0.020942 | 0.25029
3126 | TRINIDAD | 1 | 224 | 0.12183 | north | -0.024228 | 0.15749 | 0.017139 | 0.27287 | 0.017139 | west | Y | 0.024228 | 1.588
3309 | ASPN_G | 1 | 50 | 0.12405 | north | -0.022014 | 0.1597 | 0.019353 | 0.27509 | 0.019353 | west | Y | 0.022014 | 0.13306
3348 | CHAMPION | MB | 42 | 0.12406 | north | -0.022003 | 0.15972 | 0.019364 | 0.2751 | 0.019364 | west | Y | 0.022003 | 0.11084
3381 | BBRN_1G | 1 | 615 | 0.12281 | north | -0.023249 | 0.15847 | 0.018118 | 0.27385 | 0.018118 | west | Y | 0.023249 | 3.1556
3382 | BBRN_2G | 2 | 587 | 0.12281 | north | -0.023249 | 0.15847 | 0.018118 | 0.27385 | 0.018118 | west | Y | 0.023249 | 3.012
3403 | THOUSE_1 | MB | 537 | 0.083869 | north | -0.062192 | 0.11953 | -0.020825 | 0.23491 | 0.020825 | west | Y | 0.062192 | 22.2145
3404 | THOUSE_2 | 2 | 787 | 0.083869 | north | -0.062192 | 0.11953 | -0.020825 | 0.23491 | 0.020825 | west | Y | 0.062192 | 32.5564
3416 | LAKE_CRK | MB | 75 | 0.08516 | north | -0.060901 | 0.12082 | -0.019534 | 0.2362 | 0.019534 | west | Y | 0.060901 | 3.1026
3417 | LAKE_CRK | MB | 222 | 0.08516 | north | -0.060901 | 0.12082 | -0.019534 | 0.2362 | 0.019534 | west | Y | 0.060901 | 9.1836
3432 | SANDOW_4 | 4 | 569 | 0.038449 | south | -0.10761 | 0.074106 | -0.066245 | 0.18949 | 0.066245 | west | Y | 0.074106 | 4.4732
5026 | BRAUNIG_ | 1 | 209 | -0.040822 | south | -0.18688 | -0.0051648 | -0.14552 | 0.11022 | 0.0051648 | south | N | 0.0051648 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.040822 | south | -0.18688 | -0.0051648 | -0.14552 | 0.11022 | 0.0051648 | south | N | 0.0051648 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.040631 | south | -0.18669 | -0.0049738 | -0.14532 | 0.11041 | 0.0049738 | south | N | 0.0049738 | 0
5031 | BRA_VHBC | 1 | 46 | -0.040822 | south | -0.18688 | -0.0051648 | -0.14552 | 0.11022 | 0.0051648 | south | N | 0.0051648 | 0
5032 | BRA_VHBC | 2 | 47 | -0.040822 | south | -0.18688 | -0.0051648 | -0.14552 | 0.11022 | 0.0051648 | south | N | 0.0051648 | 0
5033 | BRA_VHBC | 3 | 46 | -0.040822 | south | -0.18688 | -0.0051648 | -0.14552 | 0.11022 | 0.0051648 | south | N | 0.0051648 | 0
5034 | BRA_VHBC | 4 | 46 | -0.040822 | south | -0.18688 | -0.0051648 | -0.14552 | 0.11022 | 0.0051648 | south | N | 0.0051648 | 0
5111 | CALAVER_ | 1 | 424 | -0.040695 | south | -0.18676 | -0.0050378 | -0.14539 | 0.11035 | 0.0050378 | south | N | 0.0050378 | 0
5112 | CALAVER_ | 2 | 425 | -0.040695 | south | -0.18676 | -0.0050378 | -0.14539 | 0.11035 | 0.0050378 | south | N | 0.0050378 | 0
5264 | LEON_LCP | 3 | 58 | -0.040675 | south | -0.18674 | -0.0050178 | -0.14537 | 0.11037 | 0.0050178 | south | N | 0.0050178 | 0
5265 | LEON_LCP | 4 | 89 | -0.040675 | south | -0.18674 | -0.0050178 | -0.14537 | 0.11037 | 0.0050178 | south | N | 0.0050178 | 0
5266 | LEON_LCP | 1 | 44 | -0.040675 | south | -0.18674 | -0.0050178 | -0.14537 | 0.11037 | 0.0050178 | south | N | 0.0050178 | 0
5267 | LEON_LCP | 2 | 44 | -0.040675 | south | -0.18674 | -0.0050178 | -0.14537 | 0.11037 | 0.0050178 | south | N | 0.0050178 | 0
5268 | LEON_LCP | 3 | 43 | -0.040675 | south | -0.18674 | -0.0050178 | -0.14537 | 0.11037 | 0.0050178 | south | N | 0.0050178 | 0
5269 | LEON_LCP | 4 | 45 | -0.040675 | south | -0.18674 | -0.0050178 | -0.14537 | 0.11037 | 0.0050178 | south | N | 0.0050178 | 0
5396 | CALAVER_ | 1 | 412 | -0.040677 | south | -0.18674 | -0.0050198 | -0.14537 | 0.11036 | 0.0050198 | south | N | 0.0050198 | 0
5397 | CALAVER_ | 2 | 400 | -0.040677 | south | -0.18674 | -0.0050198 | -0.14537 | 0.11036 | 0.0050198 | south | N | 0.0050198 | 0
5401 | CALAVER_ | 1 | 546 | -0.042766 | south | -0.18883 | -0.0071088 | -0.14746 | 0.10827 | 0.0071088 | south | N | 0.0071088 | 0
5402 | CALAVER_ | 2 | 750 | -0.042766 | south | -0.18883 | -0.0071088 | -0.14746 | 0.10827 | 0.0071088 | south | N | 0.0071088 | 0
5436 | TUTTL_WB | MB | 61 | -0.040851 | south | -0.18691 | -0.0051938 | -0.14554 | 0.11019 | 0.0051938 | south | N | 0.0051938 | 0
5438 | TUTTL_WB | MB | 95 | -0.040851 | south | -0.18691 | -0.0051938 | -0.14554 | 0.11019 | 0.0051938 | south | N | 0.0051938 | 0
5439 | TUTTL_WB | MB | 151 | -0.040851 | south | -0.18691 | -0.0051938 | -0.14554 | 0.11019 | 0.0051938 | south | N | 0.0051938 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.041854 | south | -0.18792 | -0.0061968 | -0.14655 | 0.10919 | 0.0061968 | south | N | 0.0061968 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.041854 | south | -0.18792 | -0.0061968 | -0.14655 | 0.10919 | 0.0061968 | south | N | 0.0061968 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.041854 | south | -0.18792 | -0.0061968 | -0.14655 | 0.10919 | 0.0061968 | south | N | 0.0061968 | 0
5503 | RAYBURNG | 1 | 22 | -0.068759 | south | -0.21482 | -0.033102 | -0.17345 | 0.082282 | 0.033102 | south | N | 0.033102 | 0
5505 | RAYBURNG | 1 | 11 | -0.068759 | south | -0.21482 | -0.033102 | -0.17345 | 0.082282 | 0.033102 | south | N | 0.033102 | 0
5506 | RAYBURNG | 1 | 11 | -0.068759 | south | -0.21482 | -0.033102 | -0.17345 | 0.082282 | 0.033102 | south | N | 0.033102 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.068081 | south | -0.21414 | -0.032424 | -0.17277 | 0.08296 | 0.032424 | south | N | 0.032424 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.068081 | south | -0.21414 | -0.032424 | -0.17277 | 0.08296 | 0.032424 | south | N | 0.032424 | 0
5511 | RAYBURNC | 1 | 46 | -0.068081 | south | -0.21414 | -0.032424 | -0.17277 | 0.08296 | 0.032424 | south | N | 0.032424 | 0
5512 | RAYBURNC | 1 | 48 | -0.068081 | south | -0.21414 | -0.032424 | -0.17277 | 0.08296 | 0.032424 | south | N | 0.032424 | 0
5728 | FALCONHY | 2 | 12 | -0.058225 | south | -0.20429 | -0.022568 | -0.16292 | 0.092816 | 0.022568 | south | N | 0.022568 | 0
5729 | FALCONHY | 3 | 11 | -0.058225 | south | -0.20429 | -0.022568 | -0.16292 | 0.092816 | 0.022568 | south | N | 0.022568 | 0
5890 | PEARSALL | 1 | 24 | -0.042087 | south | -0.18815 | -0.0064298 | -0.14678 | 0.10895 | 0.0064298 | south | N | 0.0064298 | 0
5891 | PEARSALL | 1 | 24 | -0.042087 | south | -0.18815 | -0.0064298 | -0.14678 | 0.10895 | 0.0064298 | south | N | 0.0064298 | 0
5892 | PEARSALL | 1 | 23 | -0.042087 | south | -0.18815 | -0.0064298 | -0.14678 | 0.10895 | 0.0064298 | south | N | 0.0064298 | 0
5903 | SANMIGUE | 1 | 396 | -0.048656 | south | -0.19472 | -0.012999 | -0.15335 | 0.10238 | 0.012999 | south | N | 0.012999 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.1113 | houston | -0.25736 | -0.075638 | -0.21599 | 0.039746 | 0.039746 | houston | N | 0.039746 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.1113 | houston | -0.25736 | -0.075638 | -0.21599 | 0.039746 | 0.039746 | houston | N | 0.039746 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | -0.14606 | 0.035657 | -0.10469 | 0.15104 | 0.035657 | south | Y | 0.14606 | 66.2426
5932 | SI_RAY9 | 9 | 38 | -0.063504 | south | -0.20957 | -0.027847 | -0.1682 | 0.087537 | 0.027847 | south | N | 0.027847 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.063504 | south | -0.20957 | -0.027847 | -0.1682 | 0.087537 | 0.027847 | south | N | 0.027847 | 0
5934 | SI_RAY5 | 5 | 15 | -0.063504 | south | -0.20957 | -0.027847 | -0.1682 | 0.087537 | 0.027847 | south | N | 0.027847 | 0
5935 | SI_RAY10 | 10 | 47 | -0.063504 | south | -0.20957 | -0.027847 | -0.1682 | 0.087537 | 0.027847 | south | N | 0.027847 | 0
6016 | SWMESA | 1 | 75 | 0.097677 | west | -0.048384 | 0.13333 | -0.0070167 | 0.24872 | 0.0070167 | west | N | 0.0070167 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | -0.14606 | 0.035657 | -0.10469 | 0.15104 | 0.035657 | south | Y | 0.10469 | 15.188
6144 | MCADOO1A | 1 | 150 | 0.10661 | west | -0.039454 | 0.14226 | 0.0019133 | 0.25765 | 0.0019133 | west | N | 0.0019133 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.10377 | west | -0.042295 | 0.13942 | -0.00092768 | 0.25481 | 0.00092768 | west | N | 0.00092768 | 0
6476 | LANGFORD | 1 | 150 | 0.074678 | west | -0.071383 | 0.11034 | -0.030016 | 0.22572 | 0.030016 | west | N | 0.030016 | 0
6637 | SNYDERW1 | 1 | 63 | 0.10579 | west | -0.040276 | 0.14144 | 0.0010913 | 0.25683 | 0.0010913 | west | N | 0.0010913 | 0
6752 | OKLA0A | 1 | 649.7 | 0.10983 | west | -0.036229 | 0.14549 | 0.0051383 | 0.26087 | 0.0051383 | west | N | 0.0051383 | 0
6948 | DENISNDM | 1 | 40 | 0.1196 | north | -0.026464 | 0.15525 | 0.014903 | 0.27064 | 0.014903 | west | Y | 0.026464 | 0.46244
6948 | DENISNDM | 2 | 40 | 0.1196 | north | -0.026464 | 0.15525 | 0.014903 | 0.27064 | 0.014903 | west | Y | 0.026464 | 0.46244
7000 | L_FERGUS | 1 | 422 | 0.001077 | south | -0.14498 | 0.036734 | -0.10362 | 0.15212 | 0.036734 | south | N | 0.036734 | 0
7004 | L_SIMGID | 1 | 132 | -0.013228 | south | -0.15929 | 0.022429 | -0.11792 | 0.13781 | 0.022429 | south | N | 0.022429 | 0
7005 | L_SIMGID | 2 | 134 | -0.013228 | south | -0.15929 | 0.022429 | -0.11792 | 0.13781 | 0.022429 | south | N | 0.022429 | 0
7006 | L_SIMGID | 3 | 323 | -0.013228 | south | -0.15929 | 0.022429 | -0.11792 | 0.13781 | 0.022429 | south | N | 0.022429 | 0
7007 | L_LOSTPI | 1 | 158 | -0.015275 | south | -0.16134 | 0.020382 | -0.11997 | 0.13577 | 0.020382 | south | N | 0.020382 | 0
7008 | L_LOSTPI | 2 | 160 | -0.015275 | south | -0.16134 | 0.020382 | -0.11997 | 0.13577 | 0.020382 | south | N | 0.020382 | 0
7009 | L_LOSTPI | 3 | 175 | -0.015275 | south | -0.16134 | 0.020382 | -0.11997 | 0.13577 | 0.020382 | south | N | 0.020382 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.032131 | south | -0.17819 | 0.0035262 | -0.13682 | 0.11891 | 0.0035262 | south | N | 0.0035262 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.032131 | south | -0.17819 | 0.0035262 | -0.13682 | 0.11891 | 0.0035262 | south | N | 0.0035262 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.032264 | south | -0.17833 | 0.0033932 | -0.13696 | 0.11878 | 0.0033932 | south | N | 0.0033932 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.030817 | south | -0.17688 | 0.0048402 | -0.13551 | 0.12022 | 0.0048402 | south | N | 0.0048402 | 0
7015 | L_HAYSEN | 2 | 225 | -0.030817 | south | -0.17688 | 0.0048402 | -0.13551 | 0.12022 | 0.0048402 | south | N | 0.0048402 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.030817 | south | -0.17688 | 0.0048402 | -0.13551 | 0.12022 | 0.0048402 | south | N | 0.0048402 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.030817 | south | -0.17688 | 0.0048402 | -0.13551 | 0.12022 | 0.0048402 | south | N | 0.0048402 | 0
7020 | L_AUSTPL | 1 | 8 | -0.004604 | south | -0.15067 | 0.031053 | -0.1093 | 0.14644 | 0.031053 | south | N | 0.031053 | 0
7020 | L_AUSTPL | 2 | 8 | -0.004604 | south | -0.15067 | 0.031053 | -0.1093 | 0.14644 | 0.031053 | south | N | 0.031053 | 0
7022 | L_BUCHAN | 1 | 18 | 0.009162 | south | -0.1369 | 0.044819 | -0.095532 | 0.1602 | 0.044819 | south | N | 0.044819 | 0
7023 | L_BUCHAN | 2 | 18 | 0.009162 | south | -0.1369 | 0.044819 | -0.095532 | 0.1602 | 0.044819 | south | N | 0.044819 | 0
7024 | L_BUCHAN | 3 | 15 | 0.009162 | south | -0.1369 | 0.044819 | -0.095532 | 0.1602 | 0.044819 | south | N | 0.044819 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.007727 | south | -0.13833 | 0.043384 | -0.096967 | 0.15877 | 0.043384 | south | N | 0.043384 | 0
7028 | L_MARBFA | 1 | 18 | -2.9e-05 | south | -0.14609 | 0.035628 | -0.10472 | 0.15101 | 0.035628 | south | N | 0.035628 | 0
7029 | L_MARBFA | 2 | 18 | -2.9e-05 | south | -0.14609 | 0.035628 | -0.10472 | 0.15101 | 0.035628 | south | N | 0.035628 | 0
7031 | L_MARSFO | 1 | 35 | -0.002538 | south | -0.1486 | 0.033119 | -0.10723 | 0.1485 | 0.033119 | south | N | 0.033119 | 0
7032 | L_MARSFO | 2 | 34 | -0.002538 | south | -0.1486 | 0.033119 | -0.10723 | 0.1485 | 0.033119 | south | N | 0.033119 | 0
7033 | L_MARSFO | 3 | 35 | -0.002538 | south | -0.1486 | 0.033119 | -0.10723 | 0.1485 | 0.033119 | south | N | 0.033119 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.001444 | south | -0.14462 | 0.037101 | -0.10325 | 0.15248 | 0.037101 | south | N | 0.037101 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.001444 | south | -0.14462 | 0.037101 | -0.10325 | 0.15248 | 0.037101 | south | N | 0.037101 | 0
7038 | L_DELAWA | 1 | 35 | 0.10367 | west | -0.042389 | 0.13933 | -0.0010217 | 0.25471 | 0.0010217 | west | N | 0.0010217 | 0
7038 | L_DELAWA | 2 | 30 | 0.10367 | west | -0.042389 | 0.13933 | -0.0010217 | 0.25471 | 0.0010217 | west | N | 0.0010217 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.02899 | south | -0.17505 | 0.0066672 | -0.13368 | 0.12205 | 0.0066672 | south | N | 0.0066672 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.02899 | south | -0.17505 | 0.0066672 | -0.13368 | 0.12205 | 0.0066672 | south | N | 0.0066672 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.02899 | south | -0.17505 | 0.0066672 | -0.13368 | 0.12205 | 0.0066672 | south | N | 0.0066672 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.02899 | south | -0.17505 | 0.0066672 | -0.13368 | 0.12205 | 0.0066672 | south | N | 0.0066672 | 0
7487 | L_CANYHY | 1 | 6 | -0.025314 | south | -0.17138 | 0.010343 | -0.13001 | 0.12573 | 0.010343 | south | N | 0.010343 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.034492 | south | -0.18055 | 0.0011652 | -0.13919 | 0.11655 | 0.0011652 | south | N | 0.0011652 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.034492 | south | -0.18055 | 0.0011652 | -0.13919 | 0.11655 | 0.0011652 | south | N | 0.0011652 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.034492 | south | -0.18055 | 0.0011652 | -0.13919 | 0.11655 | 0.0011652 | south | N | 0.0011652 | 0
7609 | L_SCHUMA | 1 | 4 | -0.035876 | south | -0.18194 | -0.00021883 | -0.14057 | 0.11516 | 0.00021883 | south | N | 0.00021883 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.036933 | south | -0.18299 | -0.0012758 | -0.14163 | 0.11411 | 0.0012758 | south | N | 0.0012758 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.036933 | south | -0.18299 | -0.0012758 | -0.14163 | 0.11411 | 0.0012758 | south | N | 0.0012758 | 0
7800 | L_GUADGE | 1 | 147 | -0.039635 | south | -0.1857 | -0.0039778 | -0.14433 | 0.11141 | 0.0039778 | south | N | 0.0039778 | 0
7801 | L_GUADGE | 2 | 138 | -0.039635 | south | -0.1857 | -0.0039778 | -0.14433 | 0.11141 | 0.0039778 | south | N | 0.0039778 | 0
7802 | L_GUADGE | 3 | 140 | -0.039635 | south | -0.1857 | -0.0039778 | -0.14433 | 0.11141 | 0.0039778 | south | N | 0.0039778 | 0
7803 | L_GUADGE | 4 | 147 | -0.039635 | south | -0.1857 | -0.0039778 | -0.14433 | 0.11141 | 0.0039778 | south | N | 0.0039778 | 0
7804 | L_GUADGE | 5 | 182 | -0.039635 | south | -0.1857 | -0.0039778 | -0.14433 | 0.11141 | 0.0039778 | south | N | 0.0039778 | 0
7805 | L_GUADGE | 6 | 198 | -0.039635 | south | -0.1857 | -0.0039778 | -0.14433 | 0.11141 | 0.0039778 | south | N | 0.0039778 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.012948 | south | -0.15901 | 0.022709 | -0.11764 | 0.13809 | 0.022709 | south | N | 0.022709 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.012948 | south | -0.15901 | 0.022709 | -0.11764 | 0.13809 | 0.022709 | south | N | 0.022709 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.012948 | south | -0.15901 | 0.022709 | -0.11764 | 0.13809 | 0.022709 | south | N | 0.022709 | 0
7810 | L_RIONOG | 1 | 142 | -0.03535 | south | -0.18141 | 0.00030717 | -0.14004 | 0.11569 | 0.00030717 | south | N | 0.00030717 | 0
7811 | L_RIONOG | 2 | 145 | -0.03535 | south | -0.18141 | 0.00030717 | -0.14004 | 0.11569 | 0.00030717 | south | N | 0.00030717 | 0
7812 | L_RIONOG | 3 | 151 | -0.03535 | south | -0.18141 | 0.00030717 | -0.14004 | 0.11569 | 0.00030717 | south | N | 0.00030717 | 0
7813 | L_RIONOG | 4 | 290 | -0.03535 | south | -0.18141 | 0.00030717 | -0.14004 | 0.11569 | 0.00030717 | south | N | 0.00030717 | 0
8032 | AMISTADH | 1 | 33 | -0.002962 | south | -0.14902 | 0.032695 | -0.10766 | 0.14808 | 0.032695 | south | N | 0.032695 | 0
8033 | AMISTADH | 2 | 25 | -0.002962 | south | -0.14902 | 0.032695 | -0.10766 | 0.14808 | 0.032695 | south | N | 0.032695 | 0
8048 | FALCONHY | 1 | 12 | -0.058225 | south | -0.20429 | -0.022568 | -0.16292 | 0.092816 | 0.022568 | south | N | 0.022568 | 0
8066 | DUP1V#1 | 1 | 73 | -0.068116 | south | -0.21418 | -0.032459 | -0.17281 | 0.082925 | 0.032459 | south | N | 0.032459 | 0
8134 | FOR69CG0 | 1 | 79 | -0.075898 | south | -0.22196 | -0.040241 | -0.18059 | 0.075143 | 0.040241 | south | N | 0.040241 | 0
8138 | FOR69CG0 | 2 | 81 | -0.075898 | south | -0.22196 | -0.040241 | -0.18059 | 0.075143 | 0.040241 | south | N | 0.040241 | 0
8139 | JOS #1 | MB | 255 | 0 | south | -0.14606 | 0.035657 | -0.10469 | 0.15104 | 0.035657 | south | N | 0.035657 | 0
8147 | UCAR #2 | 10 | 28 | -0.071643 | south | -0.2177 | -0.035986 | -0.17634 | 0.079398 | 0.035986 | south | N | 0.035986 | 0
8148 | UCAR #1 | 2 | 7 | -0.071643 | south | -0.2177 | -0.035986 | -0.17634 | 0.079398 | 0.035986 | south | N | 0.035986 | 0
8153 | FOR69CG0 | 3 | 79 | -0.075898 | south | -0.22196 | -0.040241 | -0.18059 | 0.075143 | 0.040241 | south | N | 0.040241 | 0
8154 | FOR69CG0 | 4 | 80 | -0.075898 | south | -0.22196 | -0.040241 | -0.18059 | 0.075143 | 0.040241 | south | N | 0.040241 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.075898 | south | -0.22196 | -0.040241 | -0.18059 | 0.075143 | 0.040241 | south | N | 0.040241 | 0
8156 | FOR69CG0 | 6 | 25 | -0.075898 | south | -0.22196 | -0.040241 | -0.18059 | 0.075143 | 0.040241 | south | N | 0.040241 | 0
8157 | FOR69CG0 | 7 | 46 | -0.075898 | south | -0.22196 | -0.040241 | -0.18059 | 0.075143 | 0.040241 | south | N | 0.040241 | 0
8161 | COLETOU1 | 1 | 629 | -0.060621 | south | -0.20668 | -0.024964 | -0.16531 | 0.09042 | 0.024964 | south | N | 0.024964 | 0
8173 | VICEC51A | 5 | 144 | -0.06681 | south | -0.21287 | -0.031153 | -0.1715 | 0.084231 | 0.031153 | south | N | 0.031153 | 0
8174 | VICEC61A | 6 | 188 | -0.06681 | south | -0.21287 | -0.031153 | -0.1715 | 0.084231 | 0.031153 | south | N | 0.031153 | 0
8189 | CUERO 2 | 1 | 12 | -0.045118 | south | -0.19118 | -0.0094608 | -0.14981 | 0.10592 | 0.0094608 | south | N | 0.0094608 | 0
8262 | ELPS | 1 | 6 | -0.015751 | south | -0.16181 | 0.019906 | -0.12044 | 0.13529 | 0.019906 | south | N | 0.019906 | 0
8285 | LAR #1 | MB | 32 | 0 | south | -0.14606 | 0.035657 | -0.10469 | 0.15104 | 0.035657 | south | N | 0.035657 | 0
8287 | LAR #2 | MB | 32 | 0 | south | -0.14606 | 0.035657 | -0.10469 | 0.15104 | 0.035657 | south | N | 0.035657 | 0
8288 | LAR #3 | MB | 105 | 0 | south | -0.14606 | 0.035657 | -0.10469 | 0.15104 | 0.035657 | south | N | 0.035657 | 0
8388 | BATES0A | MB | 70 | 0 | south | -0.14606 | 0.035657 | -0.10469 | 0.15104 | 0.035657 | south | N | 0.035657 | 0
8393 | BATES0B | MB | 110 | 0 | south | -0.14606 | 0.035657 | -0.10469 | 0.15104 | 0.035657 | south | N | 0.035657 | 0
8442 | NBEC71A | 1 | 336 | -0.06515 | south | -0.21121 | -0.029493 | -0.16984 | 0.085891 | 0.029493 | south | N | 0.029493 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | -0.14606 | 0.035657 | -0.10469 | 0.15104 | 0.035657 | south | N | 0.035657 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | -0.14606 | 0.035657 | -0.10469 | 0.15104 | 0.035657 | south | N | 0.035657 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.064854 | south | -0.21092 | -0.029197 | -0.16955 | 0.086187 | 0.029197 | south | N | 0.029197 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.064854 | south | -0.21092 | -0.029197 | -0.16955 | 0.086187 | 0.029197 | south | N | 0.029197 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.064636 | south | -0.2107 | -0.028979 | -0.16933 | 0.086405 | 0.028979 | south | N | 0.028979 | 0
8506 | VAL #1 | 1 | 25 | -0.064783 | south | -0.21084 | -0.029126 | -0.16948 | 0.086258 | 0.029126 | south | N | 0.029126 | 0
8507 | VAL #2 | 2 | 25 | -0.064783 | south | -0.21084 | -0.029126 | -0.16948 | 0.086258 | 0.029126 | south | N | 0.029126 | 0
8511 | OXY_CC0A | 1 | 38 | -0.064675 | south | -0.21074 | -0.029018 | -0.16937 | 0.086366 | 0.029018 | south | N | 0.029018 | 0
8517 | CELANEBI | 1 | 29 | -0.06399 | south | -0.21005 | -0.028333 | -0.16868 | 0.087051 | 0.028333 | south | N | 0.028333 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.065134 | south | -0.2112 | -0.029477 | -0.16983 | 0.085907 | 0.029477 | south | N | 0.029477 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.065134 | south | -0.2112 | -0.029477 | -0.16983 | 0.085907 | 0.029477 | south | N | 0.029477 | 0
8562 | CNOPST1 | 3 | 153 | -0.065134 | south | -0.2112 | -0.029477 | -0.16983 | 0.085907 | 0.029477 | south | N | 0.029477 | 0
8926 | LGE_GT10 | 1 | 158 | -0.066515 | south | -0.21258 | -0.030858 | -0.17121 | 0.084526 | 0.030858 | south | N | 0.030858 | 0
8927 | LGE_GT20 | 2 | 153 | -0.066515 | south | -0.21258 | -0.030858 | -0.17121 | 0.084526 | 0.030858 | south | N | 0.030858 | 0
8928 | LGE_STG0 | 3 | 100 | -0.066515 | south | -0.21258 | -0.030858 | -0.17121 | 0.084526 | 0.030858 | south | N | 0.030858 | 0
8930 | ICPGN10A | 1 | 145 | -0.066515 | south | -0.21258 | -0.030858 | -0.17121 | 0.084526 | 0.030858 | south | N | 0.030858 | 0
8931 | ICPGN20A | 2 | 147 | -0.066515 | south | -0.21258 | -0.030858 | -0.17121 | 0.084526 | 0.030858 | south | N | 0.030858 | 0
8932 | ICPGN30A | 3 | 127 | -0.066515 | south | -0.21258 | -0.030858 | -0.17121 | 0.084526 | 0.030858 | south | N | 0.030858 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.06234 | south | -0.2084 | -0.026683 | -0.16703 | 0.088701 | 0.026683 | south | N | 0.026683 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.06234 | south | -0.2084 | -0.026683 | -0.16703 | 0.088701 | 0.026683 | south | N | 0.026683 | 0
8935 | FGNTS201 | 3 | 173 | -0.06234 | south | -0.2084 | -0.026683 | -0.16703 | 0.088701 | 0.026683 | south | N | 0.026683 | 0
8936 | MVGN#1 | 1 | 207 | -0.063016 | south | -0.20908 | -0.027359 | -0.16771 | 0.088025 | 0.027359 | south | N | 0.027359 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.063016 | south | -0.20908 | -0.027359 | -0.16771 | 0.088025 | 0.027359 | south | N | 0.027359 | 0
8938 | MVGN#3 | 3 | 242 | -0.063016 | south | -0.20908 | -0.027359 | -0.16771 | 0.088025 | 0.027359 | south | N | 0.027359 | 0
8981 | HECN1 | 1 | 144 | -0.063021 | south | -0.20908 | -0.027364 | -0.16771 | 0.08802 | 0.027364 | south | N | 0.027364 | 0
8982 | HECN2 | 2 | 144 | -0.063021 | south | -0.20908 | -0.027364 | -0.16771 | 0.08802 | 0.027364 | south | N | 0.027364 | 0
8983 | HECN3 | 3 | 171 | -0.063021 | south | -0.20908 | -0.027364 | -0.16771 | 0.08802 | 0.027364 | south | N | 0.027364 | 0
9000 | DECKR_G1 | 1 | 310 | -0.00473 | south | -0.15079 | 0.030927 | -0.10942 | 0.14631 | 0.030927 | south | N | 0.030927 | 0
9001 | DECKR_G2 | 2 | 413 | -0.00473 | south | -0.15079 | 0.030927 | -0.10942 | 0.14631 | 0.030927 | south | N | 0.030927 | 0
9002 | DECKR_G3 | 3 | 42 | -0.003457 | south | -0.14952 | 0.0322 | -0.10815 | 0.14758 | 0.0322 | south | N | 0.0322 | 0
9003 | DECKR_G4 | 4 | 44 | -0.003457 | south | -0.14952 | 0.0322 | -0.10815 | 0.14758 | 0.0322 | south | N | 0.0322 | 0
9004 | DECKR_G5 | 5 | 44 | -0.003457 | south | -0.14952 | 0.0322 | -0.10815 | 0.14758 | 0.0322 | south | N | 0.0322 | 0
9005 | DECKR_G6 | 6 | 47 | -0.003457 | south | -0.14952 | 0.0322 | -0.10815 | 0.14758 | 0.0322 | south | N | 0.0322 | 0
9016 | SANDH_G1 | 1 | 49 | -0.006685 | south | -0.15275 | 0.028972 | -0.11138 | 0.14436 | 0.028972 | south | N | 0.028972 | 0
9017 | SANDH_G2 | 2 | 46 | -0.006685 | south | -0.15275 | 0.028972 | -0.11138 | 0.14436 | 0.028972 | south | N | 0.028972 | 0
9018 | SANDH_G3 | 3 | 46 | -0.006685 | south | -0.15275 | 0.028972 | -0.11138 | 0.14436 | 0.028972 | south | N | 0.028972 | 0
9019 | SANDH_G4 | 4 | 47 | -0.006685 | south | -0.15275 | 0.028972 | -0.11138 | 0.14436 | 0.028972 | south | N | 0.028972 | 0
9020 | SANDHG5A | 5A | 154 | -0.006685 | south | -0.15275 | 0.028972 | -0.11138 | 0.14436 | 0.028972 | south | N | 0.028972 | 0
9021 | SANDHG5C | 5C | 148 | -0.006685 | south | -0.15275 | 0.028972 | -0.11138 | 0.14436 | 0.028972 | south | N | 0.028972 | 0
9022 | SANDH_G6 | 6 | 48 | -0.006685 | south | -0.15275 | 0.028972 | -0.11138 | 0.14436 | 0.028972 | south | N | 0.028972 | 0
9023 | SANDH_G7 | 7 | 48 | -0.006685 | south | -0.15275 | 0.028972 | -0.11138 | 0.14436 | 0.028972 | south | N | 0.028972 | 0
11001 | NAV1CT | 1 | 70 | 0.10469 | west | -0.041371 | 0.14035 | -3.6842e-06 | 0.25573 | 3.6842e-06 | west | N | 3.6842e-06 | 0
11009 | NAV2CT | 1 | 70 | 0.10469 | west | -0.041371 | 0.14035 | -3.6842e-06 | 0.25573 | 3.6842e-06 | west | N | 3.6842e-06 | 0
11011 | NAV3ST | 1 | 92.8 | 0.10469 | west | -0.041371 | 0.14035 | -3.6842e-06 | 0.25573 | 3.6842e-06 | west | N | 3.6842e-06 | 0
11012 | NAV4CT | 1 | 80 | 0.10469 | west | -0.041371 | 0.14035 | -3.6842e-06 | 0.25573 | 3.6842e-06 | west | N | 3.6842e-06 | 0
11013 | NAV5CT | 1 | 80 | 0.10469 | west | -0.041371 | 0.14035 | -3.6842e-06 | 0.25573 | 3.6842e-06 | west | N | 3.6842e-06 | 0
11014 | NAV6ST | 1 | 115 | 0.10469 | west | -0.041371 | 0.14035 | -3.6842e-06 | 0.25573 | 3.6842e-06 | west | N | 3.6842e-06 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.10468 | west | -0.041381 | 0.14034 | -1.3684e-05 | 0.25572 | 1.3684e-05 | west | N | 1.3684e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.10468 | west | -0.041381 | 0.14034 | -1.3684e-05 | 0.25572 | 1.3684e-05 | west | N | 1.3684e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.10468 | west | -0.041381 | 0.14034 | -1.3684e-05 | 0.25572 | 1.3684e-05 | west | N | 1.3684e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.10468 | west | -0.041381 | 0.14034 | -1.3684e-05 | 0.25572 | 1.3684e-05 | west | N | 1.3684e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.10468 | west | -0.041381 | 0.14034 | -1.3684e-05 | 0.25572 | 1.3684e-05 | west | N | 1.3684e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.10468 | west | -0.041381 | 0.14034 | -1.3684e-05 | 0.25572 | 1.3684e-05 | west | N | 1.3684e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.10658 | west | -0.039476 | 0.14224 | 0.0018913 | 0.25763 | 0.0018913 | west | N | 0.0018913 | 0
11057 | CHAMPION | 1 | 126.5 | 0.10658 | west | -0.039476 | 0.14224 | 0.0018913 | 0.25763 | 0.0018913 | west | N | 0.0018913 | 0
11058 | PYRON_1G | 1 | 249 | 0.10658 | west | -0.039476 | 0.14224 | 0.0018913 | 0.25763 | 0.0018913 | west | N | 0.0018913 | 0
11059 | INADALE_ | 1 | 197 | 0.10658 | west | -0.039476 | 0.14224 | 0.0018913 | 0.25763 | 0.0018913 | west | N | 0.0018913 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.10562 | west | -0.040442 | 0.14128 | 0.00092532 | 0.25666 | 0.00092532 | west | N | 0.00092532 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.10562 | west | -0.040442 | 0.14128 | 0.00092532 | 0.25666 | 0.00092532 | west | N | 0.00092532 | 0
11147 | NOTREES_ | 1 | 149 | 0.10385 | west | -0.042208 | 0.13951 | -0.00084068 | 0.25489 | 0.00084068 | west | N | 0.00084068 | 0
11309 | BULLCREK | 1 | 180 | 0.10544 | west | -0.040624 | 0.14109 | 0.00074332 | 0.25648 | 0.00074332 | west | N | 0.00074332 | 0
11310 | BULLCREK | 1 | 180 | 0.10544 | west | -0.040624 | 0.14109 | 0.00074332 | 0.25648 | 0.00074332 | west | N | 0.00074332 | 0
11320 | COYOTE_1 | 1 | 225 | 0.10538 | west | -0.040679 | 0.14104 | 0.00068832 | 0.25642 | 0.00068832 | west | N | 0.00068832 | 0
11415 | LORAINE_ | 1 | 125 | 0.10619 | west | -0.039876 | 0.14184 | 0.0014913 | 0.25723 | 0.0014913 | west | N | 0.0014913 | 0
11416 | LORAINE_ | 1 | 125 | 0.10619 | west | -0.039876 | 0.14184 | 0.0014913 | 0.25723 | 0.0014913 | west | N | 0.0014913 | 0
11691 | KMICHICT | 1 | 140 | 0.12003 | north | -0.02603 | 0.15569 | 0.015337 | 0.27107 | 0.015337 | west | Y | 0.02603 | 1.497
11692 | KMICHICT | 2 | 141 | 0.12003 | north | -0.02603 | 0.15569 | 0.015337 | 0.27107 | 0.015337 | west | Y | 0.02603 | 1.5077
11693 | KMICHIST | 3 | 309 | 0.12003 | north | -0.02603 | 0.15569 | 0.015337 | 0.27107 | 0.015337 | west | Y | 0.02603 | 3.3042
11694 | KMICHICT | 4 | 143 | 0.12003 | north | -0.02603 | 0.15569 | 0.015337 | 0.27107 | 0.015337 | west | Y | 0.02603 | 1.5291
11695 | KMICHICT | 5 | 144 | 0.12003 | north | -0.02603 | 0.15569 | 0.015337 | 0.27107 | 0.015337 | west | Y | 0.02603 | 1.5398
11696 | KMICHIST | 6 | 310 | 0.12003 | north | -0.02603 | 0.15569 | 0.015337 | 0.27107 | 0.015337 | west | Y | 0.02603 | 3.3149
12322 | ENNSTRAC | 1 | 196 | 0.11882 | north | -0.027237 | 0.15448 | 0.01413 | 0.26986 | 0.01413 | west | Y | 0.027237 | 2.569
12323 | ENNSTRAC | 2 | 111 | 0.11882 | north | -0.027237 | 0.15448 | 0.01413 | 0.26986 | 0.01413 | west | Y | 0.027237 | 1.4549
12357 | RNRTPL_1 | 1 | 0 | 0.11939 | north | -0.026673 | 0.15505 | 0.014694 | 0.27043 | 0.014694 | west | Y | 0.026673 | 0
12411 | FPLEFR1A | 1 | 161 | 0.1216 | north | -0.024465 | 0.15725 | 0.016902 | 0.27264 | 0.016902 | west | Y | 0.024465 | 1.2177
12412 | FPLEFR1B | 2 | 164 | 0.1216 | north | -0.024465 | 0.15725 | 0.016902 | 0.27264 | 0.016902 | west | Y | 0.024465 | 1.2404
12413 | FPLEFR1C | 3 | 164 | 0.1216 | north | -0.024465 | 0.15725 | 0.016902 | 0.27264 | 0.016902 | west | Y | 0.024465 | 1.2404
12414 | FPLEFR1S | 4 | 414 | 0.1216 | north | -0.024465 | 0.15725 | 0.016902 | 0.27264 | 0.016902 | west | Y | 0.024465 | 3.1311
12421 | FPLEFR2A | 1 | 162 | 0.1216 | north | -0.024465 | 0.15725 | 0.016902 | 0.27264 | 0.016902 | west | Y | 0.024465 | 1.2252
12422 | FPLEFR2B | 2 | 161 | 0.1216 | north | -0.024465 | 0.15725 | 0.016902 | 0.27264 | 0.016902 | west | Y | 0.024465 | 1.2177
12423 | FPLEFR2C | 3 | 163 | 0.1216 | north | -0.024465 | 0.15725 | 0.016902 | 0.27264 | 0.016902 | west | Y | 0.024465 | 1.2328
12424 | FPLEFR2S | 4 | 409 | 0.1216 | north | -0.024465 | 0.15725 | 0.016902 | 0.27264 | 0.016902 | west | Y | 0.024465 | 3.0933
12440 | PARKD_1S | 1 | 0 | 0.12091 | north | -0.025146 | 0.15657 | 0.016221 | 0.27196 | 0.016221 | west | Y | 0.025146 | 0
12449 | PARKD_2S | 1 | 0 | 0.12091 | north | -0.025146 | 0.15657 | 0.016221 | 0.27196 | 0.016221 | west | Y | 0.025146 | 0
13116 | TGATEWAY | 1 | 148 | 0.12346 | north | -0.022604 | 0.15911 | 0.018763 | 0.2745 | 0.018763 | west | Y | 0.022604 | 0.56849
13117 | TGATEWAY | 2 | 130 | 0.12346 | north | -0.022604 | 0.15911 | 0.018763 | 0.2745 | 0.018763 | west | Y | 0.022604 | 0.49935
13118 | TGATEWAY | 3 | 145 | 0.12346 | north | -0.022604 | 0.15911 | 0.018763 | 0.2745 | 0.018763 | west | Y | 0.022604 | 0.55696
13119 | TGATEWAY | 4 | 399 | 0.12346 | north | -0.022604 | 0.15911 | 0.018763 | 0.2745 | 0.018763 | west | Y | 0.022604 | 1.5326
13131 | CALFREST | 1 | 150.7 | 0.12301 | north | -0.023051 | 0.15867 | 0.018316 | 0.27405 | 0.018316 | west | Y | 0.023051 | 0.71358
13132 | CALFREST | 2 | 151 | 0.12301 | north | -0.023051 | 0.15867 | 0.018316 | 0.27405 | 0.018316 | west | Y | 0.023051 | 0.715
13133 | CALFREST | 3 | 177.4 | 0.12301 | north | -0.023051 | 0.15867 | 0.018316 | 0.27405 | 0.018316 | west | Y | 0.023051 | 0.84001
13134 | CALFREST | 4 | 151.5 | 0.12288 | north | -0.023176 | 0.15854 | 0.018191 | 0.27393 | 0.018191 | west | Y | 0.023176 | 0.75525
13135 | CALFREST | 5 | 152.3 | 0.12288 | north | -0.023176 | 0.15854 | 0.018191 | 0.27393 | 0.018191 | west | Y | 0.023176 | 0.75923
13136 | CALFREST | 6 | 177.5 | 0.12288 | north | -0.023176 | 0.15854 | 0.018191 | 0.27393 | 0.018191 | west | Y | 0.023176 | 0.88486
13432 | SANDOW_5 | 5 | 581 | 0.038449 | south | -0.10761 | 0.074106 | -0.066245 | 0.18949 | 0.066245 | west | Y | 0.074106 | 4.5675
13691 | OAKGROVE | 1 | 855 | 0.29529 | north | 0.14922 | 0.33094 | 0.19059 | 0.44633 | 0.14922 | North | N | 0.14922 | 0
13692 | OAKGROVE | 2 | 855 | 0.29529 | north | 0.14922 | 0.33094 | 0.19059 | 0.44633 | 0.14922 | North | N | 0.14922 | 0
32798 | BRYN_TAM | 1 | 32 | 0.54391 | north | 0.39785 | 0.57957 | 0.43922 | 0.69495 | 0.39785 | North | N | 0.39785 | 0
32883 | BRYN_DNS | 1 | 48 | 0.51456 | north | 0.3685 | 0.55022 | 0.40987 | 0.6656 | 0.3685 | North | N | 0.3685 | 0
32884 | BRYN_DNS | 1 | 46 | 0.51456 | north | 0.3685 | 0.55022 | 0.40987 | 0.6656 | 0.3685 | North | N | 0.3685 | 0
32886 | BRYN_ATK | MB | 12 | 0.54 | north | 0.39394 | 0.57566 | 0.43531 | 0.69104 | 0.39394 | North | N | 0.39394 | 0
32887 | BRYN_ATK | MB | 51 | 0.54 | north | 0.39394 | 0.57566 | 0.43531 | 0.69104 | 0.39394 | North | N | 0.39394 | 0
32888 | BRYN_ATK | 1 | 17 | 0.54 | north | 0.39394 | 0.57566 | 0.43531 | 0.69104 | 0.39394 | North | N | 0.39394 | 0
32890 | BRYN_ATK | MB | 22 | 0.54 | north | 0.39394 | 0.57566 | 0.43531 | 0.69104 | 0.39394 | North | N | 0.39394 | 0
32891 | BRYN_ATK | MB | 25 | 0.54 | north | 0.39394 | 0.57566 | 0.43531 | 0.69104 | 0.39394 | North | N | 0.39394 | 0
32892 | BRYN_DNS | 1 | 105 | 0.51456 | north | 0.3685 | 0.55022 | 0.40987 | 0.6656 | 0.3685 | North | N | 0.3685 | 0
36998 | RDCNYNG1 | 1 | 84 | 0.10599 | west | -0.040074 | 0.14164 | 0.0012933 | 0.25703 | 0.0012933 | west | N | 0.0012933 | 0
38332 | WDWRDU2 | 1 | 80 | 0.09757 | west | -0.048491 | 0.13323 | -0.0071237 | 0.24861 | 0.0071237 | west | N | 0.0071237 | 0
38437 | TNSRBNMS | 1 | 150 | 0.097515 | west | -0.048546 | 0.13317 | -0.0071787 | 0.24856 | 0.0071787 | west | N | 0.0071787 | 0
38438 | TNSRBNMS | 1 | 150 | 0.097515 | west | -0.048546 | 0.13317 | -0.0071787 | 0.24856 | 0.0071787 | west | N | 0.0071787 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.1494 | houston | -0.29547 | -0.11375 | -0.2541 | 0.0016368 | 0.0016368 | houston | N | 0.0016368 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.1494 | houston | -0.29547 | -0.11375 | -0.2541 | 0.0016368 | 0.0016368 | houston | N | 0.0016368 | 0
38600 | TNBP_CGN | 5 | 53 | -0.1494 | houston | -0.29547 | -0.11375 | -0.2541 | 0.0016368 | 0.0016368 | houston | N | 0.0016368 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.1494 | houston | -0.29547 | -0.11375 | -0.2541 | 0.0016368 | 0.0016368 | houston | N | 0.0016368 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.1494 | houston | -0.29547 | -0.11375 | -0.2541 | 0.0016368 | 0.0016368 | houston | N | 0.0016368 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.1494 | houston | -0.29547 | -0.11375 | -0.2541 | 0.0016368 | 0.0016368 | houston | N | 0.0016368 | 0
38614 | TNBPAMCG | 4 | 96 | -0.1494 | houston | -0.29547 | -0.11375 | -0.2541 | 0.0016368 | 0.0016368 | houston | N | 0.0016368 | 0
38615 | TNBPAMCG | 1 | 244 | -0.1494 | houston | -0.29547 | -0.11375 | -0.2541 | 0.0016368 | 0.0016368 | houston | N | 0.0016368 | 0
38690 | TNBP_CGN | 3 | 40 | -0.1494 | houston | -0.29547 | -0.11375 | -0.2541 | 0.0016368 | 0.0016368 | houston | N | 0.0016368 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.14938 | houston | -0.29544 | -0.11372 | -0.25407 | 0.0016608 | 0.0016608 | houston | N | 0.0016608 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.14938 | houston | -0.29544 | -0.11372 | -0.25407 | 0.0016608 | 0.0016608 | houston | N | 0.0016608 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.14938 | houston | -0.29544 | -0.11372 | -0.25407 | 0.0016608 | 0.0016608 | houston | N | 0.0016608 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.14938 | houston | -0.29544 | -0.11372 | -0.25407 | 0.0016608 | 0.0016608 | houston | N | 0.0016608 | 0
39470 | TNDOWCGN | 1 | 32 | -0.14938 | houston | -0.29544 | -0.11372 | -0.25407 | 0.0016598 | 0.0016598 | houston | N | 0.0016598 | 0
39480 | TNDOWCGN | 1 | 30 | -0.14938 | houston | -0.29544 | -0.11372 | -0.25407 | 0.0016598 | 0.0016598 | houston | N | 0.0016598 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.13419 | houston | -0.28025 | -0.09853 | -0.23888 | 0.016854 | 0.016854 | houston | N | 0.016854 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.13419 | houston | -0.28025 | -0.09853 | -0.23888 | 0.016854 | 0.016854 | houston | N | 0.016854 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.13419 | houston | -0.28025 | -0.09853 | -0.23888 | 0.016854 | 0.016854 | houston | N | 0.016854 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.13419 | houston | -0.28025 | -0.09853 | -0.23888 | 0.016854 | 0.016854 | houston | N | 0.016854 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.29529 | north | 0.14922 | 0.33094 | 0.19059 | 0.44633 | 0.14922 | North | N | 0.14922 | 0
39970 | TNTNPONE | 1 | 153 | 0.29529 | north | 0.14922 | 0.33094 | 0.19059 | 0.44633 | 0.14922 | North | N | 0.14922 | 0
48500 | APD_GT1_ | 1 | 136 | -0.15864 | houston | -0.30471 | -0.12299 | -0.26334 | -0.0076032 | 0.0076032 | houston | N | 0.0076032 | 0
48510 | AK_GT1__ | 1 | 33 | -0.14434 | houston | -0.2904 | -0.10868 | -0.24903 | 0.0067048 | 0.0067048 | houston | N | 0.0067048 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.15869 | houston | -0.30475 | -0.12303 | -0.26338 | -0.0076492 | 0.0076492 | houston | N | 0.0076492 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.15869 | houston | -0.30475 | -0.12303 | -0.26338 | -0.0076492 | 0.0076492 | houston | N | 0.0076492 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.15869 | houston | -0.30475 | -0.12303 | -0.26338 | -0.0076492 | 0.0076492 | houston | N | 0.0076492 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.15869 | houston | -0.30475 | -0.12303 | -0.26338 | -0.0076492 | 0.0076492 | houston | N | 0.0076492 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.13172 | houston | -0.27778 | -0.096063 | -0.23641 | 0.019321 | 0.019321 | houston | N | 0.019321 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.13172 | houston | -0.27778 | -0.096063 | -0.23641 | 0.019321 | 0.019321 | houston | N | 0.019321 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.14347 | houston | -0.28953 | -0.10781 | -0.24816 | 0.0075738 | 0.0075738 | houston | N | 0.0075738 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.14347 | houston | -0.28953 | -0.10781 | -0.24816 | 0.0075738 | 0.0075738 | houston | N | 0.0075738 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.14347 | houston | -0.28953 | -0.10781 | -0.24816 | 0.0075738 | 0.0075738 | houston | N | 0.0075738 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.15519 | houston | -0.30125 | -0.11953 | -0.25988 | -0.0041492 | 0.0041492 | houston | N | 0.0041492 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.15519 | houston | -0.30125 | -0.11953 | -0.25988 | -0.0041492 | 0.0041492 | houston | N | 0.0041492 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.15519 | houston | -0.30125 | -0.11953 | -0.25988 | -0.0041492 | 0.0041492 | houston | N | 0.0041492 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.15519 | houston | -0.30125 | -0.11953 | -0.25988 | -0.0041492 | 0.0041492 | houston | N | 0.0041492 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.15744 | houston | -0.3035 | -0.12178 | -0.26213 | -0.0063982 | 0.0063982 | houston | N | 0.0063982 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.15744 | houston | -0.3035 | -0.12178 | -0.26213 | -0.0063982 | 0.0063982 | houston | N | 0.0063982 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.15451 | houston | -0.30057 | -0.11886 | -0.25921 | -0.0034722 | 0.0034722 | houston | N | 0.0034722 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.15451 | houston | -0.30057 | -0.11886 | -0.25921 | -0.0034722 | 0.0034722 | houston | N | 0.0034722 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.15451 | houston | -0.30057 | -0.11886 | -0.25921 | -0.0034722 | 0.0034722 | houston | N | 0.0034722 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.15451 | houston | -0.30057 | -0.11886 | -0.25921 | -0.0034722 | 0.0034722 | houston | N | 0.0034722 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.15451 | houston | -0.30057 | -0.11886 | -0.25921 | -0.0034722 | 0.0034722 | houston | N | 0.0034722 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.16151 | houston | -0.30757 | -0.12585 | -0.2662 | -0.010465 | 0.010465 | houston | N | 0.010465 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.16036 | houston | -0.30642 | -0.12471 | -0.26506 | -0.0093222 | 0.0093222 | houston | N | 0.0093222 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.16185 | houston | -0.30791 | -0.12619 | -0.26654 | -0.010809 | 0.010809 | houston | N | 0.010809 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.16185 | houston | -0.30791 | -0.12619 | -0.26654 | -0.010809 | 0.010809 | houston | N | 0.010809 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.16185 | houston | -0.30791 | -0.12619 | -0.26654 | -0.010809 | 0.010809 | houston | N | 0.010809 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.1682 | houston | -0.31426 | -0.13254 | -0.27289 | -0.017154 | 0.017154 | houston | N | 0.017154 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.15887 | houston | -0.30493 | -0.12321 | -0.26356 | -0.0078292 | 0.0078292 | houston | N | 0.0078292 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.15887 | houston | -0.30493 | -0.12321 | -0.26356 | -0.0078292 | 0.0078292 | houston | N | 0.0078292 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.16266 | houston | -0.30872 | -0.127 | -0.26735 | -0.011617 | 0.011617 | houston | N | 0.011617 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.16266 | houston | -0.30872 | -0.127 | -0.26735 | -0.011617 | 0.011617 | houston | N | 0.011617 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.16266 | houston | -0.30872 | -0.127 | -0.26735 | -0.011617 | 0.011617 | houston | N | 0.011617 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.16266 | houston | -0.30872 | -0.127 | -0.26735 | -0.011617 | 0.011617 | houston | N | 0.011617 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.15751 | houston | -0.30358 | -0.12186 | -0.26221 | -0.0064732 | 0.0064732 | houston | N | 0.0064732 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.15751 | houston | -0.30358 | -0.12186 | -0.26221 | -0.0064732 | 0.0064732 | houston | N | 0.0064732 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.15751 | houston | -0.30358 | -0.12186 | -0.26221 | -0.0064732 | 0.0064732 | houston | N | 0.0064732 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.15751 | houston | -0.30358 | -0.12186 | -0.26221 | -0.0064732 | 0.0064732 | houston | N | 0.0064732 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.15679 | houston | -0.30285 | -0.12113 | -0.26148 | -0.0057482 | 0.0057482 | houston | N | 0.0057482 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.15679 | houston | -0.30285 | -0.12113 | -0.26148 | -0.0057482 | 0.0057482 | houston | N | 0.0057482 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.15679 | houston | -0.30285 | -0.12113 | -0.26148 | -0.0057482 | 0.0057482 | houston | N | 0.0057482 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.15679 | houston | -0.30285 | -0.12113 | -0.26148 | -0.0057482 | 0.0057482 | houston | N | 0.0057482 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.15679 | houston | -0.30285 | -0.12113 | -0.26148 | -0.0057482 | 0.0057482 | houston | N | 0.0057482 | 0
48651 | EP_1_2 | 1 | 5 | -0.16145 | houston | -0.30751 | -0.12579 | -0.26614 | -0.010407 | 0.010407 | houston | N | 0.010407 | 0
48651 | EP_1_2 | 2 | 21 | -0.16145 | houston | -0.30751 | -0.12579 | -0.26614 | -0.010407 | 0.010407 | houston | N | 0.010407 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.2128 | north | -0.35887 | -0.17715 | -0.3175 | -0.061763 | 0.061763 | houston | Y | 0.35887 | 45.8132
48672 | FTR_GT2_ | 2 | 156 | -0.2128 | north | -0.35887 | -0.17715 | -0.3175 | -0.061763 | 0.061763 | houston | Y | 0.35887 | 46.3479
48673 | FTR_GT3_ | 3 | 156 | -0.2128 | north | -0.35887 | -0.17715 | -0.3175 | -0.061763 | 0.061763 | houston | Y | 0.35887 | 46.3479
48674 | FTR_CN4_ | 4 | 380 | -0.2128 | north | -0.35887 | -0.17715 | -0.3175 | -0.061763 | 0.061763 | houston | Y | 0.35887 | 112.8988
48690 | GBY_GN5_ | 5 | 398 | -0.16295 | houston | -0.30901 | -0.12729 | -0.26764 | -0.011904 | 0.011904 | houston | N | 0.011904 | 0
48691 | GBY_7374 | A | 46 | -0.15621 | houston | -0.30228 | -0.12056 | -0.26091 | -0.0051732 | 0.0051732 | houston | N | 0.0051732 | 0
48691 | GBY_7374 | B | 46 | -0.15621 | houston | -0.30228 | -0.12056 | -0.26091 | -0.0051732 | 0.0051732 | houston | N | 0.0051732 | 0
48692 | GBY_8182 | C | 46 | -0.15621 | houston | -0.30228 | -0.12056 | -0.26091 | -0.0051732 | 0.0051732 | houston | N | 0.0051732 | 0
48692 | GBY_8182 | D | 55 | -0.15621 | houston | -0.30228 | -0.12056 | -0.26091 | -0.0051732 | 0.0051732 | houston | N | 0.0051732 | 0
48693 | GBY_8384 | E | 55 | -0.15621 | houston | -0.30228 | -0.12056 | -0.26091 | -0.0051732 | 0.0051732 | houston | N | 0.0051732 | 0
48693 | GBY_8384 | F | 54 | -0.15621 | houston | -0.30228 | -0.12056 | -0.26091 | -0.0051732 | 0.0051732 | houston | N | 0.0051732 | 0
48721 | LEG_1___ | 1 | 827 | 0.17439 | north | 0.028329 | 0.21005 | 0.069696 | 0.32543 | 0.028329 | North | N | 0.028329 | 0
48722 | LEG_2___ | 2 | 819 | 0.17439 | north | 0.028329 | 0.21005 | 0.069696 | 0.32543 | 0.028329 | North | N | 0.028329 | 0
48730 | MNS_GT | 1 | 46.1 | -0.14302 | houston | -0.28908 | -0.10736 | -0.24771 | 0.0080238 | 0.0080238 | houston | N | 0.0080238 | 0
48731 | CBE_GT1 | 1 | 76 | -0.11194 | houston | -0.258 | -0.076283 | -0.21663 | 0.039101 | 0.039101 | houston | N | 0.039101 | 0
48732 | CBE_GT2 | 1 | 76 | -0.11194 | houston | -0.258 | -0.076283 | -0.21663 | 0.039101 | 0.039101 | houston | N | 0.039101 | 0
48733 | CBE_ST12 | 1 | 105 | -0.11194 | houston | -0.258 | -0.076283 | -0.21663 | 0.039101 | 0.039101 | houston | N | 0.039101 | 0
48734 | CBE_GT3 | 1 | 74 | -0.11194 | houston | -0.258 | -0.076283 | -0.21663 | 0.039101 | 0.039101 | houston | N | 0.039101 | 0
48735 | CBE_GT4 | 1 | 74 | -0.11194 | houston | -0.258 | -0.076283 | -0.21663 | 0.039101 | 0.039101 | houston | N | 0.039101 | 0
48736 | CBE_ST34 | 1 | 102 | -0.11194 | houston | -0.258 | -0.076283 | -0.21663 | 0.039101 | 0.039101 | houston | N | 0.039101 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.15754 | houston | -0.3036 | -0.12188 | -0.26223 | -0.0064952 | 0.0064952 | houston | N | 0.0064952 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.15754 | houston | -0.3036 | -0.12188 | -0.26223 | -0.0064952 | 0.0064952 | houston | N | 0.0064952 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.15754 | houston | -0.3036 | -0.12188 | -0.26223 | -0.0064952 | 0.0064952 | houston | N | 0.0064952 | 0
48761 | PR_GT1__ | 1 | 35 | -0.15708 | houston | -0.30314 | -0.12142 | -0.26177 | -0.0060382 | 0.0060382 | houston | N | 0.0060382 | 0
48772 | PHR_GN2_ | MB | 459 | -0.15278 | houston | -0.29885 | -0.11713 | -0.25748 | -0.0017432 | 0.0017432 | houston | N | 0.0017432 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.16146 | houston | -0.30752 | -0.1258 | -0.26615 | -0.010417 | 0.010417 | houston | N | 0.010417 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.16146 | houston | -0.30752 | -0.1258 | -0.26615 | -0.010417 | 0.010417 | houston | N | 0.010417 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.16146 | houston | -0.30752 | -0.1258 | -0.26615 | -0.010417 | 0.010417 | houston | N | 0.010417 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.16146 | houston | -0.30752 | -0.1258 | -0.26615 | -0.010417 | 0.010417 | houston | N | 0.010417 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.16146 | houston | -0.30752 | -0.1258 | -0.26615 | -0.010417 | 0.010417 | houston | N | 0.010417 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.16146 | houston | -0.30752 | -0.1258 | -0.26615 | -0.010417 | 0.010417 | houston | N | 0.010417 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.16146 | houston | -0.30752 | -0.1258 | -0.26615 | -0.010417 | 0.010417 | houston | N | 0.010417 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.1682 | houston | -0.31426 | -0.13254 | -0.27289 | -0.017154 | 0.017154 | houston | N | 0.017154 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.1682 | houston | -0.31426 | -0.13254 | -0.27289 | -0.017154 | 0.017154 | houston | N | 0.017154 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.1682 | houston | -0.31426 | -0.13254 | -0.27289 | -0.017154 | 0.017154 | houston | N | 0.017154 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.1682 | houston | -0.31426 | -0.13254 | -0.27289 | -0.017154 | 0.017154 | houston | N | 0.017154 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.16172 | houston | -0.30778 | -0.12606 | -0.26641 | -0.010679 | 0.010679 | houston | N | 0.010679 | 0
48820 | SHELLG1_ | 1 | 71 | -0.15796 | houston | -0.30402 | -0.1223 | -0.26265 | -0.0069202 | 0.0069202 | houston | N | 0.0069202 | 0
48821 | SHELLG2 | 2 | 72 | -0.15796 | houston | -0.30402 | -0.1223 | -0.26265 | -0.0069202 | 0.0069202 | houston | N | 0.0069202 | 0
48822 | SHELLG3_ | 1 | 39 | -0.15796 | houston | -0.30402 | -0.1223 | -0.26265 | -0.0069202 | 0.0069202 | houston | N | 0.0069202 | 0
48822 | SHELLG3_ | 2 | 30 | -0.15796 | houston | -0.30402 | -0.1223 | -0.26265 | -0.0069202 | 0.0069202 | houston | N | 0.0069202 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.15645 | houston | -0.30251 | -0.12079 | -0.26114 | -0.0054072 | 0.0054072 | houston | N | 0.0054072 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.15645 | houston | -0.30251 | -0.12079 | -0.26114 | -0.0054072 | 0.0054072 | houston | N | 0.0054072 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.15751 | houston | -0.30357 | -0.12185 | -0.2622 | -0.0064672 | 0.0064672 | houston | N | 0.0064672 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.15742 | houston | -0.30348 | -0.12176 | -0.26211 | -0.0063792 | 0.0063792 | houston | N | 0.0063792 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.1574 | houston | -0.30346 | -0.12174 | -0.26209 | -0.0063552 | 0.0063552 | houston | N | 0.0063552 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.1575 | houston | -0.30356 | -0.12184 | -0.26219 | -0.0064592 | 0.0064592 | houston | N | 0.0064592 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.15752 | houston | -0.30359 | -0.12187 | -0.26222 | -0.0064842 | 0.0064842 | houston | N | 0.0064842 | 0
48855 | SRB_GT21 | B2 | 12 | -0.15738 | houston | -0.30344 | -0.12172 | -0.26207 | -0.0063392 | 0.0063392 | houston | N | 0.0063392 | 0
48855 | SRB_GT21 | MB | 18 | -0.15738 | houston | -0.30344 | -0.12172 | -0.26207 | -0.0063392 | 0.0063392 | houston | N | 0.0063392 | 0
48865 | TECO_GT1 | 1 | 50 | -0.15133 | houston | -0.29739 | -0.11567 | -0.25602 | -0.00028923 | 0.00028923 | houston | N | 0.00028923 | 0
48873 | THW_ST3_ | 3 | 104 | -0.15997 | houston | -0.30603 | -0.12431 | -0.26466 | -0.0089252 | 0.0089252 | houston | N | 0.0089252 | 0
48874 | THW_ST4_ | 4 | 104 | -0.15997 | houston | -0.30603 | -0.12431 | -0.26466 | -0.0089252 | 0.0089252 | houston | N | 0.0089252 | 0
48875 | THW_3132 | A | 54 | -0.15997 | houston | -0.30603 | -0.12431 | -0.26466 | -0.0089252 | 0.0089252 | houston | N | 0.0089252 | 0
48875 | THW_3132 | B | 53 | -0.15997 | houston | -0.30603 | -0.12431 | -0.26466 | -0.0089252 | 0.0089252 | houston | N | 0.0089252 | 0
48877 | THW_3334 | C | 54 | -0.15997 | houston | -0.30603 | -0.12431 | -0.26466 | -0.0089252 | 0.0089252 | houston | N | 0.0089252 | 0
48877 | THW_3334 | D | 57 | -0.15997 | houston | -0.30603 | -0.12431 | -0.26466 | -0.0089252 | 0.0089252 | houston | N | 0.0089252 | 0
48879 | THW_4142 | E | 54 | -0.15997 | houston | -0.30603 | -0.12431 | -0.26466 | -0.0089252 | 0.0089252 | houston | N | 0.0089252 | 0
48879 | THW_4142 | F | 54 | -0.15997 | houston | -0.30603 | -0.12431 | -0.26466 | -0.0089252 | 0.0089252 | houston | N | 0.0089252 | 0
48881 | THW_4344 | G | 58 | -0.15997 | houston | -0.30603 | -0.12431 | -0.26466 | -0.0089252 | 0.0089252 | houston | N | 0.0089252 | 0
48881 | THW_4344 | H | 58 | -0.15997 | houston | -0.30603 | -0.12431 | -0.26466 | -0.0089252 | 0.0089252 | houston | N | 0.0089252 | 0
48883 | THW_GT1_ | B2 | 12 | -0.16101 | houston | -0.30707 | -0.12536 | -0.26571 | -0.0099722 | 0.0099722 | houston | N | 0.0099722 | 0
48885 | THW_5152 | A | 56 | -0.16344 | houston | -0.3095 | -0.12778 | -0.26813 | -0.0124 | 0.0124 | houston | N | 0.0124 | 0
48885 | THW_5152 | B | 59 | -0.16344 | houston | -0.3095 | -0.12778 | -0.26813 | -0.0124 | 0.0124 | houston | N | 0.0124 | 0
48886 | THW_5354 | C | 56 | -0.16344 | houston | -0.3095 | -0.12778 | -0.26813 | -0.0124 | 0.0124 | houston | N | 0.0124 | 0
48886 | THW_5354 | D | 56 | -0.16344 | houston | -0.3095 | -0.12778 | -0.26813 | -0.0124 | 0.0124 | houston | N | 0.0124 | 0
48887 | THW_5556 | E | 59 | -0.16344 | houston | -0.3095 | -0.12778 | -0.26813 | -0.0124 | 0.0124 | houston | N | 0.0124 | 0
48887 | THW_5556 | F | 56 | -0.16344 | houston | -0.3095 | -0.12778 | -0.26813 | -0.0124 | 0.0124 | houston | N | 0.0124 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.11579 | houston | -0.26186 | -0.080138 | -0.22049 | 0.035246 | 0.035246 | houston | N | 0.035246 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.14482 | houston | -0.29088 | -0.10916 | -0.24951 | 0.0062228 | 0.0062228 | houston | N | 0.0062228 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.14482 | houston | -0.29088 | -0.10916 | -0.24951 | 0.0062228 | 0.0062228 | houston | N | 0.0062228 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.14482 | houston | -0.29088 | -0.10916 | -0.24951 | 0.0062228 | 0.0062228 | houston | N | 0.0062228 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.14482 | houston | -0.29088 | -0.10916 | -0.24951 | 0.0062228 | 0.0062228 | houston | N | 0.0062228 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.14482 | houston | -0.29088 | -0.10916 | -0.24951 | 0.0062228 | 0.0062228 | houston | N | 0.0062228 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.14339 | houston | -0.28945 | -0.10774 | -0.24809 | 0.0076478 | 0.0076478 | houston | N | 0.0076478 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.14339 | houston | -0.28945 | -0.10774 | -0.24809 | 0.0076478 | 0.0076478 | houston | N | 0.0076478 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.14339 | houston | -0.28945 | -0.10774 | -0.24809 | 0.0076478 | 0.0076478 | houston | N | 0.0076478 | 0
48929 | WAPGT21_ | B1 | 13 | -0.14482 | houston | -0.29088 | -0.10916 | -0.24951 | 0.0062228 | 0.0062228 | houston | N | 0.0062228 | 0
48940 | WARVUE_G | G1 | 12 | -0.16148 | houston | -0.30754 | -0.12582 | -0.26617 | -0.010435 | 0.010435 | houston | N | 0.010435 | 0
49803 | EXN_15GT | 1 | 34 | -0.16064 | houston | -0.3067 | -0.12498 | -0.26534 | -0.0096012 | 0.0096012 | houston | N | 0.0096012 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.16064 | houston | -0.3067 | -0.12498 | -0.26534 | -0.0096012 | 0.0096012 | houston | N | 0.0096012 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.16064 | houston | -0.3067 | -0.12498 | -0.26534 | -0.0096012 | 0.0096012 | houston | N | 0.0096012 | 0
49826 | EXN938GT | 5 | 45.9 | -0.16064 | houston | -0.3067 | -0.12498 | -0.26534 | -0.0096012 | 0.0096012 | houston | N | 0.0096012 | 0
49828 | EXN941GT | 10 | 17.7 | -0.16064 | houston | -0.3067 | -0.12498 | -0.26534 | -0.0096012 | 0.0096012 | houston | N | 0.0096012 | 0
49829 | EXN942GT | 11 | 20.4 | -0.16064 | houston | -0.3067 | -0.12498 | -0.26534 | -0.0096012 | 0.0096012 | houston | N | 0.0096012 | 0
49830 | EXN943GT | 12 | 19.9 | -0.16064 | houston | -0.3067 | -0.12498 | -0.26534 | -0.0096012 | 0.0096012 | houston | N | 0.0096012 | 0
49831 | EXN944GT | 13 | 35 | -0.16064 | houston | -0.3067 | -0.12498 | -0.26534 | -0.0096012 | 0.0096012 | houston | N | 0.0096012 | 0
49832 | EXN945GT | 9 | 18 | -0.16064 | houston | -0.3067 | -0.12498 | -0.26534 | -0.0096012 | 0.0096012 | houston | N | 0.0096012 | 0
49837 | EXN_GT | 4 | 85.4 | -0.16064 | houston | -0.3067 | -0.12498 | -0.26534 | -0.0096012 | 0.0096012 | houston | N | 0.0096012 | 0
49838 | EXN_14GT | 14 | 148 | -0.16064 | houston | -0.3067 | -0.12498 | -0.26534 | -0.0096012 | 0.0096012 | houston | N | 0.0096012 | 0
49851 | DOW17000 | 37 | 62 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49858 | DOW38100 | 31 | 71.4 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49859 | DOW38200 | 33 | 45 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49860 | DOW38300 | 32 | 101 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49862 | DOW39100 | 36 | 86 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49863 | DOW39200 | 35 | 88 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49865 | DOW41000 | 41 | 50 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49866 | DOW42000 | 42 | 18 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49869 | DOW49000 | 45 | 94 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49870 | DOW61000 | 61 | 70 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49871 | DOW62000 | 62 | 63 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49872 | DOW63000 | 63 | 72 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49873 | DOW64000 | 64 | 64.8 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49876 | DOW65000 | 65 | 101 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49877 | DOW66000 | 66 | 97 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49878 | DOW67000 | 67 | 103 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49882 | DOW81000 | 81 | 76 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49884 | DOW82000 | 82 | 80 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49885 | DOW83000 | 83 | 80 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
49886 | DOW84000 | 84 | 171 | -0.12862 | houston | -0.27468 | -0.092964 | -0.23331 | 0.02242 | 0.02242 | houston | N | 0.02242 | 0
58909 | PEARSALL | 1 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58909 | PEARSALL | 2 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58909 | PEARSALL | 3 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58909 | PEARSALL | 4 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58909 | PEARSALL | 5 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58909 | PEARSALL | 6 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58919 | PEARSALL | 1 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58919 | PEARSALL | 2 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58919 | PEARSALL | 3 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58919 | PEARSALL | 4 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58919 | PEARSALL | 5 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58919 | PEARSALL | 6 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58929 | PEARSALL | 1 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58929 | PEARSALL | 2 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58929 | PEARSALL | 3 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58929 | PEARSALL | 4 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58929 | PEARSALL | 5 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58929 | PEARSALL | 6 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58949 | PEARSALL | 1 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58949 | PEARSALL | 2 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58949 | PEARSALL | 3 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58949 | PEARSALL | 4 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58949 | PEARSALL | 5 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
58949 | PEARSALL | 6 | 8.4 | -0.040624 | south | -0.18669 | -0.0049668 | -0.14532 | 0.11042 | 0.0049668 | south | N | 0.0049668 | 0
60000 | DSKY2 | 1 | 76.5 | 0.094977 | west | -0.051084 | 0.13063 | -0.0097167 | 0.24602 | 0.0097167 | west | N | 0.0097167 | 0
60003 | KING_NE1 | 1 | 80 | 0.097677 | west | -0.048384 | 0.13333 | -0.0070167 | 0.24872 | 0.0070167 | west | N | 0.0070167 | 0
60005 | KING_SE1 | 1 | 40 | 0.097677 | west | -0.048384 | 0.13333 | -0.0070167 | 0.24872 | 0.0070167 | west | N | 0.0070167 | 0
60007 | KING_SW1 | 1 | 80 | 0.098113 | west | -0.047948 | 0.13377 | -0.0065807 | 0.24915 | 0.0065807 | west | N | 0.0065807 | 0
60016 | WOODWRD1 | 1 | 80 | 0.097583 | west | -0.048478 | 0.13324 | -0.0071107 | 0.24862 | 0.0071107 | west | N | 0.0071107 | 0
60017 | ORNNWP1 | 1 | 80 | 0.095341 | west | -0.05072 | 0.131 | -0.0093527 | 0.24638 | 0.0093527 | west | N | 0.0093527 | 0
60018 | DSKY1 | 1 | 84 | 0.094607 | west | -0.051454 | 0.13026 | -0.010087 | 0.24565 | 0.010087 | west | N | 0.010087 | 0
60019 | KING_NW1 | 1 | 80 | 0.098113 | west | -0.047948 | 0.13377 | -0.0065807 | 0.24915 | 0.0065807 | west | N | 0.0065807 | 0
60057 | CALLAHAN | 1 | 114 | -0.03255 | south | -0.17861 | 0.0031072 | -0.13724 | 0.11849 | 0.0031072 | south | N | 0.0031072 | 0
60058 | BUFF_GAP | 1 | 120 | 0.10536 | west | -0.040706 | 0.14101 | 0.00066132 | 0.2564 | 0.00066132 | west | N | 0.00066132 | 0
60060 | CIRELLO | 1 | 233 | 0.10536 | west | -0.040706 | 0.14101 | 0.00066132 | 0.2564 | 0.00066132 | west | N | 0.00066132 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.10536 | west | -0.040706 | 0.14101 | 0.00066132 | 0.2564 | 0.00066132 | west | N | 0.00066132 | 0
60066 | H_HOLLOW | 1 | 222 | -0.03255 | south | -0.17861 | 0.0031072 | -0.13724 | 0.11849 | 0.0031072 | south | N | 0.0031072 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.03255 | south | -0.17861 | 0.0031072 | -0.13724 | 0.11849 | 0.0031072 | south | N | 0.0031072 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.03255 | south | -0.17861 | 0.0031072 | -0.13724 | 0.11849 | 0.0031072 | south | N | 0.0031072 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.03255 | south | -0.17861 | 0.0031072 | -0.13724 | 0.11849 | 0.0031072 | south | N | 0.0031072 | 0
60074 | HORSH5 | 1 | 100 | -0.03255 | south | -0.17861 | 0.0031072 | -0.13724 | 0.11849 | 0.0031072 | south | N | 0.0031072 | 0
60081 | WHRLWIND | 1 | 60 | 0.10741 | west | -0.038653 | 0.14307 | 0.0027143 | 0.25845 | 0.0027143 | west | N | 0.0027143 | 0
60201 | RIO DRCS | F | 0 | 0.023217 | south | -0.12284 | 0.058874 | -0.081477 | 0.17426 | 0.058874 | south | N | 0.058874 | 0
60202 | FRIEND_R | F | 0 | 0.082912 | west | -0.063149 | 0.11857 | -0.021782 | 0.23395 | 0.021782 | west | N | 0.021782 | 0
60203 | PRES0A | BT | 4.8 | 0.099723 | west | -0.046338 | 0.13538 | -0.0049707 | 0.25076 | 0.0049707 | west | N | 0.0049707 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.10649 | west | -0.039568 | 0.14215 | 0.0017993 | 0.25753 | 0.0017993 | west | N | 0.0017993 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.10649 | west | -0.039568 | 0.14215 | 0.0017993 | 0.25753 | 0.0017993 | west | N | 0.0017993 | 0
71057 | L_SWEETW | W1 | 135 | 0.10649 | west | -0.039568 | 0.14215 | 0.0017993 | 0.25753 | 0.0017993 | west | N | 0.0017993 | 0
71059 | L_SWEETW | W1 | 119 | 0.10649 | west | -0.039568 | 0.14215 | 0.0017993 | 0.25753 | 0.0017993 | west | N | 0.0017993 | 0
71060 | L_SWEETW | W1 | 105 | 0.10649 | west | -0.039568 | 0.14215 | 0.0017993 | 0.25753 | 0.0017993 | west | N | 0.0017993 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.10649 | west | -0.039568 | 0.14215 | 0.0017993 | 0.25753 | 0.0017993 | west | N | 0.0017993 | 0
76031 | L_GASCCR | W1 | 150 | 0.1047 | west | -0.041361 | 0.14036 | 6.3158e-06 | 0.25574 | 6.3158e-06 | west | N | 6.3158e-06 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.10447 | west | -0.041589 | 0.14013 | -0.00022168 | 0.25551 | 0.00022168 | west | N | 0.00022168 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.10447 | west | -0.041589 | 0.14013 | -0.00022168 | 0.25551 | 0.00022168 | west | N | 0.00022168 | 0
76096 | L_CAPRSI | W1 | 186 | 0.10447 | west | -0.041589 | 0.14013 | -0.00022168 | 0.25551 | 0.00022168 | west | N | 0.00022168 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.10447 | west | -0.041589 | 0.14013 | -0.00022168 | 0.25551 | 0.00022168 | west | N | 0.00022168 | 0
80003 | MILHWYS | F | 0 | -0.063504 | south | -0.20957 | -0.027847 | -0.1682 | 0.087537 | 0.027847 | south | N | 0.027847 | 0
80010 | EPLVT1 | F | 0 | -0.018726 | south | -0.16479 | 0.016931 | -0.12342 | 0.13231 | 0.016931 | south | N | 0.016931 | 0
80012 | LAR | F | 0 | -0.048387 | south | -0.19445 | -0.01273 | -0.15308 | 0.10265 | 0.01273 | south | N | 0.01273 | 0
80051 | FORPVCM0 | 8 | 28 | -0.075898 | south | -0.22196 | -0.040241 | -0.18059 | 0.075143 | 0.040241 | south | N | 0.040241 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.075898 | south | -0.22196 | -0.040241 | -0.18059 | 0.075143 | 0.040241 | south | N | 0.040241 | 0
80053 | FOR69CG0 | 10 | 74 | -0.075898 | south | -0.22196 | -0.040241 | -0.18059 | 0.075143 | 0.040241 | south | N | 0.040241 | 0
80080 | GWINDT11 | 1 | 94 | -0.063687 | south | -0.20975 | -0.02803 | -0.16838 | 0.087354 | 0.02803 | south | N | 0.02803 | 0
80080 | GWINDT11 | 2 | 41 | -0.063687 | south | -0.20975 | -0.02803 | -0.16838 | 0.087354 | 0.02803 | south | N | 0.02803 | 0
80080 | GWINDT11 | 3 | 38 | -0.063687 | south | -0.20975 | -0.02803 | -0.16838 | 0.087354 | 0.02803 | south | N | 0.02803 | 0
80080 | GWINDT11 | 4 | 19 | -0.063687 | south | -0.20975 | -0.02803 | -0.16838 | 0.087354 | 0.02803 | south | N | 0.02803 | 0
80081 | GWINDT21 | 1 | 94 | -0.063687 | south | -0.20975 | -0.02803 | -0.16838 | 0.087354 | 0.02803 | south | N | 0.02803 | 0
80081 | GWINDT21 | 2 | 36 | -0.063687 | south | -0.20975 | -0.02803 | -0.16838 | 0.087354 | 0.02803 | south | N | 0.02803 | 0
80081 | GWINDT21 | 3 | 43 | -0.063687 | south | -0.20975 | -0.02803 | -0.16838 | 0.087354 | 0.02803 | south | N | 0.02803 | 0
80081 | GWINDT21 | 4 | 22 | -0.063687 | south | -0.20975 | -0.02803 | -0.16838 | 0.087354 | 0.02803 | south | N | 0.02803 | 0
80137 | CSDR89 | 8 | 39 | -0.071643 | south | -0.2177 | -0.035986 | -0.17634 | 0.079398 | 0.035986 | south | N | 0.035986 | 0
80137 | CSDR89 | 9 | 15 | -0.071643 | south | -0.2177 | -0.035986 | -0.17634 | 0.079398 | 0.035986 | south | N | 0.035986 | 0
80138 | CSDR7 | 7 | 7 | -0.071643 | south | -0.2177 | -0.035986 | -0.17634 | 0.079398 | 0.035986 | south | N | 0.035986 | 0
80139 | CSDR56 | 5 | 15 | -0.071643 | south | -0.2177 | -0.035986 | -0.17634 | 0.079398 | 0.035986 | south | N | 0.035986 | 0
80139 | CSDR56 | 6 | 39 | -0.071643 | south | -0.2177 | -0.035986 | -0.17634 | 0.079398 | 0.035986 | south | N | 0.035986 | 0
80140 | CSDR11 | 11 | 39 | -0.071643 | south | -0.2177 | -0.035986 | -0.17634 | 0.079398 | 0.035986 | south | N | 0.035986 | 0
80180 | PNSCALT1 | 1 | 148 | -0.063687 | south | -0.20975 | -0.02803 | -0.16838 | 0.087354 | 0.02803 | south | N | 0.02803 | 0
80180 | PNSCALT1 | 2 | 50 | -0.063687 | south | -0.20975 | -0.02803 | -0.16838 | 0.087354 | 0.02803 | south | N | 0.02803 | 0
80181 | PNSCALT2 | 1 | 55 | -0.063687 | south | -0.20975 | -0.02803 | -0.16838 | 0.087354 | 0.02803 | south | N | 0.02803 | 0
80181 | PNSCALT2 | 2 | 50 | -0.063687 | south | -0.20975 | -0.02803 | -0.16838 | 0.087354 | 0.02803 | south | N | 0.02803 | 0
80223 | REYSHR G | 1 | 12 | -0.066515 | south | -0.21258 | -0.030858 | -0.17121 | 0.084526 | 0.030858 | south | N | 0.030858 | 0
80224 | VISTRONG | 1 | 15 | -0.070343 | south | -0.2164 | -0.034686 | -0.17504 | 0.080698 | 0.034686 | south | N | 0.034686 | 0
80225 | VISTRONG | 2 | 23 | -0.070343 | south | -0.2164 | -0.034686 | -0.17504 | 0.080698 | 0.034686 | south | N | 0.034686 | 0
80226 | ALCOA G | 1 | 48 | -0.07491 | south | -0.22097 | -0.039253 | -0.1796 | 0.076131 | 0.039253 | south | N | 0.039253 | 0
80227 | AIRCO G | 1 | 8 | -0.071133 | south | -0.21719 | -0.035476 | -0.17583 | 0.079908 | 0.035476 | south | N | 0.035476 | 0
80261 | NBEC81A | 1 | 180 | -0.065108 | south | -0.21117 | -0.029451 | -0.1698 | 0.085933 | 0.029451 | south | N | 0.029451 | 0
80262 | NBEC91A | 1 | 180 | -0.06515 | south | -0.21121 | -0.029493 | -0.16984 | 0.085891 | 0.029493 | south | N | 0.029493 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.064854 | south | -0.21092 | -0.029197 | -0.16955 | 0.086187 | 0.029197 | south | N | 0.029197 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.064854 | south | -0.21092 | -0.029197 | -0.16955 | 0.086187 | 0.029197 | south | N | 0.029197 | 0
80265 | LARECU40 | 4 | 100 | -0.048383 | south | -0.19444 | -0.012726 | -0.15308 | 0.10266 | 0.012726 | south | N | 0.012726 | 0
80266 | LARECU50 | 5 | 100 | -0.048383 | south | -0.19444 | -0.012726 | -0.15308 | 0.10266 | 0.012726 | south | N | 0.012726 | 0
80291 | PAPALOTE | 1 | 25 | -0.065968 | south | -0.21203 | -0.030311 | -0.17066 | 0.085073 | 0.030311 | south | N | 0.030311 | 0
80291 | PAPALOTE | 2 | 25 | -0.065968 | south | -0.21203 | -0.030311 | -0.17066 | 0.085073 | 0.030311 | south | N | 0.030311 | 0
80291 | PAPALOTE | 3 | 25 | -0.065968 | south | -0.21203 | -0.030311 | -0.17066 | 0.085073 | 0.030311 | south | N | 0.030311 | 0
80291 | PAPALOTE | 4 | 16 | -0.065968 | south | -0.21203 | -0.030311 | -0.17066 | 0.085073 | 0.030311 | south | N | 0.030311 | 0
80294 | PAPALOTE | 5 | 25 | -0.065968 | south | -0.21203 | -0.030311 | -0.17066 | 0.085073 | 0.030311 | south | N | 0.030311 | 0
80294 | PAPALOTE | 6 | 25 | -0.065968 | south | -0.21203 | -0.030311 | -0.17066 | 0.085073 | 0.030311 | south | N | 0.030311 | 0
80294 | PAPALOTE | 7 | 25 | -0.065968 | south | -0.21203 | -0.030311 | -0.17066 | 0.085073 | 0.030311 | south | N | 0.030311 | 0
80294 | PAPALOTE | 8 | 15 | -0.065968 | south | -0.21203 | -0.030311 | -0.17066 | 0.085073 | 0.030311 | south | N | 0.030311 | 0
86104 | CID-138 | EQ | 0 | -0.048383 | south | -0.19444 | -0.012726 | -0.15308 | 0.10266 | 0.012726 | south | N | 0.012726 | 0
86105 | CID-230 | EQ | 500 | -0.048383 | south | -0.19444 | -0.012726 | -0.15308 | 0.10266 | 0.012726 | south | N | 0.012726 | 0
86106 | CUF-230 | EQ | 500 | -0.048383 | south | -0.19444 | -0.012726 | -0.15308 | 0.10266 | 0.012726 | south | N | 0.012726 | 0
86107 | CUF-138 | EQ | 0 | -0.048383 | south | -0.19444 | -0.012726 | -0.15308 | 0.10266 | 0.012726 | south | N | 0.012726 | 0
88198 | BEEVILLE | F | 0 | -0.057534 | south | -0.2036 | -0.021877 | -0.16223 | 0.093507 | 0.021877 | south | N | 0.021877 | 0
88253 | HAMILTON | F | 0 | -0.002962 | south | -0.14902 | 0.032695 | -0.10766 | 0.14808 | 0.032695 | south | N | 0.032695 | 0
88299 | ZAPATA | F | 0 | -0.054289 | south | -0.20035 | -0.018632 | -0.15898 | 0.096752 | 0.018632 | south | N | 0.018632 | 0
88508 | FALFURRI | F | 0 | -0.060431 | south | -0.20649 | -0.024774 | -0.16512 | 0.09061 | 0.024774 | south | N | 0.024774 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | 0 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.63771 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 295.2616 | 463 | 0.7909 | 366.1883 | 463 | 366.1883
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.54391 | north | 7 | N | N | Nnorth | Nnorth | 1 | 17.4052 | 0 | 0.6971 | 0 | 463 | 366.1883
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.54 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.69319 | 0 | 463 | 366.1883
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.54 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.69319 | 0 | 463 | 366.1883 | Weighted Shift Factors
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.54 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.1801 | 17 | 0.69319 | 11.7843 | 480 | 377.9726 | North | 0.14606
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.54 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.69319 | 0 | 480 | 377.9726 | Houston | -0.15319
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.54 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.69319 | 0 | 480 | 377.9726 |  | 0.29925
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.51456 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 24.6988 | 48 | 0.66775 | 32.0519 | 528 | 410.0245
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.51456 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 23.6697 | 46 | 0.66775 | 30.7164 | 574 | 440.7409 | Line Rating | 2080
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.51456 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 54.0287 | 105 | 0.66775 | 70.1136 | 679 | 510.8545 | Conc Gen | 3521.3
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.29529 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 252.4695 | 855 | 0.44848 | 383.4465 | 1534 | 894.301 | Weighted Imp. | 1685.5751
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.29529 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 252.4695 | 855 | 0.44848 | 383.4465 | 2389 | 1277.7474 | PTDF | 0.47868
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.29529 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 44.9721 | 152.3 | 0.44848 | 68.3028 | 2541.3 | 1346.0502
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.29529 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 45.1788 | 153 | 0.44848 | 68.6167 | 2694.3 | 1414.667 | Concentration | 1.5996
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.17439 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 144.2205 | 827 | 0.32758 | 270.9082 | 3521.3 | 1685.5751
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.17439 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 142.8254 | 819 | 0.32758 | 268.2875
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.12512 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 22.7717 | 182 | 0.27831 | 50.6521
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.12512 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 60.5576 | 484 | 0.27831 | 134.7013
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.12406 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.27725 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.12405 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.2024 | 50 | 0.27724 | 13.8618
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.12346 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.2716 | 0 | 0.27665 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.12346 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.0494 | 0 | 0.27665 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.12346 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.9013 | 0 | 0.27665 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.12346 | north | 1 | N | N | Nnorth | Nnorth | 1 | 49.2593 | 0 | 0.27665 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.12344 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 96.9035 | 785 | 0.27663 | 217.1572
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.12344 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 98.138 | 795 | 0.27663 | 219.9236
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.12344 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 96.2863 | 780 | 0.27663 | 215.7741
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.12301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.5376 | 150.7 | 0.2762 | 41.6232
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.12301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.5745 | 151 | 0.2762 | 41.7061
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.12301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.822 | 177.4 | 0.2762 | 48.9978
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.12288 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.6171 | 151.5 | 0.27607 | 41.8253
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.12288 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.7154 | 152.3 | 0.27607 | 42.0461
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.12288 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.8121 | 177.5 | 0.27607 | 49.0032
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.12281 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 75.5294 | 615 | 0.276 | 169.7409
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.12281 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 72.0906 | 587 | 0.276 | 162.0128
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.12183 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 27.2906 | 224 | 0.27502 | 61.605
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.577 | 161 | 0.27479 | 44.2404
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9417 | 164 | 0.27479 | 45.0648
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9417 | 164 | 0.27479 | 45.0648
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 50.3407 | 414 | 0.27479 | 113.7612
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.6986 | 162 | 0.27479 | 44.5152
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.577 | 161 | 0.27479 | 44.2404
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.8201 | 163 | 0.27479 | 44.79
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 49.7328 | 409 | 0.27479 | 112.3872
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.121 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 46.948 | 388 | 0.27419 | 106.3855
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.121 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 62.315 | 515 | 0.27419 | 141.2075
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.12091 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.2741 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.12091 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.2741 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.12069 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.4139 | 20 | 0.27388 | 5.4776
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.12069 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0173 | 25 | 0.27388 | 6.8471
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.12069 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.9484 | 41 | 0.27388 | 11.2292
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.12061 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.8242 | 40 | 0.2738 | 10.9518
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.12055 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.5238 | 79 | 0.27374 | 21.6257
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.12055 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.7787 | 106 | 0.27374 | 29.0168
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.12055 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 17.6009 | 146 | 0.27374 | 39.9665
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.12055 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.1621 | 76 | 0.27374 | 20.8045
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.12029 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 67.1241 | 558 | 0.27348 | 152.6037
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.12029 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 69.6502 | 579 | 0.27348 | 158.3469
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.12029 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 97.1976 | 808 | 0.27348 | 220.9746
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.12018 | north | 8 | N | N | Nnorth | Nnorth | 1 | 9.0131 | 0 | 0.27336 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.12018 | north | 8 | N | N | Nnorth | Nnorth | 1 | 9.5659 | 0 | 0.27336 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.12018 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.6235 | 0 | 0.27336 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.2195 | 160 | 0.27331 | 43.7298
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.739 | 156 | 0.27331 | 42.6366
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5439 | 196 | 0.27331 | 53.569
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.739 | 156 | 0.27331 | 42.6366
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.8592 | 157 | 0.27331 | 42.9099
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.7842 | 198 | 0.27331 | 54.1157
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.12003 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 44.4115 | 370 | 0.27322 | 101.0915
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.8043 | 0 | 0.27322 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.9244 | 0 | 0.27322 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 37.0896 | 0 | 0.27322 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.1644 | 0 | 0.27322 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.2845 | 0 | 0.27322 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 37.2096 | 0 | 0.27322 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.11979 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 20.3635 | 170 | 0.27297 | 46.4056
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.11979 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 62.2882 | 520 | 0.27297 | 141.9467
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.11973 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.1287 | 118 | 0.27292 | 32.2051
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.11973 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 13.7695 | 115 | 0.27292 | 31.3863
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.11973 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 66.5727 | 556 | 0.27292 | 151.746
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.1196 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.7839 | 0 | 0.27279 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.1196 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.7839 | 0 | 0.27279 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.11939 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.27258 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.11907 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27226 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.11882 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2895 | 196 | 0.27201 | 53.3146
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.11882 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.1895 | 111 | 0.27201 | 30.1935
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.11701 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 7.0209 | 60 | 0.2702 | 16.2123
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.11701 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 7.3719 | 63 | 0.2702 | 17.0229
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.11567 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 13.0128 | 112.5 | 0.26886 | 30.2466
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.11546 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 50.2268 | 435 | 0.26865 | 116.8642
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.11514 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 45.4795 | 395 | 0.26833 | 105.9893
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.11514 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 50.085 | 435 | 0.26833 | 116.7224
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.11504 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26823 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.11504 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26823 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.11504 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26823 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.1142 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.7131 | 216.4 | 0.26739 | 57.8633
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.1142 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.6788 | 216.1 | 0.26739 | 57.7831
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.11386 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.7928 | 288 | 0.26705 | 76.9114
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.11386 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.738 | 147 | 0.26705 | 39.2568
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.11386 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.738 | 147 | 0.26705 | 39.2568
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.11313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.0795 | 204 | 0.26632 | 54.3302
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.11313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7401 | 201 | 0.26632 | 53.5312
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.11313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.3787 | 242 | 0.26632 | 64.4505
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.11302 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26621 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.11281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.2694 | 224 | 0.266 | 59.5839
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.11281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.4951 | 226 | 0.266 | 60.1159
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.11281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.9157 | 212 | 0.266 | 56.3919
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.11281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.8029 | 211 | 0.266 | 56.1259
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.11272 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.4938 | 217.3 | 0.26591 | 57.7819
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.11272 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1074 | 205 | 0.26591 | 54.5112
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.11272 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.7047 | 272.4 | 0.26591 | 72.4334
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.11242 | north | 3 | N | N | Nnorth | Nnorth | 1 | 130.0734 | 0 | 0.26561 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.11242 | north | 3 | N | N | Nnorth | Nnorth | 1 | 130.1858 | 0 | 0.26561 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.11237 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0227 | 18 | 0.26556 | 4.7801
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.11237 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0227 | 18 | 0.26556 | 4.7801
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.11237 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.2701 | 38 | 0.26556 | 10.0913
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.11152 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2305 | 20 | 0.26471 | 5.2942
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.11152 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2305 | 20 | 0.26471 | 5.2942
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.11152 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2305 | 20 | 0.26471 | 5.2942
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.11152 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.8959 | 17 | 0.26471 | 4.5001
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.11142 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.7997 | 70 | 0.26461 | 18.5229
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.11142 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.6883 | 69 | 0.26461 | 18.2583
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.11142 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.6883 | 69 | 0.26461 | 18.2583
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.11142 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.5768 | 68 | 0.26461 | 17.9937
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.11139 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.3367 | 0 | 0.26458 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.11139 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.3367 | 0 | 0.26458 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.11138 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 40.7647 | 366 | 0.26457 | 96.832
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.11123 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 13.3475 | 120 | 0.26442 | 31.7302
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1107 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.7889 | 242 | 0.26389 | 63.8608
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.11045 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.5563 | 168 | 0.26364 | 44.2921
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.11045 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.9409 | 90 | 0.26364 | 23.7279
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.11005 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.0336 | 73 | 0.26324 | 19.2165
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.11005 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.096 | 119 | 0.26324 | 31.3255
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.11005 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 22.5602 | 205 | 0.26324 | 53.9641
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.11005 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.2251 | 102 | 0.26324 | 26.8504
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.11005 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.5648 | 96 | 0.26324 | 25.271
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.10983 | west | 4 | Y | N | Ywest | Nwest | 1 | 71.3579 | 649.7 | 0.26302 | 170.885
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.10924 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.0254 | 165 | 0.26243 | 43.3017
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.10857 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.6228 | 236 | 0.26176 | 61.7755
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.10857 | west | 6 | Y | N | Ywest | Nwest | 1 | 43.4272 | 400 | 0.26176 | 104.703
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.10741 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4445 | 60 | 0.2606 | 15.6358
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.10661 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.991 | 150 | 0.2598 | 38.9695
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.10658 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.2763 | 209 | 0.25977 | 54.2928
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.10658 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.483 | 126.5 | 0.25977 | 32.8615
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.10658 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.5397 | 249 | 0.25977 | 64.6838
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.10658 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9972 | 197 | 0.25977 | 51.1756
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9935 | 37.5 | 0.25968 | 9.7381
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.448 | 107.5 | 0.25968 | 27.9159
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.3766 | 135 | 0.25968 | 35.0571
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6727 | 119 | 0.25968 | 30.9022
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.1818 | 105 | 0.25968 | 27.2667
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5727 | 80.5 | 0.25968 | 20.9044
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.10636 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.3818 | 60 | 0.25955 | 15.5731
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.10619 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.2731 | 125 | 0.25937 | 32.4218
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.10619 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.2731 | 125 | 0.25937 | 32.4218
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.10605 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9072 | 150 | 0.25924 | 38.8856
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.10605 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7108 | 101 | 0.25924 | 26.183
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.10599 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9029 | 84 | 0.25918 | 21.7708
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.10585 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.4788 | 99 | 0.25904 | 25.6445
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.10585 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4566 | 61 | 0.25904 | 15.8012
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.10585 | west | 7 | N | N | Nwest | Nwest | 1 | 2.6462 | 0 | 0.25904 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.10585 | west | 7 | N | N | Nwest | Nwest | 1 | 4.8372 | 0 | 0.25904 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.10585 | west | 7 | N | N | Nwest | Nwest | 1 | 4.8372 | 0 | 0.25904 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.10583 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.9219 | 141 | 0.25902 | 36.5216
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.10583 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6995 | 120 | 0.25902 | 31.0822
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.10579 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6645 | 63 | 0.25897 | 16.3154
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.9792 | 66 | 0.25893 | 17.0897
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.2964 | 69 | 0.25893 | 17.8665
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.2964 | 69 | 0.25893 | 17.8665
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.0849 | 67 | 0.25893 | 17.3486
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.0849 | 67 | 0.25893 | 17.3486
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.8734 | 65 | 0.25893 | 16.8307
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.10562 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.8429 | 150 | 0.25881 | 38.8213
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.10562 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.2362 | 220 | 0.25881 | 56.9378
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.10562 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.1238 | 200 | 0.25881 | 51.7617
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.10562 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.875 | 121.9 | 0.25881 | 31.5487
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.10545 | west | 8 | N | N | Nwest | Nwest | 1 | 7.3813 | 0 | 0.25864 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.10545 | west | 8 | N | N | Nwest | Nwest | 1 | 7.7398 | 0 | 0.25864 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.10545 | west | 8 | N | N | Nwest | Nwest | 1 | 7.4235 | 0 | 0.25864 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.10544 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.9787 | 180 | 0.25863 | 46.5528
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.10544 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.9787 | 180 | 0.25863 | 46.5528
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.10538 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.711 | 225 | 0.25857 | 58.1786
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.10536 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6426 | 120 | 0.25854 | 31.0253
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.10536 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.5477 | 233 | 0.25854 | 60.2408
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.10536 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.9314 | 170.2 | 0.25854 | 44.0043
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.10528 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6336 | 120 | 0.25847 | 31.0163
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.10526 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6308 | 120 | 0.25845 | 31.0136
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.10493 | west | 8 | N | N | Nwest | Nwest | 1 | 2.7071 | 0 | 0.25812 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.10486 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.4617 | 214.2 | 0.25805 | 55.2748
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.10474 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.5261 | 100.5 | 0.25793 | 25.9216
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.10472 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0737 | 58 | 0.25791 | 14.9587
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.1047 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.705 | 150 | 0.25789 | 38.6834
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.3283 | 70 | 0.25788 | 18.0516
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.3283 | 70 | 0.25788 | 18.0516
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.7152 | 92.8 | 0.25788 | 23.9312
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.3752 | 80 | 0.25788 | 20.6304
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.3752 | 80 | 0.25788 | 20.6304
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 1 | 12.0394 | 115 | 0.25788 | 29.6561
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 1 | 21.7944 | 208.2 | 0.25787 | 53.6884
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.875 | 142.1 | 0.25787 | 36.6432
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.8596 | 132.4 | 0.25787 | 34.1419
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.2365 | 136 | 0.25787 | 35.0702
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.388 | 147 | 0.25787 | 37.9068
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 1 | 21.9828 | 210 | 0.25787 | 54.1526
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.10447 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7531 | 112.5 | 0.25766 | 28.9869
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.10447 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.6186 | 149.5 | 0.25766 | 38.5204
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.10447 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.4318 | 186 | 0.25766 | 47.925
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.10447 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.4092 | 214.5 | 0.25766 | 55.2684
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.10417 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68754 | 6.6 | 0.25736 | 1.6986
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.10417 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5731 | 34.3 | 0.25736 | 8.8275
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.10385 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4741 | 149 | 0.25704 | 38.2993
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.10377 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.5883 | 169.5 | 0.25696 | 43.5539
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.10367 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6285 | 35 | 0.25686 | 8.9901
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.10367 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1102 | 30 | 0.25686 | 7.7058
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.8389 | 66 | 0.25681 | 16.9494
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.7352 | 65 | 0.25681 | 16.6925
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.9425 | 67 | 0.25681 | 17.2062
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.9425 | 67 | 0.25681 | 17.2062
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.9425 | 67 | 0.25681 | 17.2062
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.10362 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.25681 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.10362 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.25681 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.099723 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.47867 | 0 | 0.25291 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.098113 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.849 | 80 | 0.2513 | 20.1042
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.098113 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.849 | 80 | 0.2513 | 20.1042
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.097677 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3258 | 75 | 0.25087 | 18.815
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.097677 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8142 | 80 | 0.25087 | 20.0693
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.097677 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9071 | 40 | 0.25087 | 10.0347
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.097583 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8066 | 80 | 0.25077 | 20.0618
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.09757 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8056 | 80 | 0.25076 | 20.0608
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.097515 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.6273 | 150 | 0.2507 | 37.6057
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.097515 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.6273 | 150 | 0.2507 | 37.6057
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.095341 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6273 | 80 | 0.24853 | 19.8824
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.094977 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2657 | 76.5 | 0.24817 | 18.9847
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.094607 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.947 | 84 | 0.2478 | 20.8149
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.09441 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4162 | 0 | 0.2476 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.09441 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4162 | 0 | 0.2476 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.089545 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.4317 | 150 | 0.24273 | 36.4102
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.089545 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.1636 | 80 | 0.24273 | 19.4188
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.087047 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.197 | 255 | 0.24024 | 61.2603
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.087047 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 12.97 | 149 | 0.24024 | 35.7952
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.087047 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.3182 | 153 | 0.24024 | 36.7562
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.08516 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23835 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.08516 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23835 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.083869 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23706 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.083869 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 66.0049 | 787 | 0.23706 | 186.565
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.082912 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.2361 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.074678 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.2017 | 150 | 0.22787 | 34.1801
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.023217 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.17641 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.15319 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.15319 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -3.255 | 100 | 0.12064 | 12.0639
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.2128 | north | 1 | N | N | Nnorth | Nnorth | 1 | -32.8144 | 0 | -0.059615 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.2128 | north | 1 | N | N | Nnorth | Nnorth | 1 | -33.1974 | 0 | -0.059615 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.2128 | north | 1 | N | N | Nnorth | Nnorth | 1 | -33.1974 | 0 | -0.059615 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.2128 | north | 1 | N | N | Nnorth | Nnorth | 1 | -80.8655 | 0 | -0.059615 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.038449 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 21.8775 | 569 | -0.10761 | -61.2315
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.038449 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 22.3389 | 581 | -0.10761 | -62.5228
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.009162 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.16492 | 0 | -0.1369 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.009162 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.16492 | 0 | -0.1369 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.009162 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13743 | 0 | -0.1369 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.007727 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10586 | 0 | -0.13833 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.001444 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.040432 | 0 | -0.14462 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.001444 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.041876 | 0 | -0.14462 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001077 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.45449 | 422 | -0.14498 | -61.1834
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14606 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14606 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -2.9e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.000522 | 0 | -0.14609 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -2.9e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.000522 | 0 | -0.14609 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.002538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.08883 | 0 | -0.1486 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.002538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.086292 | 0 | -0.1486 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.002538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.08883 | 0 | -0.1486 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.002962 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.097746 | 0 | -0.14902 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.002962 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.07405 | 0 | -0.14902 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.002962 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14902 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.003457 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.14519 | 42 | -0.14952 | -6.2798
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.003457 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.15211 | 44 | -0.14952 | -6.5788
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.003457 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.15211 | 44 | -0.14952 | -6.5788
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.003457 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16248 | 47 | -0.14952 | -7.0274
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.004604 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.036832 | 0 | -0.15067 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.004604 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.036832 | 0 | -0.15067 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.00473 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4663 | 310 | -0.15079 | -46.7453
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.00473 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.9535 | 413 | -0.15079 | -62.2769
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.32756 | 49 | -0.15275 | -7.4846
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.30751 | 46 | -0.15275 | -7.0263
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.30751 | 46 | -0.15275 | -7.0263
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3142 | 47 | -0.15275 | -7.1791
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.006685 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0295 | 154 | -0.15275 | -23.523
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.006685 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.98938 | 148 | -0.15275 | -22.6065
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.32088 | 48 | -0.15275 | -7.3318
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.32088 | 48 | -0.15275 | -7.3318
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.012948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.9746 | 152.5 | -0.15901 | -24.2489
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.012948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.9357 | 149.5 | -0.15901 | -23.7719
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.012948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0117 | 232.6 | -0.15901 | -36.9856
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.013228 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.7461 | 132 | -0.15929 | -21.0262
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.013228 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.7726 | 134 | -0.15929 | -21.3448
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.013228 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.2726 | 323 | -0.15929 | -51.4505
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.015275 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.4135 | 158 | -0.16134 | -25.4912
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.015275 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.444 | 160 | -0.16134 | -25.8138
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.015275 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6731 | 175 | -0.16134 | -28.2339
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.015751 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.094506 | 0 | -0.16181 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.018726 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.16479 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.025314 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15188 | 0 | -0.17138 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.02899 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4495 | 50 | -0.17505 | -8.7526
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.02899 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4495 | 50 | -0.17505 | -8.7526
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.02899 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4495 | 50 | -0.17505 | -8.7526
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.02899 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4495 | 50 | -0.17505 | -8.7526
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.030817 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8999 | 223.9 | -0.17688 | -39.6031
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.030817 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9338 | 225 | -0.17688 | -39.7976
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.030817 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9215 | 224.6 | -0.17688 | -39.7269
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.030817 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9862 | 226.7 | -0.17688 | -40.0983
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.032131 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.7645 | 584 | -0.17819 | -104.0644
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.032131 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -19.1179 | 595 | -0.17819 | -106.0245
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.032264 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.9703 | 433 | -0.17833 | -77.2149
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7107 | 114 | -0.17861 | -20.3617
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.2261 | 222 | -0.17861 | -39.6517
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.9892 | 184 | -0.17861 | -32.8645
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.2912 | 224 | -0.17861 | -40.009
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7433 | 115 | -0.17861 | -20.5403
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.034492 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.082781 | 0 | -0.18055 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.034492 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.082781 | 0 | -0.18055 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.034492 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.096578 | 0 | -0.18055 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.03535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.0197 | 142 | -0.18141 | -25.7604
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.03535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.1258 | 145 | -0.18141 | -26.3047
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.03535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3379 | 151 | -0.18141 | -27.3931
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.03535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.2515 | 290 | -0.18141 | -52.6093
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.035876 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1435 | 0 | -0.18194 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.036933 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.088639 | 0 | -0.18299 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.036933 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.088639 | 0 | -0.18299 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8263 | 147 | -0.1857 | -27.2974
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4696 | 138 | -0.1857 | -25.6261
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.5489 | 140 | -0.1857 | -25.9975
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8263 | 147 | -0.1857 | -27.2974
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.2136 | 182 | -0.1857 | -33.7968
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.8477 | 198 | -0.1857 | -36.7679
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.040631 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.5368 | 407 | -0.18669 | -75.9838
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.040675 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.3592 | 58 | -0.18674 | -10.8307
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.040675 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.6201 | 89 | -0.18674 | -16.6195
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.040675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7897 | 44 | -0.18674 | -8.2164
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.040675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7897 | 44 | -0.18674 | -8.2164
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.040675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.749 | 43 | -0.18674 | -8.0297
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.040675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8304 | 45 | -0.18674 | -8.4031
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.040677 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.7589 | 412 | -0.18674 | -76.9362
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.040677 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.2708 | 400 | -0.18674 | -74.6954
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.040695 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -17.2547 | 424 | -0.18676 | -79.1847
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.040695 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -17.2954 | 425 | -0.18676 | -79.3715
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.040822 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.5318 | 209 | -0.18688 | -39.0586
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.040822 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.8176 | 216 | -0.18688 | -40.3668
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.040822 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8778 | 46 | -0.18688 | -8.5966
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.040822 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9186 | 47 | -0.18688 | -8.7835
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.040822 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8778 | 46 | -0.18688 | -8.5966
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.040822 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8778 | 46 | -0.18688 | -8.5966
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.040851 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18691 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.040851 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18691 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.040851 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18691 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.041854 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.4874 | 155 | -0.18792 | -29.1269
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.041854 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1152 | 170 | -0.18792 | -31.9456
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.041854 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.4874 | 155 | -0.18792 | -29.1269
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.042087 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0101 | 24 | -0.18815 | -4.5156
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.042087 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.0101 | 24 | -0.18815 | -4.5156
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.042087 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.968 | 23 | -0.18815 | -4.3274
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.042766 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -23.3502 | 546 | -0.18883 | -103.0998
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.042766 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -32.0745 | 750 | -0.18883 | -141.6206
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.045118 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54142 | 0 | -0.19118 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.048383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.8383 | 100 | -0.19444 | -19.4444
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.048383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.8383 | 100 | -0.19444 | -19.4444
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.048383 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19444 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.048383 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19444 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.048383 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19444 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.048383 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19444 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.048387 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19445 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.048656 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -19.2678 | 396 | -0.19472 | -77.1081
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.054289 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20035 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.057534 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.2036 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.058225 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6987 | 0 | -0.20429 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.058225 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.64048 | 0 | -0.20429 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.058225 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6987 | 0 | -0.20429 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.060431 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20649 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.060621 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -38.1306 | 629 | -0.20668 | -130.0033
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.06234 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.1328 | 146.5 | -0.2084 | -30.5308
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.06234 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.2201 | 147.9 | -0.2084 | -30.8226
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.06234 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7848 | 173 | -0.2084 | -36.0534
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.063016 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.0443 | 207 | -0.20908 | -43.279
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.063016 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6556 | 216.7 | -0.20908 | -45.3071
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.063016 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.2499 | 242 | -0.20908 | -50.5967
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.063021 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.075 | 144 | -0.20908 | -30.1079
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.063021 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.075 | 144 | -0.20908 | -30.1079
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.063021 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7766 | 171 | -0.20908 | -35.7531
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.063504 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20957 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.063504 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.4132 | 38 | -0.20957 | -7.9635
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.063504 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2256 | 19.3 | -0.20957 | -4.0446
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.063504 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.95256 | 15 | -0.20957 | -3.1435
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.063504 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.9847 | 47 | -0.20957 | -9.8496
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.9866 | 94 | -0.20975 | -19.7164
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6112 | 41 | -0.20975 | -8.5997
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4201 | 38 | -0.20975 | -7.9704
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2101 | 19 | -0.20975 | -3.9852
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.9866 | 94 | -0.20975 | -19.7164
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2927 | 36 | -0.20975 | -7.5509
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.7385 | 43 | -0.20975 | -9.0192
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4011 | 22 | -0.20975 | -4.6145
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -9.4257 | 148 | -0.20975 | -31.0428
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1843 | 50 | -0.20975 | -10.4874
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5028 | 55 | -0.20975 | -11.5362
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1843 | 50 | -0.20975 | -10.4874
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.06399 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8557 | 0 | -0.21005 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.064636 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.4562 | 0 | -0.2107 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.064675 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.4577 | 0 | -0.21074 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.064783 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6196 | 0 | -0.21084 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.064783 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6196 | 0 | -0.21084 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.064854 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -21.6612 | 334 | -0.21092 | -70.4458
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.064854 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.0504 | 340 | -0.21092 | -71.7112
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.064854 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.6737 | 180 | -0.21092 | -37.9648
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.064854 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.6737 | 180 | -0.21092 | -37.9648
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.065108 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7194 | 180 | -0.21117 | -38.0105
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.065134 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.6594 | 0 | -0.2112 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.065134 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.6789 | 0 | -0.2112 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.065134 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.9655 | 0 | -0.2112 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.06515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.8904 | 336 | -0.21121 | -70.967
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.06515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.727 | 180 | -0.21121 | -38.0181
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6492 | 25 | -0.21203 | -5.3007
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6492 | 25 | -0.21203 | -5.3007
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6492 | 25 | -0.21203 | -5.3007
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0555 | 16 | -0.21203 | -3.3925
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6492 | 25 | -0.21203 | -5.3007
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6492 | 25 | -0.21203 | -5.3007
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6492 | 25 | -0.21203 | -5.3007
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.98952 | 15 | -0.21203 | -3.1804
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5094 | 0 | -0.21258 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.1768 | 0 | -0.21258 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.6515 | 0 | -0.21258 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.6447 | 0 | -0.21258 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.7777 | 0 | -0.21258 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.4474 | 0 | -0.21258 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.066515 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.79818 | 0 | -0.21258 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.06681 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.6206 | 144 | -0.21287 | -30.6535
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.06681 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5603 | 188 | -0.21287 | -40.0198
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.068081 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2475 | 47.7 | -0.21414 | -10.2146
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.068081 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.5394 | 37.3 | -0.21414 | -7.9875
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.068081 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1317 | 46 | -0.21414 | -9.8506
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.068081 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2679 | 48 | -0.21414 | -10.2788
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.068116 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9725 | 0 | -0.21418 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.068759 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5127 | 22 | -0.21482 | -4.726
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.068759 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.75635 | 11 | -0.21482 | -2.363
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.068759 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.75635 | 11 | -0.21482 | -2.363
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.070343 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0551 | 0 | -0.2164 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.070343 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6179 | 0 | -0.2164 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.071133 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.56906 | 0 | -0.21719 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.006 | 0 | -0.2177 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5015 | 0 | -0.2177 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7941 | 0 | -0.2177 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0746 | 0 | -0.2177 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5015 | 0 | -0.2177 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0746 | 0 | -0.2177 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7941 | 0 | -0.2177 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7941 | 0 | -0.2177 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.07491 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5957 | 0 | -0.22097 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9959 | 0 | -0.22196 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.1477 | 0 | -0.22196 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9959 | 0 | -0.22196 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0718 | 0 | -0.22196 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9504 | 0 | -0.22196 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8975 | 0 | -0.22196 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4913 | 0 | -0.22196 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1251 | 0 | -0.22196 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3092 | 0 | -0.22196 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6165 | 0 | -0.22196 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.1113 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -148.3562 | 0 | -0.25736 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.1113 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -147.7998 | 0 | -0.25736 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5074 | 76 | -0.258 | -19.6081
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5074 | 76 | -0.258 | -19.6081
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.7537 | 105 | -0.258 | -27.0902
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2836 | 74 | -0.258 | -19.0921
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2836 | 74 | -0.258 | -19.0921
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.4179 | 102 | -0.258 | -26.3161
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.11579 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.6425 | 66 | -0.26186 | -17.2825
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.9745 | 0 | -0.27468 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.1835 | 0 | -0.27468 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.7879 | 0 | -0.27468 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.9907 | 0 | -0.27468 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0614 | 0 | -0.27468 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.3186 | 0 | -0.27468 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.431 | 0 | -0.27468 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3152 | 0 | -0.27468 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.0904 | 0 | -0.27468 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.0035 | 0 | -0.27468 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.1031 | 0 | -0.27468 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.2607 | 0 | -0.27468 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.3346 | 0 | -0.27468 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.9907 | 0 | -0.27468 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.4762 | 0 | -0.27468 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.248 | 0 | -0.27468 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.7752 | 0 | -0.27468 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.2897 | 0 | -0.27468 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.2897 | 0 | -0.27468 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -21.9942 | 0 | -0.27468 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.13172 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3521 | 0 | -0.27778 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.13172 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3172 | 0 | -0.27778 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.13419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.8948 | 0 | -0.28025 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.13419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.8948 | 0 | -0.28025 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.13419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.9683 | 0 | -0.28025 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.13419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.6935 | 0 | -0.28025 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.14302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5931 | 0 | -0.28908 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.14339 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -93.3488 | 651 | -0.28945 | -188.4348
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.14339 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -80.8737 | 564 | -0.28945 | -163.2523
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.14339 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -86.0358 | 600 | -0.28945 | -173.6727
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.14347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.3851 | 0 | -0.28953 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.14347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.3851 | 0 | -0.28953 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.14347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -35.1494 | 0 | -0.28953 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.14434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7631 | 0 | -0.2904 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.14482 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -23.3157 | 161 | -0.29088 | -46.8316
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.14482 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -24.0398 | 166 | -0.29088 | -48.286
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.14482 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -35.9149 | 248 | -0.29088 | -72.1381
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.14482 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -79.0706 | 546 | -0.29088 | -158.8202
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.14482 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -93.118 | 0 | -0.29088 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.14482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8826 | 13 | -0.29088 | -3.7814
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.14938 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.9828 | 0 | -0.29544 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.14938 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.8774 | 0 | -0.29544 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.14938 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.3413 | 0 | -0.29544 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.14938 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.2368 | 0 | -0.29544 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.14938 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7802 | 0 | -0.29544 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.14938 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4814 | 0 | -0.29544 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.1494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.5778 | 0 | -0.29547 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.1494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.9652 | 0 | -0.29547 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.1494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.9184 | 0 | -0.29547 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.8887 | 0 | -0.29547 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.9335 | 0 | -0.29547 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.7542 | 0 | -0.29547 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.3428 | 0 | -0.29547 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -36.4546 | 0 | -0.29547 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.1494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9762 | 0 | -0.29547 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.15133 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.5665 | 50 | -0.29739 | -14.8696
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.15278 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.29885 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.0607 | 0 | -0.30057 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.5353 | 0 | -0.30057 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.4426 | 0 | -0.30057 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.421 | 0 | -0.30057 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8851 | 0 | -0.30057 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.15519 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.0874 | 0 | -0.30125 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.15519 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.3114 | 0 | -0.30125 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.15519 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.0874 | 0 | -0.30125 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.15519 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.0874 | 0 | -0.30125 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.1858 | 46 | -0.30228 | -13.9047
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.1858 | 46 | -0.30228 | -13.9047
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.1858 | 46 | -0.30228 | -13.9047
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.5918 | 55 | -0.30228 | -16.6251
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.5918 | 55 | -0.30228 | -16.6251
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.4356 | 54 | -0.30228 | -16.3229
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.15645 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.2029 | 0 | -0.30251 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.15645 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.5158 | 0 | -0.30251 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.588 | 0 | -0.30285 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.6316 | 0 | -0.30285 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.6943 | 0 | -0.30285 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.6159 | 0 | -0.30285 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -42.1762 | 0 | -0.30285 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.15708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4978 | 0 | -0.30314 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.15738 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8886 | 12 | -0.30344 | -3.6413
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.15738 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.30344 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.1574 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -26.5999 | 169 | -0.30346 | -51.2843
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.15742 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -25.9743 | 165 | -0.30348 | -50.0744
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.15744 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -23.4584 | 0 | -0.3035 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.15744 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.2493 | 0 | -0.3035 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.1575 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -33.5475 | 213 | -0.30356 | -64.6586
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5516 | 0 | -0.30357 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.0809 | 0 | -0.30358 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.9549 | 0 | -0.30358 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.0107 | 0 | -0.30358 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.593 | 0 | -0.30358 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.15752 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -35.9157 | 228 | -0.30359 | -69.2177
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.15754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.3565 | 0 | -0.3036 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.15754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.9852 | 0 | -0.3036 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.15754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.7332 | 0 | -0.3036 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.15796 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.2152 | 0 | -0.30402 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.15796 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.3732 | 0 | -0.30402 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.15796 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1605 | 0 | -0.30402 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.15796 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7388 | 0 | -0.30402 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.15864 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.5756 | 0 | -0.30471 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.15869 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.665 | 42 | -0.30475 | -12.7996
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.15869 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.665 | 42 | -0.30475 | -12.7996
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.15869 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.0302 | 38 | -0.30475 | -11.5806
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.15869 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.0302 | 38 | -0.30475 | -11.5806
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.15887 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -27.4845 | 0 | -0.30493 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.15887 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.4474 | 0 | -0.30493 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -16.6365 | 104 | -0.30603 | -31.8269
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -16.6365 | 104 | -0.30603 | -31.8269
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.6382 | 54 | -0.30603 | -16.5255
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.4782 | 53 | -0.30603 | -16.2195
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.6382 | 54 | -0.30603 | -16.5255
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.1181 | 57 | -0.30603 | -17.4436
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.6382 | 54 | -0.30603 | -16.5255
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.6382 | 54 | -0.30603 | -16.5255
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.278 | 58 | -0.30603 | -17.7496
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.278 | 58 | -0.30603 | -17.7496
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.16036 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -117.8668 | 735 | -0.30642 | -225.222
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4618 | 0 | -0.3067 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5743 | 0 | -0.3067 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.253 | 0 | -0.3067 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.3735 | 0 | -0.3067 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8434 | 0 | -0.3067 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2771 | 0 | -0.3067 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1968 | 0 | -0.3067 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6225 | 0 | -0.3067 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8916 | 0 | -0.3067 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.7188 | 0 | -0.3067 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -23.775 | 0 | -0.3067 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.16101 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9322 | 12 | -0.30707 | -3.6849
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.16145 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.80724 | 0 | -0.30751 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.16145 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3904 | 0 | -0.30751 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.4948 | 0 | -0.30752 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6562 | 0 | -0.30752 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.3021 | 0 | -0.30752 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.1719 | 0 | -0.30752 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.0104 | 0 | -0.30752 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -16.7916 | 0 | -0.30752 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.526 | 0 | -0.30752 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.16148 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -1.9377 | 12 | -0.30754 | -3.6904
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.16151 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -119.999 | 743 | -0.30757 | -228.5226
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.16172 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.39 | 0 | -0.30778 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.16185 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -27.8382 | 172 | -0.30791 | -52.9608
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.16185 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -27.8382 | 172 | -0.30791 | -52.9608
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.16185 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -27.8382 | 172 | -0.30791 | -52.9608
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.16266 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.4807 | 0 | -0.30872 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.16266 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.253 | 0 | -0.30872 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.16266 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -25.8464 | 0 | -0.30872 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.16266 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -43.7875 | 0 | -0.30872 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.16295 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -64.8521 | 398 | -0.30901 | -122.9846
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.1527 | 56 | -0.3095 | -17.3321
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.643 | 59 | -0.3095 | -18.2606
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.1527 | 56 | -0.3095 | -17.3321
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.1527 | 56 | -0.3095 | -17.3321
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.643 | 59 | -0.3095 | -18.2606
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.1527 | 56 | -0.3095 | -17.3321
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.1682 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.0977 | 0 | -0.31426 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.1682 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.2384 | 0 | -0.31426 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.1682 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.902 | 0 | -0.31426 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.1682 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.902 | 0 | -0.31426 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.1682 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -27.2476 | 0 | -0.31426 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | 0 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.1682 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.0977 | 0 | -0.31426 | 0 | 0 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.1682 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.2384 | 0 | -0.31426 | 0 | 0 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.1682 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.902 | 0 | -0.31426 | 0 | 0 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.1682 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.902 | 0 | -0.31426 | 0 | 0 | 0 | Weighted Shift Factors
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.1682 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -27.2476 | 0 | -0.31426 | 0 | 0 | 0 | North | 0.14606
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.1527 | 56 | -0.3095 | -17.3321 | 56 | 17.3321 | Houston | -0.15319
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.643 | 59 | -0.3095 | -18.2606 | 115 | 35.5928 |  | 0.29925
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.1527 | 56 | -0.3095 | -17.3321 | 171 | 52.9249
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.1527 | 56 | -0.3095 | -17.3321 | 227 | 70.2571 | Line Rating | 2080
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.643 | 59 | -0.3095 | -18.2606 | 286 | 88.5177 | Conc Gen | 3997
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.16344 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.1527 | 56 | -0.3095 | -17.3321 | 342 | 105.8498 | Weighted Imp. | 1226.7005
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.16295 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -64.8521 | 398 | -0.30901 | -122.9846 | 740 | 228.8344 | PTDF | 0.30691
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.16266 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.4807 | 0 | -0.30872 | 0 | 740 | 228.8344
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.16266 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -26.253 | 0 | -0.30872 | 0 | 740 | 228.8344 | Concentration | 1.0256
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.16266 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -25.8464 | 0 | -0.30872 | 0 | 740 | 228.8344
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.16266 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -43.7875 | 0 | -0.30872 | 0 | 740 | 228.8344
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.16185 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -27.8382 | 172 | -0.30791 | -52.9608 | 912 | 281.7952
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.16185 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -27.8382 | 172 | -0.30791 | -52.9608 | 1084 | 334.7559
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.16185 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -27.8382 | 172 | -0.30791 | -52.9608 | 1256 | 387.7167
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.16172 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.39 | 0 | -0.30778 | 0 | 1256 | 387.7167
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.16151 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -119.999 | 743 | -0.30757 | -228.5226 | 1999 | 616.2393
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.16148 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -1.9377 | 0 | -0.30754 | 0 | 1999 | 616.2393
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.4948 | 0 | -0.30752 | 0 | 1999 | 616.2393
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6562 | 0 | -0.30752 | 0 | 1999 | 616.2393
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.3021 | 0 | -0.30752 | 0 | 1999 | 616.2393
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.1719 | 0 | -0.30752 | 0 | 1999 | 616.2393
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.0104 | 0 | -0.30752 | 0 | 1999 | 616.2393
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -16.7916 | 0 | -0.30752 | 0 | 1999 | 616.2393
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.16146 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.526 | 0 | -0.30752 | 0 | 1999 | 616.2393
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.16145 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.80724 | 0 | -0.30751 | 0 | 1999 | 616.2393
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.16145 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3904 | 0 | -0.30751 | 0 | 1999 | 616.2393
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.16101 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9322 | 12 | -0.30707 | -3.6849 | 2011 | 619.9242
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4618 | 0 | -0.3067 | 0 | 2011 | 619.9242
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5743 | 0 | -0.3067 | 0 | 2011 | 619.9242
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.253 | 0 | -0.3067 | 0 | 2011 | 619.9242
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.3735 | 0 | -0.3067 | 0 | 2011 | 619.9242
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8434 | 0 | -0.3067 | 0 | 2011 | 619.9242
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2771 | 0 | -0.3067 | 0 | 2011 | 619.9242
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1968 | 0 | -0.3067 | 0 | 2011 | 619.9242
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6225 | 0 | -0.3067 | 0 | 2011 | 619.9242
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8916 | 0 | -0.3067 | 0 | 2011 | 619.9242
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.7188 | 0 | -0.3067 | 0 | 2011 | 619.9242
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.16064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -23.775 | 0 | -0.3067 | 0 | 2011 | 619.9242
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.16036 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -117.8668 | 735 | -0.30642 | -225.222 | 2746 | 845.1462
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -16.6365 | 104 | -0.30603 | -31.8269 | 2850 | 876.973
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -16.6365 | 104 | -0.30603 | -31.8269 | 2954 | 908.7999
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.6382 | 54 | -0.30603 | -16.5255 | 3008 | 925.3253
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.4782 | 53 | -0.30603 | -16.2195 | 3061 | 941.5448
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.6382 | 54 | -0.30603 | -16.5255 | 3115 | 958.0703
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.1181 | 57 | -0.30603 | -17.4436 | 3172 | 975.5138
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.6382 | 54 | -0.30603 | -16.5255 | 3226 | 992.0393
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.6382 | 54 | -0.30603 | -16.5255 | 3280 | 1008.5648
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.278 | 58 | -0.30603 | -17.7496 | 3338 | 1026.3144
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.15997 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.278 | 58 | -0.30603 | -17.7496 | 3396 | 1044.064
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.15887 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -27.4845 | 0 | -0.30493 | 0 | 3396 | 1044.064
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.15887 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.4474 | 0 | -0.30493 | 0 | 3396 | 1044.064
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.15869 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.665 | 42 | -0.30475 | -12.7996 | 3438 | 1056.8635
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.15869 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.665 | 42 | -0.30475 | -12.7996 | 3480 | 1069.6631
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.15869 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.0302 | 38 | -0.30475 | -11.5806 | 3518 | 1081.2437
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.15869 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.0302 | 38 | -0.30475 | -11.5806 | 3556 | 1092.8242
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.15864 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.5756 | 0 | -0.30471 | 0 | 3556 | 1092.8242
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.15796 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.2152 | 0 | -0.30402 | 0 | 3556 | 1092.8242
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.15796 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.3732 | 0 | -0.30402 | 0 | 3556 | 1092.8242
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.15796 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1605 | 0 | -0.30402 | 0 | 3556 | 1092.8242
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.15796 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7388 | 0 | -0.30402 | 0 | 3556 | 1092.8242
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.15754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -28.3565 | 0 | -0.3036 | 0 | 3556 | 1092.8242
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.15754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.9852 | 0 | -0.3036 | 0 | 3556 | 1092.8242
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.15754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.7332 | 0 | -0.3036 | 0 | 3556 | 1092.8242
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.15752 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -35.9157 | 228 | -0.30359 | -69.2177 | 3784 | 1162.0419
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.0809 | 0 | -0.30358 | 0 | 3784 | 1162.0419
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.9549 | 0 | -0.30358 | 0 | 3784 | 1162.0419
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.0107 | 0 | -0.30358 | 0 | 3784 | 1162.0419
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.593 | 0 | -0.30358 | 0 | 3784 | 1162.0419
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.15751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5516 | 0 | -0.30357 | 0 | 3784 | 1162.0419
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.1575 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -33.5475 | 213 | -0.30356 | -64.6586 | 3997 | 1226.7005
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.15744 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -23.4584 | 0 | -0.3035 | 0 | 3997 | 1226.7005
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.15744 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.2493 | 0 | -0.3035 | 0 | 3997 | 1226.7005
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.15742 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -25.9743 | 165 | -0.30348 | -50.0744
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.1574 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -26.5999 | 169 | -0.30346 | -51.2843
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.15738 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8886 | 12 | -0.30344 | -3.6413
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.15738 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.30344 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.15708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4978 | 0 | -0.30314 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.588 | 0 | -0.30285 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.6316 | 0 | -0.30285 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.6943 | 0 | -0.30285 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -24.6159 | 0 | -0.30285 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.15679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -42.1762 | 0 | -0.30285 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.15645 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.2029 | 0 | -0.30251 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.15645 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.5158 | 0 | -0.30251 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.1858 | 46 | -0.30228 | -13.9047
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.1858 | 46 | -0.30228 | -13.9047
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.1858 | 46 | -0.30228 | -13.9047
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.5918 | 55 | -0.30228 | -16.6251
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.5918 | 55 | -0.30228 | -16.6251
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.15621 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.4356 | 54 | -0.30228 | -16.3229
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.15519 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.0874 | 0 | -0.30125 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.15519 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.3114 | 0 | -0.30125 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.15519 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.0874 | 0 | -0.30125 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.15519 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.0874 | 0 | -0.30125 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.0607 | 0 | -0.30057 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.5353 | 0 | -0.30057 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.4426 | 0 | -0.30057 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.421 | 0 | -0.30057 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.15451 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8851 | 0 | -0.30057 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.15278 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.29885 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.15133 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.5665 | 50 | -0.29739 | -14.8696
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.1494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.5778 | 0 | -0.29547 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.1494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.9652 | 0 | -0.29547 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.1494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.9184 | 0 | -0.29547 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.8887 | 0 | -0.29547 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.9335 | 0 | -0.29547 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.7542 | 0 | -0.29547 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.3428 | 0 | -0.29547 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.1494 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -36.4546 | 0 | -0.29547 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.1494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9762 | 0 | -0.29547 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.14938 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7802 | 0 | -0.29544 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.14938 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4814 | 0 | -0.29544 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.14938 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.9828 | 0 | -0.29544 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.14938 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.8774 | 0 | -0.29544 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.14938 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.3413 | 0 | -0.29544 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.14938 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.2368 | 0 | -0.29544 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.14482 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -23.3157 | 161 | -0.29088 | -46.8316
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.14482 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -24.0398 | 166 | -0.29088 | -48.286
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.14482 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -35.9149 | 248 | -0.29088 | -72.1381
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.14482 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -79.0706 | 546 | -0.29088 | -158.8202
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.14482 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -93.118 | 0 | -0.29088 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.14482 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8826 | 13 | -0.29088 | -3.7814
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.14434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7631 | 0 | -0.2904 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.14347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.3851 | 0 | -0.28953 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.14347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -23.3851 | 0 | -0.28953 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.14347 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -35.1494 | 0 | -0.28953 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.14339 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -93.3488 | 0 | -0.28945 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.14339 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -80.8737 | 0 | -0.28945 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.14339 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -86.0358 | 0 | -0.28945 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.14302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5931 | 0 | -0.28908 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.13419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.8948 | 0 | -0.28025 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.13419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.8948 | 0 | -0.28025 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.13419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.9683 | 0 | -0.28025 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.13419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.6935 | 0 | -0.28025 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.13172 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.3521 | 0 | -0.27778 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.13172 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3172 | 0 | -0.27778 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.9745 | 0 | -0.27468 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.1835 | 0 | -0.27468 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.7879 | 0 | -0.27468 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.9907 | 0 | -0.27468 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0614 | 0 | -0.27468 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.3186 | 0 | -0.27468 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.431 | 0 | -0.27468 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3152 | 0 | -0.27468 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.0904 | 0 | -0.27468 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.0035 | 0 | -0.27468 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.1031 | 0 | -0.27468 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.2607 | 0 | -0.27468 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.3346 | 0 | -0.27468 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.9907 | 0 | -0.27468 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.4762 | 0 | -0.27468 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.248 | 0 | -0.27468 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.7752 | 0 | -0.27468 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.2897 | 0 | -0.27468 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.2897 | 0 | -0.27468 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.12862 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -21.9942 | 0 | -0.27468 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.11579 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.6425 | 66 | -0.26186 | -17.2825
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5074 | 76 | -0.258 | -19.6081
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.5074 | 76 | -0.258 | -19.6081
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.7537 | 105 | -0.258 | -27.0902
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2836 | 74 | -0.258 | -19.0921
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.2836 | 74 | -0.258 | -19.0921
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.11194 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -11.4179 | 102 | -0.258 | -26.3161
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.1113 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -148.3562 | 0 | -0.25736 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.1113 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -147.7998 | 0 | -0.25736 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9959 | 0 | -0.22196 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.1477 | 0 | -0.22196 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9959 | 0 | -0.22196 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.0718 | 0 | -0.22196 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9504 | 0 | -0.22196 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8975 | 0 | -0.22196 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4913 | 0 | -0.22196 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1251 | 0 | -0.22196 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3092 | 0 | -0.22196 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.075898 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6165 | 0 | -0.22196 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.07491 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5957 | 0 | -0.22097 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.006 | 0 | -0.2177 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5015 | 0 | -0.2177 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7941 | 0 | -0.2177 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0746 | 0 | -0.2177 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5015 | 0 | -0.2177 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0746 | 0 | -0.2177 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7941 | 0 | -0.2177 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.071643 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7941 | 0 | -0.2177 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.071133 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.56906 | 0 | -0.21719 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.070343 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0551 | 0 | -0.2164 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.070343 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6179 | 0 | -0.2164 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.068759 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5127 | 22 | -0.21482 | -4.726
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.068759 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.75635 | 11 | -0.21482 | -2.363
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.068759 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.75635 | 11 | -0.21482 | -2.363
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.068116 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9725 | 0 | -0.21418 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.068081 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2475 | 47.7 | -0.21414 | -10.2146
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.068081 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.5394 | 37.3 | -0.21414 | -7.9875
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.068081 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1317 | 46 | -0.21414 | -9.8506
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.068081 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2679 | 48 | -0.21414 | -10.2788
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.06681 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.6206 | 144 | -0.21287 | -30.6535
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.06681 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5603 | 188 | -0.21287 | -40.0198
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5094 | 0 | -0.21258 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.1768 | 0 | -0.21258 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.6515 | 0 | -0.21258 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.6447 | 0 | -0.21258 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.7777 | 0 | -0.21258 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.066515 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.4474 | 0 | -0.21258 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.066515 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.79818 | 0 | -0.21258 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6492 | 0 | -0.21203 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6492 | 0 | -0.21203 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6492 | 0 | -0.21203 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0555 | 0 | -0.21203 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6492 | 0 | -0.21203 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6492 | 0 | -0.21203 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6492 | 0 | -0.21203 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.065968 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.98952 | 0 | -0.21203 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.06515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.8904 | 336 | -0.21121 | -70.967
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.06515 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.727 | 180 | -0.21121 | -38.0181
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.065134 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.6594 | 0 | -0.2112 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.065134 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.6789 | 0 | -0.2112 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.065134 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.9655 | 0 | -0.2112 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.065108 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7194 | 180 | -0.21117 | -38.0105
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.064854 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -21.6612 | 334 | -0.21092 | -70.4458
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.064854 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.0504 | 340 | -0.21092 | -71.7112
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.064854 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.6737 | 180 | -0.21092 | -37.9648
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.064854 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.6737 | 180 | -0.21092 | -37.9648
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.064783 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6196 | 0 | -0.21084 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.064783 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6196 | 0 | -0.21084 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.064675 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.4577 | 0 | -0.21074 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.064636 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.4562 | 0 | -0.2107 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.06399 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8557 | 0 | -0.21005 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.9866 | 0 | -0.20975 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6112 | 0 | -0.20975 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4201 | 0 | -0.20975 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2101 | 0 | -0.20975 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.9866 | 0 | -0.20975 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2927 | 0 | -0.20975 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.7385 | 0 | -0.20975 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4011 | 0 | -0.20975 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -9.4257 | 0 | -0.20975 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1843 | 0 | -0.20975 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.5028 | 0 | -0.20975 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.063687 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1843 | 0 | -0.20975 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.063504 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.4132 | 38 | -0.20957 | -7.9635
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.063504 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2256 | 19.3 | -0.20957 | -4.0446
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.063504 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.95256 | 15 | -0.20957 | -3.1435
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.063504 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.9847 | 47 | -0.20957 | -9.8496
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.063504 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20957 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.063021 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.075 | 144 | -0.20908 | -30.1079
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.063021 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.075 | 144 | -0.20908 | -30.1079
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.063021 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7766 | 171 | -0.20908 | -35.7531
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.063016 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.0443 | 207 | -0.20908 | -43.279
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.063016 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6556 | 216.7 | -0.20908 | -45.3071
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.063016 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.2499 | 242 | -0.20908 | -50.5967
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.06234 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.1328 | 146.5 | -0.2084 | -30.5308
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.06234 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.2201 | 147.9 | -0.2084 | -30.8226
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.06234 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7848 | 173 | -0.2084 | -36.0534
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.060621 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -38.1306 | 0 | -0.20668 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.060431 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20649 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.058225 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6987 | 0 | -0.20429 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.058225 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.64048 | 0 | -0.20429 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.058225 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6987 | 0 | -0.20429 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.057534 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.2036 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.054289 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20035 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.048656 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -19.2678 | 0 | -0.19472 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.048387 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19445 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.048383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.8383 | 100 | -0.19444 | -19.4444
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.048383 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.8383 | 100 | -0.19444 | -19.4444
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.048383 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19444 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.048383 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19444 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.048383 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19444 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.048383 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19444 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.045118 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54142 | 0 | -0.19118 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.042766 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -23.3502 | 0 | -0.18883 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.042766 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -32.0745 | 0 | -0.18883 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.042087 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0101 | 24 | -0.18815 | -4.5156
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.042087 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.0101 | 24 | -0.18815 | -4.5156
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.042087 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.968 | 23 | -0.18815 | -4.3274
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.041854 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.4874 | 155 | -0.18792 | -29.1269
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.041854 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1152 | 170 | -0.18792 | -31.9456
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.041854 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.4874 | 155 | -0.18792 | -29.1269
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.040851 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18691 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.040851 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18691 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.040851 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.18691 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.040822 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.5318 | 209 | -0.18688 | -39.0586
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.040822 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.8176 | 216 | -0.18688 | -40.3668
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.040822 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8778 | 46 | -0.18688 | -8.5966
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.040822 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9186 | 47 | -0.18688 | -8.7835
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.040822 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8778 | 46 | -0.18688 | -8.5966
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.040822 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8778 | 46 | -0.18688 | -8.5966
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.040695 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -17.2547 | 0 | -0.18676 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.040695 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -17.2954 | 0 | -0.18676 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.040677 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.7589 | 412 | -0.18674 | -76.9362
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.040677 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.2708 | 400 | -0.18674 | -74.6954
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.040675 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.3592 | 58 | -0.18674 | -10.8307
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.040675 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.6201 | 89 | -0.18674 | -16.6195
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.040675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7897 | 44 | -0.18674 | -8.2164
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.040675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7897 | 44 | -0.18674 | -8.2164
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.040675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.749 | 43 | -0.18674 | -8.0297
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.040675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.8304 | 45 | -0.18674 | -8.4031
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.040631 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.5368 | 407 | -0.18669 | -75.9838
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.040624 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.34124 | 8.4 | -0.18669 | -1.5682
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8263 | 147 | -0.1857 | -27.2974
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4696 | 138 | -0.1857 | -25.6261
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.5489 | 140 | -0.1857 | -25.9975
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8263 | 147 | -0.1857 | -27.2974
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.2136 | 182 | -0.1857 | -33.7968
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.039635 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.8477 | 198 | -0.1857 | -36.7679
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.036933 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.088639 | 0 | -0.18299 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.036933 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.088639 | 0 | -0.18299 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.035876 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1435 | 0 | -0.18194 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.03535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.0197 | 142 | -0.18141 | -25.7604
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.03535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.1258 | 145 | -0.18141 | -26.3047
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.03535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3379 | 151 | -0.18141 | -27.3931
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.03535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.2515 | 290 | -0.18141 | -52.6093
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.034492 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.082781 | 0 | -0.18055 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.034492 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.082781 | 0 | -0.18055 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.034492 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.096578 | 0 | -0.18055 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7107 | 0 | -0.17861 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.2261 | 0 | -0.17861 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.9892 | 0 | -0.17861 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.2912 | 0 | -0.17861 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7433 | 0 | -0.17861 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.032264 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.9703 | 0 | -0.17833 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.032131 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -18.7645 | 0 | -0.17819 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.032131 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -19.1179 | 0 | -0.17819 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.030817 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.8999 | 223.9 | -0.17688 | -39.6031
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.030817 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9338 | 225 | -0.17688 | -39.7976
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.030817 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9215 | 224.6 | -0.17688 | -39.7269
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.030817 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9862 | 226.7 | -0.17688 | -40.0983
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.02899 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4495 | 50 | -0.17505 | -8.7526
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.02899 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4495 | 50 | -0.17505 | -8.7526
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.02899 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4495 | 50 | -0.17505 | -8.7526
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.02899 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4495 | 50 | -0.17505 | -8.7526
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.025314 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15188 | 0 | -0.17138 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.018726 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.16479 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.015751 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.094506 | 0 | -0.16181 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.015275 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.4135 | 158 | -0.16134 | -25.4912
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.015275 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.444 | 160 | -0.16134 | -25.8138
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.015275 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6731 | 175 | -0.16134 | -28.2339
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.013228 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.7461 | 132 | -0.15929 | -21.0262
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.013228 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.7726 | 134 | -0.15929 | -21.3448
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.013228 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.2726 | 323 | -0.15929 | -51.4505
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.012948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.9746 | 152.5 | -0.15901 | -24.2489
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.012948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.9357 | 149.5 | -0.15901 | -23.7719
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.012948 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.0117 | 232.6 | -0.15901 | -36.9856
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.32756 | 49 | -0.15275 | -7.4846
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.30751 | 46 | -0.15275 | -7.0263
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.30751 | 46 | -0.15275 | -7.0263
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3142 | 47 | -0.15275 | -7.1791
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.006685 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0295 | 154 | -0.15275 | -23.523
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.006685 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.98938 | 148 | -0.15275 | -22.6065
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.32088 | 48 | -0.15275 | -7.3318
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.006685 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.32088 | 48 | -0.15275 | -7.3318
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.00473 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4663 | 310 | -0.15079 | -46.7453
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.00473 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.9535 | 413 | -0.15079 | -62.2769
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.004604 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.036832 | 0 | -0.15067 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.004604 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.036832 | 0 | -0.15067 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.003457 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.14519 | 42 | -0.14952 | -6.2798
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.003457 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.15211 | 44 | -0.14952 | -6.5788
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.003457 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.15211 | 44 | -0.14952 | -6.5788
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.003457 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16248 | 47 | -0.14952 | -7.0274
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.002962 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.097746 | 0 | -0.14902 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.002962 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.07405 | 0 | -0.14902 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.002962 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14902 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.002538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.08883 | 0 | -0.1486 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.002538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.086292 | 0 | -0.1486 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.002538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.08883 | 0 | -0.1486 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -2.9e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.000522 | 0 | -0.14609 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -2.9e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.000522 | 0 | -0.14609 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14606 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14606 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14606 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001077 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.45449 | 422 | -0.14498 | -61.1834
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.001444 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.040432 | 0 | -0.14462 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.001444 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.041876 | 0 | -0.14462 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.007727 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10586 | 0 | -0.13833 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.009162 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.16492 | 0 | -0.1369 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.009162 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.16492 | 0 | -0.1369 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.009162 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13743 | 0 | -0.1369 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.038449 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 21.8775 | 0 | -0.10761 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.038449 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 22.3389 | 0 | -0.10761 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.2128 | north | 1 | N | N | Nnorth | Nnorth | 1 | -32.8144 | 0 | -0.059615 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.2128 | north | 1 | N | N | Nnorth | Nnorth | 1 | -33.1974 | 0 | -0.059615 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.2128 | north | 1 | N | N | Nnorth | Nnorth | 1 | -33.1974 | 0 | -0.059615 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.2128 | north | 1 | N | N | Nnorth | Nnorth | 1 | -80.8655 | 0 | -0.059615 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.03255 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -3.255 | 0 | 0.12064 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.15319 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.15319 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.023217 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.17641 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.074678 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.2017 | 0 | 0.22787 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.082912 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.2361 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.083869 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23706 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.083869 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 66.0049 | 787 | 0.23706 | 186.565
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.08516 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23835 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.08516 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23835 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.087047 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.197 | 255 | 0.24024 | 61.2603
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.087047 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 12.97 | 149 | 0.24024 | 35.7952
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.087047 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.3182 | 153 | 0.24024 | 36.7562
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.089545 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.4317 | 150 | 0.24273 | 36.4102
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.089545 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.1636 | 80 | 0.24273 | 19.4188
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.09441 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4162 | 0 | 0.2476 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.09441 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4162 | 0 | 0.2476 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.094607 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.947 | 0 | 0.2478 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.094977 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2657 | 0 | 0.24817 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.095341 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6273 | 0 | 0.24853 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.097515 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.6273 | 0 | 0.2507 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.097515 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.6273 | 0 | 0.2507 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.09757 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8056 | 0 | 0.25076 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.097583 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8066 | 0 | 0.25077 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.097677 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3258 | 0 | 0.25087 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.097677 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8142 | 0 | 0.25087 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.097677 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9071 | 0 | 0.25087 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.098113 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.849 | 0 | 0.2513 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.098113 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.849 | 0 | 0.2513 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.099723 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.47867 | 0 | 0.25291 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.8389 | 66 | 0.25681 | 16.9494
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.7352 | 65 | 0.25681 | 16.6925
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.9425 | 67 | 0.25681 | 17.2062
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.9425 | 67 | 0.25681 | 17.2062
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.10362 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.9425 | 67 | 0.25681 | 17.2062
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.10362 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.25681 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.10362 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.25681 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.10367 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6285 | 0 | 0.25686 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.10367 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1102 | 0 | 0.25686 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.10377 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.5883 | 0 | 0.25696 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.10385 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4741 | 0 | 0.25704 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.10417 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68754 | 0 | 0.25736 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.10417 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5731 | 0 | 0.25736 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.10447 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7531 | 0 | 0.25766 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.10447 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.6186 | 0 | 0.25766 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.10447 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.4318 | 0 | 0.25766 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.10447 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.4092 | 0 | 0.25766 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 1 | 21.7944 | 208.2 | 0.25787 | 53.6884
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.875 | 142.1 | 0.25787 | 36.6432
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.8596 | 132.4 | 0.25787 | 34.1419
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.2365 | 136 | 0.25787 | 35.0702
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.388 | 147 | 0.25787 | 37.9068
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.10468 | west | 9 | Y | Y | Ywest | Ywest | 1 | 21.9828 | 210 | 0.25787 | 54.1526
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.3283 | 70 | 0.25788 | 18.0516
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.3283 | 70 | 0.25788 | 18.0516
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.7152 | 92.8 | 0.25788 | 23.9312
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.3752 | 80 | 0.25788 | 20.6304
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.3752 | 80 | 0.25788 | 20.6304
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.10469 | west | 9 | Y | Y | Ywest | Ywest | 1 | 12.0394 | 115 | 0.25788 | 29.6561
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.1047 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.705 | 0 | 0.25789 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.10472 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0737 | 0 | 0.25791 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.10474 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.5261 | 0 | 0.25793 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.10486 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.4617 | 0 | 0.25805 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.10493 | west | 8 | N | N | Nwest | Nwest | 1 | 2.7071 | 0 | 0.25812 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.10526 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6308 | 0 | 0.25845 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.10528 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6336 | 0 | 0.25847 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.10536 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6426 | 0 | 0.25854 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.10536 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.5477 | 0 | 0.25854 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.10536 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.9314 | 0 | 0.25854 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.10538 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.711 | 0 | 0.25857 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.10544 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.9787 | 0 | 0.25863 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.10544 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.9787 | 0 | 0.25863 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.10545 | west | 8 | N | N | Nwest | Nwest | 1 | 7.3813 | 0 | 0.25864 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.10545 | west | 8 | N | N | Nwest | Nwest | 1 | 7.7398 | 0 | 0.25864 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.10545 | west | 8 | N | N | Nwest | Nwest | 1 | 7.4235 | 0 | 0.25864 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.10562 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.8429 | 0 | 0.25881 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.10562 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.2362 | 0 | 0.25881 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.10562 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.1238 | 0 | 0.25881 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.10562 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.875 | 0 | 0.25881 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.9792 | 66 | 0.25893 | 17.0897
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.2964 | 69 | 0.25893 | 17.8665
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.2964 | 69 | 0.25893 | 17.8665
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.0849 | 67 | 0.25893 | 17.3486
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.0849 | 67 | 0.25893 | 17.3486
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.10575 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.8734 | 65 | 0.25893 | 16.8307
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.10579 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6645 | 0 | 0.25897 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.10583 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.9219 | 0 | 0.25902 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.10583 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6995 | 0 | 0.25902 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.10585 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.4788 | 0 | 0.25904 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.10585 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4566 | 0 | 0.25904 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.10585 | west | 7 | N | N | Nwest | Nwest | 1 | 2.6462 | 0 | 0.25904 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.10585 | west | 7 | N | N | Nwest | Nwest | 1 | 4.8372 | 0 | 0.25904 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.10585 | west | 7 | N | N | Nwest | Nwest | 1 | 4.8372 | 0 | 0.25904 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.10599 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9029 | 0 | 0.25918 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.10605 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9072 | 0 | 0.25924 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.10605 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7108 | 0 | 0.25924 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.10619 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.2731 | 0 | 0.25937 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.10619 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.2731 | 0 | 0.25937 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.10636 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.3818 | 0 | 0.25955 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9935 | 0 | 0.25968 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.448 | 0 | 0.25968 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.3766 | 0 | 0.25968 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6727 | 0 | 0.25968 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.1818 | 0 | 0.25968 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.10649 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5727 | 0 | 0.25968 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.10658 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.2763 | 0 | 0.25977 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.10658 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.483 | 0 | 0.25977 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.10658 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.5397 | 0 | 0.25977 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.10658 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9972 | 0 | 0.25977 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.10661 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.991 | 0 | 0.2598 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.10741 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4445 | 0 | 0.2606 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.10857 | west | 6 | Y | N | Ywest | Nwest | 1 | 43.4272 | 0 | 0.26176 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.10857 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.6228 | 0 | 0.26176 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.10924 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.0254 | 0 | 0.26243 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.10983 | west | 4 | Y | N | Ywest | Nwest | 1 | 71.3579 | 0 | 0.26302 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.11005 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.0336 | 73 | 0.26324 | 19.2165
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.11005 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.096 | 119 | 0.26324 | 31.3255
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.11005 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 22.5602 | 205 | 0.26324 | 53.9641
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.11005 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.2251 | 102 | 0.26324 | 26.8504
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.11005 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.5648 | 96 | 0.26324 | 25.271
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.11045 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.5563 | 168 | 0.26364 | 44.2921
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.11045 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.9409 | 90 | 0.26364 | 23.7279
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1107 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.7889 | 242 | 0.26389 | 63.8608
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.11123 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 13.3475 | 0 | 0.26442 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.11138 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 40.7647 | 366 | 0.26457 | 96.832
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.11139 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.3367 | 0 | 0.26458 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.11139 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.3367 | 0 | 0.26458 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.11142 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.7997 | 70 | 0.26461 | 18.5229
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.11142 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.6883 | 69 | 0.26461 | 18.2583
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.11142 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.6883 | 69 | 0.26461 | 18.2583
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.11142 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.5768 | 68 | 0.26461 | 17.9937
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.11152 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2305 | 20 | 0.26471 | 5.2942
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.11152 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2305 | 20 | 0.26471 | 5.2942
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.11152 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2305 | 20 | 0.26471 | 5.2942
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.11152 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.8959 | 17 | 0.26471 | 4.5001
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.11237 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0227 | 18 | 0.26556 | 4.7801
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.11237 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0227 | 18 | 0.26556 | 4.7801
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.11237 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.2701 | 38 | 0.26556 | 10.0913
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.11242 | north | 3 | N | N | Nnorth | Nnorth | 1 | 130.0734 | 0 | 0.26561 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.11242 | north | 3 | N | N | Nnorth | Nnorth | 1 | 130.1858 | 0 | 0.26561 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.11272 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.4938 | 217.3 | 0.26591 | 57.7819
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.11272 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1074 | 205 | 0.26591 | 54.5112
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.11272 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.7047 | 272.4 | 0.26591 | 72.4334
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.11281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.2694 | 224 | 0.266 | 59.5839
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.11281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.4951 | 226 | 0.266 | 60.1159
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.11281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.9157 | 212 | 0.266 | 56.3919
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.11281 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.8029 | 211 | 0.266 | 56.1259
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.11302 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26621 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.11313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.0795 | 204 | 0.26632 | 54.3302
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.11313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7401 | 201 | 0.26632 | 53.5312
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.11313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.3787 | 242 | 0.26632 | 64.4505
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.11386 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.7928 | 288 | 0.26705 | 76.9114
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.11386 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.738 | 147 | 0.26705 | 39.2568
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.11386 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.738 | 147 | 0.26705 | 39.2568
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.1142 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.7131 | 216.4 | 0.26739 | 57.8633
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.1142 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.6788 | 216.1 | 0.26739 | 57.7831
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.11504 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26823 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.11504 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26823 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.11504 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26823 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.11514 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 45.4795 | 395 | 0.26833 | 105.9893
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.11514 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 50.085 | 435 | 0.26833 | 116.7224
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.11546 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 50.2268 | 435 | 0.26865 | 116.8642
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.11567 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 13.0128 | 0 | 0.26886 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.11701 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 7.0209 | 60 | 0.2702 | 16.2123
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.11701 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 7.3719 | 63 | 0.2702 | 17.0229
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.11882 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2895 | 196 | 0.27201 | 53.3146
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.11882 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.1895 | 111 | 0.27201 | 30.1935
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.11907 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27226 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.11939 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.27258 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.1196 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.7839 | 0 | 0.27279 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.1196 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.7839 | 0 | 0.27279 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.11973 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.1287 | 118 | 0.27292 | 32.2051
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.11973 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 13.7695 | 115 | 0.27292 | 31.3863
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.11973 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 66.5727 | 556 | 0.27292 | 151.746
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.11979 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 20.3635 | 170 | 0.27297 | 46.4056
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.11979 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 62.2882 | 520 | 0.27297 | 141.9467
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.12003 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 44.4115 | 370 | 0.27322 | 101.0915
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.8043 | 0 | 0.27322 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.9244 | 0 | 0.27322 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 37.0896 | 0 | 0.27322 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.1644 | 0 | 0.27322 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.2845 | 0 | 0.27322 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.12003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 37.2096 | 0 | 0.27322 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.2195 | 160 | 0.27331 | 43.7298
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.739 | 156 | 0.27331 | 42.6366
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5439 | 196 | 0.27331 | 53.569
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.739 | 156 | 0.27331 | 42.6366
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.8592 | 157 | 0.27331 | 42.9099
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.12012 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.7842 | 198 | 0.27331 | 54.1157
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.12018 | north | 8 | N | N | Nnorth | Nnorth | 1 | 9.0131 | 0 | 0.27336 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.12018 | north | 8 | N | N | Nnorth | Nnorth | 1 | 9.5659 | 0 | 0.27336 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.12018 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.6235 | 0 | 0.27336 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.12029 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 67.1241 | 0 | 0.27348 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.12029 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 69.6502 | 0 | 0.27348 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.12029 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 97.1976 | 0 | 0.27348 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.12055 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.5238 | 79 | 0.27374 | 21.6257
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.12055 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.7787 | 106 | 0.27374 | 29.0168
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.12055 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 17.6009 | 146 | 0.27374 | 39.9665
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.12055 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.1621 | 76 | 0.27374 | 20.8045
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.12061 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.8242 | 40 | 0.2738 | 10.9518
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.12069 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.4139 | 20 | 0.27388 | 5.4776
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.12069 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0173 | 25 | 0.27388 | 6.8471
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.12069 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.9484 | 41 | 0.27388 | 11.2292
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.12091 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.2741 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.12091 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.2741 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.121 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 46.948 | 388 | 0.27419 | 106.3855
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.121 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 62.315 | 515 | 0.27419 | 141.2075
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.577 | 161 | 0.27479 | 44.2404
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9417 | 164 | 0.27479 | 45.0648
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9417 | 164 | 0.27479 | 45.0648
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 50.3407 | 414 | 0.27479 | 113.7612
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.6986 | 162 | 0.27479 | 44.5152
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.577 | 161 | 0.27479 | 44.2404
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.8201 | 163 | 0.27479 | 44.79
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.1216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 49.7328 | 409 | 0.27479 | 112.3872
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.12183 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 27.2906 | 224 | 0.27502 | 61.605
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.12281 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 75.5294 | 0 | 0.276 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.12281 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 72.0906 | 0 | 0.276 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.12288 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.6171 | 151.5 | 0.27607 | 41.8253
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.12288 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.7154 | 152.3 | 0.27607 | 42.0461
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.12288 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.8121 | 177.5 | 0.27607 | 49.0032
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.12301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.5376 | 150.7 | 0.2762 | 41.6232
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.12301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.5745 | 151 | 0.2762 | 41.7061
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.12301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.822 | 177.4 | 0.2762 | 48.9978
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.12344 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 96.9035 | 0 | 0.27663 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.12344 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 98.138 | 0 | 0.27663 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.12344 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 96.2863 | 0 | 0.27663 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.12346 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.2716 | 0 | 0.27665 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.12346 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.0494 | 0 | 0.27665 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.12346 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.9013 | 0 | 0.27665 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.12346 | north | 1 | N | N | Nnorth | Nnorth | 1 | 49.2593 | 0 | 0.27665 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.12405 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.2024 | 0 | 0.27724 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.12406 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.27725 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.12512 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 22.7717 | 182 | 0.27831 | 50.6521
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.12512 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 60.5576 | 484 | 0.27831 | 134.7013
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.17439 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 144.2205 | 0 | 0.32758 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.17439 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 142.8254 | 0 | 0.32758 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.29529 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 252.4695 | 0 | 0.44848 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.29529 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 252.4695 | 0 | 0.44848 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.29529 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 44.9721 | 0 | 0.44848 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.29529 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 45.1788 | 0 | 0.44848 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.51456 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 24.6988 | 48 | 0.66775 | 32.0519
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.51456 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 23.6697 | 46 | 0.66775 | 30.7164
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.51456 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 54.0287 | 105 | 0.66775 | 70.1136
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.54 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.69319 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.54 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.69319 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.54 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.1801 | 17 | 0.69319 | 11.7843
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.54 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.69319 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.54 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.69319 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.54391 | north | 7 | N | N | Nnorth | Nnorth | 1 | 17.4052 | 0 | 0.6971 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.63771 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 295.2616 | 0 | 0.7909 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
Average line rating
| min | 2080
| avg | 2080
| max | 2080