## test results
CRE test for: |  | 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99 | [5 empty] | FAIL
Line Rating: |  | 1562
Direcction |  | North | → | Houston |  | N-H
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.14014
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.047391
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.11807
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.15398
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.13098
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.049765
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.11837
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.14941
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.18991
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.021775
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.28955 | FAIL
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.16576
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.10659
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.26748
PTDF tests
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.28955 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.28955 | -0.18991
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.2927
[6 empty] | Concentration |  | -1.0109 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.11863
[6 empty] | Concentration |  | -0.40971 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 388.067
| Percent of line rating => | [6 empty] | 24.84% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -1.1879
[7 empty] | B1(N-S) | 0.002761 | 0.22835 | 0.22559 | 0.002761
[7 empty] | B2 (N-W) | 0.00026642 | 0.026133 | 0.025866 | 0.00026642
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B4 (S-W) | -0.0023841 | -0.19929 | -0.19691 | -0.0023841
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.0080851 | 0.11854 | 0.12662 | -0.0080851
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.00027083 | 0.31747 | 0.31774 | -0.00027083
[7 empty] | test | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B1 | 0.8027%
Deployment Error Percent | [6 empty] | B2 | 0.07746%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0%
[7 empty] | B4 | -0.6931%
[7 empty] | B5 | -2.351%
[7 empty] | B6 | -0.07874%
[7 empty] | Max Abs Error | 2.351% | PASS

## Generation_sensitivity
Generator Sensitivities
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99 C: SNGLTN - TOMBAL_74 (44645-46500) & SNGLTN - ROANS_75 (44645-40600) | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99 C: SNGLTN - TOMBAL_74 (44645-46500) & SNGLTN - ROANS_75 (44645-40600)
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.10021 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -25.5533
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.10021 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -14.9311
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.10692 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -1.6038
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.10692 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -1.6038
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.10021 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -15.332
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.10226 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -15.3384
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.10226 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -8.1805
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.12454 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -9.0914
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.12454 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -14.8203
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.12454 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -25.5307
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.12454 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -12.7031
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.12454 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -11.9558
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.12595 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -1.5114
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.12595 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -1.5114
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.12541 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -21.0687
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.12541 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -11.2868
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.1271 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -2.2879
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.1271 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -2.2879
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.1271 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -4.8299
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.1287 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -37.065
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.1287 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -18.9186
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.1287 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -18.9186
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.1306 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -14.6921
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.13577 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -5.4309
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.13577 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -10.7257
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.13577 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -14.3914
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.13577 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -19.8221
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.13577 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -10.3184
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.13202 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -7.9214
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.13202 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -8.3175
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.13595 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -2.719
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.13595 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -3.3987
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.13595 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -5.5739
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.20511 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -94.9673
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -7.7099
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -7.593
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -7.8267
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -7.8267
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -7.8267
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.11682 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -13.317
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.11682 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -60.1602
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -7.8743
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -8.2323
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -8.2323
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -7.9936
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -7.9936
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -7.755
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.11896 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -8.3271
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.11896 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -8.7315
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.11896 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -8.3746
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.11916 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -17.874
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.11916 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -26.2152
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.11943 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -11.8231
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.11943 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -7.2849
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.11941 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -16.8362
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.11943 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -2.9856
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.11943 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -5.4577
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.11943 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -5.4577
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.11941 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -14.3287
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.11835 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -3.0534
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.11813 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -11.8717
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.11873 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -14.2482
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.11811 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -6.8501
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.11827 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -25.3341
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.11967 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -17.9501
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.11746 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -0.77526
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.11746 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -4.029
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.11967 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -12.0864
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.11876 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -14.2516
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | -0.12589 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | -46.0768
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.12512 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -30.2778
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.12261 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -49.0432
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.12261 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -28.9364
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.1234 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -20.361
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.12793 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -26.0975
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.12793 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -25.7137
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.12793 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -30.9588
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.12604 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -2.5207
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.12604 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -2.5207
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.12604 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -2.5207
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.12604 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -2.1426
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.12577 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -15.0925
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.1203 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -7.2183
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.1355 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -10.1625
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.1355 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -10.7858
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.1355 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -11.9782
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -21.6666
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -21.1249
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -26.5415
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -21.1249
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -21.2603
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -26.8124
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.13504 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -22.9561
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.13504 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -70.2187
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.1353 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -50.0614
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.13562 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -75.6754
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.13562 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -78.5234
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.13562 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -109.5802
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.13009 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -14.5696
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.13009 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -13.0086
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.13009 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -49.1725
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.12782 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -27.7764
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.12782 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -26.2041
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.12782 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -34.8195
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.12813 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -98.6601
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.1263 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -8.8412
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.1263 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -8.7149
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.1263 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -8.7149
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.1263 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -8.5886
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.12748 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -147.5001
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.12748 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -147.6276
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.12875 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -28.8404
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.12875 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -29.098
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.13015 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -28.1634
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.13015 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -28.1243
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.12875 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -27.2954
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.12875 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -27.1667
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.13039 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -51.5033
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.13068 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -56.8458
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.13039 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -56.7188
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.13419 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -18.5179
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.13453 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -15.8747
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.13453 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -15.4711
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.13453 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -74.7992
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.13612 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -52.8146
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.13612 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -70.1018
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.14114 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -110.791
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.14114 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -112.2023
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.14114 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -110.0853
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.1424 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -25.9172
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.1424 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -68.9226
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.13721 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -30.7348
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.14232 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -7.1161
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.14226 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -5.9749
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.15014 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -92.3386
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.15014 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -88.1345
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.097858 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -52.5497
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.097858 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -77.0142
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.096283 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -7.2212
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.096283 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -21.3748
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.026032 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -14.8122
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.052629 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 10.9995
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.052629 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 11.3679
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.052417 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 21.3337
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.052629 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 2.4209
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.052629 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 2.4736
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.052629 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 2.4209
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.052629 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 2.4209
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.0525 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 22.26
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.0525 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 22.3125
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.052444 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 3.0418
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.052444 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 4.6675
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.052444 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 2.3075
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.052444 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 2.3075
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.052444 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 2.2551
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.052444 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 2.36
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.052472 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 21.6185
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.052472 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 20.9888
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.054817 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 29.9301
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.054817 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 41.1127
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.052688 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 3.214
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.052688 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 5.0054
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.052688 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 7.9559
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.0538 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 8.339
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.0538 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 9.146
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.0538 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 8.339
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.083328 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 1.8332
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.083328 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.91661
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.083328 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.91661
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.082595 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 3.9398
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.082595 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 3.0808
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.082595 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 3.7994
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.082595 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 3.9646
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.071837 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.86204
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.071837 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.79021
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.053657 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 1.2878
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.053657 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 1.2878
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.053657 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 1.2341
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.06131 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 24.2788
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.13129 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 175.0136
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.13129 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 174.3571
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.077776 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 2.9555
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.077776 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 1.5011
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.077776 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 1.1666
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.077776 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 3.6555
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.10985 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -8.2387
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.12032 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -18.0476
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.11699 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -19.8295
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.082803 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -12.4205
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.11936 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -7.5194
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.12407 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -80.6096
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.13483 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -5.393
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.13483 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -5.393
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.005159 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 2.1771
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.02225 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 2.937
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.02225 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 2.9815
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.02225 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 7.1867
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.024526 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 3.8751
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.024526 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 3.9242
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.024526 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 4.292
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.042909 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 25.0589
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.042909 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 25.5309
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.043062 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 18.6458
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.041646 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 9.3245
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.041646 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 9.3704
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.041646 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 9.3537
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.041646 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 9.4411
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.012523 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.10018
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.012523 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.10018
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.004245 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.07641
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.004245 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.07641
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.004245 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.063675
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.002584 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.035401
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.006621 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.11918
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.006621 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.11918
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.009937 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.3478
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.009937 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.33786
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.009937 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.3478
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.004765 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.13342
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.004765 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.13819
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.11688 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -4.0907
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.11688 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -3.5063
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.039111 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 1.9555
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.039111 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 1.9555
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.039111 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 1.9555
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.039111 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 1.9555
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.035456 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.21274
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.045627 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.1095
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.045627 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.1095
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.045627 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.12776
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.047201 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.1888
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.048236 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.11577
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.048236 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.11577
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 7.5555
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 7.0929
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 7.1957
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 7.5555
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 9.3544
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 10.1768
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.021988 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 3.3532
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.021988 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 3.2872
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.021988 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 5.1144
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.046659 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 6.6256
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.046659 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 6.7656
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.046659 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 7.0455
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.046659 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 13.5311
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.007918 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.26129
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.007918 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.19795
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.071837 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.86204
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.082642 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 6.0329
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 7.2086
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 7.3911
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 2.4233
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.60583
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 7.2086
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 7.2998
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 7.1538
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 2.2812
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 4.1974
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.074463 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 46.8372
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.081194 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 11.6919
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.081194 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 15.2645
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.057222 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.68666
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.022849 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.13709
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.079598 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 26.7449
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.079271 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 26.4765
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.079271 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 26.9521
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.079021 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 3.0028
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.079187 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 1.9797
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.079187 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 1.9797
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.07907 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 3.0047
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.078315 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 2.2711
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.079581 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 11.8019
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.079581 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 11.8257
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.079581 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 12.1759
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 12.8154
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 12.4098
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 8.111
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 11.7609
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 11.9232
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 10.301
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.076467 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 11.2024
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.076467 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 11.3095
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.076467 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 13.2288
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.077228 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 15.9862
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.077228 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 16.7353
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.077228 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 18.6892
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.077233 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 11.1216
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.077233 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 11.1216
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.077233 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 13.2068
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.0127 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 3.937
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.0127 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 5.2451
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.01132 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.47544
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.01132 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.49808
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.01132 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.49808
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.01132 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.53204
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.72873
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.68411
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.68411
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.69898
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.014872 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 2.2903
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.014872 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 2.2011
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.71386
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.71386
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -8.2649
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -8.2649
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -10.9569
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -9.4456
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -9.4456
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -13.578
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -24.5797
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -16.776
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -15.6309
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -16.0559
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -17.3545
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -24.7922
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.12029 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -25.1406
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.12029 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -15.2167
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.12029 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -29.9522
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.12029 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -23.6971
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.11916 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -23.832
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.11916 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -14.5256
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.11709 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -17.4464
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.11895 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -21.4103
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.11895 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -21.4103
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.11888 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -26.7482
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.11982 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -14.9779
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.11982 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -14.9779
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -18.9421
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -19.0774
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -41.808
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -19.348
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -19.4833
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -41.9433
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.13337 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -26.1403
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.13337 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -14.804
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.13449 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -22.0607
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -22.4718
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -22.4718
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -56.7275
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -22.1977
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -22.0607
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -22.3347
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -56.0424
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.13584 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.13584 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.14173 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -20.9766
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.14173 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -18.4254
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.14173 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -20.5514
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.14173 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -56.5519
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.14872 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -22.4126
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.14872 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -22.4572
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.14872 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -26.3835
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.14846 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -22.4909
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.14846 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -22.6097
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.14846 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -26.3508
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.026032 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -15.1246
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.17755 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -151.8061
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.17755 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -151.8061
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.19039 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -6.0925
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.18539 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -8.8986
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.18539 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -8.5278
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.18995 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -2.2794
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.18995 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -9.6875
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.18995 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -3.2292
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.18995 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -4.1789
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.18995 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -4.7488
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.18539 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -19.4657
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.11959 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -10.0456
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.10972 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -8.7779
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.10966 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -16.449
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.10966 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -16.449
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.1568 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 11.1012
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.1568 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 10.4584
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.1568 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 8.3102
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 24.0213
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 24.0683
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 23.8802
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 15.0525
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 38.2585
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.1568 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 6.2719
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.15681 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 15.7279
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.15681 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 14.5676
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.15681 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 16.1043
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.15681 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 15.9945
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.15681 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 5.0179
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.15681 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 4.7042
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.15018 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 16.6695
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.15018 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 16.6695
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.15018 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 17.8709
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.15018 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 16.4443
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.17755 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -27.041
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.17755 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -27.1653
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.15319 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 20.8341
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.15412 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 5.0858
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 6.3629
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 6.3629
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 5.7569
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 5.7569
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.14917 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 10.5911
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.14917 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 1.4917
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.17009 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 27.724
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.17009 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 27.724
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.17009 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 41.6711
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.15364 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 9.9869
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.15364 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 9.2186
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.15364 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 9.9869
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.15364 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 9.9869
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.15258 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 22.735
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.15258 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 9.9332
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 14.0204
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 13.4965
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 13.4041
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 8.3968
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 1.8797
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.14899 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 110.6959
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.14996 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 110.2213
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.14844 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 25.5325
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.14844 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 25.5325
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.14844 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 25.5325
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.14604 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 25.2642
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.15298 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 26.4659
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.15298 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 20.6526
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.1481 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 24.111
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.1481 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 23.9037
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.1481 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 23.5334
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.1481 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 39.8691
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.15241 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 9.7539
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.15241 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 9.632
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.15241 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 12.5887
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.15241 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 11.217
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 24.7538
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 23.8286
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 23.8893
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 23.8134
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 40.8014
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.14945 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.74726
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.14945 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 3.1385
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.14528 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 22.4016
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.14528 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 22.6631
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.14528 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 22.6631
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.14528 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 55.2049
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.14965 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 59.5623
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 7.1868
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 7.1868
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 7.1868
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 8.5929
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 8.5929
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 8.4367
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.16676 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -137.9105
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.16676 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -136.5764
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.15376 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 7.0884
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 9.8551
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 9.8551
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 13.6156
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 9.5957
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 9.5957
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 13.2265
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.15263 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 27.4734
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.15263 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 24.2071
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.15263 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 23.9629
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.15299 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 5.3547
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.15488 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 71.0904
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 9.765
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 9.9152
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 10.5162
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 9.4646
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 9.3143
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 15.624
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 8.8636
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.14604 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 22.7816
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.14604 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 22.4895
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.14604 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 22.4895
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.14604 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 23.6578
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.15013 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 23.5704
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.15217 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 10.8038
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.15217 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 10.956
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.15217 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 5.9345
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.15217 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 4.565
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.15295 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 11.9303
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.15295 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 12.2362
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.15238 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 2.4686
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.15246 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 25.1564
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.15248 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 25.769
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.15236 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 32.452
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.15244 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 34.7572
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.1525 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 1.83
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.1525 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 2.745
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.15928 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 7.9638
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 15.4073
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 15.4073
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 7.9999
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 7.8518
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 7.9999
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 8.4444
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 7.9999
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 7.9999
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 8.5925
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 8.5925
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.14678 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 1.7614
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 7.6823
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 8.0939
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 7.6823
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 7.6823
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 8.0939
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 7.6823
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.13279 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 8.7643
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.15926 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 25.6412
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.15926 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 26.4375
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.15926 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 39.497
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.15926 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 86.9571
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.15926 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 102.4055
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.17015 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 110.769
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.17015 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 95.9657
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.17015 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 102.0912
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.15926 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 2.0704
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.14923 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 1.7907
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 5.0983
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 5.2033
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 4.9034
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 6.8827
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 2.6541
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 3.059
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 2.984
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 5.2482
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 2.6991
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 12.8057
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 22.1926
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 9.1779
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 10.5693
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 6.6613
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 14.951
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 12.7306
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 13.0266
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 7.4015
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 2.6645
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 13.9148
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 10.3621
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 9.3259
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 10.6582
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 9.5923
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 14.951
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 14.3589
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 15.2471
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 11.2503
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 11.8424
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 11.8424
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 25.3131
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43652
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.10669 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -8.1614
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.10985 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -8.788
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.10985 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -4.394
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.11036 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -8.8289
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.10974 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -8.7791
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.10711 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -8.5689
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.10625 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -8.9251
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.11036 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -8.8289
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 4.9465
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.11886 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -14.2626
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.11886 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -27.6932
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.11886 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -20.2291
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 9.6326
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 7.9838
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 9.7194
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 4.9898
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 4.339
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.12125 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -7.2752
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.021677 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.092541 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.11225 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -0.5388
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -4.5069
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -12.9197
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -16.2247
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -14.3018
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -12.6192
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -9.6747
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.11809 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -17.7133
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.11782 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -13.2552
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.11782 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -17.6147
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.11782 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -21.9153
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.11782 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -25.2732
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.077775 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.026322 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.060791 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 2.5549
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 3.9784
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 6.7524
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 7.3302
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 3.1972
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 2.9633
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 1.4816
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 7.3302
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 2.8073
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 3.3532
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 1.7156
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 3.3753
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 1.2982
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.60583
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 1.2982
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 3.3753
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.086546 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 3.3753
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 11.5412
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 3.899
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 4.289
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 3.899
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.08111 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.97332
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.085121 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 1.2768
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.085121 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 1.9578
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.090158 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 4.3276
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.086006 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.68805
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.079552 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 14.3194
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.079598 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 14.3276
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.079271 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 14.2688
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.079271 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 14.2688
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.060787 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 6.0787
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.060787 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 6.0787
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 2.0127
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 2.0127
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 2.0127
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 1.2881
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 2.0127
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 2.0127
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 2.0127
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 1.2076
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.060787 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.060787 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 30.3935
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.060787 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 30.3935
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.060787 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.071059 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.007918 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.067408 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.074333 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L: 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99 C: SNGLTN - TOMBAL_74 (44645-46500) & SNGLTN - ROANS_75 (44645-40600) | [7 empty] | 388.067
Number of Bus | Name of Bus | ID | Max MW | L: 44500 OBRIEN__ 345 44645 SNGLTN_3 345 99 C: SNGLTN - TOMBAL_74 (44645-46500) & SNGLTN - ROANS_75 (44645-40600) | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.10021 | north | 0.039934 | -0.1476 | 0.017863 | -0.25419 | 0.017863 | west | Y | 0.039934 | 5.6281
239 | BOSQUESW | 1 | 149 | -0.10021 | north | 0.039934 | -0.1476 | 0.017863 | -0.25419 | 0.017863 | west | Y | 0.039934 | 3.2886
244 | WHITNYDM | 1 | 15 | -0.10692 | north | 0.033222 | -0.15431 | 0.011151 | -0.2609 | 0.011151 | west | Y | 0.033222 | 0.33106
245 | WHITNYDM | 2 | 15 | -0.10692 | north | 0.033222 | -0.15431 | 0.011151 | -0.2609 | 0.011151 | west | Y | 0.033222 | 0.33106
247 | BOSQUESW | 2 | 153 | -0.10021 | north | 0.039934 | -0.1476 | 0.017863 | -0.25419 | 0.017863 | west | Y | 0.039934 | 3.3768
251 | BOSQUESW | 2 | 150 | -0.10226 | north | 0.037887 | -0.14965 | 0.015816 | -0.25624 | 0.015816 | west | Y | 0.037887 | 3.3106
253 | BOSQUESW | 2 | 80 | -0.10226 | north | 0.037887 | -0.14965 | 0.015816 | -0.25624 | 0.015816 | west | Y | 0.037887 | 1.7657
332 | RWMILLER | 1 | 73 | -0.12454 | north | 0.015603 | -0.17193 | -0.006468 | -0.27852 | 0.006468 | west | Y | 0.015603 | 0.66685
333 | RWMILLER | 2 | 119 | -0.12454 | north | 0.015603 | -0.17193 | -0.006468 | -0.27852 | 0.006468 | west | Y | 0.015603 | 1.0871
334 | RWMILLER | 3 | 205 | -0.12454 | north | 0.015603 | -0.17193 | -0.006468 | -0.27852 | 0.006468 | west | Y | 0.015603 | 1.8727
335 | RWMILLER | 4 | 102 | -0.12454 | north | 0.015603 | -0.17193 | -0.006468 | -0.27852 | 0.006468 | west | Y | 0.015603 | 0.93176
336 | RWMILLER | 5 | 96 | -0.12454 | north | 0.015603 | -0.17193 | -0.006468 | -0.27852 | 0.006468 | west | Y | 0.015603 | 0.87695
344 | MRSSHPRD | 1 | 12 | -0.12595 | north | 0.014197 | -0.17334 | -0.007874 | -0.27993 | 0.007874 | west | Y | 0.014197 | 0.075875
345 | MRSSHPRD | 2 | 12 | -0.12595 | north | 0.014197 | -0.17334 | -0.007874 | -0.27993 | 0.007874 | west | Y | 0.014197 | 0.075875
366 | JNSNCNTY | 1 | 168 | -0.12541 | north | 0.014734 | -0.1728 | -0.007337 | -0.27939 | 0.007337 | west | Y | 0.014734 | 1.2427
367 | JNSNCNTY | 2 | 90 | -0.12541 | north | 0.014734 | -0.1728 | -0.007337 | -0.27939 | 0.007337 | west | Y | 0.014734 | 0.66572
503 | NTHTEXAS | 1 | 18 | -0.1271 | north | 0.01304 | -0.17449 | -0.009031 | -0.28109 | 0.009031 | west | Y | 0.01304 | 0.07216
504 | NTHTEXAS | 2 | 18 | -0.1271 | north | 0.01304 | -0.17449 | -0.009031 | -0.28109 | 0.009031 | west | Y | 0.01304 | 0.07216
505 | NTHTEXAS | 3 | 38 | -0.1271 | north | 0.01304 | -0.17449 | -0.009031 | -0.28109 | 0.009031 | west | Y | 0.01304 | 0.15234
580 | JCKCNTY8 | 1 | 288 | -0.1287 | north | 0.011445 | -0.17609 | -0.010626 | -0.28268 | 0.010626 | west | Y | 0.011445 | 0.23585
581 | JCKCNTY8 | 2 | 147 | -0.1287 | north | 0.011445 | -0.17609 | -0.010626 | -0.28268 | 0.010626 | west | Y | 0.011445 | 0.12038
582 | JCKCNTY8 | 3 | 147 | -0.1287 | north | 0.011445 | -0.17609 | -0.010626 | -0.28268 | 0.010626 | west | Y | 0.011445 | 0.12038
728 | WOLFRIDG | 1 | 112.5 | -0.1306 | north | 0.0095469 | -0.17799 | -0.012524 | -0.28458 | 0.0095469 | North | N | 0.0095469 | 0
837 | NEWMAN_G | 1 | 40 | -0.13577 | north | 0.0043709 | -0.18316 | -0.0177 | -0.28976 | 0.0043709 | North | N | 0.0043709 | 0
842 | OLINGER_ | 1 | 79 | -0.13577 | north | 0.0043749 | -0.18316 | -0.017696 | -0.28975 | 0.0043749 | North | N | 0.0043749 | 0
843 | OLINGER_ | 1 | 106 | -0.13577 | north | 0.0043749 | -0.18316 | -0.017696 | -0.28975 | 0.0043749 | North | N | 0.0043749 | 0
844 | OLINGER_ | 1 | 146 | -0.13577 | north | 0.0043749 | -0.18316 | -0.017696 | -0.28975 | 0.0043749 | North | N | 0.0043749 | 0
845 | OLINGER_ | 1 | 76 | -0.13577 | north | 0.0043749 | -0.18316 | -0.017696 | -0.28975 | 0.0043749 | North | N | 0.0043749 | 0
923 | SPENCER_ | 1 | 60 | -0.13202 | north | 0.0081189 | -0.17941 | -0.013952 | -0.28601 | 0.0081189 | North | N | 0.0081189 | 0
924 | SPENCER_ | 1 | 63 | -0.13202 | north | 0.0081189 | -0.17941 | -0.013952 | -0.28601 | 0.0081189 | North | N | 0.0081189 | 0
948 | STEAM1 | 1 | 20 | -0.13595 | north | 0.0041939 | -0.18334 | -0.017877 | -0.28993 | 0.0041939 | North | N | 0.0041939 | 0
949 | STEAM2 | 1 | 25 | -0.13595 | north | 0.0041939 | -0.18334 | -0.017877 | -0.28993 | 0.0041939 | North | N | 0.0041939 | 0
950 | STEAM3 | 1 | 41 | -0.13595 | north | 0.0041939 | -0.18334 | -0.017877 | -0.28993 | 0.0041939 | North | N | 0.0041939 | 0
990 | GIBN_CRE | 1 | 463 | -0.20511 | north | -0.06497 | -0.2525 | -0.087041 | -0.3591 | 0.06497 | North | N | 0.06497 | 0
1002 | PBCTAGE_ | A | 66 | -0.11682 | west | 0.023327 | -0.16421 | 0.001256 | -0.2708 | 0.001256 | west | N | 0.001256 | 0
1003 | PBCTBGE_ | B | 65 | -0.11682 | west | 0.023327 | -0.16421 | 0.001256 | -0.2708 | 0.001256 | west | N | 0.001256 | 0
1004 | PBCTCGE_ | C | 67 | -0.11682 | west | 0.023327 | -0.16421 | 0.001256 | -0.2708 | 0.001256 | west | N | 0.001256 | 0
1005 | PBCTDGE_ | D | 67 | -0.11682 | west | 0.023327 | -0.16421 | 0.001256 | -0.2708 | 0.001256 | west | N | 0.001256 | 0
1006 | PBCTEGE_ | E | 67 | -0.11682 | west | 0.023327 | -0.16421 | 0.001256 | -0.2708 | 0.001256 | west | N | 0.001256 | 0
1007 | PB5GEN_6 | MB | 114 | -0.11682 | west | 0.023327 | -0.16421 | 0.001256 | -0.2708 | 0.001256 | west | N | 0.001256 | 0
1008 | PB6GEN_7 | MB | 515 | -0.11682 | west | 0.023327 | -0.16421 | 0.001256 | -0.2708 | 0.001256 | west | N | 0.001256 | 0
1039 | MRGNAG_1 | A | 66 | -0.11931 | west | 0.020835 | -0.1667 | -0.001236 | -0.27329 | 0.001236 | west | N | 0.001236 | 0
1040 | MRGNBG_2 | B | 69 | -0.11931 | west | 0.020835 | -0.1667 | -0.001236 | -0.27329 | 0.001236 | west | N | 0.001236 | 0
1041 | MRGNCG_3 | C | 69 | -0.11931 | west | 0.020835 | -0.1667 | -0.001236 | -0.27329 | 0.001236 | west | N | 0.001236 | 0
1042 | MRGNDG_4 | D | 67 | -0.11931 | west | 0.020835 | -0.1667 | -0.001236 | -0.27329 | 0.001236 | west | N | 0.001236 | 0
1043 | MRGNEG_5 | E | 67 | -0.11931 | west | 0.020835 | -0.1667 | -0.001236 | -0.27329 | 0.001236 | west | N | 0.001236 | 0
1044 | MRGNFG_6 | F | 65 | -0.11931 | west | 0.020835 | -0.1667 | -0.001236 | -0.27329 | 0.001236 | west | N | 0.001236 | 0
1045 | CALENG1G | 1 | 70 | -0.11896 | west | 0.021185 | -0.16635 | -0.00088598 | -0.27294 | 0.00088598 | west | N | 0.00088598 | 0
1046 | CALENG2G | 2 | 73.4 | -0.11896 | west | 0.021185 | -0.16635 | -0.00088598 | -0.27294 | 0.00088598 | west | N | 0.00088598 | 0
1047 | CALENG3G | 3 | 70.4 | -0.11896 | west | 0.021185 | -0.16635 | -0.00088598 | -0.27294 | 0.00088598 | west | N | 0.00088598 | 0
1058 | LONGSHOR | 1 | 150 | -0.11916 | west | 0.020983 | -0.16655 | -0.001088 | -0.27314 | 0.001088 | west | N | 0.001088 | 0
1058 | LONGSHOR | 2 | 220 | -0.11916 | west | 0.020983 | -0.16655 | -0.001088 | -0.27314 | 0.001088 | west | N | 0.001088 | 0
1061 | CIELOGEN | 1 | 99 | -0.11943 | west | 0.020718 | -0.16682 | -0.001353 | -0.27341 | 0.001353 | west | N | 0.001353 | 0
1062 | CIELOGEN | 1 | 61 | -0.11943 | west | 0.020718 | -0.16682 | -0.001353 | -0.27341 | 0.001353 | west | N | 0.001353 | 0
1068 | SCURRYCW | 1 | 141 | -0.11941 | west | 0.020737 | -0.1668 | -0.001334 | -0.27339 | 0.001334 | west | N | 0.001334 | 0
1069 | KINDERMG | 1 | 25 | -0.11943 | west | 0.020718 | -0.16682 | -0.001353 | -0.27341 | 0.001353 | west | N | 0.001353 | 0
1070 | KINDERMG | 1 | 45.7 | -0.11943 | west | 0.020718 | -0.16682 | -0.001353 | -0.27341 | 0.001353 | west | N | 0.001353 | 0
1071 | KINDERMG | 1 | 45.7 | -0.11943 | west | 0.020718 | -0.16682 | -0.001353 | -0.27341 | 0.001353 | west | N | 0.001353 | 0
1073 | SCURRYCW | 2 | 120 | -0.11941 | west | 0.020737 | -0.1668 | -0.001334 | -0.27339 | 0.001334 | west | N | 0.001334 | 0
1320 | BSP 1 | 1 | 25.8 | -0.11835 | west | 0.021796 | -0.16574 | -0.00027498 | -0.27233 | 0.00027498 | west | N | 0.00027498 | 0
1326 | STANTONW | 1 | 100.5 | -0.11813 | west | 0.022017 | -0.16552 | -5.3984e-05 | -0.27211 | 5.3984e-05 | west | N | 5.3984e-05 | 0
1327 | WILDHRSE | 1 | 120 | -0.11873 | west | 0.021408 | -0.16613 | -0.00066298 | -0.27272 | 0.00066298 | west | N | 0.00066298 | 0
1328 | OCOTILLO | 1 | 58 | -0.11811 | west | 0.022038 | -0.1655 | -3.2984e-05 | -0.27209 | 3.2984e-05 | west | N | 3.2984e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.11827 | west | 0.02187 | -0.16566 | -0.00020098 | -0.27226 | 0.00020098 | west | N | 0.00020098 | 0
1343 | TRENTIPP | 1 | 150 | -0.11967 | west | 0.020476 | -0.16706 | -0.001595 | -0.27365 | 0.001595 | west | N | 0.001595 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.11746 | west | 0.02268 | -0.16485 | 0.00060902 | -0.27145 | 0.00060902 | west | N | 0.00060902 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.11746 | west | 0.02268 | -0.16485 | 0.00060902 | -0.27145 | 0.00060902 | west | N | 0.00060902 | 0
1354 | AEPWIND_ | 1 | 101 | -0.11967 | west | 0.020476 | -0.16706 | -0.001595 | -0.27365 | 0.001595 | west | N | 0.001595 | 0
1360 | GUNSIGHT | 1 | 120 | -0.11876 | west | 0.02138 | -0.16615 | -0.00069098 | -0.27275 | 0.00069098 | west | N | 0.00069098 | 0
1432 | GRHAMSES | 2 | 366 | -0.12589 | north | 0.01425 | -0.17328 | -0.007821 | -0.27988 | 0.007821 | west | Y | 0.01425 | 2.353
1433 | GRHAMSES | 1 | 242 | -0.12512 | north | 0.015028 | -0.17251 | -0.007043 | -0.2791 | 0.007043 | west | Y | 0.015028 | 1.9323
1437 | MESQUITW | 1 | 400 | -0.12261 | west | 0.017535 | -0.17 | -0.004536 | -0.27659 | 0.004536 | west | N | 0.004536 | 0
1438 | MESQUITW | 1 | 236 | -0.12261 | west | 0.017531 | -0.17 | -0.00454 | -0.2766 | 0.00454 | west | N | 0.00454 | 0
1442 | COKFIELD | 1 | 165 | -0.1234 | west | 0.016743 | -0.17079 | -0.005328 | -0.27738 | 0.005328 | west | N | 0.005328 | 0
1453 | WCPWRCO_ | 1 | 204 | -0.12793 | north | 0.012214 | -0.17532 | -0.009857 | -0.28191 | 0.009857 | west | Y | 0.012214 | 0.48081
1454 | WCPWRCO_ | 2 | 201 | -0.12793 | north | 0.012214 | -0.17532 | -0.009857 | -0.28191 | 0.009857 | west | Y | 0.012214 | 0.47374
1455 | WCPWRCO_ | 3 | 242 | -0.12793 | north | 0.012214 | -0.17532 | -0.009857 | -0.28191 | 0.009857 | west | Y | 0.012214 | 0.57037
1479 | WFCOGEN_ | 1 | 20 | -0.12604 | west | 0.014106 | -0.17343 | -0.007965 | -0.28002 | 0.007965 | west | N | 0.007965 | 0
1479 | WFCOGEN_ | 2 | 20 | -0.12604 | west | 0.014106 | -0.17343 | -0.007965 | -0.28002 | 0.007965 | west | N | 0.007965 | 0
1482 | WFCOGEN_ | 1 | 20 | -0.12604 | west | 0.014106 | -0.17343 | -0.007965 | -0.28002 | 0.007965 | west | N | 0.007965 | 0
1482 | WFCOGEN_ | 2 | 17 | -0.12604 | west | 0.014106 | -0.17343 | -0.007965 | -0.28002 | 0.007965 | west | N | 0.007965 | 0
1600 | BARTNWND | 1 | 120 | -0.12577 | north | 0.014372 | -0.17316 | -0.007699 | -0.27975 | 0.007699 | west | Y | 0.014372 | 0.80075
1643 | SLSTR1PP | 1 | 60 | -0.1203 | north | 0.019838 | -0.1677 | -0.002233 | -0.27429 | 0.002233 | west | Y | 0.019838 | 1.0563
1675 | PEC_1G | 1 | 75 | -0.1355 | north | 0.0046429 | -0.18289 | -0.017428 | -0.28948 | 0.0046429 | North | N | 0.0046429 | 0
1676 | PEC_2G | 2 | 79.6 | -0.1355 | north | 0.0046429 | -0.18289 | -0.017428 | -0.28948 | 0.0046429 | North | N | 0.0046429 | 0
1677 | PEC_3G | 3 | 88.4 | -0.1355 | north | 0.0046429 | -0.18289 | -0.017428 | -0.28948 | 0.0046429 | North | N | 0.0046429 | 0
1678 | LAMARPWR | 1 | 160 | -0.13542 | north | 0.0047269 | -0.18281 | -0.017344 | -0.2894 | 0.0047269 | North | N | 0.0047269 | 0
1679 | LAMARPWR | 2 | 156 | -0.13542 | north | 0.0047269 | -0.18281 | -0.017344 | -0.2894 | 0.0047269 | North | N | 0.0047269 | 0
1680 | LAMARPWR | 3 | 196 | -0.13542 | north | 0.0047269 | -0.18281 | -0.017344 | -0.2894 | 0.0047269 | North | N | 0.0047269 | 0
1681 | LAMARPWR | 4 | 156 | -0.13542 | north | 0.0047269 | -0.18281 | -0.017344 | -0.2894 | 0.0047269 | North | N | 0.0047269 | 0
1682 | LAMARPWR | 5 | 157 | -0.13542 | north | 0.0047269 | -0.18281 | -0.017344 | -0.2894 | 0.0047269 | North | N | 0.0047269 | 0
1683 | LAMARPWR | 6 | 198 | -0.13542 | north | 0.0047269 | -0.18281 | -0.017344 | -0.2894 | 0.0047269 | North | N | 0.0047269 | 0
1687 | VALLEY_1 | 1 | 170 | -0.13504 | north | 0.0051069 | -0.18243 | -0.016964 | -0.28902 | 0.0051069 | North | N | 0.0051069 | 0
1688 | VALLEY_2 | 2 | 520 | -0.13504 | north | 0.0051069 | -0.18243 | -0.016964 | -0.28902 | 0.0051069 | North | N | 0.0051069 | 0
1689 | VALLEY_3 | 3 | 370 | -0.1353 | north | 0.0048419 | -0.18269 | -0.017229 | -0.28928 | 0.0048419 | North | N | 0.0048419 | 0
1701 | MOSES_1G | 1 | 558 | -0.13562 | north | 0.0045239 | -0.18301 | -0.017547 | -0.2896 | 0.0045239 | North | N | 0.0045239 | 0
1702 | MOSES_2G | 2 | 579 | -0.13562 | north | 0.0045239 | -0.18301 | -0.017547 | -0.2896 | 0.0045239 | North | N | 0.0045239 | 0
1703 | MOSES_3G | 3 | 808 | -0.13562 | north | 0.0045239 | -0.18301 | -0.017547 | -0.2896 | 0.0045239 | North | N | 0.0045239 | 0
1861 | EAGLEMNT | MB | 112 | -0.13009 | north | 0.010057 | -0.17748 | -0.012014 | -0.28407 | 0.010057 | North | N | 0.010057 | 0
1862 | EAGLEMNT | MB | 100 | -0.13009 | north | 0.010057 | -0.17748 | -0.012014 | -0.28407 | 0.010057 | North | N | 0.010057 | 0
1863 | EAGLEMNT | MB | 378 | -0.13009 | north | 0.010057 | -0.17748 | -0.012014 | -0.28407 | 0.010057 | North | N | 0.010057 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.12782 | north | 0.012318 | -0.17522 | -0.009753 | -0.28181 | 0.009753 | west | Y | 0.012318 | 0.55735
1878 | WLFHOLW_ | 2 | 205 | -0.12782 | north | 0.012318 | -0.17522 | -0.009753 | -0.28181 | 0.009753 | west | Y | 0.012318 | 0.52581
1879 | WLFHOLW_ | 3 | 272.4 | -0.12782 | north | 0.012318 | -0.17522 | -0.009753 | -0.28181 | 0.009753 | west | Y | 0.012318 | 0.69868
1889 | DECRDOVA | MB | 770 | -0.12813 | north | 0.012013 | -0.17552 | -0.010058 | -0.28211 | 0.010058 | west | Y | 0.012013 | 1.5053
1892 | DECRDOVA | A | 70 | -0.1263 | north | 0.01384 | -0.17369 | -0.008231 | -0.28029 | 0.008231 | west | Y | 0.01384 | 0.39262
1893 | DECRDOVA | B | 69 | -0.1263 | north | 0.01384 | -0.17369 | -0.008231 | -0.28029 | 0.008231 | west | Y | 0.01384 | 0.38701
1894 | DECRDOVA | C | 69 | -0.1263 | north | 0.01384 | -0.17369 | -0.008231 | -0.28029 | 0.008231 | west | Y | 0.01384 | 0.38701
1895 | DECRDOVA | D | 68 | -0.1263 | north | 0.01384 | -0.17369 | -0.008231 | -0.28029 | 0.008231 | west | Y | 0.01384 | 0.38141
1898 | COMCHEPK | 1 | 1157 | -0.12748 | north | 0.012658 | -0.17488 | -0.009413 | -0.28147 | 0.009413 | west | Y | 0.012658 | 3.7544
1899 | COMCHEPK | 2 | 1158 | -0.12748 | north | 0.012658 | -0.17488 | -0.009413 | -0.28147 | 0.009413 | west | Y | 0.012658 | 3.7576
1937 | MDLTHELP | 5 | 224 | -0.12875 | north | 0.011391 | -0.17614 | -0.01068 | -0.28274 | 0.01068 | west | Y | 0.011391 | 0.15924
1938 | MDLTHELP | 6 | 226 | -0.12875 | north | 0.011391 | -0.17614 | -0.01068 | -0.28274 | 0.01068 | west | Y | 0.011391 | 0.16067
1941 | MDLTHELP | 1 | 216.4 | -0.13015 | north | 0.0099979 | -0.17754 | -0.012073 | -0.28413 | 0.0099979 | North | N | 0.0099979 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.13015 | north | 0.0099979 | -0.17754 | -0.012073 | -0.28413 | 0.0099979 | North | N | 0.0099979 | 0
1943 | MDLTHELP | 3 | 212 | -0.12875 | north | 0.011391 | -0.17614 | -0.01068 | -0.28274 | 0.01068 | west | Y | 0.011391 | 0.15071
1944 | MDLTHELP | 4 | 211 | -0.12875 | north | 0.011391 | -0.17614 | -0.01068 | -0.28274 | 0.01068 | west | Y | 0.011391 | 0.15
1947 | HANDLEY_ | 3 | 395 | -0.13039 | north | 0.0097549 | -0.17778 | -0.012316 | -0.28437 | 0.0097549 | North | N | 0.0097549 | 0
1948 | HANDLEY_ | 4 | 435 | -0.13068 | north | 0.0094629 | -0.17807 | -0.012608 | -0.28466 | 0.0094629 | North | N | 0.0094629 | 0
1949 | HANDLEY_ | 5 | 435 | -0.13039 | north | 0.0097549 | -0.17778 | -0.012316 | -0.28437 | 0.0097549 | North | N | 0.0097549 | 0
2371 | COLLIN_1 | MB | 138 | -0.13419 | north | 0.0059549 | -0.18158 | -0.016116 | -0.28817 | 0.0059549 | North | N | 0.0059549 | 0
2413 | MTCK6_G | 6 | 118 | -0.13453 | north | 0.0056119 | -0.18192 | -0.016459 | -0.28851 | 0.0056119 | North | N | 0.0056119 | 0
2414 | MTCK7_G | 7 | 115 | -0.13453 | north | 0.0056119 | -0.18192 | -0.016459 | -0.28851 | 0.0056119 | North | N | 0.0056119 | 0
2417 | MTCK8_G | 8 | 556 | -0.13453 | north | 0.0056119 | -0.18192 | -0.016459 | -0.28851 | 0.0056119 | North | N | 0.0056119 | 0
2451 | LKHB1_G | 1 | 388 | -0.13612 | north | 0.0040229 | -0.18351 | -0.018048 | -0.2901 | 0.0040229 | North | N | 0.0040229 | 0
2452 | LKHB2_G | 2 | 515 | -0.13612 | north | 0.0040229 | -0.18351 | -0.018048 | -0.2901 | 0.0040229 | North | N | 0.0040229 | 0
3097 | MARTLAKE | 1 | 785 | -0.14114 | north | -0.00099211 | -0.18853 | -0.023063 | -0.29512 | 0.00099211 | North | N | 0.00099211 | 0
3098 | MARTLAKE | 2 | 795 | -0.14114 | north | -0.00099211 | -0.18853 | -0.023063 | -0.29512 | 0.00099211 | North | N | 0.00099211 | 0
3099 | MARTLAKE | 3 | 780 | -0.14114 | north | -0.00099211 | -0.18853 | -0.023063 | -0.29512 | 0.00099211 | North | N | 0.00099211 | 0
3107 | STRYKER_ | 1 | 182 | -0.1424 | north | -0.0022591 | -0.18979 | -0.02433 | -0.29639 | 0.0022591 | North | N | 0.0022591 | 0
3108 | STRYKER_ | 2 | 484 | -0.1424 | north | -0.0022591 | -0.18979 | -0.02433 | -0.29639 | 0.0022591 | North | N | 0.0022591 | 0
3126 | TRINIDAD | 1 | 224 | -0.13721 | north | 0.0029339 | -0.1846 | -0.019137 | -0.29119 | 0.0029339 | North | N | 0.0029339 | 0
3309 | ASPN_G | 1 | 50 | -0.14232 | north | -0.0021781 | -0.18971 | -0.024249 | -0.2963 | 0.0021781 | North | N | 0.0021781 | 0
3348 | CHAMPION | MB | 42 | -0.14226 | north | -0.0021161 | -0.18965 | -0.024187 | -0.29624 | 0.0021161 | North | N | 0.0021161 | 0
3381 | BBRN_1G | 1 | 615 | -0.15014 | north | -0.010001 | -0.19753 | -0.032072 | -0.30413 | 0.010001 | North | N | 0.010001 | 0
3382 | BBRN_2G | 2 | 587 | -0.15014 | north | -0.010001 | -0.19753 | -0.032072 | -0.30413 | 0.010001 | North | N | 0.010001 | 0
3403 | THOUSE_1 | MB | 537 | -0.097858 | north | 0.042285 | -0.14525 | 0.020214 | -0.25184 | 0.020214 | west | Y | 0.042285 | 11.8521
3404 | THOUSE_2 | 2 | 787 | -0.097858 | north | 0.042285 | -0.14525 | 0.020214 | -0.25184 | 0.020214 | west | Y | 0.042285 | 17.3698
3416 | LAKE_CRK | MB | 75 | -0.096283 | north | 0.04386 | -0.14367 | 0.021789 | -0.25027 | 0.021789 | west | Y | 0.04386 | 1.6553
3417 | LAKE_CRK | MB | 222 | -0.096283 | north | 0.04386 | -0.14367 | 0.021789 | -0.25027 | 0.021789 | west | Y | 0.04386 | 4.8997
3432 | SANDOW_4 | 4 | 569 | -0.026032 | south | 0.11411 | -0.073423 | 0.09204 | -0.18002 | 0.073423 | south | N | 0.073423 | 0
5026 | BRAUNIG_ | 1 | 209 | 0.052629 | south | 0.19277 | 0.0052383 | 0.1707 | -0.10135 | 0.0052383 | south | N | 0.0052383 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.052629 | south | 0.19277 | 0.0052383 | 0.1707 | -0.10135 | 0.0052383 | south | N | 0.0052383 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.052417 | south | 0.19256 | 0.0050263 | 0.17049 | -0.10157 | 0.0050263 | south | N | 0.0050263 | 0
5031 | BRA_VHBC | 1 | 46 | 0.052629 | south | 0.19277 | 0.0052383 | 0.1707 | -0.10135 | 0.0052383 | south | N | 0.0052383 | 0
5032 | BRA_VHBC | 2 | 47 | 0.052629 | south | 0.19277 | 0.0052383 | 0.1707 | -0.10135 | 0.0052383 | south | N | 0.0052383 | 0
5033 | BRA_VHBC | 3 | 46 | 0.052629 | south | 0.19277 | 0.0052383 | 0.1707 | -0.10135 | 0.0052383 | south | N | 0.0052383 | 0
5034 | BRA_VHBC | 4 | 46 | 0.052629 | south | 0.19277 | 0.0052383 | 0.1707 | -0.10135 | 0.0052383 | south | N | 0.0052383 | 0
5111 | CALAVER_ | 1 | 424 | 0.0525 | south | 0.19264 | 0.0051093 | 0.17057 | -0.10148 | 0.0051093 | south | N | 0.0051093 | 0
5112 | CALAVER_ | 2 | 425 | 0.0525 | south | 0.19264 | 0.0051093 | 0.17057 | -0.10148 | 0.0051093 | south | N | 0.0051093 | 0
5264 | LEON_LCP | 3 | 58 | 0.052444 | south | 0.19259 | 0.0050533 | 0.17052 | -0.10154 | 0.0050533 | south | N | 0.0050533 | 0
5265 | LEON_LCP | 4 | 89 | 0.052444 | south | 0.19259 | 0.0050533 | 0.17052 | -0.10154 | 0.0050533 | south | N | 0.0050533 | 0
5266 | LEON_LCP | 1 | 44 | 0.052444 | south | 0.19259 | 0.0050533 | 0.17052 | -0.10154 | 0.0050533 | south | N | 0.0050533 | 0
5267 | LEON_LCP | 2 | 44 | 0.052444 | south | 0.19259 | 0.0050533 | 0.17052 | -0.10154 | 0.0050533 | south | N | 0.0050533 | 0
5268 | LEON_LCP | 3 | 43 | 0.052444 | south | 0.19259 | 0.0050533 | 0.17052 | -0.10154 | 0.0050533 | south | N | 0.0050533 | 0
5269 | LEON_LCP | 4 | 45 | 0.052444 | south | 0.19259 | 0.0050533 | 0.17052 | -0.10154 | 0.0050533 | south | N | 0.0050533 | 0
5396 | CALAVER_ | 1 | 412 | 0.052472 | south | 0.19261 | 0.0050813 | 0.17054 | -0.10151 | 0.0050813 | south | N | 0.0050813 | 0
5397 | CALAVER_ | 2 | 400 | 0.052472 | south | 0.19261 | 0.0050813 | 0.17054 | -0.10151 | 0.0050813 | south | N | 0.0050813 | 0
5401 | CALAVER_ | 1 | 546 | 0.054817 | south | 0.19496 | 0.0074263 | 0.17289 | -0.099166 | 0.0074263 | south | N | 0.0074263 | 0
5402 | CALAVER_ | 2 | 750 | 0.054817 | south | 0.19496 | 0.0074263 | 0.17289 | -0.099166 | 0.0074263 | south | N | 0.0074263 | 0
5436 | TUTTL_WB | MB | 61 | 0.052688 | south | 0.19283 | 0.0052973 | 0.17076 | -0.1013 | 0.0052973 | south | N | 0.0052973 | 0
5438 | TUTTL_WB | MB | 95 | 0.052688 | south | 0.19283 | 0.0052973 | 0.17076 | -0.1013 | 0.0052973 | south | N | 0.0052973 | 0
5439 | TUTTL_WB | MB | 151 | 0.052688 | south | 0.19283 | 0.0052973 | 0.17076 | -0.1013 | 0.0052973 | south | N | 0.0052973 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.0538 | south | 0.19394 | 0.0064093 | 0.17187 | -0.10018 | 0.0064093 | south | N | 0.0064093 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.0538 | south | 0.19394 | 0.0064093 | 0.17187 | -0.10018 | 0.0064093 | south | N | 0.0064093 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.0538 | south | 0.19394 | 0.0064093 | 0.17187 | -0.10018 | 0.0064093 | south | N | 0.0064093 | 0
5503 | RAYBURNG | 1 | 22 | 0.083328 | south | 0.22347 | 0.035937 | 0.2014 | -0.070655 | 0.035937 | south | N | 0.035937 | 0
5505 | RAYBURNG | 1 | 11 | 0.083328 | south | 0.22347 | 0.035937 | 0.2014 | -0.070655 | 0.035937 | south | N | 0.035937 | 0
5506 | RAYBURNG | 1 | 11 | 0.083328 | south | 0.22347 | 0.035937 | 0.2014 | -0.070655 | 0.035937 | south | N | 0.035937 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.082595 | south | 0.22274 | 0.035204 | 0.20067 | -0.071388 | 0.035204 | south | N | 0.035204 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.082595 | south | 0.22274 | 0.035204 | 0.20067 | -0.071388 | 0.035204 | south | N | 0.035204 | 0
5511 | RAYBURNC | 1 | 46 | 0.082595 | south | 0.22274 | 0.035204 | 0.20067 | -0.071388 | 0.035204 | south | N | 0.035204 | 0
5512 | RAYBURNC | 1 | 48 | 0.082595 | south | 0.22274 | 0.035204 | 0.20067 | -0.071388 | 0.035204 | south | N | 0.035204 | 0
5728 | FALCONHY | 2 | 12 | 0.071837 | south | 0.21198 | 0.024446 | 0.18991 | -0.082146 | 0.024446 | south | N | 0.024446 | 0
5729 | FALCONHY | 3 | 11 | 0.071837 | south | 0.21198 | 0.024446 | 0.18991 | -0.082146 | 0.024446 | south | N | 0.024446 | 0
5890 | PEARSALL | 1 | 24 | 0.053657 | south | 0.1938 | 0.0062663 | 0.17173 | -0.10033 | 0.0062663 | south | N | 0.0062663 | 0
5891 | PEARSALL | 1 | 24 | 0.053657 | south | 0.1938 | 0.0062663 | 0.17173 | -0.10033 | 0.0062663 | south | N | 0.0062663 | 0
5892 | PEARSALL | 1 | 23 | 0.053657 | south | 0.1938 | 0.0062663 | 0.17173 | -0.10033 | 0.0062663 | south | N | 0.0062663 | 0
5903 | SANMIGUE | 1 | 396 | 0.06131 | south | 0.20145 | 0.013919 | 0.17938 | -0.092673 | 0.013919 | south | N | 0.013919 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.13129 | houston | 0.27144 | 0.083902 | 0.24937 | -0.02269 | 0.02269 | houston | N | 0.02269 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.13129 | houston | 0.27144 | 0.083902 | 0.24937 | -0.02269 | 0.02269 | houston | N | 0.02269 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | 0.14014 | -0.047391 | 0.11807 | -0.15398 | 0.047391 | south | Y | 0.14014 | 55.6513
5932 | SI_RAY9 | 9 | 38 | 0.077776 | south | 0.21792 | 0.030385 | 0.19585 | -0.076207 | 0.030385 | south | N | 0.030385 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.077776 | south | 0.21792 | 0.030385 | 0.19585 | -0.076207 | 0.030385 | south | N | 0.030385 | 0
5934 | SI_RAY5 | 5 | 15 | 0.077776 | south | 0.21792 | 0.030385 | 0.19585 | -0.076207 | 0.030385 | south | N | 0.030385 | 0
5935 | SI_RAY10 | 10 | 47 | 0.077776 | south | 0.21792 | 0.030385 | 0.19585 | -0.076207 | 0.030385 | south | N | 0.030385 | 0
6016 | SWMESA | 1 | 75 | -0.10985 | west | 0.030293 | -0.15724 | 0.008222 | -0.26383 | 0.008222 | west | N | 0.008222 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | 0.14014 | -0.047391 | 0.11807 | -0.15398 | 0.047391 | south | Y | 0.11807 | 15.5499
6144 | MCADOO1A | 1 | 150 | -0.12032 | west | 0.019826 | -0.16771 | -0.002245 | -0.2743 | 0.002245 | west | N | 0.002245 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.11699 | west | 0.023155 | -0.16438 | 0.001084 | -0.27097 | 0.001084 | west | N | 0.001084 | 0
6476 | LANGFORD | 1 | 150 | -0.082803 | west | 0.05734 | -0.13019 | 0.035269 | -0.23679 | 0.035269 | west | N | 0.035269 | 0
6637 | SNYDERW1 | 1 | 63 | -0.11936 | west | 0.020788 | -0.16675 | -0.001283 | -0.27334 | 0.001283 | west | N | 0.001283 | 0
6752 | OKLA0A | 1 | 649.7 | -0.12407 | west | 0.016071 | -0.17146 | -0.006 | -0.27806 | 0.006 | west | N | 0.006 | 0
6948 | DENISNDM | 1 | 40 | -0.13483 | north | 0.0053179 | -0.18222 | -0.016753 | -0.28881 | 0.0053179 | North | N | 0.0053179 | 0
6948 | DENISNDM | 2 | 40 | -0.13483 | north | 0.0053179 | -0.18222 | -0.016753 | -0.28881 | 0.0053179 | North | N | 0.0053179 | 0
7000 | L_FERGUS | 1 | 422 | 0.005159 | south | 0.1453 | -0.042232 | 0.12323 | -0.14882 | 0.042232 | south | N | 0.042232 | 0
7004 | L_SIMGID | 1 | 132 | 0.02225 | south | 0.16239 | -0.025141 | 0.14032 | -0.13173 | 0.025141 | south | N | 0.025141 | 0
7005 | L_SIMGID | 2 | 134 | 0.02225 | south | 0.16239 | -0.025141 | 0.14032 | -0.13173 | 0.025141 | south | N | 0.025141 | 0
7006 | L_SIMGID | 3 | 323 | 0.02225 | south | 0.16239 | -0.025141 | 0.14032 | -0.13173 | 0.025141 | south | N | 0.025141 | 0
7007 | L_LOSTPI | 1 | 158 | 0.024526 | south | 0.16467 | -0.022865 | 0.1426 | -0.12946 | 0.022865 | south | N | 0.022865 | 0
7008 | L_LOSTPI | 2 | 160 | 0.024526 | south | 0.16467 | -0.022865 | 0.1426 | -0.12946 | 0.022865 | south | N | 0.022865 | 0
7009 | L_LOSTPI | 3 | 175 | 0.024526 | south | 0.16467 | -0.022865 | 0.1426 | -0.12946 | 0.022865 | south | N | 0.022865 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.042909 | south | 0.18305 | -0.0044817 | 0.16098 | -0.11107 | 0.0044817 | south | N | 0.0044817 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.042909 | south | 0.18305 | -0.0044817 | 0.16098 | -0.11107 | 0.0044817 | south | N | 0.0044817 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.043062 | south | 0.1832 | -0.0043287 | 0.16113 | -0.11092 | 0.0043287 | south | N | 0.0043287 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.041646 | south | 0.18179 | -0.0057447 | 0.15972 | -0.11234 | 0.0057447 | south | N | 0.0057447 | 0
7015 | L_HAYSEN | 2 | 225 | 0.041646 | south | 0.18179 | -0.0057447 | 0.15972 | -0.11234 | 0.0057447 | south | N | 0.0057447 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.041646 | south | 0.18179 | -0.0057447 | 0.15972 | -0.11234 | 0.0057447 | south | N | 0.0057447 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.041646 | south | 0.18179 | -0.0057447 | 0.15972 | -0.11234 | 0.0057447 | south | N | 0.0057447 | 0
7020 | L_AUSTPL | 1 | 8 | 0.012523 | south | 0.15267 | -0.034868 | 0.1306 | -0.14146 | 0.034868 | south | N | 0.034868 | 0
7020 | L_AUSTPL | 2 | 8 | 0.012523 | south | 0.15267 | -0.034868 | 0.1306 | -0.14146 | 0.034868 | south | N | 0.034868 | 0
7022 | L_BUCHAN | 1 | 18 | -0.004245 | south | 0.1359 | -0.051636 | 0.11383 | -0.15823 | 0.051636 | south | N | 0.051636 | 0
7023 | L_BUCHAN | 2 | 18 | -0.004245 | south | 0.1359 | -0.051636 | 0.11383 | -0.15823 | 0.051636 | south | N | 0.051636 | 0
7024 | L_BUCHAN | 3 | 15 | -0.004245 | south | 0.1359 | -0.051636 | 0.11383 | -0.15823 | 0.051636 | south | N | 0.051636 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.002584 | south | 0.13756 | -0.049975 | 0.11549 | -0.15657 | 0.049975 | south | N | 0.049975 | 0
7028 | L_MARBFA | 1 | 18 | 0.006621 | south | 0.14676 | -0.04077 | 0.12469 | -0.14736 | 0.04077 | south | N | 0.04077 | 0
7029 | L_MARBFA | 2 | 18 | 0.006621 | south | 0.14676 | -0.04077 | 0.12469 | -0.14736 | 0.04077 | south | N | 0.04077 | 0
7031 | L_MARSFO | 1 | 35 | 0.009937 | south | 0.15008 | -0.037454 | 0.12801 | -0.14405 | 0.037454 | south | N | 0.037454 | 0
7032 | L_MARSFO | 2 | 34 | 0.009937 | south | 0.15008 | -0.037454 | 0.12801 | -0.14405 | 0.037454 | south | N | 0.037454 | 0
7033 | L_MARSFO | 3 | 35 | 0.009937 | south | 0.15008 | -0.037454 | 0.12801 | -0.14405 | 0.037454 | south | N | 0.037454 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.004765 | south | 0.14491 | -0.042626 | 0.12284 | -0.14922 | 0.042626 | south | N | 0.042626 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.004765 | south | 0.14491 | -0.042626 | 0.12284 | -0.14922 | 0.042626 | south | N | 0.042626 | 0
7038 | L_DELAWA | 1 | 35 | -0.11688 | west | 0.023265 | -0.16427 | 0.001194 | -0.27086 | 0.001194 | west | N | 0.001194 | 0
7038 | L_DELAWA | 2 | 30 | -0.11688 | west | 0.023265 | -0.16427 | 0.001194 | -0.27086 | 0.001194 | west | N | 0.001194 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.039111 | south | 0.17925 | -0.0082797 | 0.15718 | -0.11487 | 0.0082797 | south | N | 0.0082797 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.039111 | south | 0.17925 | -0.0082797 | 0.15718 | -0.11487 | 0.0082797 | south | N | 0.0082797 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.039111 | south | 0.17925 | -0.0082797 | 0.15718 | -0.11487 | 0.0082797 | south | N | 0.0082797 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.039111 | south | 0.17925 | -0.0082797 | 0.15718 | -0.11487 | 0.0082797 | south | N | 0.0082797 | 0
7487 | L_CANYHY | 1 | 6 | 0.035456 | south | 0.1756 | -0.011935 | 0.15353 | -0.11853 | 0.011935 | south | N | 0.011935 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.045627 | south | 0.18577 | -0.0017637 | 0.1637 | -0.10836 | 0.0017637 | south | N | 0.0017637 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.045627 | south | 0.18577 | -0.0017637 | 0.1637 | -0.10836 | 0.0017637 | south | N | 0.0017637 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.045627 | south | 0.18577 | -0.0017637 | 0.1637 | -0.10836 | 0.0017637 | south | N | 0.0017637 | 0
7609 | L_SCHUMA | 1 | 4 | 0.047201 | south | 0.18734 | -0.0001897 | 0.16527 | -0.10678 | 0.0001897 | south | N | 0.0001897 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.048236 | south | 0.18838 | 0.0008453 | 0.16631 | -0.10575 | 0.0008453 | south | N | 0.0008453 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.048236 | south | 0.18838 | 0.0008453 | 0.16631 | -0.10575 | 0.0008453 | south | N | 0.0008453 | 0
7800 | L_GUADGE | 1 | 147 | 0.051398 | south | 0.19154 | 0.0040073 | 0.16947 | -0.10259 | 0.0040073 | south | N | 0.0040073 | 0
7801 | L_GUADGE | 2 | 138 | 0.051398 | south | 0.19154 | 0.0040073 | 0.16947 | -0.10259 | 0.0040073 | south | N | 0.0040073 | 0
7802 | L_GUADGE | 3 | 140 | 0.051398 | south | 0.19154 | 0.0040073 | 0.16947 | -0.10259 | 0.0040073 | south | N | 0.0040073 | 0
7803 | L_GUADGE | 4 | 147 | 0.051398 | south | 0.19154 | 0.0040073 | 0.16947 | -0.10259 | 0.0040073 | south | N | 0.0040073 | 0
7804 | L_GUADGE | 5 | 182 | 0.051398 | south | 0.19154 | 0.0040073 | 0.16947 | -0.10259 | 0.0040073 | south | N | 0.0040073 | 0
7805 | L_GUADGE | 6 | 198 | 0.051398 | south | 0.19154 | 0.0040073 | 0.16947 | -0.10259 | 0.0040073 | south | N | 0.0040073 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.021988 | south | 0.16213 | -0.025403 | 0.14006 | -0.132 | 0.025403 | south | N | 0.025403 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.021988 | south | 0.16213 | -0.025403 | 0.14006 | -0.132 | 0.025403 | south | N | 0.025403 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.021988 | south | 0.16213 | -0.025403 | 0.14006 | -0.132 | 0.025403 | south | N | 0.025403 | 0
7810 | L_RIONOG | 1 | 142 | 0.046659 | south | 0.1868 | -0.0007317 | 0.16473 | -0.10732 | 0.0007317 | south | N | 0.0007317 | 0
7811 | L_RIONOG | 2 | 145 | 0.046659 | south | 0.1868 | -0.0007317 | 0.16473 | -0.10732 | 0.0007317 | south | N | 0.0007317 | 0
7812 | L_RIONOG | 3 | 151 | 0.046659 | south | 0.1868 | -0.0007317 | 0.16473 | -0.10732 | 0.0007317 | south | N | 0.0007317 | 0
7813 | L_RIONOG | 4 | 290 | 0.046659 | south | 0.1868 | -0.0007317 | 0.16473 | -0.10732 | 0.0007317 | south | N | 0.0007317 | 0
8032 | AMISTADH | 1 | 33 | 0.007918 | south | 0.14806 | -0.039473 | 0.12599 | -0.14607 | 0.039473 | south | N | 0.039473 | 0
8033 | AMISTADH | 2 | 25 | 0.007918 | south | 0.14806 | -0.039473 | 0.12599 | -0.14607 | 0.039473 | south | N | 0.039473 | 0
8048 | FALCONHY | 1 | 12 | 0.071837 | south | 0.21198 | 0.024446 | 0.18991 | -0.082146 | 0.024446 | south | N | 0.024446 | 0
8066 | DUP1V#1 | 1 | 73 | 0.082642 | south | 0.22278 | 0.035251 | 0.20071 | -0.071341 | 0.035251 | south | N | 0.035251 | 0
8134 | FOR69CG0 | 1 | 79 | 0.091248 | south | 0.23139 | 0.043857 | 0.20932 | -0.062735 | 0.043857 | south | N | 0.043857 | 0
8138 | FOR69CG0 | 2 | 81 | 0.091248 | south | 0.23139 | 0.043857 | 0.20932 | -0.062735 | 0.043857 | south | N | 0.043857 | 0
8139 | JOS #1 | MB | 255 | 0 | south | 0.14014 | -0.047391 | 0.11807 | -0.15398 | 0.047391 | south | N | 0.047391 | 0
8147 | UCAR #2 | 10 | 28 | 0.086547 | south | 0.22669 | 0.039156 | 0.20462 | -0.067436 | 0.039156 | south | N | 0.039156 | 0
8148 | UCAR #1 | 2 | 7 | 0.086547 | south | 0.22669 | 0.039156 | 0.20462 | -0.067436 | 0.039156 | south | N | 0.039156 | 0
8153 | FOR69CG0 | 3 | 79 | 0.091248 | south | 0.23139 | 0.043857 | 0.20932 | -0.062735 | 0.043857 | south | N | 0.043857 | 0
8154 | FOR69CG0 | 4 | 80 | 0.091248 | south | 0.23139 | 0.043857 | 0.20932 | -0.062735 | 0.043857 | south | N | 0.043857 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.091248 | south | 0.23139 | 0.043857 | 0.20932 | -0.062735 | 0.043857 | south | N | 0.043857 | 0
8156 | FOR69CG0 | 6 | 25 | 0.091248 | south | 0.23139 | 0.043857 | 0.20932 | -0.062735 | 0.043857 | south | N | 0.043857 | 0
8157 | FOR69CG0 | 7 | 46 | 0.091248 | south | 0.23139 | 0.043857 | 0.20932 | -0.062735 | 0.043857 | south | N | 0.043857 | 0
8161 | COLETOU1 | 1 | 629 | 0.074463 | south | 0.21461 | 0.027072 | 0.19254 | -0.07952 | 0.027072 | south | N | 0.027072 | 0
8173 | VICEC51A | 5 | 144 | 0.081194 | south | 0.22134 | 0.033803 | 0.19927 | -0.072789 | 0.033803 | south | N | 0.033803 | 0
8174 | VICEC61A | 6 | 188 | 0.081194 | south | 0.22134 | 0.033803 | 0.19927 | -0.072789 | 0.033803 | south | N | 0.033803 | 0
8189 | CUERO 2 | 1 | 12 | 0.057222 | south | 0.19736 | 0.0098313 | 0.17529 | -0.096761 | 0.0098313 | south | N | 0.0098313 | 0
8262 | ELPS | 1 | 6 | 0.022849 | south | 0.16299 | -0.024542 | 0.14092 | -0.13113 | 0.024542 | south | N | 0.024542 | 0
8285 | LAR #1 | MB | 32 | 0 | south | 0.14014 | -0.047391 | 0.11807 | -0.15398 | 0.047391 | south | N | 0.047391 | 0
8287 | LAR #2 | MB | 32 | 0 | south | 0.14014 | -0.047391 | 0.11807 | -0.15398 | 0.047391 | south | N | 0.047391 | 0
8288 | LAR #3 | MB | 105 | 0 | south | 0.14014 | -0.047391 | 0.11807 | -0.15398 | 0.047391 | south | N | 0.047391 | 0
8388 | BATES0A | MB | 70 | 0 | south | 0.14014 | -0.047391 | 0.11807 | -0.15398 | 0.047391 | south | N | 0.047391 | 0
8393 | BATES0B | MB | 110 | 0 | south | 0.14014 | -0.047391 | 0.11807 | -0.15398 | 0.047391 | south | N | 0.047391 | 0
8442 | NBEC71A | 1 | 336 | 0.079598 | south | 0.21974 | 0.032207 | 0.19767 | -0.074385 | 0.032207 | south | N | 0.032207 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | 0.14014 | -0.047391 | 0.11807 | -0.15398 | 0.047391 | south | N | 0.047391 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | 0.14014 | -0.047391 | 0.11807 | -0.15398 | 0.047391 | south | N | 0.047391 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.079271 | south | 0.21941 | 0.03188 | 0.19734 | -0.074712 | 0.03188 | south | N | 0.03188 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.079271 | south | 0.21941 | 0.03188 | 0.19734 | -0.074712 | 0.03188 | south | N | 0.03188 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.079021 | south | 0.21916 | 0.03163 | 0.19709 | -0.074962 | 0.03163 | south | N | 0.03163 | 0
8506 | VAL #1 | 1 | 25 | 0.079187 | south | 0.21933 | 0.031796 | 0.19726 | -0.074796 | 0.031796 | south | N | 0.031796 | 0
8507 | VAL #2 | 2 | 25 | 0.079187 | south | 0.21933 | 0.031796 | 0.19726 | -0.074796 | 0.031796 | south | N | 0.031796 | 0
8511 | OXY_CC0A | 1 | 38 | 0.07907 | south | 0.21921 | 0.031679 | 0.19714 | -0.074913 | 0.031679 | south | N | 0.031679 | 0
8517 | CELANEBI | 1 | 29 | 0.078315 | south | 0.21846 | 0.030924 | 0.19639 | -0.075668 | 0.030924 | south | N | 0.030924 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.079581 | south | 0.21972 | 0.03219 | 0.19765 | -0.074402 | 0.03219 | south | N | 0.03219 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.079581 | south | 0.21972 | 0.03219 | 0.19765 | -0.074402 | 0.03219 | south | N | 0.03219 | 0
8562 | CNOPST1 | 3 | 153 | 0.079581 | south | 0.21972 | 0.03219 | 0.19765 | -0.074402 | 0.03219 | south | N | 0.03219 | 0
8926 | LGE_GT10 | 1 | 158 | 0.08111 | south | 0.22125 | 0.033719 | 0.19918 | -0.072873 | 0.033719 | south | N | 0.033719 | 0
8927 | LGE_GT20 | 2 | 153 | 0.08111 | south | 0.22125 | 0.033719 | 0.19918 | -0.072873 | 0.033719 | south | N | 0.033719 | 0
8928 | LGE_STG0 | 3 | 100 | 0.08111 | south | 0.22125 | 0.033719 | 0.19918 | -0.072873 | 0.033719 | south | N | 0.033719 | 0
8930 | ICPGN10A | 1 | 145 | 0.08111 | south | 0.22125 | 0.033719 | 0.19918 | -0.072873 | 0.033719 | south | N | 0.033719 | 0
8931 | ICPGN20A | 2 | 147 | 0.08111 | south | 0.22125 | 0.033719 | 0.19918 | -0.072873 | 0.033719 | south | N | 0.033719 | 0
8932 | ICPGN30A | 3 | 127 | 0.08111 | south | 0.22125 | 0.033719 | 0.19918 | -0.072873 | 0.033719 | south | N | 0.033719 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.076467 | south | 0.21661 | 0.029076 | 0.19454 | -0.077516 | 0.029076 | south | N | 0.029076 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.076467 | south | 0.21661 | 0.029076 | 0.19454 | -0.077516 | 0.029076 | south | N | 0.029076 | 0
8935 | FGNTS201 | 3 | 173 | 0.076467 | south | 0.21661 | 0.029076 | 0.19454 | -0.077516 | 0.029076 | south | N | 0.029076 | 0
8936 | MVGN#1 | 1 | 207 | 0.077228 | south | 0.21737 | 0.029837 | 0.1953 | -0.076755 | 0.029837 | south | N | 0.029837 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.077228 | south | 0.21737 | 0.029837 | 0.1953 | -0.076755 | 0.029837 | south | N | 0.029837 | 0
8938 | MVGN#3 | 3 | 242 | 0.077228 | south | 0.21737 | 0.029837 | 0.1953 | -0.076755 | 0.029837 | south | N | 0.029837 | 0
8981 | HECN1 | 1 | 144 | 0.077233 | south | 0.21738 | 0.029842 | 0.19531 | -0.07675 | 0.029842 | south | N | 0.029842 | 0
8982 | HECN2 | 2 | 144 | 0.077233 | south | 0.21738 | 0.029842 | 0.19531 | -0.07675 | 0.029842 | south | N | 0.029842 | 0
8983 | HECN3 | 3 | 171 | 0.077233 | south | 0.21738 | 0.029842 | 0.19531 | -0.07675 | 0.029842 | south | N | 0.029842 | 0
9000 | DECKR_G1 | 1 | 310 | 0.0127 | south | 0.15284 | -0.034691 | 0.13077 | -0.14128 | 0.034691 | south | N | 0.034691 | 0
9001 | DECKR_G2 | 2 | 413 | 0.0127 | south | 0.15284 | -0.034691 | 0.13077 | -0.14128 | 0.034691 | south | N | 0.034691 | 0
9002 | DECKR_G3 | 3 | 42 | 0.01132 | south | 0.15146 | -0.036071 | 0.12939 | -0.14266 | 0.036071 | south | N | 0.036071 | 0
9003 | DECKR_G4 | 4 | 44 | 0.01132 | south | 0.15146 | -0.036071 | 0.12939 | -0.14266 | 0.036071 | south | N | 0.036071 | 0
9004 | DECKR_G5 | 5 | 44 | 0.01132 | south | 0.15146 | -0.036071 | 0.12939 | -0.14266 | 0.036071 | south | N | 0.036071 | 0
9005 | DECKR_G6 | 6 | 47 | 0.01132 | south | 0.15146 | -0.036071 | 0.12939 | -0.14266 | 0.036071 | south | N | 0.036071 | 0
9016 | SANDH_G1 | 1 | 49 | 0.014872 | south | 0.15501 | -0.032519 | 0.13294 | -0.13911 | 0.032519 | south | N | 0.032519 | 0
9017 | SANDH_G2 | 2 | 46 | 0.014872 | south | 0.15501 | -0.032519 | 0.13294 | -0.13911 | 0.032519 | south | N | 0.032519 | 0
9018 | SANDH_G3 | 3 | 46 | 0.014872 | south | 0.15501 | -0.032519 | 0.13294 | -0.13911 | 0.032519 | south | N | 0.032519 | 0
9019 | SANDH_G4 | 4 | 47 | 0.014872 | south | 0.15501 | -0.032519 | 0.13294 | -0.13911 | 0.032519 | south | N | 0.032519 | 0
9020 | SANDHG5A | 5A | 154 | 0.014872 | south | 0.15501 | -0.032519 | 0.13294 | -0.13911 | 0.032519 | south | N | 0.032519 | 0
9021 | SANDHG5C | 5C | 148 | 0.014872 | south | 0.15501 | -0.032519 | 0.13294 | -0.13911 | 0.032519 | south | N | 0.032519 | 0
9022 | SANDH_G6 | 6 | 48 | 0.014872 | south | 0.15501 | -0.032519 | 0.13294 | -0.13911 | 0.032519 | south | N | 0.032519 | 0
9023 | SANDH_G7 | 7 | 48 | 0.014872 | south | 0.15501 | -0.032519 | 0.13294 | -0.13911 | 0.032519 | south | N | 0.032519 | 0
11001 | NAV1CT | 1 | 70 | -0.11807 | west | 0.022073 | -0.16546 | 2.0156e-06 | -0.27205 | 2.0156e-06 | west | N | 2.0156e-06 | 0
11009 | NAV2CT | 1 | 70 | -0.11807 | west | 0.022073 | -0.16546 | 2.0156e-06 | -0.27205 | 2.0156e-06 | west | N | 2.0156e-06 | 0
11011 | NAV3ST | 1 | 92.8 | -0.11807 | west | 0.022073 | -0.16546 | 2.0156e-06 | -0.27205 | 2.0156e-06 | west | N | 2.0156e-06 | 0
11012 | NAV4CT | 1 | 80 | -0.11807 | west | 0.022073 | -0.16546 | 2.0156e-06 | -0.27205 | 2.0156e-06 | west | N | 2.0156e-06 | 0
11013 | NAV5CT | 1 | 80 | -0.11807 | west | 0.022073 | -0.16546 | 2.0156e-06 | -0.27205 | 2.0156e-06 | west | N | 2.0156e-06 | 0
11014 | NAV6ST | 1 | 115 | -0.11807 | west | 0.022073 | -0.16546 | 2.0156e-06 | -0.27205 | 2.0156e-06 | west | N | 2.0156e-06 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.11806 | west | 0.022085 | -0.16545 | 1.4016e-05 | -0.27204 | 1.4016e-05 | west | N | 1.4016e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.11806 | west | 0.022085 | -0.16545 | 1.4016e-05 | -0.27204 | 1.4016e-05 | west | N | 1.4016e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.11806 | west | 0.022085 | -0.16545 | 1.4016e-05 | -0.27204 | 1.4016e-05 | west | N | 1.4016e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.11806 | west | 0.022085 | -0.16545 | 1.4016e-05 | -0.27204 | 1.4016e-05 | west | N | 1.4016e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.11806 | west | 0.022085 | -0.16545 | 1.4016e-05 | -0.27204 | 1.4016e-05 | west | N | 1.4016e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.11806 | west | 0.022085 | -0.16545 | 1.4016e-05 | -0.27204 | 1.4016e-05 | west | N | 1.4016e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.12029 | west | 0.019853 | -0.16768 | -0.002218 | -0.27427 | 0.002218 | west | N | 0.002218 | 0
11057 | CHAMPION | 1 | 126.5 | -0.12029 | west | 0.019853 | -0.16768 | -0.002218 | -0.27427 | 0.002218 | west | N | 0.002218 | 0
11058 | PYRON_1G | 1 | 249 | -0.12029 | west | 0.019853 | -0.16768 | -0.002218 | -0.27427 | 0.002218 | west | N | 0.002218 | 0
11059 | INADALE_ | 1 | 197 | -0.12029 | west | 0.019853 | -0.16768 | -0.002218 | -0.27427 | 0.002218 | west | N | 0.002218 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.11916 | west | 0.020983 | -0.16655 | -0.001088 | -0.27314 | 0.001088 | west | N | 0.001088 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.11916 | west | 0.020983 | -0.16655 | -0.001088 | -0.27314 | 0.001088 | west | N | 0.001088 | 0
11147 | NOTREES_ | 1 | 149 | -0.11709 | west | 0.023053 | -0.16448 | 0.00098202 | -0.27107 | 0.00098202 | west | N | 0.00098202 | 0
11309 | BULLCREK | 1 | 180 | -0.11895 | west | 0.021197 | -0.16634 | -0.00087398 | -0.27293 | 0.00087398 | west | N | 0.00087398 | 0
11310 | BULLCREK | 1 | 180 | -0.11895 | west | 0.021197 | -0.16634 | -0.00087398 | -0.27293 | 0.00087398 | west | N | 0.00087398 | 0
11320 | COYOTE_1 | 1 | 225 | -0.11888 | west | 0.021262 | -0.16627 | -0.00080898 | -0.27286 | 0.00080898 | west | N | 0.00080898 | 0
11415 | LORAINE_ | 1 | 125 | -0.11982 | west | 0.02032 | -0.16721 | -0.001751 | -0.27381 | 0.001751 | west | N | 0.001751 | 0
11416 | LORAINE_ | 1 | 125 | -0.11982 | west | 0.02032 | -0.16721 | -0.001751 | -0.27381 | 0.001751 | west | N | 0.001751 | 0
11691 | KMICHICT | 1 | 140 | -0.1353 | north | 0.0048419 | -0.18269 | -0.017229 | -0.28928 | 0.0048419 | North | N | 0.0048419 | 0
11692 | KMICHICT | 2 | 141 | -0.1353 | north | 0.0048419 | -0.18269 | -0.017229 | -0.28928 | 0.0048419 | North | N | 0.0048419 | 0
11693 | KMICHIST | 3 | 309 | -0.1353 | north | 0.0048419 | -0.18269 | -0.017229 | -0.28928 | 0.0048419 | North | N | 0.0048419 | 0
11694 | KMICHICT | 4 | 143 | -0.1353 | north | 0.0048419 | -0.18269 | -0.017229 | -0.28928 | 0.0048419 | North | N | 0.0048419 | 0
11695 | KMICHICT | 5 | 144 | -0.1353 | north | 0.0048419 | -0.18269 | -0.017229 | -0.28928 | 0.0048419 | North | N | 0.0048419 | 0
11696 | KMICHIST | 6 | 310 | -0.1353 | north | 0.0048419 | -0.18269 | -0.017229 | -0.28928 | 0.0048419 | North | N | 0.0048419 | 0
12322 | ENNSTRAC | 1 | 196 | -0.13337 | north | 0.0067739 | -0.18076 | -0.015297 | -0.28735 | 0.0067739 | North | N | 0.0067739 | 0
12323 | ENNSTRAC | 2 | 111 | -0.13337 | north | 0.0067739 | -0.18076 | -0.015297 | -0.28735 | 0.0067739 | North | N | 0.0067739 | 0
12357 | RNRTPL_1 | 1 | 0 | -0.13449 | north | 0.0056489 | -0.18188 | -0.016422 | -0.28848 | 0.0056489 | North | N | 0.0056489 | 0
12411 | FPLEFR1A | 1 | 161 | -0.13702 | north | 0.0031199 | -0.18441 | -0.018951 | -0.29101 | 0.0031199 | North | N | 0.0031199 | 0
12412 | FPLEFR1B | 2 | 164 | -0.13702 | north | 0.0031199 | -0.18441 | -0.018951 | -0.29101 | 0.0031199 | North | N | 0.0031199 | 0
12413 | FPLEFR1C | 3 | 164 | -0.13702 | north | 0.0031199 | -0.18441 | -0.018951 | -0.29101 | 0.0031199 | North | N | 0.0031199 | 0
12414 | FPLEFR1S | 4 | 414 | -0.13702 | north | 0.0031199 | -0.18441 | -0.018951 | -0.29101 | 0.0031199 | North | N | 0.0031199 | 0
12421 | FPLEFR2A | 1 | 162 | -0.13702 | north | 0.0031199 | -0.18441 | -0.018951 | -0.29101 | 0.0031199 | North | N | 0.0031199 | 0
12422 | FPLEFR2B | 2 | 161 | -0.13702 | north | 0.0031199 | -0.18441 | -0.018951 | -0.29101 | 0.0031199 | North | N | 0.0031199 | 0
12423 | FPLEFR2C | 3 | 163 | -0.13702 | north | 0.0031199 | -0.18441 | -0.018951 | -0.29101 | 0.0031199 | North | N | 0.0031199 | 0
12424 | FPLEFR2S | 4 | 409 | -0.13702 | north | 0.0031199 | -0.18441 | -0.018951 | -0.29101 | 0.0031199 | North | N | 0.0031199 | 0
12440 | PARKD_1S | 1 | 0 | -0.13584 | north | 0.0042989 | -0.18323 | -0.017772 | -0.28983 | 0.0042989 | North | N | 0.0042989 | 0
12449 | PARKD_2S | 1 | 0 | -0.13584 | north | 0.0042989 | -0.18323 | -0.017772 | -0.28983 | 0.0042989 | North | N | 0.0042989 | 0
13116 | TGATEWAY | 1 | 148 | -0.14173 | north | -0.0015911 | -0.18912 | -0.023662 | -0.29572 | 0.0015911 | North | N | 0.0015911 | 0
13117 | TGATEWAY | 2 | 130 | -0.14173 | north | -0.0015911 | -0.18912 | -0.023662 | -0.29572 | 0.0015911 | North | N | 0.0015911 | 0
13118 | TGATEWAY | 3 | 145 | -0.14173 | north | -0.0015911 | -0.18912 | -0.023662 | -0.29572 | 0.0015911 | North | N | 0.0015911 | 0
13119 | TGATEWAY | 4 | 399 | -0.14173 | north | -0.0015911 | -0.18912 | -0.023662 | -0.29572 | 0.0015911 | North | N | 0.0015911 | 0
13131 | CALFREST | 1 | 150.7 | -0.14872 | north | -0.0085801 | -0.19611 | -0.030651 | -0.30271 | 0.0085801 | North | N | 0.0085801 | 0
13132 | CALFREST | 2 | 151 | -0.14872 | north | -0.0085801 | -0.19611 | -0.030651 | -0.30271 | 0.0085801 | North | N | 0.0085801 | 0
13133 | CALFREST | 3 | 177.4 | -0.14872 | north | -0.0085801 | -0.19611 | -0.030651 | -0.30271 | 0.0085801 | North | N | 0.0085801 | 0
13134 | CALFREST | 4 | 151.5 | -0.14846 | north | -0.0083121 | -0.19585 | -0.030383 | -0.30244 | 0.0083121 | North | N | 0.0083121 | 0
13135 | CALFREST | 5 | 152.3 | -0.14846 | north | -0.0083121 | -0.19585 | -0.030383 | -0.30244 | 0.0083121 | North | N | 0.0083121 | 0
13136 | CALFREST | 6 | 177.5 | -0.14846 | north | -0.0083121 | -0.19585 | -0.030383 | -0.30244 | 0.0083121 | North | N | 0.0083121 | 0
13432 | SANDOW_5 | 5 | 581 | -0.026032 | south | 0.11411 | -0.073423 | 0.09204 | -0.18002 | 0.073423 | south | N | 0.073423 | 0
13691 | OAKGROVE | 1 | 855 | -0.17755 | north | -0.037408 | -0.22494 | -0.059479 | -0.33153 | 0.037408 | North | N | 0.037408 | 0
13692 | OAKGROVE | 2 | 855 | -0.17755 | north | -0.037408 | -0.22494 | -0.059479 | -0.33153 | 0.037408 | North | N | 0.037408 | 0
32798 | BRYN_TAM | 1 | 32 | -0.19039 | north | -0.050248 | -0.23778 | -0.072319 | -0.34437 | 0.050248 | North | N | 0.050248 | 0
32883 | BRYN_DNS | 1 | 48 | -0.18539 | north | -0.045245 | -0.23278 | -0.067316 | -0.33937 | 0.045245 | North | N | 0.045245 | 0
32884 | BRYN_DNS | 1 | 46 | -0.18539 | north | -0.045245 | -0.23278 | -0.067316 | -0.33937 | 0.045245 | North | N | 0.045245 | 0
32886 | BRYN_ATK | MB | 12 | -0.18995 | north | -0.049808 | -0.23734 | -0.071879 | -0.34393 | 0.049808 | North | N | 0.049808 | 0
32887 | BRYN_ATK | MB | 51 | -0.18995 | north | -0.049808 | -0.23734 | -0.071879 | -0.34393 | 0.049808 | North | N | 0.049808 | 0
32888 | BRYN_ATK | 1 | 17 | -0.18995 | north | -0.049808 | -0.23734 | -0.071879 | -0.34393 | 0.049808 | North | N | 0.049808 | 0
32890 | BRYN_ATK | MB | 22 | -0.18995 | north | -0.049808 | -0.23734 | -0.071879 | -0.34393 | 0.049808 | North | N | 0.049808 | 0
32891 | BRYN_ATK | MB | 25 | -0.18995 | north | -0.049808 | -0.23734 | -0.071879 | -0.34393 | 0.049808 | North | N | 0.049808 | 0
32892 | BRYN_DNS | 1 | 105 | -0.18539 | north | -0.045245 | -0.23278 | -0.067316 | -0.33937 | 0.045245 | North | N | 0.045245 | 0
36998 | RDCNYNG1 | 1 | 84 | -0.11959 | west | 0.020552 | -0.16698 | -0.001519 | -0.27357 | 0.001519 | west | N | 0.001519 | 0
38332 | WDWRDU2 | 1 | 80 | -0.10972 | west | 0.030419 | -0.15711 | 0.008348 | -0.26371 | 0.008348 | west | N | 0.008348 | 0
38437 | TNSRBNMS | 1 | 150 | -0.10966 | west | 0.030483 | -0.15705 | 0.008412 | -0.26364 | 0.008412 | west | N | 0.008412 | 0
38438 | TNSRBNMS | 1 | 150 | -0.10966 | west | 0.030483 | -0.15705 | 0.008412 | -0.26364 | 0.008412 | west | N | 0.008412 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.1568 | houston | 0.29694 | 0.10941 | 0.27487 | 0.0028136 | 0.0028136 | houston | N | 0.0028136 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.1568 | houston | 0.29694 | 0.10941 | 0.27487 | 0.0028136 | 0.0028136 | houston | N | 0.0028136 | 0
38600 | TNBP_CGN | 5 | 53 | 0.1568 | houston | 0.29694 | 0.10941 | 0.27487 | 0.0028136 | 0.0028136 | houston | N | 0.0028136 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.1568 | houston | 0.29694 | 0.10941 | 0.27487 | 0.0028136 | 0.0028136 | houston | N | 0.0028136 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.1568 | houston | 0.29694 | 0.10941 | 0.27487 | 0.0028136 | 0.0028136 | houston | N | 0.0028136 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.1568 | houston | 0.29694 | 0.10941 | 0.27487 | 0.0028136 | 0.0028136 | houston | N | 0.0028136 | 0
38614 | TNBPAMCG | 4 | 96 | 0.1568 | houston | 0.29694 | 0.10941 | 0.27487 | 0.0028136 | 0.0028136 | houston | N | 0.0028136 | 0
38615 | TNBPAMCG | 1 | 244 | 0.1568 | houston | 0.29694 | 0.10941 | 0.27487 | 0.0028136 | 0.0028136 | houston | N | 0.0028136 | 0
38690 | TNBP_CGN | 3 | 40 | 0.1568 | houston | 0.29694 | 0.10941 | 0.27487 | 0.0028136 | 0.0028136 | houston | N | 0.0028136 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.15681 | houston | 0.29695 | 0.10942 | 0.27488 | 0.0028256 | 0.0028256 | houston | N | 0.0028256 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.15681 | houston | 0.29695 | 0.10942 | 0.27488 | 0.0028256 | 0.0028256 | houston | N | 0.0028256 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.15681 | houston | 0.29695 | 0.10942 | 0.27488 | 0.0028256 | 0.0028256 | houston | N | 0.0028256 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.15681 | houston | 0.29695 | 0.10942 | 0.27488 | 0.0028256 | 0.0028256 | houston | N | 0.0028256 | 0
39470 | TNDOWCGN | 1 | 32 | 0.15681 | houston | 0.29695 | 0.10942 | 0.27488 | 0.0028246 | 0.0028246 | houston | N | 0.0028246 | 0
39480 | TNDOWCGN | 1 | 30 | 0.15681 | houston | 0.29695 | 0.10942 | 0.27488 | 0.0028246 | 0.0028246 | houston | N | 0.0028246 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.15018 | houston | 0.29032 | 0.10279 | 0.26825 | -0.0038074 | 0.0038074 | houston | N | 0.0038074 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.15018 | houston | 0.29032 | 0.10279 | 0.26825 | -0.0038074 | 0.0038074 | houston | N | 0.0038074 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.15018 | houston | 0.29032 | 0.10279 | 0.26825 | -0.0038074 | 0.0038074 | houston | N | 0.0038074 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.15018 | houston | 0.29032 | 0.10279 | 0.26825 | -0.0038074 | 0.0038074 | houston | N | 0.0038074 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.17755 | north | -0.037408 | -0.22494 | -0.059479 | -0.33153 | 0.037408 | North | N | 0.037408 | 0
39970 | TNTNPONE | 1 | 153 | -0.17755 | north | -0.037408 | -0.22494 | -0.059479 | -0.33153 | 0.037408 | North | N | 0.037408 | 0
48500 | APD_GT1_ | 1 | 136 | 0.15319 | houston | 0.29333 | 0.1058 | 0.27126 | -0.00079143 | 0.00079143 | houston | N | 0.00079143 | 0
48510 | AK_GT1__ | 1 | 33 | 0.15412 | houston | 0.29426 | 0.10672 | 0.27219 | 0.00013157 | 0.00013157 | houston | N | 0.00013157 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.1515 | houston | 0.29164 | 0.10411 | 0.26957 | -0.0024864 | 0.0024864 | houston | N | 0.0024864 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.1515 | houston | 0.29164 | 0.10411 | 0.26957 | -0.0024864 | 0.0024864 | houston | N | 0.0024864 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.1515 | houston | 0.29164 | 0.10411 | 0.26957 | -0.0024864 | 0.0024864 | houston | N | 0.0024864 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.1515 | houston | 0.29164 | 0.10411 | 0.26957 | -0.0024864 | 0.0024864 | houston | N | 0.0024864 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.14917 | houston | 0.28931 | 0.10178 | 0.26724 | -0.0048124 | 0.0048124 | houston | N | 0.0048124 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.14917 | houston | 0.28931 | 0.10178 | 0.26724 | -0.0048124 | 0.0048124 | houston | N | 0.0048124 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.17009 | houston | 0.31023 | 0.1227 | 0.28816 | 0.016103 | 0.016103 | houston | N | 0.016103 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.17009 | houston | 0.31023 | 0.1227 | 0.28816 | 0.016103 | 0.016103 | houston | N | 0.016103 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.17009 | houston | 0.31023 | 0.1227 | 0.28816 | 0.016103 | 0.016103 | houston | N | 0.016103 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.15364 | houston | 0.29379 | 0.10625 | 0.27172 | -0.00033943 | 0.00033943 | houston | N | 0.00033943 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.15364 | houston | 0.29379 | 0.10625 | 0.27172 | -0.00033943 | 0.00033943 | houston | N | 0.00033943 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.15364 | houston | 0.29379 | 0.10625 | 0.27172 | -0.00033943 | 0.00033943 | houston | N | 0.00033943 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.15364 | houston | 0.29379 | 0.10625 | 0.27172 | -0.00033943 | 0.00033943 | houston | N | 0.00033943 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.15258 | houston | 0.29273 | 0.10519 | 0.27066 | -0.0013994 | 0.0013994 | houston | N | 0.0013994 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.15258 | houston | 0.29273 | 0.10519 | 0.27066 | -0.0013994 | 0.0013994 | houston | N | 0.0013994 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.15407 | houston | 0.29421 | 0.10668 | 0.27214 | 8.6569e-05 | 8.6569e-05 | houston | N | 8.6569e-05 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.15407 | houston | 0.29421 | 0.10668 | 0.27214 | 8.6569e-05 | 8.6569e-05 | houston | N | 8.6569e-05 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.15407 | houston | 0.29421 | 0.10668 | 0.27214 | 8.6569e-05 | 8.6569e-05 | houston | N | 8.6569e-05 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.15407 | houston | 0.29421 | 0.10668 | 0.27214 | 8.6569e-05 | 8.6569e-05 | houston | N | 8.6569e-05 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.15407 | houston | 0.29421 | 0.10668 | 0.27214 | 8.6569e-05 | 8.6569e-05 | houston | N | 8.6569e-05 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.14899 | houston | 0.28913 | 0.10159 | 0.26706 | -0.0049984 | 0.0049984 | houston | N | 0.0049984 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.14996 | houston | 0.2901 | 0.10257 | 0.26803 | -0.0040224 | 0.0040224 | houston | N | 0.0040224 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.14844 | houston | 0.28859 | 0.10105 | 0.26652 | -0.0055384 | 0.0055384 | houston | N | 0.0055384 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.14844 | houston | 0.28859 | 0.10105 | 0.26652 | -0.0055384 | 0.0055384 | houston | N | 0.0055384 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.14844 | houston | 0.28859 | 0.10105 | 0.26652 | -0.0055384 | 0.0055384 | houston | N | 0.0055384 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.14604 | houston | 0.28618 | 0.098645 | 0.26411 | -0.0079474 | 0.0079474 | houston | N | 0.0079474 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.15298 | houston | 0.29312 | 0.10559 | 0.27105 | -0.0010014 | 0.0010014 | houston | N | 0.0010014 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.15298 | houston | 0.29312 | 0.10559 | 0.27105 | -0.0010014 | 0.0010014 | houston | N | 0.0010014 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.1481 | houston | 0.28824 | 0.10071 | 0.26617 | -0.0058814 | 0.0058814 | houston | N | 0.0058814 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.1481 | houston | 0.28824 | 0.10071 | 0.26617 | -0.0058814 | 0.0058814 | houston | N | 0.0058814 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.1481 | houston | 0.28824 | 0.10071 | 0.26617 | -0.0058814 | 0.0058814 | houston | N | 0.0058814 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.1481 | houston | 0.28824 | 0.10071 | 0.26617 | -0.0058814 | 0.0058814 | houston | N | 0.0058814 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.15241 | houston | 0.29255 | 0.10501 | 0.27048 | -0.0015784 | 0.0015784 | houston | N | 0.0015784 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.15241 | houston | 0.29255 | 0.10501 | 0.27048 | -0.0015784 | 0.0015784 | houston | N | 0.0015784 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.15241 | houston | 0.29255 | 0.10501 | 0.27048 | -0.0015784 | 0.0015784 | houston | N | 0.0015784 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.15241 | houston | 0.29255 | 0.10501 | 0.27048 | -0.0015784 | 0.0015784 | houston | N | 0.0015784 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.15168 | houston | 0.29182 | 0.10429 | 0.26975 | -0.0023054 | 0.0023054 | houston | N | 0.0023054 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.15168 | houston | 0.29182 | 0.10429 | 0.26975 | -0.0023054 | 0.0023054 | houston | N | 0.0023054 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.15168 | houston | 0.29182 | 0.10429 | 0.26975 | -0.0023054 | 0.0023054 | houston | N | 0.0023054 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.15168 | houston | 0.29182 | 0.10429 | 0.26975 | -0.0023054 | 0.0023054 | houston | N | 0.0023054 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.15168 | houston | 0.29182 | 0.10429 | 0.26975 | -0.0023054 | 0.0023054 | houston | N | 0.0023054 | 0
48651 | EP_1_2 | 1 | 5 | 0.14945 | houston | 0.28959 | 0.10206 | 0.26752 | -0.0045324 | 0.0045324 | houston | N | 0.0045324 | 0
48651 | EP_1_2 | 2 | 21 | 0.14945 | houston | 0.28959 | 0.10206 | 0.26752 | -0.0045324 | 0.0045324 | houston | N | 0.0045324 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.14528 | north | 0.28542 | 0.097885 | 0.26335 | -0.0087074 | 0.0087074 | houston | Y | 0.28542 | 42.6689
48672 | FTR_GT2_ | 2 | 156 | 0.14528 | north | 0.28542 | 0.097885 | 0.26335 | -0.0087074 | 0.0087074 | houston | Y | 0.28542 | 43.167
48673 | FTR_GT3_ | 3 | 156 | 0.14528 | north | 0.28542 | 0.097885 | 0.26335 | -0.0087074 | 0.0087074 | houston | Y | 0.28542 | 43.167
48674 | FTR_CN4_ | 4 | 380 | 0.14528 | north | 0.28542 | 0.097885 | 0.26335 | -0.0087074 | 0.0087074 | houston | Y | 0.28542 | 105.1504
48690 | GBY_GN5_ | 5 | 398 | 0.14965 | houston | 0.2898 | 0.10226 | 0.26773 | -0.0043294 | 0.0043294 | houston | N | 0.0043294 | 0
48691 | GBY_7374 | A | 46 | 0.15624 | houston | 0.29638 | 0.10884 | 0.27431 | 0.0022516 | 0.0022516 | houston | N | 0.0022516 | 0
48691 | GBY_7374 | B | 46 | 0.15624 | houston | 0.29638 | 0.10884 | 0.27431 | 0.0022516 | 0.0022516 | houston | N | 0.0022516 | 0
48692 | GBY_8182 | C | 46 | 0.15624 | houston | 0.29638 | 0.10884 | 0.27431 | 0.0022516 | 0.0022516 | houston | N | 0.0022516 | 0
48692 | GBY_8182 | D | 55 | 0.15624 | houston | 0.29638 | 0.10884 | 0.27431 | 0.0022516 | 0.0022516 | houston | N | 0.0022516 | 0
48693 | GBY_8384 | E | 55 | 0.15624 | houston | 0.29638 | 0.10884 | 0.27431 | 0.0022516 | 0.0022516 | houston | N | 0.0022516 | 0
48693 | GBY_8384 | F | 54 | 0.15624 | houston | 0.29638 | 0.10884 | 0.27431 | 0.0022516 | 0.0022516 | houston | N | 0.0022516 | 0
48721 | LEG_1___ | 1 | 827 | -0.16676 | north | -0.026617 | -0.21415 | -0.048688 | -0.32074 | 0.026617 | North | N | 0.026617 | 0
48722 | LEG_2___ | 2 | 819 | -0.16676 | north | -0.026617 | -0.21415 | -0.048688 | -0.32074 | 0.026617 | North | N | 0.026617 | 0
48730 | MNS_GT | 1 | 46.1 | 0.15376 | houston | 0.2939 | 0.10637 | 0.27183 | -0.00022143 | 0.00022143 | houston | N | 0.00022143 | 0
48731 | CBE_GT1 | 1 | 76 | 0.12967 | houston | 0.26981 | 0.082281 | 0.24774 | -0.024311 | 0.024311 | houston | N | 0.024311 | 0
48732 | CBE_GT2 | 1 | 76 | 0.12967 | houston | 0.26981 | 0.082281 | 0.24774 | -0.024311 | 0.024311 | houston | N | 0.024311 | 0
48733 | CBE_ST12 | 1 | 105 | 0.12967 | houston | 0.26981 | 0.082281 | 0.24774 | -0.024311 | 0.024311 | houston | N | 0.024311 | 0
48734 | CBE_GT3 | 1 | 74 | 0.12967 | houston | 0.26981 | 0.082281 | 0.24774 | -0.024311 | 0.024311 | houston | N | 0.024311 | 0
48735 | CBE_GT4 | 1 | 74 | 0.12967 | houston | 0.26981 | 0.082281 | 0.24774 | -0.024311 | 0.024311 | houston | N | 0.024311 | 0
48736 | CBE_ST34 | 1 | 102 | 0.12967 | houston | 0.26981 | 0.082281 | 0.24774 | -0.024311 | 0.024311 | houston | N | 0.024311 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.15263 | houston | 0.29277 | 0.10524 | 0.2707 | -0.0013534 | 0.0013534 | houston | N | 0.0013534 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.15263 | houston | 0.29277 | 0.10524 | 0.2707 | -0.0013534 | 0.0013534 | houston | N | 0.0013534 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.15263 | houston | 0.29277 | 0.10524 | 0.2707 | -0.0013534 | 0.0013534 | houston | N | 0.0013534 | 0
48761 | PR_GT1__ | 1 | 35 | 0.15299 | houston | 0.29313 | 0.1056 | 0.27106 | -0.00099343 | 0.00099343 | houston | N | 0.00099343 | 0
48772 | PHR_GN2_ | MB | 459 | 0.15488 | houston | 0.29502 | 0.10749 | 0.27295 | 0.00089757 | 0.00089757 | houston | N | 0.00089757 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.15023 | houston | 0.29037 | 0.10284 | 0.2683 | -0.0037524 | 0.0037524 | houston | N | 0.0037524 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.15023 | houston | 0.29037 | 0.10284 | 0.2683 | -0.0037524 | 0.0037524 | houston | N | 0.0037524 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.15023 | houston | 0.29037 | 0.10284 | 0.2683 | -0.0037524 | 0.0037524 | houston | N | 0.0037524 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.15023 | houston | 0.29037 | 0.10284 | 0.2683 | -0.0037524 | 0.0037524 | houston | N | 0.0037524 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.15023 | houston | 0.29037 | 0.10284 | 0.2683 | -0.0037524 | 0.0037524 | houston | N | 0.0037524 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.15023 | houston | 0.29037 | 0.10284 | 0.2683 | -0.0037524 | 0.0037524 | houston | N | 0.0037524 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.15023 | houston | 0.29037 | 0.10284 | 0.2683 | -0.0037524 | 0.0037524 | houston | N | 0.0037524 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.14604 | houston | 0.28618 | 0.098645 | 0.26411 | -0.0079474 | 0.0079474 | houston | N | 0.0079474 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.14604 | houston | 0.28618 | 0.098645 | 0.26411 | -0.0079474 | 0.0079474 | houston | N | 0.0079474 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.14604 | houston | 0.28618 | 0.098645 | 0.26411 | -0.0079474 | 0.0079474 | houston | N | 0.0079474 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.14604 | houston | 0.28618 | 0.098645 | 0.26411 | -0.0079474 | 0.0079474 | houston | N | 0.0079474 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.15013 | houston | 0.29027 | 0.10274 | 0.2682 | -0.0038534 | 0.0038534 | houston | N | 0.0038534 | 0
48820 | SHELLG1_ | 1 | 71 | 0.15217 | houston | 0.29231 | 0.10478 | 0.27024 | -0.0018174 | 0.0018174 | houston | N | 0.0018174 | 0
48821 | SHELLG2 | 2 | 72 | 0.15217 | houston | 0.29231 | 0.10478 | 0.27024 | -0.0018174 | 0.0018174 | houston | N | 0.0018174 | 0
48822 | SHELLG3_ | 1 | 39 | 0.15217 | houston | 0.29231 | 0.10478 | 0.27024 | -0.0018174 | 0.0018174 | houston | N | 0.0018174 | 0
48822 | SHELLG3_ | 2 | 30 | 0.15217 | houston | 0.29231 | 0.10478 | 0.27024 | -0.0018174 | 0.0018174 | houston | N | 0.0018174 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.15295 | houston | 0.29309 | 0.10556 | 0.27102 | -0.0010314 | 0.0010314 | houston | N | 0.0010314 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.15295 | houston | 0.29309 | 0.10556 | 0.27102 | -0.0010314 | 0.0010314 | houston | N | 0.0010314 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.15238 | houston | 0.29253 | 0.10499 | 0.27046 | -0.0015984 | 0.0015984 | houston | N | 0.0015984 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.15246 | houston | 0.29261 | 0.10507 | 0.27054 | -0.0015204 | 0.0015204 | houston | N | 0.0015204 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.15248 | houston | 0.29262 | 0.10509 | 0.27055 | -0.0015044 | 0.0015044 | houston | N | 0.0015044 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.15236 | houston | 0.2925 | 0.10497 | 0.27043 | -0.0016264 | 0.0016264 | houston | N | 0.0016264 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.15244 | houston | 0.29259 | 0.10505 | 0.27052 | -0.0015394 | 0.0015394 | houston | N | 0.0015394 | 0
48855 | SRB_GT21 | B2 | 12 | 0.1525 | houston | 0.29264 | 0.10511 | 0.27057 | -0.0014844 | 0.0014844 | houston | N | 0.0014844 | 0
48855 | SRB_GT21 | MB | 18 | 0.1525 | houston | 0.29264 | 0.10511 | 0.27057 | -0.0014844 | 0.0014844 | houston | N | 0.0014844 | 0
48865 | TECO_GT1 | 1 | 50 | 0.15928 | houston | 0.29942 | 0.11189 | 0.27735 | 0.0052926 | 0.0052926 | houston | N | 0.0052926 | 0
48873 | THW_ST3_ | 3 | 104 | 0.14815 | houston | 0.28829 | 0.10076 | 0.26622 | -0.0058364 | 0.0058364 | houston | N | 0.0058364 | 0
48874 | THW_ST4_ | 4 | 104 | 0.14815 | houston | 0.28829 | 0.10076 | 0.26622 | -0.0058364 | 0.0058364 | houston | N | 0.0058364 | 0
48875 | THW_3132 | A | 54 | 0.14815 | houston | 0.28829 | 0.10076 | 0.26622 | -0.0058364 | 0.0058364 | houston | N | 0.0058364 | 0
48875 | THW_3132 | B | 53 | 0.14815 | houston | 0.28829 | 0.10076 | 0.26622 | -0.0058364 | 0.0058364 | houston | N | 0.0058364 | 0
48877 | THW_3334 | C | 54 | 0.14815 | houston | 0.28829 | 0.10076 | 0.26622 | -0.0058364 | 0.0058364 | houston | N | 0.0058364 | 0
48877 | THW_3334 | D | 57 | 0.14815 | houston | 0.28829 | 0.10076 | 0.26622 | -0.0058364 | 0.0058364 | houston | N | 0.0058364 | 0
48879 | THW_4142 | E | 54 | 0.14815 | houston | 0.28829 | 0.10076 | 0.26622 | -0.0058364 | 0.0058364 | houston | N | 0.0058364 | 0
48879 | THW_4142 | F | 54 | 0.14815 | houston | 0.28829 | 0.10076 | 0.26622 | -0.0058364 | 0.0058364 | houston | N | 0.0058364 | 0
48881 | THW_4344 | G | 58 | 0.14815 | houston | 0.28829 | 0.10076 | 0.26622 | -0.0058364 | 0.0058364 | houston | N | 0.0058364 | 0
48881 | THW_4344 | H | 58 | 0.14815 | houston | 0.28829 | 0.10076 | 0.26622 | -0.0058364 | 0.0058364 | houston | N | 0.0058364 | 0
48883 | THW_GT1_ | B2 | 12 | 0.14678 | houston | 0.28693 | 0.099393 | 0.26486 | -0.0071994 | 0.0071994 | houston | N | 0.0071994 | 0
48885 | THW_5152 | A | 56 | 0.13718 | houston | 0.27733 | 0.089793 | 0.25526 | -0.016799 | 0.016799 | houston | N | 0.016799 | 0
48885 | THW_5152 | B | 59 | 0.13718 | houston | 0.27733 | 0.089793 | 0.25526 | -0.016799 | 0.016799 | houston | N | 0.016799 | 0
48886 | THW_5354 | C | 56 | 0.13718 | houston | 0.27733 | 0.089793 | 0.25526 | -0.016799 | 0.016799 | houston | N | 0.016799 | 0
48886 | THW_5354 | D | 56 | 0.13718 | houston | 0.27733 | 0.089793 | 0.25526 | -0.016799 | 0.016799 | houston | N | 0.016799 | 0
48887 | THW_5556 | E | 59 | 0.13718 | houston | 0.27733 | 0.089793 | 0.25526 | -0.016799 | 0.016799 | houston | N | 0.016799 | 0
48887 | THW_5556 | F | 56 | 0.13718 | houston | 0.27733 | 0.089793 | 0.25526 | -0.016799 | 0.016799 | houston | N | 0.016799 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.13279 | houston | 0.27294 | 0.085402 | 0.25087 | -0.02119 | 0.02119 | houston | N | 0.02119 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.15926 | houston | 0.2994 | 0.11187 | 0.27733 | 0.0052786 | 0.0052786 | houston | N | 0.0052786 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.15926 | houston | 0.2994 | 0.11187 | 0.27733 | 0.0052786 | 0.0052786 | houston | N | 0.0052786 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.15926 | houston | 0.2994 | 0.11187 | 0.27733 | 0.0052786 | 0.0052786 | houston | N | 0.0052786 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.15926 | houston | 0.2994 | 0.11187 | 0.27733 | 0.0052786 | 0.0052786 | houston | N | 0.0052786 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.15926 | houston | 0.2994 | 0.11187 | 0.27733 | 0.0052786 | 0.0052786 | houston | N | 0.0052786 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.17015 | houston | 0.31029 | 0.12276 | 0.28822 | 0.016169 | 0.016169 | houston | N | 0.016169 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.17015 | houston | 0.31029 | 0.12276 | 0.28822 | 0.016169 | 0.016169 | houston | N | 0.016169 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.17015 | houston | 0.31029 | 0.12276 | 0.28822 | 0.016169 | 0.016169 | houston | N | 0.016169 | 0
48929 | WAPGT21_ | B1 | 13 | 0.15926 | houston | 0.2994 | 0.11187 | 0.27733 | 0.0052786 | 0.0052786 | houston | N | 0.0052786 | 0
48940 | WARVUE_G | G1 | 12 | 0.14923 | houston | 0.28937 | 0.10184 | 0.2673 | -0.0047554 | 0.0047554 | houston | N | 0.0047554 | 0
49803 | EXN_15GT | 1 | 34 | 0.14995 | houston | 0.29009 | 0.10256 | 0.26802 | -0.0040334 | 0.0040334 | houston | N | 0.0040334 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.14995 | houston | 0.29009 | 0.10256 | 0.26802 | -0.0040334 | 0.0040334 | houston | N | 0.0040334 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.14995 | houston | 0.29009 | 0.10256 | 0.26802 | -0.0040334 | 0.0040334 | houston | N | 0.0040334 | 0
49826 | EXN938GT | 5 | 45.9 | 0.14995 | houston | 0.29009 | 0.10256 | 0.26802 | -0.0040334 | 0.0040334 | houston | N | 0.0040334 | 0
49828 | EXN941GT | 10 | 17.7 | 0.14995 | houston | 0.29009 | 0.10256 | 0.26802 | -0.0040334 | 0.0040334 | houston | N | 0.0040334 | 0
49829 | EXN942GT | 11 | 20.4 | 0.14995 | houston | 0.29009 | 0.10256 | 0.26802 | -0.0040334 | 0.0040334 | houston | N | 0.0040334 | 0
49830 | EXN943GT | 12 | 19.9 | 0.14995 | houston | 0.29009 | 0.10256 | 0.26802 | -0.0040334 | 0.0040334 | houston | N | 0.0040334 | 0
49831 | EXN944GT | 13 | 35 | 0.14995 | houston | 0.29009 | 0.10256 | 0.26802 | -0.0040334 | 0.0040334 | houston | N | 0.0040334 | 0
49832 | EXN945GT | 9 | 18 | 0.14995 | houston | 0.29009 | 0.10256 | 0.26802 | -0.0040334 | 0.0040334 | houston | N | 0.0040334 | 0
49837 | EXN_GT | 4 | 85.4 | 0.14995 | houston | 0.29009 | 0.10256 | 0.26802 | -0.0040334 | 0.0040334 | houston | N | 0.0040334 | 0
49838 | EXN_14GT | 14 | 148 | 0.14995 | houston | 0.29009 | 0.10256 | 0.26802 | -0.0040334 | 0.0040334 | houston | N | 0.0040334 | 0
49851 | DOW17000 | 37 | 62 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49858 | DOW38100 | 31 | 71.4 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49859 | DOW38200 | 33 | 45 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49860 | DOW38300 | 32 | 101 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49862 | DOW39100 | 36 | 86 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49863 | DOW39200 | 35 | 88 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49865 | DOW41000 | 41 | 50 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49866 | DOW42000 | 42 | 18 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49869 | DOW49000 | 45 | 94 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49870 | DOW61000 | 61 | 70 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49871 | DOW62000 | 62 | 63 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49872 | DOW63000 | 63 | 72 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49873 | DOW64000 | 64 | 64.8 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49876 | DOW65000 | 65 | 101 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49877 | DOW66000 | 66 | 97 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49878 | DOW67000 | 67 | 103 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49882 | DOW81000 | 81 | 76 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49884 | DOW82000 | 82 | 80 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49885 | DOW83000 | 83 | 80 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
49886 | DOW84000 | 84 | 171 | 0.14803 | houston | 0.28817 | 0.10064 | 0.2661 | -0.0059534 | 0.0059534 | houston | N | 0.0059534 | 0
58909 | PEARSALL | 1 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58909 | PEARSALL | 2 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58909 | PEARSALL | 3 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58909 | PEARSALL | 4 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58909 | PEARSALL | 5 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58909 | PEARSALL | 6 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58919 | PEARSALL | 1 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58919 | PEARSALL | 2 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58919 | PEARSALL | 3 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58919 | PEARSALL | 4 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58919 | PEARSALL | 5 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58919 | PEARSALL | 6 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58929 | PEARSALL | 1 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58929 | PEARSALL | 2 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58929 | PEARSALL | 3 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58929 | PEARSALL | 4 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58929 | PEARSALL | 5 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58929 | PEARSALL | 6 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58949 | PEARSALL | 1 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58949 | PEARSALL | 2 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58949 | PEARSALL | 3 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58949 | PEARSALL | 4 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58949 | PEARSALL | 5 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
58949 | PEARSALL | 6 | 8.4 | 0.051967 | south | 0.19211 | 0.0045763 | 0.17004 | -0.10202 | 0.0045763 | south | N | 0.0045763 | 0
60000 | DSKY2 | 1 | 76.5 | -0.10669 | west | 0.033458 | -0.15408 | 0.011387 | -0.26067 | 0.011387 | west | N | 0.011387 | 0
60003 | KING_NE1 | 1 | 80 | -0.10985 | west | 0.030293 | -0.15724 | 0.008222 | -0.26383 | 0.008222 | west | N | 0.008222 | 0
60005 | KING_SE1 | 1 | 40 | -0.10985 | west | 0.030293 | -0.15724 | 0.008222 | -0.26383 | 0.008222 | west | N | 0.008222 | 0
60007 | KING_SW1 | 1 | 80 | -0.11036 | west | 0.029782 | -0.15775 | 0.007711 | -0.26434 | 0.007711 | west | N | 0.007711 | 0
60016 | WOODWRD1 | 1 | 80 | -0.10974 | west | 0.030404 | -0.15713 | 0.008333 | -0.26372 | 0.008333 | west | N | 0.008333 | 0
60017 | ORNNWP1 | 1 | 80 | -0.10711 | west | 0.033032 | -0.1545 | 0.010961 | -0.26109 | 0.010961 | west | N | 0.010961 | 0
60018 | DSKY1 | 1 | 84 | -0.10625 | west | 0.033892 | -0.15364 | 0.011821 | -0.26023 | 0.011821 | west | N | 0.011821 | 0
60019 | KING_NW1 | 1 | 80 | -0.11036 | west | 0.029782 | -0.15775 | 0.007711 | -0.26434 | 0.007711 | west | N | 0.007711 | 0
60057 | CALLAHAN | 1 | 114 | 0.04339 | south | 0.18353 | -0.0040007 | 0.16146 | -0.11059 | 0.0040007 | south | N | 0.0040007 | 0
60058 | BUFF_GAP | 1 | 120 | -0.11886 | west | 0.021288 | -0.16625 | -0.00078298 | -0.27284 | 0.00078298 | west | N | 0.00078298 | 0
60060 | CIRELLO | 1 | 233 | -0.11886 | west | 0.021288 | -0.16625 | -0.00078298 | -0.27284 | 0.00078298 | west | N | 0.00078298 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.11886 | west | 0.021288 | -0.16625 | -0.00078298 | -0.27284 | 0.00078298 | west | N | 0.00078298 | 0
60066 | H_HOLLOW | 1 | 222 | 0.04339 | south | 0.18353 | -0.0040007 | 0.16146 | -0.11059 | 0.0040007 | south | N | 0.0040007 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.04339 | south | 0.18353 | -0.0040007 | 0.16146 | -0.11059 | 0.0040007 | south | N | 0.0040007 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.04339 | south | 0.18353 | -0.0040007 | 0.16146 | -0.11059 | 0.0040007 | south | N | 0.0040007 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.04339 | south | 0.18353 | -0.0040007 | 0.16146 | -0.11059 | 0.0040007 | south | N | 0.0040007 | 0
60074 | HORSH5 | 1 | 100 | 0.04339 | south | 0.18353 | -0.0040007 | 0.16146 | -0.11059 | 0.0040007 | south | N | 0.0040007 | 0
60081 | WHRLWIND | 1 | 60 | -0.12125 | west | 0.01889 | -0.16864 | -0.003181 | -0.27524 | 0.003181 | west | N | 0.003181 | 0
60201 | RIO DRCS | F | 0 | -0.021677 | south | 0.11847 | -0.069068 | 0.096395 | -0.17566 | 0.069068 | south | N | 0.069068 | 0
60202 | FRIEND_R | F | 0 | -0.092541 | west | 0.047602 | -0.13993 | 0.025531 | -0.24652 | 0.025531 | west | N | 0.025531 | 0
60203 | PRES0A | BT | 4.8 | -0.11225 | west | 0.027894 | -0.15964 | 0.005823 | -0.26623 | 0.005823 | west | N | 0.005823 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.12018 | west | 0.01996 | -0.16757 | -0.002111 | -0.27417 | 0.002111 | west | N | 0.002111 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.12018 | west | 0.01996 | -0.16757 | -0.002111 | -0.27417 | 0.002111 | west | N | 0.002111 | 0
71057 | L_SWEETW | W1 | 135 | -0.12018 | west | 0.01996 | -0.16757 | -0.002111 | -0.27417 | 0.002111 | west | N | 0.002111 | 0
71059 | L_SWEETW | W1 | 119 | -0.12018 | west | 0.01996 | -0.16757 | -0.002111 | -0.27417 | 0.002111 | west | N | 0.002111 | 0
71060 | L_SWEETW | W1 | 105 | -0.12018 | west | 0.01996 | -0.16757 | -0.002111 | -0.27417 | 0.002111 | west | N | 0.002111 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.12018 | west | 0.01996 | -0.16757 | -0.002111 | -0.27417 | 0.002111 | west | N | 0.002111 | 0
76031 | L_GASCCR | W1 | 150 | -0.11809 | west | 0.022054 | -0.16548 | -1.6984e-05 | -0.27207 | 1.6984e-05 | west | N | 1.6984e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.11782 | west | 0.022319 | -0.16521 | 0.00024802 | -0.27181 | 0.00024802 | west | N | 0.00024802 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.11782 | west | 0.022319 | -0.16521 | 0.00024802 | -0.27181 | 0.00024802 | west | N | 0.00024802 | 0
76096 | L_CAPRSI | W1 | 186 | -0.11782 | west | 0.022319 | -0.16521 | 0.00024802 | -0.27181 | 0.00024802 | west | N | 0.00024802 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.11782 | west | 0.022319 | -0.16521 | 0.00024802 | -0.27181 | 0.00024802 | west | N | 0.00024802 | 0
80003 | MILHWYS | F | 0 | 0.077775 | south | 0.21792 | 0.030384 | 0.19585 | -0.076208 | 0.030384 | south | N | 0.030384 | 0
80010 | EPLVT1 | F | 0 | 0.026322 | south | 0.16646 | -0.021069 | 0.14439 | -0.12766 | 0.021069 | south | N | 0.021069 | 0
80012 | LAR | F | 0 | 0.060791 | south | 0.20093 | 0.0134 | 0.17886 | -0.093192 | 0.0134 | south | N | 0.0134 | 0
80051 | FORPVCM0 | 8 | 28 | 0.091248 | south | 0.23139 | 0.043857 | 0.20932 | -0.062735 | 0.043857 | south | N | 0.043857 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.091248 | south | 0.23139 | 0.043857 | 0.20932 | -0.062735 | 0.043857 | south | N | 0.043857 | 0
80053 | FOR69CG0 | 10 | 74 | 0.091248 | south | 0.23139 | 0.043857 | 0.20932 | -0.062735 | 0.043857 | south | N | 0.043857 | 0
80080 | GWINDT11 | 1 | 94 | 0.077981 | south | 0.21812 | 0.03059 | 0.19605 | -0.076002 | 0.03059 | south | N | 0.03059 | 0
80080 | GWINDT11 | 2 | 41 | 0.077981 | south | 0.21812 | 0.03059 | 0.19605 | -0.076002 | 0.03059 | south | N | 0.03059 | 0
80080 | GWINDT11 | 3 | 38 | 0.077981 | south | 0.21812 | 0.03059 | 0.19605 | -0.076002 | 0.03059 | south | N | 0.03059 | 0
80080 | GWINDT11 | 4 | 19 | 0.077981 | south | 0.21812 | 0.03059 | 0.19605 | -0.076002 | 0.03059 | south | N | 0.03059 | 0
80081 | GWINDT21 | 1 | 94 | 0.077981 | south | 0.21812 | 0.03059 | 0.19605 | -0.076002 | 0.03059 | south | N | 0.03059 | 0
80081 | GWINDT21 | 2 | 36 | 0.077981 | south | 0.21812 | 0.03059 | 0.19605 | -0.076002 | 0.03059 | south | N | 0.03059 | 0
80081 | GWINDT21 | 3 | 43 | 0.077981 | south | 0.21812 | 0.03059 | 0.19605 | -0.076002 | 0.03059 | south | N | 0.03059 | 0
80081 | GWINDT21 | 4 | 22 | 0.077981 | south | 0.21812 | 0.03059 | 0.19605 | -0.076002 | 0.03059 | south | N | 0.03059 | 0
80137 | CSDR89 | 8 | 39 | 0.086547 | south | 0.22669 | 0.039156 | 0.20462 | -0.067436 | 0.039156 | south | N | 0.039156 | 0
80137 | CSDR89 | 9 | 15 | 0.086547 | south | 0.22669 | 0.039156 | 0.20462 | -0.067436 | 0.039156 | south | N | 0.039156 | 0
80138 | CSDR7 | 7 | 7 | 0.086547 | south | 0.22669 | 0.039156 | 0.20462 | -0.067436 | 0.039156 | south | N | 0.039156 | 0
80139 | CSDR56 | 5 | 15 | 0.086547 | south | 0.22669 | 0.039156 | 0.20462 | -0.067436 | 0.039156 | south | N | 0.039156 | 0
80139 | CSDR56 | 6 | 39 | 0.086547 | south | 0.22669 | 0.039156 | 0.20462 | -0.067436 | 0.039156 | south | N | 0.039156 | 0
80140 | CSDR11 | 11 | 39 | 0.086546 | south | 0.22669 | 0.039155 | 0.20462 | -0.067437 | 0.039155 | south | N | 0.039155 | 0
80180 | PNSCALT1 | 1 | 148 | 0.077981 | south | 0.21812 | 0.03059 | 0.19605 | -0.076002 | 0.03059 | south | N | 0.03059 | 0
80180 | PNSCALT1 | 2 | 50 | 0.077981 | south | 0.21812 | 0.03059 | 0.19605 | -0.076002 | 0.03059 | south | N | 0.03059 | 0
80181 | PNSCALT2 | 1 | 55 | 0.077981 | south | 0.21812 | 0.03059 | 0.19605 | -0.076002 | 0.03059 | south | N | 0.03059 | 0
80181 | PNSCALT2 | 2 | 50 | 0.077981 | south | 0.21812 | 0.03059 | 0.19605 | -0.076002 | 0.03059 | south | N | 0.03059 | 0
80223 | REYSHR G | 1 | 12 | 0.08111 | south | 0.22125 | 0.033719 | 0.19918 | -0.072873 | 0.033719 | south | N | 0.033719 | 0
80224 | VISTRONG | 1 | 15 | 0.085121 | south | 0.22526 | 0.03773 | 0.20319 | -0.068862 | 0.03773 | south | N | 0.03773 | 0
80225 | VISTRONG | 2 | 23 | 0.085121 | south | 0.22526 | 0.03773 | 0.20319 | -0.068862 | 0.03773 | south | N | 0.03773 | 0
80226 | ALCOA G | 1 | 48 | 0.090158 | south | 0.2303 | 0.042767 | 0.20823 | -0.063825 | 0.042767 | south | N | 0.042767 | 0
80227 | AIRCO G | 1 | 8 | 0.086006 | south | 0.22615 | 0.038615 | 0.20408 | -0.067977 | 0.038615 | south | N | 0.038615 | 0
80261 | NBEC81A | 1 | 180 | 0.079552 | south | 0.21969 | 0.032161 | 0.19762 | -0.074431 | 0.032161 | south | N | 0.032161 | 0
80262 | NBEC91A | 1 | 180 | 0.079598 | south | 0.21974 | 0.032207 | 0.19767 | -0.074385 | 0.032207 | south | N | 0.032207 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.079271 | south | 0.21941 | 0.03188 | 0.19734 | -0.074712 | 0.03188 | south | N | 0.03188 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.079271 | south | 0.21941 | 0.03188 | 0.19734 | -0.074712 | 0.03188 | south | N | 0.03188 | 0
80265 | LARECU40 | 4 | 100 | 0.060787 | south | 0.20093 | 0.013396 | 0.17886 | -0.093196 | 0.013396 | south | N | 0.013396 | 0
80266 | LARECU50 | 5 | 100 | 0.060787 | south | 0.20093 | 0.013396 | 0.17886 | -0.093196 | 0.013396 | south | N | 0.013396 | 0
80291 | PAPALOTE | 1 | 25 | 0.080508 | south | 0.22065 | 0.033117 | 0.19858 | -0.073475 | 0.033117 | south | N | 0.033117 | 0
80291 | PAPALOTE | 2 | 25 | 0.080508 | south | 0.22065 | 0.033117 | 0.19858 | -0.073475 | 0.033117 | south | N | 0.033117 | 0
80291 | PAPALOTE | 3 | 25 | 0.080508 | south | 0.22065 | 0.033117 | 0.19858 | -0.073475 | 0.033117 | south | N | 0.033117 | 0
80291 | PAPALOTE | 4 | 16 | 0.080508 | south | 0.22065 | 0.033117 | 0.19858 | -0.073475 | 0.033117 | south | N | 0.033117 | 0
80294 | PAPALOTE | 5 | 25 | 0.080508 | south | 0.22065 | 0.033117 | 0.19858 | -0.073475 | 0.033117 | south | N | 0.033117 | 0
80294 | PAPALOTE | 6 | 25 | 0.080508 | south | 0.22065 | 0.033117 | 0.19858 | -0.073475 | 0.033117 | south | N | 0.033117 | 0
80294 | PAPALOTE | 7 | 25 | 0.080508 | south | 0.22065 | 0.033117 | 0.19858 | -0.073475 | 0.033117 | south | N | 0.033117 | 0
80294 | PAPALOTE | 8 | 15 | 0.080508 | south | 0.22065 | 0.033117 | 0.19858 | -0.073475 | 0.033117 | south | N | 0.033117 | 0
86104 | CID-138 | EQ | 0 | 0.060787 | south | 0.20093 | 0.013396 | 0.17886 | -0.093196 | 0.013396 | south | N | 0.013396 | 0
86105 | CID-230 | EQ | 500 | 0.060787 | south | 0.20093 | 0.013396 | 0.17886 | -0.093196 | 0.013396 | south | N | 0.013396 | 0
86106 | CUF-230 | EQ | 500 | 0.060787 | south | 0.20093 | 0.013396 | 0.17886 | -0.093196 | 0.013396 | south | N | 0.013396 | 0
86107 | CUF-138 | EQ | 0 | 0.060787 | south | 0.20093 | 0.013396 | 0.17886 | -0.093196 | 0.013396 | south | N | 0.013396 | 0
88198 | BEEVILLE | F | 0 | 0.071059 | south | 0.2112 | 0.023668 | 0.18913 | -0.082924 | 0.023668 | south | N | 0.023668 | 0
88253 | HAMILTON | F | 0 | 0.007918 | south | 0.14806 | -0.039473 | 0.12599 | -0.14607 | 0.039473 | south | N | 0.039473 | 0
88299 | ZAPATA | F | 0 | 0.067408 | south | 0.20755 | 0.020017 | 0.18548 | -0.086575 | 0.020017 | south | N | 0.020017 | 0
88508 | FALFURRI | F | 0 | 0.074333 | south | 0.21448 | 0.026942 | 0.19241 | -0.07965 | 0.026942 | south | N | 0.026942 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | 0 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.14528 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.4016 | 0 | -0.0041325 | 0 | 0 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.14528 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.6631 | 0 | -0.0041325 | 0 | 0 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.14528 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.6631 | 0 | -0.0041325 | 0 | 0 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.14528 | north | 1 | N | N | Nnorth | Nnorth | 1 | 55.2049 | 0 | -0.0041325 | 0 | 0 | 0 | Weighted Shift Factors
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 4.339 | 100 | -0.10602 | -10.6018 | 100 | 10.6018 | North | -0.14014
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.14941 | 0 | 100 | 10.6018 | Houston | 0.14941
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.14941 | 0 | 100 | 10.6018 |  | -0.28955
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.17015 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 110.769 | 651 | 0.31029 | 202.002 | 751 | 191.4001
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.17015 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 95.9657 | 564 | 0.31029 | 175.0063 | 1315 | 366.4064 | Line Rating | 1562
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.17015 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 102.0912 | 600 | 0.31029 | 186.1769 | 1915 | 552.5834 | Conc Gen | 3099
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.17009 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 27.724 | 0 | 0.31023 | 0 | 1915 | 552.5834 | Weighted Imp. | 907.0795
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.17009 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 27.724 | 0 | 0.31023 | 0 | 1915 | 552.5834 | PTDF | 0.2927
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.17009 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 41.6711 | 0 | 0.31023 | 0 | 1915 | 552.5834
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.15928 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9638 | 50 | 0.29942 | 14.9709 | 1965 | 567.5543 | Concentration | -1.0109
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.15926 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 25.6412 | 161 | 0.2994 | 48.2042 | 2126 | 615.7585
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.15926 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 26.4375 | 166 | 0.2994 | 49.7012 | 2292 | 665.4597
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.15926 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 39.497 | 248 | 0.2994 | 74.2524 | 2540 | 739.7121
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.15926 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 86.9571 | 546 | 0.2994 | 163.4751 | 3086 | 903.1872
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.15926 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 102.4055 | 0 | 0.2994 | 0 | 3086 | 903.1872
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.15926 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 2.0704 | 13 | 0.2994 | 3.8923 | 3099 | 907.0795
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.15681 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 15.7279 | 0 | 0.29695 | 0 | 3099 | 907.0795
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.15681 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 14.5676 | 0 | 0.29695 | 0 | 3099 | 907.0795
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.15681 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 16.1043 | 0 | 0.29695 | 0 | 3099 | 907.0795
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.15681 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 15.9945 | 0 | 0.29695 | 0 | 3099 | 907.0795
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.15681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.0179 | 0 | 0.29695 | 0 | 3099 | 907.0795
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.15681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.7042 | 0 | 0.29695 | 0 | 3099 | 907.0795
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.1568 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.1012 | 0 | 0.29694 | 0 | 3099 | 907.0795
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.1568 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.4584 | 0 | 0.29694 | 0 | 3099 | 907.0795
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.1568 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 8.3102 | 0 | 0.29694 | 0 | 3099 | 907.0795
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 24.0213 | 0 | 0.29694 | 0 | 3099 | 907.0795
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 24.0683 | 0 | 0.29694 | 0 | 3099 | 907.0795
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 23.8802 | 0 | 0.29694 | 0 | 3099 | 907.0795
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 15.0525 | 0 | 0.29694 | 0 | 3099 | 907.0795
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 38.2585 | 0 | 0.29694 | 0 | 3099 | 907.0795
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.1568 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.2719 | 0 | 0.29694 | 0 | 3099 | 907.0795
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.021677 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.17109 | 0 | 3099 | 907.0795
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.1868 | 46 | 0.29638 | 13.6334
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.1868 | 46 | 0.29638 | 13.6334
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.1868 | 46 | 0.29638 | 13.6334
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 8.5929 | 55 | 0.29638 | 16.3008
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 8.5929 | 55 | 0.29638 | 16.3008
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 8.4367 | 54 | 0.29638 | 16.0044
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.15488 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.29502 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.15412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.0858 | 0 | 0.29426 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 14.0204 | 0 | 0.29421 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 13.4965 | 0 | 0.29421 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 13.4041 | 0 | 0.29421 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 8.3968 | 0 | 0.29421 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8797 | 0 | 0.29421 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.15376 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.0884 | 0 | 0.2939 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.15364 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 9.9869 | 0 | 0.29379 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.15364 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 9.2186 | 0 | 0.29379 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.15364 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 9.9869 | 0 | 0.29379 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.15364 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 9.9869 | 0 | 0.29379 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.15319 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 20.8341 | 0 | 0.29333 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.15299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.3547 | 0 | 0.29313 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.15298 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 26.4659 | 0 | 0.29312 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.15298 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 20.6526 | 0 | 0.29312 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.15295 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 11.9303 | 0 | 0.29309 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.15295 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.2362 | 0 | 0.29309 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.15263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 27.4734 | 0 | 0.29277 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.15263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 24.2071 | 0 | 0.29277 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.15263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 23.9629 | 0 | 0.29277 | 0
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.15258 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 22.735 | 0 | 0.29273 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.15258 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.9332 | 0 | 0.29273 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.1525 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.83 | 12 | 0.29264 | 3.5117
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.1525 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.29264 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.15248 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 25.769 | 169 | 0.29262 | 49.4531
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.15246 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 25.1564 | 165 | 0.29261 | 48.28
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.15244 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 34.7572 | 228 | 0.29259 | 66.7098
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.15241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.7539 | 0 | 0.29255 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.15241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.632 | 0 | 0.29255 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.15241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 12.5887 | 0 | 0.29255 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.15241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.217 | 0 | 0.29255 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.15238 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4686 | 0 | 0.29253 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.15236 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 32.452 | 213 | 0.2925 | 62.3025
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.15217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.8038 | 0 | 0.29231 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.15217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.956 | 0 | 0.29231 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.15217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.9345 | 0 | 0.29231 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.15217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.565 | 0 | 0.29231 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 24.7538 | 0 | 0.29182 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 23.8286 | 0 | 0.29182 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 23.8893 | 0 | 0.29182 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 23.8134 | 0 | 0.29182 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 40.8014 | 0 | 0.29182 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 6.3629 | 42 | 0.29164 | 12.2489
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 6.3629 | 42 | 0.29164 | 12.2489
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 5.7569 | 38 | 0.29164 | 11.0823
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 5.7569 | 38 | 0.29164 | 11.0823
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.765 | 0 | 0.29037 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.9152 | 0 | 0.29037 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.5162 | 0 | 0.29037 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.4646 | 0 | 0.29037 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.3143 | 0 | 0.29037 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 15.624 | 0 | 0.29037 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 8.8636 | 0 | 0.29037 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.15018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 16.6695 | 0 | 0.29032 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.15018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 16.6695 | 0 | 0.29032 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.15018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 17.8709 | 0 | 0.29032 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.15018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 16.4443 | 0 | 0.29032 | 0
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.15013 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 23.5704 | 0 | 0.29027 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.14996 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 110.2213 | 735 | 0.2901 | 213.2264
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.0983 | 0 | 0.29009 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.2033 | 0 | 0.29009 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.9034 | 0 | 0.29009 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.8827 | 0 | 0.29009 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6541 | 0 | 0.29009 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.059 | 0 | 0.29009 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.984 | 0 | 0.29009 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.2482 | 0 | 0.29009 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6991 | 0 | 0.29009 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 12.8057 | 0 | 0.29009 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 22.1926 | 0 | 0.29009 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.14965 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 59.5623 | 398 | 0.2898 | 115.3392
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.14945 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.74726 | 0 | 0.28959 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.14945 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1385 | 0 | 0.28959 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.14923 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 1.7907 | 12 | 0.28937 | 3.4725
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.14917 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.5911 | 0 | 0.28931 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.14917 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4917 | 0 | 0.28931 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.14899 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 110.6959 | 743 | 0.28913 | 214.822
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.14844 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 25.5325 | 172 | 0.28859 | 49.6371
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.14844 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 25.5325 | 172 | 0.28859 | 49.6371
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.14844 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 25.5325 | 172 | 0.28859 | 49.6371
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 15.4073 | 104 | 0.28829 | 29.9821
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 15.4073 | 104 | 0.28829 | 29.9821
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9999 | 54 | 0.28829 | 15.5677
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.8518 | 53 | 0.28829 | 15.2794
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9999 | 54 | 0.28829 | 15.5677
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 8.4444 | 57 | 0.28829 | 16.4325
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9999 | 54 | 0.28829 | 15.5677
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9999 | 54 | 0.28829 | 15.5677
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 8.5925 | 58 | 0.28829 | 16.7208
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 8.5925 | 58 | 0.28829 | 16.7208
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.1481 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 24.111 | 0 | 0.28824 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.1481 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 23.9037 | 0 | 0.28824 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.1481 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 23.5334 | 0 | 0.28824 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.1481 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 39.8691 | 0 | 0.28824 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.1779 | 0 | 0.28817 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.5693 | 0 | 0.28817 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.6613 | 0 | 0.28817 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 14.951 | 0 | 0.28817 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 12.7306 | 0 | 0.28817 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 13.0266 | 0 | 0.28817 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.4015 | 0 | 0.28817 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6645 | 0 | 0.28817 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 13.9148 | 0 | 0.28817 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.3621 | 0 | 0.28817 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.3259 | 0 | 0.28817 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.6582 | 0 | 0.28817 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.5923 | 0 | 0.28817 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 14.951 | 0 | 0.28817 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 14.3589 | 0 | 0.28817 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 15.2471 | 0 | 0.28817 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.2503 | 0 | 0.28817 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.8424 | 0 | 0.28817 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.8424 | 0 | 0.28817 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 25.3131 | 0 | 0.28817 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.14678 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.7614 | 12 | 0.28693 | 3.4431
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.14604 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 25.2642 | 0 | 0.28618 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.14604 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 22.7816 | 0 | 0.28618 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.14604 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 22.4895 | 0 | 0.28618 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.14604 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 22.4895 | 0 | 0.28618 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.14604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 23.6578 | 0 | 0.28618 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.6823 | 56 | 0.27733 | 15.5303
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 8.0939 | 59 | 0.27733 | 16.3623
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.6823 | 56 | 0.27733 | 15.5303
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.6823 | 56 | 0.27733 | 15.5303
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 8.0939 | 59 | 0.27733 | 16.3623
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.6823 | 56 | 0.27733 | 15.5303
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.13279 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 8.7643 | 66 | 0.27294 | 18.0138
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.13129 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 175.0136 | 0 | 0.27144 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.13129 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 174.3571 | 0 | 0.27144 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 9.8551 | 76 | 0.26981 | 20.5059
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 9.8551 | 76 | 0.26981 | 20.5059
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 13.6156 | 105 | 0.26981 | 28.3306
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 9.5957 | 74 | 0.26981 | 19.9663
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 9.5957 | 74 | 0.26981 | 19.9663
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 13.2265 | 102 | 0.26981 | 27.5211
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.082803 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4205 | 150 | -0.23221 | -34.8317
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 7.2086 | 0 | 0.23139 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 7.3911 | 0 | 0.23139 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 7.2086 | 0 | 0.23139 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 7.2998 | 0 | 0.23139 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 7.1538 | 0 | 0.23139 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.2812 | 0 | 0.23139 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.1974 | 0 | 0.23139 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.5549 | 0 | 0.23139 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.9784 | 0 | 0.23139 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 6.7524 | 0 | 0.23139 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.090158 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.3276 | 0 | 0.2303 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.4233 | 0 | 0.22669 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.60583 | 0 | 0.22669 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.3753 | 0 | 0.22669 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2982 | 0 | 0.22669 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.60583 | 0 | 0.22669 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2982 | 0 | 0.22669 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.3753 | 0 | 0.22669 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.086546 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.3753 | 0 | 0.22669 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.086006 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.68805 | 0 | 0.22615 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.092541 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.24195 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.085121 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2768 | 0 | 0.22526 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.085121 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9578 | 0 | 0.22526 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.083328 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8332 | 22 | 0.22347 | 4.9164
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.083328 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.91661 | 11 | 0.22347 | 2.4582
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.083328 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.91661 | 11 | 0.22347 | 2.4582
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.082642 | south | 7 | N | N | Nsouth | Nsouth | -1 | 6.0329 | 0 | 0.22278 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.082595 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9398 | 47.7 | 0.22274 | 10.6246
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.082595 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0808 | 37.3 | 0.22274 | 8.3081
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.082595 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.7994 | 46 | 0.22274 | 10.2459
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.082595 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9646 | 48 | 0.22274 | 10.6914
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.096283 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.24569 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.096283 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.24569 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.081194 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.6919 | 144 | 0.22134 | 31.8725
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.081194 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.2645 | 188 | 0.22134 | 41.6113
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.8154 | 0 | 0.22125 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.4098 | 0 | 0.22125 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -1 | 8.111 | 0 | 0.22125 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -1 | 11.7609 | 0 | 0.22125 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -1 | 11.9232 | 0 | 0.22125 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -1 | 10.301 | 0 | 0.22125 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.08111 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.97332 | 0 | 0.22125 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.097858 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.24727 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.097858 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -77.0142 | 787 | -0.24727 | -194.5987
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0127 | 25 | 0.22065 | 5.5163
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0127 | 25 | 0.22065 | 5.5163
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0127 | 25 | 0.22065 | 5.5163
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.2881 | 16 | 0.22065 | 3.5304
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0127 | 25 | 0.22065 | 5.5163
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0127 | 25 | 0.22065 | 5.5163
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0127 | 25 | 0.22065 | 5.5163
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.2076 | 15 | 0.22065 | 3.3098
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.079598 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 26.7449 | 336 | 0.21974 | 73.8329
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.079598 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.3276 | 180 | 0.21974 | 39.5534
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.079581 | south | 8 | N | N | Nsouth | Nsouth | -1 | 11.8019 | 0 | 0.21972 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.079581 | south | 8 | N | N | Nsouth | Nsouth | -1 | 11.8257 | 0 | 0.21972 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.079581 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.1759 | 0 | 0.21972 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.079552 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.3194 | 180 | 0.21969 | 39.5451
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.079271 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 26.4765 | 334 | 0.21941 | 73.2842
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.079271 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 26.9521 | 340 | 0.21941 | 74.6007
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.079271 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.2688 | 180 | 0.21941 | 39.4945
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.079271 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.2688 | 180 | 0.21941 | 39.4945
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.079187 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9797 | 0 | 0.21933 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.079187 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9797 | 0 | 0.21933 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.07907 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0047 | 0 | 0.21921 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.079021 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0028 | 0 | 0.21916 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.078315 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.2711 | 0 | 0.21846 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.10021 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -25.5533 | 255 | -0.24962 | -63.6525
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.10021 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -14.9311 | 149 | -0.24962 | -37.193
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.10021 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -15.332 | 153 | -0.24962 | -38.1915
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.3302 | 94 | 0.21812 | 20.5036
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1972 | 41 | 0.21812 | 8.9431
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.9633 | 38 | 0.21812 | 8.2887
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.4816 | 19 | 0.21812 | 4.1444
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.3302 | 94 | 0.21812 | 20.5036
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.8073 | 36 | 0.21812 | 7.8525
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3532 | 43 | 0.21812 | 9.3793
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7156 | 22 | 0.21812 | 4.7987
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 11.5412 | 148 | 0.21812 | 32.2823
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.899 | 50 | 0.21812 | 10.9062
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.289 | 55 | 0.21812 | 11.9968
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.899 | 50 | 0.21812 | 10.9062
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.077776 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.9555 | 38 | 0.21792 | 8.2809
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.077776 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.5011 | 19.3 | 0.21792 | 4.2058
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.077776 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.1666 | 15 | 0.21792 | 3.2688
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.077776 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 3.6555 | 47 | 0.21792 | 10.2422
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.077775 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21792 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.077233 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.1216 | 144 | 0.21738 | 31.3021
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.077233 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.1216 | 144 | 0.21738 | 31.3021
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.077233 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 13.2068 | 171 | 0.21738 | 37.1713
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.077228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.9862 | 207 | 0.21737 | 44.9958
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.077228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 16.7353 | 216.7 | 0.21737 | 47.1043
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.077228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.6892 | 242 | 0.21737 | 52.6038
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.076467 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.2024 | 146.5 | 0.21661 | 31.7333
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.076467 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.3095 | 147.9 | 0.21661 | 32.0366
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.076467 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 13.2288 | 173 | 0.21661 | 37.4735
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.10226 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.3384 | 150 | -0.25166 | -37.7497
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.10226 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.1805 | 80 | -0.25166 | -20.1332
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.074463 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 46.8372 | 629 | 0.21461 | 134.9871
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.074333 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21448 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.10625 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.9251 | 84 | -0.25566 | -21.4754
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.071837 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.86204 | 0 | 0.21198 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.071837 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.79021 | 0 | 0.21198 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.071837 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.86204 | 0 | 0.21198 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.10669 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1614 | 76.5 | -0.25609 | -19.5912
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.10692 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.6038 | 0 | -0.25633 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.10692 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.6038 | 0 | -0.25633 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.10711 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.5689 | 80 | -0.25652 | -20.5216
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.071059 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.2112 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.10966 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.449 | 150 | -0.25907 | -38.8603
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.10966 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.449 | 150 | -0.25907 | -38.8603
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.10972 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.7779 | 80 | -0.25913 | -20.7306
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.10974 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.7791 | 80 | -0.25915 | -20.7318
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.10985 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2387 | 75 | -0.25926 | -19.4444
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.10985 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.788 | 80 | -0.25926 | -20.7407
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.10985 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.394 | 40 | -0.25926 | -10.3703
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.11036 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8289 | 80 | -0.25977 | -20.7816
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.11036 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8289 | 80 | -0.25977 | -20.7816
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.067408 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.20755 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.11225 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.5388 | 0 | -0.26166 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.7099 | 66 | -0.26622 | -17.5708
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.593 | 65 | -0.26622 | -17.3046
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.8267 | 67 | -0.26622 | -17.837
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.8267 | 67 | -0.26622 | -17.837
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.8267 | 67 | -0.26622 | -17.837
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.11682 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.26622 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.11682 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.26622 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.11688 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0907 | 35 | -0.26629 | -9.32
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.11688 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.5063 | 30 | -0.26629 | -7.9886
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.11699 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.8295 | 169.5 | -0.2664 | -45.1542
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.06131 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 24.2788 | 396 | 0.20145 | 79.7753
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.11709 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.4464 | 149 | -0.2665 | -39.7083
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.11746 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.77526 | 6.6 | -0.26687 | -1.7614
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.11746 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.029 | 34.3 | -0.26687 | -9.1537
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.060791 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.20093 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.060787 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.0787 | 100 | 0.20093 | 20.093
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.060787 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.0787 | 100 | 0.20093 | 20.093
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.060787 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.20093 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.060787 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.20093 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.060787 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.20093 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.060787 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.20093 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.11782 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.2552 | 112.5 | -0.26723 | -30.0637
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.11782 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.6147 | 149.5 | -0.26723 | -39.9513
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.11782 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.9153 | 186 | -0.26723 | -49.7052
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.11782 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.2732 | 214.5 | -0.26723 | -57.3214
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 1 | -24.5797 | 208.2 | -0.26747 | -55.6865
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 1 | -16.776 | 142.1 | -0.26747 | -38.007
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 1 | -15.6309 | 132.4 | -0.26747 | -35.4126
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 1 | -16.0559 | 136 | -0.26747 | -36.3754
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 1 | -17.3545 | 147 | -0.26747 | -39.3176
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 1 | -24.7922 | 210 | -0.26747 | -56.168
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 1 | -8.2649 | 70 | -0.26748 | -18.7235
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 1 | -8.2649 | 70 | -0.26748 | -18.7235
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 1 | -10.9569 | 92.8 | -0.26748 | -24.822
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 1 | -9.4456 | 80 | -0.26748 | -21.3983
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 1 | -9.4456 | 80 | -0.26748 | -21.3983
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 1 | -13.578 | 115 | -0.26748 | -30.76
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.11809 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.7133 | 150 | -0.2675 | -40.1246
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.11811 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.8501 | 58 | -0.26751 | -15.5158
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.11813 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8717 | 100.5 | -0.26753 | -26.8872
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.11827 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.3341 | 214.2 | -0.26768 | -57.3374
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.11835 | west | 8 | N | N | Nwest | Nwest | 1 | -3.0534 | 0 | -0.26776 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.11873 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.2482 | 120 | -0.26814 | -32.1772
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.11876 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.2516 | 120 | -0.26817 | -32.1806
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.11886 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.2626 | 120 | -0.26826 | -32.1916
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.11886 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.6932 | 233 | -0.26826 | -62.5054
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.11886 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.2291 | 170.2 | -0.26826 | -45.6584
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.11888 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.7482 | 225 | -0.26829 | -60.3651
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.11895 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.4103 | 180 | -0.26835 | -48.3038
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.11895 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.4103 | 180 | -0.26835 | -48.3038
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.11896 | west | 8 | N | N | Nwest | Nwest | 1 | -8.3271 | 0 | -0.26837 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.11896 | west | 8 | N | N | Nwest | Nwest | 1 | -8.7315 | 0 | -0.26837 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.11896 | west | 8 | N | N | Nwest | Nwest | 1 | -8.3746 | 0 | -0.26837 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.11916 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.874 | 150 | -0.26857 | -40.2853
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.11916 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.2152 | 220 | -0.26857 | -59.0851
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.11916 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.832 | 200 | -0.26857 | -53.7137
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.11916 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.5256 | 121.9 | -0.26857 | -32.7385
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.8743 | 66 | -0.26872 | -17.7353
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 1 | -8.2323 | 69 | -0.26872 | -18.5414
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 1 | -8.2323 | 69 | -0.26872 | -18.5414
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.9936 | 67 | -0.26872 | -18.004
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.9936 | 67 | -0.26872 | -18.004
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.755 | 65 | -0.26872 | -17.4666
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.11936 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.5194 | 63 | -0.26876 | -16.9321
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.11941 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.8362 | 141 | -0.26881 | -37.9028
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.11941 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.3287 | 120 | -0.26881 | -32.2577
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.11943 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8231 | 99 | -0.26883 | -26.6145
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.11943 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2849 | 61 | -0.26883 | -16.3988
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.11943 | west | 7 | N | N | Nwest | Nwest | 1 | -2.9856 | 0 | -0.26883 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.11943 | west | 7 | N | N | Nwest | Nwest | 1 | -5.4577 | 0 | -0.26883 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.11943 | west | 7 | N | N | Nwest | Nwest | 1 | -5.4577 | 0 | -0.26883 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.11959 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.0456 | 84 | -0.269 | -22.596
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.11967 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.9501 | 150 | -0.26908 | -40.3613
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.11967 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.0864 | 101 | -0.26908 | -27.1766
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.11982 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.9779 | 125 | -0.26923 | -33.6539
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.11982 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.9779 | 125 | -0.26923 | -33.6539
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5069 | 37.5 | -0.26959 | -10.1097
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.9197 | 107.5 | -0.26959 | -28.9811
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.2247 | 135 | -0.26959 | -36.3948
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.3018 | 119 | -0.26959 | -32.0814
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.6192 | 105 | -0.26959 | -28.3071
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.6747 | 80.5 | -0.26959 | -21.7021
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.12029 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.1406 | 209 | -0.2697 | -56.367
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.12029 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.2167 | 126.5 | -0.2697 | -34.1169
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.12029 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.9522 | 249 | -0.2697 | -67.1549
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.12029 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.6971 | 197 | -0.2697 | -53.1306
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.1203 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -7.2183 | 60 | -0.26971 | -16.1828
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.12032 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.0476 | 150 | -0.26973 | -40.4588
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.057222 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.68666 | 0 | 0.19736 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.12125 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2752 | 60 | -0.27066 | -16.2397
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.12261 | west | 6 | Y | N | Ywest | Nwest | 1 | -49.0432 | 400 | -0.27202 | -108.8066
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.12261 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.9364 | 236 | -0.27202 | -64.1968
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.1234 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.361 | 165 | -0.27281 | -45.0134
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.054817 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 29.9301 | 546 | 0.19496 | 106.4481
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.054817 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 41.1127 | 750 | 0.19496 | 146.2199
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.12407 | west | 4 | Y | N | Ywest | Nwest | 1 | -80.6096 | 649.7 | -0.27348 | -177.6803
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.12454 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -9.0914 | 73 | -0.27395 | -19.9982
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.12454 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -14.8203 | 119 | -0.27395 | -32.5999
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.12454 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -25.5307 | 205 | -0.27395 | -56.1594
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.12454 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -12.7031 | 102 | -0.27395 | -27.9427
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.12454 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -11.9558 | 96 | -0.27395 | -26.2991
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.0538 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.339 | 155 | 0.19394 | 30.0611
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.0538 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.146 | 170 | 0.19394 | 32.9703
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.0538 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.339 | 155 | 0.19394 | 30.0611
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.053657 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2878 | 24 | 0.1938 | 4.6512
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.053657 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 1.2878 | 24 | 0.1938 | 4.6512
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.053657 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 1.2341 | 23 | 0.1938 | 4.4574
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.12512 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -30.2778 | 242 | -0.27452 | -66.4347
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.12541 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -21.0687 | 168 | -0.27482 | -46.1693
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.12541 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.2868 | 90 | -0.27482 | -24.7336
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.052688 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19283 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.052688 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19283 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.052688 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19283 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.052629 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 10.9995 | 209 | 0.19277 | 40.2893
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.052629 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 11.3679 | 216 | 0.19277 | 41.6387
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.052629 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4209 | 46 | 0.19277 | 8.8675
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.052629 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4736 | 47 | 0.19277 | 9.0603
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.052629 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4209 | 46 | 0.19277 | 8.8675
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.052629 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4209 | 46 | 0.19277 | 8.8675
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.12577 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -15.0925 | 120 | -0.27518 | -33.0215
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.0525 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 22.26 | 424 | 0.19264 | 81.6806
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.0525 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 22.3125 | 425 | 0.19264 | 81.8732
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.12589 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -46.0768 | 366 | -0.2753 | -100.7603
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.052472 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 21.6185 | 412 | 0.19261 | 79.3573
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.052472 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 20.9888 | 400 | 0.19261 | 77.046
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.052444 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.0418 | 58 | 0.19259 | 11.17
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.052444 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.6675 | 89 | 0.19259 | 17.1402
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.052444 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.3075 | 44 | 0.19259 | 8.4738
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.052444 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.3075 | 44 | 0.19259 | 8.4738
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.052444 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.2551 | 43 | 0.19259 | 8.2812
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.052444 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.36 | 45 | 0.19259 | 8.6664
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.12595 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.5114 | 0 | -0.27535 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.12595 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.5114 | 0 | -0.27535 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.052417 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 21.3337 | 407 | 0.19256 | 78.3719
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.12604 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.5207 | 20 | -0.27545 | -5.5089
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.12604 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.5207 | 20 | -0.27545 | -5.5089
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.12604 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.5207 | 20 | -0.27545 | -5.5089
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.12604 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.1426 | 17 | -0.27545 | -4.6826
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.1263 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.8412 | 70 | -0.27571 | -19.2998
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.1263 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.7149 | 69 | -0.27571 | -19.0241
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.1263 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.7149 | 69 | -0.27571 | -19.0241
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.1263 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.5886 | 68 | -0.27571 | -18.7484
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.5555 | 147 | 0.19154 | 28.1565
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.0929 | 138 | 0.19154 | 26.4326
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.1957 | 140 | 0.19154 | 26.8157
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.5555 | 147 | 0.19154 | 28.1565
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.3544 | 182 | 0.19154 | 34.8604
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 10.1768 | 198 | 0.19154 | 37.9251
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.1271 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.2879 | 18 | -0.27651 | -4.9772
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.1271 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.2879 | 18 | -0.27651 | -4.9772
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.1271 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -4.8299 | 38 | -0.27651 | -10.5074
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.12748 | north | 3 | N | N | Nnorth | Nnorth | 1 | -147.5001 | 0 | -0.27689 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.12748 | north | 3 | N | N | Nnorth | Nnorth | 1 | -147.6276 | 0 | -0.27689 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.12782 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -27.7764 | 217.3 | -0.27723 | -60.2428
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.12782 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.2041 | 205 | -0.27723 | -56.8329
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.12782 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -34.8195 | 272.4 | -0.27723 | -75.5184
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12793 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.0975 | 204 | -0.27734 | -56.5768
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12793 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -25.7137 | 201 | -0.27734 | -55.7448
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12793 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -30.9588 | 242 | -0.27734 | -67.1157
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.12813 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.27754 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.1287 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -37.065 | 288 | -0.27811 | -80.0947
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.1287 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -18.9186 | 147 | -0.27811 | -40.8817
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.1287 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -18.9186 | 147 | -0.27811 | -40.8817
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.12875 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -28.8404 | 224 | -0.27816 | -62.3079
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.12875 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -29.098 | 226 | -0.27816 | -62.8643
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.12875 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -27.2954 | 212 | -0.27816 | -58.97
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.12875 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -27.1667 | 211 | -0.27816 | -58.6919
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.13009 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.27949 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.13009 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.27949 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.13009 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.27949 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.048236 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11577 | 0 | 0.18838 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.048236 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11577 | 0 | 0.18838 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.13015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -28.1634 | 216.4 | -0.27955 | -60.4954
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.13015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -28.1243 | 216.1 | -0.27955 | -60.4115
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.13039 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -51.5033 | 395 | -0.2798 | -110.5196
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.13039 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -56.7188 | 435 | -0.2798 | -121.7115
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.1306 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -14.6921 | 112.5 | -0.28 | -31.5005
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.13068 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -56.8458 | 435 | -0.28009 | -121.8385
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.047201 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1888 | 0 | 0.18734 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.046659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.6256 | 142 | 0.1868 | 26.5259
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.046659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.7656 | 145 | 0.1868 | 27.0863
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.046659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.0455 | 151 | 0.1868 | 28.2071
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.046659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 13.5311 | 290 | 0.1868 | 54.1725
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.13202 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -7.9214 | 60 | -0.28143 | -16.8859
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.13202 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -8.3175 | 63 | -0.28143 | -17.7302
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.045627 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1095 | 0 | 0.18577 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.045627 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1095 | 0 | 0.18577 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.045627 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.12776 | 0 | 0.18577 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.13337 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.1403 | 196 | -0.28278 | -55.4244
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.13337 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -14.804 | 111 | -0.28278 | -31.3883
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.13419 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.2836 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.13449 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.2839 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.13453 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -15.8747 | 118 | -0.28394 | -33.5049
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.13453 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -15.4711 | 115 | -0.28394 | -32.653
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.13453 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -74.7992 | 556 | -0.28394 | -157.8703
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.13483 | north | 5 | N | N | Nnorth | Nnorth | 1 | -5.393 | 0 | -0.28423 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.13483 | north | 5 | N | N | Nnorth | Nnorth | 1 | -5.393 | 0 | -0.28423 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.9465 | 114 | 0.18353 | 20.9227
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 9.6326 | 222 | 0.18353 | 40.7443
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.9838 | 184 | 0.18353 | 33.7701
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 9.7194 | 224 | 0.18353 | 41.1114
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.9898 | 115 | 0.18353 | 21.1063
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.13504 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -22.9561 | 170 | -0.28444 | -48.3556
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.13504 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -70.2187 | 520 | -0.28444 | -147.9111
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.1353 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -50.0614 | 370 | -0.28471 | -105.3425
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | 1 | -18.9421 | 0 | -0.28471 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | 1 | -19.0774 | 0 | -0.28471 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | 1 | -41.808 | 0 | -0.28471 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | 1 | -19.348 | 0 | -0.28471 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | 1 | -19.4833 | 0 | -0.28471 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | 1 | -41.9433 | 0 | -0.28471 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.043062 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 18.6458 | 433 | 0.1832 | 79.3277
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -21.6666 | 160 | -0.28482 | -45.5719
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -21.1249 | 156 | -0.28482 | -44.4326
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.5415 | 196 | -0.28482 | -55.8256
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -21.1249 | 156 | -0.28482 | -44.4326
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -21.2603 | 157 | -0.28482 | -44.7174
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.8124 | 198 | -0.28482 | -56.3952
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.042909 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 25.0589 | 584 | 0.18305 | 106.9023
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.042909 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 25.5309 | 595 | 0.18305 | 108.9159
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.1355 | north | 8 | N | N | Nnorth | Nnorth | 1 | -10.1625 | 0 | -0.28491 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.1355 | north | 8 | N | N | Nnorth | Nnorth | 1 | -10.7858 | 0 | -0.28491 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.1355 | north | 8 | N | N | Nnorth | Nnorth | 1 | -11.9782 | 0 | -0.28491 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.13562 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -75.6754 | 558 | -0.28503 | -159.0453
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.13562 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -78.5234 | 579 | -0.28503 | -165.0309
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.13562 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -109.5802 | 808 | -0.28503 | -230.3022
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.13577 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -10.7257 | 79 | -0.28518 | -22.5289
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.13577 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -14.3914 | 106 | -0.28518 | -30.2287
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.13577 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -19.8221 | 146 | -0.28518 | -41.6358
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.13577 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -10.3184 | 76 | -0.28518 | -21.6734
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.13577 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -5.4309 | 40 | -0.28518 | -11.4072
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.13584 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.28525 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.13584 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.28525 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.13595 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.719 | 20 | -0.28536 | -5.7071
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.13595 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.3987 | 25 | -0.28536 | -7.1339
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.13595 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -5.5739 | 41 | -0.28536 | -11.6997
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.13612 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -52.8146 | 388 | -0.28553 | -110.785
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.13612 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -70.1018 | 515 | -0.28553 | -147.0472
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.041646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.3245 | 223.9 | 0.18179 | 40.7025
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.041646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.3704 | 225 | 0.18179 | 40.9025
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.041646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.3537 | 224.6 | 0.18179 | 40.8298
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.041646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.4411 | 226.7 | 0.18179 | 41.2115
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.0607 | 161 | -0.28643 | -46.1155
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.4718 | 164 | -0.28643 | -46.9748
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.4718 | 164 | -0.28643 | -46.9748
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -56.7275 | 414 | -0.28643 | -118.5826
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.1977 | 162 | -0.28643 | -46.4019
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.0607 | 161 | -0.28643 | -46.1155
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.3347 | 163 | -0.28643 | -46.6883
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -56.0424 | 409 | -0.28643 | -117.1505
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.13721 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -30.7348 | 224 | -0.28662 | -64.2023
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.039111 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.9555 | 50 | 0.17925 | 8.9627
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.039111 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.9555 | 50 | 0.17925 | 8.9627
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.039111 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.9555 | 50 | 0.17925 | 8.9627
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.039111 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.9555 | 50 | 0.17925 | 8.9627
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.14114 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -110.791 | 785 | -0.29054 | -228.0766
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.14114 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -112.2023 | 795 | -0.29054 | -230.9821
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.14114 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -110.0853 | 780 | -0.29054 | -226.6239
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.14173 | north | 1 | N | N | Nnorth | Nnorth | 1 | -20.9766 | 0 | -0.29114 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.14173 | north | 1 | N | N | Nnorth | Nnorth | 1 | -18.4254 | 0 | -0.29114 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.14173 | north | 1 | N | N | Nnorth | Nnorth | 1 | -20.5514 | 0 | -0.29114 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.14173 | north | 1 | N | N | Nnorth | Nnorth | 1 | -56.5519 | 0 | -0.29114 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.14226 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.29167 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.14232 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -7.1161 | 50 | -0.29173 | -14.5865
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.1424 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -25.9172 | 182 | -0.29181 | -53.1095
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.1424 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -68.9226 | 484 | -0.29181 | -141.2363
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.035456 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.21274 | 0 | 0.1756 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.14846 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.4909 | 151.5 | -0.29786 | -45.1263
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.14846 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.6097 | 152.3 | -0.29786 | -45.3646
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.14846 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.3508 | 177.5 | -0.29786 | -52.8708
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.14872 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.4126 | 150.7 | -0.29813 | -44.9284
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.14872 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.4572 | 151 | -0.29813 | -45.0179
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.14872 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.3835 | 177.4 | -0.29813 | -52.8885
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.15014 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -92.3386 | 615 | -0.29955 | -184.2248
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.15014 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -88.1345 | 587 | -0.29955 | -175.8373
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.026322 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16646 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.024526 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8751 | 158 | 0.16467 | 26.0177
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.024526 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9242 | 160 | 0.16467 | 26.347
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.024526 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.292 | 175 | 0.16467 | 28.8171
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.022849 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13709 | 0 | 0.16299 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.02225 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.937 | 132 | 0.16239 | 21.4359
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.02225 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.9815 | 134 | 0.16239 | 21.7606
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.02225 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 7.1867 | 323 | 0.16239 | 52.4529
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.021988 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3532 | 152.5 | 0.16213 | 24.725
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.021988 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2872 | 149.5 | 0.16213 | 24.2386
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.021988 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.1144 | 232.6 | 0.16213 | 37.7116
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72873 | 49 | 0.15501 | 7.5957
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.68411 | 46 | 0.15501 | 7.1307
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.68411 | 46 | 0.15501 | 7.1307
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.69898 | 47 | 0.15501 | 7.2857
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.014872 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2903 | 154 | 0.15501 | 23.8723
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.014872 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2011 | 148 | 0.15501 | 22.9422
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.71386 | 48 | 0.15501 | 7.4407
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.71386 | 48 | 0.15501 | 7.4407
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.0127 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.937 | 310 | 0.15284 | 47.3813
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.0127 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.2451 | 413 | 0.15284 | 63.1241
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.012523 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10018 | 0 | 0.15267 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.012523 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10018 | 0 | 0.15267 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.16676 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -137.9105 | 827 | -0.31617 | -261.4713
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.16676 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -136.5764 | 819 | -0.31617 | -258.942
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.01132 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.47544 | 42 | 0.15146 | 6.3614
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.01132 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.49808 | 44 | 0.15146 | 6.6644
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.01132 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.49808 | 44 | 0.15146 | 6.6644
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.01132 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.53204 | 47 | 0.15146 | 7.1188
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.009937 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3478 | 0 | 0.15008 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.009937 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.33786 | 0 | 0.15008 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.009937 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3478 | 0 | 0.15008 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.007918 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.26129 | 0 | 0.14806 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.007918 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19795 | 0 | 0.14806 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.007918 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.14806 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.006621 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11918 | 0 | 0.14676 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.006621 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11918 | 0 | 0.14676 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.005159 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.1771 | 422 | 0.1453 | 61.3174
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.004765 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13342 | 0 | 0.14491 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.004765 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13819 | 0 | 0.14491 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.17755 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -151.8061 | 855 | -0.32696 | -279.5503
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.17755 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -151.8061 | 855 | -0.32696 | -279.5503
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.17755 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -27.041 | 152.3 | -0.32696 | -49.7959
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.17755 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -27.1653 | 153 | -0.32696 | -50.0248
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14014 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14014 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14014 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14014 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14014 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14014 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.14014 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.14014 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.002584 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.035401 | 0 | 0.13756 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004245 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.07641 | 0 | 0.1359 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004245 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.07641 | 0 | 0.1359 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.004245 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.063675 | 0 | 0.1359 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.18539 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.8986 | 48 | -0.3348 | -16.0702
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.18539 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.5278 | 46 | -0.3348 | -15.4006
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.18539 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -19.4657 | 105 | -0.3348 | -35.1536
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.18995 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.33936 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.18995 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.33936 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.18995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -3.2292 | 17 | -0.33936 | -5.7691
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.18995 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.33936 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.18995 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.33936 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.19039 | north | 7 | N | N | Nnorth | Nnorth | 1 | -6.0925 | 0 | -0.3398 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.026032 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -14.8122 | 569 | 0.11411 | 64.9291
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.026032 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -15.1246 | 581 | 0.11411 | 66.2984
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.20511 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -94.9673 | 463 | -0.35452 | -164.1434

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | 0 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.20511 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -94.9673 | 0 | -0.35452 | 0 | 0 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.026032 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -14.8122 | 0 | 0.11411 | 0 | 0 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.026032 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -15.1246 | 0 | 0.11411 | 0 | 0 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.19039 | north | 7 | N | N | Nnorth | Nnorth | 1 | -6.0925 | 0 | -0.3398 | 0 | 0 | 0 | Weighted Shift Factors
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.18995 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.33936 | 0 | 0 | 0 | North | -0.14014
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.18995 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.33936 | 0 | 0 | 0 | Houston | 0.14941
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.18995 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -3.2292 | 17 | -0.33936 | -5.7691 | 17 | 5.7691 |  | -0.28955
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.18995 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.33936 | 0 | 17 | 5.7691
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.18995 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.33936 | 0 | 17 | 5.7691 | Line Rating | 1562
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.18539 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.8986 | 48 | -0.3348 | -16.0702 | 65 | 21.8393 | Conc Gen | 2924.6
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.18539 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.5278 | 46 | -0.3348 | -15.4006 | 111 | 37.24 | Weighted Imp. | 346.9485
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.18539 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -19.4657 | 105 | -0.3348 | -35.1536 | 216 | 72.3936 | PTDF | 0.11863
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004245 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.07641 | 0 | 0.1359 | 0 | 216 | 72.3936
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004245 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.07641 | 0 | 0.1359 | 0 | 216 | 72.3936 | Concentration | -0.40971
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.004245 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.063675 | 0 | 0.1359 | 0 | 216 | 72.3936
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.002584 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.035401 | 0 | 0.13756 | 0 | 216 | 72.3936
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14014 | 0 | 216 | 72.3936
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14014 | 0 | 216 | 72.3936
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14014 | 0 | 216 | 72.3936
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14014 | 0 | 216 | 72.3936
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14014 | 0 | 216 | 72.3936
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14014 | 0 | 216 | 72.3936
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.14014 | 0 | 216 | 72.3936
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.14014 | 0 | 216 | 72.3936
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.17755 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -151.8061 | 0 | -0.32696 | 0 | 216 | 72.3936
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.17755 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -151.8061 | 0 | -0.32696 | 0 | 216 | 72.3936
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.17755 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -27.041 | 0 | -0.32696 | 0 | 216 | 72.3936
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.17755 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -27.1653 | 0 | -0.32696 | 0 | 216 | 72.3936
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.004765 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13342 | 0 | 0.14491 | 0 | 216 | 72.3936
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.004765 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13819 | 0 | 0.14491 | 0 | 216 | 72.3936
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.005159 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.1771 | 422 | 0.1453 | 61.3174 | 638 | 11.0762
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.006621 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11918 | 0 | 0.14676 | 0 | 638 | 11.0762
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.006621 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11918 | 0 | 0.14676 | 0 | 638 | 11.0762
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.007918 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.26129 | 0 | 0.14806 | 0 | 638 | 11.0762
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.007918 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19795 | 0 | 0.14806 | 0 | 638 | 11.0762
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.007918 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.14806 | 0 | 638 | 11.0762
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.009937 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3478 | 0 | 0.15008 | 0 | 638 | 11.0762
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.009937 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.33786 | 0 | 0.15008 | 0 | 638 | 11.0762
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.009937 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3478 | 0 | 0.15008 | 0 | 638 | 11.0762
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.01132 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.47544 | 42 | 0.15146 | 6.3614 | 680 | 4.7148
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.01132 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.49808 | 44 | 0.15146 | 6.6644 | 724 | 1.9496
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.01132 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.49808 | 44 | 0.15146 | 6.6644 | 768 | 8.614
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.01132 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.53204 | 47 | 0.15146 | 7.1188 | 815 | 15.7327
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.16676 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -137.9105 | 0 | -0.31617 | 0 | 815 | 15.7327
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.16676 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -136.5764 | 0 | -0.31617 | 0 | 815 | 15.7327
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.012523 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10018 | 0 | 0.15267 | 0 | 815 | 15.7327
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.012523 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10018 | 0 | 0.15267 | 0 | 815 | 15.7327
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.0127 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.937 | 310 | 0.15284 | 47.3813 | 1125 | 63.114
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.0127 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.2451 | 413 | 0.15284 | 63.1241 | 1538 | 126.2381
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.72873 | 49 | 0.15501 | 7.5957 | 1587 | 133.8339
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.68411 | 46 | 0.15501 | 7.1307 | 1633 | 140.9645
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.68411 | 46 | 0.15501 | 7.1307 | 1679 | 148.0952
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.69898 | 47 | 0.15501 | 7.2857 | 1726 | 155.3809
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.014872 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2903 | 154 | 0.15501 | 23.8723 | 1880 | 179.2532
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.014872 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2011 | 148 | 0.15501 | 22.9422 | 2028 | 202.1954
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.71386 | 48 | 0.15501 | 7.4407 | 2076 | 209.6361
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.014872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.71386 | 48 | 0.15501 | 7.4407 | 2124 | 217.0769
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.021988 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3532 | 152.5 | 0.16213 | 24.725 | 2276.5 | 241.8018
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.021988 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.2872 | 149.5 | 0.16213 | 24.2386 | 2426 | 266.0404
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.021988 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.1144 | 232.6 | 0.16213 | 37.7116 | 2658.6 | 303.752
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.02225 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.937 | 132 | 0.16239 | 21.4359 | 2790.6 | 325.1879
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.02225 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.9815 | 134 | 0.16239 | 21.7606 | 2924.6 | 346.9485
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.02225 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 7.1867 | 323 | 0.16239 | 52.4529
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.022849 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13709 | 0 | 0.16299 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.024526 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8751 | 158 | 0.16467 | 26.0177
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.024526 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9242 | 160 | 0.16467 | 26.347
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.024526 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.292 | 175 | 0.16467 | 28.8171
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.026322 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16646 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.15014 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -92.3386 | 0 | -0.29955 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.15014 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -88.1345 | 0 | -0.29955 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.14872 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.4126 | 150.7 | -0.29813 | -44.9284
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.14872 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.4572 | 151 | -0.29813 | -45.0179
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.14872 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.3835 | 177.4 | -0.29813 | -52.8885
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.14846 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.4909 | 151.5 | -0.29786 | -45.1263
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.14846 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.6097 | 152.3 | -0.29786 | -45.3646
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.14846 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.3508 | 177.5 | -0.29786 | -52.8708
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.035456 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.21274 | 0 | 0.1756 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.1424 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -25.9172 | 182 | -0.29181 | -53.1095
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.1424 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -68.9226 | 484 | -0.29181 | -141.2363
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.14232 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -7.1161 | 0 | -0.29173 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.14226 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.29167 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.14173 | north | 1 | N | N | Nnorth | Nnorth | 1 | -20.9766 | 0 | -0.29114 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.14173 | north | 1 | N | N | Nnorth | Nnorth | 1 | -18.4254 | 0 | -0.29114 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.14173 | north | 1 | N | N | Nnorth | Nnorth | 1 | -20.5514 | 0 | -0.29114 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.14173 | north | 1 | N | N | Nnorth | Nnorth | 1 | -56.5519 | 0 | -0.29114 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.14114 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -110.791 | 0 | -0.29054 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.14114 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -112.2023 | 0 | -0.29054 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.14114 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -110.0853 | 0 | -0.29054 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.039111 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.9555 | 50 | 0.17925 | 8.9627
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.039111 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.9555 | 50 | 0.17925 | 8.9627
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.039111 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.9555 | 50 | 0.17925 | 8.9627
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.039111 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.9555 | 50 | 0.17925 | 8.9627
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.13721 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -30.7348 | 224 | -0.28662 | -64.2023
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.0607 | 161 | -0.28643 | -46.1155
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.4718 | 164 | -0.28643 | -46.9748
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.4718 | 164 | -0.28643 | -46.9748
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -56.7275 | 414 | -0.28643 | -118.5826
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.1977 | 162 | -0.28643 | -46.4019
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.0607 | 161 | -0.28643 | -46.1155
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -22.3347 | 163 | -0.28643 | -46.6883
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.13702 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -56.0424 | 409 | -0.28643 | -117.1505
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.041646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.3245 | 223.9 | 0.18179 | 40.7025
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.041646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.3704 | 225 | 0.18179 | 40.9025
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.041646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.3537 | 224.6 | 0.18179 | 40.8298
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.041646 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.4411 | 226.7 | 0.18179 | 41.2115
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.13612 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -52.8146 | 388 | -0.28553 | -110.785
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.13612 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -70.1018 | 515 | -0.28553 | -147.0472
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.13595 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.719 | 20 | -0.28536 | -5.7071
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.13595 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.3987 | 25 | -0.28536 | -7.1339
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.13595 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -5.5739 | 41 | -0.28536 | -11.6997
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.13584 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.28525 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.13584 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.28525 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.13577 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -5.4309 | 40 | -0.28518 | -11.4072
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.13577 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -10.7257 | 79 | -0.28518 | -22.5289
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.13577 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -14.3914 | 106 | -0.28518 | -30.2287
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.13577 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -19.8221 | 146 | -0.28518 | -41.6358
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.13577 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -10.3184 | 76 | -0.28518 | -21.6734
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.13562 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -75.6754 | 0 | -0.28503 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.13562 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -78.5234 | 0 | -0.28503 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.13562 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -109.5802 | 0 | -0.28503 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.1355 | north | 8 | N | N | Nnorth | Nnorth | 1 | -10.1625 | 0 | -0.28491 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.1355 | north | 8 | N | N | Nnorth | Nnorth | 1 | -10.7858 | 0 | -0.28491 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.1355 | north | 8 | N | N | Nnorth | Nnorth | 1 | -11.9782 | 0 | -0.28491 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.042909 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 25.0589 | 0 | 0.18305 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.042909 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 25.5309 | 0 | 0.18305 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -21.6666 | 160 | -0.28482 | -45.5719
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -21.1249 | 156 | -0.28482 | -44.4326
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.5415 | 196 | -0.28482 | -55.8256
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -21.1249 | 156 | -0.28482 | -44.4326
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -21.2603 | 157 | -0.28482 | -44.7174
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.13542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.8124 | 198 | -0.28482 | -56.3952
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.043062 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 18.6458 | 0 | 0.1832 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.1353 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -50.0614 | 370 | -0.28471 | -105.3425
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | 1 | -18.9421 | 0 | -0.28471 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | 1 | -19.0774 | 0 | -0.28471 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | 1 | -41.808 | 0 | -0.28471 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | 1 | -19.348 | 0 | -0.28471 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | 1 | -19.4833 | 0 | -0.28471 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.1353 | north | 1 | N | N | Nnorth | Nnorth | 1 | -41.9433 | 0 | -0.28471 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.13504 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -22.9561 | 170 | -0.28444 | -48.3556
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.13504 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -70.2187 | 520 | -0.28444 | -147.9111
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.9465 | 0 | 0.18353 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 9.6326 | 0 | 0.18353 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.9838 | 0 | 0.18353 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 9.7194 | 0 | 0.18353 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.9898 | 0 | 0.18353 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.13483 | north | 5 | N | N | Nnorth | Nnorth | 1 | -5.393 | 0 | -0.28423 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.13483 | north | 5 | N | N | Nnorth | Nnorth | 1 | -5.393 | 0 | -0.28423 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.13453 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -15.8747 | 118 | -0.28394 | -33.5049
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.13453 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -15.4711 | 115 | -0.28394 | -32.653
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.13453 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -74.7992 | 556 | -0.28394 | -157.8703
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.13449 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.2839 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.13419 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.2836 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.13337 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.1403 | 196 | -0.28278 | -55.4244
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.13337 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -14.804 | 111 | -0.28278 | -31.3883
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.045627 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1095 | 0 | 0.18577 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.045627 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1095 | 0 | 0.18577 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.045627 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.12776 | 0 | 0.18577 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.13202 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -7.9214 | 60 | -0.28143 | -16.8859
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.13202 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -8.3175 | 63 | -0.28143 | -17.7302
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.046659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.6256 | 142 | 0.1868 | 26.5259
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.046659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.7656 | 145 | 0.1868 | 27.0863
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.046659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.0455 | 151 | 0.1868 | 28.2071
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.046659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 13.5311 | 290 | 0.1868 | 54.1725
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.047201 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1888 | 0 | 0.18734 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.13068 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -56.8458 | 435 | -0.28009 | -121.8385
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.1306 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -14.6921 | 0 | -0.28 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.13039 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -51.5033 | 395 | -0.2798 | -110.5196
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.13039 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -56.7188 | 435 | -0.2798 | -121.7115
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.13015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -28.1634 | 216.4 | -0.27955 | -60.4954
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.13015 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -28.1243 | 216.1 | -0.27955 | -60.4115
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.048236 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11577 | 0 | 0.18838 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.048236 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11577 | 0 | 0.18838 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.13009 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.27949 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.13009 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.27949 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.13009 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.27949 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.12875 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -28.8404 | 224 | -0.27816 | -62.3079
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.12875 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -29.098 | 226 | -0.27816 | -62.8643
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.12875 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -27.2954 | 212 | -0.27816 | -58.97
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.12875 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -27.1667 | 211 | -0.27816 | -58.6919
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.1287 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -37.065 | 288 | -0.27811 | -80.0947
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.1287 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -18.9186 | 147 | -0.27811 | -40.8817
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.1287 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -18.9186 | 147 | -0.27811 | -40.8817
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.12813 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.27754 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12793 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.0975 | 204 | -0.27734 | -56.5768
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12793 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -25.7137 | 201 | -0.27734 | -55.7448
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12793 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -30.9588 | 242 | -0.27734 | -67.1157
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.12782 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -27.7764 | 217.3 | -0.27723 | -60.2428
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.12782 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -26.2041 | 205 | -0.27723 | -56.8329
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.12782 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -34.8195 | 272.4 | -0.27723 | -75.5184
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.12748 | north | 3 | N | N | Nnorth | Nnorth | 1 | -147.5001 | 0 | -0.27689 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.12748 | north | 3 | N | N | Nnorth | Nnorth | 1 | -147.6276 | 0 | -0.27689 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.1271 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.2879 | 18 | -0.27651 | -4.9772
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.1271 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.2879 | 18 | -0.27651 | -4.9772
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.1271 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -4.8299 | 38 | -0.27651 | -10.5074
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.5555 | 147 | 0.19154 | 28.1565
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.0929 | 138 | 0.19154 | 26.4326
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.1957 | 140 | 0.19154 | 26.8157
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.5555 | 147 | 0.19154 | 28.1565
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.3544 | 182 | 0.19154 | 34.8604
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.051398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 10.1768 | 198 | 0.19154 | 37.9251
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.051967 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43652 | 8.4 | 0.19211 | 1.6137
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.1263 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.8412 | 70 | -0.27571 | -19.2998
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.1263 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.7149 | 69 | -0.27571 | -19.0241
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.1263 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.7149 | 69 | -0.27571 | -19.0241
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.1263 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.5886 | 68 | -0.27571 | -18.7484
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.12604 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.5207 | 20 | -0.27545 | -5.5089
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.12604 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.5207 | 20 | -0.27545 | -5.5089
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.12604 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.5207 | 20 | -0.27545 | -5.5089
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.12604 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.1426 | 17 | -0.27545 | -4.6826
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.052417 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 21.3337 | 407 | 0.19256 | 78.3719
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.12595 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.5114 | 0 | -0.27535 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.12595 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.5114 | 0 | -0.27535 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.052444 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.0418 | 58 | 0.19259 | 11.17
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.052444 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.6675 | 89 | 0.19259 | 17.1402
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.052444 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.3075 | 44 | 0.19259 | 8.4738
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.052444 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.3075 | 44 | 0.19259 | 8.4738
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.052444 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.2551 | 43 | 0.19259 | 8.2812
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.052444 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.36 | 45 | 0.19259 | 8.6664
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.052472 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 21.6185 | 412 | 0.19261 | 79.3573
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.052472 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 20.9888 | 400 | 0.19261 | 77.046
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.12589 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -46.0768 | 366 | -0.2753 | -100.7603
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.0525 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 22.26 | 0 | 0.19264 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.0525 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 22.3125 | 0 | 0.19264 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.12577 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -15.0925 | 0 | -0.27518 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.052629 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 10.9995 | 209 | 0.19277 | 40.2893
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.052629 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 11.3679 | 216 | 0.19277 | 41.6387
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.052629 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4209 | 46 | 0.19277 | 8.8675
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.052629 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4736 | 47 | 0.19277 | 9.0603
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.052629 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4209 | 46 | 0.19277 | 8.8675
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.052629 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4209 | 46 | 0.19277 | 8.8675
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.052688 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19283 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.052688 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19283 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.052688 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.19283 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.12541 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -21.0687 | 168 | -0.27482 | -46.1693
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.12541 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.2868 | 90 | -0.27482 | -24.7336
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.12512 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -30.2778 | 242 | -0.27452 | -66.4347
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.053657 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2878 | 24 | 0.1938 | 4.6512
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.053657 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 1.2878 | 24 | 0.1938 | 4.6512
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.053657 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 1.2341 | 23 | 0.1938 | 4.4574
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.0538 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.339 | 155 | 0.19394 | 30.0611
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.0538 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.146 | 170 | 0.19394 | 32.9703
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.0538 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.339 | 155 | 0.19394 | 30.0611
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.12454 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -9.0914 | 73 | -0.27395 | -19.9982
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.12454 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -14.8203 | 119 | -0.27395 | -32.5999
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.12454 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -25.5307 | 205 | -0.27395 | -56.1594
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.12454 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -12.7031 | 102 | -0.27395 | -27.9427
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.12454 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -11.9558 | 96 | -0.27395 | -26.2991
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.12407 | west | 4 | Y | N | Ywest | Nwest | 1 | -80.6096 | 0 | -0.27348 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.054817 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 29.9301 | 0 | 0.19496 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.054817 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 41.1127 | 0 | 0.19496 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.1234 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.361 | 0 | -0.27281 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.12261 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.9364 | 0 | -0.27202 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.12261 | west | 6 | Y | N | Ywest | Nwest | 1 | -49.0432 | 0 | -0.27202 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.12125 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2752 | 0 | -0.27066 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.057222 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.68666 | 0 | 0.19736 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.12032 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.0476 | 0 | -0.26973 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.1203 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -7.2183 | 0 | -0.26971 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.12029 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.1406 | 0 | -0.2697 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.12029 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.2167 | 0 | -0.2697 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.12029 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.9522 | 0 | -0.2697 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.12029 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.6971 | 0 | -0.2697 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5069 | 0 | -0.26959 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.9197 | 0 | -0.26959 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.2247 | 0 | -0.26959 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.3018 | 0 | -0.26959 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.6192 | 0 | -0.26959 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.12018 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.6747 | 0 | -0.26959 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.11982 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.9779 | 0 | -0.26923 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.11982 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.9779 | 0 | -0.26923 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.11967 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.9501 | 0 | -0.26908 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.11967 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.0864 | 0 | -0.26908 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.11959 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.0456 | 0 | -0.269 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.11943 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8231 | 0 | -0.26883 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.11943 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2849 | 0 | -0.26883 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.11943 | west | 7 | N | N | Nwest | Nwest | 1 | -2.9856 | 0 | -0.26883 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.11943 | west | 7 | N | N | Nwest | Nwest | 1 | -5.4577 | 0 | -0.26883 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.11943 | west | 7 | N | N | Nwest | Nwest | 1 | -5.4577 | 0 | -0.26883 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.11941 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.8362 | 0 | -0.26881 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.11941 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.3287 | 0 | -0.26881 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.11936 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.5194 | 0 | -0.26876 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.8743 | 66 | -0.26872 | -17.7353
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 1 | -8.2323 | 69 | -0.26872 | -18.5414
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 1 | -8.2323 | 69 | -0.26872 | -18.5414
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.9936 | 67 | -0.26872 | -18.004
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.9936 | 67 | -0.26872 | -18.004
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.11931 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.755 | 65 | -0.26872 | -17.4666
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.11916 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.874 | 0 | -0.26857 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.11916 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.2152 | 0 | -0.26857 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.11916 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.832 | 0 | -0.26857 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.11916 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.5256 | 0 | -0.26857 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.11896 | west | 8 | N | N | Nwest | Nwest | 1 | -8.3271 | 0 | -0.26837 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.11896 | west | 8 | N | N | Nwest | Nwest | 1 | -8.7315 | 0 | -0.26837 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.11896 | west | 8 | N | N | Nwest | Nwest | 1 | -8.3746 | 0 | -0.26837 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.11895 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.4103 | 0 | -0.26835 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.11895 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.4103 | 0 | -0.26835 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.11888 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.7482 | 0 | -0.26829 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.11886 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.2626 | 0 | -0.26826 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.11886 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.6932 | 0 | -0.26826 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.11886 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.2291 | 0 | -0.26826 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.11876 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.2516 | 0 | -0.26817 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.11873 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.2482 | 0 | -0.26814 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.11835 | west | 8 | N | N | Nwest | Nwest | 1 | -3.0534 | 0 | -0.26776 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.11827 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.3341 | 0 | -0.26768 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.11813 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8717 | 0 | -0.26753 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.11811 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.8501 | 0 | -0.26751 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.11809 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.7133 | 0 | -0.2675 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 1 | -8.2649 | 70 | -0.26748 | -18.7235
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 1 | -8.2649 | 70 | -0.26748 | -18.7235
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 1 | -10.9569 | 92.8 | -0.26748 | -24.822
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 1 | -9.4456 | 80 | -0.26748 | -21.3983
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 1 | -9.4456 | 80 | -0.26748 | -21.3983
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.11807 | west | 9 | Y | Y | Ywest | Ywest | 1 | -13.578 | 115 | -0.26748 | -30.76
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 1 | -24.5797 | 208.2 | -0.26747 | -55.6865
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 1 | -16.776 | 142.1 | -0.26747 | -38.007
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 1 | -15.6309 | 132.4 | -0.26747 | -35.4126
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 1 | -16.0559 | 136 | -0.26747 | -36.3754
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 1 | -17.3545 | 147 | -0.26747 | -39.3176
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.11806 | west | 9 | Y | Y | Ywest | Ywest | 1 | -24.7922 | 210 | -0.26747 | -56.168
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.11782 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.2552 | 0 | -0.26723 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.11782 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.6147 | 0 | -0.26723 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.11782 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.9153 | 0 | -0.26723 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.11782 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.2732 | 0 | -0.26723 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.060787 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.0787 | 100 | 0.20093 | 20.093
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.060787 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 6.0787 | 100 | 0.20093 | 20.093
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.060787 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.20093 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.060787 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.20093 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.060787 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.20093 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.060787 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.20093 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.060791 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.20093 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.11746 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.77526 | 0 | -0.26687 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.11746 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.029 | 0 | -0.26687 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.11709 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.4464 | 0 | -0.2665 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.06131 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 24.2788 | 0 | 0.20145 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.11699 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.8295 | 0 | -0.2664 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.11688 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0907 | 0 | -0.26629 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.11688 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.5063 | 0 | -0.26629 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.7099 | 66 | -0.26622 | -17.5708
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.593 | 65 | -0.26622 | -17.3046
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.8267 | 67 | -0.26622 | -17.837
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.8267 | 67 | -0.26622 | -17.837
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.11682 | west | 13 | Y | Y | Ywest | Ywest | 1 | -7.8267 | 67 | -0.26622 | -17.837
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.11682 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.26622 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.11682 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.26622 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.11225 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.5388 | 0 | -0.26166 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.067408 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.20755 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.11036 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8289 | 0 | -0.25977 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.11036 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8289 | 0 | -0.25977 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.10985 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2387 | 0 | -0.25926 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.10985 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.788 | 0 | -0.25926 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.10985 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.394 | 0 | -0.25926 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.10974 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.7791 | 0 | -0.25915 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.10972 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.7779 | 0 | -0.25913 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.10966 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.449 | 0 | -0.25907 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.10966 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.449 | 0 | -0.25907 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.071059 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.2112 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.10711 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.5689 | 0 | -0.25652 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.10692 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.6038 | 0 | -0.25633 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.10692 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.6038 | 0 | -0.25633 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.10669 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1614 | 0 | -0.25609 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.071837 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.86204 | 0 | 0.21198 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.071837 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.79021 | 0 | 0.21198 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.071837 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.86204 | 0 | 0.21198 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.10625 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.9251 | 0 | -0.25566 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.074333 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21448 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.074463 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 46.8372 | 0 | 0.21461 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.10226 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.3384 | 150 | -0.25166 | -37.7497
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.10226 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.1805 | 80 | -0.25166 | -20.1332
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.076467 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.2024 | 146.5 | 0.21661 | 31.7333
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.076467 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.3095 | 147.9 | 0.21661 | 32.0366
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.076467 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 13.2288 | 173 | 0.21661 | 37.4735
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.077228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.9862 | 207 | 0.21737 | 44.9958
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.077228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 16.7353 | 216.7 | 0.21737 | 47.1043
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.077228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.6892 | 242 | 0.21737 | 52.6038
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.077233 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.1216 | 144 | 0.21738 | 31.3021
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.077233 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.1216 | 144 | 0.21738 | 31.3021
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.077233 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 13.2068 | 171 | 0.21738 | 37.1713
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.077775 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21792 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.077776 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.9555 | 38 | 0.21792 | 8.2809
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.077776 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.5011 | 19.3 | 0.21792 | 4.2058
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.077776 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.1666 | 15 | 0.21792 | 3.2688
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.077776 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 3.6555 | 47 | 0.21792 | 10.2422
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.3302 | 0 | 0.21812 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.1972 | 0 | 0.21812 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.9633 | 0 | 0.21812 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.4816 | 0 | 0.21812 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.3302 | 0 | 0.21812 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.8073 | 0 | 0.21812 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3532 | 0 | 0.21812 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7156 | 0 | 0.21812 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 11.5412 | 0 | 0.21812 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.899 | 0 | 0.21812 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.289 | 0 | 0.21812 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.077981 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.899 | 0 | 0.21812 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.10021 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -25.5533 | 255 | -0.24962 | -63.6525
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.10021 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -14.9311 | 149 | -0.24962 | -37.193
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.10021 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -15.332 | 153 | -0.24962 | -38.1915
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.078315 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.2711 | 0 | 0.21846 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.079021 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0028 | 0 | 0.21916 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.07907 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.0047 | 0 | 0.21921 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.079187 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9797 | 0 | 0.21933 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.079187 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9797 | 0 | 0.21933 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.079271 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 26.4765 | 334 | 0.21941 | 73.2842
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.079271 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 26.9521 | 340 | 0.21941 | 74.6007
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.079271 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.2688 | 180 | 0.21941 | 39.4945
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.079271 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.2688 | 180 | 0.21941 | 39.4945
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.079552 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.3194 | 180 | 0.21969 | 39.5451
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.079581 | south | 8 | N | N | Nsouth | Nsouth | -1 | 11.8019 | 0 | 0.21972 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.079581 | south | 8 | N | N | Nsouth | Nsouth | -1 | 11.8257 | 0 | 0.21972 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.079581 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.1759 | 0 | 0.21972 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.079598 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 26.7449 | 336 | 0.21974 | 73.8329
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.079598 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.3276 | 180 | 0.21974 | 39.5534
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0127 | 0 | 0.22065 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0127 | 0 | 0.22065 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0127 | 0 | 0.22065 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.2881 | 0 | 0.22065 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0127 | 0 | 0.22065 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0127 | 0 | 0.22065 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0127 | 0 | 0.22065 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.080508 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.2076 | 0 | 0.22065 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.097858 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.24727 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.097858 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -77.0142 | 787 | -0.24727 | -194.5987
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.8154 | 0 | 0.22125 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -1 | 12.4098 | 0 | 0.22125 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -1 | 8.111 | 0 | 0.22125 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -1 | 11.7609 | 0 | 0.22125 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -1 | 11.9232 | 0 | 0.22125 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.08111 | south | 8 | N | N | Nsouth | Nsouth | -1 | 10.301 | 0 | 0.22125 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.08111 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.97332 | 0 | 0.22125 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.081194 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.6919 | 144 | 0.22134 | 31.8725
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.081194 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 15.2645 | 188 | 0.22134 | 41.6113
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.096283 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.24569 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.096283 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.24569 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.082595 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9398 | 47.7 | 0.22274 | 10.6246
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.082595 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.0808 | 37.3 | 0.22274 | 8.3081
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.082595 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.7994 | 46 | 0.22274 | 10.2459
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.082595 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9646 | 48 | 0.22274 | 10.6914
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.082642 | south | 7 | N | N | Nsouth | Nsouth | -1 | 6.0329 | 0 | 0.22278 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.083328 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8332 | 22 | 0.22347 | 4.9164
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.083328 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.91661 | 11 | 0.22347 | 2.4582
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.083328 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.91661 | 11 | 0.22347 | 2.4582
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.085121 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2768 | 0 | 0.22526 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.085121 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9578 | 0 | 0.22526 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.092541 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.24195 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.086006 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.68805 | 0 | 0.22615 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.086546 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.3753 | 0 | 0.22669 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.4233 | 0 | 0.22669 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.60583 | 0 | 0.22669 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.3753 | 0 | 0.22669 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2982 | 0 | 0.22669 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.60583 | 0 | 0.22669 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2982 | 0 | 0.22669 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.086547 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.3753 | 0 | 0.22669 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.090158 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.3276 | 0 | 0.2303 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 7.2086 | 0 | 0.23139 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 7.3911 | 0 | 0.23139 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 7.2086 | 0 | 0.23139 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 7.2998 | 0 | 0.23139 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 7.1538 | 0 | 0.23139 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.2812 | 0 | 0.23139 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 4.1974 | 0 | 0.23139 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.5549 | 0 | 0.23139 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.9784 | 0 | 0.23139 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.091248 | south | 7 | N | N | Nsouth | Nsouth | -1 | 6.7524 | 0 | 0.23139 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.082803 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.4205 | 0 | -0.23221 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 9.8551 | 76 | 0.26981 | 20.5059
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 9.8551 | 76 | 0.26981 | 20.5059
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 13.6156 | 105 | 0.26981 | 28.3306
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 9.5957 | 74 | 0.26981 | 19.9663
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 9.5957 | 74 | 0.26981 | 19.9663
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.12967 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 13.2265 | 102 | 0.26981 | 27.5211
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.13129 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 175.0136 | 0 | 0.27144 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.13129 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 174.3571 | 0 | 0.27144 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.13279 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 8.7643 | 66 | 0.27294 | 18.0138
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.6823 | 56 | 0.27733 | 15.5303
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 8.0939 | 59 | 0.27733 | 16.3623
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.6823 | 56 | 0.27733 | 15.5303
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.6823 | 56 | 0.27733 | 15.5303
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 8.0939 | 59 | 0.27733 | 16.3623
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.13718 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.6823 | 56 | 0.27733 | 15.5303
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.14604 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 25.2642 | 0 | 0.28618 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.14604 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 22.7816 | 0 | 0.28618 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.14604 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 22.4895 | 0 | 0.28618 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.14604 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 22.4895 | 0 | 0.28618 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.14604 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 23.6578 | 0 | 0.28618 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.14678 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.7614 | 12 | 0.28693 | 3.4431
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.1779 | 0 | 0.28817 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.5693 | 0 | 0.28817 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.6613 | 0 | 0.28817 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 14.951 | 0 | 0.28817 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 12.7306 | 0 | 0.28817 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 13.0266 | 0 | 0.28817 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.4015 | 0 | 0.28817 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6645 | 0 | 0.28817 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 13.9148 | 0 | 0.28817 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.3621 | 0 | 0.28817 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.3259 | 0 | 0.28817 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.6582 | 0 | 0.28817 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.5923 | 0 | 0.28817 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 14.951 | 0 | 0.28817 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 14.3589 | 0 | 0.28817 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 15.2471 | 0 | 0.28817 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.2503 | 0 | 0.28817 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.8424 | 0 | 0.28817 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.8424 | 0 | 0.28817 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.14803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 25.3131 | 0 | 0.28817 | 0
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.1481 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 24.111 | 0 | 0.28824 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.1481 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 23.9037 | 0 | 0.28824 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.1481 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 23.5334 | 0 | 0.28824 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.1481 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 39.8691 | 0 | 0.28824 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 15.4073 | 104 | 0.28829 | 29.9821
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 15.4073 | 104 | 0.28829 | 29.9821
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9999 | 54 | 0.28829 | 15.5677
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.8518 | 53 | 0.28829 | 15.2794
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9999 | 54 | 0.28829 | 15.5677
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 8.4444 | 57 | 0.28829 | 16.4325
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9999 | 54 | 0.28829 | 15.5677
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9999 | 54 | 0.28829 | 15.5677
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 8.5925 | 58 | 0.28829 | 16.7208
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.14815 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 8.5925 | 58 | 0.28829 | 16.7208
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.14844 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 25.5325 | 172 | 0.28859 | 49.6371
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.14844 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 25.5325 | 172 | 0.28859 | 49.6371
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.14844 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 25.5325 | 172 | 0.28859 | 49.6371
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.14899 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 110.6959 | 743 | 0.28913 | 214.822
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.14917 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.5911 | 0 | 0.28931 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.14917 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4917 | 0 | 0.28931 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.14923 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 1.7907 | 0 | 0.28937 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.14945 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.74726 | 0 | 0.28959 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.14945 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1385 | 0 | 0.28959 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.14965 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 59.5623 | 398 | 0.2898 | 115.3392
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.0983 | 0 | 0.29009 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.2033 | 0 | 0.29009 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.9034 | 0 | 0.29009 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.8827 | 0 | 0.29009 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6541 | 0 | 0.29009 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.059 | 0 | 0.29009 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.984 | 0 | 0.29009 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.2482 | 0 | 0.29009 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.6991 | 0 | 0.29009 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 12.8057 | 0 | 0.29009 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.14995 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 22.1926 | 0 | 0.29009 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.14996 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 110.2213 | 735 | 0.2901 | 213.2264
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.15013 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 23.5704 | 0 | 0.29027 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.15018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 16.6695 | 0 | 0.29032 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.15018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 16.6695 | 0 | 0.29032 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.15018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 17.8709 | 0 | 0.29032 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.15018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 16.4443 | 0 | 0.29032 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.765 | 0 | 0.29037 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.9152 | 0 | 0.29037 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.5162 | 0 | 0.29037 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.4646 | 0 | 0.29037 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.3143 | 0 | 0.29037 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 15.624 | 0 | 0.29037 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.15023 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 8.8636 | 0 | 0.29037 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 6.3629 | 42 | 0.29164 | 12.2489
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 6.3629 | 42 | 0.29164 | 12.2489
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 5.7569 | 38 | 0.29164 | 11.0823
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 5.7569 | 38 | 0.29164 | 11.0823
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 24.7538 | 0 | 0.29182 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 23.8286 | 0 | 0.29182 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 23.8893 | 0 | 0.29182 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 23.8134 | 0 | 0.29182 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.15168 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 40.8014 | 0 | 0.29182 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.15217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.8038 | 0 | 0.29231 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.15217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.956 | 0 | 0.29231 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.15217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.9345 | 0 | 0.29231 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.15217 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.565 | 0 | 0.29231 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.15236 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 32.452 | 213 | 0.2925 | 62.3025
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.15238 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4686 | 0 | 0.29253 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.15241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.7539 | 0 | 0.29255 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.15241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.632 | 0 | 0.29255 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.15241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 12.5887 | 0 | 0.29255 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.15241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.217 | 0 | 0.29255 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.15244 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 34.7572 | 228 | 0.29259 | 66.7098
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.15246 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 25.1564 | 165 | 0.29261 | 48.28
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.15248 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 25.769 | 169 | 0.29262 | 49.4531
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.1525 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.83 | 12 | 0.29264 | 3.5117
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.1525 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.29264 | 0
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.15258 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 22.735 | 0 | 0.29273 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.15258 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 9.9332 | 0 | 0.29273 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.15263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 27.4734 | 0 | 0.29277 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.15263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 24.2071 | 0 | 0.29277 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.15263 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 23.9629 | 0 | 0.29277 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.15295 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 11.9303 | 0 | 0.29309 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.15295 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 12.2362 | 0 | 0.29309 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.15298 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 26.4659 | 0 | 0.29312 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.15298 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 20.6526 | 0 | 0.29312 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.15299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.3547 | 0 | 0.29313 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.15319 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 20.8341 | 0 | 0.29333 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.15364 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 9.9869 | 0 | 0.29379 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.15364 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 9.2186 | 0 | 0.29379 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.15364 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 9.9869 | 0 | 0.29379 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.15364 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 9.9869 | 0 | 0.29379 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.15376 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 7.0884 | 0 | 0.2939 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 14.0204 | 0 | 0.29421 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 13.4965 | 0 | 0.29421 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 13.4041 | 0 | 0.29421 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 8.3968 | 0 | 0.29421 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.15407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8797 | 0 | 0.29421 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.15412 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.0858 | 0 | 0.29426 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.15488 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.29502 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.1868 | 46 | 0.29638 | 13.6334
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.1868 | 46 | 0.29638 | 13.6334
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 7.1868 | 46 | 0.29638 | 13.6334
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 8.5929 | 55 | 0.29638 | 16.3008
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 8.5929 | 55 | 0.29638 | 16.3008
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.15624 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 8.4367 | 54 | 0.29638 | 16.0044
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.021677 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.17109 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.1568 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 11.1012 | 0 | 0.29694 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.1568 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 10.4584 | 0 | 0.29694 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.1568 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 8.3102 | 0 | 0.29694 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 24.0213 | 0 | 0.29694 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 24.0683 | 0 | 0.29694 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 23.8802 | 0 | 0.29694 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 15.0525 | 0 | 0.29694 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.1568 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 38.2585 | 0 | 0.29694 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.1568 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 6.2719 | 0 | 0.29694 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.15681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 5.0179 | 0 | 0.29695 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.15681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 4.7042 | 0 | 0.29695 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.15681 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 15.7279 | 0 | 0.29695 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.15681 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 14.5676 | 0 | 0.29695 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.15681 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 16.1043 | 0 | 0.29695 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.15681 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 15.9945 | 0 | 0.29695 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.15926 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 25.6412 | 161 | 0.2994 | 48.2042
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.15926 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 26.4375 | 166 | 0.2994 | 49.7012
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.15926 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 39.497 | 248 | 0.2994 | 74.2524
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.15926 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 86.9571 | 546 | 0.2994 | 163.4751
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.15926 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 102.4055 | 0 | 0.2994 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.15926 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 2.0704 | 13 | 0.2994 | 3.8923
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.15928 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 7.9638 | 50 | 0.29942 | 14.9709
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.17009 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 27.724 | 0 | 0.31023 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.17009 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 27.724 | 0 | 0.31023 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.17009 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 41.6711 | 0 | 0.31023 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.17015 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 110.769 | 0 | 0.31029 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.17015 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 95.9657 | 0 | 0.31029 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.17015 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 102.0912 | 0 | 0.31029 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.14941 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.14941 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.04339 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 4.339 | 0 | -0.10602 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.14528 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.4016 | 0 | -0.0041325 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.14528 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.6631 | 0 | -0.0041325 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.14528 | north | 1 | N | N | Nnorth | Nnorth | 1 | 22.6631 | 0 | -0.0041325 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.14528 | north | 1 | N | N | Nnorth | Nnorth | 1 | 55.2049 | 0 | -0.0041325 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
Average line rating
Temp | Obrien -Singleton
20 | 1562
25 | 1538
30 | 1515
35 | 1490
40 | 1466
45 | 1441
50 | 1415
55 | 1389
60 | 1362
65 | 1334
70 | 1306
75 | 1276
80 | 1246
85 | 1215
90 | 1183
95 | 1150
100 | 1116
105 | 1080
110 | 1043
115 | 1043
26170
avg | 1308.5