## test results
CRE test for: |  | 173 CRAWFORD 177 BOSQUE | [5 empty] | FAIL
Line Rating: |  | 226.45
Direcction |  | North | → | South |  | N-S
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 173 CRAWFORD 177 BOSQUE
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.023701
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.029262
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.022223
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.0069217
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 173 CRAWFORD 177 BOSQUE
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.026717
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.028794
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.022318
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.0064976
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 173 CRAWFORD 177 BOSQUE
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.052495
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.0013834
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.030199
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.051581
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.022341
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.02872
PTDF tests
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.052495 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.052495 | -0.052495
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.066948
[6 empty] | Concentration |  | -1.2753 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.11231
[6 empty] | Concentration |  | -2.1395 | FAIL
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 53.0825
| Percent of line rating => | [6 empty] | 23.44% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -7.6564
[7 empty] | B1(N-S) | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B2 (N-W) | 0.0060222 | 0.016614 | 0.010592 | 0.0060222
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.012065 | 0.21915 | 0.23122 | -0.012065
[7 empty] | B4 (S-W) | 0.0053388 | -0.38958 | -0.39492 | 0.0053388
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.015995 | -0.18705 | -0.17105 | -0.015995
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0181 | 0.20179 | 0.21989 | -0.0181
[7 empty] | test | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B1 | 0%
Deployment Error Percent | [6 empty] | B2 | 1.498%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -3.002%
[7 empty] | B4 | 1.328%
[7 empty] | B5 | -3.98%
[7 empty] | B6 | -4.503%
[7 empty] | Max Abs Error | 4.503% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-S
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:173 CRAWFORD 177 BOSQUE C:THOUSE__5-AEP_PEC__5 C:LAKE_CRK1_5-AEP_SS__59 [3405 - 3412] and [3409 - 3414] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:173 CRAWFORD 177 BOSQUE C:THOUSE__5-AEP_PEC__5 C:LAKE_CRK1_5-AEP_SS__59 [3405 - 3412] and [3409 - 3414]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.059587 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -15.1947
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.059587 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -8.8785
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.074008 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -1.1101
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.074008 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -1.1101
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.059587 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -9.1168
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.083518 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -12.5277
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.083518 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -6.6814
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.02975 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -2.1717
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.02975 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -3.5402
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.02975 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -6.0987
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.02975 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -3.0345
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.02975 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -2.856
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.026615 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.31938
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.026615 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.31938
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.032115 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -5.3953
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.032115 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -2.8904
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.027625 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.49725
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.027625 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.49725
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.027625 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -1.0497
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.026253 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -7.5609
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.026253 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -3.8592
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.026253 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -3.8592
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.025112 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -2.8251
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.023958 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -0.95832
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.023931 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -1.8905
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.023931 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -2.5367
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.023931 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -3.4939
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.023931 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -1.8188
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.024604 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -1.4762
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.024604 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -1.5501
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.023898 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -0.47796
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.023898 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -0.59745
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.023898 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -0.97982
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.006942 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -3.2141
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -1.4424
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -1.4206
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -1.4643
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -1.4643
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -1.4643
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.021855 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -2.4915
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.021855 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -11.2553
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -1.4928
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -1.5606
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -1.5606
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -1.5154
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -1.5154
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -1.4702
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.022485 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -1.5739
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.022485 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -1.6504
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.022485 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -1.5829
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.022544 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -3.3816
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.022544 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -4.9597
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.022691 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -2.2464
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.022691 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -1.3842
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.022684 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -3.1984
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.022691 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -0.56727
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.022691 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -1.037
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.022691 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -1.037
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.022684 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -2.7221
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.022322 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -0.57591
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.022252 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -2.2363
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.022448 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -2.6938
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.022249 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -1.2904
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.022301 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -4.7769
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.022924 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -3.4386
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.02203 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -0.1454
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.02203 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -0.75563
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.022924 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -2.3153
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.02246 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -2.6952
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | -0.024407 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | -8.933
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.025152 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -6.0868
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.023528 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -9.4112
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.023529 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -5.5528
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.02374 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -3.9171
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.02476 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -5.051
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.02476 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -4.9768
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.02476 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -5.9919
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.024609 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.49218
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.024609 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.49218
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.024609 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.49218
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.024609 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -0.41835
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.026664 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -3.1997
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.031539 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -1.8923
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.023937 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -1.7953
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.023937 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -1.9054
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.023937 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -2.116
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -3.8318
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -3.736
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -4.694
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -3.736
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -3.76
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -4.7419
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.024036 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -4.0861
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.024036 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -12.4987
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.023972 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -8.8696
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.023906 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -13.3395
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.023906 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -13.8416
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.023906 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -19.316
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.025192 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -2.8215
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.025192 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -2.5192
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.025192 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -9.5226
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.025666 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -5.5772
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.025666 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -5.2615
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.025666 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -6.9914
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.025939 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -19.973
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.028895 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -2.0227
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.028895 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -1.9938
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.028895 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -1.9938
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.028895 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -1.9649
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.025724 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -29.7627
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.025724 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -29.7884
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.025729 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -5.7633
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.025729 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -5.8148
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.024977 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -5.405
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.024977 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -5.3975
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.025729 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -5.4545
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.025729 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -5.4288
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.025271 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -9.982
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.025279 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -10.9964
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.025271 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -10.9929
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.024202 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -3.3399
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.024314 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -2.8691
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.024314 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -2.7961
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.024314 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -13.5186
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.023842 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -9.2507
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.023842 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -12.2786
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.022456 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -17.628
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.022456 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -17.8525
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.022456 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -17.5157
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.022024 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -4.0084
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.022024 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -10.6596
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.026427 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -5.9196
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.02209 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -1.1045
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.02211 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -0.92862
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.019819 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -12.1887
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.019819 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -11.6338
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.030835 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -16.5584
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.030835 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -24.2671
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.018636 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -1.3977
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.018636 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -4.1372
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.043247 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 24.6075
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.027875 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 5.8259
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.027875 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 6.021
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.027863 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 11.3402
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.027875 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 1.2822
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.027875 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 1.3101
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.027875 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 1.2822
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.027875 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 1.2822
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.027927 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 11.841
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.027927 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 11.869
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.027708 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 1.6071
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.027708 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 2.466
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.027708 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 1.2192
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.027708 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 1.2192
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.027708 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 1.1914
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.027708 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 1.2469
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.027906 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 11.4973
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.027906 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 11.1624
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.027669 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 15.1073
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.027669 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 20.7518
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.028002 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 1.7081
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.028002 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 2.6602
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.028002 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 4.2283
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.027814 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 4.3112
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.027814 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 4.7284
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.027814 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 4.3112
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.022491 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.4948
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.022491 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.2474
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.022491 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.2474
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.022697 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 1.0826
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.022697 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.8466
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.022697 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 1.0441
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.022697 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 1.0895
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.023642 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.2837
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.023642 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.26006
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.024575 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.5898
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.024575 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.5898
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.024575 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.56522
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.026167 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 10.3621
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.014699 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 19.5938
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.014699 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 19.5203
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.023313 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.88589
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.023313 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.44994
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.023313 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.34969
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.023313 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 1.0957
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.019788 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -1.4841
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.023071 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -3.4606
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.021865 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -3.7061
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.01085 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -1.6275
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.022664 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -1.4278
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.02396 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -15.5668
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.024085 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.9634
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.024085 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.9634
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.033781 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 14.2556
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.035173 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 4.6428
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.035173 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 4.7132
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.035173 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 11.3609
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.0348 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 5.4984
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.0348 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 5.568
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.0348 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 6.09
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.031196 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 18.2185
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.031196 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 18.5616
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.031167 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 13.4953
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.03066 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 6.8648
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.03066 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 6.8985
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.03066 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 6.8862
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.03066 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 6.9506
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.037053 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.29642
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.037053 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.29642
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.034939 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.6289
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.034939 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.6289
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.034939 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.52409
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.033884 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.46421
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.034605 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.62289
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.034605 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.62289
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.036472 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 1.2765
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.036472 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 1.24
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.036472 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 1.2765
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.034072 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.95402
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.034072 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.98809
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.021875 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -0.76562
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.021875 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -0.65625
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.031843 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 1.5921
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.031843 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 1.5921
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.031843 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 1.5921
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.031843 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 1.5921
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.031695 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.19017
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.0298 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.07152
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.0298 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.07152
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.0298 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.08344
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.029354 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.11742
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.029423 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.070615
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.029423 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.070615
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 4.2018
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 3.9446
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 4.0018
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 4.2018
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 5.2023
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 5.6596
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.03518 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 5.365
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.03518 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 5.2594
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.03518 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 8.1829
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.029597 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 4.2028
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.029597 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 4.2916
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.029597 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 4.4691
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.029597 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 8.5831
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.012504 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.41263
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.012504 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.3126
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.023642 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.2837
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.022749 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 1.6607
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 1.6818
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 1.7243
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.61771
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.15443
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 1.6818
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 1.703
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 1.669
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.5322
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.97925
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.024059 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 15.1331
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.022999 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 3.3119
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.022999 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 4.3238
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.02765 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.3318
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.016264 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.097584
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.023074 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 7.7529
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.023126 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 7.7241
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.023126 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 7.8628
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.023157 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.87997
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.023134 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.57835
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.023134 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.57835
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.023156 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.87993
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.023264 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.67466
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.023077 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 3.4223
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.023077 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 3.4292
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.023077 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 3.5308
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 3.6092
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 3.495
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 2.2843
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 3.3122
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 3.3579
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 2.9011
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.023394 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 3.4272
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.023394 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 3.46
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.023394 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 4.0472
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.023354 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 4.8343
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.023354 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 5.0608
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.023354 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 5.6517
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.023353 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 3.3628
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.023353 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 3.3628
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.023353 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 3.9934
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.037078 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 11.4942
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.037078 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 15.3132
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.037419 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 1.5716
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.037419 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 1.6464
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.037419 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 1.6464
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.037419 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 1.7587
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 1.7924
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 1.6826
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 1.6826
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 1.7192
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.036579 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 5.6332
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.036579 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 5.4137
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 1.7558
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 1.7558
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -1.5557
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -1.5557
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -2.0624
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -1.7779
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -1.7779
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -2.5558
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -4.6262
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -3.1575
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -2.9419
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -3.0219
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -3.2663
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -4.6662
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.022862 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -4.7782
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.022862 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -2.892
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.022862 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -5.6926
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.022862 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -4.5038
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.022544 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -4.5088
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.022544 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -2.7481
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.021941 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -3.2692
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.022529 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -4.0552
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.022529 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -4.0552
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.022509 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -5.0645
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.022736 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -2.842
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.022736 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -2.842
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -3.3561
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -3.3801
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -7.4073
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -3.428
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -3.452
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -7.4313
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.027019 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -5.2957
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.027019 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -2.9991
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.024155 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -3.798
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -3.8688
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -3.8688
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -9.7663
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -3.8216
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -3.798
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -3.8452
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -9.6483
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.023911 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.023911 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.022301 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -3.3005
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.022301 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -2.8991
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.022301 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -3.2336
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.022301 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -8.8981
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.02023 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -3.0487
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.02023 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -3.0547
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.02023 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -3.5888
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.020359 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -3.0844
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.020359 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -3.1007
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.020359 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -3.6137
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.043247 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 25.1265
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.012844 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -10.9816
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.012844 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -10.9816
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.00548 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.17536
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.00483 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -0.23184
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.00483 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -0.22218
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.005492 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.065904
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.005492 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -0.28009
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.005492 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.093364
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.005492 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.12082
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.005492 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.1373
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.00483 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -0.50715
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.022761 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -1.9119
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.019751 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -1.5801
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.019732 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -2.9598
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.019732 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -2.9598
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007241 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 0.51266
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007241 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 0.48297
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007241 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 0.38377
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 1.1093
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 1.1115
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 1.1028
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 0.69514
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 1.7668
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007241 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 0.28964
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.007245 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 0.72667
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.007245 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 0.67306
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.007245 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 0.74406
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.007245 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 0.73899
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.007245 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 0.23184
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.007245 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 0.21735
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.010228 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 1.1353
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.010228 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 1.1353
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.010228 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 1.2171
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.010228 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 1.12
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.012844 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -1.9561
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.012844 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -1.9651
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.005424 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 0.73766
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.008236 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.27179
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.005413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.22735
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.005413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.22735
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.005413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.20569
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.005413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.20569
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.010707 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 0.7602
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.010707 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.10707
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.008416 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.3718
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.008416 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.3718
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.008416 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 2.0619
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.006102 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.39663
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.006102 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 0.36612
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.006102 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.39663
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.006102 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.39663
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.00566 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 0.84334
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.00566 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 0.36847
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 0.56739
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 0.54619
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 0.54244
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 0.33981
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.076067
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.004858 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 3.6095
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.005083 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 3.736
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.00479 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.82388
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.00479 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.82388
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.00479 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.82388
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00354 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 0.61242
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.005379 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 0.93057
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.005379 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 0.72616
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.004631 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 0.75393
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.004631 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 0.74744
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.004631 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 0.73587
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.004631 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 1.2467
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.005645 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 0.36128
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.005645 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 0.35676
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.005645 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 0.46628
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.005645 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 0.41547
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 0.94428
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 0.90898
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 0.91129
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 0.9084
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 1.5564
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.00487 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.02435
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.00487 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 0.10227
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.005274 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -0.81325
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.005274 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.82274
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.005274 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.82274
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.005274 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -2.0041
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.004575 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 1.8209
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.27158
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.27158
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.27158
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.32472
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.32472
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 0.31882
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.01534 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -12.6862
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.01534 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -12.5635
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.008495 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.39162
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 1.1104
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 1.1104
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 1.534
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 1.0811
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 1.0811
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 1.4902
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.005641 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 1.0154
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.005641 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 0.89466
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.005641 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 0.88564
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.005731 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 0.20059
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.006575 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 3.0179
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 0.31642
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 0.32129
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 0.34076
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 0.30668
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 0.30182
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 0.50627
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 0.28721
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00354 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 0.55224
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00354 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 0.54516
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00354 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 0.54516
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00354 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 0.57348
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.004817 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 0.75627
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.005557 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 0.39455
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.005557 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 0.4001
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.005557 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 0.21672
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.005557 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 0.16671
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.005855 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 0.45669
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.005855 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 0.4684
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.005646 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 0.091465
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.005663 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 0.93439
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.005668 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 0.95789
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.005647 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 1.2028
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.005643 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 1.2866
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.005671 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.068052
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.005671 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 0.10208
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.006867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 0.34335
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.53716
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.53716
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.27891
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.27375
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.27891
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.2944
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.27891
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.27891
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.29957
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.29957
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.004958 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.059496
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.25077
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.2642
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.25077
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.25077
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.2642
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.25077
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.013818 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 0.91199
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008157 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 1.3133
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008157 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 1.3541
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008157 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 2.0229
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008157 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 4.4537
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008157 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 5.245
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.008431 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 5.4886
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.008431 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 4.7551
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.008431 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 5.0586
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008157 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.10604
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.004864 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.058368
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 0.17095
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 0.17447
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 0.16442
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 0.23079
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 0.088996
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 0.10257
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 0.10006
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 0.17598
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 0.090504
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 0.42939
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 0.74414
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 0.70134
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 0.80768
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.50904
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 1.1425
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 0.97283
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 0.99546
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.5656
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.20362
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 1.0633
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 0.79184
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 0.71266
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 0.81446
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 0.73302
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 1.1425
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 1.0973
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 1.1651
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 0.85971
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.90496
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.90496
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 1.9344
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.20387
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.018848 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -1.4419
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.019788 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -1.583
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.019788 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -0.79152
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.019939 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -1.5951
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.019755 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -1.5804
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.018977 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -1.5182
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.018723 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -1.5727
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.019939 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -1.5951
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 3.3424
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.022506 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -2.7007
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.022506 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -5.2439
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.022506 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -3.8305
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 6.5088
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 5.3947
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 6.5675
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 3.3717
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 2.9319
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.023393 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -1.4036
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.01558 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.014666 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.0205 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -0.0984
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -0.85721
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -2.4573
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -3.086
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -2.7202
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -2.4002
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -1.8401
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.022215 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -3.3323
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.022134 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -2.4901
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.022134 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -3.309
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.022134 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -4.1169
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.022134 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -4.7477
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.023313 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.017139 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.02445 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.59606
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.92816
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 1.5753
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 2.1901
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.95526
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.88536
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.44268
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 2.1901
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.83876
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 1.0019
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.51258
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.86038
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.33092
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.15443
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.33092
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.86038
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.86038
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 3.4483
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 1.1649
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 1.2814
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 1.1649
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.022843 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.27412
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.022309 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.33464
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.022309 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.51311
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.02147 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 1.0306
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.022148 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.17718
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.023081 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 4.1546
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.023074 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 4.1533
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.023126 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 4.1627
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.023126 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 4.1627
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.024452 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 2.4452
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.024452 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 2.4452
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.57335
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.57335
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.57335
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.36694
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.57335
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.57335
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.57335
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.34401
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.024452 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.024452 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 12.226
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.024452 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 12.226
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.024452 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.024358 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.012504 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.023879 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.023671 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L:173 CRAWFORD 177 BOSQUE C:THOUSE__5-AEP_PEC__5 C:LAKE_CRK1_5-AEP_SS__59 [3405 - 3412] and [3409 - 3414] | [7 empty] | 53.0825
Number of Bus | Name of Bus | ID | Max MW | L:173 CRAWFORD 177 BOSQUE C:THOUSE__5-AEP_PEC__5 C:LAKE_CRK1_5-AEP_SS__59 [3405 - 3412] and [3409 - 3414] | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.059587 | north | -0.035886 | -0.088849 | -0.037364 | -0.066509 | 0.035886 | North | N | 0.035886 | 0
239 | BOSQUESW | 1 | 149 | -0.059587 | north | -0.035886 | -0.088849 | -0.037364 | -0.066509 | 0.035886 | North | N | 0.035886 | 0
244 | WHITNYDM | 1 | 15 | -0.074008 | north | -0.050307 | -0.10327 | -0.051785 | -0.08093 | 0.050307 | North | N | 0.050307 | 0
245 | WHITNYDM | 2 | 15 | -0.074008 | north | -0.050307 | -0.10327 | -0.051785 | -0.08093 | 0.050307 | North | N | 0.050307 | 0
247 | BOSQUESW | 2 | 153 | -0.059587 | north | -0.035886 | -0.088849 | -0.037364 | -0.066509 | 0.035886 | North | N | 0.035886 | 0
251 | BOSQUESW | 2 | 150 | -0.083518 | north | -0.059817 | -0.11278 | -0.061295 | -0.09044 | 0.059817 | North | N | 0.059817 | 0
253 | BOSQUESW | 2 | 80 | -0.083518 | north | -0.059817 | -0.11278 | -0.061295 | -0.09044 | 0.059817 | North | N | 0.059817 | 0
332 | RWMILLER | 1 | 73 | -0.02975 | north | -0.0060485 | -0.059012 | -0.0075274 | -0.036672 | 0.0060485 | North | N | 0.0060485 | 0
333 | RWMILLER | 2 | 119 | -0.02975 | north | -0.0060485 | -0.059012 | -0.0075274 | -0.036672 | 0.0060485 | North | N | 0.0060485 | 0
334 | RWMILLER | 3 | 205 | -0.02975 | north | -0.0060485 | -0.059012 | -0.0075274 | -0.036672 | 0.0060485 | North | N | 0.0060485 | 0
335 | RWMILLER | 4 | 102 | -0.02975 | north | -0.0060485 | -0.059012 | -0.0075274 | -0.036672 | 0.0060485 | North | N | 0.0060485 | 0
336 | RWMILLER | 5 | 96 | -0.02975 | north | -0.0060485 | -0.059012 | -0.0075274 | -0.036672 | 0.0060485 | North | N | 0.0060485 | 0
344 | MRSSHPRD | 1 | 12 | -0.026615 | north | -0.0029135 | -0.055877 | -0.0043924 | -0.033537 | 0.0029135 | North | N | 0.0029135 | 0
345 | MRSSHPRD | 2 | 12 | -0.026615 | north | -0.0029135 | -0.055877 | -0.0043924 | -0.033537 | 0.0029135 | North | N | 0.0029135 | 0
366 | JNSNCNTY | 1 | 168 | -0.032115 | north | -0.0084135 | -0.061377 | -0.0098924 | -0.039037 | 0.0084135 | North | N | 0.0084135 | 0
367 | JNSNCNTY | 2 | 90 | -0.032115 | north | -0.0084135 | -0.061377 | -0.0098924 | -0.039037 | 0.0084135 | North | N | 0.0084135 | 0
503 | NTHTEXAS | 1 | 18 | -0.027625 | north | -0.0039235 | -0.056887 | -0.0054024 | -0.034547 | 0.0039235 | North | N | 0.0039235 | 0
504 | NTHTEXAS | 2 | 18 | -0.027625 | north | -0.0039235 | -0.056887 | -0.0054024 | -0.034547 | 0.0039235 | North | N | 0.0039235 | 0
505 | NTHTEXAS | 3 | 38 | -0.027625 | north | -0.0039235 | -0.056887 | -0.0054024 | -0.034547 | 0.0039235 | North | N | 0.0039235 | 0
580 | JCKCNTY8 | 1 | 288 | -0.026253 | north | -0.0025515 | -0.055515 | -0.0040304 | -0.033175 | 0.0025515 | North | N | 0.0025515 | 0
581 | JCKCNTY8 | 2 | 147 | -0.026253 | north | -0.0025515 | -0.055515 | -0.0040304 | -0.033175 | 0.0025515 | North | N | 0.0025515 | 0
582 | JCKCNTY8 | 3 | 147 | -0.026253 | north | -0.0025515 | -0.055515 | -0.0040304 | -0.033175 | 0.0025515 | North | N | 0.0025515 | 0
728 | WOLFRIDG | 1 | 112.5 | -0.025112 | north | -0.0014105 | -0.054374 | -0.0028894 | -0.032034 | 0.0014105 | North | N | 0.0014105 | 0
837 | NEWMAN_G | 1 | 40 | -0.023958 | north | -0.00025652 | -0.05322 | -0.0017354 | -0.03088 | 0.00025652 | North | N | 0.00025652 | 0
842 | OLINGER_ | 1 | 79 | -0.023931 | north | -0.00022952 | -0.053193 | -0.0017084 | -0.030853 | 0.00022952 | North | N | 0.00022952 | 0
843 | OLINGER_ | 1 | 106 | -0.023931 | north | -0.00022952 | -0.053193 | -0.0017084 | -0.030853 | 0.00022952 | North | N | 0.00022952 | 0
844 | OLINGER_ | 1 | 146 | -0.023931 | north | -0.00022952 | -0.053193 | -0.0017084 | -0.030853 | 0.00022952 | North | N | 0.00022952 | 0
845 | OLINGER_ | 1 | 76 | -0.023931 | north | -0.00022952 | -0.053193 | -0.0017084 | -0.030853 | 0.00022952 | North | N | 0.00022952 | 0
923 | SPENCER_ | 1 | 60 | -0.024604 | north | -0.00090252 | -0.053866 | -0.0023814 | -0.031526 | 0.00090252 | North | N | 0.00090252 | 0
924 | SPENCER_ | 1 | 63 | -0.024604 | north | -0.00090252 | -0.053866 | -0.0023814 | -0.031526 | 0.00090252 | North | N | 0.00090252 | 0
948 | STEAM1 | 1 | 20 | -0.023898 | north | -0.00019652 | -0.05316 | -0.0016754 | -0.03082 | 0.00019652 | North | N | 0.00019652 | 0
949 | STEAM2 | 1 | 25 | -0.023898 | north | -0.00019652 | -0.05316 | -0.0016754 | -0.03082 | 0.00019652 | North | N | 0.00019652 | 0
950 | STEAM3 | 1 | 41 | -0.023898 | north | -0.00019652 | -0.05316 | -0.0016754 | -0.03082 | 0.00019652 | North | N | 0.00019652 | 0
990 | GIBN_CRE | 1 | 463 | -0.006942 | north | 0.016759 | -0.036204 | 0.015281 | -0.013864 | 0.013864 | houston | Y | 0.016759 | 1.3408
1002 | PBCTAGE_ | A | 66 | -0.021855 | west | 0.0018465 | -0.051117 | 0.0003676 | -0.028777 | 0.0003676 | west | N | 0.0003676 | 0
1003 | PBCTBGE_ | B | 65 | -0.021855 | west | 0.0018465 | -0.051117 | 0.0003676 | -0.028777 | 0.0003676 | west | N | 0.0003676 | 0
1004 | PBCTCGE_ | C | 67 | -0.021855 | west | 0.0018465 | -0.051117 | 0.0003676 | -0.028777 | 0.0003676 | west | N | 0.0003676 | 0
1005 | PBCTDGE_ | D | 67 | -0.021855 | west | 0.0018465 | -0.051117 | 0.0003676 | -0.028777 | 0.0003676 | west | N | 0.0003676 | 0
1006 | PBCTEGE_ | E | 67 | -0.021855 | west | 0.0018465 | -0.051117 | 0.0003676 | -0.028777 | 0.0003676 | west | N | 0.0003676 | 0
1007 | PB5GEN_6 | MB | 114 | -0.021855 | west | 0.0018465 | -0.051117 | 0.0003676 | -0.028777 | 0.0003676 | west | N | 0.0003676 | 0
1008 | PB6GEN_7 | MB | 515 | -0.021855 | west | 0.0018465 | -0.051117 | 0.0003676 | -0.028777 | 0.0003676 | west | N | 0.0003676 | 0
1039 | MRGNAG_1 | A | 66 | -0.022618 | west | 0.0010835 | -0.05188 | -0.0003954 | -0.02954 | 0.0003954 | west | N | 0.0003954 | 0
1040 | MRGNBG_2 | B | 69 | -0.022618 | west | 0.0010835 | -0.05188 | -0.0003954 | -0.02954 | 0.0003954 | west | N | 0.0003954 | 0
1041 | MRGNCG_3 | C | 69 | -0.022618 | west | 0.0010835 | -0.05188 | -0.0003954 | -0.02954 | 0.0003954 | west | N | 0.0003954 | 0
1042 | MRGNDG_4 | D | 67 | -0.022618 | west | 0.0010835 | -0.05188 | -0.0003954 | -0.02954 | 0.0003954 | west | N | 0.0003954 | 0
1043 | MRGNEG_5 | E | 67 | -0.022618 | west | 0.0010835 | -0.05188 | -0.0003954 | -0.02954 | 0.0003954 | west | N | 0.0003954 | 0
1044 | MRGNFG_6 | F | 65 | -0.022618 | west | 0.0010835 | -0.05188 | -0.0003954 | -0.02954 | 0.0003954 | west | N | 0.0003954 | 0
1045 | CALENG1G | 1 | 70 | -0.022485 | west | 0.0012165 | -0.051747 | -0.0002624 | -0.029407 | 0.0002624 | west | N | 0.0002624 | 0
1046 | CALENG2G | 2 | 73.4 | -0.022485 | west | 0.0012165 | -0.051747 | -0.0002624 | -0.029407 | 0.0002624 | west | N | 0.0002624 | 0
1047 | CALENG3G | 3 | 70.4 | -0.022485 | west | 0.0012165 | -0.051747 | -0.0002624 | -0.029407 | 0.0002624 | west | N | 0.0002624 | 0
1058 | LONGSHOR | 1 | 150 | -0.022544 | west | 0.0011575 | -0.051806 | -0.0003214 | -0.029466 | 0.0003214 | west | N | 0.0003214 | 0
1058 | LONGSHOR | 2 | 220 | -0.022544 | west | 0.0011575 | -0.051806 | -0.0003214 | -0.029466 | 0.0003214 | west | N | 0.0003214 | 0
1061 | CIELOGEN | 1 | 99 | -0.022691 | west | 0.0010105 | -0.051953 | -0.0004684 | -0.029613 | 0.0004684 | west | N | 0.0004684 | 0
1062 | CIELOGEN | 1 | 61 | -0.022691 | west | 0.0010105 | -0.051953 | -0.0004684 | -0.029613 | 0.0004684 | west | N | 0.0004684 | 0
1068 | SCURRYCW | 1 | 141 | -0.022684 | west | 0.0010175 | -0.051946 | -0.0004614 | -0.029606 | 0.0004614 | west | N | 0.0004614 | 0
1069 | KINDERMG | 1 | 25 | -0.022691 | west | 0.0010105 | -0.051953 | -0.0004684 | -0.029613 | 0.0004684 | west | N | 0.0004684 | 0
1070 | KINDERMG | 1 | 45.7 | -0.022691 | west | 0.0010105 | -0.051953 | -0.0004684 | -0.029613 | 0.0004684 | west | N | 0.0004684 | 0
1071 | KINDERMG | 1 | 45.7 | -0.022691 | west | 0.0010105 | -0.051953 | -0.0004684 | -0.029613 | 0.0004684 | west | N | 0.0004684 | 0
1073 | SCURRYCW | 2 | 120 | -0.022684 | west | 0.0010175 | -0.051946 | -0.0004614 | -0.029606 | 0.0004614 | west | N | 0.0004614 | 0
1320 | BSP 1 | 1 | 25.8 | -0.022322 | west | 0.0013795 | -0.051584 | -9.9396e-05 | -0.029244 | 9.9396e-05 | west | N | 9.9396e-05 | 0
1326 | STANTONW | 1 | 100.5 | -0.022252 | west | 0.0014495 | -0.051514 | -2.9396e-05 | -0.029174 | 2.9396e-05 | west | N | 2.9396e-05 | 0
1327 | WILDHRSE | 1 | 120 | -0.022448 | west | 0.0012535 | -0.05171 | -0.0002254 | -0.02937 | 0.0002254 | west | N | 0.0002254 | 0
1328 | OCOTILLO | 1 | 58 | -0.022249 | west | 0.0014525 | -0.051511 | -2.6396e-05 | -0.029171 | 2.6396e-05 | west | N | 2.6396e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.022301 | west | 0.0014005 | -0.051563 | -7.8396e-05 | -0.029223 | 7.8396e-05 | west | N | 7.8396e-05 | 0
1343 | TRENTIPP | 1 | 150 | -0.022924 | west | 0.00077748 | -0.052186 | -0.0007014 | -0.029846 | 0.0007014 | west | N | 0.0007014 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.02203 | west | 0.0016715 | -0.051292 | 0.0001926 | -0.028952 | 0.0001926 | west | N | 0.0001926 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.02203 | west | 0.0016715 | -0.051292 | 0.0001926 | -0.028952 | 0.0001926 | west | N | 0.0001926 | 0
1354 | AEPWIND_ | 1 | 101 | -0.022924 | west | 0.00077748 | -0.052186 | -0.0007014 | -0.029846 | 0.0007014 | west | N | 0.0007014 | 0
1360 | GUNSIGHT | 1 | 120 | -0.02246 | west | 0.0012415 | -0.051722 | -0.0002374 | -0.029382 | 0.0002374 | west | N | 0.0002374 | 0
1432 | GRHAMSES | 2 | 366 | -0.024407 | north | -0.00070552 | -0.053669 | -0.0021844 | -0.031329 | 0.00070552 | North | N | 0.00070552 | 0
1433 | GRHAMSES | 1 | 242 | -0.025152 | north | -0.0014505 | -0.054414 | -0.0029294 | -0.032074 | 0.0014505 | North | N | 0.0014505 | 0
1437 | MESQUITW | 1 | 400 | -0.023528 | west | 0.00017348 | -0.05279 | -0.0013054 | -0.03045 | 0.00017348 | North | Y | 0.0013054 | 0.45277
1438 | MESQUITW | 1 | 236 | -0.023529 | west | 0.00017248 | -0.052791 | -0.0013064 | -0.030451 | 0.00017248 | North | Y | 0.0013064 | 0.2676
1442 | COKFIELD | 1 | 165 | -0.02374 | west | -3.8517e-05 | -0.053002 | -0.0015174 | -0.030662 | 3.8517e-05 | North | Y | 0.0015174 | 0.24401
1453 | WCPWRCO_ | 1 | 204 | -0.02476 | north | -0.0010585 | -0.054022 | -0.0025374 | -0.031682 | 0.0010585 | North | N | 0.0010585 | 0
1454 | WCPWRCO_ | 2 | 201 | -0.02476 | north | -0.0010585 | -0.054022 | -0.0025374 | -0.031682 | 0.0010585 | North | N | 0.0010585 | 0
1455 | WCPWRCO_ | 3 | 242 | -0.02476 | north | -0.0010585 | -0.054022 | -0.0025374 | -0.031682 | 0.0010585 | North | N | 0.0010585 | 0
1479 | WFCOGEN_ | 1 | 20 | -0.024609 | west | -0.00090752 | -0.053871 | -0.0023864 | -0.031531 | 0.00090752 | North | Y | 0.0023864 | 0.029578
1479 | WFCOGEN_ | 2 | 20 | -0.024609 | west | -0.00090752 | -0.053871 | -0.0023864 | -0.031531 | 0.00090752 | North | Y | 0.0023864 | 0.029578
1482 | WFCOGEN_ | 1 | 20 | -0.024609 | west | -0.00090752 | -0.053871 | -0.0023864 | -0.031531 | 0.00090752 | North | Y | 0.0023864 | 0.029578
1482 | WFCOGEN_ | 2 | 17 | -0.024609 | west | -0.00090752 | -0.053871 | -0.0023864 | -0.031531 | 0.00090752 | North | Y | 0.0023864 | 0.025141
1600 | BARTNWND | 1 | 120 | -0.026664 | north | -0.0029625 | -0.055926 | -0.0044414 | -0.033586 | 0.0029625 | North | N | 0.0029625 | 0
1643 | SLSTR1PP | 1 | 60 | -0.031539 | north | -0.0078375 | -0.060801 | -0.0093164 | -0.038461 | 0.0078375 | North | N | 0.0078375 | 0
1675 | PEC_1G | 1 | 75 | -0.023937 | north | -0.00023552 | -0.053199 | -0.0017144 | -0.030859 | 0.00023552 | North | N | 0.00023552 | 0
1676 | PEC_2G | 2 | 79.6 | -0.023937 | north | -0.00023552 | -0.053199 | -0.0017144 | -0.030859 | 0.00023552 | North | N | 0.00023552 | 0
1677 | PEC_3G | 3 | 88.4 | -0.023937 | north | -0.00023552 | -0.053199 | -0.0017144 | -0.030859 | 0.00023552 | North | N | 0.00023552 | 0
1678 | LAMARPWR | 1 | 160 | -0.023949 | north | -0.00024752 | -0.053211 | -0.0017264 | -0.030871 | 0.00024752 | North | N | 0.00024752 | 0
1679 | LAMARPWR | 2 | 156 | -0.023949 | north | -0.00024752 | -0.053211 | -0.0017264 | -0.030871 | 0.00024752 | North | N | 0.00024752 | 0
1680 | LAMARPWR | 3 | 196 | -0.023949 | north | -0.00024752 | -0.053211 | -0.0017264 | -0.030871 | 0.00024752 | North | N | 0.00024752 | 0
1681 | LAMARPWR | 4 | 156 | -0.023949 | north | -0.00024752 | -0.053211 | -0.0017264 | -0.030871 | 0.00024752 | North | N | 0.00024752 | 0
1682 | LAMARPWR | 5 | 157 | -0.023949 | north | -0.00024752 | -0.053211 | -0.0017264 | -0.030871 | 0.00024752 | North | N | 0.00024752 | 0
1683 | LAMARPWR | 6 | 198 | -0.023949 | north | -0.00024752 | -0.053211 | -0.0017264 | -0.030871 | 0.00024752 | North | N | 0.00024752 | 0
1687 | VALLEY_1 | 1 | 170 | -0.024036 | north | -0.00033452 | -0.053298 | -0.0018134 | -0.030958 | 0.00033452 | North | N | 0.00033452 | 0
1688 | VALLEY_2 | 2 | 520 | -0.024036 | north | -0.00033452 | -0.053298 | -0.0018134 | -0.030958 | 0.00033452 | North | N | 0.00033452 | 0
1689 | VALLEY_3 | 3 | 370 | -0.023972 | north | -0.00027052 | -0.053234 | -0.0017494 | -0.030894 | 0.00027052 | North | N | 0.00027052 | 0
1701 | MOSES_1G | 1 | 558 | -0.023906 | north | -0.00020452 | -0.053168 | -0.0016834 | -0.030828 | 0.00020452 | North | N | 0.00020452 | 0
1702 | MOSES_2G | 2 | 579 | -0.023906 | north | -0.00020452 | -0.053168 | -0.0016834 | -0.030828 | 0.00020452 | North | N | 0.00020452 | 0
1703 | MOSES_3G | 3 | 808 | -0.023906 | north | -0.00020452 | -0.053168 | -0.0016834 | -0.030828 | 0.00020452 | North | N | 0.00020452 | 0
1861 | EAGLEMNT | MB | 112 | -0.025192 | north | -0.0014905 | -0.054454 | -0.0029694 | -0.032114 | 0.0014905 | North | N | 0.0014905 | 0
1862 | EAGLEMNT | MB | 100 | -0.025192 | north | -0.0014905 | -0.054454 | -0.0029694 | -0.032114 | 0.0014905 | North | N | 0.0014905 | 0
1863 | EAGLEMNT | MB | 378 | -0.025192 | north | -0.0014905 | -0.054454 | -0.0029694 | -0.032114 | 0.0014905 | North | N | 0.0014905 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.025666 | north | -0.0019645 | -0.054928 | -0.0034434 | -0.032588 | 0.0019645 | North | N | 0.0019645 | 0
1878 | WLFHOLW_ | 2 | 205 | -0.025666 | north | -0.0019645 | -0.054928 | -0.0034434 | -0.032588 | 0.0019645 | North | N | 0.0019645 | 0
1879 | WLFHOLW_ | 3 | 272.4 | -0.025666 | north | -0.0019645 | -0.054928 | -0.0034434 | -0.032588 | 0.0019645 | North | N | 0.0019645 | 0
1889 | DECRDOVA | MB | 770 | -0.025939 | north | -0.0022375 | -0.055201 | -0.0037164 | -0.032861 | 0.0022375 | North | N | 0.0022375 | 0
1892 | DECRDOVA | A | 70 | -0.028895 | north | -0.0051935 | -0.058157 | -0.0066724 | -0.035817 | 0.0051935 | North | N | 0.0051935 | 0
1893 | DECRDOVA | B | 69 | -0.028895 | north | -0.0051935 | -0.058157 | -0.0066724 | -0.035817 | 0.0051935 | North | N | 0.0051935 | 0
1894 | DECRDOVA | C | 69 | -0.028895 | north | -0.0051935 | -0.058157 | -0.0066724 | -0.035817 | 0.0051935 | North | N | 0.0051935 | 0
1895 | DECRDOVA | D | 68 | -0.028895 | north | -0.0051935 | -0.058157 | -0.0066724 | -0.035817 | 0.0051935 | North | N | 0.0051935 | 0
1898 | COMCHEPK | 1 | 1157 | -0.025724 | north | -0.0020225 | -0.054986 | -0.0035014 | -0.032646 | 0.0020225 | North | N | 0.0020225 | 0
1899 | COMCHEPK | 2 | 1158 | -0.025724 | north | -0.0020225 | -0.054986 | -0.0035014 | -0.032646 | 0.0020225 | North | N | 0.0020225 | 0
1937 | MDLTHELP | 5 | 224 | -0.025729 | north | -0.0020275 | -0.054991 | -0.0035064 | -0.032651 | 0.0020275 | North | N | 0.0020275 | 0
1938 | MDLTHELP | 6 | 226 | -0.025729 | north | -0.0020275 | -0.054991 | -0.0035064 | -0.032651 | 0.0020275 | North | N | 0.0020275 | 0
1941 | MDLTHELP | 1 | 216.4 | -0.024977 | north | -0.0012755 | -0.054239 | -0.0027544 | -0.031899 | 0.0012755 | North | N | 0.0012755 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.024977 | north | -0.0012755 | -0.054239 | -0.0027544 | -0.031899 | 0.0012755 | North | N | 0.0012755 | 0
1943 | MDLTHELP | 3 | 212 | -0.025729 | north | -0.0020275 | -0.054991 | -0.0035064 | -0.032651 | 0.0020275 | North | N | 0.0020275 | 0
1944 | MDLTHELP | 4 | 211 | -0.025729 | north | -0.0020275 | -0.054991 | -0.0035064 | -0.032651 | 0.0020275 | North | N | 0.0020275 | 0
1947 | HANDLEY_ | 3 | 395 | -0.025271 | north | -0.0015695 | -0.054533 | -0.0030484 | -0.032193 | 0.0015695 | North | N | 0.0015695 | 0
1948 | HANDLEY_ | 4 | 435 | -0.025279 | north | -0.0015775 | -0.054541 | -0.0030564 | -0.032201 | 0.0015775 | North | N | 0.0015775 | 0
1949 | HANDLEY_ | 5 | 435 | -0.025271 | north | -0.0015695 | -0.054533 | -0.0030484 | -0.032193 | 0.0015695 | North | N | 0.0015695 | 0
2371 | COLLIN_1 | MB | 138 | -0.024202 | north | -0.00050052 | -0.053464 | -0.0019794 | -0.031124 | 0.00050052 | North | N | 0.00050052 | 0
2413 | MTCK6_G | 6 | 118 | -0.024314 | north | -0.00061252 | -0.053576 | -0.0020914 | -0.031236 | 0.00061252 | North | N | 0.00061252 | 0
2414 | MTCK7_G | 7 | 115 | -0.024314 | north | -0.00061252 | -0.053576 | -0.0020914 | -0.031236 | 0.00061252 | North | N | 0.00061252 | 0
2417 | MTCK8_G | 8 | 556 | -0.024314 | north | -0.00061252 | -0.053576 | -0.0020914 | -0.031236 | 0.00061252 | North | N | 0.00061252 | 0
2451 | LKHB1_G | 1 | 388 | -0.023842 | north | -0.00014052 | -0.053104 | -0.0016194 | -0.030764 | 0.00014052 | North | N | 0.00014052 | 0
2452 | LKHB2_G | 2 | 515 | -0.023842 | north | -0.00014052 | -0.053104 | -0.0016194 | -0.030764 | 0.00014052 | North | N | 0.00014052 | 0
3097 | MARTLAKE | 1 | 785 | -0.022456 | north | 0.0012455 | -0.051718 | -0.0002334 | -0.029378 | 0.0002334 | west | Y | 0.0012455 | 0.79449
3098 | MARTLAKE | 2 | 795 | -0.022456 | north | 0.0012455 | -0.051718 | -0.0002334 | -0.029378 | 0.0002334 | west | Y | 0.0012455 | 0.80461
3099 | MARTLAKE | 3 | 780 | -0.022456 | north | 0.0012455 | -0.051718 | -0.0002334 | -0.029378 | 0.0002334 | west | Y | 0.0012455 | 0.78943
3107 | STRYKER_ | 1 | 182 | -0.022024 | north | 0.0016775 | -0.051286 | 0.0001986 | -0.028946 | 0.0001986 | west | Y | 0.0016775 | 0.26916
3108 | STRYKER_ | 2 | 484 | -0.022024 | north | 0.0016775 | -0.051286 | 0.0001986 | -0.028946 | 0.0001986 | west | Y | 0.0016775 | 0.71578
3126 | TRINIDAD | 1 | 224 | -0.026427 | north | -0.0027255 | -0.055689 | -0.0042044 | -0.033349 | 0.0027255 | North | N | 0.0027255 | 0
3309 | ASPN_G | 1 | 50 | -0.02209 | north | 0.0016115 | -0.051352 | 0.0001326 | -0.029012 | 0.0001326 | west | Y | 0.0016115 | 0.073944
3348 | CHAMPION | MB | 42 | -0.02211 | north | 0.0015915 | -0.051372 | 0.0001126 | -0.029032 | 0.0001126 | west | Y | 0.0015915 | 0.062113
3381 | BBRN_1G | 1 | 615 | -0.019819 | north | 0.0038825 | -0.049081 | 0.0024036 | -0.026741 | 0.0024036 | west | Y | 0.0038825 | 0.90951
3382 | BBRN_2G | 2 | 587 | -0.019819 | north | 0.0038825 | -0.049081 | 0.0024036 | -0.026741 | 0.0024036 | west | Y | 0.0038825 | 0.8681
3403 | THOUSE_1 | MB | 537 | -0.030835 | north | -0.0071335 | -0.060097 | -0.0086124 | -0.037757 | 0.0071335 | North | N | 0.0071335 | 0
3404 | THOUSE_2 | 2 | 787 | -0.030835 | north | -0.0071335 | -0.060097 | -0.0086124 | -0.037757 | 0.0071335 | North | N | 0.0071335 | 0
3416 | LAKE_CRK | MB | 75 | -0.018636 | north | 0.0050655 | -0.047898 | 0.0035866 | -0.025558 | 0.0035866 | west | Y | 0.0050655 | 0.11092
3417 | LAKE_CRK | MB | 222 | -0.018636 | north | 0.0050655 | -0.047898 | 0.0035866 | -0.025558 | 0.0035866 | west | Y | 0.0050655 | 0.32831
3432 | SANDOW_4 | 4 | 569 | 0.043247 | south | 0.066948 | 0.013985 | 0.06547 | 0.036325 | 0.013985 | south | N | 0.013985 | 0
5026 | BRAUNIG_ | 1 | 209 | 0.027875 | south | 0.051576 | -0.0013875 | 0.050098 | 0.020953 | 0.0013875 | south | N | 0.0013875 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.027875 | south | 0.051576 | -0.0013875 | 0.050098 | 0.020953 | 0.0013875 | south | N | 0.0013875 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.027863 | south | 0.051564 | -0.0013995 | 0.050086 | 0.020941 | 0.0013995 | south | N | 0.0013995 | 0
5031 | BRA_VHBC | 1 | 46 | 0.027875 | south | 0.051576 | -0.0013875 | 0.050098 | 0.020953 | 0.0013875 | south | N | 0.0013875 | 0
5032 | BRA_VHBC | 2 | 47 | 0.027875 | south | 0.051576 | -0.0013875 | 0.050098 | 0.020953 | 0.0013875 | south | N | 0.0013875 | 0
5033 | BRA_VHBC | 3 | 46 | 0.027875 | south | 0.051576 | -0.0013875 | 0.050098 | 0.020953 | 0.0013875 | south | N | 0.0013875 | 0
5034 | BRA_VHBC | 4 | 46 | 0.027875 | south | 0.051576 | -0.0013875 | 0.050098 | 0.020953 | 0.0013875 | south | N | 0.0013875 | 0
5111 | CALAVER_ | 1 | 424 | 0.027927 | south | 0.051628 | -0.0013355 | 0.05015 | 0.021005 | 0.0013355 | south | N | 0.0013355 | 0
5112 | CALAVER_ | 2 | 425 | 0.027927 | south | 0.051628 | -0.0013355 | 0.05015 | 0.021005 | 0.0013355 | south | N | 0.0013355 | 0
5264 | LEON_LCP | 3 | 58 | 0.027708 | south | 0.051409 | -0.0015545 | 0.049931 | 0.020786 | 0.0015545 | south | N | 0.0015545 | 0
5265 | LEON_LCP | 4 | 89 | 0.027708 | south | 0.051409 | -0.0015545 | 0.049931 | 0.020786 | 0.0015545 | south | N | 0.0015545 | 0
5266 | LEON_LCP | 1 | 44 | 0.027708 | south | 0.051409 | -0.0015545 | 0.049931 | 0.020786 | 0.0015545 | south | N | 0.0015545 | 0
5267 | LEON_LCP | 2 | 44 | 0.027708 | south | 0.051409 | -0.0015545 | 0.049931 | 0.020786 | 0.0015545 | south | N | 0.0015545 | 0
5268 | LEON_LCP | 3 | 43 | 0.027708 | south | 0.051409 | -0.0015545 | 0.049931 | 0.020786 | 0.0015545 | south | N | 0.0015545 | 0
5269 | LEON_LCP | 4 | 45 | 0.027708 | south | 0.051409 | -0.0015545 | 0.049931 | 0.020786 | 0.0015545 | south | N | 0.0015545 | 0
5396 | CALAVER_ | 1 | 412 | 0.027906 | south | 0.051607 | -0.0013565 | 0.050129 | 0.020984 | 0.0013565 | south | N | 0.0013565 | 0
5397 | CALAVER_ | 2 | 400 | 0.027906 | south | 0.051607 | -0.0013565 | 0.050129 | 0.020984 | 0.0013565 | south | N | 0.0013565 | 0
5401 | CALAVER_ | 1 | 546 | 0.027669 | south | 0.05137 | -0.0015935 | 0.049892 | 0.020747 | 0.0015935 | south | N | 0.0015935 | 0
5402 | CALAVER_ | 2 | 750 | 0.027669 | south | 0.05137 | -0.0015935 | 0.049892 | 0.020747 | 0.0015935 | south | N | 0.0015935 | 0
5436 | TUTTL_WB | MB | 61 | 0.028002 | south | 0.051703 | -0.0012605 | 0.050225 | 0.02108 | 0.0012605 | south | N | 0.0012605 | 0
5438 | TUTTL_WB | MB | 95 | 0.028002 | south | 0.051703 | -0.0012605 | 0.050225 | 0.02108 | 0.0012605 | south | N | 0.0012605 | 0
5439 | TUTTL_WB | MB | 151 | 0.028002 | south | 0.051703 | -0.0012605 | 0.050225 | 0.02108 | 0.0012605 | south | N | 0.0012605 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.027814 | south | 0.051515 | -0.0014485 | 0.050037 | 0.020892 | 0.0014485 | south | N | 0.0014485 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.027814 | south | 0.051515 | -0.0014485 | 0.050037 | 0.020892 | 0.0014485 | south | N | 0.0014485 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.027814 | south | 0.051515 | -0.0014485 | 0.050037 | 0.020892 | 0.0014485 | south | N | 0.0014485 | 0
5503 | RAYBURNG | 1 | 22 | 0.022491 | south | 0.046192 | -0.0067715 | 0.044714 | 0.015569 | 0.0067715 | south | N | 0.0067715 | 0
5505 | RAYBURNG | 1 | 11 | 0.022491 | south | 0.046192 | -0.0067715 | 0.044714 | 0.015569 | 0.0067715 | south | N | 0.0067715 | 0
5506 | RAYBURNG | 1 | 11 | 0.022491 | south | 0.046192 | -0.0067715 | 0.044714 | 0.015569 | 0.0067715 | south | N | 0.0067715 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.022697 | south | 0.046398 | -0.0065655 | 0.04492 | 0.015775 | 0.0065655 | south | N | 0.0065655 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.022697 | south | 0.046398 | -0.0065655 | 0.04492 | 0.015775 | 0.0065655 | south | N | 0.0065655 | 0
5511 | RAYBURNC | 1 | 46 | 0.022697 | south | 0.046398 | -0.0065655 | 0.04492 | 0.015775 | 0.0065655 | south | N | 0.0065655 | 0
5512 | RAYBURNC | 1 | 48 | 0.022697 | south | 0.046398 | -0.0065655 | 0.04492 | 0.015775 | 0.0065655 | south | N | 0.0065655 | 0
5728 | FALCONHY | 2 | 12 | 0.023642 | south | 0.047343 | -0.0056205 | 0.045865 | 0.01672 | 0.0056205 | south | N | 0.0056205 | 0
5729 | FALCONHY | 3 | 11 | 0.023642 | south | 0.047343 | -0.0056205 | 0.045865 | 0.01672 | 0.0056205 | south | N | 0.0056205 | 0
5890 | PEARSALL | 1 | 24 | 0.024575 | south | 0.048276 | -0.0046875 | 0.046798 | 0.017653 | 0.0046875 | south | N | 0.0046875 | 0
5891 | PEARSALL | 1 | 24 | 0.024575 | south | 0.048276 | -0.0046875 | 0.046798 | 0.017653 | 0.0046875 | south | N | 0.0046875 | 0
5892 | PEARSALL | 1 | 23 | 0.024575 | south | 0.048276 | -0.0046875 | 0.046798 | 0.017653 | 0.0046875 | south | N | 0.0046875 | 0
5903 | SANMIGUE | 1 | 396 | 0.026167 | south | 0.049868 | -0.0030955 | 0.04839 | 0.019245 | 0.0030955 | south | N | 0.0030955 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.014699 | houston | 0.0384 | -0.014563 | 0.036922 | 0.0077773 | 0.0077773 | houston | N | 0.0077773 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.014699 | houston | 0.0384 | -0.014563 | 0.036922 | 0.0077773 | 0.0077773 | houston | N | 0.0077773 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | 0.023701 | -0.029262 | 0.022223 | -0.0069217 | 0.0069217 | houston | Y | 0.023701 | 10.0679
5932 | SI_RAY9 | 9 | 38 | 0.023313 | south | 0.047014 | -0.0059495 | 0.045536 | 0.016391 | 0.0059495 | south | N | 0.0059495 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.023313 | south | 0.047014 | -0.0059495 | 0.045536 | 0.016391 | 0.0059495 | south | N | 0.0059495 | 0
5934 | SI_RAY5 | 5 | 15 | 0.023313 | south | 0.047014 | -0.0059495 | 0.045536 | 0.016391 | 0.0059495 | south | N | 0.0059495 | 0
5935 | SI_RAY10 | 10 | 47 | 0.023313 | south | 0.047014 | -0.0059495 | 0.045536 | 0.016391 | 0.0059495 | south | N | 0.0059495 | 0
6016 | SWMESA | 1 | 75 | -0.019788 | west | 0.0039135 | -0.04905 | 0.0024346 | -0.02671 | 0.0024346 | west | N | 0.0024346 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | 0.023701 | -0.029262 | 0.022223 | -0.0069217 | 0.0069217 | houston | Y | 0.022223 | 3.3662
6144 | MCADOO1A | 1 | 150 | -0.023071 | west | 0.00063048 | -0.052333 | -0.0008484 | -0.029993 | 0.00063048 | North | Y | 0.0008484 | 0.032687
6407 | TURKTRAK | 1 | 169.5 | -0.021865 | west | 0.0018365 | -0.051127 | 0.0003576 | -0.028787 | 0.0003576 | west | N | 0.0003576 | 0
6476 | LANGFORD | 1 | 150 | -0.01085 | west | 0.012851 | -0.040112 | 0.011373 | -0.017772 | 0.011373 | west | N | 0.011373 | 0
6637 | SNYDERW1 | 1 | 63 | -0.022664 | west | 0.0010375 | -0.051926 | -0.0004414 | -0.029586 | 0.0004414 | west | N | 0.0004414 | 0
6752 | OKLA0A | 1 | 649.7 | -0.02396 | west | -0.00025852 | -0.053222 | -0.0017374 | -0.030882 | 0.00025852 | North | Y | 0.0017374 | 0.96083
6948 | DENISNDM | 1 | 40 | -0.024085 | north | -0.00038352 | -0.053347 | -0.0018624 | -0.031007 | 0.00038352 | North | N | 0.00038352 | 0
6948 | DENISNDM | 2 | 40 | -0.024085 | north | -0.00038352 | -0.053347 | -0.0018624 | -0.031007 | 0.00038352 | North | N | 0.00038352 | 0
7000 | L_FERGUS | 1 | 422 | 0.033781 | south | 0.057482 | 0.0045185 | 0.056004 | 0.026859 | 0.0045185 | south | N | 0.0045185 | 0
7004 | L_SIMGID | 1 | 132 | 0.035173 | south | 0.058874 | 0.0059105 | 0.057396 | 0.028251 | 0.0059105 | south | N | 0.0059105 | 0
7005 | L_SIMGID | 2 | 134 | 0.035173 | south | 0.058874 | 0.0059105 | 0.057396 | 0.028251 | 0.0059105 | south | N | 0.0059105 | 0
7006 | L_SIMGID | 3 | 323 | 0.035173 | south | 0.058874 | 0.0059105 | 0.057396 | 0.028251 | 0.0059105 | south | N | 0.0059105 | 0
7007 | L_LOSTPI | 1 | 158 | 0.0348 | south | 0.058501 | 0.0055375 | 0.057023 | 0.027878 | 0.0055375 | south | N | 0.0055375 | 0
7008 | L_LOSTPI | 2 | 160 | 0.0348 | south | 0.058501 | 0.0055375 | 0.057023 | 0.027878 | 0.0055375 | south | N | 0.0055375 | 0
7009 | L_LOSTPI | 3 | 175 | 0.0348 | south | 0.058501 | 0.0055375 | 0.057023 | 0.027878 | 0.0055375 | south | N | 0.0055375 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.031196 | south | 0.054897 | 0.0019335 | 0.053419 | 0.024274 | 0.0019335 | south | N | 0.0019335 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.031196 | south | 0.054897 | 0.0019335 | 0.053419 | 0.024274 | 0.0019335 | south | N | 0.0019335 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.031167 | south | 0.054868 | 0.0019045 | 0.05339 | 0.024245 | 0.0019045 | south | N | 0.0019045 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.03066 | south | 0.054361 | 0.0013975 | 0.052883 | 0.023738 | 0.0013975 | south | N | 0.0013975 | 0
7015 | L_HAYSEN | 2 | 225 | 0.03066 | south | 0.054361 | 0.0013975 | 0.052883 | 0.023738 | 0.0013975 | south | N | 0.0013975 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.03066 | south | 0.054361 | 0.0013975 | 0.052883 | 0.023738 | 0.0013975 | south | N | 0.0013975 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.03066 | south | 0.054361 | 0.0013975 | 0.052883 | 0.023738 | 0.0013975 | south | N | 0.0013975 | 0
7020 | L_AUSTPL | 1 | 8 | 0.037053 | south | 0.060754 | 0.0077905 | 0.059276 | 0.030131 | 0.0077905 | south | N | 0.0077905 | 0
7020 | L_AUSTPL | 2 | 8 | 0.037053 | south | 0.060754 | 0.0077905 | 0.059276 | 0.030131 | 0.0077905 | south | N | 0.0077905 | 0
7022 | L_BUCHAN | 1 | 18 | 0.034939 | south | 0.05864 | 0.0056765 | 0.057162 | 0.028017 | 0.0056765 | south | N | 0.0056765 | 0
7023 | L_BUCHAN | 2 | 18 | 0.034939 | south | 0.05864 | 0.0056765 | 0.057162 | 0.028017 | 0.0056765 | south | N | 0.0056765 | 0
7024 | L_BUCHAN | 3 | 15 | 0.034939 | south | 0.05864 | 0.0056765 | 0.057162 | 0.028017 | 0.0056765 | south | N | 0.0056765 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.033884 | south | 0.057585 | 0.0046215 | 0.056107 | 0.026962 | 0.0046215 | south | N | 0.0046215 | 0
7028 | L_MARBFA | 1 | 18 | 0.034605 | south | 0.058306 | 0.0053425 | 0.056828 | 0.027683 | 0.0053425 | south | N | 0.0053425 | 0
7029 | L_MARBFA | 2 | 18 | 0.034605 | south | 0.058306 | 0.0053425 | 0.056828 | 0.027683 | 0.0053425 | south | N | 0.0053425 | 0
7031 | L_MARSFO | 1 | 35 | 0.036472 | south | 0.060173 | 0.0072095 | 0.058695 | 0.02955 | 0.0072095 | south | N | 0.0072095 | 0
7032 | L_MARSFO | 2 | 34 | 0.036472 | south | 0.060173 | 0.0072095 | 0.058695 | 0.02955 | 0.0072095 | south | N | 0.0072095 | 0
7033 | L_MARSFO | 3 | 35 | 0.036472 | south | 0.060173 | 0.0072095 | 0.058695 | 0.02955 | 0.0072095 | south | N | 0.0072095 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.034072 | south | 0.057773 | 0.0048095 | 0.056295 | 0.02715 | 0.0048095 | south | N | 0.0048095 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.034072 | south | 0.057773 | 0.0048095 | 0.056295 | 0.02715 | 0.0048095 | south | N | 0.0048095 | 0
7038 | L_DELAWA | 1 | 35 | -0.021875 | west | 0.0018265 | -0.051137 | 0.0003476 | -0.028797 | 0.0003476 | west | N | 0.0003476 | 0
7038 | L_DELAWA | 2 | 30 | -0.021875 | west | 0.0018265 | -0.051137 | 0.0003476 | -0.028797 | 0.0003476 | west | N | 0.0003476 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.031843 | south | 0.055544 | 0.0025805 | 0.054066 | 0.024921 | 0.0025805 | south | N | 0.0025805 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.031843 | south | 0.055544 | 0.0025805 | 0.054066 | 0.024921 | 0.0025805 | south | N | 0.0025805 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.031843 | south | 0.055544 | 0.0025805 | 0.054066 | 0.024921 | 0.0025805 | south | N | 0.0025805 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.031843 | south | 0.055544 | 0.0025805 | 0.054066 | 0.024921 | 0.0025805 | south | N | 0.0025805 | 0
7487 | L_CANYHY | 1 | 6 | 0.031695 | south | 0.055396 | 0.0024325 | 0.053918 | 0.024773 | 0.0024325 | south | N | 0.0024325 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.0298 | south | 0.053501 | 0.00053754 | 0.052023 | 0.022878 | 0.00053754 | south | N | 0.00053754 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.0298 | south | 0.053501 | 0.00053754 | 0.052023 | 0.022878 | 0.00053754 | south | N | 0.00053754 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.0298 | south | 0.053501 | 0.00053754 | 0.052023 | 0.022878 | 0.00053754 | south | N | 0.00053754 | 0
7609 | L_SCHUMA | 1 | 4 | 0.029354 | south | 0.053055 | 9.1541e-05 | 0.051577 | 0.022432 | 9.1541e-05 | south | N | 9.1541e-05 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.029423 | south | 0.053124 | 0.00016054 | 0.051646 | 0.022501 | 0.00016054 | south | N | 0.00016054 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.029423 | south | 0.053124 | 0.00016054 | 0.051646 | 0.022501 | 0.00016054 | south | N | 0.00016054 | 0
7800 | L_GUADGE | 1 | 147 | 0.028584 | south | 0.052285 | -0.00067846 | 0.050807 | 0.021662 | 0.00067846 | south | N | 0.00067846 | 0
7801 | L_GUADGE | 2 | 138 | 0.028584 | south | 0.052285 | -0.00067846 | 0.050807 | 0.021662 | 0.00067846 | south | N | 0.00067846 | 0
7802 | L_GUADGE | 3 | 140 | 0.028584 | south | 0.052285 | -0.00067846 | 0.050807 | 0.021662 | 0.00067846 | south | N | 0.00067846 | 0
7803 | L_GUADGE | 4 | 147 | 0.028584 | south | 0.052285 | -0.00067846 | 0.050807 | 0.021662 | 0.00067846 | south | N | 0.00067846 | 0
7804 | L_GUADGE | 5 | 182 | 0.028584 | south | 0.052285 | -0.00067846 | 0.050807 | 0.021662 | 0.00067846 | south | N | 0.00067846 | 0
7805 | L_GUADGE | 6 | 198 | 0.028584 | south | 0.052285 | -0.00067846 | 0.050807 | 0.021662 | 0.00067846 | south | N | 0.00067846 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.03518 | south | 0.058881 | 0.0059175 | 0.057403 | 0.028258 | 0.0059175 | south | N | 0.0059175 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.03518 | south | 0.058881 | 0.0059175 | 0.057403 | 0.028258 | 0.0059175 | south | N | 0.0059175 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.03518 | south | 0.058881 | 0.0059175 | 0.057403 | 0.028258 | 0.0059175 | south | N | 0.0059175 | 0
7810 | L_RIONOG | 1 | 142 | 0.029597 | south | 0.053298 | 0.00033454 | 0.05182 | 0.022675 | 0.00033454 | south | N | 0.00033454 | 0
7811 | L_RIONOG | 2 | 145 | 0.029597 | south | 0.053298 | 0.00033454 | 0.05182 | 0.022675 | 0.00033454 | south | N | 0.00033454 | 0
7812 | L_RIONOG | 3 | 151 | 0.029597 | south | 0.053298 | 0.00033454 | 0.05182 | 0.022675 | 0.00033454 | south | N | 0.00033454 | 0
7813 | L_RIONOG | 4 | 290 | 0.029597 | south | 0.053298 | 0.00033454 | 0.05182 | 0.022675 | 0.00033454 | south | N | 0.00033454 | 0
8032 | AMISTADH | 1 | 33 | 0.012504 | south | 0.036205 | -0.016758 | 0.034727 | 0.0055823 | 0.0055823 | houston | Y | 0.016758 | 0.36881
8033 | AMISTADH | 2 | 25 | 0.012504 | south | 0.036205 | -0.016758 | 0.034727 | 0.0055823 | 0.0055823 | houston | Y | 0.016758 | 0.2794
8048 | FALCONHY | 1 | 12 | 0.023642 | south | 0.047343 | -0.0056205 | 0.045865 | 0.01672 | 0.0056205 | south | N | 0.0056205 | 0
8066 | DUP1V#1 | 1 | 73 | 0.022749 | south | 0.04645 | -0.0065135 | 0.044972 | 0.015827 | 0.0065135 | south | N | 0.0065135 | 0
8134 | FOR69CG0 | 1 | 79 | 0.021288 | south | 0.044989 | -0.0079745 | 0.043511 | 0.014366 | 0.0079745 | south | N | 0.0079745 | 0
8138 | FOR69CG0 | 2 | 81 | 0.021288 | south | 0.044989 | -0.0079745 | 0.043511 | 0.014366 | 0.0079745 | south | N | 0.0079745 | 0
8139 | JOS #1 | MB | 255 | 0 | south | 0.023701 | -0.029262 | 0.022223 | -0.0069217 | 0.0069217 | houston | Y | 0.029262 | 5.6969
8147 | UCAR #2 | 10 | 28 | 0.022061 | south | 0.045762 | -0.0072015 | 0.044284 | 0.015139 | 0.0072015 | south | N | 0.0072015 | 0
8148 | UCAR #1 | 2 | 7 | 0.022061 | south | 0.045762 | -0.0072015 | 0.044284 | 0.015139 | 0.0072015 | south | N | 0.0072015 | 0
8153 | FOR69CG0 | 3 | 79 | 0.021288 | south | 0.044989 | -0.0079745 | 0.043511 | 0.014366 | 0.0079745 | south | N | 0.0079745 | 0
8154 | FOR69CG0 | 4 | 80 | 0.021288 | south | 0.044989 | -0.0079745 | 0.043511 | 0.014366 | 0.0079745 | south | N | 0.0079745 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.021288 | south | 0.044989 | -0.0079745 | 0.043511 | 0.014366 | 0.0079745 | south | N | 0.0079745 | 0
8156 | FOR69CG0 | 6 | 25 | 0.021288 | south | 0.044989 | -0.0079745 | 0.043511 | 0.014366 | 0.0079745 | south | N | 0.0079745 | 0
8157 | FOR69CG0 | 7 | 46 | 0.021288 | south | 0.044989 | -0.0079745 | 0.043511 | 0.014366 | 0.0079745 | south | N | 0.0079745 | 0
8161 | COLETOU1 | 1 | 629 | 0.024059 | south | 0.04776 | -0.0052035 | 0.046282 | 0.017137 | 0.0052035 | south | N | 0.0052035 | 0
8173 | VICEC51A | 5 | 144 | 0.022999 | south | 0.0467 | -0.0062635 | 0.045222 | 0.016077 | 0.0062635 | south | N | 0.0062635 | 0
8174 | VICEC61A | 6 | 188 | 0.022999 | south | 0.0467 | -0.0062635 | 0.045222 | 0.016077 | 0.0062635 | south | N | 0.0062635 | 0
8189 | CUERO 2 | 1 | 12 | 0.02765 | south | 0.051351 | -0.0016125 | 0.049873 | 0.020728 | 0.0016125 | south | N | 0.0016125 | 0
8262 | ELPS | 1 | 6 | 0.016264 | south | 0.039965 | -0.012998 | 0.038487 | 0.0093423 | 0.0093423 | houston | Y | 0.012998 | 0.021937
8285 | LAR #1 | MB | 32 | 0 | south | 0.023701 | -0.029262 | 0.022223 | -0.0069217 | 0.0069217 | houston | Y | 0.029262 | 0.71491
8287 | LAR #2 | MB | 32 | 0 | south | 0.023701 | -0.029262 | 0.022223 | -0.0069217 | 0.0069217 | houston | Y | 0.029262 | 0.71491
8288 | LAR #3 | MB | 105 | 0 | south | 0.023701 | -0.029262 | 0.022223 | -0.0069217 | 0.0069217 | houston | Y | 0.029262 | 2.3458
8388 | BATES0A | MB | 70 | 0 | south | 0.023701 | -0.029262 | 0.022223 | -0.0069217 | 0.0069217 | houston | Y | 0.029262 | 1.5639
8393 | BATES0B | MB | 110 | 0 | south | 0.023701 | -0.029262 | 0.022223 | -0.0069217 | 0.0069217 | houston | Y | 0.029262 | 2.4575
8442 | NBEC71A | 1 | 336 | 0.023074 | south | 0.046775 | -0.0061885 | 0.045297 | 0.016152 | 0.0061885 | south | N | 0.0061885 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | 0.023701 | -0.029262 | 0.022223 | -0.0069217 | 0.0069217 | houston | Y | 0.029262 | 0.44682
8457 | COSW#2 | 2 | 14 | 0 | south | 0.023701 | -0.029262 | 0.022223 | -0.0069217 | 0.0069217 | houston | Y | 0.029262 | 0.31277
8459 | B_DAVIS1 | 1 | 334 | 0.023126 | south | 0.046827 | -0.0061365 | 0.045349 | 0.016204 | 0.0061365 | south | N | 0.0061365 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.023126 | south | 0.046827 | -0.0061365 | 0.045349 | 0.016204 | 0.0061365 | south | N | 0.0061365 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.023157 | south | 0.046858 | -0.0061055 | 0.04538 | 0.016235 | 0.0061055 | south | N | 0.0061055 | 0
8506 | VAL #1 | 1 | 25 | 0.023134 | south | 0.046835 | -0.0061285 | 0.045357 | 0.016212 | 0.0061285 | south | N | 0.0061285 | 0
8507 | VAL #2 | 2 | 25 | 0.023134 | south | 0.046835 | -0.0061285 | 0.045357 | 0.016212 | 0.0061285 | south | N | 0.0061285 | 0
8511 | OXY_CC0A | 1 | 38 | 0.023156 | south | 0.046857 | -0.0061065 | 0.045379 | 0.016234 | 0.0061065 | south | N | 0.0061065 | 0
8517 | CELANEBI | 1 | 29 | 0.023264 | south | 0.046965 | -0.0059985 | 0.045487 | 0.016342 | 0.0059985 | south | N | 0.0059985 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.023077 | south | 0.046778 | -0.0061855 | 0.0453 | 0.016155 | 0.0061855 | south | N | 0.0061855 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.023077 | south | 0.046778 | -0.0061855 | 0.0453 | 0.016155 | 0.0061855 | south | N | 0.0061855 | 0
8562 | CNOPST1 | 3 | 153 | 0.023077 | south | 0.046778 | -0.0061855 | 0.0453 | 0.016155 | 0.0061855 | south | N | 0.0061855 | 0
8926 | LGE_GT10 | 1 | 158 | 0.022843 | south | 0.046544 | -0.0064195 | 0.045066 | 0.015921 | 0.0064195 | south | N | 0.0064195 | 0
8927 | LGE_GT20 | 2 | 153 | 0.022843 | south | 0.046544 | -0.0064195 | 0.045066 | 0.015921 | 0.0064195 | south | N | 0.0064195 | 0
8928 | LGE_STG0 | 3 | 100 | 0.022843 | south | 0.046544 | -0.0064195 | 0.045066 | 0.015921 | 0.0064195 | south | N | 0.0064195 | 0
8930 | ICPGN10A | 1 | 145 | 0.022843 | south | 0.046544 | -0.0064195 | 0.045066 | 0.015921 | 0.0064195 | south | N | 0.0064195 | 0
8931 | ICPGN20A | 2 | 147 | 0.022843 | south | 0.046544 | -0.0064195 | 0.045066 | 0.015921 | 0.0064195 | south | N | 0.0064195 | 0
8932 | ICPGN30A | 3 | 127 | 0.022843 | south | 0.046544 | -0.0064195 | 0.045066 | 0.015921 | 0.0064195 | south | N | 0.0064195 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.023394 | south | 0.047095 | -0.0058685 | 0.045617 | 0.016472 | 0.0058685 | south | N | 0.0058685 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.023394 | south | 0.047095 | -0.0058685 | 0.045617 | 0.016472 | 0.0058685 | south | N | 0.0058685 | 0
8935 | FGNTS201 | 3 | 173 | 0.023394 | south | 0.047095 | -0.0058685 | 0.045617 | 0.016472 | 0.0058685 | south | N | 0.0058685 | 0
8936 | MVGN#1 | 1 | 207 | 0.023354 | south | 0.047055 | -0.0059085 | 0.045577 | 0.016432 | 0.0059085 | south | N | 0.0059085 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.023354 | south | 0.047055 | -0.0059085 | 0.045577 | 0.016432 | 0.0059085 | south | N | 0.0059085 | 0
8938 | MVGN#3 | 3 | 242 | 0.023354 | south | 0.047055 | -0.0059085 | 0.045577 | 0.016432 | 0.0059085 | south | N | 0.0059085 | 0
8981 | HECN1 | 1 | 144 | 0.023353 | south | 0.047054 | -0.0059095 | 0.045576 | 0.016431 | 0.0059095 | south | N | 0.0059095 | 0
8982 | HECN2 | 2 | 144 | 0.023353 | south | 0.047054 | -0.0059095 | 0.045576 | 0.016431 | 0.0059095 | south | N | 0.0059095 | 0
8983 | HECN3 | 3 | 171 | 0.023353 | south | 0.047054 | -0.0059095 | 0.045576 | 0.016431 | 0.0059095 | south | N | 0.0059095 | 0
9000 | DECKR_G1 | 1 | 310 | 0.037078 | south | 0.060779 | 0.0078155 | 0.059301 | 0.030156 | 0.0078155 | south | N | 0.0078155 | 0
9001 | DECKR_G2 | 2 | 413 | 0.037078 | south | 0.060779 | 0.0078155 | 0.059301 | 0.030156 | 0.0078155 | south | N | 0.0078155 | 0
9002 | DECKR_G3 | 3 | 42 | 0.037419 | south | 0.06112 | 0.0081565 | 0.059642 | 0.030497 | 0.0081565 | south | N | 0.0081565 | 0
9003 | DECKR_G4 | 4 | 44 | 0.037419 | south | 0.06112 | 0.0081565 | 0.059642 | 0.030497 | 0.0081565 | south | N | 0.0081565 | 0
9004 | DECKR_G5 | 5 | 44 | 0.037419 | south | 0.06112 | 0.0081565 | 0.059642 | 0.030497 | 0.0081565 | south | N | 0.0081565 | 0
9005 | DECKR_G6 | 6 | 47 | 0.037419 | south | 0.06112 | 0.0081565 | 0.059642 | 0.030497 | 0.0081565 | south | N | 0.0081565 | 0
9016 | SANDH_G1 | 1 | 49 | 0.036579 | south | 0.06028 | 0.0073165 | 0.058802 | 0.029657 | 0.0073165 | south | N | 0.0073165 | 0
9017 | SANDH_G2 | 2 | 46 | 0.036579 | south | 0.06028 | 0.0073165 | 0.058802 | 0.029657 | 0.0073165 | south | N | 0.0073165 | 0
9018 | SANDH_G3 | 3 | 46 | 0.036579 | south | 0.06028 | 0.0073165 | 0.058802 | 0.029657 | 0.0073165 | south | N | 0.0073165 | 0
9019 | SANDH_G4 | 4 | 47 | 0.036579 | south | 0.06028 | 0.0073165 | 0.058802 | 0.029657 | 0.0073165 | south | N | 0.0073165 | 0
9020 | SANDHG5A | 5A | 154 | 0.036579 | south | 0.06028 | 0.0073165 | 0.058802 | 0.029657 | 0.0073165 | south | N | 0.0073165 | 0
9021 | SANDHG5C | 5C | 148 | 0.036579 | south | 0.06028 | 0.0073165 | 0.058802 | 0.029657 | 0.0073165 | south | N | 0.0073165 | 0
9022 | SANDH_G6 | 6 | 48 | 0.036579 | south | 0.06028 | 0.0073165 | 0.058802 | 0.029657 | 0.0073165 | south | N | 0.0073165 | 0
9023 | SANDH_G7 | 7 | 48 | 0.036579 | south | 0.06028 | 0.0073165 | 0.058802 | 0.029657 | 0.0073165 | south | N | 0.0073165 | 0
11001 | NAV1CT | 1 | 70 | -0.022224 | west | 0.0014775 | -0.051486 | -1.3959e-06 | -0.029146 | 1.3959e-06 | west | N | 1.3959e-06 | 0
11009 | NAV2CT | 1 | 70 | -0.022224 | west | 0.0014775 | -0.051486 | -1.3959e-06 | -0.029146 | 1.3959e-06 | west | N | 1.3959e-06 | 0
11011 | NAV3ST | 1 | 92.8 | -0.022224 | west | 0.0014775 | -0.051486 | -1.3959e-06 | -0.029146 | 1.3959e-06 | west | N | 1.3959e-06 | 0
11012 | NAV4CT | 1 | 80 | -0.022224 | west | 0.0014775 | -0.051486 | -1.3959e-06 | -0.029146 | 1.3959e-06 | west | N | 1.3959e-06 | 0
11013 | NAV5CT | 1 | 80 | -0.022224 | west | 0.0014775 | -0.051486 | -1.3959e-06 | -0.029146 | 1.3959e-06 | west | N | 1.3959e-06 | 0
11014 | NAV6ST | 1 | 115 | -0.022224 | west | 0.0014775 | -0.051486 | -1.3959e-06 | -0.029146 | 1.3959e-06 | west | N | 1.3959e-06 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.02222 | west | 0.0014815 | -0.051482 | 2.6041e-06 | -0.029142 | 2.6041e-06 | west | N | 2.6041e-06 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.02222 | west | 0.0014815 | -0.051482 | 2.6041e-06 | -0.029142 | 2.6041e-06 | west | N | 2.6041e-06 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.02222 | west | 0.0014815 | -0.051482 | 2.6041e-06 | -0.029142 | 2.6041e-06 | west | N | 2.6041e-06 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.02222 | west | 0.0014815 | -0.051482 | 2.6041e-06 | -0.029142 | 2.6041e-06 | west | N | 2.6041e-06 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.02222 | west | 0.0014815 | -0.051482 | 2.6041e-06 | -0.029142 | 2.6041e-06 | west | N | 2.6041e-06 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.02222 | west | 0.0014815 | -0.051482 | 2.6041e-06 | -0.029142 | 2.6041e-06 | west | N | 2.6041e-06 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.022862 | west | 0.00083948 | -0.052124 | -0.0006394 | -0.029784 | 0.0006394 | west | N | 0.0006394 | 0
11057 | CHAMPION | 1 | 126.5 | -0.022862 | west | 0.00083948 | -0.052124 | -0.0006394 | -0.029784 | 0.0006394 | west | N | 0.0006394 | 0
11058 | PYRON_1G | 1 | 249 | -0.022862 | west | 0.00083948 | -0.052124 | -0.0006394 | -0.029784 | 0.0006394 | west | N | 0.0006394 | 0
11059 | INADALE_ | 1 | 197 | -0.022862 | west | 0.00083948 | -0.052124 | -0.0006394 | -0.029784 | 0.0006394 | west | N | 0.0006394 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.022544 | west | 0.0011575 | -0.051806 | -0.0003214 | -0.029466 | 0.0003214 | west | N | 0.0003214 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.022544 | west | 0.0011575 | -0.051806 | -0.0003214 | -0.029466 | 0.0003214 | west | N | 0.0003214 | 0
11147 | NOTREES_ | 1 | 149 | -0.021941 | west | 0.0017605 | -0.051203 | 0.0002816 | -0.028863 | 0.0002816 | west | N | 0.0002816 | 0
11309 | BULLCREK | 1 | 180 | -0.022529 | west | 0.0011725 | -0.051791 | -0.0003064 | -0.029451 | 0.0003064 | west | N | 0.0003064 | 0
11310 | BULLCREK | 1 | 180 | -0.022529 | west | 0.0011725 | -0.051791 | -0.0003064 | -0.029451 | 0.0003064 | west | N | 0.0003064 | 0
11320 | COYOTE_1 | 1 | 225 | -0.022509 | west | 0.0011925 | -0.051771 | -0.0002864 | -0.029431 | 0.0002864 | west | N | 0.0002864 | 0
11415 | LORAINE_ | 1 | 125 | -0.022736 | west | 0.00096548 | -0.051998 | -0.0005134 | -0.029658 | 0.0005134 | west | N | 0.0005134 | 0
11416 | LORAINE_ | 1 | 125 | -0.022736 | west | 0.00096548 | -0.051998 | -0.0005134 | -0.029658 | 0.0005134 | west | N | 0.0005134 | 0
11691 | KMICHICT | 1 | 140 | -0.023972 | north | -0.00027052 | -0.053234 | -0.0017494 | -0.030894 | 0.00027052 | North | N | 0.00027052 | 0
11692 | KMICHICT | 2 | 141 | -0.023972 | north | -0.00027052 | -0.053234 | -0.0017494 | -0.030894 | 0.00027052 | North | N | 0.00027052 | 0
11693 | KMICHIST | 3 | 309 | -0.023972 | north | -0.00027052 | -0.053234 | -0.0017494 | -0.030894 | 0.00027052 | North | N | 0.00027052 | 0
11694 | KMICHICT | 4 | 143 | -0.023972 | north | -0.00027052 | -0.053234 | -0.0017494 | -0.030894 | 0.00027052 | North | N | 0.00027052 | 0
11695 | KMICHICT | 5 | 144 | -0.023972 | north | -0.00027052 | -0.053234 | -0.0017494 | -0.030894 | 0.00027052 | North | N | 0.00027052 | 0
11696 | KMICHIST | 6 | 310 | -0.023972 | north | -0.00027052 | -0.053234 | -0.0017494 | -0.030894 | 0.00027052 | North | N | 0.00027052 | 0
12322 | ENNSTRAC | 1 | 196 | -0.027019 | north | -0.0033175 | -0.056281 | -0.0047964 | -0.033941 | 0.0033175 | North | N | 0.0033175 | 0
12323 | ENNSTRAC | 2 | 111 | -0.027019 | north | -0.0033175 | -0.056281 | -0.0047964 | -0.033941 | 0.0033175 | North | N | 0.0033175 | 0
12357 | RNRTPL_1 | 1 | 0 | -0.024155 | north | -0.00045352 | -0.053417 | -0.0019324 | -0.031077 | 0.00045352 | North | N | 0.00045352 | 0
12411 | FPLEFR1A | 1 | 161 | -0.02359 | north | 0.00011148 | -0.052852 | -0.0013674 | -0.030512 | 0.00011148 | North | N | 0.00011148 | 0
12412 | FPLEFR1B | 2 | 164 | -0.02359 | north | 0.00011148 | -0.052852 | -0.0013674 | -0.030512 | 0.00011148 | North | N | 0.00011148 | 0
12413 | FPLEFR1C | 3 | 164 | -0.02359 | north | 0.00011148 | -0.052852 | -0.0013674 | -0.030512 | 0.00011148 | North | N | 0.00011148 | 0
12414 | FPLEFR1S | 4 | 414 | -0.02359 | north | 0.00011148 | -0.052852 | -0.0013674 | -0.030512 | 0.00011148 | North | N | 0.00011148 | 0
12421 | FPLEFR2A | 1 | 162 | -0.02359 | north | 0.00011148 | -0.052852 | -0.0013674 | -0.030512 | 0.00011148 | North | N | 0.00011148 | 0
12422 | FPLEFR2B | 2 | 161 | -0.02359 | north | 0.00011148 | -0.052852 | -0.0013674 | -0.030512 | 0.00011148 | North | N | 0.00011148 | 0
12423 | FPLEFR2C | 3 | 163 | -0.02359 | north | 0.00011148 | -0.052852 | -0.0013674 | -0.030512 | 0.00011148 | North | N | 0.00011148 | 0
12424 | FPLEFR2S | 4 | 409 | -0.02359 | north | 0.00011148 | -0.052852 | -0.0013674 | -0.030512 | 0.00011148 | North | N | 0.00011148 | 0
12440 | PARKD_1S | 1 | 0 | -0.023911 | north | -0.00020952 | -0.053173 | -0.0016884 | -0.030833 | 0.00020952 | North | N | 0.00020952 | 0
12449 | PARKD_2S | 1 | 0 | -0.023911 | north | -0.00020952 | -0.053173 | -0.0016884 | -0.030833 | 0.00020952 | North | N | 0.00020952 | 0
13116 | TGATEWAY | 1 | 148 | -0.022301 | north | 0.0014005 | -0.051563 | -7.8396e-05 | -0.029223 | 7.8396e-05 | west | Y | 0.0014005 | 0.19567
13117 | TGATEWAY | 2 | 130 | -0.022301 | north | 0.0014005 | -0.051563 | -7.8396e-05 | -0.029223 | 7.8396e-05 | west | Y | 0.0014005 | 0.17187
13118 | TGATEWAY | 3 | 145 | -0.022301 | north | 0.0014005 | -0.051563 | -7.8396e-05 | -0.029223 | 7.8396e-05 | west | Y | 0.0014005 | 0.1917
13119 | TGATEWAY | 4 | 399 | -0.022301 | north | 0.0014005 | -0.051563 | -7.8396e-05 | -0.029223 | 7.8396e-05 | west | Y | 0.0014005 | 0.52751
13131 | CALFREST | 1 | 150.7 | -0.02023 | north | 0.0034715 | -0.049492 | 0.0019926 | -0.027152 | 0.0019926 | west | Y | 0.0034715 | 0.22287
13132 | CALFREST | 2 | 151 | -0.02023 | north | 0.0034715 | -0.049492 | 0.0019926 | -0.027152 | 0.0019926 | west | Y | 0.0034715 | 0.22331
13133 | CALFREST | 3 | 177.4 | -0.02023 | north | 0.0034715 | -0.049492 | 0.0019926 | -0.027152 | 0.0019926 | west | Y | 0.0034715 | 0.26235
13134 | CALFREST | 4 | 151.5 | -0.020359 | north | 0.0033425 | -0.049621 | 0.0018636 | -0.027281 | 0.0018636 | west | Y | 0.0033425 | 0.22405
13135 | CALFREST | 5 | 152.3 | -0.020359 | north | 0.0033425 | -0.049621 | 0.0018636 | -0.027281 | 0.0018636 | west | Y | 0.0033425 | 0.22523
13136 | CALFREST | 6 | 177.5 | -0.020359 | north | 0.0033425 | -0.049621 | 0.0018636 | -0.027281 | 0.0018636 | west | Y | 0.0033425 | 0.2625
13432 | SANDOW_5 | 5 | 581 | 0.043247 | south | 0.066948 | 0.013985 | 0.06547 | 0.036325 | 0.013985 | south | N | 0.013985 | 0
13691 | OAKGROVE | 1 | 855 | -0.012844 | north | 0.010857 | -0.042106 | 0.0093786 | -0.019766 | 0.0093786 | west | Y | 0.010857 | 1.2644
13692 | OAKGROVE | 2 | 855 | -0.012844 | north | 0.010857 | -0.042106 | 0.0093786 | -0.019766 | 0.0093786 | west | Y | 0.010857 | 1.2644
32798 | BRYN_TAM | 1 | 32 | -0.00548 | north | 0.018221 | -0.034742 | 0.016743 | -0.012402 | 0.012402 | houston | Y | 0.018221 | 0.18623
32883 | BRYN_DNS | 1 | 48 | -0.00483 | north | 0.018871 | -0.034092 | 0.017393 | -0.011752 | 0.011752 | houston | Y | 0.018871 | 0.34175
32884 | BRYN_DNS | 1 | 46 | -0.00483 | north | 0.018871 | -0.034092 | 0.017393 | -0.011752 | 0.011752 | houston | Y | 0.018871 | 0.32751
32886 | BRYN_ATK | MB | 12 | -0.005492 | north | 0.018209 | -0.034754 | 0.016731 | -0.012414 | 0.012414 | houston | Y | 0.018209 | 0.06955
32887 | BRYN_ATK | MB | 51 | -0.005492 | north | 0.018209 | -0.034754 | 0.016731 | -0.012414 | 0.012414 | houston | Y | 0.018209 | 0.29559
32888 | BRYN_ATK | 1 | 17 | -0.005492 | north | 0.018209 | -0.034754 | 0.016731 | -0.012414 | 0.012414 | houston | Y | 0.018209 | 0.098529
32890 | BRYN_ATK | MB | 22 | -0.005492 | north | 0.018209 | -0.034754 | 0.016731 | -0.012414 | 0.012414 | houston | Y | 0.018209 | 0.12751
32891 | BRYN_ATK | MB | 25 | -0.005492 | north | 0.018209 | -0.034754 | 0.016731 | -0.012414 | 0.012414 | houston | Y | 0.018209 | 0.1449
32892 | BRYN_DNS | 1 | 105 | -0.00483 | north | 0.018871 | -0.034092 | 0.017393 | -0.011752 | 0.011752 | houston | Y | 0.018871 | 0.74758
36998 | RDCNYNG1 | 1 | 84 | -0.022761 | west | 0.00094048 | -0.052023 | -0.0005384 | -0.029683 | 0.0005384 | west | N | 0.0005384 | 0
38332 | WDWRDU2 | 1 | 80 | -0.019751 | west | 0.0039505 | -0.049013 | 0.0024716 | -0.026673 | 0.0024716 | west | N | 0.0024716 | 0
38437 | TNSRBNMS | 1 | 150 | -0.019732 | west | 0.0039695 | -0.048994 | 0.0024906 | -0.026654 | 0.0024906 | west | N | 0.0024906 | 0
38438 | TNSRBNMS | 1 | 150 | -0.019732 | west | 0.0039695 | -0.048994 | 0.0024906 | -0.026654 | 0.0024906 | west | N | 0.0024906 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.007241 | houston | 0.030942 | -0.022021 | 0.029464 | 0.00031934 | 0.00031934 | houston | N | 0.00031934 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.007241 | houston | 0.030942 | -0.022021 | 0.029464 | 0.00031934 | 0.00031934 | houston | N | 0.00031934 | 0
38600 | TNBP_CGN | 5 | 53 | 0.007241 | houston | 0.030942 | -0.022021 | 0.029464 | 0.00031934 | 0.00031934 | houston | N | 0.00031934 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.007241 | houston | 0.030942 | -0.022021 | 0.029464 | 0.00031934 | 0.00031934 | houston | N | 0.00031934 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.007241 | houston | 0.030942 | -0.022021 | 0.029464 | 0.00031934 | 0.00031934 | houston | N | 0.00031934 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.007241 | houston | 0.030942 | -0.022021 | 0.029464 | 0.00031934 | 0.00031934 | houston | N | 0.00031934 | 0
38614 | TNBPAMCG | 4 | 96 | 0.007241 | houston | 0.030942 | -0.022021 | 0.029464 | 0.00031934 | 0.00031934 | houston | N | 0.00031934 | 0
38615 | TNBPAMCG | 1 | 244 | 0.007241 | houston | 0.030942 | -0.022021 | 0.029464 | 0.00031934 | 0.00031934 | houston | N | 0.00031934 | 0
38690 | TNBP_CGN | 3 | 40 | 0.007241 | houston | 0.030942 | -0.022021 | 0.029464 | 0.00031934 | 0.00031934 | houston | N | 0.00031934 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.007245 | houston | 0.030946 | -0.022017 | 0.029468 | 0.00032334 | 0.00032334 | houston | N | 0.00032334 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.007245 | houston | 0.030946 | -0.022017 | 0.029468 | 0.00032334 | 0.00032334 | houston | N | 0.00032334 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.007245 | houston | 0.030946 | -0.022017 | 0.029468 | 0.00032334 | 0.00032334 | houston | N | 0.00032334 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.007245 | houston | 0.030946 | -0.022017 | 0.029468 | 0.00032334 | 0.00032334 | houston | N | 0.00032334 | 0
39470 | TNDOWCGN | 1 | 32 | 0.007245 | houston | 0.030946 | -0.022017 | 0.029468 | 0.00032334 | 0.00032334 | houston | N | 0.00032334 | 0
39480 | TNDOWCGN | 1 | 30 | 0.007245 | houston | 0.030946 | -0.022017 | 0.029468 | 0.00032334 | 0.00032334 | houston | N | 0.00032334 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.010228 | houston | 0.033929 | -0.019034 | 0.032451 | 0.0033063 | 0.0033063 | houston | N | 0.0033063 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.010228 | houston | 0.033929 | -0.019034 | 0.032451 | 0.0033063 | 0.0033063 | houston | N | 0.0033063 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.010228 | houston | 0.033929 | -0.019034 | 0.032451 | 0.0033063 | 0.0033063 | houston | N | 0.0033063 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.010228 | houston | 0.033929 | -0.019034 | 0.032451 | 0.0033063 | 0.0033063 | houston | N | 0.0033063 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.012844 | north | 0.010857 | -0.042106 | 0.0093786 | -0.019766 | 0.0093786 | west | Y | 0.010857 | 0.22523
39970 | TNTNPONE | 1 | 153 | -0.012844 | north | 0.010857 | -0.042106 | 0.0093786 | -0.019766 | 0.0093786 | west | Y | 0.010857 | 0.22627
48500 | APD_GT1_ | 1 | 136 | 0.005424 | houston | 0.029125 | -0.023838 | 0.027647 | -0.0014977 | 0.0014977 | houston | N | 0.0014977 | 0
48510 | AK_GT1__ | 1 | 33 | 0.008236 | houston | 0.031937 | -0.021026 | 0.030459 | 0.0013143 | 0.0013143 | houston | N | 0.0013143 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.005413 | houston | 0.029114 | -0.023849 | 0.027636 | -0.0015087 | 0.0015087 | houston | N | 0.0015087 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.005413 | houston | 0.029114 | -0.023849 | 0.027636 | -0.0015087 | 0.0015087 | houston | N | 0.0015087 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.005413 | houston | 0.029114 | -0.023849 | 0.027636 | -0.0015087 | 0.0015087 | houston | N | 0.0015087 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.005413 | houston | 0.029114 | -0.023849 | 0.027636 | -0.0015087 | 0.0015087 | houston | N | 0.0015087 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.010707 | houston | 0.034408 | -0.018555 | 0.03293 | 0.0037853 | 0.0037853 | houston | N | 0.0037853 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.010707 | houston | 0.034408 | -0.018555 | 0.03293 | 0.0037853 | 0.0037853 | houston | N | 0.0037853 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.008416 | houston | 0.032117 | -0.020846 | 0.030639 | 0.0014943 | 0.0014943 | houston | N | 0.0014943 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.008416 | houston | 0.032117 | -0.020846 | 0.030639 | 0.0014943 | 0.0014943 | houston | N | 0.0014943 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.008416 | houston | 0.032117 | -0.020846 | 0.030639 | 0.0014943 | 0.0014943 | houston | N | 0.0014943 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.006102 | houston | 0.029803 | -0.02316 | 0.028325 | -0.00081966 | 0.00081966 | houston | N | 0.00081966 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.006102 | houston | 0.029803 | -0.02316 | 0.028325 | -0.00081966 | 0.00081966 | houston | N | 0.00081966 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.006102 | houston | 0.029803 | -0.02316 | 0.028325 | -0.00081966 | 0.00081966 | houston | N | 0.00081966 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.006102 | houston | 0.029803 | -0.02316 | 0.028325 | -0.00081966 | 0.00081966 | houston | N | 0.00081966 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.00566 | houston | 0.029361 | -0.023602 | 0.027883 | -0.0012617 | 0.0012617 | houston | N | 0.0012617 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.00566 | houston | 0.029361 | -0.023602 | 0.027883 | -0.0012617 | 0.0012617 | houston | N | 0.0012617 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.006235 | houston | 0.029936 | -0.023027 | 0.028458 | -0.00068666 | 0.00068666 | houston | N | 0.00068666 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.006235 | houston | 0.029936 | -0.023027 | 0.028458 | -0.00068666 | 0.00068666 | houston | N | 0.00068666 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.006235 | houston | 0.029936 | -0.023027 | 0.028458 | -0.00068666 | 0.00068666 | houston | N | 0.00068666 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.006235 | houston | 0.029936 | -0.023027 | 0.028458 | -0.00068666 | 0.00068666 | houston | N | 0.00068666 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.006235 | houston | 0.029936 | -0.023027 | 0.028458 | -0.00068666 | 0.00068666 | houston | N | 0.00068666 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.004858 | houston | 0.028559 | -0.024404 | 0.027081 | -0.0020637 | 0.0020637 | houston | N | 0.0020637 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.005083 | houston | 0.028784 | -0.024179 | 0.027306 | -0.0018387 | 0.0018387 | houston | N | 0.0018387 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.00479 | houston | 0.028491 | -0.024472 | 0.027013 | -0.0021317 | 0.0021317 | houston | N | 0.0021317 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.00479 | houston | 0.028491 | -0.024472 | 0.027013 | -0.0021317 | 0.0021317 | houston | N | 0.0021317 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.00479 | houston | 0.028491 | -0.024472 | 0.027013 | -0.0021317 | 0.0021317 | houston | N | 0.0021317 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.00354 | houston | 0.027241 | -0.025722 | 0.025763 | -0.0033817 | 0.0033817 | houston | N | 0.0033817 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.005379 | houston | 0.02908 | -0.023883 | 0.027602 | -0.0015427 | 0.0015427 | houston | N | 0.0015427 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.005379 | houston | 0.02908 | -0.023883 | 0.027602 | -0.0015427 | 0.0015427 | houston | N | 0.0015427 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.004631 | houston | 0.028332 | -0.024631 | 0.026854 | -0.0022907 | 0.0022907 | houston | N | 0.0022907 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.004631 | houston | 0.028332 | -0.024631 | 0.026854 | -0.0022907 | 0.0022907 | houston | N | 0.0022907 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.004631 | houston | 0.028332 | -0.024631 | 0.026854 | -0.0022907 | 0.0022907 | houston | N | 0.0022907 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.004631 | houston | 0.028332 | -0.024631 | 0.026854 | -0.0022907 | 0.0022907 | houston | N | 0.0022907 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.005645 | houston | 0.029346 | -0.023617 | 0.027868 | -0.0012767 | 0.0012767 | houston | N | 0.0012767 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.005645 | houston | 0.029346 | -0.023617 | 0.027868 | -0.0012767 | 0.0012767 | houston | N | 0.0012767 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.005645 | houston | 0.029346 | -0.023617 | 0.027868 | -0.0012767 | 0.0012767 | houston | N | 0.0012767 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.005645 | houston | 0.029346 | -0.023617 | 0.027868 | -0.0012767 | 0.0012767 | houston | N | 0.0012767 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.005786 | houston | 0.029487 | -0.023476 | 0.028009 | -0.0011357 | 0.0011357 | houston | N | 0.0011357 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.005786 | houston | 0.029487 | -0.023476 | 0.028009 | -0.0011357 | 0.0011357 | houston | N | 0.0011357 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.005786 | houston | 0.029487 | -0.023476 | 0.028009 | -0.0011357 | 0.0011357 | houston | N | 0.0011357 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.005786 | houston | 0.029487 | -0.023476 | 0.028009 | -0.0011357 | 0.0011357 | houston | N | 0.0011357 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.005786 | houston | 0.029487 | -0.023476 | 0.028009 | -0.0011357 | 0.0011357 | houston | N | 0.0011357 | 0
48651 | EP_1_2 | 1 | 5 | 0.00487 | houston | 0.028571 | -0.024392 | 0.027093 | -0.0020517 | 0.0020517 | houston | N | 0.0020517 | 0
48651 | EP_1_2 | 2 | 21 | 0.00487 | houston | 0.028571 | -0.024392 | 0.027093 | -0.0020517 | 0.0020517 | houston | N | 0.0020517 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.005274 | north | 0.018427 | -0.034536 | 0.016949 | -0.012196 | 0.012196 | houston | Y | 0.018427 | 0.96095
48672 | FTR_GT2_ | 2 | 156 | -0.005274 | north | 0.018427 | -0.034536 | 0.016949 | -0.012196 | 0.012196 | houston | Y | 0.018427 | 0.97216
48673 | FTR_GT3_ | 3 | 156 | -0.005274 | north | 0.018427 | -0.034536 | 0.016949 | -0.012196 | 0.012196 | houston | Y | 0.018427 | 0.97216
48674 | FTR_CN4_ | 4 | 380 | -0.005274 | north | 0.018427 | -0.034536 | 0.016949 | -0.012196 | 0.012196 | houston | Y | 0.018427 | 2.3681
48690 | GBY_GN5_ | 5 | 398 | 0.004575 | houston | 0.028276 | -0.024687 | 0.026798 | -0.0023467 | 0.0023467 | houston | N | 0.0023467 | 0
48691 | GBY_7374 | A | 46 | 0.005904 | houston | 0.029605 | -0.023358 | 0.028127 | -0.0010177 | 0.0010177 | houston | N | 0.0010177 | 0
48691 | GBY_7374 | B | 46 | 0.005904 | houston | 0.029605 | -0.023358 | 0.028127 | -0.0010177 | 0.0010177 | houston | N | 0.0010177 | 0
48692 | GBY_8182 | C | 46 | 0.005904 | houston | 0.029605 | -0.023358 | 0.028127 | -0.0010177 | 0.0010177 | houston | N | 0.0010177 | 0
48692 | GBY_8182 | D | 55 | 0.005904 | houston | 0.029605 | -0.023358 | 0.028127 | -0.0010177 | 0.0010177 | houston | N | 0.0010177 | 0
48693 | GBY_8384 | E | 55 | 0.005904 | houston | 0.029605 | -0.023358 | 0.028127 | -0.0010177 | 0.0010177 | houston | N | 0.0010177 | 0
48693 | GBY_8384 | F | 54 | 0.005904 | houston | 0.029605 | -0.023358 | 0.028127 | -0.0010177 | 0.0010177 | houston | N | 0.0010177 | 0
48721 | LEG_1___ | 1 | 827 | -0.01534 | north | 0.0083615 | -0.044602 | 0.0068826 | -0.022262 | 0.0068826 | west | Y | 0.0083615 | 1.223
48722 | LEG_2___ | 2 | 819 | -0.01534 | north | 0.0083615 | -0.044602 | 0.0068826 | -0.022262 | 0.0068826 | west | Y | 0.0083615 | 1.2112
48730 | MNS_GT | 1 | 46.1 | 0.008495 | houston | 0.032196 | -0.020767 | 0.030718 | 0.0015733 | 0.0015733 | houston | N | 0.0015733 | 0
48731 | CBE_GT1 | 1 | 76 | 0.01461 | houston | 0.038311 | -0.014652 | 0.036833 | 0.0076883 | 0.0076883 | houston | N | 0.0076883 | 0
48732 | CBE_GT2 | 1 | 76 | 0.01461 | houston | 0.038311 | -0.014652 | 0.036833 | 0.0076883 | 0.0076883 | houston | N | 0.0076883 | 0
48733 | CBE_ST12 | 1 | 105 | 0.01461 | houston | 0.038311 | -0.014652 | 0.036833 | 0.0076883 | 0.0076883 | houston | N | 0.0076883 | 0
48734 | CBE_GT3 | 1 | 74 | 0.01461 | houston | 0.038311 | -0.014652 | 0.036833 | 0.0076883 | 0.0076883 | houston | N | 0.0076883 | 0
48735 | CBE_GT4 | 1 | 74 | 0.01461 | houston | 0.038311 | -0.014652 | 0.036833 | 0.0076883 | 0.0076883 | houston | N | 0.0076883 | 0
48736 | CBE_ST34 | 1 | 102 | 0.01461 | houston | 0.038311 | -0.014652 | 0.036833 | 0.0076883 | 0.0076883 | houston | N | 0.0076883 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.005641 | houston | 0.029342 | -0.023621 | 0.027864 | -0.0012807 | 0.0012807 | houston | N | 0.0012807 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.005641 | houston | 0.029342 | -0.023621 | 0.027864 | -0.0012807 | 0.0012807 | houston | N | 0.0012807 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.005641 | houston | 0.029342 | -0.023621 | 0.027864 | -0.0012807 | 0.0012807 | houston | N | 0.0012807 | 0
48761 | PR_GT1__ | 1 | 35 | 0.005731 | houston | 0.029432 | -0.023531 | 0.027954 | -0.0011907 | 0.0011907 | houston | N | 0.0011907 | 0
48772 | PHR_GN2_ | MB | 459 | 0.006575 | houston | 0.030276 | -0.022687 | 0.028798 | -0.00034666 | 0.00034666 | houston | N | 0.00034666 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.004868 | houston | 0.028569 | -0.024394 | 0.027091 | -0.0020537 | 0.0020537 | houston | N | 0.0020537 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.004868 | houston | 0.028569 | -0.024394 | 0.027091 | -0.0020537 | 0.0020537 | houston | N | 0.0020537 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.004868 | houston | 0.028569 | -0.024394 | 0.027091 | -0.0020537 | 0.0020537 | houston | N | 0.0020537 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.004868 | houston | 0.028569 | -0.024394 | 0.027091 | -0.0020537 | 0.0020537 | houston | N | 0.0020537 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.004868 | houston | 0.028569 | -0.024394 | 0.027091 | -0.0020537 | 0.0020537 | houston | N | 0.0020537 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.004868 | houston | 0.028569 | -0.024394 | 0.027091 | -0.0020537 | 0.0020537 | houston | N | 0.0020537 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.004868 | houston | 0.028569 | -0.024394 | 0.027091 | -0.0020537 | 0.0020537 | houston | N | 0.0020537 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.00354 | houston | 0.027241 | -0.025722 | 0.025763 | -0.0033817 | 0.0033817 | houston | N | 0.0033817 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.00354 | houston | 0.027241 | -0.025722 | 0.025763 | -0.0033817 | 0.0033817 | houston | N | 0.0033817 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.00354 | houston | 0.027241 | -0.025722 | 0.025763 | -0.0033817 | 0.0033817 | houston | N | 0.0033817 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.00354 | houston | 0.027241 | -0.025722 | 0.025763 | -0.0033817 | 0.0033817 | houston | N | 0.0033817 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.004817 | houston | 0.028518 | -0.024445 | 0.02704 | -0.0021047 | 0.0021047 | houston | N | 0.0021047 | 0
48820 | SHELLG1_ | 1 | 71 | 0.005557 | houston | 0.029258 | -0.023705 | 0.02778 | -0.0013647 | 0.0013647 | houston | N | 0.0013647 | 0
48821 | SHELLG2 | 2 | 72 | 0.005557 | houston | 0.029258 | -0.023705 | 0.02778 | -0.0013647 | 0.0013647 | houston | N | 0.0013647 | 0
48822 | SHELLG3_ | 1 | 39 | 0.005557 | houston | 0.029258 | -0.023705 | 0.02778 | -0.0013647 | 0.0013647 | houston | N | 0.0013647 | 0
48822 | SHELLG3_ | 2 | 30 | 0.005557 | houston | 0.029258 | -0.023705 | 0.02778 | -0.0013647 | 0.0013647 | houston | N | 0.0013647 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.005855 | houston | 0.029556 | -0.023407 | 0.028078 | -0.0010667 | 0.0010667 | houston | N | 0.0010667 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.005855 | houston | 0.029556 | -0.023407 | 0.028078 | -0.0010667 | 0.0010667 | houston | N | 0.0010667 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.005646 | houston | 0.029347 | -0.023616 | 0.027869 | -0.0012757 | 0.0012757 | houston | N | 0.0012757 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.005663 | houston | 0.029364 | -0.023599 | 0.027886 | -0.0012587 | 0.0012587 | houston | N | 0.0012587 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.005668 | houston | 0.029369 | -0.023594 | 0.027891 | -0.0012537 | 0.0012537 | houston | N | 0.0012537 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.005647 | houston | 0.029348 | -0.023615 | 0.02787 | -0.0012747 | 0.0012747 | houston | N | 0.0012747 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.005643 | houston | 0.029344 | -0.023619 | 0.027866 | -0.0012787 | 0.0012787 | houston | N | 0.0012787 | 0
48855 | SRB_GT21 | B2 | 12 | 0.005671 | houston | 0.029372 | -0.023591 | 0.027894 | -0.0012507 | 0.0012507 | houston | N | 0.0012507 | 0
48855 | SRB_GT21 | MB | 18 | 0.005671 | houston | 0.029372 | -0.023591 | 0.027894 | -0.0012507 | 0.0012507 | houston | N | 0.0012507 | 0
48865 | TECO_GT1 | 1 | 50 | 0.006867 | houston | 0.030568 | -0.022395 | 0.02909 | -5.4659e-05 | 5.4659e-05 | houston | N | 5.4659e-05 | 0
48873 | THW_ST3_ | 3 | 104 | 0.005165 | houston | 0.028866 | -0.024097 | 0.027388 | -0.0017567 | 0.0017567 | houston | N | 0.0017567 | 0
48874 | THW_ST4_ | 4 | 104 | 0.005165 | houston | 0.028866 | -0.024097 | 0.027388 | -0.0017567 | 0.0017567 | houston | N | 0.0017567 | 0
48875 | THW_3132 | A | 54 | 0.005165 | houston | 0.028866 | -0.024097 | 0.027388 | -0.0017567 | 0.0017567 | houston | N | 0.0017567 | 0
48875 | THW_3132 | B | 53 | 0.005165 | houston | 0.028866 | -0.024097 | 0.027388 | -0.0017567 | 0.0017567 | houston | N | 0.0017567 | 0
48877 | THW_3334 | C | 54 | 0.005165 | houston | 0.028866 | -0.024097 | 0.027388 | -0.0017567 | 0.0017567 | houston | N | 0.0017567 | 0
48877 | THW_3334 | D | 57 | 0.005165 | houston | 0.028866 | -0.024097 | 0.027388 | -0.0017567 | 0.0017567 | houston | N | 0.0017567 | 0
48879 | THW_4142 | E | 54 | 0.005165 | houston | 0.028866 | -0.024097 | 0.027388 | -0.0017567 | 0.0017567 | houston | N | 0.0017567 | 0
48879 | THW_4142 | F | 54 | 0.005165 | houston | 0.028866 | -0.024097 | 0.027388 | -0.0017567 | 0.0017567 | houston | N | 0.0017567 | 0
48881 | THW_4344 | G | 58 | 0.005165 | houston | 0.028866 | -0.024097 | 0.027388 | -0.0017567 | 0.0017567 | houston | N | 0.0017567 | 0
48881 | THW_4344 | H | 58 | 0.005165 | houston | 0.028866 | -0.024097 | 0.027388 | -0.0017567 | 0.0017567 | houston | N | 0.0017567 | 0
48883 | THW_GT1_ | B2 | 12 | 0.004958 | houston | 0.028659 | -0.024304 | 0.027181 | -0.0019637 | 0.0019637 | houston | N | 0.0019637 | 0
48885 | THW_5152 | A | 56 | 0.004478 | houston | 0.028179 | -0.024784 | 0.026701 | -0.0024437 | 0.0024437 | houston | N | 0.0024437 | 0
48885 | THW_5152 | B | 59 | 0.004478 | houston | 0.028179 | -0.024784 | 0.026701 | -0.0024437 | 0.0024437 | houston | N | 0.0024437 | 0
48886 | THW_5354 | C | 56 | 0.004478 | houston | 0.028179 | -0.024784 | 0.026701 | -0.0024437 | 0.0024437 | houston | N | 0.0024437 | 0
48886 | THW_5354 | D | 56 | 0.004478 | houston | 0.028179 | -0.024784 | 0.026701 | -0.0024437 | 0.0024437 | houston | N | 0.0024437 | 0
48887 | THW_5556 | E | 59 | 0.004478 | houston | 0.028179 | -0.024784 | 0.026701 | -0.0024437 | 0.0024437 | houston | N | 0.0024437 | 0
48887 | THW_5556 | F | 56 | 0.004478 | houston | 0.028179 | -0.024784 | 0.026701 | -0.0024437 | 0.0024437 | houston | N | 0.0024437 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.013818 | houston | 0.037519 | -0.015444 | 0.036041 | 0.0068963 | 0.0068963 | houston | N | 0.0068963 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.008157 | houston | 0.031858 | -0.021105 | 0.03038 | 0.0012353 | 0.0012353 | houston | N | 0.0012353 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.008157 | houston | 0.031858 | -0.021105 | 0.03038 | 0.0012353 | 0.0012353 | houston | N | 0.0012353 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.008157 | houston | 0.031858 | -0.021105 | 0.03038 | 0.0012353 | 0.0012353 | houston | N | 0.0012353 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.008157 | houston | 0.031858 | -0.021105 | 0.03038 | 0.0012353 | 0.0012353 | houston | N | 0.0012353 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.008157 | houston | 0.031858 | -0.021105 | 0.03038 | 0.0012353 | 0.0012353 | houston | N | 0.0012353 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.008431 | houston | 0.032132 | -0.020831 | 0.030654 | 0.0015093 | 0.0015093 | houston | N | 0.0015093 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.008431 | houston | 0.032132 | -0.020831 | 0.030654 | 0.0015093 | 0.0015093 | houston | N | 0.0015093 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.008431 | houston | 0.032132 | -0.020831 | 0.030654 | 0.0015093 | 0.0015093 | houston | N | 0.0015093 | 0
48929 | WAPGT21_ | B1 | 13 | 0.008157 | houston | 0.031858 | -0.021105 | 0.03038 | 0.0012353 | 0.0012353 | houston | N | 0.0012353 | 0
48940 | WARVUE_G | G1 | 12 | 0.004864 | houston | 0.028565 | -0.024398 | 0.027087 | -0.0020577 | 0.0020577 | houston | N | 0.0020577 | 0
49803 | EXN_15GT | 1 | 34 | 0.005028 | houston | 0.028729 | -0.024234 | 0.027251 | -0.0018937 | 0.0018937 | houston | N | 0.0018937 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.005028 | houston | 0.028729 | -0.024234 | 0.027251 | -0.0018937 | 0.0018937 | houston | N | 0.0018937 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.005028 | houston | 0.028729 | -0.024234 | 0.027251 | -0.0018937 | 0.0018937 | houston | N | 0.0018937 | 0
49826 | EXN938GT | 5 | 45.9 | 0.005028 | houston | 0.028729 | -0.024234 | 0.027251 | -0.0018937 | 0.0018937 | houston | N | 0.0018937 | 0
49828 | EXN941GT | 10 | 17.7 | 0.005028 | houston | 0.028729 | -0.024234 | 0.027251 | -0.0018937 | 0.0018937 | houston | N | 0.0018937 | 0
49829 | EXN942GT | 11 | 20.4 | 0.005028 | houston | 0.028729 | -0.024234 | 0.027251 | -0.0018937 | 0.0018937 | houston | N | 0.0018937 | 0
49830 | EXN943GT | 12 | 19.9 | 0.005028 | houston | 0.028729 | -0.024234 | 0.027251 | -0.0018937 | 0.0018937 | houston | N | 0.0018937 | 0
49831 | EXN944GT | 13 | 35 | 0.005028 | houston | 0.028729 | -0.024234 | 0.027251 | -0.0018937 | 0.0018937 | houston | N | 0.0018937 | 0
49832 | EXN945GT | 9 | 18 | 0.005028 | houston | 0.028729 | -0.024234 | 0.027251 | -0.0018937 | 0.0018937 | houston | N | 0.0018937 | 0
49837 | EXN_GT | 4 | 85.4 | 0.005028 | houston | 0.028729 | -0.024234 | 0.027251 | -0.0018937 | 0.0018937 | houston | N | 0.0018937 | 0
49838 | EXN_14GT | 14 | 148 | 0.005028 | houston | 0.028729 | -0.024234 | 0.027251 | -0.0018937 | 0.0018937 | houston | N | 0.0018937 | 0
49851 | DOW17000 | 37 | 62 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49858 | DOW38100 | 31 | 71.4 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49859 | DOW38200 | 33 | 45 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49860 | DOW38300 | 32 | 101 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49862 | DOW39100 | 36 | 86 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49863 | DOW39200 | 35 | 88 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49865 | DOW41000 | 41 | 50 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49866 | DOW42000 | 42 | 18 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49869 | DOW49000 | 45 | 94 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49870 | DOW61000 | 61 | 70 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49871 | DOW62000 | 62 | 63 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49872 | DOW63000 | 63 | 72 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49873 | DOW64000 | 64 | 64.8 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49876 | DOW65000 | 65 | 101 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49877 | DOW66000 | 66 | 97 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49878 | DOW67000 | 67 | 103 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49882 | DOW81000 | 81 | 76 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49884 | DOW82000 | 82 | 80 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49885 | DOW83000 | 83 | 80 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
49886 | DOW84000 | 84 | 171 | 0.011312 | houston | 0.035013 | -0.01795 | 0.033535 | 0.0043903 | 0.0043903 | houston | N | 0.0043903 | 0
58909 | PEARSALL | 1 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58909 | PEARSALL | 2 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58909 | PEARSALL | 3 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58909 | PEARSALL | 4 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58909 | PEARSALL | 5 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58909 | PEARSALL | 6 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58919 | PEARSALL | 1 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58919 | PEARSALL | 2 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58919 | PEARSALL | 3 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58919 | PEARSALL | 4 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58919 | PEARSALL | 5 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58919 | PEARSALL | 6 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58929 | PEARSALL | 1 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58929 | PEARSALL | 2 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58929 | PEARSALL | 3 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58929 | PEARSALL | 4 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58929 | PEARSALL | 5 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58929 | PEARSALL | 6 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58949 | PEARSALL | 1 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58949 | PEARSALL | 2 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58949 | PEARSALL | 3 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58949 | PEARSALL | 4 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58949 | PEARSALL | 5 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
58949 | PEARSALL | 6 | 8.4 | 0.02427 | south | 0.047971 | -0.0049925 | 0.046493 | 0.017348 | 0.0049925 | south | N | 0.0049925 | 0
60000 | DSKY2 | 1 | 76.5 | -0.018848 | west | 0.0048535 | -0.04811 | 0.0033746 | -0.02577 | 0.0033746 | west | N | 0.0033746 | 0
60003 | KING_NE1 | 1 | 80 | -0.019788 | west | 0.0039135 | -0.04905 | 0.0024346 | -0.02671 | 0.0024346 | west | N | 0.0024346 | 0
60005 | KING_SE1 | 1 | 40 | -0.019788 | west | 0.0039135 | -0.04905 | 0.0024346 | -0.02671 | 0.0024346 | west | N | 0.0024346 | 0
60007 | KING_SW1 | 1 | 80 | -0.019939 | west | 0.0037625 | -0.049201 | 0.0022836 | -0.026861 | 0.0022836 | west | N | 0.0022836 | 0
60016 | WOODWRD1 | 1 | 80 | -0.019755 | west | 0.0039465 | -0.049017 | 0.0024676 | -0.026677 | 0.0024676 | west | N | 0.0024676 | 0
60017 | ORNNWP1 | 1 | 80 | -0.018977 | west | 0.0047245 | -0.048239 | 0.0032456 | -0.025899 | 0.0032456 | west | N | 0.0032456 | 0
60018 | DSKY1 | 1 | 84 | -0.018723 | west | 0.0049785 | -0.047985 | 0.0034996 | -0.025645 | 0.0034996 | west | N | 0.0034996 | 0
60019 | KING_NW1 | 1 | 80 | -0.019939 | west | 0.0037625 | -0.049201 | 0.0022836 | -0.026861 | 0.0022836 | west | N | 0.0022836 | 0
60057 | CALLAHAN | 1 | 114 | 0.029319 | south | 0.05302 | 5.6541e-05 | 0.051542 | 0.022397 | 5.6541e-05 | south | N | 5.6541e-05 | 0
60058 | BUFF_GAP | 1 | 120 | -0.022506 | west | 0.0011955 | -0.051768 | -0.0002834 | -0.029428 | 0.0002834 | west | N | 0.0002834 | 0
60060 | CIRELLO | 1 | 233 | -0.022506 | west | 0.0011955 | -0.051768 | -0.0002834 | -0.029428 | 0.0002834 | west | N | 0.0002834 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.022506 | west | 0.0011955 | -0.051768 | -0.0002834 | -0.029428 | 0.0002834 | west | N | 0.0002834 | 0
60066 | H_HOLLOW | 1 | 222 | 0.029319 | south | 0.05302 | 5.6541e-05 | 0.051542 | 0.022397 | 5.6541e-05 | south | N | 5.6541e-05 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.029319 | south | 0.05302 | 5.6541e-05 | 0.051542 | 0.022397 | 5.6541e-05 | south | N | 5.6541e-05 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.029319 | south | 0.05302 | 5.6541e-05 | 0.051542 | 0.022397 | 5.6541e-05 | south | N | 5.6541e-05 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.029319 | south | 0.05302 | 5.6541e-05 | 0.051542 | 0.022397 | 5.6541e-05 | south | N | 5.6541e-05 | 0
60074 | HORSH5 | 1 | 100 | 0.029319 | south | 0.05302 | 5.6541e-05 | 0.051542 | 0.022397 | 5.6541e-05 | south | N | 5.6541e-05 | 0
60081 | WHRLWIND | 1 | 60 | -0.023393 | west | 0.00030848 | -0.052655 | -0.0011704 | -0.030315 | 0.00030848 | North | Y | 0.0011704 | 0.051715
60201 | RIO DRCS | F | 0 | 0.01558 | south | 0.039281 | -0.013682 | 0.037803 | 0.0086583 | 0.0086583 | houston | Y | 0.013682 | 0
60202 | FRIEND_R | F | 0 | -0.014666 | west | 0.0090355 | -0.043928 | 0.0075566 | -0.021588 | 0.0075566 | west | N | 0.0075566 | 0
60203 | PRES0A | BT | 4.8 | -0.0205 | west | 0.0032015 | -0.049762 | 0.0017226 | -0.027422 | 0.0017226 | west | N | 0.0017226 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.022859 | west | 0.00084248 | -0.052121 | -0.0006364 | -0.029781 | 0.0006364 | west | N | 0.0006364 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.022859 | west | 0.00084248 | -0.052121 | -0.0006364 | -0.029781 | 0.0006364 | west | N | 0.0006364 | 0
71057 | L_SWEETW | W1 | 135 | -0.022859 | west | 0.00084248 | -0.052121 | -0.0006364 | -0.029781 | 0.0006364 | west | N | 0.0006364 | 0
71059 | L_SWEETW | W1 | 119 | -0.022859 | west | 0.00084248 | -0.052121 | -0.0006364 | -0.029781 | 0.0006364 | west | N | 0.0006364 | 0
71060 | L_SWEETW | W1 | 105 | -0.022859 | west | 0.00084248 | -0.052121 | -0.0006364 | -0.029781 | 0.0006364 | west | N | 0.0006364 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.022859 | west | 0.00084248 | -0.052121 | -0.0006364 | -0.029781 | 0.0006364 | west | N | 0.0006364 | 0
76031 | L_GASCCR | W1 | 150 | -0.022215 | west | 0.0014865 | -0.051477 | 7.6041e-06 | -0.029137 | 7.6041e-06 | west | N | 7.6041e-06 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.022134 | west | 0.0015675 | -0.051396 | 8.8604e-05 | -0.029056 | 8.8604e-05 | west | N | 8.8604e-05 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.022134 | west | 0.0015675 | -0.051396 | 8.8604e-05 | -0.029056 | 8.8604e-05 | west | N | 8.8604e-05 | 0
76096 | L_CAPRSI | W1 | 186 | -0.022134 | west | 0.0015675 | -0.051396 | 8.8604e-05 | -0.029056 | 8.8604e-05 | west | N | 8.8604e-05 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.022134 | west | 0.0015675 | -0.051396 | 8.8604e-05 | -0.029056 | 8.8604e-05 | west | N | 8.8604e-05 | 0
80003 | MILHWYS | F | 0 | 0.023313 | south | 0.047014 | -0.0059495 | 0.045536 | 0.016391 | 0.0059495 | south | N | 0.0059495 | 0
80010 | EPLVT1 | F | 0 | 0.017139 | south | 0.04084 | -0.012123 | 0.039362 | 0.010217 | 0.010217 | houston | Y | 0.012123 | 0
80012 | LAR | F | 0 | 0.02445 | south | 0.048151 | -0.0048125 | 0.046673 | 0.017528 | 0.0048125 | south | N | 0.0048125 | 0
80051 | FORPVCM0 | 8 | 28 | 0.021288 | south | 0.044989 | -0.0079745 | 0.043511 | 0.014366 | 0.0079745 | south | N | 0.0079745 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.021288 | south | 0.044989 | -0.0079745 | 0.043511 | 0.014366 | 0.0079745 | south | N | 0.0079745 | 0
80053 | FOR69CG0 | 10 | 74 | 0.021288 | south | 0.044989 | -0.0079745 | 0.043511 | 0.014366 | 0.0079745 | south | N | 0.0079745 | 0
80080 | GWINDT11 | 1 | 94 | 0.023299 | south | 0.047 | -0.0059635 | 0.045522 | 0.016377 | 0.0059635 | south | N | 0.0059635 | 0
80080 | GWINDT11 | 2 | 41 | 0.023299 | south | 0.047 | -0.0059635 | 0.045522 | 0.016377 | 0.0059635 | south | N | 0.0059635 | 0
80080 | GWINDT11 | 3 | 38 | 0.023299 | south | 0.047 | -0.0059635 | 0.045522 | 0.016377 | 0.0059635 | south | N | 0.0059635 | 0
80080 | GWINDT11 | 4 | 19 | 0.023299 | south | 0.047 | -0.0059635 | 0.045522 | 0.016377 | 0.0059635 | south | N | 0.0059635 | 0
80081 | GWINDT21 | 1 | 94 | 0.023299 | south | 0.047 | -0.0059635 | 0.045522 | 0.016377 | 0.0059635 | south | N | 0.0059635 | 0
80081 | GWINDT21 | 2 | 36 | 0.023299 | south | 0.047 | -0.0059635 | 0.045522 | 0.016377 | 0.0059635 | south | N | 0.0059635 | 0
80081 | GWINDT21 | 3 | 43 | 0.023299 | south | 0.047 | -0.0059635 | 0.045522 | 0.016377 | 0.0059635 | south | N | 0.0059635 | 0
80081 | GWINDT21 | 4 | 22 | 0.023299 | south | 0.047 | -0.0059635 | 0.045522 | 0.016377 | 0.0059635 | south | N | 0.0059635 | 0
80137 | CSDR89 | 8 | 39 | 0.022061 | south | 0.045762 | -0.0072015 | 0.044284 | 0.015139 | 0.0072015 | south | N | 0.0072015 | 0
80137 | CSDR89 | 9 | 15 | 0.022061 | south | 0.045762 | -0.0072015 | 0.044284 | 0.015139 | 0.0072015 | south | N | 0.0072015 | 0
80138 | CSDR7 | 7 | 7 | 0.022061 | south | 0.045762 | -0.0072015 | 0.044284 | 0.015139 | 0.0072015 | south | N | 0.0072015 | 0
80139 | CSDR56 | 5 | 15 | 0.022061 | south | 0.045762 | -0.0072015 | 0.044284 | 0.015139 | 0.0072015 | south | N | 0.0072015 | 0
80139 | CSDR56 | 6 | 39 | 0.022061 | south | 0.045762 | -0.0072015 | 0.044284 | 0.015139 | 0.0072015 | south | N | 0.0072015 | 0
80140 | CSDR11 | 11 | 39 | 0.022061 | south | 0.045762 | -0.0072015 | 0.044284 | 0.015139 | 0.0072015 | south | N | 0.0072015 | 0
80180 | PNSCALT1 | 1 | 148 | 0.023299 | south | 0.047 | -0.0059635 | 0.045522 | 0.016377 | 0.0059635 | south | N | 0.0059635 | 0
80180 | PNSCALT1 | 2 | 50 | 0.023299 | south | 0.047 | -0.0059635 | 0.045522 | 0.016377 | 0.0059635 | south | N | 0.0059635 | 0
80181 | PNSCALT2 | 1 | 55 | 0.023299 | south | 0.047 | -0.0059635 | 0.045522 | 0.016377 | 0.0059635 | south | N | 0.0059635 | 0
80181 | PNSCALT2 | 2 | 50 | 0.023299 | south | 0.047 | -0.0059635 | 0.045522 | 0.016377 | 0.0059635 | south | N | 0.0059635 | 0
80223 | REYSHR G | 1 | 12 | 0.022843 | south | 0.046544 | -0.0064195 | 0.045066 | 0.015921 | 0.0064195 | south | N | 0.0064195 | 0
80224 | VISTRONG | 1 | 15 | 0.022309 | south | 0.04601 | -0.0069535 | 0.044532 | 0.015387 | 0.0069535 | south | N | 0.0069535 | 0
80225 | VISTRONG | 2 | 23 | 0.022309 | south | 0.04601 | -0.0069535 | 0.044532 | 0.015387 | 0.0069535 | south | N | 0.0069535 | 0
80226 | ALCOA G | 1 | 48 | 0.02147 | south | 0.045171 | -0.0077925 | 0.043693 | 0.014548 | 0.0077925 | south | N | 0.0077925 | 0
80227 | AIRCO G | 1 | 8 | 0.022148 | south | 0.045849 | -0.0071145 | 0.044371 | 0.015226 | 0.0071145 | south | N | 0.0071145 | 0
80261 | NBEC81A | 1 | 180 | 0.023081 | south | 0.046782 | -0.0061815 | 0.045304 | 0.016159 | 0.0061815 | south | N | 0.0061815 | 0
80262 | NBEC91A | 1 | 180 | 0.023074 | south | 0.046775 | -0.0061885 | 0.045297 | 0.016152 | 0.0061885 | south | N | 0.0061885 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.023126 | south | 0.046827 | -0.0061365 | 0.045349 | 0.016204 | 0.0061365 | south | N | 0.0061365 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.023126 | south | 0.046827 | -0.0061365 | 0.045349 | 0.016204 | 0.0061365 | south | N | 0.0061365 | 0
80265 | LARECU40 | 4 | 100 | 0.024452 | south | 0.048153 | -0.0048105 | 0.046675 | 0.01753 | 0.0048105 | south | N | 0.0048105 | 0
80266 | LARECU50 | 5 | 100 | 0.024452 | south | 0.048153 | -0.0048105 | 0.046675 | 0.01753 | 0.0048105 | south | N | 0.0048105 | 0
80291 | PAPALOTE | 1 | 25 | 0.022934 | south | 0.046635 | -0.0063285 | 0.045157 | 0.016012 | 0.0063285 | south | N | 0.0063285 | 0
80291 | PAPALOTE | 2 | 25 | 0.022934 | south | 0.046635 | -0.0063285 | 0.045157 | 0.016012 | 0.0063285 | south | N | 0.0063285 | 0
80291 | PAPALOTE | 3 | 25 | 0.022934 | south | 0.046635 | -0.0063285 | 0.045157 | 0.016012 | 0.0063285 | south | N | 0.0063285 | 0
80291 | PAPALOTE | 4 | 16 | 0.022934 | south | 0.046635 | -0.0063285 | 0.045157 | 0.016012 | 0.0063285 | south | N | 0.0063285 | 0
80294 | PAPALOTE | 5 | 25 | 0.022934 | south | 0.046635 | -0.0063285 | 0.045157 | 0.016012 | 0.0063285 | south | N | 0.0063285 | 0
80294 | PAPALOTE | 6 | 25 | 0.022934 | south | 0.046635 | -0.0063285 | 0.045157 | 0.016012 | 0.0063285 | south | N | 0.0063285 | 0
80294 | PAPALOTE | 7 | 25 | 0.022934 | south | 0.046635 | -0.0063285 | 0.045157 | 0.016012 | 0.0063285 | south | N | 0.0063285 | 0
80294 | PAPALOTE | 8 | 15 | 0.022934 | south | 0.046635 | -0.0063285 | 0.045157 | 0.016012 | 0.0063285 | south | N | 0.0063285 | 0
86104 | CID-138 | EQ | 0 | 0.024452 | south | 0.048153 | -0.0048105 | 0.046675 | 0.01753 | 0.0048105 | south | N | 0.0048105 | 0
86105 | CID-230 | EQ | 500 | 0.024452 | south | 0.048153 | -0.0048105 | 0.046675 | 0.01753 | 0.0048105 | south | N | 0.0048105 | 0
86106 | CUF-230 | EQ | 500 | 0.024452 | south | 0.048153 | -0.0048105 | 0.046675 | 0.01753 | 0.0048105 | south | N | 0.0048105 | 0
86107 | CUF-138 | EQ | 0 | 0.024452 | south | 0.048153 | -0.0048105 | 0.046675 | 0.01753 | 0.0048105 | south | N | 0.0048105 | 0
88198 | BEEVILLE | F | 0 | 0.024358 | south | 0.048059 | -0.0049045 | 0.046581 | 0.017436 | 0.0049045 | south | N | 0.0049045 | 0
88253 | HAMILTON | F | 0 | 0.012504 | south | 0.036205 | -0.016758 | 0.034727 | 0.0055823 | 0.0055823 | houston | Y | 0.016758 | 0
88299 | ZAPATA | F | 0 | 0.023879 | south | 0.04758 | -0.0053835 | 0.046102 | 0.016957 | 0.0053835 | south | N | 0.0053835 | 0
88508 | FALFURRI | F | 0 | 0.023671 | south | 0.047372 | -0.0055915 | 0.045894 | 0.016749 | 0.0055915 | south | N | 0.0055915 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:173 CRAWFORD 177 BOSQUE C:THOUSE__5-AEP_PEC__5 C:LAKE_CRK1_5-AEP_SS__59 [3405 - 3412] and [3409 - 3414] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.043247 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 24.6075 | 569 | 0.066948 | 38.0937 | 569 | 38.0937
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.043247 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 25.1265 | 581 | 0.066948 | 38.8971
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.037419 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5716 | 42 | 0.06112 | 2.5671
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.037419 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6464 | 44 | 0.06112 | 2.6893 |  |  | Weighted Shift Factors
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.037419 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6464 | 44 | 0.06112 | 2.6893 |  |  | North | -0.023701
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.037419 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.7587 | 47 | 0.06112 | 2.8727 |  |  | South | 0.028794
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.037078 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 11.4942 | 310 | 0.060779 | 18.8416 |  |  |  | -0.052495
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.037078 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 15.3132 | 413 | 0.060779 | 25.1019
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.037053 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.29642 | 0 | 0.060754 | 0 |  |  | Line Rating | 226.45
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.037053 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.29642 | 0 | 0.060754 | 0 |  |  | Conc Gen | 569
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.7924 | 49 | 0.06028 | 2.9537 |  |  | Weighted Imp. | 38.0937
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6826 | 46 | 0.06028 | 2.7729 |  |  | PTDF | 0.066948
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6826 | 46 | 0.06028 | 2.7729
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.7192 | 47 | 0.06028 | 2.8332 |  |  | Concentration | -1.2753
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.036579 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.6332 | 154 | 0.06028 | 9.2832
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.036579 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.4137 | 148 | 0.06028 | 8.9215
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.7558 | 48 | 0.06028 | 2.8935
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.7558 | 48 | 0.06028 | 2.8935
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.036472 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.2765 | 0 | 0.060173 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.036472 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.24 | 0 | 0.060173 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.036472 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.2765 | 0 | 0.060173 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.03518 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.365 | 152.5 | 0.058881 | 8.9794
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.03518 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.2594 | 149.5 | 0.058881 | 8.8028
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.03518 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.1829 | 232.6 | 0.058881 | 13.6958
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.035173 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.6428 | 132 | 0.058874 | 7.7714
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.035173 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.7132 | 134 | 0.058874 | 7.8892
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.035173 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 11.3609 | 323 | 0.058874 | 19.0165
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.034939 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.6289 | 0 | 0.05864 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.034939 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.6289 | 0 | 0.05864 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.034939 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.52409 | 0 | 0.05864 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.0348 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.4984 | 158 | 0.058501 | 9.2432
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.0348 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.568 | 160 | 0.058501 | 9.3602
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.0348 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.09 | 175 | 0.058501 | 10.2378
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.034605 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.62289 | 0 | 0.058306 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.034605 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.62289 | 0 | 0.058306 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.034072 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.95402 | 0 | 0.057773 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.034072 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.98809 | 0 | 0.057773 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.033884 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.46421 | 0 | 0.057585 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.033781 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 14.2556 | 422 | 0.057482 | 24.2576
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.031843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5921 | 50 | 0.055544 | 2.7772
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.031843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5921 | 50 | 0.055544 | 2.7772
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.031843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5921 | 50 | 0.055544 | 2.7772
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.031843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5921 | 50 | 0.055544 | 2.7772
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.031695 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19017 | 0 | 0.055396 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.031196 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 18.2185 | 584 | 0.054897 | 32.0601
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.031196 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 18.5616 | 595 | 0.054897 | 32.664
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.031167 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 13.4953 | 433 | 0.054868 | 23.7581
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.03066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.8648 | 223.9 | 0.054361 | 12.1715
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.03066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.8985 | 225 | 0.054361 | 12.2313
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.03066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.8862 | 224.6 | 0.054361 | 12.2096
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.03066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.9506 | 226.7 | 0.054361 | 12.3237
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.0298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.07152 | 0 | 0.053501 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.0298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.07152 | 0 | 0.053501 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.0298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.08344 | 0 | 0.053501 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.029597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.2028 | 142 | 0.053298 | 7.5684
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.029597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.2916 | 145 | 0.053298 | 7.7283
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.029597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.4691 | 151 | 0.053298 | 8.0481
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.029597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.5831 | 290 | 0.053298 | 15.4566
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.029423 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.070615 | 0 | 0.053124 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.029423 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.070615 | 0 | 0.053124 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.029354 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11742 | 0 | 0.053055 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3424 | 114 | 0.05302 | 6.0443
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 6.5088 | 222 | 0.05302 | 11.7705
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 5.3947 | 184 | 0.05302 | 9.7558
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 6.5675 | 224 | 0.05302 | 11.8766
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3717 | 115 | 0.05302 | 6.0974
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.2018 | 147 | 0.052285 | 7.686
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9446 | 138 | 0.052285 | 7.2154
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.0018 | 140 | 0.052285 | 7.32
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.2018 | 147 | 0.052285 | 7.686
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.2023 | 182 | 0.052285 | 9.516
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.6596 | 198 | 0.052285 | 10.3525
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.028002 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051703 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.028002 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051703 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.028002 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051703 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.027927 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.841 | 424 | 0.051628 | 21.8905
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.027927 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.869 | 425 | 0.051628 | 21.9421
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.027906 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 11.4973 | 412 | 0.051607 | 21.2623
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.027906 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 11.1624 | 400 | 0.051607 | 20.643
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.027875 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.8259 | 209 | 0.051576 | 10.7795
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.027875 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.021 | 216 | 0.051576 | 11.1405
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.027875 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2822 | 46 | 0.051576 | 2.3725
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.027875 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.3101 | 47 | 0.051576 | 2.4241
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.027875 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2822 | 46 | 0.051576 | 2.3725
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.027875 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2822 | 46 | 0.051576 | 2.3725
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.027863 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 11.3402 | 407 | 0.051564 | 20.9867
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.027814 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.3112 | 155 | 0.051515 | 7.9849
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.027814 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7284 | 170 | 0.051515 | 8.7576
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.027814 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.3112 | 155 | 0.051515 | 7.9849
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.027708 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.6071 | 58 | 0.051409 | 2.9817
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.027708 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.466 | 89 | 0.051409 | 4.5754
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.027708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2192 | 44 | 0.051409 | 2.262
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.027708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2192 | 44 | 0.051409 | 2.262
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.027708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.1914 | 43 | 0.051409 | 2.2106
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.027708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2469 | 45 | 0.051409 | 2.3134
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.027669 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 15.1073 | 546 | 0.05137 | 28.0483
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.027669 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 20.7518 | 750 | 0.05137 | 38.5279
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.02765 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3318 | 0 | 0.051351 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.026167 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 10.3621 | 396 | 0.049868 | 19.7479
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.024575 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.5898 | 24 | 0.048276 | 1.1586
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.024575 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.5898 | 24 | 0.048276 | 1.1586
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.024575 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.56522 | 23 | 0.048276 | 1.1104
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.024452 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4452 | 100 | 0.048153 | 4.8153
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.024452 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4452 | 100 | 0.048153 | 4.8153
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.024452 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.048153 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.024452 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.048153 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.024452 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.048153 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.024452 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.048153 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.02445 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.048151 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.024358 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.048059 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.024059 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 15.1331 | 629 | 0.04776 | 30.0413
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.023879 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.04758 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.023671 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.047372 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.023642 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2837 | 0 | 0.047343 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.023642 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.26006 | 0 | 0.047343 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.023642 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2837 | 0 | 0.047343 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.023394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4272 | 146.5 | 0.047095 | 6.8995
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.023394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.46 | 147.9 | 0.047095 | 6.9654
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.023394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.0472 | 173 | 0.047095 | 8.1475
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.023354 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8343 | 207 | 0.047055 | 9.7405
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.023354 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.0608 | 216.7 | 0.047055 | 10.1969
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.023354 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.6517 | 242 | 0.047055 | 11.3874
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.023353 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3628 | 144 | 0.047054 | 6.7758
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.023353 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3628 | 144 | 0.047054 | 6.7758
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.023353 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9934 | 171 | 0.047054 | 8.0463
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.023313 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.047014 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.023313 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.88589 | 38 | 0.047014 | 1.7866
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.023313 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.44994 | 19.3 | 0.047014 | 0.90738
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.023313 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34969 | 15 | 0.047014 | 0.70522
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.023313 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.0957 | 47 | 0.047014 | 2.2097
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.1901 | 94 | 0.047 | 4.418
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.95526 | 41 | 0.047 | 1.927
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.88536 | 38 | 0.047 | 1.786
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.44268 | 19 | 0.047 | 0.89301
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.1901 | 94 | 0.047 | 4.418
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.83876 | 36 | 0.047 | 1.692
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.0019 | 43 | 0.047 | 2.021
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.51258 | 22 | 0.047 | 1.034
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.4483 | 148 | 0.047 | 6.9561
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.1649 | 50 | 0.047 | 2.35
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.2814 | 55 | 0.047 | 2.585
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.1649 | 50 | 0.047 | 2.35
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.023264 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.67466 | 0 | 0.046965 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.023157 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.87997 | 0 | 0.046858 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.023156 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.87993 | 0 | 0.046857 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.023134 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.57835 | 0 | 0.046835 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.023134 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.57835 | 0 | 0.046835 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.023126 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 7.7241 | 334 | 0.046827 | 15.6404
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.023126 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 7.8628 | 340 | 0.046827 | 15.9213
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.023126 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.1627 | 180 | 0.046827 | 8.4289
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.023126 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.1627 | 180 | 0.046827 | 8.4289
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.023081 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.1546 | 180 | 0.046782 | 8.4208
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.023077 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.4223 | 0 | 0.046778 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.023077 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.4292 | 0 | 0.046778 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.023077 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.5308 | 0 | 0.046778 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.023074 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.7529 | 336 | 0.046775 | 15.7166
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.023074 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.1533 | 180 | 0.046775 | 8.4196
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.022999 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3119 | 144 | 0.0467 | 6.7249
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.022999 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.3238 | 188 | 0.0467 | 8.7797
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.57335 | 25 | 0.046635 | 1.1659
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.57335 | 25 | 0.046635 | 1.1659
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.57335 | 25 | 0.046635 | 1.1659
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.36694 | 16 | 0.046635 | 0.74617
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.57335 | 25 | 0.046635 | 1.1659
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.57335 | 25 | 0.046635 | 1.1659
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.57335 | 25 | 0.046635 | 1.1659
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.34401 | 15 | 0.046635 | 0.69953
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.6092 | 0 | 0.046544 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.495 | 0 | 0.046544 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.2843 | 0 | 0.046544 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.3122 | 0 | 0.046544 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.3579 | 0 | 0.046544 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.9011 | 0 | 0.046544 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.022843 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.27412 | 0 | 0.046544 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.022749 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.6607 | 0 | 0.04645 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.022697 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0826 | 47.7 | 0.046398 | 2.2132
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.022697 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.8466 | 37.3 | 0.046398 | 1.7307
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.022697 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0441 | 46 | 0.046398 | 2.1343
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.022697 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0895 | 48 | 0.046398 | 2.2271
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.022491 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.4948 | 22 | 0.046192 | 1.0162
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.022491 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2474 | 11 | 0.046192 | 0.50812
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.022491 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2474 | 11 | 0.046192 | 0.50812
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.022309 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.33464 | 0 | 0.04601 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.022309 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.51311 | 0 | 0.04601 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.022148 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.17718 | 0 | 0.045849 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.61771 | 0 | 0.045762 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15443 | 0 | 0.045762 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.86038 | 0 | 0.045762 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.33092 | 0 | 0.045762 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15443 | 0 | 0.045762 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.33092 | 0 | 0.045762 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.86038 | 0 | 0.045762 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.86038 | 0 | 0.045762 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.02147 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0306 | 0 | 0.045171 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.6818 | 0 | 0.044989 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.7243 | 0 | 0.044989 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.6818 | 0 | 0.044989 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.703 | 0 | 0.044989 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.669 | 0 | 0.044989 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.5322 | 0 | 0.044989 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.97925 | 0 | 0.044989 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.59606 | 0 | 0.044989 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.92816 | 0 | 0.044989 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5753 | 0 | 0.044989 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.017139 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.04084 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.016264 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.097584 | 0 | 0.039965 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.014699 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 19.5938 | 0 | 0.0384 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.014699 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 19.5203 | 0 | 0.0384 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1104 | 76 | 0.038311 | 2.9117
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1104 | 76 | 0.038311 | 2.9117
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.534 | 105 | 0.038311 | 4.0227
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.0811 | 74 | 0.038311 | 2.835
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.0811 | 74 | 0.038311 | 2.835
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.4902 | 102 | 0.038311 | 3.9078
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.013818 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.91199 | 66 | 0.037519 | 2.4763
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.012504 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.41263 | 0 | 0.036205 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.012504 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3126 | 0 | 0.036205 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.012504 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.036205 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.70134 | 0 | 0.035013 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80768 | 0 | 0.035013 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.50904 | 0 | 0.035013 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1425 | 0 | 0.035013 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.97283 | 0 | 0.035013 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.99546 | 0 | 0.035013 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5656 | 0 | 0.035013 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20362 | 0 | 0.035013 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0633 | 0 | 0.035013 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79184 | 0 | 0.035013 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71266 | 0 | 0.035013 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.81446 | 0 | 0.035013 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.73302 | 0 | 0.035013 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1425 | 0 | 0.035013 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0973 | 0 | 0.035013 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1651 | 0 | 0.035013 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.85971 | 0 | 0.035013 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.90496 | 0 | 0.035013 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.90496 | 0 | 0.035013 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9344 | 0 | 0.035013 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.010707 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7602 | 0 | 0.034408 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.010707 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10707 | 0 | 0.034408 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.010228 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1353 | 0 | 0.033929 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.010228 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1353 | 0 | 0.033929 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.010228 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2171 | 0 | 0.033929 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.010228 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.12 | 0 | 0.033929 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.008495 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39162 | 0 | 0.032196 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.008431 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.4886 | 651 | 0.032132 | 20.9182
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.008431 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.7551 | 564 | 0.032132 | 18.1227
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.008431 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.0586 | 600 | 0.032132 | 19.2795
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.008416 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3718 | 0 | 0.032117 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.008416 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3718 | 0 | 0.032117 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.008416 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.0619 | 0 | 0.032117 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.008236 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27179 | 0 | 0.031937 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.008157 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.3133 | 161 | 0.031858 | 5.1292
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.008157 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.3541 | 166 | 0.031858 | 5.2885
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.008157 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.0229 | 248 | 0.031858 | 7.9009
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.008157 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 4.4537 | 546 | 0.031858 | 17.3947
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.008157 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 5.245 | 0 | 0.031858 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.008157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.10604 | 13 | 0.031858 | 0.41416
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.007245 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23184 | 0 | 0.030946 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.007245 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21735 | 0 | 0.030946 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.007245 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72667 | 0 | 0.030946 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.007245 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.67306 | 0 | 0.030946 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.007245 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.74406 | 0 | 0.030946 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.007245 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.73899 | 0 | 0.030946 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.007241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.51266 | 0 | 0.030942 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.007241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.48297 | 0 | 0.030942 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.007241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.38377 | 0 | 0.030942 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1093 | 0 | 0.030942 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1115 | 0 | 0.030942 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1028 | 0 | 0.030942 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.69514 | 0 | 0.030942 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7668 | 0 | 0.030942 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.007241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28964 | 0 | 0.030942 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.006867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.34335 | 50 | 0.030568 | 1.5284
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.006575 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.030276 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.56739 | 0 | 0.029936 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.54619 | 0 | 0.029936 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.54244 | 0 | 0.029936 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33981 | 0 | 0.029936 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.076067 | 0 | 0.029936 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.006102 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39663 | 0 | 0.029803 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.006102 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.36612 | 0 | 0.029803 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.006102 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39663 | 0 | 0.029803 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.006102 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39663 | 0 | 0.029803 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.27158 | 46 | 0.029605 | 1.3619
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.27158 | 46 | 0.029605 | 1.3619
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.27158 | 46 | 0.029605 | 1.3619
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.32472 | 55 | 0.029605 | 1.6283
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.32472 | 55 | 0.029605 | 1.6283
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.31882 | 54 | 0.029605 | 1.5987
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.005855 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.45669 | 0 | 0.029556 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.005855 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.4684 | 0 | 0.029556 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.94428 | 0 | 0.029487 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90898 | 0 | 0.029487 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91129 | 0 | 0.029487 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.9084 | 0 | 0.029487 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5564 | 0 | 0.029487 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.005731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20059 | 0 | 0.029432 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.005671 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.068052 | 12 | 0.029372 | 0.35247
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.005671 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.029372 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.005668 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.95789 | 169 | 0.029369 | 4.9634
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.005663 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.93439 | 165 | 0.029364 | 4.8451
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.00566 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.84334 | 0 | 0.029361 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.00566 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.36847 | 0 | 0.029361 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.005647 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.2028 | 213 | 0.029348 | 6.2512
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.005646 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.091465 | 0 | 0.029347 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.005645 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.36128 | 0 | 0.029346 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.005645 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35676 | 0 | 0.029346 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.005645 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.46628 | 0 | 0.029346 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.005645 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.41547 | 0 | 0.029346 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.005643 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.2866 | 228 | 0.029344 | 6.6905
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.005641 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0154 | 0 | 0.029342 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.005641 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.89466 | 0 | 0.029342 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.005641 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.88564 | 0 | 0.029342 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.005557 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39455 | 0 | 0.029258 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.005557 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4001 | 0 | 0.029258 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.005557 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21672 | 0 | 0.029258 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.005557 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16671 | 0 | 0.029258 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.005424 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.73766 | 0 | 0.029125 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.005413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.22735 | 42 | 0.029114 | 1.2228
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.005413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.22735 | 42 | 0.029114 | 1.2228
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.005413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.20569 | 38 | 0.029114 | 1.1064
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.005413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.20569 | 38 | 0.029114 | 1.1064
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.005379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.93057 | 0 | 0.02908 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.005379 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72616 | 0 | 0.02908 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.53716 | 104 | 0.028866 | 3.0021
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.53716 | 104 | 0.028866 | 3.0021
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27891 | 54 | 0.028866 | 1.5588
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27375 | 53 | 0.028866 | 1.5299
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27891 | 54 | 0.028866 | 1.5588
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.2944 | 57 | 0.028866 | 1.6454
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27891 | 54 | 0.028866 | 1.5588
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27891 | 54 | 0.028866 | 1.5588
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.29957 | 58 | 0.028866 | 1.6743
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.29957 | 58 | 0.028866 | 1.6743
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.005083 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 3.736 | 735 | 0.028784 | 21.1566
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17095 | 0 | 0.028729 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17447 | 0 | 0.028729 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16442 | 0 | 0.028729 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23079 | 0 | 0.028729 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.088996 | 0 | 0.028729 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10257 | 0 | 0.028729 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10006 | 0 | 0.028729 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17598 | 0 | 0.028729 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.090504 | 0 | 0.028729 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42939 | 0 | 0.028729 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.74414 | 0 | 0.028729 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.004958 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.059496 | 12 | 0.028659 | 0.34391
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.00487 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.02435 | 0 | 0.028571 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.00487 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10227 | 0 | 0.028571 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.31642 | 0 | 0.028569 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32129 | 0 | 0.028569 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34076 | 0 | 0.028569 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30668 | 0 | 0.028569 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30182 | 0 | 0.028569 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.50627 | 0 | 0.028569 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28721 | 0 | 0.028569 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.004864 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.058368 | 12 | 0.028565 | 0.34279
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.004858 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 3.6095 | 743 | 0.028559 | 21.2197
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.004817 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.75627 | 0 | 0.028518 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.00479 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.82388 | 172 | 0.028491 | 4.9005
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.00479 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.82388 | 172 | 0.028491 | 4.9005
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.00479 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.82388 | 172 | 0.028491 | 4.9005
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.004631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75393 | 0 | 0.028332 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.004631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.74744 | 0 | 0.028332 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.004631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.73587 | 0 | 0.028332 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.004631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2467 | 0 | 0.028332 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.004575 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.8209 | 398 | 0.028276 | 11.254
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.25077 | 56 | 0.028179 | 1.5781
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.2642 | 59 | 0.028179 | 1.6626
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.25077 | 56 | 0.028179 | 1.5781
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.25077 | 56 | 0.028179 | 1.5781
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.2642 | 59 | 0.028179 | 1.6626
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.25077 | 56 | 0.028179 | 1.5781
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.00354 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.61242 | 0 | 0.027241 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.00354 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.55224 | 0 | 0.027241 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.00354 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.54516 | 0 | 0.027241 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.00354 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.54516 | 0 | 0.027241 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.00354 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57348 | 0 | 0.027241 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023701 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023701 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023701 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023701 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023701 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023701 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023701 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023701 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 2.9319 | 100 | 0.0005252 | 0.05252
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.01558 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.013214 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.028794 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.028794 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.00483 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.23184 | 48 | -0.033624 | -1.6139
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.00483 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.22218 | 46 | -0.033624 | -1.5467
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.00483 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.50715 | 105 | -0.033624 | -3.5305
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.005274 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.81325 | 0 | -0.034068 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.005274 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.82274 | 0 | -0.034068 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.005274 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.82274 | 0 | -0.034068 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.005274 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.0041 | 0 | -0.034068 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.00548 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.17536 | 0 | -0.034274 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.005492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.034286 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.005492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.034286 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.005492 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.093364 | 17 | -0.034286 | -0.58286
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.005492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.034286 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.005492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.034286 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.006942 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.2141 | 463 | -0.035736 | -16.5457
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.01085 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.6275 | 150 | -0.039644 | -5.9466
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.012844 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.9816 | 855 | -0.041638 | -35.6003
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.012844 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.9816 | 855 | -0.041638 | -35.6003
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.012844 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9561 | 152.3 | -0.041638 | -6.3414
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.012844 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9651 | 153 | -0.041638 | -6.3706
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.014666 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.04346 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.01534 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.6862 | 827 | -0.044134 | -36.4986
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.01534 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.5635 | 819 | -0.044134 | -36.1456
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.018636 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.04743 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.018636 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.04743 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.018723 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5727 | 84 | -0.047517 | -3.9914
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.018848 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4419 | 76.5 | -0.047642 | -3.6446
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.018977 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5182 | 80 | -0.047771 | -3.8217
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.019732 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9598 | 150 | -0.048526 | -7.2789
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.019732 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9598 | 150 | -0.048526 | -7.2789
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.019751 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5801 | 80 | -0.048545 | -3.8836
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.019755 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5804 | 80 | -0.048549 | -3.8839
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.019788 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4841 | 75 | -0.048582 | -3.6436
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.019788 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.583 | 80 | -0.048582 | -3.8865
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.019788 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.79152 | 40 | -0.048582 | -1.9433
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.019819 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.1887 | 615 | -0.048613 | -29.8969
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.019819 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -11.6338 | 587 | -0.048613 | -28.5357
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.019939 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5951 | 80 | -0.048733 | -3.8986
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.019939 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5951 | 80 | -0.048733 | -3.8986
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.02023 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0487 | 150.7 | -0.049024 | -7.3879
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.02023 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0547 | 151 | -0.049024 | -7.4026
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.02023 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5888 | 177.4 | -0.049024 | -8.6968
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.020359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0844 | 151.5 | -0.049153 | -7.4466
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.020359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.1007 | 152.3 | -0.049153 | -7.486
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.020359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.6137 | 177.5 | -0.049153 | -8.7246
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.0205 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.0984 | 0 | -0.049294 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4424 | 66 | -0.050649 | -3.3428
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4206 | 65 | -0.050649 | -3.2922
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4643 | 67 | -0.050649 | -3.3935
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4643 | 67 | -0.050649 | -3.3935
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4643 | 67 | -0.050649 | -3.3935
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.021855 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.050649 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.021855 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.050649 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.021865 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7061 | 169.5 | -0.050659 | -8.5867
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.021875 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.76562 | 35 | -0.050669 | -1.7734
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.021875 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.65625 | 30 | -0.050669 | -1.5201
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.021941 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.2692 | 149 | -0.050735 | -7.5595
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.022024 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.0084 | 182 | -0.050818 | -9.2488
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.022024 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.6596 | 484 | -0.050818 | -24.5958
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.02203 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.1454 | 6.6 | -0.050824 | -0.33544
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.02203 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.75563 | 34.3 | -0.050824 | -1.7433
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.02209 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.1045 | 50 | -0.050884 | -2.5442
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.02211 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.050904 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.022134 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4901 | 112.5 | -0.050928 | -5.7294
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.022134 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.309 | 149.5 | -0.050928 | -7.6137
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.022134 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1169 | 186 | -0.050928 | -9.4726
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.022134 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7477 | 214.5 | -0.050928 | -10.924
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.022215 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.3323 | 150 | -0.051009 | -7.6513
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.6262 | 208.2 | -0.051014 | -10.6211
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.1575 | 142.1 | -0.051014 | -7.2491
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.9419 | 132.4 | -0.051014 | -6.7542
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.0219 | 136 | -0.051014 | -6.9379
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.2663 | 147 | -0.051014 | -7.499
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.6662 | 210 | -0.051014 | -10.7129
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.5557 | 70 | -0.051018 | -3.5712
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.5557 | 70 | -0.051018 | -3.5712
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.0624 | 92.8 | -0.051018 | -4.7345
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.7779 | 80 | -0.051018 | -4.0814
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.7779 | 80 | -0.051018 | -4.0814
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.5558 | 115 | -0.051018 | -5.867
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.022249 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2904 | 58 | -0.051043 | -2.9605
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.022252 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2363 | 100.5 | -0.051046 | -5.1301
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.022301 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7769 | 214.2 | -0.051095 | -10.9445
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.022301 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3005 | 0 | -0.051095 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.022301 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.8991 | 0 | -0.051095 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.022301 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2336 | 0 | -0.051095 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.022301 | north | 1 | N | N | Nnorth | Nnorth | 1 | -8.8981 | 0 | -0.051095 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.022322 | west | 8 | N | N | Nwest | Nwest | 1 | -0.57591 | 0 | -0.051116 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.022448 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.6938 | 120 | -0.051242 | -6.149
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.022456 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.628 | 785 | -0.05125 | -40.2311
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.022456 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.8525 | 795 | -0.05125 | -40.7436
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.022456 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.5157 | 780 | -0.05125 | -39.9748
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.02246 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.6952 | 120 | -0.051254 | -6.1505
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.022485 | west | 8 | N | N | Nwest | Nwest | 1 | -1.5739 | 0 | -0.051279 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.022485 | west | 8 | N | N | Nwest | Nwest | 1 | -1.6504 | 0 | -0.051279 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.022485 | west | 8 | N | N | Nwest | Nwest | 1 | -1.5829 | 0 | -0.051279 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.022506 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7007 | 120 | -0.0513 | -6.156
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.022506 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2439 | 233 | -0.0513 | -11.9529
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.022506 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8305 | 170.2 | -0.0513 | -8.7312
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.022509 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.0645 | 225 | -0.051303 | -11.5431
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.022529 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0552 | 180 | -0.051323 | -9.2381
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.022529 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0552 | 180 | -0.051323 | -9.2381
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.022544 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.3816 | 150 | -0.051338 | -7.7007
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.022544 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.9597 | 220 | -0.051338 | -11.2943
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.022544 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5088 | 200 | -0.051338 | -10.2676
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.022544 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7481 | 121.9 | -0.051338 | -6.2581
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4928 | 66 | -0.051412 | -3.3932
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.5606 | 69 | -0.051412 | -3.5474
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.5606 | 69 | -0.051412 | -3.5474
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.5154 | 67 | -0.051412 | -3.4446
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.5154 | 67 | -0.051412 | -3.4446
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4702 | 65 | -0.051412 | -3.3418
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.022664 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4278 | 63 | -0.051458 | -3.2418
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.022684 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.1984 | 141 | -0.051478 | -7.2584
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.022684 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7221 | 120 | -0.051478 | -6.1773
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.022691 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2464 | 99 | -0.051485 | -5.097
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.022691 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3842 | 61 | -0.051485 | -3.1406
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.022691 | west | 7 | N | N | Nwest | Nwest | 1 | -0.56727 | 0 | -0.051485 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.022691 | west | 7 | N | N | Nwest | Nwest | 1 | -1.037 | 0 | -0.051485 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.022691 | west | 7 | N | N | Nwest | Nwest | 1 | -1.037 | 0 | -0.051485 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.022736 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.842 | 125 | -0.05153 | -6.4412
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.022736 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.842 | 125 | -0.05153 | -6.4412
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.022761 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.9119 | 84 | -0.051555 | -4.3306
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.85721 | 37.5 | -0.051653 | -1.937
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4573 | 107.5 | -0.051653 | -5.5527
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.086 | 135 | -0.051653 | -6.9731
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7202 | 119 | -0.051653 | -6.1467
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4002 | 105 | -0.051653 | -5.4235
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.8401 | 80.5 | -0.051653 | -4.1581
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.022862 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7782 | 209 | -0.051656 | -10.7961
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.022862 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.892 | 126.5 | -0.051656 | -6.5345
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.022862 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.6926 | 249 | -0.051656 | -12.8623
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.022862 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5038 | 197 | -0.051656 | -10.1762
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.022924 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4386 | 150 | -0.051718 | -7.7577
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.022924 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3153 | 101 | -0.051718 | -5.2235
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.023071 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4606 | 150 | -0.051865 | -7.7797
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.023393 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4036 | 60 | -0.052187 | -3.1312
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.023528 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.4112 | 400 | -0.052322 | -20.9287
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.023529 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.5528 | 236 | -0.052323 | -12.3482
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.798 | 161 | -0.052384 | -8.4338
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8688 | 164 | -0.052384 | -8.5909
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8688 | 164 | -0.052384 | -8.5909
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.7663 | 414 | -0.052384 | -21.6869
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8216 | 162 | -0.052384 | -8.4862
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.798 | 161 | -0.052384 | -8.4338
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8452 | 163 | -0.052384 | -8.5386
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.6483 | 409 | -0.052384 | -21.425
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.02374 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.9171 | 165 | -0.052534 | -8.6681
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.023842 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -9.2507 | 388 | -0.052636 | -20.4227
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.023842 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -12.2786 | 515 | -0.052636 | -27.1074
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.023898 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.47796 | 20 | -0.052692 | -1.0538
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.023898 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.59745 | 25 | -0.052692 | -1.3173
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.023898 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.97982 | 41 | -0.052692 | -2.1604
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.023906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.3395 | 558 | -0.0527 | -29.4065
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.023906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.8416 | 579 | -0.0527 | -30.5132
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.023906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -19.316 | 808 | -0.0527 | -42.5814
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.023911 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.052705 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.023911 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.052705 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.023931 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.8905 | 79 | -0.052725 | -4.1653
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.023931 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.5367 | 106 | -0.052725 | -5.5888
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.023931 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.4939 | 146 | -0.052725 | -7.6978
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.023931 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.8188 | 76 | -0.052725 | -4.0071
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.023937 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.7953 | 0 | -0.052731 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.023937 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.9054 | 0 | -0.052731 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.023937 | north | 8 | N | N | Nnorth | Nnorth | 1 | -2.116 | 0 | -0.052731 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8318 | 160 | -0.052743 | -8.4388
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.736 | 156 | -0.052743 | -8.2279
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.694 | 196 | -0.052743 | -10.3376
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.736 | 156 | -0.052743 | -8.2279
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.76 | 157 | -0.052743 | -8.2806
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.7419 | 198 | -0.052743 | -10.4431
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.023958 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.95832 | 40 | -0.052752 | -2.1101
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.02396 | west | 4 | Y | N | Ywest | Nwest | 1 | -15.5668 | 649.7 | -0.052754 | -34.2741
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.023972 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.8696 | 370 | -0.052766 | -19.5233
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3561 | 0 | -0.052766 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3801 | 0 | -0.052766 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.4073 | 0 | -0.052766 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.428 | 0 | -0.052766 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.452 | 0 | -0.052766 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.4313 | 0 | -0.052766 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.024036 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -4.0861 | 170 | -0.05283 | -8.9811
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.024036 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -12.4987 | 520 | -0.05283 | -27.4715
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.024085 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.9634 | 0 | -0.052879 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.024085 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.9634 | 0 | -0.052879 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.024155 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.052949 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.024202 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.052996 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.024314 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.8691 | 118 | -0.053108 | -6.2667
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.024314 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.7961 | 115 | -0.053108 | -6.1074
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.024314 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -13.5186 | 556 | -0.053108 | -29.5279
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.024407 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.933 | 366 | -0.053201 | -19.4715
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.024604 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4762 | 60 | -0.053398 | -3.2039
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.024604 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.5501 | 63 | -0.053398 | -3.3641
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.024609 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.49218 | 20 | -0.053403 | -1.0681
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.024609 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.49218 | 20 | -0.053403 | -1.0681
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.024609 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.49218 | 20 | -0.053403 | -1.0681
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.024609 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.41835 | 17 | -0.053403 | -0.90785
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.02476 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.051 | 204 | -0.053554 | -10.925
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.02476 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.9768 | 201 | -0.053554 | -10.7643
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.02476 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.9919 | 242 | -0.053554 | -12.96
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.024977 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.405 | 216.4 | -0.053771 | -11.636
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.024977 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.3975 | 216.1 | -0.053771 | -11.6199
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.025112 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.8251 | 112.5 | -0.053906 | -6.0644
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.025152 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -6.0868 | 242 | -0.053946 | -13.0549
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.025192 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053986 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.025192 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053986 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.025192 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053986 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.025271 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.982 | 395 | -0.054065 | -21.3556
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.025271 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -10.9929 | 435 | -0.054065 | -23.5182
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.025279 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -10.9964 | 435 | -0.054073 | -23.5217
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.025666 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.5772 | 217.3 | -0.05446 | -11.8341
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.025666 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.2615 | 205 | -0.05446 | -11.1643
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.025666 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.9914 | 272.4 | -0.05446 | -14.8348
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.025724 | north | 3 | N | N | Nnorth | Nnorth | 1 | -29.7627 | 0 | -0.054518 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.025724 | north | 3 | N | N | Nnorth | Nnorth | 1 | -29.7884 | 0 | -0.054518 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.025729 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.7633 | 224 | -0.054523 | -12.2131
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.025729 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.8148 | 226 | -0.054523 | -12.3222
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.025729 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4545 | 212 | -0.054523 | -11.5588
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.025729 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4288 | 211 | -0.054523 | -11.5043
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.025939 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.054733 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.026253 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.5609 | 288 | -0.055047 | -15.8535
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.026253 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8592 | 147 | -0.055047 | -8.0919
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.026253 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8592 | 147 | -0.055047 | -8.0919
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.026427 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.9196 | 224 | -0.055221 | -12.3695
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.026615 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.31938 | 0 | -0.055409 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.026615 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.31938 | 0 | -0.055409 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.026664 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -3.1997 | 120 | -0.055458 | -6.6549
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.027019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.2957 | 196 | -0.055813 | -10.9393
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.027019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9991 | 111 | -0.055813 | -6.1952
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.027625 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.49725 | 18 | -0.056419 | -1.0155
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.027625 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.49725 | 18 | -0.056419 | -1.0155
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.027625 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.0497 | 38 | -0.056419 | -2.1439
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.028895 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.0227 | 70 | -0.057689 | -4.0382
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.028895 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.9938 | 69 | -0.057689 | -3.9805
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.028895 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.9938 | 69 | -0.057689 | -3.9805
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.028895 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.9649 | 68 | -0.057689 | -3.9228
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.02975 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.1717 | 73 | -0.058544 | -4.2737
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.02975 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.5402 | 119 | -0.058544 | -6.9667
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.02975 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -6.0987 | 205 | -0.058544 | -12.0015
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.02975 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -3.0345 | 102 | -0.058544 | -5.9715
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.02975 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.856 | 96 | -0.058544 | -5.6202
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.030835 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.059629 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.030835 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -24.2671 | 787 | -0.059629 | -46.9279
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.031539 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.8923 | 60 | -0.060333 | -3.62
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.032115 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.3953 | 168 | -0.060909 | -10.2327
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.032115 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.8904 | 90 | -0.060909 | -5.4818
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.059587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.1947 | 255 | -0.088381 | -22.5371
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.059587 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.8785 | 149 | -0.088381 | -13.1687
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.059587 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -9.1168 | 153 | -0.088381 | -13.5223
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.074008 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.1101 | 0 | -0.1028 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.074008 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.1101 | 0 | -0.1028 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.083518 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.5277 | 150 | -0.11231 | -16.8468
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.083518 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.6814 | 80 | -0.11231 | -8.9849

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:173 CRAWFORD 177 BOSQUE C:THOUSE__5-AEP_PEC__5 C:LAKE_CRK1_5-AEP_SS__59 [3405 - 3412] and [3409 - 3414] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.083518 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -12.5277 | 150 | -0.11231 | -16.8468 | 150 | 16.8468
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.083518 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.6814 | 80 | -0.11231 | -8.9849 | 230 | 25.8317
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.074008 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.1101 | 0 | -0.1028 | 0 | 230 | 25.8317
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.074008 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.1101 | 0 | -0.1028 | 0 | 230 | 25.8317 | Weighted Shift Factors
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.059587 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -15.1947 | 255 | -0.088381 | -22.5371 |  |  | North | -0.023701
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.059587 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.8785 | 149 | -0.088381 | -13.1687 |  |  | South | 0.028794
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.059587 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -9.1168 | 153 | -0.088381 | -13.5223 |  |  |  | -0.052495
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.032115 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.3953 | 168 | -0.060909 | -10.2327
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.032115 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.8904 | 90 | -0.060909 | -5.4818 |  |  | Line Rating | 226.45
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.031539 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.8923 | 0 | -0.060333 | 0 |  |  | Conc Gen | 230
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.030835 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.059629 | 0 |  |  | Weighted Imp. | 25.8317
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.030835 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -24.2671 | 787 | -0.059629 | -46.9279 |  |  | PTDF | 0.11231
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.02975 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.1717 | 73 | -0.058544 | -4.2737
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.02975 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.5402 | 119 | -0.058544 | -6.9667 |  |  | Concentration | -2.1395
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.02975 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -6.0987 | 205 | -0.058544 | -12.0015
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.02975 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -3.0345 | 102 | -0.058544 | -5.9715
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.02975 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.856 | 96 | -0.058544 | -5.6202
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.028895 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.0227 | 70 | -0.057689 | -4.0382
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.028895 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.9938 | 69 | -0.057689 | -3.9805
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.028895 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.9938 | 69 | -0.057689 | -3.9805
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.028895 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.9649 | 68 | -0.057689 | -3.9228
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.027625 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.49725 | 18 | -0.056419 | -1.0155
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.027625 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.49725 | 18 | -0.056419 | -1.0155
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.027625 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.0497 | 38 | -0.056419 | -2.1439
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.027019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.2957 | 196 | -0.055813 | -10.9393
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.027019 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9991 | 111 | -0.055813 | -6.1952
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.026664 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -3.1997 | 0 | -0.055458 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.026615 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.31938 | 0 | -0.055409 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.026615 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.31938 | 0 | -0.055409 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.026427 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.9196 | 224 | -0.055221 | -12.3695
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.026253 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.5609 | 288 | -0.055047 | -15.8535
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.026253 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8592 | 147 | -0.055047 | -8.0919
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.026253 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8592 | 147 | -0.055047 | -8.0919
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.025939 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.054733 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.025729 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.7633 | 224 | -0.054523 | -12.2131
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.025729 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.8148 | 226 | -0.054523 | -12.3222
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.025729 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4545 | 212 | -0.054523 | -11.5588
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.025729 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4288 | 211 | -0.054523 | -11.5043
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.025724 | north | 3 | N | N | Nnorth | Nnorth | 1 | -29.7627 | 0 | -0.054518 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.025724 | north | 3 | N | N | Nnorth | Nnorth | 1 | -29.7884 | 0 | -0.054518 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.025666 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.5772 | 217.3 | -0.05446 | -11.8341
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.025666 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.2615 | 205 | -0.05446 | -11.1643
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.025666 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.9914 | 272.4 | -0.05446 | -14.8348
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.025279 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -10.9964 | 435 | -0.054073 | -23.5217
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.025271 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.982 | 395 | -0.054065 | -21.3556
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.025271 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -10.9929 | 435 | -0.054065 | -23.5182
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.025192 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053986 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.025192 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053986 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.025192 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.053986 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.025152 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -6.0868 | 242 | -0.053946 | -13.0549
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.025112 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.8251 | 0 | -0.053906 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.024977 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.405 | 216.4 | -0.053771 | -11.636
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.024977 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.3975 | 216.1 | -0.053771 | -11.6199
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.02476 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.051 | 204 | -0.053554 | -10.925
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.02476 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.9768 | 201 | -0.053554 | -10.7643
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.02476 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.9919 | 242 | -0.053554 | -12.96
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.024609 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.49218 | 20 | -0.053403 | -1.0681
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.024609 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.49218 | 20 | -0.053403 | -1.0681
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.024609 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.49218 | 20 | -0.053403 | -1.0681
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.024609 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.41835 | 17 | -0.053403 | -0.90785
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.024604 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4762 | 60 | -0.053398 | -3.2039
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.024604 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.5501 | 63 | -0.053398 | -3.3641
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.024407 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.933 | 366 | -0.053201 | -19.4715
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.024314 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.8691 | 118 | -0.053108 | -6.2667
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.024314 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.7961 | 115 | -0.053108 | -6.1074
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.024314 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -13.5186 | 556 | -0.053108 | -29.5279
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.024202 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.052996 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.024155 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.052949 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.024085 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.9634 | 0 | -0.052879 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.024085 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.9634 | 0 | -0.052879 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.024036 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -4.0861 | 170 | -0.05283 | -8.9811
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.024036 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -12.4987 | 520 | -0.05283 | -27.4715
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.023972 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.8696 | 370 | -0.052766 | -19.5233
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3561 | 0 | -0.052766 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3801 | 0 | -0.052766 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.4073 | 0 | -0.052766 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.428 | 0 | -0.052766 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.452 | 0 | -0.052766 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.023972 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.4313 | 0 | -0.052766 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.02396 | west | 4 | Y | N | Ywest | Nwest | 1 | -15.5668 | 0 | -0.052754 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.023958 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.95832 | 40 | -0.052752 | -2.1101
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8318 | 160 | -0.052743 | -8.4388
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.736 | 156 | -0.052743 | -8.2279
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.694 | 196 | -0.052743 | -10.3376
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.736 | 156 | -0.052743 | -8.2279
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.76 | 157 | -0.052743 | -8.2806
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.023949 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.7419 | 198 | -0.052743 | -10.4431
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.023937 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.7953 | 0 | -0.052731 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.023937 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.9054 | 0 | -0.052731 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.023937 | north | 8 | N | N | Nnorth | Nnorth | 1 | -2.116 | 0 | -0.052731 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.023931 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.8905 | 79 | -0.052725 | -4.1653
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.023931 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.5367 | 106 | -0.052725 | -5.5888
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.023931 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.4939 | 146 | -0.052725 | -7.6978
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.023931 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.8188 | 76 | -0.052725 | -4.0071
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.023911 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.052705 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.023911 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.052705 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.023906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.3395 | 0 | -0.0527 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.023906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.8416 | 0 | -0.0527 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.023906 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -19.316 | 0 | -0.0527 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.023898 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.47796 | 20 | -0.052692 | -1.0538
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.023898 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.59745 | 25 | -0.052692 | -1.3173
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.023898 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.97982 | 41 | -0.052692 | -2.1604
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.023842 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -9.2507 | 388 | -0.052636 | -20.4227
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.023842 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -12.2786 | 515 | -0.052636 | -27.1074
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.02374 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.9171 | 0 | -0.052534 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.798 | 161 | -0.052384 | -8.4338
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8688 | 164 | -0.052384 | -8.5909
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8688 | 164 | -0.052384 | -8.5909
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.7663 | 414 | -0.052384 | -21.6869
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8216 | 162 | -0.052384 | -8.4862
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.798 | 161 | -0.052384 | -8.4338
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8452 | 163 | -0.052384 | -8.5386
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.02359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.6483 | 409 | -0.052384 | -21.425
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.023529 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.5528 | 0 | -0.052323 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.023528 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.4112 | 0 | -0.052322 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.023393 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4036 | 0 | -0.052187 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.023071 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4606 | 0 | -0.051865 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.022924 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4386 | 0 | -0.051718 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.022924 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3153 | 0 | -0.051718 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.022862 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7782 | 0 | -0.051656 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.022862 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.892 | 0 | -0.051656 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.022862 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.6926 | 0 | -0.051656 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.022862 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5038 | 0 | -0.051656 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.85721 | 0 | -0.051653 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4573 | 0 | -0.051653 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.086 | 0 | -0.051653 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7202 | 0 | -0.051653 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4002 | 0 | -0.051653 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.022859 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.8401 | 0 | -0.051653 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.022761 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.9119 | 0 | -0.051555 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.022736 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.842 | 0 | -0.05153 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.022736 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.842 | 0 | -0.05153 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.022691 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2464 | 0 | -0.051485 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.022691 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3842 | 0 | -0.051485 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.022691 | west | 7 | N | N | Nwest | Nwest | 1 | -0.56727 | 0 | -0.051485 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.022691 | west | 7 | N | N | Nwest | Nwest | 1 | -1.037 | 0 | -0.051485 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.022691 | west | 7 | N | N | Nwest | Nwest | 1 | -1.037 | 0 | -0.051485 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.022684 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.1984 | 0 | -0.051478 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.022684 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7221 | 0 | -0.051478 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.022664 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4278 | 0 | -0.051458 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4928 | 66 | -0.051412 | -3.3932
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.5606 | 69 | -0.051412 | -3.5474
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.5606 | 69 | -0.051412 | -3.5474
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.5154 | 67 | -0.051412 | -3.4446
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.5154 | 67 | -0.051412 | -3.4446
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.022618 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4702 | 65 | -0.051412 | -3.3418
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.022544 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.3816 | 0 | -0.051338 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.022544 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.9597 | 0 | -0.051338 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.022544 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5088 | 0 | -0.051338 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.022544 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7481 | 0 | -0.051338 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.022529 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0552 | 0 | -0.051323 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.022529 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0552 | 0 | -0.051323 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.022509 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.0645 | 0 | -0.051303 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.022506 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7007 | 0 | -0.0513 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.022506 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2439 | 0 | -0.0513 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.022506 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8305 | 0 | -0.0513 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.022485 | west | 8 | N | N | Nwest | Nwest | 1 | -1.5739 | 0 | -0.051279 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.022485 | west | 8 | N | N | Nwest | Nwest | 1 | -1.6504 | 0 | -0.051279 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.022485 | west | 8 | N | N | Nwest | Nwest | 1 | -1.5829 | 0 | -0.051279 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.02246 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.6952 | 0 | -0.051254 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.022456 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.628 | 0 | -0.05125 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.022456 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.8525 | 0 | -0.05125 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.022456 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.5157 | 0 | -0.05125 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.022448 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.6938 | 0 | -0.051242 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.022322 | west | 8 | N | N | Nwest | Nwest | 1 | -0.57591 | 0 | -0.051116 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.022301 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.3005 | 0 | -0.051095 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.022301 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.8991 | 0 | -0.051095 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.022301 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2336 | 0 | -0.051095 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.022301 | north | 1 | N | N | Nnorth | Nnorth | 1 | -8.8981 | 0 | -0.051095 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.022301 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7769 | 0 | -0.051095 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.022252 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2363 | 0 | -0.051046 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.022249 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2904 | 0 | -0.051043 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.5557 | 70 | -0.051018 | -3.5712
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.5557 | 70 | -0.051018 | -3.5712
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.0624 | 92.8 | -0.051018 | -4.7345
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.7779 | 80 | -0.051018 | -4.0814
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.7779 | 80 | -0.051018 | -4.0814
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.022224 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.5558 | 115 | -0.051018 | -5.867
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.6262 | 208.2 | -0.051014 | -10.6211
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.1575 | 142.1 | -0.051014 | -7.2491
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.9419 | 132.4 | -0.051014 | -6.7542
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.0219 | 136 | -0.051014 | -6.9379
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.2663 | 147 | -0.051014 | -7.499
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.02222 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.6662 | 210 | -0.051014 | -10.7129
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.022215 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.3323 | 0 | -0.051009 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.022134 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4901 | 0 | -0.050928 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.022134 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.309 | 0 | -0.050928 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.022134 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1169 | 0 | -0.050928 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.022134 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7477 | 0 | -0.050928 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.02211 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.050904 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.02209 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.1045 | 0 | -0.050884 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.02203 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.1454 | 0 | -0.050824 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.02203 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.75563 | 0 | -0.050824 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.022024 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.0084 | 182 | -0.050818 | -9.2488
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.022024 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.6596 | 484 | -0.050818 | -24.5958
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.021941 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.2692 | 0 | -0.050735 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.021875 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.76562 | 0 | -0.050669 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.021875 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.65625 | 0 | -0.050669 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.021865 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.7061 | 0 | -0.050659 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4424 | 66 | -0.050649 | -3.3428
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4206 | 65 | -0.050649 | -3.2922
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4643 | 67 | -0.050649 | -3.3935
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4643 | 67 | -0.050649 | -3.3935
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.021855 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.4643 | 67 | -0.050649 | -3.3935
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.021855 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.050649 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.021855 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.050649 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.0205 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.0984 | 0 | -0.049294 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.020359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0844 | 151.5 | -0.049153 | -7.4466
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.020359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.1007 | 152.3 | -0.049153 | -7.486
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.020359 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.6137 | 177.5 | -0.049153 | -8.7246
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.02023 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0487 | 150.7 | -0.049024 | -7.3879
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.02023 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0547 | 151 | -0.049024 | -7.4026
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.02023 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5888 | 177.4 | -0.049024 | -8.6968
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.019939 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5951 | 0 | -0.048733 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.019939 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5951 | 0 | -0.048733 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.019819 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.1887 | 0 | -0.048613 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.019819 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -11.6338 | 0 | -0.048613 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.019788 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4841 | 0 | -0.048582 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.019788 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.583 | 0 | -0.048582 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.019788 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.79152 | 0 | -0.048582 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.019755 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5804 | 0 | -0.048549 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.019751 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5801 | 0 | -0.048545 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.019732 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9598 | 0 | -0.048526 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.019732 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9598 | 0 | -0.048526 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.018977 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5182 | 0 | -0.047771 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.018848 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4419 | 0 | -0.047642 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.018723 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.5727 | 0 | -0.047517 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.018636 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.04743 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.018636 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.04743 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.01534 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.6862 | 0 | -0.044134 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.01534 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.5635 | 0 | -0.044134 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.014666 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.04346 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.012844 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.9816 | 0 | -0.041638 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.012844 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.9816 | 0 | -0.041638 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.012844 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9561 | 0 | -0.041638 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.012844 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9651 | 0 | -0.041638 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.01085 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.6275 | 0 | -0.039644 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.006942 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.2141 | 0 | -0.035736 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.005492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.034286 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.005492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.034286 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.005492 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.093364 | 17 | -0.034286 | -0.58286
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.005492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.034286 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.005492 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.034286 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.00548 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.17536 | 0 | -0.034274 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.005274 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.81325 | 0 | -0.034068 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.005274 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.82274 | 0 | -0.034068 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.005274 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.82274 | 0 | -0.034068 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.005274 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.0041 | 0 | -0.034068 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.00483 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.23184 | 48 | -0.033624 | -1.6139
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.00483 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.22218 | 46 | -0.033624 | -1.5467
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.00483 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.50715 | 105 | -0.033624 | -3.5305
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.028794 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.028794 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.01558 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.013214 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 2.9319 | 0 | 0.0005252 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023701 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023701 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023701 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023701 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023701 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023701 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023701 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023701 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.00354 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.61242 | 0 | 0.027241 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.00354 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.55224 | 0 | 0.027241 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.00354 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.54516 | 0 | 0.027241 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.00354 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.54516 | 0 | 0.027241 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.00354 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57348 | 0 | 0.027241 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.25077 | 56 | 0.028179 | 1.5781
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.2642 | 59 | 0.028179 | 1.6626
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.25077 | 56 | 0.028179 | 1.5781
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.25077 | 56 | 0.028179 | 1.5781
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.2642 | 59 | 0.028179 | 1.6626
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.004478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.25077 | 56 | 0.028179 | 1.5781
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.004575 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.8209 | 398 | 0.028276 | 11.254
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.004631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75393 | 0 | 0.028332 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.004631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.74744 | 0 | 0.028332 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.004631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.73587 | 0 | 0.028332 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.004631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2467 | 0 | 0.028332 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.00479 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.82388 | 172 | 0.028491 | 4.9005
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.00479 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.82388 | 172 | 0.028491 | 4.9005
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.00479 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.82388 | 172 | 0.028491 | 4.9005
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.004817 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.75627 | 0 | 0.028518 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.004858 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 3.6095 | 743 | 0.028559 | 21.2197
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.004864 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.058368 | 0 | 0.028565 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.31642 | 0 | 0.028569 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32129 | 0 | 0.028569 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34076 | 0 | 0.028569 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30668 | 0 | 0.028569 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30182 | 0 | 0.028569 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.50627 | 0 | 0.028569 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.004868 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28721 | 0 | 0.028569 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.00487 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.02435 | 0 | 0.028571 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.00487 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10227 | 0 | 0.028571 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.004958 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.059496 | 12 | 0.028659 | 0.34391
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17095 | 0 | 0.028729 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17447 | 0 | 0.028729 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16442 | 0 | 0.028729 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23079 | 0 | 0.028729 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.088996 | 0 | 0.028729 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10257 | 0 | 0.028729 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10006 | 0 | 0.028729 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17598 | 0 | 0.028729 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.090504 | 0 | 0.028729 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42939 | 0 | 0.028729 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.005028 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.74414 | 0 | 0.028729 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.005083 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 3.736 | 735 | 0.028784 | 21.1566
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.53716 | 104 | 0.028866 | 3.0021
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.53716 | 104 | 0.028866 | 3.0021
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27891 | 54 | 0.028866 | 1.5588
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27375 | 53 | 0.028866 | 1.5299
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27891 | 54 | 0.028866 | 1.5588
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.2944 | 57 | 0.028866 | 1.6454
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27891 | 54 | 0.028866 | 1.5588
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27891 | 54 | 0.028866 | 1.5588
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.29957 | 58 | 0.028866 | 1.6743
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.005165 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.29957 | 58 | 0.028866 | 1.6743
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.005379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.93057 | 0 | 0.02908 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.005379 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72616 | 0 | 0.02908 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.005413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.22735 | 42 | 0.029114 | 1.2228
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.005413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.22735 | 42 | 0.029114 | 1.2228
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.005413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.20569 | 38 | 0.029114 | 1.1064
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.005413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.20569 | 38 | 0.029114 | 1.1064
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.005424 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.73766 | 0 | 0.029125 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.005557 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39455 | 0 | 0.029258 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.005557 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4001 | 0 | 0.029258 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.005557 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21672 | 0 | 0.029258 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.005557 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16671 | 0 | 0.029258 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.005641 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0154 | 0 | 0.029342 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.005641 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.89466 | 0 | 0.029342 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.005641 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.88564 | 0 | 0.029342 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.005643 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.2866 | 228 | 0.029344 | 6.6905
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.005645 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.36128 | 0 | 0.029346 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.005645 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35676 | 0 | 0.029346 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.005645 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.46628 | 0 | 0.029346 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.005645 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.41547 | 0 | 0.029346 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.005646 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.091465 | 0 | 0.029347 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.005647 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.2028 | 213 | 0.029348 | 6.2512
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.00566 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.84334 | 0 | 0.029361 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.00566 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.36847 | 0 | 0.029361 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.005663 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.93439 | 165 | 0.029364 | 4.8451
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.005668 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.95789 | 169 | 0.029369 | 4.9634
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.005671 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.068052 | 12 | 0.029372 | 0.35247
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.005671 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.029372 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.005731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20059 | 0 | 0.029432 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.94428 | 0 | 0.029487 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90898 | 0 | 0.029487 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91129 | 0 | 0.029487 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.9084 | 0 | 0.029487 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.005786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5564 | 0 | 0.029487 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.005855 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.45669 | 0 | 0.029556 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.005855 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.4684 | 0 | 0.029556 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.27158 | 46 | 0.029605 | 1.3619
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.27158 | 46 | 0.029605 | 1.3619
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.27158 | 46 | 0.029605 | 1.3619
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.32472 | 55 | 0.029605 | 1.6283
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.32472 | 55 | 0.029605 | 1.6283
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.005904 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.31882 | 54 | 0.029605 | 1.5987
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.006102 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39663 | 0 | 0.029803 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.006102 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.36612 | 0 | 0.029803 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.006102 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39663 | 0 | 0.029803 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.006102 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.39663 | 0 | 0.029803 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.56739 | 0 | 0.029936 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.54619 | 0 | 0.029936 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.54244 | 0 | 0.029936 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33981 | 0 | 0.029936 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.006235 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.076067 | 0 | 0.029936 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.006575 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.030276 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.006867 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.34335 | 50 | 0.030568 | 1.5284
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.007241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.51266 | 0 | 0.030942 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.007241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.48297 | 0 | 0.030942 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.007241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.38377 | 0 | 0.030942 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1093 | 0 | 0.030942 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1115 | 0 | 0.030942 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1028 | 0 | 0.030942 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.69514 | 0 | 0.030942 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.007241 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7668 | 0 | 0.030942 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.007241 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28964 | 0 | 0.030942 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.007245 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72667 | 0 | 0.030946 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.007245 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.67306 | 0 | 0.030946 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.007245 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.74406 | 0 | 0.030946 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.007245 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.73899 | 0 | 0.030946 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.007245 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23184 | 0 | 0.030946 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.007245 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21735 | 0 | 0.030946 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.008157 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.3133 | 161 | 0.031858 | 5.1292
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.008157 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.3541 | 166 | 0.031858 | 5.2885
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.008157 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.0229 | 248 | 0.031858 | 7.9009
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.008157 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 4.4537 | 546 | 0.031858 | 17.3947
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.008157 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 5.245 | 0 | 0.031858 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.008157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.10604 | 13 | 0.031858 | 0.41416
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.008236 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27179 | 0 | 0.031937 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.008416 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3718 | 0 | 0.032117 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.008416 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3718 | 0 | 0.032117 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.008416 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.0619 | 0 | 0.032117 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.008431 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.4886 | 0 | 0.032132 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.008431 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.7551 | 0 | 0.032132 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.008431 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.0586 | 0 | 0.032132 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.008495 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39162 | 0 | 0.032196 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.010228 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1353 | 0 | 0.033929 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.010228 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1353 | 0 | 0.033929 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.010228 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2171 | 0 | 0.033929 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.010228 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.12 | 0 | 0.033929 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.010707 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7602 | 0 | 0.034408 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.010707 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10707 | 0 | 0.034408 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.70134 | 0 | 0.035013 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80768 | 0 | 0.035013 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.50904 | 0 | 0.035013 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1425 | 0 | 0.035013 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.97283 | 0 | 0.035013 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.99546 | 0 | 0.035013 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5656 | 0 | 0.035013 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20362 | 0 | 0.035013 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0633 | 0 | 0.035013 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79184 | 0 | 0.035013 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71266 | 0 | 0.035013 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.81446 | 0 | 0.035013 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.73302 | 0 | 0.035013 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1425 | 0 | 0.035013 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0973 | 0 | 0.035013 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1651 | 0 | 0.035013 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.85971 | 0 | 0.035013 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.90496 | 0 | 0.035013 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.90496 | 0 | 0.035013 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.011312 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9344 | 0 | 0.035013 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.012504 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.41263 | 0 | 0.036205 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.012504 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3126 | 0 | 0.036205 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.012504 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.036205 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.013818 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.91199 | 66 | 0.037519 | 2.4763
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1104 | 76 | 0.038311 | 2.9117
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1104 | 76 | 0.038311 | 2.9117
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.534 | 105 | 0.038311 | 4.0227
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.0811 | 74 | 0.038311 | 2.835
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.0811 | 74 | 0.038311 | 2.835
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.01461 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.4902 | 102 | 0.038311 | 3.9078
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.014699 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 19.5938 | 0 | 0.0384 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.014699 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 19.5203 | 0 | 0.0384 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.016264 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.097584 | 0 | 0.039965 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.017139 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.04084 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.6818 | 0 | 0.044989 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.7243 | 0 | 0.044989 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.6818 | 0 | 0.044989 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.703 | 0 | 0.044989 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.669 | 0 | 0.044989 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.5322 | 0 | 0.044989 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.97925 | 0 | 0.044989 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.59606 | 0 | 0.044989 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.92816 | 0 | 0.044989 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.021288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.5753 | 0 | 0.044989 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.02147 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0306 | 0 | 0.045171 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.61771 | 0 | 0.045762 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15443 | 0 | 0.045762 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.86038 | 0 | 0.045762 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.33092 | 0 | 0.045762 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15443 | 0 | 0.045762 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.33092 | 0 | 0.045762 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.86038 | 0 | 0.045762 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.022061 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.86038 | 0 | 0.045762 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.022148 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.17718 | 0 | 0.045849 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.022309 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.33464 | 0 | 0.04601 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.022309 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.51311 | 0 | 0.04601 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.022491 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.4948 | 22 | 0.046192 | 1.0162
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.022491 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2474 | 11 | 0.046192 | 0.50812
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.022491 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2474 | 11 | 0.046192 | 0.50812
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.022697 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0826 | 47.7 | 0.046398 | 2.2132
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.022697 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.8466 | 37.3 | 0.046398 | 1.7307
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.022697 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0441 | 46 | 0.046398 | 2.1343
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.022697 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0895 | 48 | 0.046398 | 2.2271
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.022749 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.6607 | 0 | 0.04645 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.6092 | 0 | 0.046544 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.495 | 0 | 0.046544 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.2843 | 0 | 0.046544 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.3122 | 0 | 0.046544 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.3579 | 0 | 0.046544 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.022843 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.9011 | 0 | 0.046544 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.022843 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.27412 | 0 | 0.046544 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.57335 | 0 | 0.046635 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.57335 | 0 | 0.046635 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.57335 | 0 | 0.046635 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.36694 | 0 | 0.046635 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.57335 | 0 | 0.046635 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.57335 | 0 | 0.046635 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.57335 | 0 | 0.046635 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.022934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.34401 | 0 | 0.046635 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.022999 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3119 | 144 | 0.0467 | 6.7249
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.022999 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.3238 | 188 | 0.0467 | 8.7797
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.023074 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.7529 | 336 | 0.046775 | 15.7166
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.023074 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.1533 | 180 | 0.046775 | 8.4196
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.023077 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.4223 | 0 | 0.046778 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.023077 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.4292 | 0 | 0.046778 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.023077 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.5308 | 0 | 0.046778 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.023081 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.1546 | 180 | 0.046782 | 8.4208
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.023126 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 7.7241 | 334 | 0.046827 | 15.6404
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.023126 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 7.8628 | 340 | 0.046827 | 15.9213
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.023126 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.1627 | 180 | 0.046827 | 8.4289
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.023126 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.1627 | 180 | 0.046827 | 8.4289
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.023134 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.57835 | 0 | 0.046835 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.023134 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.57835 | 0 | 0.046835 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.023156 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.87993 | 0 | 0.046857 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.023157 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.87997 | 0 | 0.046858 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.023264 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.67466 | 0 | 0.046965 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.1901 | 0 | 0.047 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.95526 | 0 | 0.047 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.88536 | 0 | 0.047 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.44268 | 0 | 0.047 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.1901 | 0 | 0.047 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.83876 | 0 | 0.047 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.0019 | 0 | 0.047 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.51258 | 0 | 0.047 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.4483 | 0 | 0.047 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.1649 | 0 | 0.047 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.2814 | 0 | 0.047 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.023299 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.1649 | 0 | 0.047 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.023313 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.88589 | 38 | 0.047014 | 1.7866
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.023313 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.44994 | 19.3 | 0.047014 | 0.90738
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.023313 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34969 | 15 | 0.047014 | 0.70522
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.023313 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.0957 | 47 | 0.047014 | 2.2097
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.023313 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.047014 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.023353 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3628 | 144 | 0.047054 | 6.7758
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.023353 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.3628 | 144 | 0.047054 | 6.7758
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.023353 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9934 | 171 | 0.047054 | 8.0463
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.023354 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8343 | 207 | 0.047055 | 9.7405
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.023354 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.0608 | 216.7 | 0.047055 | 10.1969
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.023354 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.6517 | 242 | 0.047055 | 11.3874
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.023394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.4272 | 146.5 | 0.047095 | 6.8995
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.023394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.46 | 147.9 | 0.047095 | 6.9654
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.023394 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.0472 | 173 | 0.047095 | 8.1475
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.023642 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2837 | 0 | 0.047343 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.023642 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.26006 | 0 | 0.047343 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.023642 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.2837 | 0 | 0.047343 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.023671 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.047372 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.023879 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.04758 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.024059 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 15.1331 | 0 | 0.04776 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.02427 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.20387 | 8.4 | 0.047971 | 0.40296
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.024358 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.048059 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.02445 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.048151 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.024452 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4452 | 100 | 0.048153 | 4.8153
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.024452 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4452 | 100 | 0.048153 | 4.8153
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.024452 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.048153 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.024452 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.048153 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.024452 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.048153 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.024452 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.048153 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.024575 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.5898 | 24 | 0.048276 | 1.1586
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.024575 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.5898 | 24 | 0.048276 | 1.1586
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.024575 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.56522 | 23 | 0.048276 | 1.1104
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.026167 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 10.3621 | 0 | 0.049868 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.02765 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3318 | 0 | 0.051351 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.027669 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 15.1073 | 0 | 0.05137 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.027669 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 20.7518 | 0 | 0.05137 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.027708 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.6071 | 58 | 0.051409 | 2.9817
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.027708 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.466 | 89 | 0.051409 | 4.5754
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.027708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2192 | 44 | 0.051409 | 2.262
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.027708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2192 | 44 | 0.051409 | 2.262
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.027708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.1914 | 43 | 0.051409 | 2.2106
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.027708 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2469 | 45 | 0.051409 | 2.3134
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.027814 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.3112 | 155 | 0.051515 | 7.9849
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.027814 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7284 | 170 | 0.051515 | 8.7576
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.027814 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.3112 | 155 | 0.051515 | 7.9849
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.027863 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 11.3402 | 407 | 0.051564 | 20.9867
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.027875 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.8259 | 209 | 0.051576 | 10.7795
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.027875 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.021 | 216 | 0.051576 | 11.1405
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.027875 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2822 | 46 | 0.051576 | 2.3725
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.027875 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.3101 | 47 | 0.051576 | 2.4241
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.027875 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2822 | 46 | 0.051576 | 2.3725
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.027875 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2822 | 46 | 0.051576 | 2.3725
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.027906 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 11.4973 | 412 | 0.051607 | 21.2623
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.027906 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 11.1624 | 400 | 0.051607 | 20.643
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.027927 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.841 | 0 | 0.051628 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.027927 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.869 | 0 | 0.051628 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.028002 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051703 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.028002 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051703 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.028002 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051703 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.2018 | 147 | 0.052285 | 7.686
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9446 | 138 | 0.052285 | 7.2154
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.0018 | 140 | 0.052285 | 7.32
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.2018 | 147 | 0.052285 | 7.686
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.2023 | 182 | 0.052285 | 9.516
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.028584 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.6596 | 198 | 0.052285 | 10.3525
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3424 | 0 | 0.05302 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 6.5088 | 0 | 0.05302 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 5.3947 | 0 | 0.05302 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 6.5675 | 0 | 0.05302 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.029319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.3717 | 0 | 0.05302 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.029354 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11742 | 0 | 0.053055 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.029423 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.070615 | 0 | 0.053124 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.029423 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.070615 | 0 | 0.053124 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.029597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.2028 | 142 | 0.053298 | 7.5684
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.029597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.2916 | 145 | 0.053298 | 7.7283
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.029597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.4691 | 151 | 0.053298 | 8.0481
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.029597 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.5831 | 290 | 0.053298 | 15.4566
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.0298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.07152 | 0 | 0.053501 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.0298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.07152 | 0 | 0.053501 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.0298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.08344 | 0 | 0.053501 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.03066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.8648 | 223.9 | 0.054361 | 12.1715
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.03066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.8985 | 225 | 0.054361 | 12.2313
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.03066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.8862 | 224.6 | 0.054361 | 12.2096
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.03066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.9506 | 226.7 | 0.054361 | 12.3237
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.031167 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 13.4953 | 0 | 0.054868 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.031196 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 18.2185 | 0 | 0.054897 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.031196 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 18.5616 | 0 | 0.054897 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.031695 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19017 | 0 | 0.055396 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.031843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5921 | 50 | 0.055544 | 2.7772
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.031843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5921 | 50 | 0.055544 | 2.7772
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.031843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5921 | 50 | 0.055544 | 2.7772
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.031843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5921 | 50 | 0.055544 | 2.7772
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.033781 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 14.2556 | 422 | 0.057482 | 24.2576
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.033884 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.46421 | 0 | 0.057585 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.034072 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.95402 | 0 | 0.057773 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.034072 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.98809 | 0 | 0.057773 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.034605 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.62289 | 0 | 0.058306 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.034605 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.62289 | 0 | 0.058306 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.0348 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.4984 | 158 | 0.058501 | 9.2432
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.0348 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.568 | 160 | 0.058501 | 9.3602
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.0348 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.09 | 175 | 0.058501 | 10.2378
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.034939 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.6289 | 0 | 0.05864 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.034939 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.6289 | 0 | 0.05864 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.034939 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.52409 | 0 | 0.05864 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.035173 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.6428 | 132 | 0.058874 | 7.7714
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.035173 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 4.7132 | 134 | 0.058874 | 7.8892
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.035173 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 11.3609 | 323 | 0.058874 | 19.0165
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.03518 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.365 | 152.5 | 0.058881 | 8.9794
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.03518 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.2594 | 149.5 | 0.058881 | 8.8028
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.03518 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.1829 | 232.6 | 0.058881 | 13.6958
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.036472 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.2765 | 0 | 0.060173 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.036472 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.24 | 0 | 0.060173 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.036472 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.2765 | 0 | 0.060173 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.7924 | 49 | 0.06028 | 2.9537
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6826 | 46 | 0.06028 | 2.7729
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6826 | 46 | 0.06028 | 2.7729
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.7192 | 47 | 0.06028 | 2.8332
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.036579 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.6332 | 154 | 0.06028 | 9.2832
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.036579 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.4137 | 148 | 0.06028 | 8.9215
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.7558 | 48 | 0.06028 | 2.8935
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.036579 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.7558 | 48 | 0.06028 | 2.8935
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.037053 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.29642 | 0 | 0.060754 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.037053 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.29642 | 0 | 0.060754 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.037078 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 11.4942 | 310 | 0.060779 | 18.8416
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.037078 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 15.3132 | 413 | 0.060779 | 25.1019
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.037419 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.5716 | 42 | 0.06112 | 2.5671
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.037419 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6464 | 44 | 0.06112 | 2.6893
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.037419 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.6464 | 44 | 0.06112 | 2.6893
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.037419 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.7587 | 47 | 0.06112 | 2.8727
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.043247 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 24.6075 | 0 | 0.066948 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.043247 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 25.1265 | 0 | 0.066948 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 284
| 25 | 278
| 30 | 273
| 35 | 268
| 40 | 263
| 45 | 257
| 50 | 251
| 55 | 245
| 60 | 240
| 65 | 233
| 70 | 227
| 75 | 220
| 80 | 213
| 85 | 207
| 90 | 199
| 95 | 191
| 100 | 183
| 105 | 175
| 110 | 166
| 115 | 156
| Max | 284
| Min | 156
| Avg | 226.45