## test results
CRE test for: |  | 3412 TEMP_PEC - 3420 TEMP_PEC | [5 empty] | PASS
Line Rating: |  | 750
Direcction |  | North | → | South |  | N-S
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3412 TEMP_PEC - 3420 TEMP_PEC
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.072453
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.092655
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.065348
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.018741
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3412 TEMP_PEC - 3420 TEMP_PEC
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.078797
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.090994
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.065657
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.017341
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3412 TEMP_PEC - 3420 TEMP_PEC
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.16345
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.0067966
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.089794
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.15831
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.073915
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.082689
PTDF tests
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.16345 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.16345 | 0.16345
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.2114
[6 empty] | Concentration |  | 1.2934 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.19049
[6 empty] | Concentration |  | 1.1654 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 149.0455
| Percent of line rating => | [6 empty] | 19.87% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 2.4591
[7 empty] | B1(N-S) | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B2 (N-W) | -9.9313e-05 | 0.016614 | 0.016713 | -9.9313e-05
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.0016571 | 0.21915 | 0.22081 | -0.0016571
[7 empty] | B4 (S-W) | -0.0002864 | -0.38958 | -0.3893 | -0.0002864
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.0052857 | -0.18705 | -0.18176 | -0.0052857
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0015437 | 0.20179 | 0.20334 | -0.0015437
[7 empty] | test | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B1 | 0%
Deployment Error Percent | [6 empty] | B2 | -0.02471%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -0.4123%
[7 empty] | B4 | -0.07126%
[7 empty] | B5 | -1.315%
[7 empty] | B6 | -0.3841%
[7 empty] | Max Abs Error | 1.315% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-S
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3412 TEMP_PEC - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3412 TEMP_PEC - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.098838 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 25.2037
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.098838 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 14.7269
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.075711 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.1357
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.075711 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.1357
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.098838 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 15.1222
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.076168 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 11.4252
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.076168 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 6.0934
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.073999 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 5.4019
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.073999 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 8.8059
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.073999 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 15.1698
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.073999 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 7.5479
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.073999 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 7.1039
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.074036 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.88843
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.074036 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.88843
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.078647 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 13.2127
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.078647 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 7.0782
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.075504 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 1.3591
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.075504 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 1.3591
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.075504 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 2.8692
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.075909 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 21.8618
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.075909 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 11.1586
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.075909 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 11.1586
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.075996 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 8.5495
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.07553 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 3.0212
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.075548 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 5.9683
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.075548 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 8.0081
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.075548 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 11.03
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.075548 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 5.7416
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.076565 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 4.5939
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.076565 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 4.8236
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.075431 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 1.5086
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.075432 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 1.8858
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.075432 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 3.0927
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.026937 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 12.4718
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 4.237
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 4.1728
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 4.3012
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 4.3012
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 4.3012
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.064197 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 7.3185
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.064197 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 33.0615
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 4.3889
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 4.5884
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 4.5884
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 4.4554
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 4.4554
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 4.3224
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.066181 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 4.6327
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.066181 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 4.8577
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.066181 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 4.6591
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.06637 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 9.9555
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.06637 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 14.6014
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.066619 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 6.5953
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.066619 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 4.0638
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.066601 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 9.3907
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.066619 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 1.6655
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.066619 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 3.0445
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.066619 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 3.0445
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.066601 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 7.9921
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.065511 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 1.6902
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.065386 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 6.5713
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.065936 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 7.9123
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.065378 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 3.7919
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.065535 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 14.0376
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.066753 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 10.013
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.064509 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.42576
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.064509 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 2.2127
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.066753 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 6.7421
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.065963 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 7.9156
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.07346 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 26.8864
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.072799 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 17.6174
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.069918 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 27.9672
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.069923 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 16.5018
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.070772 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 11.6774
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.075525 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 15.4071
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.075525 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 15.1805
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.075525 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 18.277
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.07344 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.4688
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.07344 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.4688
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.07344 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.4688
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.07344 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 1.2485
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.073935 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 8.8722
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.069854 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 4.1912
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.0756 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 5.67
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.0756 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 6.0178
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.0756 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 6.683
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 12.1072
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 11.8045
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 14.8313
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 11.8045
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 11.8802
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 14.9827
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.0758 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 12.886
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.0758 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 39.416
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.075734 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 28.0216
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.075576 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 42.1714
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.075576 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 43.7585
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.075576 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 61.0654
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.077524 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 8.6827
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.077524 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 7.7524
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.077524 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 29.3041
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.077906 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 16.929
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.077906 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 15.9707
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.077906 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 21.2216
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.078104 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 60.1401
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.077065 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 5.3945
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.077065 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 5.3175
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.077065 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 5.3175
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.077065 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 5.2404
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.077514 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 89.6837
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.077514 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 89.7612
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.083592 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 18.7246
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.083592 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 18.8918
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.08397 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 18.1711
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.08397 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 18.1459
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.083592 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 17.7215
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.083592 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 17.6379
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.079375 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 31.3531
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.079171 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 34.4394
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.079375 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 34.5281
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.076301 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 10.5295
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.077179 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 9.1071
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.077179 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 8.8756
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.077179 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 42.9115
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.075598 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 29.332
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.075598 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 38.933
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.071998 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 56.5184
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.071998 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 57.2384
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.071998 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 56.1584
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.070644 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 12.8572
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.070644 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 34.1917
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.071594 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 16.0371
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.071139 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 3.557
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.071161 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 2.9888
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.066926 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 41.1595
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.066926 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 39.2856
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.13567 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 72.8564
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.13567 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 106.7747
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.054698 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 4.1024
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.054698 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 12.143
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.14089 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -80.1681
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.087991 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -18.3901
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.087991 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -19.0061
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.087955 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -35.7977
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.087991 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -4.0476
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.087991 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -4.1356
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.087991 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -4.0476
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.087991 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -4.0476
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.088154 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -37.3773
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.088154 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -37.4654
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.087462 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -5.0728
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.087462 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -7.7841
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.087462 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -3.8483
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.087462 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -3.8483
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.087462 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -3.7609
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.087462 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -3.9358
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.088093 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -36.2943
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.088093 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -35.2372
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.087285 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -47.6576
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.087285 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -65.4638
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.088393 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -5.392
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.088393 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -8.3973
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.088393 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -13.3473
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.087765 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -13.6036
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.087765 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -14.92
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.087765 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -13.6036
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.070237 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -1.5452
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.070237 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.77261
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.070237 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.77261
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.070906 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -3.3822
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.070906 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -2.6448
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.070906 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -3.2617
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.070906 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -3.4035
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.074167 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.89
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.074167 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.81584
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.077588 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.8621
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.077588 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.8621
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.077588 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -1.7845
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.082396 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -32.6288
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.044425 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -59.2185
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.044425 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -58.9964
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.072972 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -2.7729
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.072972 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -1.4084
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.072972 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -1.0946
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.072972 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -3.4297
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.057773 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 4.333
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.067506 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 10.1259
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.063738 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 10.8036
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.030037 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 4.5056
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.066545 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 4.1923
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.071382 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 46.3769
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.075868 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 3.0347
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.075868 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 3.0347
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.10582 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -44.6544
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.1122 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -14.8099
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.1122 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -15.0343
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.1122 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -36.2393
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.11063 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -17.4795
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.11063 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -17.7008
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.11063 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -19.3603
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.098804 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -57.7015
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.098804 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -58.7884
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.098707 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -42.7401
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.097094 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -21.7393
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.097094 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -21.8462
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.097094 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -21.8073
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.097094 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -22.0112
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.11851 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.94812
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.11851 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.94812
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.10805 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -1.9449
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.10805 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -1.9449
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.10805 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -1.6207
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.10569 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -1.4479
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.10902 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.9624
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.10902 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.9624
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.11629 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -4.0703
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.11629 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -3.954
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.11629 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -4.0703
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.1067 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -2.9877
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.1067 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -3.0944
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.064254 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 2.2489
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.064254 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 1.9276
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.10109 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -5.0544
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.10109 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -5.0544
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.10109 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -5.0544
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.10109 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -5.0544
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.10053 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.60318
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.094298 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.22632
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.094298 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.22632
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.094298 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.26403
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.092826 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.3713
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.09308 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.22339
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.09308 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.22339
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -13.271
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -12.4585
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -12.6391
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -13.271
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -16.4308
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -17.8752
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.11193 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -17.069
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.11193 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -16.7332
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.11193 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -26.0345
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.093607 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -13.2922
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.093607 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -13.573
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.093607 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -14.1347
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.093607 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -27.146
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.040863 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -1.3485
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.040863 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -1.0216
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.074167 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.89
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.071072 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -5.1883
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -5.2329
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -5.3654
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -1.9263
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.48159
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -5.2329
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -5.2991
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -5.1931
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -1.656
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -3.047
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.075413 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -47.4348
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.0719 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -10.3536
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.0719 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -13.5172
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.087247 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -1.047
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.052284 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.3137
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.072173 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -24.2501
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.072343 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -24.1626
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.072343 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -24.5966
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.07245 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -2.7531
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.072371 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.8093
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.072371 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.8093
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.072444 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -2.7529
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.072804 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -2.1113
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.072182 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -10.7046
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.072182 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -10.7262
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.072182 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -11.0438
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -11.2818
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -10.9248
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -7.1404
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -10.3536
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -10.4964
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -9.0683
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.073262 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -10.7329
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.073262 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -10.8354
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.073262 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -12.6743
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.073117 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -15.1352
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.073117 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -15.8445
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.073117 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -17.6943
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.073114 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -10.5284
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.073114 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -10.5284
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.073114 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -12.5025
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.11857 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -36.7576
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.11857 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -48.9706
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.11969 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -5.0271
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.11969 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -5.2665
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.11969 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -5.2665
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.11969 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -5.6256
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -5.7265
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -5.3759
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -5.3759
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -5.4927
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.11687 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -17.9975
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.11687 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -17.2963
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -5.6096
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -5.6096
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 4.5751
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 4.5751
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 6.0652
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 5.2286
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 5.2286
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 7.5162
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 13.6052
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 9.2858
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 8.6519
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 8.8872
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 9.606
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 13.7229
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.067528 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 14.1134
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.067528 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 8.5423
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.067528 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 16.8145
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.067528 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 13.303
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.06637 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 13.274
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.06637 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 8.0905
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.064449 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 9.6029
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.066164 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 11.9095
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.066164 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 11.9095
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.066104 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 14.8734
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.067026 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 8.3782
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.067026 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 8.3782
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 10.6028
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 10.6785
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 23.4018
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 10.83
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 10.9057
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 23.4775
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 14.8313
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 8.3994
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.076347 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 12.0581
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 12.2828
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 12.2828
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 31.0065
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 12.133
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 12.0581
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 12.2079
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 30.6321
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.07595 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.07595 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.071647 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 10.6038
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.071647 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 9.3141
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.071647 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 10.3888
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.071647 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 28.5872
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.067816 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 10.2199
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.067816 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 10.2402
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.067816 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 12.0306
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.067899 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 10.2867
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.067899 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 10.341
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.067899 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 12.0521
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.14089 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -81.8588
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.046247 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 39.5412
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.046247 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 39.5412
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.021478 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.6873
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.019125 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.918
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.019125 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.87975
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.021507 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.25808
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.021507 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 1.0969
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.021507 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.36562
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.021507 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.47315
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.021507 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.53768
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.019125 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 2.0081
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.066784 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 5.6099
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.057658 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 4.6126
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.057599 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 8.6398
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.057599 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 8.6398
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019794 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -1.4014
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019794 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -1.3203
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019794 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -1.0491
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -3.0324
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -3.0384
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -3.0146
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -1.9002
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -4.8297
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.019794 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.79176
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.01981 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -1.9869
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.01981 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -1.8403
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.01981 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -2.0345
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.01981 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -2.0206
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.019809 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.63389
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.019809 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.59427
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.029662 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -3.2925
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.029662 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -3.2925
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.029662 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -3.5298
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.029662 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -3.248
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.046247 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 7.0434
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.046247 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 7.0758
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.013794 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -1.876
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.023081 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.76167
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.013759 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.57788
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.013759 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.57788
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.013759 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.52284
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.013759 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.52284
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.031242 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -2.2182
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.031242 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.31242
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.023674 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -3.8589
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.023674 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -3.8589
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.023674 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -5.8001
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.016034 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -1.0422
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.016034 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.96204
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.016034 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -1.0422
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.016034 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -1.0422
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.014573 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -2.1714
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.014573 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.9487
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -1.4991
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -1.4431
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -1.4332
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.89783
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.20098
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.011925 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -8.8603
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.012669 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -9.3117
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.011701 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -2.0126
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.011701 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -2.0126
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.011701 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -2.0126
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.007573 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -1.3101
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.013646 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -2.3608
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.013646 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -1.8422
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.011175 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -1.8193
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.011175 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -1.8036
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.011175 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -1.7757
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.011175 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -3.0083
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.014524 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.92954
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.014524 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.91792
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.014524 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -1.1997
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.014524 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -1.069
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -2.4465
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -2.3551
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -2.3611
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -2.3536
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -4.0326
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.011965 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.059825
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.011965 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.25127
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.021529 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 3.3198
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.021529 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 3.3585
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.021529 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 3.3585
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.021529 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 8.181
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.010993 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -4.3752
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.70743
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.70743
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.70743
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.84584
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.84584
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.83047
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.05461 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 45.1625
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.05461 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 44.7256
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.023936 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -1.1034
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -3.3545
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -3.3545
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -4.6345
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -3.2662
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -3.2662
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -4.5021
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.01451 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -2.6118
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.01451 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -2.3013
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.01451 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -2.2781
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.014808 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.51828
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.017597 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -8.077
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.7774
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.78936
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.8372
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.75348
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.74152
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -1.2438
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.70564
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.007573 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -1.1814
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.007573 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -1.1662
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.007573 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -1.1662
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.007573 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -1.2268
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.01179 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -1.851
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.014233 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -1.0105
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.014233 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -1.0248
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.014233 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.55509
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.014233 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.42699
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.015216 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -1.1868
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.015216 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -1.2173
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.014528 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.23535
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.014585 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -2.4065
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.0146 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -2.4674
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.014533 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -3.0955
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.014517 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -3.3099
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.014611 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.17533
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.014611 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.263
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.018559 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.92795
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -1.3458
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -1.3458
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.69876
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.68582
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.69876
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.73758
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.69876
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.69876
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.75052
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.75052
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.012257 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.14708
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.59763
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.62965
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.59763
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.59763
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.62965
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.59763
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.041523 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -2.7405
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.02282 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -3.674
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.02282 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -3.7881
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.02282 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -5.6594
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.02282 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -12.4597
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.02282 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -14.6733
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.023722 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -15.443
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.023722 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -13.3792
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.023722 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -14.2332
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.02282 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.29666
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.011946 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.14335
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.42463
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.43337
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.40839
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.57325
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.22106
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.25478
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.24853
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.43711
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.2248
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -1.0666
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -1.8484
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -2.0609
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -2.3733
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -1.4958
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -3.3572
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -2.8586
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -2.9251
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -1.662
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.59832
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -3.1246
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -2.3268
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -2.0941
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -2.3933
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -2.154
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -3.3572
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -3.2243
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -3.4237
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -2.5262
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -2.6592
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -2.6592
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -5.684
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64405
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.054851 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 4.1961
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.057773 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 4.6218
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.057773 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 2.3109
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.05824 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 4.6592
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.057672 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 4.6138
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.055263 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 4.421
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.054475 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 4.5759
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.05824 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 4.6592
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -10.5653
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.065794 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 7.8953
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.065794 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 15.33
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.065794 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 11.1981
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -20.5745
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -17.0528
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -20.7599
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -10.658
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -9.2678
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.06846 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 4.1076
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.050537 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.041916 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.059986 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.28793
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 2.5257
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 7.2403
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 9.0925
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 8.0149
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 7.072
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 5.4218
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.065096 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 9.7644
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.064794 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 7.2893
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.064794 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 9.6867
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.064794 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 12.0517
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.064794 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 13.8983
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.072972 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.054941 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.077008 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -1.8547
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -2.888
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -4.9017
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.8547
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -2.9898
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -2.771
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -1.3855
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.8547
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -2.6252
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -3.1356
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -1.6043
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.6831
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.032
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.48159
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.032
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.6831
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.6831
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -10.7925
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.6461
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -4.0107
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.6461
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.071404 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.85685
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.069621 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -1.0443
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.069621 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -1.6013
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.066842 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -3.2084
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.069088 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.5527
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.072196 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -12.9953
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.072173 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -12.9911
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.072343 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -13.0217
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.072343 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -13.0217
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077015 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -7.7015
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077015 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -7.7015
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.7927
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.7927
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.7927
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -1.1473
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.7927
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.7927
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.7927
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -1.0756
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077015 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077015 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -38.5075
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077015 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -38.5075
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077015 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.076447 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.040863 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.075034 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.074193 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L:3412 TEMP_PEC - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | [7 empty] | 149.0455
Number of Bus | Name of Bus | ID | Max MW | L:3412 TEMP_PEC - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.098838 | north | 0.026385 | 0.19149 | 0.03349 | 0.11758 | 0.026385 | North | N | 0.026385 | 0
239 | BOSQUESW | 1 | 149 | 0.098838 | north | 0.026385 | 0.19149 | 0.03349 | 0.11758 | 0.026385 | North | N | 0.026385 | 0
244 | WHITNYDM | 1 | 15 | 0.075711 | north | 0.0032577 | 0.16837 | 0.010363 | 0.094452 | 0.0032577 | North | N | 0.0032577 | 0
245 | WHITNYDM | 2 | 15 | 0.075711 | north | 0.0032577 | 0.16837 | 0.010363 | 0.094452 | 0.0032577 | North | N | 0.0032577 | 0
247 | BOSQUESW | 2 | 153 | 0.098838 | north | 0.026385 | 0.19149 | 0.03349 | 0.11758 | 0.026385 | North | N | 0.026385 | 0
251 | BOSQUESW | 2 | 150 | 0.076168 | north | 0.0037147 | 0.16882 | 0.01082 | 0.094909 | 0.0037147 | North | N | 0.0037147 | 0
253 | BOSQUESW | 2 | 80 | 0.076168 | north | 0.0037147 | 0.16882 | 0.01082 | 0.094909 | 0.0037147 | North | N | 0.0037147 | 0
332 | RWMILLER | 1 | 73 | 0.073999 | north | 0.0015457 | 0.16665 | 0.0086506 | 0.09274 | 0.0015457 | North | N | 0.0015457 | 0
333 | RWMILLER | 2 | 119 | 0.073999 | north | 0.0015457 | 0.16665 | 0.0086506 | 0.09274 | 0.0015457 | North | N | 0.0015457 | 0
334 | RWMILLER | 3 | 205 | 0.073999 | north | 0.0015457 | 0.16665 | 0.0086506 | 0.09274 | 0.0015457 | North | N | 0.0015457 | 0
335 | RWMILLER | 4 | 102 | 0.073999 | north | 0.0015457 | 0.16665 | 0.0086506 | 0.09274 | 0.0015457 | North | N | 0.0015457 | 0
336 | RWMILLER | 5 | 96 | 0.073999 | north | 0.0015457 | 0.16665 | 0.0086506 | 0.09274 | 0.0015457 | North | N | 0.0015457 | 0
344 | MRSSHPRD | 1 | 12 | 0.074036 | north | 0.0015827 | 0.16669 | 0.0086876 | 0.092777 | 0.0015827 | North | N | 0.0015827 | 0
345 | MRSSHPRD | 2 | 12 | 0.074036 | north | 0.0015827 | 0.16669 | 0.0086876 | 0.092777 | 0.0015827 | North | N | 0.0015827 | 0
366 | JNSNCNTY | 1 | 168 | 0.078647 | north | 0.0061937 | 0.1713 | 0.013299 | 0.097388 | 0.0061937 | North | N | 0.0061937 | 0
367 | JNSNCNTY | 2 | 90 | 0.078647 | north | 0.0061937 | 0.1713 | 0.013299 | 0.097388 | 0.0061937 | North | N | 0.0061937 | 0
503 | NTHTEXAS | 1 | 18 | 0.075504 | north | 0.0030507 | 0.16816 | 0.010156 | 0.094245 | 0.0030507 | North | N | 0.0030507 | 0
504 | NTHTEXAS | 2 | 18 | 0.075504 | north | 0.0030507 | 0.16816 | 0.010156 | 0.094245 | 0.0030507 | North | N | 0.0030507 | 0
505 | NTHTEXAS | 3 | 38 | 0.075504 | north | 0.0030507 | 0.16816 | 0.010156 | 0.094245 | 0.0030507 | North | N | 0.0030507 | 0
580 | JCKCNTY8 | 1 | 288 | 0.075909 | north | 0.0034557 | 0.16856 | 0.010561 | 0.09465 | 0.0034557 | North | N | 0.0034557 | 0
581 | JCKCNTY8 | 2 | 147 | 0.075909 | north | 0.0034557 | 0.16856 | 0.010561 | 0.09465 | 0.0034557 | North | N | 0.0034557 | 0
582 | JCKCNTY8 | 3 | 147 | 0.075909 | north | 0.0034557 | 0.16856 | 0.010561 | 0.09465 | 0.0034557 | North | N | 0.0034557 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.075996 | north | 0.0035427 | 0.16865 | 0.010648 | 0.094737 | 0.0035427 | North | N | 0.0035427 | 0
837 | NEWMAN_G | 1 | 40 | 0.07553 | north | 0.0030767 | 0.16819 | 0.010182 | 0.094271 | 0.0030767 | North | N | 0.0030767 | 0
842 | OLINGER_ | 1 | 79 | 0.075548 | north | 0.0030947 | 0.1682 | 0.0102 | 0.094289 | 0.0030947 | North | N | 0.0030947 | 0
843 | OLINGER_ | 1 | 106 | 0.075548 | north | 0.0030947 | 0.1682 | 0.0102 | 0.094289 | 0.0030947 | North | N | 0.0030947 | 0
844 | OLINGER_ | 1 | 146 | 0.075548 | north | 0.0030947 | 0.1682 | 0.0102 | 0.094289 | 0.0030947 | North | N | 0.0030947 | 0
845 | OLINGER_ | 1 | 76 | 0.075548 | north | 0.0030947 | 0.1682 | 0.0102 | 0.094289 | 0.0030947 | North | N | 0.0030947 | 0
923 | SPENCER_ | 1 | 60 | 0.076565 | north | 0.0041117 | 0.16922 | 0.011217 | 0.095306 | 0.0041117 | North | N | 0.0041117 | 0
924 | SPENCER_ | 1 | 63 | 0.076565 | north | 0.0041117 | 0.16922 | 0.011217 | 0.095306 | 0.0041117 | North | N | 0.0041117 | 0
948 | STEAM1 | 1 | 20 | 0.075431 | north | 0.0029777 | 0.16809 | 0.010083 | 0.094172 | 0.0029777 | North | N | 0.0029777 | 0
949 | STEAM2 | 1 | 25 | 0.075432 | north | 0.0029787 | 0.16809 | 0.010084 | 0.094173 | 0.0029787 | North | N | 0.0029787 | 0
950 | STEAM3 | 1 | 41 | 0.075432 | north | 0.0029787 | 0.16809 | 0.010084 | 0.094173 | 0.0029787 | North | N | 0.0029787 | 0
990 | GIBN_CRE | 1 | 463 | 0.026937 | north | -0.045516 | 0.11959 | -0.038411 | 0.045678 | 0.038411 | west | Y | 0.045516 | 3.2895
1002 | PBCTAGE_ | A | 66 | 0.064197 | west | -0.0082563 | 0.15685 | -0.0011514 | 0.082938 | 0.0011514 | west | N | 0.0011514 | 0
1003 | PBCTBGE_ | B | 65 | 0.064197 | west | -0.0082563 | 0.15685 | -0.0011514 | 0.082938 | 0.0011514 | west | N | 0.0011514 | 0
1004 | PBCTCGE_ | C | 67 | 0.064197 | west | -0.0082563 | 0.15685 | -0.0011514 | 0.082938 | 0.0011514 | west | N | 0.0011514 | 0
1005 | PBCTDGE_ | D | 67 | 0.064197 | west | -0.0082563 | 0.15685 | -0.0011514 | 0.082938 | 0.0011514 | west | N | 0.0011514 | 0
1006 | PBCTEGE_ | E | 67 | 0.064197 | west | -0.0082563 | 0.15685 | -0.0011514 | 0.082938 | 0.0011514 | west | N | 0.0011514 | 0
1007 | PB5GEN_6 | MB | 114 | 0.064197 | west | -0.0082563 | 0.15685 | -0.0011514 | 0.082938 | 0.0011514 | west | N | 0.0011514 | 0
1008 | PB6GEN_7 | MB | 515 | 0.064197 | west | -0.0082563 | 0.15685 | -0.0011514 | 0.082938 | 0.0011514 | west | N | 0.0011514 | 0
1039 | MRGNAG_1 | A | 66 | 0.066498 | west | -0.0059553 | 0.15915 | 0.0011496 | 0.085239 | 0.0011496 | west | N | 0.0011496 | 0
1040 | MRGNBG_2 | B | 69 | 0.066498 | west | -0.0059553 | 0.15915 | 0.0011496 | 0.085239 | 0.0011496 | west | N | 0.0011496 | 0
1041 | MRGNCG_3 | C | 69 | 0.066498 | west | -0.0059553 | 0.15915 | 0.0011496 | 0.085239 | 0.0011496 | west | N | 0.0011496 | 0
1042 | MRGNDG_4 | D | 67 | 0.066498 | west | -0.0059553 | 0.15915 | 0.0011496 | 0.085239 | 0.0011496 | west | N | 0.0011496 | 0
1043 | MRGNEG_5 | E | 67 | 0.066498 | west | -0.0059553 | 0.15915 | 0.0011496 | 0.085239 | 0.0011496 | west | N | 0.0011496 | 0
1044 | MRGNFG_6 | F | 65 | 0.066498 | west | -0.0059553 | 0.15915 | 0.0011496 | 0.085239 | 0.0011496 | west | N | 0.0011496 | 0
1045 | CALENG1G | 1 | 70 | 0.066181 | west | -0.0062723 | 0.15884 | 0.0008326 | 0.084922 | 0.0008326 | west | N | 0.0008326 | 0
1046 | CALENG2G | 2 | 73.4 | 0.066181 | west | -0.0062723 | 0.15884 | 0.0008326 | 0.084922 | 0.0008326 | west | N | 0.0008326 | 0
1047 | CALENG3G | 3 | 70.4 | 0.066181 | west | -0.0062723 | 0.15884 | 0.0008326 | 0.084922 | 0.0008326 | west | N | 0.0008326 | 0
1058 | LONGSHOR | 1 | 150 | 0.06637 | west | -0.0060833 | 0.15903 | 0.0010216 | 0.085111 | 0.0010216 | west | N | 0.0010216 | 0
1058 | LONGSHOR | 2 | 220 | 0.06637 | west | -0.0060833 | 0.15903 | 0.0010216 | 0.085111 | 0.0010216 | west | N | 0.0010216 | 0
1061 | CIELOGEN | 1 | 99 | 0.066619 | west | -0.0058343 | 0.15927 | 0.0012706 | 0.08536 | 0.0012706 | west | N | 0.0012706 | 0
1062 | CIELOGEN | 1 | 61 | 0.066619 | west | -0.0058343 | 0.15927 | 0.0012706 | 0.08536 | 0.0012706 | west | N | 0.0012706 | 0
1068 | SCURRYCW | 1 | 141 | 0.066601 | west | -0.0058523 | 0.15926 | 0.0012526 | 0.085342 | 0.0012526 | west | N | 0.0012526 | 0
1069 | KINDERMG | 1 | 25 | 0.066619 | west | -0.0058343 | 0.15927 | 0.0012706 | 0.08536 | 0.0012706 | west | N | 0.0012706 | 0
1070 | KINDERMG | 1 | 45.7 | 0.066619 | west | -0.0058343 | 0.15927 | 0.0012706 | 0.08536 | 0.0012706 | west | N | 0.0012706 | 0
1071 | KINDERMG | 1 | 45.7 | 0.066619 | west | -0.0058343 | 0.15927 | 0.0012706 | 0.08536 | 0.0012706 | west | N | 0.0012706 | 0
1073 | SCURRYCW | 2 | 120 | 0.066601 | west | -0.0058523 | 0.15926 | 0.0012526 | 0.085342 | 0.0012526 | west | N | 0.0012526 | 0
1320 | BSP 1 | 1 | 25.8 | 0.065511 | west | -0.0069423 | 0.15817 | 0.0001626 | 0.084252 | 0.0001626 | west | N | 0.0001626 | 0
1326 | STANTONW | 1 | 100.5 | 0.065386 | west | -0.0070673 | 0.15804 | 3.7601e-05 | 0.084127 | 3.7601e-05 | west | N | 3.7601e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.065936 | west | -0.0065173 | 0.15859 | 0.0005876 | 0.084677 | 0.0005876 | west | N | 0.0005876 | 0
1328 | OCOTILLO | 1 | 58 | 0.065378 | west | -0.0070753 | 0.15803 | 2.9601e-05 | 0.084119 | 2.9601e-05 | west | N | 2.9601e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.065535 | west | -0.0069183 | 0.15819 | 0.0001866 | 0.084276 | 0.0001866 | west | N | 0.0001866 | 0
1343 | TRENTIPP | 1 | 150 | 0.066753 | west | -0.0057003 | 0.15941 | 0.0014046 | 0.085494 | 0.0014046 | west | N | 0.0014046 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.064509 | west | -0.0079443 | 0.15716 | -0.0008394 | 0.08325 | 0.0008394 | west | N | 0.0008394 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.064509 | west | -0.0079443 | 0.15716 | -0.0008394 | 0.08325 | 0.0008394 | west | N | 0.0008394 | 0
1354 | AEPWIND_ | 1 | 101 | 0.066753 | west | -0.0057003 | 0.15941 | 0.0014046 | 0.085494 | 0.0014046 | west | N | 0.0014046 | 0
1360 | GUNSIGHT | 1 | 120 | 0.065963 | west | -0.0064903 | 0.15862 | 0.0006146 | 0.084704 | 0.0006146 | west | N | 0.0006146 | 0
1432 | GRHAMSES | 2 | 366 | 0.07346 | north | 0.0010067 | 0.16612 | 0.0081116 | 0.092201 | 0.0010067 | North | N | 0.0010067 | 0
1433 | GRHAMSES | 1 | 242 | 0.072799 | north | 0.00034575 | 0.16545 | 0.0074506 | 0.09154 | 0.00034575 | North | N | 0.00034575 | 0
1437 | MESQUITW | 1 | 400 | 0.069918 | west | -0.0025353 | 0.16257 | 0.0045696 | 0.088659 | 0.0025353 | North | Y | 0.0045696 | 0.81374
1438 | MESQUITW | 1 | 236 | 0.069923 | west | -0.0025303 | 0.16258 | 0.0045746 | 0.088664 | 0.0025303 | North | Y | 0.0045746 | 0.48247
1442 | COKFIELD | 1 | 165 | 0.070772 | west | -0.0016813 | 0.16343 | 0.0054236 | 0.089513 | 0.0016813 | North | Y | 0.0054236 | 0.61749
1453 | WCPWRCO_ | 1 | 204 | 0.075525 | north | 0.0030717 | 0.16818 | 0.010177 | 0.094266 | 0.0030717 | North | N | 0.0030717 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.075525 | north | 0.0030717 | 0.16818 | 0.010177 | 0.094266 | 0.0030717 | North | N | 0.0030717 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.075525 | north | 0.0030717 | 0.16818 | 0.010177 | 0.094266 | 0.0030717 | North | N | 0.0030717 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.07344 | west | 0.00098675 | 0.1661 | 0.0080916 | 0.092181 | 0.00098675 | North | Y | 0.0080916 | 0.1421
1479 | WFCOGEN_ | 2 | 20 | 0.07344 | west | 0.00098675 | 0.1661 | 0.0080916 | 0.092181 | 0.00098675 | North | Y | 0.0080916 | 0.1421
1482 | WFCOGEN_ | 1 | 20 | 0.07344 | west | 0.00098675 | 0.1661 | 0.0080916 | 0.092181 | 0.00098675 | North | Y | 0.0080916 | 0.1421
1482 | WFCOGEN_ | 2 | 17 | 0.07344 | west | 0.00098675 | 0.1661 | 0.0080916 | 0.092181 | 0.00098675 | North | Y | 0.0080916 | 0.12078
1600 | BARTNWND | 1 | 120 | 0.073935 | north | 0.0014817 | 0.16659 | 0.0085866 | 0.092676 | 0.0014817 | North | N | 0.0014817 | 0
1643 | SLSTR1PP | 1 | 60 | 0.069854 | north | -0.0025993 | 0.16251 | 0.0045056 | 0.088595 | 0.0025993 | North | N | 0.0025993 | 0
1675 | PEC_1G | 1 | 75 | 0.0756 | north | 0.0031467 | 0.16826 | 0.010252 | 0.094341 | 0.0031467 | North | N | 0.0031467 | 0
1676 | PEC_2G | 2 | 79.6 | 0.0756 | north | 0.0031467 | 0.16826 | 0.010252 | 0.094341 | 0.0031467 | North | N | 0.0031467 | 0
1677 | PEC_3G | 3 | 88.4 | 0.0756 | north | 0.0031467 | 0.16826 | 0.010252 | 0.094341 | 0.0031467 | North | N | 0.0031467 | 0
1678 | LAMARPWR | 1 | 160 | 0.07567 | north | 0.0032167 | 0.16833 | 0.010322 | 0.094411 | 0.0032167 | North | N | 0.0032167 | 0
1679 | LAMARPWR | 2 | 156 | 0.07567 | north | 0.0032167 | 0.16833 | 0.010322 | 0.094411 | 0.0032167 | North | N | 0.0032167 | 0
1680 | LAMARPWR | 3 | 196 | 0.07567 | north | 0.0032167 | 0.16833 | 0.010322 | 0.094411 | 0.0032167 | North | N | 0.0032167 | 0
1681 | LAMARPWR | 4 | 156 | 0.07567 | north | 0.0032167 | 0.16833 | 0.010322 | 0.094411 | 0.0032167 | North | N | 0.0032167 | 0
1682 | LAMARPWR | 5 | 157 | 0.07567 | north | 0.0032167 | 0.16833 | 0.010322 | 0.094411 | 0.0032167 | North | N | 0.0032167 | 0
1683 | LAMARPWR | 6 | 198 | 0.07567 | north | 0.0032167 | 0.16833 | 0.010322 | 0.094411 | 0.0032167 | North | N | 0.0032167 | 0
1687 | VALLEY_1 | 1 | 170 | 0.0758 | north | 0.0033467 | 0.16846 | 0.010452 | 0.094541 | 0.0033467 | North | N | 0.0033467 | 0
1688 | VALLEY_2 | 2 | 520 | 0.0758 | north | 0.0033467 | 0.16846 | 0.010452 | 0.094541 | 0.0033467 | North | N | 0.0033467 | 0
1689 | VALLEY_3 | 3 | 370 | 0.075734 | north | 0.0032807 | 0.16839 | 0.010386 | 0.094475 | 0.0032807 | North | N | 0.0032807 | 0
1701 | MOSES_1G | 1 | 558 | 0.075576 | north | 0.0031227 | 0.16823 | 0.010228 | 0.094317 | 0.0031227 | North | N | 0.0031227 | 0
1702 | MOSES_2G | 2 | 579 | 0.075576 | north | 0.0031227 | 0.16823 | 0.010228 | 0.094317 | 0.0031227 | North | N | 0.0031227 | 0
1703 | MOSES_3G | 3 | 808 | 0.075576 | north | 0.0031227 | 0.16823 | 0.010228 | 0.094317 | 0.0031227 | North | N | 0.0031227 | 0
1861 | EAGLEMNT | MB | 112 | 0.077524 | north | 0.0050707 | 0.17018 | 0.012176 | 0.096265 | 0.0050707 | North | N | 0.0050707 | 0
1862 | EAGLEMNT | MB | 100 | 0.077524 | north | 0.0050707 | 0.17018 | 0.012176 | 0.096265 | 0.0050707 | North | N | 0.0050707 | 0
1863 | EAGLEMNT | MB | 378 | 0.077524 | north | 0.0050707 | 0.17018 | 0.012176 | 0.096265 | 0.0050707 | North | N | 0.0050707 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.077906 | north | 0.0054527 | 0.17056 | 0.012558 | 0.096647 | 0.0054527 | North | N | 0.0054527 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.077906 | north | 0.0054527 | 0.17056 | 0.012558 | 0.096647 | 0.0054527 | North | N | 0.0054527 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.077906 | north | 0.0054527 | 0.17056 | 0.012558 | 0.096647 | 0.0054527 | North | N | 0.0054527 | 0
1889 | DECRDOVA | MB | 770 | 0.078104 | north | 0.0056507 | 0.17076 | 0.012756 | 0.096845 | 0.0056507 | North | N | 0.0056507 | 0
1892 | DECRDOVA | A | 70 | 0.077065 | north | 0.0046117 | 0.16972 | 0.011717 | 0.095806 | 0.0046117 | North | N | 0.0046117 | 0
1893 | DECRDOVA | B | 69 | 0.077065 | north | 0.0046117 | 0.16972 | 0.011717 | 0.095806 | 0.0046117 | North | N | 0.0046117 | 0
1894 | DECRDOVA | C | 69 | 0.077065 | north | 0.0046117 | 0.16972 | 0.011717 | 0.095806 | 0.0046117 | North | N | 0.0046117 | 0
1895 | DECRDOVA | D | 68 | 0.077065 | north | 0.0046117 | 0.16972 | 0.011717 | 0.095806 | 0.0046117 | North | N | 0.0046117 | 0
1898 | COMCHEPK | 1 | 1157 | 0.077514 | north | 0.0050607 | 0.17017 | 0.012166 | 0.096255 | 0.0050607 | North | N | 0.0050607 | 0
1899 | COMCHEPK | 2 | 1158 | 0.077514 | north | 0.0050607 | 0.17017 | 0.012166 | 0.096255 | 0.0050607 | North | N | 0.0050607 | 0
1937 | MDLTHELP | 5 | 224 | 0.083592 | north | 0.011139 | 0.17625 | 0.018244 | 0.10233 | 0.011139 | North | N | 0.011139 | 0
1938 | MDLTHELP | 6 | 226 | 0.083592 | north | 0.011139 | 0.17625 | 0.018244 | 0.10233 | 0.011139 | North | N | 0.011139 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.08397 | north | 0.011517 | 0.17663 | 0.018622 | 0.10271 | 0.011517 | North | N | 0.011517 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.08397 | north | 0.011517 | 0.17663 | 0.018622 | 0.10271 | 0.011517 | North | N | 0.011517 | 0
1943 | MDLTHELP | 3 | 212 | 0.083592 | north | 0.011139 | 0.17625 | 0.018244 | 0.10233 | 0.011139 | North | N | 0.011139 | 0
1944 | MDLTHELP | 4 | 211 | 0.083592 | north | 0.011139 | 0.17625 | 0.018244 | 0.10233 | 0.011139 | North | N | 0.011139 | 0
1947 | HANDLEY_ | 3 | 395 | 0.079375 | north | 0.0069217 | 0.17203 | 0.014027 | 0.098116 | 0.0069217 | North | N | 0.0069217 | 0
1948 | HANDLEY_ | 4 | 435 | 0.079171 | north | 0.0067177 | 0.17183 | 0.013823 | 0.097912 | 0.0067177 | North | N | 0.0067177 | 0
1949 | HANDLEY_ | 5 | 435 | 0.079375 | north | 0.0069217 | 0.17203 | 0.014027 | 0.098116 | 0.0069217 | North | N | 0.0069217 | 0
2371 | COLLIN_1 | MB | 138 | 0.076301 | north | 0.0038477 | 0.16896 | 0.010953 | 0.095042 | 0.0038477 | North | N | 0.0038477 | 0
2413 | MTCK6_G | 6 | 118 | 0.077179 | north | 0.0047257 | 0.16983 | 0.011831 | 0.09592 | 0.0047257 | North | N | 0.0047257 | 0
2414 | MTCK7_G | 7 | 115 | 0.077179 | north | 0.0047257 | 0.16983 | 0.011831 | 0.09592 | 0.0047257 | North | N | 0.0047257 | 0
2417 | MTCK8_G | 8 | 556 | 0.077179 | north | 0.0047257 | 0.16983 | 0.011831 | 0.09592 | 0.0047257 | North | N | 0.0047257 | 0
2451 | LKHB1_G | 1 | 388 | 0.075598 | north | 0.0031447 | 0.16825 | 0.01025 | 0.094339 | 0.0031447 | North | N | 0.0031447 | 0
2452 | LKHB2_G | 2 | 515 | 0.075598 | north | 0.0031447 | 0.16825 | 0.01025 | 0.094339 | 0.0031447 | North | N | 0.0031447 | 0
3097 | MARTLAKE | 1 | 785 | 0.071998 | north | -0.00045525 | 0.16465 | 0.0066496 | 0.090739 | 0.00045525 | North | N | 0.00045525 | 0
3098 | MARTLAKE | 2 | 795 | 0.071998 | north | -0.00045525 | 0.16465 | 0.0066496 | 0.090739 | 0.00045525 | North | N | 0.00045525 | 0
3099 | MARTLAKE | 3 | 780 | 0.071998 | north | -0.00045525 | 0.16465 | 0.0066496 | 0.090739 | 0.00045525 | North | N | 0.00045525 | 0
3107 | STRYKER_ | 1 | 182 | 0.070644 | north | -0.0018093 | 0.1633 | 0.0052956 | 0.089385 | 0.0018093 | North | N | 0.0018093 | 0
3108 | STRYKER_ | 2 | 484 | 0.070644 | north | -0.0018093 | 0.1633 | 0.0052956 | 0.089385 | 0.0018093 | North | N | 0.0018093 | 0
3126 | TRINIDAD | 1 | 224 | 0.071594 | north | -0.00085925 | 0.16425 | 0.0062456 | 0.090335 | 0.00085925 | North | N | 0.00085925 | 0
3309 | ASPN_G | 1 | 50 | 0.071139 | north | -0.0013143 | 0.16379 | 0.0057906 | 0.08988 | 0.0013143 | North | N | 0.0013143 | 0
3348 | CHAMPION | MB | 42 | 0.071161 | north | -0.0012923 | 0.16382 | 0.0058126 | 0.089902 | 0.0012923 | North | N | 0.0012923 | 0
3381 | BBRN_1G | 1 | 615 | 0.066926 | north | -0.0055273 | 0.15958 | 0.0015776 | 0.085667 | 0.0015776 | west | Y | 0.0055273 | 2.429
3382 | BBRN_2G | 2 | 587 | 0.066926 | north | -0.0055273 | 0.15958 | 0.0015776 | 0.085667 | 0.0015776 | west | Y | 0.0055273 | 2.3184
3403 | THOUSE_1 | MB | 537 | 0.13567 | north | 0.06322 | 0.22833 | 0.070325 | 0.15441 | 0.06322 | North | N | 0.06322 | 0
3404 | THOUSE_2 | 2 | 787 | 0.13567 | north | 0.06322 | 0.22833 | 0.070325 | 0.15441 | 0.06322 | North | N | 0.06322 | 0
3416 | LAKE_CRK | MB | 75 | 0.054698 | north | -0.017755 | 0.14735 | -0.01065 | 0.073439 | 0.01065 | west | Y | 0.017755 | 0.53286
3417 | LAKE_CRK | MB | 222 | 0.054698 | north | -0.017755 | 0.14735 | -0.01065 | 0.073439 | 0.01065 | west | Y | 0.017755 | 1.5773
3432 | SANDOW_4 | 4 | 569 | -0.14089 | south | -0.21335 | -0.048238 | -0.20624 | -0.12215 | 0.048238 | south | N | 0.048238 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.087991 | south | -0.16044 | 0.0046643 | -0.15334 | -0.06925 | 0.0046643 | south | N | 0.0046643 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.087991 | south | -0.16044 | 0.0046643 | -0.15334 | -0.06925 | 0.0046643 | south | N | 0.0046643 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.087955 | south | -0.16041 | 0.0047003 | -0.1533 | -0.069214 | 0.0047003 | south | N | 0.0047003 | 0
5031 | BRA_VHBC | 1 | 46 | -0.087991 | south | -0.16044 | 0.0046643 | -0.15334 | -0.06925 | 0.0046643 | south | N | 0.0046643 | 0
5032 | BRA_VHBC | 2 | 47 | -0.087991 | south | -0.16044 | 0.0046643 | -0.15334 | -0.06925 | 0.0046643 | south | N | 0.0046643 | 0
5033 | BRA_VHBC | 3 | 46 | -0.087991 | south | -0.16044 | 0.0046643 | -0.15334 | -0.06925 | 0.0046643 | south | N | 0.0046643 | 0
5034 | BRA_VHBC | 4 | 46 | -0.087991 | south | -0.16044 | 0.0046643 | -0.15334 | -0.06925 | 0.0046643 | south | N | 0.0046643 | 0
5111 | CALAVER_ | 1 | 424 | -0.088154 | south | -0.16061 | 0.0045013 | -0.1535 | -0.069413 | 0.0045013 | south | N | 0.0045013 | 0
5112 | CALAVER_ | 2 | 425 | -0.088154 | south | -0.16061 | 0.0045013 | -0.1535 | -0.069413 | 0.0045013 | south | N | 0.0045013 | 0
5264 | LEON_LCP | 3 | 58 | -0.087462 | south | -0.15992 | 0.0051933 | -0.15281 | -0.068721 | 0.0051933 | south | N | 0.0051933 | 0
5265 | LEON_LCP | 4 | 89 | -0.087462 | south | -0.15992 | 0.0051933 | -0.15281 | -0.068721 | 0.0051933 | south | N | 0.0051933 | 0
5266 | LEON_LCP | 1 | 44 | -0.087462 | south | -0.15992 | 0.0051933 | -0.15281 | -0.068721 | 0.0051933 | south | N | 0.0051933 | 0
5267 | LEON_LCP | 2 | 44 | -0.087462 | south | -0.15992 | 0.0051933 | -0.15281 | -0.068721 | 0.0051933 | south | N | 0.0051933 | 0
5268 | LEON_LCP | 3 | 43 | -0.087462 | south | -0.15992 | 0.0051933 | -0.15281 | -0.068721 | 0.0051933 | south | N | 0.0051933 | 0
5269 | LEON_LCP | 4 | 45 | -0.087462 | south | -0.15992 | 0.0051933 | -0.15281 | -0.068721 | 0.0051933 | south | N | 0.0051933 | 0
5396 | CALAVER_ | 1 | 412 | -0.088093 | south | -0.16055 | 0.0045623 | -0.15344 | -0.069352 | 0.0045623 | south | N | 0.0045623 | 0
5397 | CALAVER_ | 2 | 400 | -0.088093 | south | -0.16055 | 0.0045623 | -0.15344 | -0.069352 | 0.0045623 | south | N | 0.0045623 | 0
5401 | CALAVER_ | 1 | 546 | -0.087285 | south | -0.15974 | 0.0053703 | -0.15263 | -0.068544 | 0.0053703 | south | N | 0.0053703 | 0
5402 | CALAVER_ | 2 | 750 | -0.087285 | south | -0.15974 | 0.0053703 | -0.15263 | -0.068544 | 0.0053703 | south | N | 0.0053703 | 0
5436 | TUTTL_WB | MB | 61 | -0.088393 | south | -0.16085 | 0.0042623 | -0.15374 | -0.069652 | 0.0042623 | south | N | 0.0042623 | 0
5438 | TUTTL_WB | MB | 95 | -0.088393 | south | -0.16085 | 0.0042623 | -0.15374 | -0.069652 | 0.0042623 | south | N | 0.0042623 | 0
5439 | TUTTL_WB | MB | 151 | -0.088393 | south | -0.16085 | 0.0042623 | -0.15374 | -0.069652 | 0.0042623 | south | N | 0.0042623 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.087765 | south | -0.16022 | 0.0048903 | -0.15311 | -0.069024 | 0.0048903 | south | N | 0.0048903 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.087765 | south | -0.16022 | 0.0048903 | -0.15311 | -0.069024 | 0.0048903 | south | N | 0.0048903 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.087765 | south | -0.16022 | 0.0048903 | -0.15311 | -0.069024 | 0.0048903 | south | N | 0.0048903 | 0
5503 | RAYBURNG | 1 | 22 | -0.070237 | south | -0.14269 | 0.022418 | -0.13559 | -0.051496 | 0.022418 | south | N | 0.022418 | 0
5505 | RAYBURNG | 1 | 11 | -0.070237 | south | -0.14269 | 0.022418 | -0.13559 | -0.051496 | 0.022418 | south | N | 0.022418 | 0
5506 | RAYBURNG | 1 | 11 | -0.070237 | south | -0.14269 | 0.022418 | -0.13559 | -0.051496 | 0.022418 | south | N | 0.022418 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.070906 | south | -0.14336 | 0.021749 | -0.13625 | -0.052165 | 0.021749 | south | N | 0.021749 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.070906 | south | -0.14336 | 0.021749 | -0.13625 | -0.052165 | 0.021749 | south | N | 0.021749 | 0
5511 | RAYBURNC | 1 | 46 | -0.070906 | south | -0.14336 | 0.021749 | -0.13625 | -0.052165 | 0.021749 | south | N | 0.021749 | 0
5512 | RAYBURNC | 1 | 48 | -0.070906 | south | -0.14336 | 0.021749 | -0.13625 | -0.052165 | 0.021749 | south | N | 0.021749 | 0
5728 | FALCONHY | 2 | 12 | -0.074167 | south | -0.14662 | 0.018488 | -0.13952 | -0.055426 | 0.018488 | south | N | 0.018488 | 0
5729 | FALCONHY | 3 | 11 | -0.074167 | south | -0.14662 | 0.018488 | -0.13952 | -0.055426 | 0.018488 | south | N | 0.018488 | 0
5890 | PEARSALL | 1 | 24 | -0.077588 | south | -0.15004 | 0.015067 | -0.14294 | -0.058847 | 0.015067 | south | N | 0.015067 | 0
5891 | PEARSALL | 1 | 24 | -0.077588 | south | -0.15004 | 0.015067 | -0.14294 | -0.058847 | 0.015067 | south | N | 0.015067 | 0
5892 | PEARSALL | 1 | 23 | -0.077588 | south | -0.15004 | 0.015067 | -0.14294 | -0.058847 | 0.015067 | south | N | 0.015067 | 0
5903 | SANMIGUE | 1 | 396 | -0.082396 | south | -0.15485 | 0.010259 | -0.14774 | -0.063655 | 0.010259 | south | N | 0.010259 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.044425 | houston | -0.11688 | 0.04823 | -0.10977 | -0.025684 | 0.025684 | houston | N | 0.025684 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.044425 | houston | -0.11688 | 0.04823 | -0.10977 | -0.025684 | 0.025684 | houston | N | 0.025684 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | -0.072453 | 0.092655 | -0.065348 | 0.018741 | 0.018741 | houston | Y | 0.072453 | 32.2276
5932 | SI_RAY9 | 9 | 38 | -0.072972 | south | -0.14543 | 0.019683 | -0.13832 | -0.054231 | 0.019683 | south | N | 0.019683 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.072972 | south | -0.14543 | 0.019683 | -0.13832 | -0.054231 | 0.019683 | south | N | 0.019683 | 0
5934 | SI_RAY5 | 5 | 15 | -0.072972 | south | -0.14543 | 0.019683 | -0.13832 | -0.054231 | 0.019683 | south | N | 0.019683 | 0
5935 | SI_RAY10 | 10 | 47 | -0.072972 | south | -0.14543 | 0.019683 | -0.13832 | -0.054231 | 0.019683 | south | N | 0.019683 | 0
6016 | SWMESA | 1 | 75 | 0.057773 | west | -0.01468 | 0.15043 | -0.0075754 | 0.076514 | 0.0075754 | west | N | 0.0075754 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | -0.072453 | 0.092655 | -0.065348 | 0.018741 | 0.018741 | houston | Y | 0.065348 | 10.2537
6144 | MCADOO1A | 1 | 150 | 0.067506 | west | -0.0049473 | 0.16016 | 0.0021576 | 0.086247 | 0.0021576 | west | N | 0.0021576 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.063738 | west | -0.0087153 | 0.15639 | -0.0016104 | 0.082479 | 0.0016104 | west | N | 0.0016104 | 0
6476 | LANGFORD | 1 | 150 | 0.030037 | west | -0.042416 | 0.12269 | -0.035311 | 0.048778 | 0.035311 | west | N | 0.035311 | 0
6637 | SNYDERW1 | 1 | 63 | 0.066545 | west | -0.0059083 | 0.1592 | 0.0011966 | 0.085286 | 0.0011966 | west | N | 0.0011966 | 0
6752 | OKLA0A | 1 | 649.7 | 0.071382 | west | -0.0010713 | 0.16404 | 0.0060336 | 0.090123 | 0.0010713 | North | Y | 0.0060336 | 3.224
6948 | DENISNDM | 1 | 40 | 0.075868 | north | 0.0034147 | 0.16852 | 0.01052 | 0.094609 | 0.0034147 | North | N | 0.0034147 | 0
6948 | DENISNDM | 2 | 40 | 0.075868 | north | 0.0034147 | 0.16852 | 0.01052 | 0.094609 | 0.0034147 | North | N | 0.0034147 | 0
7000 | L_FERGUS | 1 | 422 | -0.10582 | south | -0.17827 | -0.013161 | -0.17116 | -0.087075 | 0.013161 | south | N | 0.013161 | 0
7004 | L_SIMGID | 1 | 132 | -0.1122 | south | -0.18465 | -0.019541 | -0.17754 | -0.093455 | 0.019541 | south | N | 0.019541 | 0
7005 | L_SIMGID | 2 | 134 | -0.1122 | south | -0.18465 | -0.019541 | -0.17754 | -0.093455 | 0.019541 | south | N | 0.019541 | 0
7006 | L_SIMGID | 3 | 323 | -0.1122 | south | -0.18465 | -0.019541 | -0.17754 | -0.093455 | 0.019541 | south | N | 0.019541 | 0
7007 | L_LOSTPI | 1 | 158 | -0.11063 | south | -0.18308 | -0.017975 | -0.17598 | -0.091889 | 0.017975 | south | N | 0.017975 | 0
7008 | L_LOSTPI | 2 | 160 | -0.11063 | south | -0.18308 | -0.017975 | -0.17598 | -0.091889 | 0.017975 | south | N | 0.017975 | 0
7009 | L_LOSTPI | 3 | 175 | -0.11063 | south | -0.18308 | -0.017975 | -0.17598 | -0.091889 | 0.017975 | south | N | 0.017975 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.098804 | south | -0.17126 | -0.0061487 | -0.16415 | -0.080063 | 0.0061487 | south | N | 0.0061487 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.098804 | south | -0.17126 | -0.0061487 | -0.16415 | -0.080063 | 0.0061487 | south | N | 0.0061487 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.098707 | south | -0.17116 | -0.0060517 | -0.16406 | -0.079966 | 0.0060517 | south | N | 0.0060517 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.097094 | south | -0.16955 | -0.0044387 | -0.16244 | -0.078353 | 0.0044387 | south | N | 0.0044387 | 0
7015 | L_HAYSEN | 2 | 225 | -0.097094 | south | -0.16955 | -0.0044387 | -0.16244 | -0.078353 | 0.0044387 | south | N | 0.0044387 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.097094 | south | -0.16955 | -0.0044387 | -0.16244 | -0.078353 | 0.0044387 | south | N | 0.0044387 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.097094 | south | -0.16955 | -0.0044387 | -0.16244 | -0.078353 | 0.0044387 | south | N | 0.0044387 | 0
7020 | L_AUSTPL | 1 | 8 | -0.11851 | south | -0.19097 | -0.02586 | -0.18386 | -0.099774 | 0.02586 | south | N | 0.02586 | 0
7020 | L_AUSTPL | 2 | 8 | -0.11851 | south | -0.19097 | -0.02586 | -0.18386 | -0.099774 | 0.02586 | south | N | 0.02586 | 0
7022 | L_BUCHAN | 1 | 18 | -0.10805 | south | -0.1805 | -0.015395 | -0.1734 | -0.089309 | 0.015395 | south | N | 0.015395 | 0
7023 | L_BUCHAN | 2 | 18 | -0.10805 | south | -0.1805 | -0.015395 | -0.1734 | -0.089309 | 0.015395 | south | N | 0.015395 | 0
7024 | L_BUCHAN | 3 | 15 | -0.10805 | south | -0.1805 | -0.015395 | -0.1734 | -0.089309 | 0.015395 | south | N | 0.015395 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.10569 | south | -0.17814 | -0.01303 | -0.17103 | -0.086944 | 0.01303 | south | N | 0.01303 | 0
7028 | L_MARBFA | 1 | 18 | -0.10902 | south | -0.18148 | -0.016368 | -0.17437 | -0.090282 | 0.016368 | south | N | 0.016368 | 0
7029 | L_MARBFA | 2 | 18 | -0.10902 | south | -0.18148 | -0.016368 | -0.17437 | -0.090282 | 0.016368 | south | N | 0.016368 | 0
7031 | L_MARSFO | 1 | 35 | -0.11629 | south | -0.18875 | -0.023639 | -0.18164 | -0.097553 | 0.023639 | south | N | 0.023639 | 0
7032 | L_MARSFO | 2 | 34 | -0.11629 | south | -0.18875 | -0.023639 | -0.18164 | -0.097553 | 0.023639 | south | N | 0.023639 | 0
7033 | L_MARSFO | 3 | 35 | -0.11629 | south | -0.18875 | -0.023639 | -0.18164 | -0.097553 | 0.023639 | south | N | 0.023639 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.1067 | south | -0.17916 | -0.014048 | -0.17205 | -0.087962 | 0.014048 | south | N | 0.014048 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.1067 | south | -0.17916 | -0.014048 | -0.17205 | -0.087962 | 0.014048 | south | N | 0.014048 | 0
7038 | L_DELAWA | 1 | 35 | 0.064254 | west | -0.0081993 | 0.15691 | -0.0010944 | 0.082995 | 0.0010944 | west | N | 0.0010944 | 0
7038 | L_DELAWA | 2 | 30 | 0.064254 | west | -0.0081993 | 0.15691 | -0.0010944 | 0.082995 | 0.0010944 | west | N | 0.0010944 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.10109 | south | -0.17354 | -0.0084327 | -0.16644 | -0.082347 | 0.0084327 | south | N | 0.0084327 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.10109 | south | -0.17354 | -0.0084327 | -0.16644 | -0.082347 | 0.0084327 | south | N | 0.0084327 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.10109 | south | -0.17354 | -0.0084327 | -0.16644 | -0.082347 | 0.0084327 | south | N | 0.0084327 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.10109 | south | -0.17354 | -0.0084327 | -0.16644 | -0.082347 | 0.0084327 | south | N | 0.0084327 | 0
7487 | L_CANYHY | 1 | 6 | -0.10053 | south | -0.17298 | -0.0078747 | -0.16588 | -0.081789 | 0.0078747 | south | N | 0.0078747 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.094298 | south | -0.16675 | -0.0016427 | -0.15965 | -0.075557 | 0.0016427 | south | N | 0.0016427 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.094298 | south | -0.16675 | -0.0016427 | -0.15965 | -0.075557 | 0.0016427 | south | N | 0.0016427 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.094298 | south | -0.16675 | -0.0016427 | -0.15965 | -0.075557 | 0.0016427 | south | N | 0.0016427 | 0
7609 | L_SCHUMA | 1 | 4 | -0.092826 | south | -0.16528 | -0.00017071 | -0.15817 | -0.074085 | 0.00017071 | south | N | 0.00017071 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.09308 | south | -0.16553 | -0.00042471 | -0.15843 | -0.074339 | 0.00042471 | south | N | 0.00042471 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.09308 | south | -0.16553 | -0.00042471 | -0.15843 | -0.074339 | 0.00042471 | south | N | 0.00042471 | 0
7800 | L_GUADGE | 1 | 147 | -0.090279 | south | -0.16273 | 0.0023763 | -0.15563 | -0.071538 | 0.0023763 | south | N | 0.0023763 | 0
7801 | L_GUADGE | 2 | 138 | -0.090279 | south | -0.16273 | 0.0023763 | -0.15563 | -0.071538 | 0.0023763 | south | N | 0.0023763 | 0
7802 | L_GUADGE | 3 | 140 | -0.090279 | south | -0.16273 | 0.0023763 | -0.15563 | -0.071538 | 0.0023763 | south | N | 0.0023763 | 0
7803 | L_GUADGE | 4 | 147 | -0.090279 | south | -0.16273 | 0.0023763 | -0.15563 | -0.071538 | 0.0023763 | south | N | 0.0023763 | 0
7804 | L_GUADGE | 5 | 182 | -0.090279 | south | -0.16273 | 0.0023763 | -0.15563 | -0.071538 | 0.0023763 | south | N | 0.0023763 | 0
7805 | L_GUADGE | 6 | 198 | -0.090279 | south | -0.16273 | 0.0023763 | -0.15563 | -0.071538 | 0.0023763 | south | N | 0.0023763 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.11193 | south | -0.18438 | -0.019273 | -0.17728 | -0.093187 | 0.019273 | south | N | 0.019273 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.11193 | south | -0.18438 | -0.019273 | -0.17728 | -0.093187 | 0.019273 | south | N | 0.019273 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.11193 | south | -0.18438 | -0.019273 | -0.17728 | -0.093187 | 0.019273 | south | N | 0.019273 | 0
7810 | L_RIONOG | 1 | 142 | -0.093607 | south | -0.16606 | -0.00095171 | -0.15896 | -0.074866 | 0.00095171 | south | N | 0.00095171 | 0
7811 | L_RIONOG | 2 | 145 | -0.093607 | south | -0.16606 | -0.00095171 | -0.15896 | -0.074866 | 0.00095171 | south | N | 0.00095171 | 0
7812 | L_RIONOG | 3 | 151 | -0.093607 | south | -0.16606 | -0.00095171 | -0.15896 | -0.074866 | 0.00095171 | south | N | 0.00095171 | 0
7813 | L_RIONOG | 4 | 290 | -0.093607 | south | -0.16606 | -0.00095171 | -0.15896 | -0.074866 | 0.00095171 | south | N | 0.00095171 | 0
8032 | AMISTADH | 1 | 33 | -0.040863 | south | -0.11332 | 0.051792 | -0.10621 | -0.022122 | 0.022122 | houston | Y | 0.051792 | 0.97911
8033 | AMISTADH | 2 | 25 | -0.040863 | south | -0.11332 | 0.051792 | -0.10621 | -0.022122 | 0.022122 | houston | Y | 0.051792 | 0.74175
8048 | FALCONHY | 1 | 12 | -0.074167 | south | -0.14662 | 0.018488 | -0.13952 | -0.055426 | 0.018488 | south | N | 0.018488 | 0
8066 | DUP1V#1 | 1 | 73 | -0.071072 | south | -0.14353 | 0.021583 | -0.13642 | -0.052331 | 0.021583 | south | N | 0.021583 | 0
8134 | FOR69CG0 | 1 | 79 | -0.066239 | south | -0.13869 | 0.026416 | -0.13159 | -0.047498 | 0.026416 | south | N | 0.026416 | 0
8138 | FOR69CG0 | 2 | 81 | -0.066239 | south | -0.13869 | 0.026416 | -0.13159 | -0.047498 | 0.026416 | south | N | 0.026416 | 0
8139 | JOS #1 | MB | 255 | 0 | south | -0.072453 | 0.092655 | -0.065348 | 0.018741 | 0.018741 | houston | Y | 0.092655 | 18.8482
8147 | UCAR #2 | 10 | 28 | -0.068798 | south | -0.14125 | 0.023857 | -0.13415 | -0.050057 | 0.023857 | south | N | 0.023857 | 0
8148 | UCAR #1 | 2 | 7 | -0.068798 | south | -0.14125 | 0.023857 | -0.13415 | -0.050057 | 0.023857 | south | N | 0.023857 | 0
8153 | FOR69CG0 | 3 | 79 | -0.066239 | south | -0.13869 | 0.026416 | -0.13159 | -0.047498 | 0.026416 | south | N | 0.026416 | 0
8154 | FOR69CG0 | 4 | 80 | -0.066239 | south | -0.13869 | 0.026416 | -0.13159 | -0.047498 | 0.026416 | south | N | 0.026416 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.066239 | south | -0.13869 | 0.026416 | -0.13159 | -0.047498 | 0.026416 | south | N | 0.026416 | 0
8156 | FOR69CG0 | 6 | 25 | -0.066239 | south | -0.13869 | 0.026416 | -0.13159 | -0.047498 | 0.026416 | south | N | 0.026416 | 0
8157 | FOR69CG0 | 7 | 46 | -0.066239 | south | -0.13869 | 0.026416 | -0.13159 | -0.047498 | 0.026416 | south | N | 0.026416 | 0
8161 | COLETOU1 | 1 | 629 | -0.075413 | south | -0.14787 | 0.017242 | -0.14076 | -0.056672 | 0.017242 | south | N | 0.017242 | 0
8173 | VICEC51A | 5 | 144 | -0.0719 | south | -0.14435 | 0.020755 | -0.13725 | -0.053159 | 0.020755 | south | N | 0.020755 | 0
8174 | VICEC61A | 6 | 188 | -0.0719 | south | -0.14435 | 0.020755 | -0.13725 | -0.053159 | 0.020755 | south | N | 0.020755 | 0
8189 | CUERO 2 | 1 | 12 | -0.087247 | south | -0.1597 | 0.0054083 | -0.1526 | -0.068506 | 0.0054083 | south | N | 0.0054083 | 0
8262 | ELPS | 1 | 6 | -0.052284 | south | -0.12474 | 0.040371 | -0.11763 | -0.033543 | 0.033543 | houston | Y | 0.040371 | 0.040967
8285 | LAR #1 | MB | 32 | 0 | south | -0.072453 | 0.092655 | -0.065348 | 0.018741 | 0.018741 | houston | Y | 0.092655 | 2.3653
8287 | LAR #2 | MB | 32 | 0 | south | -0.072453 | 0.092655 | -0.065348 | 0.018741 | 0.018741 | houston | Y | 0.092655 | 2.3653
8288 | LAR #3 | MB | 105 | 0 | south | -0.072453 | 0.092655 | -0.065348 | 0.018741 | 0.018741 | houston | Y | 0.092655 | 7.761
8388 | BATES0A | MB | 70 | 0 | south | -0.072453 | 0.092655 | -0.065348 | 0.018741 | 0.018741 | houston | Y | 0.092655 | 5.174
8393 | BATES0B | MB | 110 | 0 | south | -0.072453 | 0.092655 | -0.065348 | 0.018741 | 0.018741 | houston | Y | 0.092655 | 8.1306
8442 | NBEC71A | 1 | 336 | -0.072173 | south | -0.14463 | 0.020482 | -0.13752 | -0.053432 | 0.020482 | south | N | 0.020482 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | -0.072453 | 0.092655 | -0.065348 | 0.018741 | 0.018741 | houston | Y | 0.092655 | 1.4783
8457 | COSW#2 | 2 | 14 | 0 | south | -0.072453 | 0.092655 | -0.065348 | 0.018741 | 0.018741 | houston | Y | 0.092655 | 1.0348
8459 | B_DAVIS1 | 1 | 334 | -0.072343 | south | -0.1448 | 0.020312 | -0.13769 | -0.053602 | 0.020312 | south | N | 0.020312 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.072343 | south | -0.1448 | 0.020312 | -0.13769 | -0.053602 | 0.020312 | south | N | 0.020312 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.07245 | south | -0.1449 | 0.020205 | -0.1378 | -0.053709 | 0.020205 | south | N | 0.020205 | 0
8506 | VAL #1 | 1 | 25 | -0.072371 | south | -0.14482 | 0.020284 | -0.13772 | -0.05363 | 0.020284 | south | N | 0.020284 | 0
8507 | VAL #2 | 2 | 25 | -0.072371 | south | -0.14482 | 0.020284 | -0.13772 | -0.05363 | 0.020284 | south | N | 0.020284 | 0
8511 | OXY_CC0A | 1 | 38 | -0.072444 | south | -0.1449 | 0.020211 | -0.13779 | -0.053703 | 0.020211 | south | N | 0.020211 | 0
8517 | CELANEBI | 1 | 29 | -0.072804 | south | -0.14526 | 0.019851 | -0.13815 | -0.054063 | 0.019851 | south | N | 0.019851 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.072182 | south | -0.14464 | 0.020473 | -0.13753 | -0.053441 | 0.020473 | south | N | 0.020473 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.072182 | south | -0.14464 | 0.020473 | -0.13753 | -0.053441 | 0.020473 | south | N | 0.020473 | 0
8562 | CNOPST1 | 3 | 153 | -0.072182 | south | -0.14464 | 0.020473 | -0.13753 | -0.053441 | 0.020473 | south | N | 0.020473 | 0
8926 | LGE_GT10 | 1 | 158 | -0.071404 | south | -0.14386 | 0.021251 | -0.13675 | -0.052663 | 0.021251 | south | N | 0.021251 | 0
8927 | LGE_GT20 | 2 | 153 | -0.071404 | south | -0.14386 | 0.021251 | -0.13675 | -0.052663 | 0.021251 | south | N | 0.021251 | 0
8928 | LGE_STG0 | 3 | 100 | -0.071404 | south | -0.14386 | 0.021251 | -0.13675 | -0.052663 | 0.021251 | south | N | 0.021251 | 0
8930 | ICPGN10A | 1 | 145 | -0.071404 | south | -0.14386 | 0.021251 | -0.13675 | -0.052663 | 0.021251 | south | N | 0.021251 | 0
8931 | ICPGN20A | 2 | 147 | -0.071404 | south | -0.14386 | 0.021251 | -0.13675 | -0.052663 | 0.021251 | south | N | 0.021251 | 0
8932 | ICPGN30A | 3 | 127 | -0.071404 | south | -0.14386 | 0.021251 | -0.13675 | -0.052663 | 0.021251 | south | N | 0.021251 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.073262 | south | -0.14572 | 0.019393 | -0.13861 | -0.054521 | 0.019393 | south | N | 0.019393 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.073262 | south | -0.14572 | 0.019393 | -0.13861 | -0.054521 | 0.019393 | south | N | 0.019393 | 0
8935 | FGNTS201 | 3 | 173 | -0.073262 | south | -0.14572 | 0.019393 | -0.13861 | -0.054521 | 0.019393 | south | N | 0.019393 | 0
8936 | MVGN#1 | 1 | 207 | -0.073117 | south | -0.14557 | 0.019538 | -0.13847 | -0.054376 | 0.019538 | south | N | 0.019538 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.073117 | south | -0.14557 | 0.019538 | -0.13847 | -0.054376 | 0.019538 | south | N | 0.019538 | 0
8938 | MVGN#3 | 3 | 242 | -0.073117 | south | -0.14557 | 0.019538 | -0.13847 | -0.054376 | 0.019538 | south | N | 0.019538 | 0
8981 | HECN1 | 1 | 144 | -0.073114 | south | -0.14557 | 0.019541 | -0.13846 | -0.054373 | 0.019541 | south | N | 0.019541 | 0
8982 | HECN2 | 2 | 144 | -0.073114 | south | -0.14557 | 0.019541 | -0.13846 | -0.054373 | 0.019541 | south | N | 0.019541 | 0
8983 | HECN3 | 3 | 171 | -0.073114 | south | -0.14557 | 0.019541 | -0.13846 | -0.054373 | 0.019541 | south | N | 0.019541 | 0
9000 | DECKR_G1 | 1 | 310 | -0.11857 | south | -0.19103 | -0.025918 | -0.18392 | -0.099832 | 0.025918 | south | N | 0.025918 | 0
9001 | DECKR_G2 | 2 | 413 | -0.11857 | south | -0.19103 | -0.025918 | -0.18392 | -0.099832 | 0.025918 | south | N | 0.025918 | 0
9002 | DECKR_G3 | 3 | 42 | -0.11969 | south | -0.19215 | -0.027039 | -0.18504 | -0.10095 | 0.027039 | south | N | 0.027039 | 0
9003 | DECKR_G4 | 4 | 44 | -0.11969 | south | -0.19215 | -0.027039 | -0.18504 | -0.10095 | 0.027039 | south | N | 0.027039 | 0
9004 | DECKR_G5 | 5 | 44 | -0.11969 | south | -0.19215 | -0.027039 | -0.18504 | -0.10095 | 0.027039 | south | N | 0.027039 | 0
9005 | DECKR_G6 | 6 | 47 | -0.11969 | south | -0.19215 | -0.027039 | -0.18504 | -0.10095 | 0.027039 | south | N | 0.027039 | 0
9016 | SANDH_G1 | 1 | 49 | -0.11687 | south | -0.18932 | -0.024212 | -0.18222 | -0.098126 | 0.024212 | south | N | 0.024212 | 0
9017 | SANDH_G2 | 2 | 46 | -0.11687 | south | -0.18932 | -0.024212 | -0.18222 | -0.098126 | 0.024212 | south | N | 0.024212 | 0
9018 | SANDH_G3 | 3 | 46 | -0.11687 | south | -0.18932 | -0.024212 | -0.18222 | -0.098126 | 0.024212 | south | N | 0.024212 | 0
9019 | SANDH_G4 | 4 | 47 | -0.11687 | south | -0.18932 | -0.024212 | -0.18222 | -0.098126 | 0.024212 | south | N | 0.024212 | 0
9020 | SANDHG5A | 5A | 154 | -0.11687 | south | -0.18932 | -0.024212 | -0.18222 | -0.098126 | 0.024212 | south | N | 0.024212 | 0
9021 | SANDHG5C | 5C | 148 | -0.11687 | south | -0.18932 | -0.024212 | -0.18222 | -0.098126 | 0.024212 | south | N | 0.024212 | 0
9022 | SANDH_G6 | 6 | 48 | -0.11687 | south | -0.18932 | -0.024212 | -0.18222 | -0.098126 | 0.024212 | south | N | 0.024212 | 0
9023 | SANDH_G7 | 7 | 48 | -0.11687 | south | -0.18932 | -0.024212 | -0.18222 | -0.098126 | 0.024212 | south | N | 0.024212 | 0
11001 | NAV1CT | 1 | 70 | 0.065358 | west | -0.0070953 | 0.15801 | 9.6012e-06 | 0.084099 | 9.6012e-06 | west | N | 9.6012e-06 | 0
11009 | NAV2CT | 1 | 70 | 0.065358 | west | -0.0070953 | 0.15801 | 9.6012e-06 | 0.084099 | 9.6012e-06 | west | N | 9.6012e-06 | 0
11011 | NAV3ST | 1 | 92.8 | 0.065358 | west | -0.0070953 | 0.15801 | 9.6012e-06 | 0.084099 | 9.6012e-06 | west | N | 9.6012e-06 | 0
11012 | NAV4CT | 1 | 80 | 0.065358 | west | -0.0070953 | 0.15801 | 9.6012e-06 | 0.084099 | 9.6012e-06 | west | N | 9.6012e-06 | 0
11013 | NAV5CT | 1 | 80 | 0.065358 | west | -0.0070953 | 0.15801 | 9.6012e-06 | 0.084099 | 9.6012e-06 | west | N | 9.6012e-06 | 0
11014 | NAV6ST | 1 | 115 | 0.065358 | west | -0.0070953 | 0.15801 | 9.6012e-06 | 0.084099 | 9.6012e-06 | west | N | 9.6012e-06 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.065347 | west | -0.0071063 | 0.158 | -1.3988e-06 | 0.084088 | 1.3988e-06 | west | N | 1.3988e-06 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.065347 | west | -0.0071063 | 0.158 | -1.3988e-06 | 0.084088 | 1.3988e-06 | west | N | 1.3988e-06 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.065347 | west | -0.0071063 | 0.158 | -1.3988e-06 | 0.084088 | 1.3988e-06 | west | N | 1.3988e-06 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.065347 | west | -0.0071063 | 0.158 | -1.3988e-06 | 0.084088 | 1.3988e-06 | west | N | 1.3988e-06 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.065347 | west | -0.0071063 | 0.158 | -1.3988e-06 | 0.084088 | 1.3988e-06 | west | N | 1.3988e-06 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.065347 | west | -0.0071063 | 0.158 | -1.3988e-06 | 0.084088 | 1.3988e-06 | west | N | 1.3988e-06 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.067528 | west | -0.0049253 | 0.16018 | 0.0021796 | 0.086269 | 0.0021796 | west | N | 0.0021796 | 0
11057 | CHAMPION | 1 | 126.5 | 0.067528 | west | -0.0049253 | 0.16018 | 0.0021796 | 0.086269 | 0.0021796 | west | N | 0.0021796 | 0
11058 | PYRON_1G | 1 | 249 | 0.067528 | west | -0.0049253 | 0.16018 | 0.0021796 | 0.086269 | 0.0021796 | west | N | 0.0021796 | 0
11059 | INADALE_ | 1 | 197 | 0.067528 | west | -0.0049253 | 0.16018 | 0.0021796 | 0.086269 | 0.0021796 | west | N | 0.0021796 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.06637 | west | -0.0060833 | 0.15903 | 0.0010216 | 0.085111 | 0.0010216 | west | N | 0.0010216 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.06637 | west | -0.0060833 | 0.15903 | 0.0010216 | 0.085111 | 0.0010216 | west | N | 0.0010216 | 0
11147 | NOTREES_ | 1 | 149 | 0.064449 | west | -0.0080043 | 0.1571 | -0.0008994 | 0.08319 | 0.0008994 | west | N | 0.0008994 | 0
11309 | BULLCREK | 1 | 180 | 0.066164 | west | -0.0062893 | 0.15882 | 0.0008156 | 0.084905 | 0.0008156 | west | N | 0.0008156 | 0
11310 | BULLCREK | 1 | 180 | 0.066164 | west | -0.0062893 | 0.15882 | 0.0008156 | 0.084905 | 0.0008156 | west | N | 0.0008156 | 0
11320 | COYOTE_1 | 1 | 225 | 0.066104 | west | -0.0063493 | 0.15876 | 0.0007556 | 0.084845 | 0.0007556 | west | N | 0.0007556 | 0
11415 | LORAINE_ | 1 | 125 | 0.067026 | west | -0.0054273 | 0.15968 | 0.0016776 | 0.085767 | 0.0016776 | west | N | 0.0016776 | 0
11416 | LORAINE_ | 1 | 125 | 0.067026 | west | -0.0054273 | 0.15968 | 0.0016776 | 0.085767 | 0.0016776 | west | N | 0.0016776 | 0
11691 | KMICHICT | 1 | 140 | 0.075734 | north | 0.0032807 | 0.16839 | 0.010386 | 0.094475 | 0.0032807 | North | N | 0.0032807 | 0
11692 | KMICHICT | 2 | 141 | 0.075734 | north | 0.0032807 | 0.16839 | 0.010386 | 0.094475 | 0.0032807 | North | N | 0.0032807 | 0
11693 | KMICHIST | 3 | 309 | 0.075734 | north | 0.0032807 | 0.16839 | 0.010386 | 0.094475 | 0.0032807 | North | N | 0.0032807 | 0
11694 | KMICHICT | 4 | 143 | 0.075734 | north | 0.0032807 | 0.16839 | 0.010386 | 0.094475 | 0.0032807 | North | N | 0.0032807 | 0
11695 | KMICHICT | 5 | 144 | 0.075734 | north | 0.0032807 | 0.16839 | 0.010386 | 0.094475 | 0.0032807 | North | N | 0.0032807 | 0
11696 | KMICHIST | 6 | 310 | 0.075734 | north | 0.0032807 | 0.16839 | 0.010386 | 0.094475 | 0.0032807 | North | N | 0.0032807 | 0
12322 | ENNSTRAC | 1 | 196 | 0.07567 | north | 0.0032167 | 0.16833 | 0.010322 | 0.094411 | 0.0032167 | North | N | 0.0032167 | 0
12323 | ENNSTRAC | 2 | 111 | 0.07567 | north | 0.0032167 | 0.16833 | 0.010322 | 0.094411 | 0.0032167 | North | N | 0.0032167 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.076347 | north | 0.0038937 | 0.169 | 0.010999 | 0.095088 | 0.0038937 | North | N | 0.0038937 | 0
12411 | FPLEFR1A | 1 | 161 | 0.074895 | north | 0.0024417 | 0.16755 | 0.0095466 | 0.093636 | 0.0024417 | North | N | 0.0024417 | 0
12412 | FPLEFR1B | 2 | 164 | 0.074895 | north | 0.0024417 | 0.16755 | 0.0095466 | 0.093636 | 0.0024417 | North | N | 0.0024417 | 0
12413 | FPLEFR1C | 3 | 164 | 0.074895 | north | 0.0024417 | 0.16755 | 0.0095466 | 0.093636 | 0.0024417 | North | N | 0.0024417 | 0
12414 | FPLEFR1S | 4 | 414 | 0.074895 | north | 0.0024417 | 0.16755 | 0.0095466 | 0.093636 | 0.0024417 | North | N | 0.0024417 | 0
12421 | FPLEFR2A | 1 | 162 | 0.074895 | north | 0.0024417 | 0.16755 | 0.0095466 | 0.093636 | 0.0024417 | North | N | 0.0024417 | 0
12422 | FPLEFR2B | 2 | 161 | 0.074895 | north | 0.0024417 | 0.16755 | 0.0095466 | 0.093636 | 0.0024417 | North | N | 0.0024417 | 0
12423 | FPLEFR2C | 3 | 163 | 0.074895 | north | 0.0024417 | 0.16755 | 0.0095466 | 0.093636 | 0.0024417 | North | N | 0.0024417 | 0
12424 | FPLEFR2S | 4 | 409 | 0.074895 | north | 0.0024417 | 0.16755 | 0.0095466 | 0.093636 | 0.0024417 | North | N | 0.0024417 | 0
12440 | PARKD_1S | 1 | 0 | 0.07595 | north | 0.0034967 | 0.16861 | 0.010602 | 0.094691 | 0.0034967 | North | N | 0.0034967 | 0
12449 | PARKD_2S | 1 | 0 | 0.07595 | north | 0.0034967 | 0.16861 | 0.010602 | 0.094691 | 0.0034967 | North | N | 0.0034967 | 0
13116 | TGATEWAY | 1 | 148 | 0.071647 | north | -0.00080625 | 0.1643 | 0.0062986 | 0.090388 | 0.00080625 | North | N | 0.00080625 | 0
13117 | TGATEWAY | 2 | 130 | 0.071647 | north | -0.00080625 | 0.1643 | 0.0062986 | 0.090388 | 0.00080625 | North | N | 0.00080625 | 0
13118 | TGATEWAY | 3 | 145 | 0.071647 | north | -0.00080625 | 0.1643 | 0.0062986 | 0.090388 | 0.00080625 | North | N | 0.00080625 | 0
13119 | TGATEWAY | 4 | 399 | 0.071647 | north | -0.00080625 | 0.1643 | 0.0062986 | 0.090388 | 0.00080625 | North | N | 0.00080625 | 0
13131 | CALFREST | 1 | 150.7 | 0.067816 | north | -0.0046373 | 0.16047 | 0.0024676 | 0.086557 | 0.0024676 | west | Y | 0.0046373 | 0.32697
13132 | CALFREST | 2 | 151 | 0.067816 | north | -0.0046373 | 0.16047 | 0.0024676 | 0.086557 | 0.0024676 | west | Y | 0.0046373 | 0.32762
13133 | CALFREST | 3 | 177.4 | 0.067816 | north | -0.0046373 | 0.16047 | 0.0024676 | 0.086557 | 0.0024676 | west | Y | 0.0046373 | 0.3849
13134 | CALFREST | 4 | 151.5 | 0.067899 | north | -0.0045543 | 0.16055 | 0.0025506 | 0.08664 | 0.0025506 | west | Y | 0.0045543 | 0.30355
13135 | CALFREST | 5 | 152.3 | 0.067899 | north | -0.0045543 | 0.16055 | 0.0025506 | 0.08664 | 0.0025506 | west | Y | 0.0045543 | 0.30516
13136 | CALFREST | 6 | 177.5 | 0.067899 | north | -0.0045543 | 0.16055 | 0.0025506 | 0.08664 | 0.0025506 | west | Y | 0.0045543 | 0.35565
13432 | SANDOW_5 | 5 | 581 | -0.14089 | south | -0.21335 | -0.048238 | -0.20624 | -0.12215 | 0.048238 | south | N | 0.048238 | 0
13691 | OAKGROVE | 1 | 855 | 0.046247 | north | -0.026206 | 0.1389 | -0.019101 | 0.064988 | 0.019101 | west | Y | 0.026206 | 6.0746
13692 | OAKGROVE | 2 | 855 | 0.046247 | north | -0.026206 | 0.1389 | -0.019101 | 0.064988 | 0.019101 | west | Y | 0.026206 | 6.0746
32798 | BRYN_TAM | 1 | 32 | 0.021478 | north | -0.050975 | 0.11413 | -0.04387 | 0.040219 | 0.040219 | houston | Y | 0.050975 | 0.34421
32883 | BRYN_DNS | 1 | 48 | 0.019125 | north | -0.053328 | 0.11178 | -0.046223 | 0.037866 | 0.037866 | houston | Y | 0.053328 | 0.74221
32884 | BRYN_DNS | 1 | 46 | 0.019125 | north | -0.053328 | 0.11178 | -0.046223 | 0.037866 | 0.037866 | houston | Y | 0.053328 | 0.71128
32886 | BRYN_ATK | MB | 12 | 0.021507 | north | -0.050946 | 0.11416 | -0.043841 | 0.040248 | 0.040248 | houston | Y | 0.050946 | 0.12838
32887 | BRYN_ATK | MB | 51 | 0.021507 | north | -0.050946 | 0.11416 | -0.043841 | 0.040248 | 0.040248 | houston | Y | 0.050946 | 0.54563
32888 | BRYN_ATK | 1 | 17 | 0.021507 | north | -0.050946 | 0.11416 | -0.043841 | 0.040248 | 0.040248 | houston | Y | 0.050946 | 0.18188
32890 | BRYN_ATK | MB | 22 | 0.021507 | north | -0.050946 | 0.11416 | -0.043841 | 0.040248 | 0.040248 | houston | Y | 0.050946 | 0.23537
32891 | BRYN_ATK | MB | 25 | 0.021507 | north | -0.050946 | 0.11416 | -0.043841 | 0.040248 | 0.040248 | houston | Y | 0.050946 | 0.26747
32892 | BRYN_DNS | 1 | 105 | 0.019125 | north | -0.053328 | 0.11178 | -0.046223 | 0.037866 | 0.037866 | houston | Y | 0.053328 | 1.6236
36998 | RDCNYNG1 | 1 | 84 | 0.066784 | west | -0.0056693 | 0.15944 | 0.0014356 | 0.085525 | 0.0014356 | west | N | 0.0014356 | 0
38332 | WDWRDU2 | 1 | 80 | 0.057658 | west | -0.014795 | 0.15031 | -0.0076904 | 0.076399 | 0.0076904 | west | N | 0.0076904 | 0
38437 | TNSRBNMS | 1 | 150 | 0.057599 | west | -0.014854 | 0.15025 | -0.0077494 | 0.07634 | 0.0077494 | west | N | 0.0077494 | 0
38438 | TNSRBNMS | 1 | 150 | 0.057599 | west | -0.014854 | 0.15025 | -0.0077494 | 0.07634 | 0.0077494 | west | N | 0.0077494 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.019794 | houston | -0.092247 | 0.072861 | -0.085142 | -0.0010534 | 0.0010534 | houston | N | 0.0010534 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.019794 | houston | -0.092247 | 0.072861 | -0.085142 | -0.0010534 | 0.0010534 | houston | N | 0.0010534 | 0
38600 | TNBP_CGN | 5 | 53 | -0.019794 | houston | -0.092247 | 0.072861 | -0.085142 | -0.0010534 | 0.0010534 | houston | N | 0.0010534 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.019794 | houston | -0.092247 | 0.072861 | -0.085142 | -0.0010534 | 0.0010534 | houston | N | 0.0010534 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.019794 | houston | -0.092247 | 0.072861 | -0.085142 | -0.0010534 | 0.0010534 | houston | N | 0.0010534 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.019794 | houston | -0.092247 | 0.072861 | -0.085142 | -0.0010534 | 0.0010534 | houston | N | 0.0010534 | 0
38614 | TNBPAMCG | 4 | 96 | -0.019794 | houston | -0.092247 | 0.072861 | -0.085142 | -0.0010534 | 0.0010534 | houston | N | 0.0010534 | 0
38615 | TNBPAMCG | 1 | 244 | -0.019794 | houston | -0.092247 | 0.072861 | -0.085142 | -0.0010534 | 0.0010534 | houston | N | 0.0010534 | 0
38690 | TNBP_CGN | 3 | 40 | -0.019794 | houston | -0.092247 | 0.072861 | -0.085142 | -0.0010534 | 0.0010534 | houston | N | 0.0010534 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.01981 | houston | -0.092263 | 0.072845 | -0.085158 | -0.0010694 | 0.0010694 | houston | N | 0.0010694 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.01981 | houston | -0.092263 | 0.072845 | -0.085158 | -0.0010694 | 0.0010694 | houston | N | 0.0010694 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.01981 | houston | -0.092263 | 0.072845 | -0.085158 | -0.0010694 | 0.0010694 | houston | N | 0.0010694 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.01981 | houston | -0.092263 | 0.072845 | -0.085158 | -0.0010694 | 0.0010694 | houston | N | 0.0010694 | 0
39470 | TNDOWCGN | 1 | 32 | -0.019809 | houston | -0.092262 | 0.072846 | -0.085157 | -0.0010684 | 0.0010684 | houston | N | 0.0010684 | 0
39480 | TNDOWCGN | 1 | 30 | -0.019809 | houston | -0.092262 | 0.072846 | -0.085157 | -0.0010684 | 0.0010684 | houston | N | 0.0010684 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.029662 | houston | -0.10212 | 0.062993 | -0.09501 | -0.010921 | 0.010921 | houston | N | 0.010921 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.029662 | houston | -0.10212 | 0.062993 | -0.09501 | -0.010921 | 0.010921 | houston | N | 0.010921 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.029662 | houston | -0.10212 | 0.062993 | -0.09501 | -0.010921 | 0.010921 | houston | N | 0.010921 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.029662 | houston | -0.10212 | 0.062993 | -0.09501 | -0.010921 | 0.010921 | houston | N | 0.010921 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.046247 | north | -0.026206 | 0.1389 | -0.019101 | 0.064988 | 0.019101 | west | Y | 0.026206 | 1.0821
39970 | TNTNPONE | 1 | 153 | 0.046247 | north | -0.026206 | 0.1389 | -0.019101 | 0.064988 | 0.019101 | west | Y | 0.026206 | 1.087
48500 | APD_GT1_ | 1 | 136 | -0.013794 | houston | -0.086247 | 0.078861 | -0.079142 | 0.0049466 | 0.0049466 | houston | N | 0.0049466 | 0
48510 | AK_GT1__ | 1 | 33 | -0.023081 | houston | -0.095534 | 0.069574 | -0.088429 | -0.0043404 | 0.0043404 | houston | N | 0.0043404 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.013759 | houston | -0.086212 | 0.078896 | -0.079107 | 0.0049816 | 0.0049816 | houston | N | 0.0049816 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.013759 | houston | -0.086212 | 0.078896 | -0.079107 | 0.0049816 | 0.0049816 | houston | N | 0.0049816 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.013759 | houston | -0.086212 | 0.078896 | -0.079107 | 0.0049816 | 0.0049816 | houston | N | 0.0049816 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.013759 | houston | -0.086212 | 0.078896 | -0.079107 | 0.0049816 | 0.0049816 | houston | N | 0.0049816 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.031242 | houston | -0.1037 | 0.061413 | -0.09659 | -0.012501 | 0.012501 | houston | N | 0.012501 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.031242 | houston | -0.1037 | 0.061413 | -0.09659 | -0.012501 | 0.012501 | houston | N | 0.012501 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.023674 | houston | -0.096127 | 0.068981 | -0.089022 | -0.0049334 | 0.0049334 | houston | N | 0.0049334 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.023674 | houston | -0.096127 | 0.068981 | -0.089022 | -0.0049334 | 0.0049334 | houston | N | 0.0049334 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.023674 | houston | -0.096127 | 0.068981 | -0.089022 | -0.0049334 | 0.0049334 | houston | N | 0.0049334 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.016034 | houston | -0.088487 | 0.076621 | -0.081382 | 0.0027066 | 0.0027066 | houston | N | 0.0027066 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.016034 | houston | -0.088487 | 0.076621 | -0.081382 | 0.0027066 | 0.0027066 | houston | N | 0.0027066 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.016034 | houston | -0.088487 | 0.076621 | -0.081382 | 0.0027066 | 0.0027066 | houston | N | 0.0027066 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.016034 | houston | -0.088487 | 0.076621 | -0.081382 | 0.0027066 | 0.0027066 | houston | N | 0.0027066 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.014573 | houston | -0.087026 | 0.078082 | -0.079921 | 0.0041676 | 0.0041676 | houston | N | 0.0041676 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.014573 | houston | -0.087026 | 0.078082 | -0.079921 | 0.0041676 | 0.0041676 | houston | N | 0.0041676 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.016474 | houston | -0.088927 | 0.076181 | -0.081822 | 0.0022666 | 0.0022666 | houston | N | 0.0022666 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.016474 | houston | -0.088927 | 0.076181 | -0.081822 | 0.0022666 | 0.0022666 | houston | N | 0.0022666 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.016474 | houston | -0.088927 | 0.076181 | -0.081822 | 0.0022666 | 0.0022666 | houston | N | 0.0022666 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.016474 | houston | -0.088927 | 0.076181 | -0.081822 | 0.0022666 | 0.0022666 | houston | N | 0.0022666 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.016474 | houston | -0.088927 | 0.076181 | -0.081822 | 0.0022666 | 0.0022666 | houston | N | 0.0022666 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.011925 | houston | -0.084378 | 0.08073 | -0.077273 | 0.0068156 | 0.0068156 | houston | N | 0.0068156 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.012669 | houston | -0.085122 | 0.079986 | -0.078017 | 0.0060716 | 0.0060716 | houston | N | 0.0060716 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.011701 | houston | -0.084154 | 0.080954 | -0.077049 | 0.0070396 | 0.0070396 | houston | N | 0.0070396 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.011701 | houston | -0.084154 | 0.080954 | -0.077049 | 0.0070396 | 0.0070396 | houston | N | 0.0070396 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.011701 | houston | -0.084154 | 0.080954 | -0.077049 | 0.0070396 | 0.0070396 | houston | N | 0.0070396 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.007573 | houston | -0.080026 | 0.085082 | -0.072921 | 0.011168 | 0.011168 | houston | N | 0.011168 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.013646 | houston | -0.086099 | 0.079009 | -0.078994 | 0.0050946 | 0.0050946 | houston | N | 0.0050946 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.013646 | houston | -0.086099 | 0.079009 | -0.078994 | 0.0050946 | 0.0050946 | houston | N | 0.0050946 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.011175 | houston | -0.083628 | 0.08148 | -0.076523 | 0.0075656 | 0.0075656 | houston | N | 0.0075656 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.011175 | houston | -0.083628 | 0.08148 | -0.076523 | 0.0075656 | 0.0075656 | houston | N | 0.0075656 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.011175 | houston | -0.083628 | 0.08148 | -0.076523 | 0.0075656 | 0.0075656 | houston | N | 0.0075656 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.011175 | houston | -0.083628 | 0.08148 | -0.076523 | 0.0075656 | 0.0075656 | houston | N | 0.0075656 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.014524 | houston | -0.086977 | 0.078131 | -0.079872 | 0.0042166 | 0.0042166 | houston | N | 0.0042166 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.014524 | houston | -0.086977 | 0.078131 | -0.079872 | 0.0042166 | 0.0042166 | houston | N | 0.0042166 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.014524 | houston | -0.086977 | 0.078131 | -0.079872 | 0.0042166 | 0.0042166 | houston | N | 0.0042166 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.014524 | houston | -0.086977 | 0.078131 | -0.079872 | 0.0042166 | 0.0042166 | houston | N | 0.0042166 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.014991 | houston | -0.087444 | 0.077664 | -0.080339 | 0.0037496 | 0.0037496 | houston | N | 0.0037496 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.014991 | houston | -0.087444 | 0.077664 | -0.080339 | 0.0037496 | 0.0037496 | houston | N | 0.0037496 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.014991 | houston | -0.087444 | 0.077664 | -0.080339 | 0.0037496 | 0.0037496 | houston | N | 0.0037496 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.014991 | houston | -0.087444 | 0.077664 | -0.080339 | 0.0037496 | 0.0037496 | houston | N | 0.0037496 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.014991 | houston | -0.087444 | 0.077664 | -0.080339 | 0.0037496 | 0.0037496 | houston | N | 0.0037496 | 0
48651 | EP_1_2 | 1 | 5 | -0.011965 | houston | -0.084418 | 0.08069 | -0.077313 | 0.0067756 | 0.0067756 | houston | N | 0.0067756 | 0
48651 | EP_1_2 | 2 | 21 | -0.011965 | houston | -0.084418 | 0.08069 | -0.077313 | 0.0067756 | 0.0067756 | houston | N | 0.0067756 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.021529 | north | -0.050924 | 0.11418 | -0.043819 | 0.04027 | 0.04027 | houston | Y | 0.050924 | 1.6429
48672 | FTR_GT2_ | 2 | 156 | 0.021529 | north | -0.050924 | 0.11418 | -0.043819 | 0.04027 | 0.04027 | houston | Y | 0.050924 | 1.6621
48673 | FTR_GT3_ | 3 | 156 | 0.021529 | north | -0.050924 | 0.11418 | -0.043819 | 0.04027 | 0.04027 | houston | Y | 0.050924 | 1.6621
48674 | FTR_CN4_ | 4 | 380 | 0.021529 | north | -0.050924 | 0.11418 | -0.043819 | 0.04027 | 0.04027 | houston | Y | 0.050924 | 4.0488
48690 | GBY_GN5_ | 5 | 398 | -0.010993 | houston | -0.083446 | 0.081662 | -0.076341 | 0.0077476 | 0.0077476 | houston | N | 0.0077476 | 0
48691 | GBY_7374 | A | 46 | -0.015379 | houston | -0.087832 | 0.077276 | -0.080727 | 0.0033616 | 0.0033616 | houston | N | 0.0033616 | 0
48691 | GBY_7374 | B | 46 | -0.015379 | houston | -0.087832 | 0.077276 | -0.080727 | 0.0033616 | 0.0033616 | houston | N | 0.0033616 | 0
48692 | GBY_8182 | C | 46 | -0.015379 | houston | -0.087832 | 0.077276 | -0.080727 | 0.0033616 | 0.0033616 | houston | N | 0.0033616 | 0
48692 | GBY_8182 | D | 55 | -0.015379 | houston | -0.087832 | 0.077276 | -0.080727 | 0.0033616 | 0.0033616 | houston | N | 0.0033616 | 0
48693 | GBY_8384 | E | 55 | -0.015379 | houston | -0.087832 | 0.077276 | -0.080727 | 0.0033616 | 0.0033616 | houston | N | 0.0033616 | 0
48693 | GBY_8384 | F | 54 | -0.015379 | houston | -0.087832 | 0.077276 | -0.080727 | 0.0033616 | 0.0033616 | houston | N | 0.0033616 | 0
48721 | LEG_1___ | 1 | 827 | 0.05461 | north | -0.017843 | 0.14727 | -0.010738 | 0.073351 | 0.010738 | west | Y | 0.017843 | 5.8757
48722 | LEG_2___ | 2 | 819 | 0.05461 | north | -0.017843 | 0.14727 | -0.010738 | 0.073351 | 0.010738 | west | Y | 0.017843 | 5.8189
48730 | MNS_GT | 1 | 46.1 | -0.023936 | houston | -0.096389 | 0.068719 | -0.089284 | -0.0051954 | 0.0051954 | houston | N | 0.0051954 | 0
48731 | CBE_GT1 | 1 | 76 | -0.044138 | houston | -0.11659 | 0.048517 | -0.10949 | -0.025397 | 0.025397 | houston | N | 0.025397 | 0
48732 | CBE_GT2 | 1 | 76 | -0.044138 | houston | -0.11659 | 0.048517 | -0.10949 | -0.025397 | 0.025397 | houston | N | 0.025397 | 0
48733 | CBE_ST12 | 1 | 105 | -0.044138 | houston | -0.11659 | 0.048517 | -0.10949 | -0.025397 | 0.025397 | houston | N | 0.025397 | 0
48734 | CBE_GT3 | 1 | 74 | -0.044138 | houston | -0.11659 | 0.048517 | -0.10949 | -0.025397 | 0.025397 | houston | N | 0.025397 | 0
48735 | CBE_GT4 | 1 | 74 | -0.044138 | houston | -0.11659 | 0.048517 | -0.10949 | -0.025397 | 0.025397 | houston | N | 0.025397 | 0
48736 | CBE_ST34 | 1 | 102 | -0.044138 | houston | -0.11659 | 0.048517 | -0.10949 | -0.025397 | 0.025397 | houston | N | 0.025397 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.01451 | houston | -0.086963 | 0.078145 | -0.079858 | 0.0042306 | 0.0042306 | houston | N | 0.0042306 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.01451 | houston | -0.086963 | 0.078145 | -0.079858 | 0.0042306 | 0.0042306 | houston | N | 0.0042306 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.01451 | houston | -0.086963 | 0.078145 | -0.079858 | 0.0042306 | 0.0042306 | houston | N | 0.0042306 | 0
48761 | PR_GT1__ | 1 | 35 | -0.014808 | houston | -0.087261 | 0.077847 | -0.080156 | 0.0039326 | 0.0039326 | houston | N | 0.0039326 | 0
48772 | PHR_GN2_ | MB | 459 | -0.017597 | houston | -0.09005 | 0.075058 | -0.082945 | 0.0011436 | 0.0011436 | houston | N | 0.0011436 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.01196 | houston | -0.084413 | 0.080695 | -0.077308 | 0.0067806 | 0.0067806 | houston | N | 0.0067806 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.01196 | houston | -0.084413 | 0.080695 | -0.077308 | 0.0067806 | 0.0067806 | houston | N | 0.0067806 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.01196 | houston | -0.084413 | 0.080695 | -0.077308 | 0.0067806 | 0.0067806 | houston | N | 0.0067806 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.01196 | houston | -0.084413 | 0.080695 | -0.077308 | 0.0067806 | 0.0067806 | houston | N | 0.0067806 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.01196 | houston | -0.084413 | 0.080695 | -0.077308 | 0.0067806 | 0.0067806 | houston | N | 0.0067806 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.01196 | houston | -0.084413 | 0.080695 | -0.077308 | 0.0067806 | 0.0067806 | houston | N | 0.0067806 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.01196 | houston | -0.084413 | 0.080695 | -0.077308 | 0.0067806 | 0.0067806 | houston | N | 0.0067806 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.007573 | houston | -0.080026 | 0.085082 | -0.072921 | 0.011168 | 0.011168 | houston | N | 0.011168 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.007573 | houston | -0.080026 | 0.085082 | -0.072921 | 0.011168 | 0.011168 | houston | N | 0.011168 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.007573 | houston | -0.080026 | 0.085082 | -0.072921 | 0.011168 | 0.011168 | houston | N | 0.011168 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.007573 | houston | -0.080026 | 0.085082 | -0.072921 | 0.011168 | 0.011168 | houston | N | 0.011168 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.01179 | houston | -0.084243 | 0.080865 | -0.077138 | 0.0069506 | 0.0069506 | houston | N | 0.0069506 | 0
48820 | SHELLG1_ | 1 | 71 | -0.014233 | houston | -0.086686 | 0.078422 | -0.079581 | 0.0045076 | 0.0045076 | houston | N | 0.0045076 | 0
48821 | SHELLG2 | 2 | 72 | -0.014233 | houston | -0.086686 | 0.078422 | -0.079581 | 0.0045076 | 0.0045076 | houston | N | 0.0045076 | 0
48822 | SHELLG3_ | 1 | 39 | -0.014233 | houston | -0.086686 | 0.078422 | -0.079581 | 0.0045076 | 0.0045076 | houston | N | 0.0045076 | 0
48822 | SHELLG3_ | 2 | 30 | -0.014233 | houston | -0.086686 | 0.078422 | -0.079581 | 0.0045076 | 0.0045076 | houston | N | 0.0045076 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.015216 | houston | -0.087669 | 0.077439 | -0.080564 | 0.0035246 | 0.0035246 | houston | N | 0.0035246 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.015216 | houston | -0.087669 | 0.077439 | -0.080564 | 0.0035246 | 0.0035246 | houston | N | 0.0035246 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.014528 | houston | -0.086981 | 0.078127 | -0.079876 | 0.0042126 | 0.0042126 | houston | N | 0.0042126 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.014585 | houston | -0.087038 | 0.07807 | -0.079933 | 0.0041556 | 0.0041556 | houston | N | 0.0041556 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.0146 | houston | -0.087053 | 0.078055 | -0.079948 | 0.0041406 | 0.0041406 | houston | N | 0.0041406 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.014533 | houston | -0.086986 | 0.078122 | -0.079881 | 0.0042076 | 0.0042076 | houston | N | 0.0042076 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.014517 | houston | -0.08697 | 0.078138 | -0.079865 | 0.0042236 | 0.0042236 | houston | N | 0.0042236 | 0
48855 | SRB_GT21 | B2 | 12 | -0.014611 | houston | -0.087064 | 0.078044 | -0.079959 | 0.0041296 | 0.0041296 | houston | N | 0.0041296 | 0
48855 | SRB_GT21 | MB | 18 | -0.014611 | houston | -0.087064 | 0.078044 | -0.079959 | 0.0041296 | 0.0041296 | houston | N | 0.0041296 | 0
48865 | TECO_GT1 | 1 | 50 | -0.018559 | houston | -0.091012 | 0.074096 | -0.083907 | 0.00018161 | 0.00018161 | houston | N | 0.00018161 | 0
48873 | THW_ST3_ | 3 | 104 | -0.01294 | houston | -0.085393 | 0.079715 | -0.078288 | 0.0058006 | 0.0058006 | houston | N | 0.0058006 | 0
48874 | THW_ST4_ | 4 | 104 | -0.01294 | houston | -0.085393 | 0.079715 | -0.078288 | 0.0058006 | 0.0058006 | houston | N | 0.0058006 | 0
48875 | THW_3132 | A | 54 | -0.01294 | houston | -0.085393 | 0.079715 | -0.078288 | 0.0058006 | 0.0058006 | houston | N | 0.0058006 | 0
48875 | THW_3132 | B | 53 | -0.01294 | houston | -0.085393 | 0.079715 | -0.078288 | 0.0058006 | 0.0058006 | houston | N | 0.0058006 | 0
48877 | THW_3334 | C | 54 | -0.01294 | houston | -0.085393 | 0.079715 | -0.078288 | 0.0058006 | 0.0058006 | houston | N | 0.0058006 | 0
48877 | THW_3334 | D | 57 | -0.01294 | houston | -0.085393 | 0.079715 | -0.078288 | 0.0058006 | 0.0058006 | houston | N | 0.0058006 | 0
48879 | THW_4142 | E | 54 | -0.01294 | houston | -0.085393 | 0.079715 | -0.078288 | 0.0058006 | 0.0058006 | houston | N | 0.0058006 | 0
48879 | THW_4142 | F | 54 | -0.01294 | houston | -0.085393 | 0.079715 | -0.078288 | 0.0058006 | 0.0058006 | houston | N | 0.0058006 | 0
48881 | THW_4344 | G | 58 | -0.01294 | houston | -0.085393 | 0.079715 | -0.078288 | 0.0058006 | 0.0058006 | houston | N | 0.0058006 | 0
48881 | THW_4344 | H | 58 | -0.01294 | houston | -0.085393 | 0.079715 | -0.078288 | 0.0058006 | 0.0058006 | houston | N | 0.0058006 | 0
48883 | THW_GT1_ | B2 | 12 | -0.012257 | houston | -0.08471 | 0.080398 | -0.077605 | 0.0064836 | 0.0064836 | houston | N | 0.0064836 | 0
48885 | THW_5152 | A | 56 | -0.010672 | houston | -0.083125 | 0.081983 | -0.07602 | 0.0080686 | 0.0080686 | houston | N | 0.0080686 | 0
48885 | THW_5152 | B | 59 | -0.010672 | houston | -0.083125 | 0.081983 | -0.07602 | 0.0080686 | 0.0080686 | houston | N | 0.0080686 | 0
48886 | THW_5354 | C | 56 | -0.010672 | houston | -0.083125 | 0.081983 | -0.07602 | 0.0080686 | 0.0080686 | houston | N | 0.0080686 | 0
48886 | THW_5354 | D | 56 | -0.010672 | houston | -0.083125 | 0.081983 | -0.07602 | 0.0080686 | 0.0080686 | houston | N | 0.0080686 | 0
48887 | THW_5556 | E | 59 | -0.010672 | houston | -0.083125 | 0.081983 | -0.07602 | 0.0080686 | 0.0080686 | houston | N | 0.0080686 | 0
48887 | THW_5556 | F | 56 | -0.010672 | houston | -0.083125 | 0.081983 | -0.07602 | 0.0080686 | 0.0080686 | houston | N | 0.0080686 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.041523 | houston | -0.11398 | 0.051132 | -0.10687 | -0.022782 | 0.022782 | houston | N | 0.022782 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.02282 | houston | -0.095273 | 0.069835 | -0.088168 | -0.0040794 | 0.0040794 | houston | N | 0.0040794 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.02282 | houston | -0.095273 | 0.069835 | -0.088168 | -0.0040794 | 0.0040794 | houston | N | 0.0040794 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.02282 | houston | -0.095273 | 0.069835 | -0.088168 | -0.0040794 | 0.0040794 | houston | N | 0.0040794 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.02282 | houston | -0.095273 | 0.069835 | -0.088168 | -0.0040794 | 0.0040794 | houston | N | 0.0040794 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.02282 | houston | -0.095273 | 0.069835 | -0.088168 | -0.0040794 | 0.0040794 | houston | N | 0.0040794 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.023722 | houston | -0.096175 | 0.068933 | -0.08907 | -0.0049814 | 0.0049814 | houston | N | 0.0049814 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.023722 | houston | -0.096175 | 0.068933 | -0.08907 | -0.0049814 | 0.0049814 | houston | N | 0.0049814 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.023722 | houston | -0.096175 | 0.068933 | -0.08907 | -0.0049814 | 0.0049814 | houston | N | 0.0049814 | 0
48929 | WAPGT21_ | B1 | 13 | -0.02282 | houston | -0.095273 | 0.069835 | -0.088168 | -0.0040794 | 0.0040794 | houston | N | 0.0040794 | 0
48940 | WARVUE_G | G1 | 12 | -0.011946 | houston | -0.084399 | 0.080709 | -0.077294 | 0.0067946 | 0.0067946 | houston | N | 0.0067946 | 0
49803 | EXN_15GT | 1 | 34 | -0.012489 | houston | -0.084942 | 0.080166 | -0.077837 | 0.0062516 | 0.0062516 | houston | N | 0.0062516 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.012489 | houston | -0.084942 | 0.080166 | -0.077837 | 0.0062516 | 0.0062516 | houston | N | 0.0062516 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.012489 | houston | -0.084942 | 0.080166 | -0.077837 | 0.0062516 | 0.0062516 | houston | N | 0.0062516 | 0
49826 | EXN938GT | 5 | 45.9 | -0.012489 | houston | -0.084942 | 0.080166 | -0.077837 | 0.0062516 | 0.0062516 | houston | N | 0.0062516 | 0
49828 | EXN941GT | 10 | 17.7 | -0.012489 | houston | -0.084942 | 0.080166 | -0.077837 | 0.0062516 | 0.0062516 | houston | N | 0.0062516 | 0
49829 | EXN942GT | 11 | 20.4 | -0.012489 | houston | -0.084942 | 0.080166 | -0.077837 | 0.0062516 | 0.0062516 | houston | N | 0.0062516 | 0
49830 | EXN943GT | 12 | 19.9 | -0.012489 | houston | -0.084942 | 0.080166 | -0.077837 | 0.0062516 | 0.0062516 | houston | N | 0.0062516 | 0
49831 | EXN944GT | 13 | 35 | -0.012489 | houston | -0.084942 | 0.080166 | -0.077837 | 0.0062516 | 0.0062516 | houston | N | 0.0062516 | 0
49832 | EXN945GT | 9 | 18 | -0.012489 | houston | -0.084942 | 0.080166 | -0.077837 | 0.0062516 | 0.0062516 | houston | N | 0.0062516 | 0
49837 | EXN_GT | 4 | 85.4 | -0.012489 | houston | -0.084942 | 0.080166 | -0.077837 | 0.0062516 | 0.0062516 | houston | N | 0.0062516 | 0
49838 | EXN_14GT | 14 | 148 | -0.012489 | houston | -0.084942 | 0.080166 | -0.077837 | 0.0062516 | 0.0062516 | houston | N | 0.0062516 | 0
49851 | DOW17000 | 37 | 62 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49858 | DOW38100 | 31 | 71.4 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49859 | DOW38200 | 33 | 45 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49860 | DOW38300 | 32 | 101 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49862 | DOW39100 | 36 | 86 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49863 | DOW39200 | 35 | 88 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49865 | DOW41000 | 41 | 50 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49866 | DOW42000 | 42 | 18 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49869 | DOW49000 | 45 | 94 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49870 | DOW61000 | 61 | 70 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49871 | DOW62000 | 62 | 63 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49872 | DOW63000 | 63 | 72 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49873 | DOW64000 | 64 | 64.8 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49876 | DOW65000 | 65 | 101 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49877 | DOW66000 | 66 | 97 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49878 | DOW67000 | 67 | 103 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49882 | DOW81000 | 81 | 76 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49884 | DOW82000 | 82 | 80 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49885 | DOW83000 | 83 | 80 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
49886 | DOW84000 | 84 | 171 | -0.03324 | houston | -0.10569 | 0.059415 | -0.098588 | -0.014499 | 0.014499 | houston | N | 0.014499 | 0
58909 | PEARSALL | 1 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58909 | PEARSALL | 2 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58909 | PEARSALL | 3 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58909 | PEARSALL | 4 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58909 | PEARSALL | 5 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58909 | PEARSALL | 6 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58919 | PEARSALL | 1 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58919 | PEARSALL | 2 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58919 | PEARSALL | 3 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58919 | PEARSALL | 4 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58919 | PEARSALL | 5 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58919 | PEARSALL | 6 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58929 | PEARSALL | 1 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58929 | PEARSALL | 2 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58929 | PEARSALL | 3 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58929 | PEARSALL | 4 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58929 | PEARSALL | 5 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58929 | PEARSALL | 6 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58949 | PEARSALL | 1 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58949 | PEARSALL | 2 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58949 | PEARSALL | 3 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58949 | PEARSALL | 4 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58949 | PEARSALL | 5 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
58949 | PEARSALL | 6 | 8.4 | -0.076673 | south | -0.14913 | 0.015982 | -0.14202 | -0.057932 | 0.015982 | south | N | 0.015982 | 0
60000 | DSKY2 | 1 | 76.5 | 0.054851 | west | -0.017602 | 0.14751 | -0.010497 | 0.073592 | 0.010497 | west | N | 0.010497 | 0
60003 | KING_NE1 | 1 | 80 | 0.057773 | west | -0.01468 | 0.15043 | -0.0075754 | 0.076514 | 0.0075754 | west | N | 0.0075754 | 0
60005 | KING_SE1 | 1 | 40 | 0.057773 | west | -0.01468 | 0.15043 | -0.0075754 | 0.076514 | 0.0075754 | west | N | 0.0075754 | 0
60007 | KING_SW1 | 1 | 80 | 0.05824 | west | -0.014213 | 0.1509 | -0.0071084 | 0.076981 | 0.0071084 | west | N | 0.0071084 | 0
60016 | WOODWRD1 | 1 | 80 | 0.057672 | west | -0.014781 | 0.15033 | -0.0076764 | 0.076413 | 0.0076764 | west | N | 0.0076764 | 0
60017 | ORNNWP1 | 1 | 80 | 0.055263 | west | -0.01719 | 0.14792 | -0.010085 | 0.074004 | 0.010085 | west | N | 0.010085 | 0
60018 | DSKY1 | 1 | 84 | 0.054475 | west | -0.017978 | 0.14713 | -0.010873 | 0.073216 | 0.010873 | west | N | 0.010873 | 0
60019 | KING_NW1 | 1 | 80 | 0.05824 | west | -0.014213 | 0.1509 | -0.0071084 | 0.076981 | 0.0071084 | west | N | 0.0071084 | 0
60057 | CALLAHAN | 1 | 114 | -0.092678 | south | -0.16513 | -2.2705e-05 | -0.15803 | -0.073937 | 2.2705e-05 | south | N | 2.2705e-05 | 0
60058 | BUFF_GAP | 1 | 120 | 0.065794 | west | -0.0066593 | 0.15845 | 0.0004456 | 0.084535 | 0.0004456 | west | N | 0.0004456 | 0
60060 | CIRELLO | 1 | 233 | 0.065794 | west | -0.0066593 | 0.15845 | 0.0004456 | 0.084535 | 0.0004456 | west | N | 0.0004456 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.065794 | west | -0.0066593 | 0.15845 | 0.0004456 | 0.084535 | 0.0004456 | west | N | 0.0004456 | 0
60066 | H_HOLLOW | 1 | 222 | -0.092678 | south | -0.16513 | -2.2705e-05 | -0.15803 | -0.073937 | 2.2705e-05 | south | N | 2.2705e-05 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.092678 | south | -0.16513 | -2.2705e-05 | -0.15803 | -0.073937 | 2.2705e-05 | south | N | 2.2705e-05 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.092678 | south | -0.16513 | -2.2705e-05 | -0.15803 | -0.073937 | 2.2705e-05 | south | N | 2.2705e-05 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.092678 | south | -0.16513 | -2.2705e-05 | -0.15803 | -0.073937 | 2.2705e-05 | south | N | 2.2705e-05 | 0
60074 | HORSH5 | 1 | 100 | -0.092678 | south | -0.16513 | -2.2705e-05 | -0.15803 | -0.073937 | 2.2705e-05 | south | N | 2.2705e-05 | 0
60081 | WHRLWIND | 1 | 60 | 0.06846 | west | -0.0039933 | 0.16112 | 0.0031116 | 0.087201 | 0.0031116 | west | N | 0.0031116 | 0
60201 | RIO DRCS | F | 0 | -0.050537 | south | -0.12299 | 0.042118 | -0.11589 | -0.031796 | 0.031796 | houston | Y | 0.042118 | 0
60202 | FRIEND_R | F | 0 | 0.041916 | west | -0.030537 | 0.13457 | -0.023432 | 0.060657 | 0.023432 | west | N | 0.023432 | 0
60203 | PRES0A | BT | 4.8 | 0.059986 | west | -0.012467 | 0.15264 | -0.0053624 | 0.078727 | 0.0053624 | west | N | 0.0053624 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.067352 | west | -0.0051013 | 0.16001 | 0.0020036 | 0.086093 | 0.0020036 | west | N | 0.0020036 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.067352 | west | -0.0051013 | 0.16001 | 0.0020036 | 0.086093 | 0.0020036 | west | N | 0.0020036 | 0
71057 | L_SWEETW | W1 | 135 | 0.067352 | west | -0.0051013 | 0.16001 | 0.0020036 | 0.086093 | 0.0020036 | west | N | 0.0020036 | 0
71059 | L_SWEETW | W1 | 119 | 0.067352 | west | -0.0051013 | 0.16001 | 0.0020036 | 0.086093 | 0.0020036 | west | N | 0.0020036 | 0
71060 | L_SWEETW | W1 | 105 | 0.067352 | west | -0.0051013 | 0.16001 | 0.0020036 | 0.086093 | 0.0020036 | west | N | 0.0020036 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.067352 | west | -0.0051013 | 0.16001 | 0.0020036 | 0.086093 | 0.0020036 | west | N | 0.0020036 | 0
76031 | L_GASCCR | W1 | 150 | 0.065096 | west | -0.0073573 | 0.15775 | -0.0002524 | 0.083837 | 0.0002524 | west | N | 0.0002524 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.064794 | west | -0.0076593 | 0.15745 | -0.0005544 | 0.083535 | 0.0005544 | west | N | 0.0005544 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.064794 | west | -0.0076593 | 0.15745 | -0.0005544 | 0.083535 | 0.0005544 | west | N | 0.0005544 | 0
76096 | L_CAPRSI | W1 | 186 | 0.064794 | west | -0.0076593 | 0.15745 | -0.0005544 | 0.083535 | 0.0005544 | west | N | 0.0005544 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.064794 | west | -0.0076593 | 0.15745 | -0.0005544 | 0.083535 | 0.0005544 | west | N | 0.0005544 | 0
80003 | MILHWYS | F | 0 | -0.072972 | south | -0.14543 | 0.019683 | -0.13832 | -0.054231 | 0.019683 | south | N | 0.019683 | 0
80010 | EPLVT1 | F | 0 | -0.054941 | south | -0.12739 | 0.037714 | -0.12029 | -0.0362 | 0.0362 | houston | Y | 0.037714 | 0
80012 | LAR | F | 0 | -0.077008 | south | -0.14946 | 0.015647 | -0.14236 | -0.058267 | 0.015647 | south | N | 0.015647 | 0
80051 | FORPVCM0 | 8 | 28 | -0.066239 | south | -0.13869 | 0.026416 | -0.13159 | -0.047498 | 0.026416 | south | N | 0.026416 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.066239 | south | -0.13869 | 0.026416 | -0.13159 | -0.047498 | 0.026416 | south | N | 0.026416 | 0
80053 | FOR69CG0 | 10 | 74 | -0.066239 | south | -0.13869 | 0.026416 | -0.13159 | -0.047498 | 0.026416 | south | N | 0.026416 | 0
80080 | GWINDT11 | 1 | 94 | -0.072922 | south | -0.14538 | 0.019733 | -0.13827 | -0.054181 | 0.019733 | south | N | 0.019733 | 0
80080 | GWINDT11 | 2 | 41 | -0.072922 | south | -0.14538 | 0.019733 | -0.13827 | -0.054181 | 0.019733 | south | N | 0.019733 | 0
80080 | GWINDT11 | 3 | 38 | -0.072922 | south | -0.14538 | 0.019733 | -0.13827 | -0.054181 | 0.019733 | south | N | 0.019733 | 0
80080 | GWINDT11 | 4 | 19 | -0.072922 | south | -0.14538 | 0.019733 | -0.13827 | -0.054181 | 0.019733 | south | N | 0.019733 | 0
80081 | GWINDT21 | 1 | 94 | -0.072922 | south | -0.14538 | 0.019733 | -0.13827 | -0.054181 | 0.019733 | south | N | 0.019733 | 0
80081 | GWINDT21 | 2 | 36 | -0.072922 | south | -0.14538 | 0.019733 | -0.13827 | -0.054181 | 0.019733 | south | N | 0.019733 | 0
80081 | GWINDT21 | 3 | 43 | -0.072922 | south | -0.14538 | 0.019733 | -0.13827 | -0.054181 | 0.019733 | south | N | 0.019733 | 0
80081 | GWINDT21 | 4 | 22 | -0.072922 | south | -0.14538 | 0.019733 | -0.13827 | -0.054181 | 0.019733 | south | N | 0.019733 | 0
80137 | CSDR89 | 8 | 39 | -0.068798 | south | -0.14125 | 0.023857 | -0.13415 | -0.050057 | 0.023857 | south | N | 0.023857 | 0
80137 | CSDR89 | 9 | 15 | -0.068798 | south | -0.14125 | 0.023857 | -0.13415 | -0.050057 | 0.023857 | south | N | 0.023857 | 0
80138 | CSDR7 | 7 | 7 | -0.068798 | south | -0.14125 | 0.023857 | -0.13415 | -0.050057 | 0.023857 | south | N | 0.023857 | 0
80139 | CSDR56 | 5 | 15 | -0.068798 | south | -0.14125 | 0.023857 | -0.13415 | -0.050057 | 0.023857 | south | N | 0.023857 | 0
80139 | CSDR56 | 6 | 39 | -0.068798 | south | -0.14125 | 0.023857 | -0.13415 | -0.050057 | 0.023857 | south | N | 0.023857 | 0
80140 | CSDR11 | 11 | 39 | -0.068798 | south | -0.14125 | 0.023857 | -0.13415 | -0.050057 | 0.023857 | south | N | 0.023857 | 0
80180 | PNSCALT1 | 1 | 148 | -0.072922 | south | -0.14538 | 0.019733 | -0.13827 | -0.054181 | 0.019733 | south | N | 0.019733 | 0
80180 | PNSCALT1 | 2 | 50 | -0.072922 | south | -0.14538 | 0.019733 | -0.13827 | -0.054181 | 0.019733 | south | N | 0.019733 | 0
80181 | PNSCALT2 | 1 | 55 | -0.072922 | south | -0.14538 | 0.019733 | -0.13827 | -0.054181 | 0.019733 | south | N | 0.019733 | 0
80181 | PNSCALT2 | 2 | 50 | -0.072922 | south | -0.14538 | 0.019733 | -0.13827 | -0.054181 | 0.019733 | south | N | 0.019733 | 0
80223 | REYSHR G | 1 | 12 | -0.071404 | south | -0.14386 | 0.021251 | -0.13675 | -0.052663 | 0.021251 | south | N | 0.021251 | 0
80224 | VISTRONG | 1 | 15 | -0.069621 | south | -0.14207 | 0.023034 | -0.13497 | -0.05088 | 0.023034 | south | N | 0.023034 | 0
80225 | VISTRONG | 2 | 23 | -0.069621 | south | -0.14207 | 0.023034 | -0.13497 | -0.05088 | 0.023034 | south | N | 0.023034 | 0
80226 | ALCOA G | 1 | 48 | -0.066842 | south | -0.1393 | 0.025813 | -0.13219 | -0.048101 | 0.025813 | south | N | 0.025813 | 0
80227 | AIRCO G | 1 | 8 | -0.069088 | south | -0.14154 | 0.023567 | -0.13444 | -0.050347 | 0.023567 | south | N | 0.023567 | 0
80261 | NBEC81A | 1 | 180 | -0.072196 | south | -0.14465 | 0.020459 | -0.13754 | -0.053455 | 0.020459 | south | N | 0.020459 | 0
80262 | NBEC91A | 1 | 180 | -0.072173 | south | -0.14463 | 0.020482 | -0.13752 | -0.053432 | 0.020482 | south | N | 0.020482 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.072343 | south | -0.1448 | 0.020312 | -0.13769 | -0.053602 | 0.020312 | south | N | 0.020312 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.072343 | south | -0.1448 | 0.020312 | -0.13769 | -0.053602 | 0.020312 | south | N | 0.020312 | 0
80265 | LARECU40 | 4 | 100 | -0.077015 | south | -0.14947 | 0.01564 | -0.14236 | -0.058274 | 0.01564 | south | N | 0.01564 | 0
80266 | LARECU50 | 5 | 100 | -0.077015 | south | -0.14947 | 0.01564 | -0.14236 | -0.058274 | 0.01564 | south | N | 0.01564 | 0
80291 | PAPALOTE | 1 | 25 | -0.071707 | south | -0.14416 | 0.020948 | -0.13706 | -0.052966 | 0.020948 | south | N | 0.020948 | 0
80291 | PAPALOTE | 2 | 25 | -0.071707 | south | -0.14416 | 0.020948 | -0.13706 | -0.052966 | 0.020948 | south | N | 0.020948 | 0
80291 | PAPALOTE | 3 | 25 | -0.071707 | south | -0.14416 | 0.020948 | -0.13706 | -0.052966 | 0.020948 | south | N | 0.020948 | 0
80291 | PAPALOTE | 4 | 16 | -0.071707 | south | -0.14416 | 0.020948 | -0.13706 | -0.052966 | 0.020948 | south | N | 0.020948 | 0
80294 | PAPALOTE | 5 | 25 | -0.071707 | south | -0.14416 | 0.020948 | -0.13706 | -0.052966 | 0.020948 | south | N | 0.020948 | 0
80294 | PAPALOTE | 6 | 25 | -0.071707 | south | -0.14416 | 0.020948 | -0.13706 | -0.052966 | 0.020948 | south | N | 0.020948 | 0
80294 | PAPALOTE | 7 | 25 | -0.071707 | south | -0.14416 | 0.020948 | -0.13706 | -0.052966 | 0.020948 | south | N | 0.020948 | 0
80294 | PAPALOTE | 8 | 15 | -0.071707 | south | -0.14416 | 0.020948 | -0.13706 | -0.052966 | 0.020948 | south | N | 0.020948 | 0
86104 | CID-138 | EQ | 0 | -0.077015 | south | -0.14947 | 0.01564 | -0.14236 | -0.058274 | 0.01564 | south | N | 0.01564 | 0
86105 | CID-230 | EQ | 500 | -0.077015 | south | -0.14947 | 0.01564 | -0.14236 | -0.058274 | 0.01564 | south | N | 0.01564 | 0
86106 | CUF-230 | EQ | 500 | -0.077015 | south | -0.14947 | 0.01564 | -0.14236 | -0.058274 | 0.01564 | south | N | 0.01564 | 0
86107 | CUF-138 | EQ | 0 | -0.077015 | south | -0.14947 | 0.01564 | -0.14236 | -0.058274 | 0.01564 | south | N | 0.01564 | 0
88198 | BEEVILLE | F | 0 | -0.076447 | south | -0.1489 | 0.016208 | -0.1418 | -0.057706 | 0.016208 | south | N | 0.016208 | 0
88253 | HAMILTON | F | 0 | -0.040863 | south | -0.11332 | 0.051792 | -0.10621 | -0.022122 | 0.022122 | houston | Y | 0.051792 | 0
88299 | ZAPATA | F | 0 | -0.075034 | south | -0.14749 | 0.017621 | -0.14038 | -0.056293 | 0.017621 | south | N | 0.017621 | 0
88508 | FALFURRI | F | 0 | -0.074193 | south | -0.14665 | 0.018462 | -0.13954 | -0.055452 | 0.018462 | south | N | 0.018462 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3412 TEMP_PEC - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.13567 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.22667 | 0 | 0 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.13567 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 106.7747 | 787 | 0.22667 | 178.3871 | 787 | 178.3871
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.098838 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.2037 | 255 | 0.18983 | 48.4072 | 1042 | 226.7943
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.098838 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.7269 | 149 | 0.18983 | 28.285 | 1191 | 255.0794 | Weighted Shift Factors
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.098838 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 15.1222 | 153 | 0.18983 | 29.0443 | 1344 | 284.1237 | North | 0.072453
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.08397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.1711 | 216.4 | 0.17496 | 37.8623 |  |  | South | -0.090994
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.08397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.1459 | 216.1 | 0.17496 | 37.8098 |  |  |  | 0.16345
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.083592 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.7246 | 224 | 0.17459 | 39.1073
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.083592 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.8918 | 226 | 0.17459 | 39.4565 |  |  | Line Rating | 750
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.083592 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.7215 | 212 | 0.17459 | 37.0123 |  |  | Conc Gen | 1344
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.083592 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.6379 | 211 | 0.17459 | 36.8377 |  |  | Weighted Imp. | 284.1237
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.079375 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.3531 | 395 | 0.17037 | 67.2959 |  |  | PTDF | 0.2114
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.079375 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 34.5281 | 435 | 0.17037 | 74.1106
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.079171 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 34.4394 | 435 | 0.17017 | 74.0219 |  |  | Concentration | 1.2934
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.078647 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.2127 | 168 | 0.16964 | 28.4997
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.078647 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.0782 | 90 | 0.16964 | 15.2677
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.078104 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1691 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.077906 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.929 | 217.3 | 0.1689 | 36.702
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.077906 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.9707 | 205 | 0.1689 | 34.6246
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.077906 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.2216 | 272.4 | 0.1689 | 46.0084
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.077524 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.16852 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.077524 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.16852 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.077524 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.16852 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.077514 | north | 3 | N | N | Nnorth | Nnorth | 1 | 89.6837 | 0 | 0.16851 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.077514 | north | 3 | N | N | Nnorth | Nnorth | 1 | 89.7612 | 0 | 0.16851 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.077179 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.1071 | 118 | 0.16817 | 19.8444
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.077179 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.8756 | 115 | 0.16817 | 19.3399
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.077179 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 42.9115 | 556 | 0.16817 | 93.5043
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.077065 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3945 | 70 | 0.16806 | 11.7641
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.077065 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3175 | 69 | 0.16806 | 11.5961
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.077065 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3175 | 69 | 0.16806 | 11.5961
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.077065 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.2404 | 68 | 0.16806 | 11.428
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.076565 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.5939 | 60 | 0.16756 | 10.0536
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.076565 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.8236 | 63 | 0.16756 | 10.5562
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.076347 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.16734 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.076301 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1673 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.076168 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.4252 | 150 | 0.16716 | 25.0743
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.076168 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0934 | 80 | 0.16716 | 13.373
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.075996 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 8.5495 | 112.5 | 0.16699 | 18.7864
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.07595 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.16694 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.07595 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.16694 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.075909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.8618 | 288 | 0.1669 | 48.0681
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.075909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.1586 | 147 | 0.1669 | 24.5348
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.075909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.1586 | 147 | 0.1669 | 24.5348
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.075868 | north | 5 | N | N | Nnorth | Nnorth | 1 | 3.0347 | 0 | 0.16686 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.075868 | north | 5 | N | N | Nnorth | Nnorth | 1 | 3.0347 | 0 | 0.16686 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.0758 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.886 | 170 | 0.16679 | 28.355
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.0758 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 39.416 | 520 | 0.16679 | 86.733
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.075734 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 28.0216 | 370 | 0.16673 | 61.6895
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.6028 | 0 | 0.16673 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.6785 | 0 | 0.16673 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | 1 | 23.4018 | 0 | 0.16673 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.83 | 0 | 0.16673 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.9057 | 0 | 0.16673 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | 1 | 23.4775 | 0 | 0.16673 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.075711 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.1357 | 0 | 0.16671 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.075711 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.1357 | 0 | 0.16671 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.8313 | 196 | 0.16666 | 32.6662
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.3994 | 111 | 0.16666 | 18.4997
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.1072 | 160 | 0.16666 | 26.6663
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8045 | 156 | 0.16666 | 25.9996
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.8313 | 196 | 0.16666 | 32.6662
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8045 | 156 | 0.16666 | 25.9996
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8802 | 157 | 0.16666 | 26.1663
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.9827 | 198 | 0.16666 | 32.9995
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.0756 | north | 8 | N | N | Nnorth | Nnorth | 1 | 5.67 | 0 | 0.16659 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.0756 | north | 8 | N | N | Nnorth | Nnorth | 1 | 6.0178 | 0 | 0.16659 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.0756 | north | 8 | N | N | Nnorth | Nnorth | 1 | 6.683 | 0 | 0.16659 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.075598 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 29.332 | 388 | 0.16659 | 64.6378
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.075598 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 38.933 | 515 | 0.16659 | 85.795
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.075576 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 42.1714 | 558 | 0.16657 | 92.9462
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.075576 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 43.7585 | 579 | 0.16657 | 96.4442
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.075576 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 61.0654 | 808 | 0.16657 | 134.5888
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.075548 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.9683 | 79 | 0.16654 | 13.1568
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.075548 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.0081 | 106 | 0.16654 | 17.6535
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.075548 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.03 | 146 | 0.16654 | 24.3152
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.075548 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.7416 | 76 | 0.16654 | 12.6572
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.07553 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0212 | 40 | 0.16652 | 6.661
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.075525 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.4071 | 204 | 0.16652 | 33.9699
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.075525 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.1805 | 201 | 0.16652 | 33.4704
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.075525 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.277 | 242 | 0.16652 | 40.2977
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.075504 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.3591 | 18 | 0.1665 | 2.997
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.075504 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.3591 | 18 | 0.1665 | 2.997
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.075504 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.8692 | 38 | 0.1665 | 6.3269
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.075432 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8858 | 25 | 0.16643 | 4.1607
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.075432 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0927 | 41 | 0.16643 | 6.8235
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.075431 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.5086 | 20 | 0.16643 | 3.3285
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.0581 | 161 | 0.16589 | 26.7082
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.2828 | 164 | 0.16589 | 27.2058
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.2828 | 164 | 0.16589 | 27.2058
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.0065 | 414 | 0.16589 | 68.6781
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.133 | 162 | 0.16589 | 26.8741
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.0581 | 161 | 0.16589 | 26.7082
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.2079 | 163 | 0.16589 | 27.0399
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.6321 | 409 | 0.16589 | 67.8487
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.074036 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.88843 | 0 | 0.16503 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.074036 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.88843 | 0 | 0.16503 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.073999 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.4019 | 73 | 0.16499 | 12.0445
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.073999 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.8059 | 119 | 0.16499 | 19.6342
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.073999 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.1698 | 205 | 0.16499 | 33.8236
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.073999 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.5479 | 102 | 0.16499 | 16.8293
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.073999 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.1039 | 96 | 0.16499 | 15.8394
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.073935 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 8.8722 | 120 | 0.16493 | 19.7915
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.07346 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.8864 | 366 | 0.16445 | 60.1903
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.07344 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.4688 | 20 | 0.16443 | 3.2887
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.07344 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.4688 | 20 | 0.16443 | 3.2887
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.07344 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.4688 | 20 | 0.16443 | 3.2887
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.07344 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2485 | 17 | 0.16443 | 2.7954
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.072799 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 17.6174 | 242 | 0.16379 | 39.638
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.071998 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 56.5184 | 785 | 0.16299 | 127.9489
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.071998 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 57.2384 | 795 | 0.16299 | 129.5788
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.071998 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 56.1584 | 780 | 0.16299 | 127.134
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.071647 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.6038 | 0 | 0.16264 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.071647 | north | 1 | N | N | Nnorth | Nnorth | 1 | 9.3141 | 0 | 0.16264 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.071647 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.3888 | 0 | 0.16264 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.071647 | north | 1 | N | N | Nnorth | Nnorth | 1 | 28.5872 | 0 | 0.16264 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.071594 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.0371 | 224 | 0.16259 | 36.4198
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.071382 | west | 4 | Y | N | Ywest | Nwest | 1 | 46.3769 | 649.7 | 0.16238 | 105.4958
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.071161 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.16216 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.071139 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.557 | 50 | 0.16213 | 8.1067
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.070772 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6774 | 165 | 0.16177 | 26.6914
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.070644 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.8572 | 182 | 0.16164 | 29.4182
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.070644 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 34.1917 | 484 | 0.16164 | 78.2329
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.069923 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.5018 | 236 | 0.16092 | 37.9765
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.069918 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.9672 | 400 | 0.16091 | 64.3649
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.069854 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.1912 | 60 | 0.16085 | 9.6509
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.06846 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1076 | 60 | 0.15945 | 9.5673
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.067899 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.2867 | 151.5 | 0.15889 | 24.0723
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.067899 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.341 | 152.3 | 0.15889 | 24.1994
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.067899 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.0521 | 177.5 | 0.15889 | 28.2036
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.067816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.2199 | 150.7 | 0.15881 | 23.9327
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.067816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.2402 | 151 | 0.15881 | 23.9803
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.067816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.0306 | 177.4 | 0.15881 | 28.1729
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.067528 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1134 | 209 | 0.15852 | 33.1312
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.067528 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5423 | 126.5 | 0.15852 | 20.0531
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.067528 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.8145 | 249 | 0.15852 | 39.472
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.067528 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.303 | 197 | 0.15852 | 31.2289
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.067506 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.1259 | 150 | 0.1585 | 23.775
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5257 | 37.5 | 0.15835 | 5.938
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2403 | 107.5 | 0.15835 | 17.0222
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.0925 | 135 | 0.15835 | 21.3767
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0149 | 119 | 0.15835 | 18.8432
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.072 | 105 | 0.15835 | 16.6264
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4218 | 80.5 | 0.15835 | 12.7469
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.067026 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3782 | 125 | 0.15802 | 19.7525
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.067026 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3782 | 125 | 0.15802 | 19.7525
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.066926 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 41.1595 | 615 | 0.15792 | 97.121
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.066926 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 39.2856 | 587 | 0.15792 | 92.6992
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.066784 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.6099 | 84 | 0.15778 | 13.2534
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.066753 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.013 | 150 | 0.15775 | 23.6621
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.066753 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7421 | 101 | 0.15775 | 15.9325
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.066619 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5953 | 99 | 0.15761 | 15.6037
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.066619 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0638 | 61 | 0.15761 | 9.6144
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.066619 | west | 7 | N | N | Nwest | Nwest | 1 | 1.6655 | 0 | 0.15761 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.066619 | west | 7 | N | N | Nwest | Nwest | 1 | 3.0445 | 0 | 0.15761 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.066619 | west | 7 | N | N | Nwest | Nwest | 1 | 3.0445 | 0 | 0.15761 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.066601 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3907 | 141 | 0.1576 | 22.2209
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.066601 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9921 | 120 | 0.1576 | 18.9114
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.066545 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1923 | 63 | 0.15754 | 9.925
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3889 | 66 | 0.15749 | 10.3945
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.5884 | 69 | 0.15749 | 10.867
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.5884 | 69 | 0.15749 | 10.867
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.4554 | 67 | 0.15749 | 10.552
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.4554 | 67 | 0.15749 | 10.552
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3224 | 65 | 0.15749 | 10.237
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.06637 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9555 | 150 | 0.15736 | 23.6046
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.06637 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.6014 | 220 | 0.15736 | 34.6201
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.06637 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.274 | 200 | 0.15736 | 31.4728
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.06637 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0905 | 121.9 | 0.15736 | 19.1827
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.066181 | west | 8 | N | N | Nwest | Nwest | 1 | 4.6327 | 0 | 0.15718 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.066181 | west | 8 | N | N | Nwest | Nwest | 1 | 4.8577 | 0 | 0.15718 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.066181 | west | 8 | N | N | Nwest | Nwest | 1 | 4.6591 | 0 | 0.15718 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.066164 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.9095 | 180 | 0.15716 | 28.2885
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.066164 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.9095 | 180 | 0.15716 | 28.2885
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.066104 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8734 | 225 | 0.1571 | 35.3471
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.065963 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9156 | 120 | 0.15696 | 18.8349
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.065936 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9123 | 120 | 0.15693 | 18.8316
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.065794 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8953 | 120 | 0.15679 | 18.8146
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.065794 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.33 | 233 | 0.15679 | 36.5317
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.065794 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.1981 | 170.2 | 0.15679 | 26.6854
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.065535 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0376 | 214.2 | 0.15653 | 33.5286
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.065511 | west | 8 | N | N | Nwest | Nwest | 1 | 1.6902 | 0 | 0.15651 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.065386 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5713 | 100.5 | 0.15638 | 15.7162
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.065378 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7919 | 58 | 0.15637 | 9.0696
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.5751 | 70 | 0.15635 | 10.9447
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.5751 | 70 | 0.15635 | 10.9447
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.0652 | 92.8 | 0.15635 | 14.5095
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.2286 | 80 | 0.15635 | 12.5082
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.2286 | 80 | 0.15635 | 12.5082
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.5162 | 115 | 0.15635 | 17.9805
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.6052 | 208.2 | 0.15634 | 32.5502
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.2858 | 142.1 | 0.15634 | 22.2161
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.6519 | 132.4 | 0.15634 | 20.6996
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.8872 | 136 | 0.15634 | 21.2624
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.606 | 147 | 0.15634 | 22.9822
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.7229 | 210 | 0.15634 | 32.8317
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.065096 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.7644 | 150 | 0.15609 | 23.4135
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.064794 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2893 | 112.5 | 0.15579 | 17.5262
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.064794 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6867 | 149.5 | 0.15579 | 23.2903
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.064794 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.0517 | 186 | 0.15579 | 28.9766
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.064794 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.8983 | 214.5 | 0.15579 | 33.4166
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.064509 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.42576 | 6.6 | 0.1555 | 1.0263
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.064509 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2127 | 34.3 | 0.1555 | 5.3338
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.064449 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6029 | 149 | 0.15544 | 23.161
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.064254 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2489 | 35 | 0.15525 | 5.4337
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.064254 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9276 | 30 | 0.15525 | 4.6574
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.237 | 66 | 0.15519 | 10.2426
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1728 | 65 | 0.15519 | 10.0874
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3012 | 67 | 0.15519 | 10.3978
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3012 | 67 | 0.15519 | 10.3978
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3012 | 67 | 0.15519 | 10.3978
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.064197 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.15519 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.064197 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.15519 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.063738 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.8036 | 169.5 | 0.15473 | 26.2271
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.059986 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.28793 | 0 | 0.15098 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.05824 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6592 | 80 | 0.14923 | 11.9387
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.05824 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6592 | 80 | 0.14923 | 11.9387
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.057773 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.333 | 75 | 0.14877 | 11.1575
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.057773 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6218 | 80 | 0.14877 | 11.9014
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.057773 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3109 | 40 | 0.14877 | 5.9507
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.057672 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6138 | 80 | 0.14867 | 11.8933
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.057658 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6126 | 80 | 0.14865 | 11.8922
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.057599 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6398 | 150 | 0.14859 | 22.289
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.057599 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6398 | 150 | 0.14859 | 22.289
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.055263 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.421 | 80 | 0.14626 | 11.7006
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.054851 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1961 | 76.5 | 0.14585 | 11.1572
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.054698 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14569 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.054698 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14569 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.05461 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 45.1625 | 827 | 0.1456 | 120.4147
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.05461 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 44.7256 | 819 | 0.1456 | 119.2499
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.054475 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5759 | 84 | 0.14547 | 12.2194
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.046247 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 39.5412 | 855 | 0.13724 | 117.3413
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.046247 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 39.5412 | 855 | 0.13724 | 117.3413
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.046247 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0434 | 152.3 | 0.13724 | 20.9018
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.046247 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0758 | 153 | 0.13724 | 20.9979
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.041916 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.13291 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.030037 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5056 | 150 | 0.12103 | 18.1547
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.026937 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.4718 | 463 | 0.11793 | 54.6022
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.021529 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.3198 | 0 | 0.11252 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.021529 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.3585 | 0 | 0.11252 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.021529 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.3585 | 0 | 0.11252 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.021529 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.181 | 0 | 0.11252 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.021507 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1125 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.021507 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1125 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.021507 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.36562 | 17 | 0.1125 | 1.9125
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.021507 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1125 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.021507 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1125 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.021478 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.6873 | 0 | 0.11247 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.019125 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.918 | 48 | 0.11012 | 5.2857
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.019125 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.87975 | 46 | 0.11012 | 5.0655
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.019125 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0081 | 105 | 0.11012 | 11.5625
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.090994 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.090994 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.050537 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.040457 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -9.2678 | 100 | -0.0016838 | -0.16838
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.072453 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.072453 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.072453 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.072453 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.072453 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.072453 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.072453 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.072453 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.007573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3101 | 0 | -0.080026 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.007573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1814 | 0 | -0.080026 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.007573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1662 | 0 | -0.080026 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.007573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1662 | 0 | -0.080026 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.007573 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2268 | 0 | -0.080026 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59763 | 56 | -0.083125 | -4.655
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.62965 | 59 | -0.083125 | -4.9044
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59763 | 56 | -0.083125 | -4.655
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59763 | 56 | -0.083125 | -4.655
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.62965 | 59 | -0.083125 | -4.9044
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59763 | 56 | -0.083125 | -4.655
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.010993 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.3752 | 398 | -0.083446 | -33.2116
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.011175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8193 | 0 | -0.083628 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.011175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8036 | 0 | -0.083628 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.011175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7757 | 0 | -0.083628 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.011175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0083 | 0 | -0.083628 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.011701 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.0126 | 172 | -0.084154 | -14.4745
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.011701 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.0126 | 172 | -0.084154 | -14.4745
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.011701 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.0126 | 172 | -0.084154 | -14.4745
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.01179 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.851 | 0 | -0.084243 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.011925 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -8.8603 | 743 | -0.084378 | -62.693
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.011946 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.14335 | 12 | -0.084399 | -1.0128
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.7774 | 0 | -0.084413 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.78936 | 0 | -0.084413 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8372 | 0 | -0.084413 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.75348 | 0 | -0.084413 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74152 | 0 | -0.084413 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2438 | 0 | -0.084413 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70564 | 0 | -0.084413 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.011965 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.059825 | 0 | -0.084418 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.011965 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25127 | 0 | -0.084418 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.012257 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14708 | 12 | -0.08471 | -1.0165
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42463 | 0 | -0.084942 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43337 | 0 | -0.084942 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40839 | 0 | -0.084942 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.57325 | 0 | -0.084942 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22106 | 0 | -0.084942 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25478 | 0 | -0.084942 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.24853 | 0 | -0.084942 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43711 | 0 | -0.084942 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2248 | 0 | -0.084942 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0666 | 0 | -0.084942 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8484 | 0 | -0.084942 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.012669 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -9.3117 | 735 | -0.085122 | -62.5649
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.3458 | 104 | -0.085393 | -8.8809
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.3458 | 104 | -0.085393 | -8.8809
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.69876 | 54 | -0.085393 | -4.6112
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.68582 | 53 | -0.085393 | -4.5258
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.69876 | 54 | -0.085393 | -4.6112
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.73758 | 57 | -0.085393 | -4.8674
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.69876 | 54 | -0.085393 | -4.6112
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.69876 | 54 | -0.085393 | -4.6112
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.75052 | 58 | -0.085393 | -4.9528
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.75052 | 58 | -0.085393 | -4.9528
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.013646 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3608 | 0 | -0.086099 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.013646 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8422 | 0 | -0.086099 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.013759 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.57788 | 42 | -0.086212 | -3.6209
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.013759 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.57788 | 42 | -0.086212 | -3.6209
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.013759 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.52284 | 38 | -0.086212 | -3.2761
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.013759 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.52284 | 38 | -0.086212 | -3.2761
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.013794 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.876 | 0 | -0.086247 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.014233 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0105 | 0 | -0.086686 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.014233 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0248 | 0 | -0.086686 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.014233 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55509 | 0 | -0.086686 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.014233 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42699 | 0 | -0.086686 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.01451 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6118 | 0 | -0.086963 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.01451 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3013 | 0 | -0.086963 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.01451 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2781 | 0 | -0.086963 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.014517 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.3099 | 228 | -0.08697 | -19.8292
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.014524 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92954 | 0 | -0.086977 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.014524 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.91792 | 0 | -0.086977 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.014524 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1997 | 0 | -0.086977 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.014524 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.069 | 0 | -0.086977 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.014528 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23535 | 0 | -0.086981 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.014533 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.0955 | 213 | -0.086986 | -18.5281
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.014573 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1714 | 0 | -0.087026 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.014573 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9487 | 0 | -0.087026 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.014585 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.4065 | 165 | -0.087038 | -14.3613
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.0146 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.4674 | 169 | -0.087053 | -14.712
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.014611 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.17533 | 12 | -0.087064 | -1.0448
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.014611 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.087064 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.014808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51828 | 0 | -0.087261 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4465 | 0 | -0.087444 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3551 | 0 | -0.087444 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3611 | 0 | -0.087444 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3536 | 0 | -0.087444 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0326 | 0 | -0.087444 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.015216 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1868 | 0 | -0.087669 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.015216 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2173 | 0 | -0.087669 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.70743 | 46 | -0.087832 | -4.0403
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.70743 | 46 | -0.087832 | -4.0403
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.70743 | 46 | -0.087832 | -4.0403
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.84584 | 55 | -0.087832 | -4.8308
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.84584 | 55 | -0.087832 | -4.8308
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.83047 | 54 | -0.087832 | -4.7429
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.016034 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0422 | 0 | -0.088487 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.016034 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.96204 | 0 | -0.088487 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.016034 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0422 | 0 | -0.088487 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.016034 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0422 | 0 | -0.088487 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4991 | 0 | -0.088927 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4431 | 0 | -0.088927 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4332 | 0 | -0.088927 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89783 | 0 | -0.088927 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20098 | 0 | -0.088927 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.017597 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.09005 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.018559 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.92795 | 50 | -0.091012 | -4.5506
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.019794 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4014 | 0 | -0.092247 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.019794 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3203 | 0 | -0.092247 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.019794 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0491 | 0 | -0.092247 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0324 | 0 | -0.092247 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0384 | 0 | -0.092247 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0146 | 0 | -0.092247 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9002 | 0 | -0.092247 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8297 | 0 | -0.092247 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.019794 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.79176 | 0 | -0.092247 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.019809 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63389 | 0 | -0.092262 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.019809 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59427 | 0 | -0.092262 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.01981 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9869 | 0 | -0.092263 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.01981 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8403 | 0 | -0.092263 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.01981 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0345 | 0 | -0.092263 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.01981 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0206 | 0 | -0.092263 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.02282 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.674 | 161 | -0.095273 | -15.339
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.02282 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.7881 | 166 | -0.095273 | -15.8154
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.02282 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.6594 | 248 | -0.095273 | -23.6278
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.02282 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -12.4597 | 546 | -0.095273 | -52.0192
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.02282 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -14.6733 | 0 | -0.095273 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.02282 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.29666 | 13 | -0.095273 | -1.2386
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.023081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.76167 | 0 | -0.095534 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.023674 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8589 | 0 | -0.096127 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.023674 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8589 | 0 | -0.096127 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.023674 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.8001 | 0 | -0.096127 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.023722 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -15.443 | 651 | -0.096175 | -62.6101
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.023722 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -13.3792 | 564 | -0.096175 | -54.2428
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.023722 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -14.2332 | 600 | -0.096175 | -57.7052
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.023936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1034 | 0 | -0.096389 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.029662 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2925 | 0 | -0.10212 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.029662 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2925 | 0 | -0.10212 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.029662 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.5298 | 0 | -0.10212 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.029662 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.248 | 0 | -0.10212 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.031242 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2182 | 0 | -0.1037 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.031242 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31242 | 0 | -0.1037 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0609 | 0 | -0.10569 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3733 | 0 | -0.10569 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4958 | 0 | -0.10569 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3572 | 0 | -0.10569 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8586 | 0 | -0.10569 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9251 | 0 | -0.10569 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.662 | 0 | -0.10569 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59832 | 0 | -0.10569 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1246 | 0 | -0.10569 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3268 | 0 | -0.10569 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0941 | 0 | -0.10569 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3933 | 0 | -0.10569 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.154 | 0 | -0.10569 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3572 | 0 | -0.10569 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2243 | 0 | -0.10569 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4237 | 0 | -0.10569 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5262 | 0 | -0.10569 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6592 | 0 | -0.10569 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6592 | 0 | -0.10569 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.684 | 0 | -0.10569 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.040863 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3485 | 0 | -0.11332 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.040863 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0216 | 0 | -0.11332 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.040863 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11332 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.041523 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.7405 | 66 | -0.11398 | -7.5224
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.3545 | 76 | -0.11659 | -8.8609
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.3545 | 76 | -0.11659 | -8.8609
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.6345 | 105 | -0.11659 | -12.2421
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.2662 | 74 | -0.11659 | -8.6278
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.2662 | 74 | -0.11659 | -8.6278
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.5021 | 102 | -0.11659 | -11.8923
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.044425 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -59.2185 | 0 | -0.11688 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.044425 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -58.9964 | 0 | -0.11688 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.052284 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.3137 | 0 | -0.12474 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.054941 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12739 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2329 | 0 | -0.13869 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3654 | 0 | -0.13869 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2329 | 0 | -0.13869 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2991 | 0 | -0.13869 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.1931 | 0 | -0.13869 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.656 | 0 | -0.13869 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.047 | 0 | -0.13869 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8547 | 0 | -0.13869 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.888 | 0 | -0.13869 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9017 | 0 | -0.13869 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.066842 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2084 | 0 | -0.1393 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9263 | 0 | -0.14125 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48159 | 0 | -0.14125 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.6831 | 0 | -0.14125 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.032 | 0 | -0.14125 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48159 | 0 | -0.14125 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.032 | 0 | -0.14125 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.6831 | 0 | -0.14125 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.6831 | 0 | -0.14125 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.069088 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5527 | 0 | -0.14154 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.069621 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0443 | 0 | -0.14207 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.069621 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6013 | 0 | -0.14207 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.070237 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5452 | 22 | -0.14269 | -3.1392
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.070237 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.77261 | 11 | -0.14269 | -1.5696
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.070237 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.77261 | 11 | -0.14269 | -1.5696
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.070906 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3822 | 47.7 | -0.14336 | -6.8382
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.070906 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6448 | 37.3 | -0.14336 | -5.3473
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.070906 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2617 | 46 | -0.14336 | -6.5945
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.070906 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4035 | 48 | -0.14336 | -6.8812
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.071072 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.1883 | 0 | -0.14353 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.2818 | 0 | -0.14386 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.9248 | 0 | -0.14386 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.1404 | 0 | -0.14386 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.3536 | 0 | -0.14386 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.4964 | 0 | -0.14386 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.0683 | 0 | -0.14386 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.071404 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.85685 | 0 | -0.14386 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7927 | 25 | -0.14416 | -3.604
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7927 | 25 | -0.14416 | -3.604
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7927 | 25 | -0.14416 | -3.604
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1473 | 16 | -0.14416 | -2.3066
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7927 | 25 | -0.14416 | -3.604
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7927 | 25 | -0.14416 | -3.604
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7927 | 25 | -0.14416 | -3.604
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0756 | 15 | -0.14416 | -2.1624
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.0719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.3536 | 144 | -0.14435 | -20.7869
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.0719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.5172 | 188 | -0.14435 | -27.1384
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.072173 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.2501 | 336 | -0.14463 | -48.5944
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.072173 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.9911 | 180 | -0.14463 | -26.0327
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.072182 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.7046 | 0 | -0.14464 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.072182 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.7262 | 0 | -0.14464 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.072182 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.0438 | 0 | -0.14464 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.072196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.9953 | 180 | -0.14465 | -26.0369
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.072343 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -24.1626 | 334 | -0.1448 | -48.3619
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.072343 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -24.5966 | 340 | -0.1448 | -49.2307
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.072343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.0217 | 180 | -0.1448 | -26.0633
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.072343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.0217 | 180 | -0.1448 | -26.0633
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.072371 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8093 | 0 | -0.14482 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.072371 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8093 | 0 | -0.14482 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.072444 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7529 | 0 | -0.1449 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.07245 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7531 | 0 | -0.1449 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.072804 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1113 | 0 | -0.14526 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.8547 | 94 | -0.14538 | -13.6653
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9898 | 41 | -0.14538 | -5.9604
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.771 | 38 | -0.14538 | -5.5243
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.3855 | 19 | -0.14538 | -2.7621
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.8547 | 94 | -0.14538 | -13.6653
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6252 | 36 | -0.14538 | -5.2335
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1356 | 43 | -0.14538 | -6.2511
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6043 | 22 | -0.14538 | -3.1983
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.7925 | 148 | -0.14538 | -21.5155
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6461 | 50 | -0.14538 | -7.2688
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.0107 | 55 | -0.14538 | -7.9956
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6461 | 50 | -0.14538 | -7.2688
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.072972 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14543 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.072972 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.7729 | 38 | -0.14543 | -5.5262
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.072972 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4084 | 19.3 | -0.14543 | -2.8067
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.072972 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0946 | 15 | -0.14543 | -2.1814
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.072972 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.4297 | 47 | -0.14543 | -6.835
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.073114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.5284 | 144 | -0.14557 | -20.9617
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.073114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.5284 | 144 | -0.14557 | -20.9617
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.073114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5025 | 171 | -0.14557 | -24.892
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.073117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.1352 | 207 | -0.14557 | -30.133
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.073117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.8445 | 216.7 | -0.14557 | -31.5451
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.073117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.6943 | 242 | -0.14557 | -35.228
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.073262 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7329 | 146.5 | -0.14572 | -21.3473
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.073262 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.8354 | 147.9 | -0.14572 | -21.5513
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.073262 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6743 | 173 | -0.14572 | -25.2087
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.074167 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.89 | 0 | -0.14662 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.074167 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.81584 | 0 | -0.14662 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.074167 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.89 | 0 | -0.14662 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.074193 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14665 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.075034 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14749 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.075413 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -47.4348 | 629 | -0.14787 | -93.0079
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.076447 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1489 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.077008 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14946 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.077015 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7015 | 100 | -0.14947 | -14.9468
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.077015 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7015 | 100 | -0.14947 | -14.9468
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.077015 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14947 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.077015 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14947 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.077015 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14947 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.077015 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14947 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.077588 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.8621 | 24 | -0.15004 | -3.601
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.077588 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.8621 | 24 | -0.15004 | -3.601
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.077588 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.7845 | 23 | -0.15004 | -3.4509
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.082396 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -32.6288 | 396 | -0.15485 | -61.3203
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.087247 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.047 | 0 | -0.1597 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.087285 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -47.6576 | 546 | -0.15974 | -87.2171
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.087285 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -65.4638 | 750 | -0.15974 | -119.8037
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.087462 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.0728 | 58 | -0.15992 | -9.2751
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.087462 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.7841 | 89 | -0.15992 | -14.2325
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.087462 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.8483 | 44 | -0.15992 | -7.0363
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.087462 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.8483 | 44 | -0.15992 | -7.0363
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.087462 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.7609 | 43 | -0.15992 | -6.8764
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.087462 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9358 | 45 | -0.15992 | -7.1962
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.087765 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6036 | 155 | -0.16022 | -24.8338
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.087765 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.92 | 170 | -0.16022 | -27.2371
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.087765 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6036 | 155 | -0.16022 | -24.8338
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.087955 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.7977 | 407 | -0.16041 | -65.2862
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.087991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -18.3901 | 209 | -0.16044 | -33.5328
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.087991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -19.0061 | 216 | -0.16044 | -34.656
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.087991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0476 | 46 | -0.16044 | -7.3804
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.087991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.1356 | 47 | -0.16044 | -7.5409
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.087991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0476 | 46 | -0.16044 | -7.3804
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.087991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0476 | 46 | -0.16044 | -7.3804
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.088093 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -36.2943 | 412 | -0.16055 | -66.1451
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.088093 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.2372 | 400 | -0.16055 | -64.2185
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.088154 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -37.3773 | 424 | -0.16061 | -68.0975
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.088154 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -37.4654 | 425 | -0.16061 | -68.2581
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.088393 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16085 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.088393 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16085 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.088393 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16085 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.271 | 147 | -0.16273 | -23.9216
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.4585 | 138 | -0.16273 | -22.4571
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6391 | 140 | -0.16273 | -22.7825
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.271 | 147 | -0.16273 | -23.9216
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.4308 | 182 | -0.16273 | -29.6173
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.8752 | 198 | -0.16273 | -32.221
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.5653 | 114 | -0.16513 | -18.825
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -20.5745 | 222 | -0.16513 | -36.6591
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -17.0528 | 184 | -0.16513 | -30.3842
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -20.7599 | 224 | -0.16513 | -36.9894
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.658 | 115 | -0.16513 | -18.9901
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.092826 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.3713 | 0 | -0.16528 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.09308 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22339 | 0 | -0.16553 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.09308 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22339 | 0 | -0.16553 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.093607 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2922 | 142 | -0.16606 | -23.5806
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.093607 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.573 | 145 | -0.16606 | -24.0787
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.093607 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.1347 | 151 | -0.16606 | -25.0751
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.093607 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.146 | 290 | -0.16606 | -48.1575
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.094298 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22632 | 0 | -0.16675 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.094298 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22632 | 0 | -0.16675 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.094298 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.26403 | 0 | -0.16675 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.097094 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.7393 | 223.9 | -0.16955 | -37.9616
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.097094 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.8462 | 225 | -0.16955 | -38.1481
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.097094 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.8073 | 224.6 | -0.16955 | -38.0803
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.097094 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.0112 | 226.7 | -0.16955 | -38.4364
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.098707 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -42.7401 | 433 | -0.17116 | -74.1124
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.098804 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -57.7015 | 584 | -0.17126 | -100.0142
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.098804 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -58.7884 | 595 | -0.17126 | -101.8981
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.10053 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.60318 | 0 | -0.17298 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.10109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0544 | 50 | -0.17354 | -8.6771
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.10109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0544 | 50 | -0.17354 | -8.6771
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.10109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0544 | 50 | -0.17354 | -8.6771
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.10109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0544 | 50 | -0.17354 | -8.6771
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.10569 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4479 | 0 | -0.17814 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.10582 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -44.6544 | 422 | -0.17827 | -75.2296
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.1067 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.9877 | 0 | -0.17916 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.1067 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.0944 | 0 | -0.17916 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.10805 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9449 | 0 | -0.1805 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.10805 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9449 | 0 | -0.1805 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.10805 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6207 | 0 | -0.1805 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.10902 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9624 | 0 | -0.18148 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.10902 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9624 | 0 | -0.18148 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.11063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.4795 | 158 | -0.18308 | -28.9272
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.11063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.7008 | 160 | -0.18308 | -29.2933
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.11063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.3603 | 175 | -0.18308 | -32.0396
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.11193 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.069 | 152.5 | -0.18438 | -28.1181
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.11193 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.7332 | 149.5 | -0.18438 | -27.565
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.11193 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.0345 | 232.6 | -0.18438 | -42.8871
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.1122 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -14.8099 | 132 | -0.18465 | -24.3737
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.1122 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.0343 | 134 | -0.18465 | -24.743
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.1122 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -36.2393 | 323 | -0.18465 | -59.6417
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.11629 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.0703 | 0 | -0.18875 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.11629 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.954 | 0 | -0.18875 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.11629 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.0703 | 0 | -0.18875 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.7265 | 49 | -0.18932 | -9.2767
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.3759 | 46 | -0.18932 | -8.7087
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.3759 | 46 | -0.18932 | -8.7087
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.4927 | 47 | -0.18932 | -8.8981
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.11687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.9975 | 154 | -0.18932 | -29.1553
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.11687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.2963 | 148 | -0.18932 | -28.0194
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.6096 | 48 | -0.18932 | -9.0874
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.6096 | 48 | -0.18932 | -9.0874
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.11851 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.94812 | 0 | -0.19097 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.11851 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.94812 | 0 | -0.19097 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.11857 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -36.7576 | 310 | -0.19103 | -59.2181
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.11857 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -48.9706 | 413 | -0.19103 | -78.8938
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.11969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0271 | 42 | -0.19215 | -8.0702
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.11969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.2665 | 44 | -0.19215 | -8.4545
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.11969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.2665 | 44 | -0.19215 | -8.4545
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.11969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.6256 | 47 | -0.19215 | -9.0309
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.14089 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -80.1681 | 569 | -0.21335 | -121.394
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.14089 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -81.8588 | 581 | -0.21335 | -123.9542

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3412 TEMP_PEC - 3420 TEMP_PEC C:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.14089 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -80.1681 | 0 | -0.21335 | 0 | 0 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.14089 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -81.8588 | 0 | -0.21335 | 0 | 0 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.11969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0271 | 42 | -0.19215 | -8.0702 | 42 | 8.0702
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.11969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.2665 | 44 | -0.19215 | -8.4545 | 86 | 16.5247 | Weighted Shift Factors
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.11969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.2665 | 44 | -0.19215 | -8.4545 | 130 | 24.9791 | North | 0.072453
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.11969 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.6256 | 47 | -0.19215 | -9.0309 | 177 | 34.0101 | South | -0.090994
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.11857 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -36.7576 | 310 | -0.19103 | -59.2181 | 487 | 93.2282 |  | 0.16345
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.11857 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -48.9706 | 413 | -0.19103 | -78.8938 | 900 | 172.122
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.11851 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.94812 | 0 | -0.19097 | 0 | 900 | 172.122 | Line Rating | 750
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.11851 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.94812 | 0 | -0.19097 | 0 | 900 | 172.122 | Conc Gen | 1486
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.7265 | 49 | -0.18932 | -9.2767 | 949 | 181.3987 | Weighted Imp. | 283.0637
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.3759 | 46 | -0.18932 | -8.7087 | 995 | 190.1075 | PTDF | 0.19049
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.3759 | 46 | -0.18932 | -8.7087 | 1041 | 198.8162
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.4927 | 47 | -0.18932 | -8.8981 | 1088 | 207.7143 | Concentration | 1.1654
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.11687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.9975 | 154 | -0.18932 | -29.1553 | 1242 | 236.8696
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.11687 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.2963 | 148 | -0.18932 | -28.0194 | 1390 | 264.889
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.6096 | 48 | -0.18932 | -9.0874 | 1438 | 273.9763
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.11687 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.6096 | 48 | -0.18932 | -9.0874 | 1486 | 283.0637
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.11629 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.0703 | 0 | -0.18875 | 0 | 1486 | 283.0637
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.11629 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.954 | 0 | -0.18875 | 0 | 1486 | 283.0637
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.11629 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.0703 | 0 | -0.18875 | 0 | 1486 | 283.0637
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.1122 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -14.8099 | 132 | -0.18465 | -24.3737
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.1122 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.0343 | 134 | -0.18465 | -24.743
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.1122 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -36.2393 | 323 | -0.18465 | -59.6417
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.11193 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.069 | 152.5 | -0.18438 | -28.1181
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.11193 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.7332 | 149.5 | -0.18438 | -27.565
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.11193 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.0345 | 232.6 | -0.18438 | -42.8871
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.11063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.4795 | 158 | -0.18308 | -28.9272
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.11063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.7008 | 160 | -0.18308 | -29.2933
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.11063 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.3603 | 175 | -0.18308 | -32.0396
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.10902 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9624 | 0 | -0.18148 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.10902 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9624 | 0 | -0.18148 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.10805 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9449 | 0 | -0.1805 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.10805 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9449 | 0 | -0.1805 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.10805 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6207 | 0 | -0.1805 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.1067 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.9877 | 0 | -0.17916 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.1067 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.0944 | 0 | -0.17916 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.10582 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -44.6544 | 422 | -0.17827 | -75.2296
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.10569 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4479 | 0 | -0.17814 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.10109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0544 | 50 | -0.17354 | -8.6771
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.10109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0544 | 50 | -0.17354 | -8.6771
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.10109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0544 | 50 | -0.17354 | -8.6771
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.10109 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0544 | 50 | -0.17354 | -8.6771
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.10053 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.60318 | 0 | -0.17298 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.098804 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -57.7015 | 0 | -0.17126 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.098804 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -58.7884 | 0 | -0.17126 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.098707 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -42.7401 | 0 | -0.17116 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.097094 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.7393 | 223.9 | -0.16955 | -37.9616
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.097094 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.8462 | 225 | -0.16955 | -38.1481
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.097094 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.8073 | 224.6 | -0.16955 | -38.0803
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.097094 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.0112 | 226.7 | -0.16955 | -38.4364
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.094298 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22632 | 0 | -0.16675 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.094298 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22632 | 0 | -0.16675 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.094298 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.26403 | 0 | -0.16675 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.093607 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2922 | 142 | -0.16606 | -23.5806
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.093607 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.573 | 145 | -0.16606 | -24.0787
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.093607 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.1347 | 151 | -0.16606 | -25.0751
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.093607 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.146 | 290 | -0.16606 | -48.1575
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.09308 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22339 | 0 | -0.16553 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.09308 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22339 | 0 | -0.16553 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.092826 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.3713 | 0 | -0.16528 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.5653 | 0 | -0.16513 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -20.5745 | 0 | -0.16513 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -17.0528 | 0 | -0.16513 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -20.7599 | 0 | -0.16513 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.658 | 0 | -0.16513 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.271 | 147 | -0.16273 | -23.9216
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.4585 | 138 | -0.16273 | -22.4571
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6391 | 140 | -0.16273 | -22.7825
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.271 | 147 | -0.16273 | -23.9216
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.4308 | 182 | -0.16273 | -29.6173
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.090279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.8752 | 198 | -0.16273 | -32.221
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.088393 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16085 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.088393 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16085 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.088393 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16085 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.088154 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -37.3773 | 0 | -0.16061 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.088154 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -37.4654 | 0 | -0.16061 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.088093 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -36.2943 | 412 | -0.16055 | -66.1451
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.088093 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.2372 | 400 | -0.16055 | -64.2185
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.087991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -18.3901 | 209 | -0.16044 | -33.5328
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.087991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -19.0061 | 216 | -0.16044 | -34.656
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.087991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0476 | 46 | -0.16044 | -7.3804
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.087991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.1356 | 47 | -0.16044 | -7.5409
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.087991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0476 | 46 | -0.16044 | -7.3804
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.087991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0476 | 46 | -0.16044 | -7.3804
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.087955 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.7977 | 407 | -0.16041 | -65.2862
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.087765 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6036 | 155 | -0.16022 | -24.8338
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.087765 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.92 | 170 | -0.16022 | -27.2371
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.087765 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6036 | 155 | -0.16022 | -24.8338
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.087462 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.0728 | 58 | -0.15992 | -9.2751
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.087462 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.7841 | 89 | -0.15992 | -14.2325
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.087462 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.8483 | 44 | -0.15992 | -7.0363
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.087462 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.8483 | 44 | -0.15992 | -7.0363
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.087462 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.7609 | 43 | -0.15992 | -6.8764
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.087462 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9358 | 45 | -0.15992 | -7.1962
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.087285 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -47.6576 | 0 | -0.15974 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.087285 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -65.4638 | 0 | -0.15974 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.087247 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.047 | 0 | -0.1597 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.082396 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -32.6288 | 0 | -0.15485 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.077588 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.8621 | 24 | -0.15004 | -3.601
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.077588 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.8621 | 24 | -0.15004 | -3.601
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.077588 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.7845 | 23 | -0.15004 | -3.4509
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.077015 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7015 | 100 | -0.14947 | -14.9468
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.077015 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7015 | 100 | -0.14947 | -14.9468
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.077015 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14947 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.077015 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14947 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.077015 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14947 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.077015 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14947 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.077008 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14946 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076673 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64405 | 8.4 | -0.14913 | -1.2527
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.076447 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1489 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.075413 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -47.4348 | 0 | -0.14787 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.075034 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14749 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.074193 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14665 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.074167 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.89 | 0 | -0.14662 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.074167 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.81584 | 0 | -0.14662 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.074167 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.89 | 0 | -0.14662 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.073262 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7329 | 146.5 | -0.14572 | -21.3473
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.073262 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.8354 | 147.9 | -0.14572 | -21.5513
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.073262 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6743 | 173 | -0.14572 | -25.2087
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.073117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.1352 | 207 | -0.14557 | -30.133
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.073117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.8445 | 216.7 | -0.14557 | -31.5451
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.073117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.6943 | 242 | -0.14557 | -35.228
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.073114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.5284 | 144 | -0.14557 | -20.9617
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.073114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.5284 | 144 | -0.14557 | -20.9617
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.073114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5025 | 171 | -0.14557 | -24.892
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.072972 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.7729 | 38 | -0.14543 | -5.5262
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.072972 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4084 | 19.3 | -0.14543 | -2.8067
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.072972 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0946 | 15 | -0.14543 | -2.1814
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.072972 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.4297 | 47 | -0.14543 | -6.835
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.072972 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.14543 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.8547 | 0 | -0.14538 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9898 | 0 | -0.14538 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.771 | 0 | -0.14538 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.3855 | 0 | -0.14538 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.8547 | 0 | -0.14538 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6252 | 0 | -0.14538 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1356 | 0 | -0.14538 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6043 | 0 | -0.14538 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.7925 | 0 | -0.14538 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6461 | 0 | -0.14538 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.0107 | 0 | -0.14538 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.072922 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6461 | 0 | -0.14538 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.072804 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1113 | 0 | -0.14526 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.07245 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7531 | 0 | -0.1449 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.072444 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7529 | 0 | -0.1449 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.072371 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8093 | 0 | -0.14482 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.072371 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8093 | 0 | -0.14482 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.072343 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -24.1626 | 334 | -0.1448 | -48.3619
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.072343 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -24.5966 | 340 | -0.1448 | -49.2307
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.072343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.0217 | 180 | -0.1448 | -26.0633
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.072343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.0217 | 180 | -0.1448 | -26.0633
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.072196 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.9953 | 180 | -0.14465 | -26.0369
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.072182 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.7046 | 0 | -0.14464 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.072182 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.7262 | 0 | -0.14464 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.072182 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.0438 | 0 | -0.14464 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.072173 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.2501 | 336 | -0.14463 | -48.5944
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.072173 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.9911 | 180 | -0.14463 | -26.0327
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.0719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.3536 | 144 | -0.14435 | -20.7869
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.0719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.5172 | 188 | -0.14435 | -27.1384
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7927 | 0 | -0.14416 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7927 | 0 | -0.14416 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7927 | 0 | -0.14416 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1473 | 0 | -0.14416 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7927 | 0 | -0.14416 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7927 | 0 | -0.14416 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7927 | 0 | -0.14416 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.071707 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0756 | 0 | -0.14416 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.2818 | 0 | -0.14386 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.9248 | 0 | -0.14386 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.1404 | 0 | -0.14386 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.3536 | 0 | -0.14386 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.4964 | 0 | -0.14386 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.071404 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.0683 | 0 | -0.14386 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.071404 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.85685 | 0 | -0.14386 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.071072 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.1883 | 0 | -0.14353 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.070906 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3822 | 47.7 | -0.14336 | -6.8382
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.070906 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6448 | 37.3 | -0.14336 | -5.3473
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.070906 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2617 | 46 | -0.14336 | -6.5945
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.070906 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4035 | 48 | -0.14336 | -6.8812
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.070237 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5452 | 22 | -0.14269 | -3.1392
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.070237 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.77261 | 11 | -0.14269 | -1.5696
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.070237 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.77261 | 11 | -0.14269 | -1.5696
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.069621 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0443 | 0 | -0.14207 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.069621 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6013 | 0 | -0.14207 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.069088 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5527 | 0 | -0.14154 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9263 | 0 | -0.14125 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48159 | 0 | -0.14125 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.6831 | 0 | -0.14125 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.032 | 0 | -0.14125 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48159 | 0 | -0.14125 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.032 | 0 | -0.14125 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.6831 | 0 | -0.14125 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.068798 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.6831 | 0 | -0.14125 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.066842 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2084 | 0 | -0.1393 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2329 | 0 | -0.13869 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3654 | 0 | -0.13869 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2329 | 0 | -0.13869 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2991 | 0 | -0.13869 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.1931 | 0 | -0.13869 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.656 | 0 | -0.13869 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.047 | 0 | -0.13869 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8547 | 0 | -0.13869 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.888 | 0 | -0.13869 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.066239 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9017 | 0 | -0.13869 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.054941 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12739 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.052284 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.3137 | 0 | -0.12474 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.044425 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -59.2185 | 0 | -0.11688 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.044425 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -58.9964 | 0 | -0.11688 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.3545 | 76 | -0.11659 | -8.8609
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.3545 | 76 | -0.11659 | -8.8609
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.6345 | 105 | -0.11659 | -12.2421
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.2662 | 74 | -0.11659 | -8.6278
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.2662 | 74 | -0.11659 | -8.6278
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.044138 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.5021 | 102 | -0.11659 | -11.8923
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.041523 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.7405 | 66 | -0.11398 | -7.5224
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.040863 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3485 | 0 | -0.11332 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.040863 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0216 | 0 | -0.11332 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.040863 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11332 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0609 | 0 | -0.10569 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3733 | 0 | -0.10569 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4958 | 0 | -0.10569 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3572 | 0 | -0.10569 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8586 | 0 | -0.10569 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9251 | 0 | -0.10569 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.662 | 0 | -0.10569 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59832 | 0 | -0.10569 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1246 | 0 | -0.10569 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3268 | 0 | -0.10569 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0941 | 0 | -0.10569 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3933 | 0 | -0.10569 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.154 | 0 | -0.10569 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3572 | 0 | -0.10569 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2243 | 0 | -0.10569 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4237 | 0 | -0.10569 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5262 | 0 | -0.10569 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6592 | 0 | -0.10569 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6592 | 0 | -0.10569 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.03324 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.684 | 0 | -0.10569 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.031242 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2182 | 0 | -0.1037 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.031242 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31242 | 0 | -0.1037 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.029662 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2925 | 0 | -0.10212 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.029662 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2925 | 0 | -0.10212 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.029662 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.5298 | 0 | -0.10212 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.029662 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.248 | 0 | -0.10212 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.023936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1034 | 0 | -0.096389 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.023722 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -15.443 | 0 | -0.096175 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.023722 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -13.3792 | 0 | -0.096175 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.023722 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -14.2332 | 0 | -0.096175 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.023674 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8589 | 0 | -0.096127 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.023674 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8589 | 0 | -0.096127 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.023674 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.8001 | 0 | -0.096127 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.023081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.76167 | 0 | -0.095534 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.02282 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.674 | 161 | -0.095273 | -15.339
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.02282 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.7881 | 166 | -0.095273 | -15.8154
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.02282 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.6594 | 248 | -0.095273 | -23.6278
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.02282 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -12.4597 | 546 | -0.095273 | -52.0192
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.02282 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -14.6733 | 0 | -0.095273 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.02282 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.29666 | 13 | -0.095273 | -1.2386
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.01981 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9869 | 0 | -0.092263 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.01981 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8403 | 0 | -0.092263 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.01981 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0345 | 0 | -0.092263 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.01981 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0206 | 0 | -0.092263 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.019809 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63389 | 0 | -0.092262 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.019809 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59427 | 0 | -0.092262 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.019794 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4014 | 0 | -0.092247 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.019794 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3203 | 0 | -0.092247 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.019794 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0491 | 0 | -0.092247 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0324 | 0 | -0.092247 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0384 | 0 | -0.092247 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0146 | 0 | -0.092247 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9002 | 0 | -0.092247 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.019794 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8297 | 0 | -0.092247 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.019794 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.79176 | 0 | -0.092247 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.018559 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.92795 | 50 | -0.091012 | -4.5506
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.017597 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.09005 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4991 | 0 | -0.088927 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4431 | 0 | -0.088927 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4332 | 0 | -0.088927 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89783 | 0 | -0.088927 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.016474 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20098 | 0 | -0.088927 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.016034 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0422 | 0 | -0.088487 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.016034 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.96204 | 0 | -0.088487 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.016034 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0422 | 0 | -0.088487 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.016034 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0422 | 0 | -0.088487 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.70743 | 46 | -0.087832 | -4.0403
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.70743 | 46 | -0.087832 | -4.0403
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.70743 | 46 | -0.087832 | -4.0403
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.84584 | 55 | -0.087832 | -4.8308
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.84584 | 55 | -0.087832 | -4.8308
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.015379 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.83047 | 54 | -0.087832 | -4.7429
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.015216 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1868 | 0 | -0.087669 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.015216 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2173 | 0 | -0.087669 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4465 | 0 | -0.087444 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3551 | 0 | -0.087444 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3611 | 0 | -0.087444 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3536 | 0 | -0.087444 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.014991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0326 | 0 | -0.087444 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.014808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51828 | 0 | -0.087261 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.014611 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.17533 | 12 | -0.087064 | -1.0448
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.014611 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.087064 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.0146 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.4674 | 169 | -0.087053 | -14.712
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.014585 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.4065 | 165 | -0.087038 | -14.3613
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.014573 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1714 | 0 | -0.087026 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.014573 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9487 | 0 | -0.087026 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.014533 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.0955 | 213 | -0.086986 | -18.5281
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.014528 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23535 | 0 | -0.086981 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.014524 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92954 | 0 | -0.086977 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.014524 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.91792 | 0 | -0.086977 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.014524 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1997 | 0 | -0.086977 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.014524 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.069 | 0 | -0.086977 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.014517 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.3099 | 228 | -0.08697 | -19.8292
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.01451 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6118 | 0 | -0.086963 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.01451 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3013 | 0 | -0.086963 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.01451 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2781 | 0 | -0.086963 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.014233 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0105 | 0 | -0.086686 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.014233 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0248 | 0 | -0.086686 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.014233 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55509 | 0 | -0.086686 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.014233 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42699 | 0 | -0.086686 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.013794 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.876 | 0 | -0.086247 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.013759 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.57788 | 42 | -0.086212 | -3.6209
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.013759 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.57788 | 42 | -0.086212 | -3.6209
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.013759 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.52284 | 38 | -0.086212 | -3.2761
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.013759 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.52284 | 38 | -0.086212 | -3.2761
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.013646 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3608 | 0 | -0.086099 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.013646 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8422 | 0 | -0.086099 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.3458 | 104 | -0.085393 | -8.8809
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.3458 | 104 | -0.085393 | -8.8809
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.69876 | 54 | -0.085393 | -4.6112
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.68582 | 53 | -0.085393 | -4.5258
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.69876 | 54 | -0.085393 | -4.6112
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.73758 | 57 | -0.085393 | -4.8674
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.69876 | 54 | -0.085393 | -4.6112
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.69876 | 54 | -0.085393 | -4.6112
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.75052 | 58 | -0.085393 | -4.9528
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.01294 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.75052 | 58 | -0.085393 | -4.9528
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.012669 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -9.3117 | 735 | -0.085122 | -62.5649
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42463 | 0 | -0.084942 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43337 | 0 | -0.084942 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40839 | 0 | -0.084942 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.57325 | 0 | -0.084942 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22106 | 0 | -0.084942 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25478 | 0 | -0.084942 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.24853 | 0 | -0.084942 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43711 | 0 | -0.084942 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2248 | 0 | -0.084942 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0666 | 0 | -0.084942 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.012489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8484 | 0 | -0.084942 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.012257 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.14708 | 12 | -0.08471 | -1.0165
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.011965 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.059825 | 0 | -0.084418 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.011965 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25127 | 0 | -0.084418 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.7774 | 0 | -0.084413 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.78936 | 0 | -0.084413 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8372 | 0 | -0.084413 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.75348 | 0 | -0.084413 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74152 | 0 | -0.084413 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2438 | 0 | -0.084413 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.01196 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70564 | 0 | -0.084413 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.011946 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.14335 | 0 | -0.084399 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.011925 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -8.8603 | 743 | -0.084378 | -62.693
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.01179 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.851 | 0 | -0.084243 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.011701 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.0126 | 172 | -0.084154 | -14.4745
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.011701 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.0126 | 172 | -0.084154 | -14.4745
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.011701 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.0126 | 172 | -0.084154 | -14.4745
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.011175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8193 | 0 | -0.083628 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.011175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8036 | 0 | -0.083628 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.011175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7757 | 0 | -0.083628 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.011175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0083 | 0 | -0.083628 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.010993 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.3752 | 398 | -0.083446 | -33.2116
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59763 | 56 | -0.083125 | -4.655
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.62965 | 59 | -0.083125 | -4.9044
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59763 | 56 | -0.083125 | -4.655
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59763 | 56 | -0.083125 | -4.655
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.62965 | 59 | -0.083125 | -4.9044
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.010672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59763 | 56 | -0.083125 | -4.655
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.007573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3101 | 0 | -0.080026 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.007573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1814 | 0 | -0.080026 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.007573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1662 | 0 | -0.080026 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.007573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1662 | 0 | -0.080026 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.007573 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2268 | 0 | -0.080026 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.072453 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.072453 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.072453 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.072453 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.072453 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.072453 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.072453 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.072453 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.092678 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -9.2678 | 0 | -0.0016838 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.050537 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.040457 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.090994 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.090994 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.019125 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.918 | 48 | 0.11012 | 5.2857
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.019125 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.87975 | 46 | 0.11012 | 5.0655
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.019125 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0081 | 105 | 0.11012 | 11.5625
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.021478 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.6873 | 0 | 0.11247 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.021507 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1125 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.021507 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1125 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.021507 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.36562 | 17 | 0.1125 | 1.9125
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.021507 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1125 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.021507 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1125 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.021529 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.3198 | 0 | 0.11252 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.021529 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.3585 | 0 | 0.11252 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.021529 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.3585 | 0 | 0.11252 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.021529 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.181 | 0 | 0.11252 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.026937 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.4718 | 0 | 0.11793 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.030037 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5056 | 0 | 0.12103 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.041916 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.13291 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.046247 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 39.5412 | 0 | 0.13724 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.046247 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 39.5412 | 0 | 0.13724 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.046247 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0434 | 0 | 0.13724 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.046247 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0758 | 0 | 0.13724 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.054475 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5759 | 0 | 0.14547 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.05461 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 45.1625 | 0 | 0.1456 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.05461 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 44.7256 | 0 | 0.1456 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.054698 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14569 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.054698 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14569 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.054851 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1961 | 0 | 0.14585 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.055263 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.421 | 0 | 0.14626 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.057599 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6398 | 0 | 0.14859 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.057599 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6398 | 0 | 0.14859 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.057658 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6126 | 0 | 0.14865 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.057672 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6138 | 0 | 0.14867 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.057773 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.333 | 0 | 0.14877 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.057773 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6218 | 0 | 0.14877 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.057773 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3109 | 0 | 0.14877 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.05824 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6592 | 0 | 0.14923 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.05824 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6592 | 0 | 0.14923 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.059986 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.28793 | 0 | 0.15098 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.063738 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.8036 | 0 | 0.15473 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.237 | 66 | 0.15519 | 10.2426
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.1728 | 65 | 0.15519 | 10.0874
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3012 | 67 | 0.15519 | 10.3978
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3012 | 67 | 0.15519 | 10.3978
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.064197 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3012 | 67 | 0.15519 | 10.3978
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.064197 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.15519 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.064197 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.15519 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.064254 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2489 | 0 | 0.15525 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.064254 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.9276 | 0 | 0.15525 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.064449 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6029 | 0 | 0.15544 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.064509 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.42576 | 0 | 0.1555 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.064509 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2127 | 0 | 0.1555 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.064794 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2893 | 0 | 0.15579 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.064794 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6867 | 0 | 0.15579 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.064794 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.0517 | 0 | 0.15579 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.064794 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.8983 | 0 | 0.15579 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.065096 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.7644 | 0 | 0.15609 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.6052 | 208.2 | 0.15634 | 32.5502
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.2858 | 142.1 | 0.15634 | 22.2161
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.6519 | 132.4 | 0.15634 | 20.6996
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.8872 | 136 | 0.15634 | 21.2624
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.606 | 147 | 0.15634 | 22.9822
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.065347 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.7229 | 210 | 0.15634 | 32.8317
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.5751 | 70 | 0.15635 | 10.9447
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.5751 | 70 | 0.15635 | 10.9447
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.0652 | 92.8 | 0.15635 | 14.5095
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.2286 | 80 | 0.15635 | 12.5082
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.2286 | 80 | 0.15635 | 12.5082
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.065358 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.5162 | 115 | 0.15635 | 17.9805
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.065378 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7919 | 0 | 0.15637 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.065386 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5713 | 0 | 0.15638 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.065511 | west | 8 | N | N | Nwest | Nwest | 1 | 1.6902 | 0 | 0.15651 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.065535 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.0376 | 0 | 0.15653 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.065794 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8953 | 0 | 0.15679 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.065794 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.33 | 0 | 0.15679 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.065794 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.1981 | 0 | 0.15679 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.065936 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9123 | 0 | 0.15693 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.065963 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9156 | 0 | 0.15696 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.066104 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8734 | 0 | 0.1571 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.066164 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.9095 | 0 | 0.15716 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.066164 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.9095 | 0 | 0.15716 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.066181 | west | 8 | N | N | Nwest | Nwest | 1 | 4.6327 | 0 | 0.15718 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.066181 | west | 8 | N | N | Nwest | Nwest | 1 | 4.8577 | 0 | 0.15718 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.066181 | west | 8 | N | N | Nwest | Nwest | 1 | 4.6591 | 0 | 0.15718 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.06637 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9555 | 0 | 0.15736 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.06637 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.6014 | 0 | 0.15736 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.06637 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.274 | 0 | 0.15736 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.06637 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0905 | 0 | 0.15736 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3889 | 66 | 0.15749 | 10.3945
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.5884 | 69 | 0.15749 | 10.867
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.5884 | 69 | 0.15749 | 10.867
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.4554 | 67 | 0.15749 | 10.552
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.4554 | 67 | 0.15749 | 10.552
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.066498 | west | 13 | Y | Y | Ywest | Ywest | 1 | 4.3224 | 65 | 0.15749 | 10.237
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.066545 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1923 | 0 | 0.15754 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.066601 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3907 | 0 | 0.1576 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.066601 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9921 | 0 | 0.1576 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.066619 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5953 | 0 | 0.15761 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.066619 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0638 | 0 | 0.15761 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.066619 | west | 7 | N | N | Nwest | Nwest | 1 | 1.6655 | 0 | 0.15761 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.066619 | west | 7 | N | N | Nwest | Nwest | 1 | 3.0445 | 0 | 0.15761 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.066619 | west | 7 | N | N | Nwest | Nwest | 1 | 3.0445 | 0 | 0.15761 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.066753 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.013 | 0 | 0.15775 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.066753 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7421 | 0 | 0.15775 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.066784 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.6099 | 0 | 0.15778 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.066926 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 41.1595 | 0 | 0.15792 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.066926 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 39.2856 | 0 | 0.15792 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.067026 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3782 | 0 | 0.15802 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.067026 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3782 | 0 | 0.15802 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5257 | 0 | 0.15835 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2403 | 0 | 0.15835 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.0925 | 0 | 0.15835 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0149 | 0 | 0.15835 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.072 | 0 | 0.15835 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.067352 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4218 | 0 | 0.15835 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.067506 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.1259 | 0 | 0.1585 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.067528 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1134 | 0 | 0.15852 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.067528 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5423 | 0 | 0.15852 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.067528 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.8145 | 0 | 0.15852 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.067528 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.303 | 0 | 0.15852 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.067816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.2199 | 150.7 | 0.15881 | 23.9327
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.067816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.2402 | 151 | 0.15881 | 23.9803
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.067816 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.0306 | 177.4 | 0.15881 | 28.1729
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.067899 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.2867 | 151.5 | 0.15889 | 24.0723
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.067899 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.341 | 152.3 | 0.15889 | 24.1994
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.067899 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.0521 | 177.5 | 0.15889 | 28.2036
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.06846 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1076 | 0 | 0.15945 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.069854 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.1912 | 0 | 0.16085 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.069918 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.9672 | 0 | 0.16091 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.069923 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.5018 | 0 | 0.16092 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.070644 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.8572 | 182 | 0.16164 | 29.4182
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.070644 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 34.1917 | 484 | 0.16164 | 78.2329
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.070772 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6774 | 0 | 0.16177 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.071139 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.557 | 0 | 0.16213 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.071161 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.16216 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.071382 | west | 4 | Y | N | Ywest | Nwest | 1 | 46.3769 | 0 | 0.16238 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.071594 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.0371 | 224 | 0.16259 | 36.4198
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.071647 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.6038 | 0 | 0.16264 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.071647 | north | 1 | N | N | Nnorth | Nnorth | 1 | 9.3141 | 0 | 0.16264 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.071647 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.3888 | 0 | 0.16264 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.071647 | north | 1 | N | N | Nnorth | Nnorth | 1 | 28.5872 | 0 | 0.16264 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.071998 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 56.5184 | 0 | 0.16299 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.071998 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 57.2384 | 0 | 0.16299 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.071998 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 56.1584 | 0 | 0.16299 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.072799 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 17.6174 | 242 | 0.16379 | 39.638
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.07344 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.4688 | 20 | 0.16443 | 3.2887
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.07344 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.4688 | 20 | 0.16443 | 3.2887
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.07344 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.4688 | 20 | 0.16443 | 3.2887
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.07344 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.2485 | 17 | 0.16443 | 2.7954
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.07346 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.8864 | 366 | 0.16445 | 60.1903
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.073935 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 8.8722 | 0 | 0.16493 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.073999 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.4019 | 73 | 0.16499 | 12.0445
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.073999 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.8059 | 119 | 0.16499 | 19.6342
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.073999 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.1698 | 205 | 0.16499 | 33.8236
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.073999 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.5479 | 102 | 0.16499 | 16.8293
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.073999 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.1039 | 96 | 0.16499 | 15.8394
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.074036 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.88843 | 0 | 0.16503 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.074036 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.88843 | 0 | 0.16503 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.0581 | 161 | 0.16589 | 26.7082
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.2828 | 164 | 0.16589 | 27.2058
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.2828 | 164 | 0.16589 | 27.2058
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.0065 | 414 | 0.16589 | 68.6781
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.133 | 162 | 0.16589 | 26.8741
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.0581 | 161 | 0.16589 | 26.7082
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.2079 | 163 | 0.16589 | 27.0399
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.074895 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.6321 | 409 | 0.16589 | 67.8487
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.075431 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.5086 | 20 | 0.16643 | 3.3285
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.075432 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8858 | 25 | 0.16643 | 4.1607
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.075432 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0927 | 41 | 0.16643 | 6.8235
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.075504 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.3591 | 18 | 0.1665 | 2.997
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.075504 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.3591 | 18 | 0.1665 | 2.997
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.075504 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.8692 | 38 | 0.1665 | 6.3269
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.075525 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.4071 | 204 | 0.16652 | 33.9699
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.075525 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.1805 | 201 | 0.16652 | 33.4704
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.075525 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.277 | 242 | 0.16652 | 40.2977
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.07553 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0212 | 40 | 0.16652 | 6.661
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.075548 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.9683 | 79 | 0.16654 | 13.1568
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.075548 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.0081 | 106 | 0.16654 | 17.6535
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.075548 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.03 | 146 | 0.16654 | 24.3152
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.075548 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.7416 | 76 | 0.16654 | 12.6572
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.075576 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 42.1714 | 0 | 0.16657 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.075576 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 43.7585 | 0 | 0.16657 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.075576 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 61.0654 | 0 | 0.16657 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.075598 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 29.332 | 388 | 0.16659 | 64.6378
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.075598 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 38.933 | 515 | 0.16659 | 85.795
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.0756 | north | 8 | N | N | Nnorth | Nnorth | 1 | 5.67 | 0 | 0.16659 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.0756 | north | 8 | N | N | Nnorth | Nnorth | 1 | 6.0178 | 0 | 0.16659 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.0756 | north | 8 | N | N | Nnorth | Nnorth | 1 | 6.683 | 0 | 0.16659 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.1072 | 160 | 0.16666 | 26.6663
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8045 | 156 | 0.16666 | 25.9996
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.8313 | 196 | 0.16666 | 32.6662
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8045 | 156 | 0.16666 | 25.9996
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8802 | 157 | 0.16666 | 26.1663
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.9827 | 198 | 0.16666 | 32.9995
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.8313 | 196 | 0.16666 | 32.6662
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.07567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.3994 | 111 | 0.16666 | 18.4997
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.075711 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.1357 | 0 | 0.16671 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.075711 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.1357 | 0 | 0.16671 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.075734 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 28.0216 | 370 | 0.16673 | 61.6895
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.6028 | 0 | 0.16673 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.6785 | 0 | 0.16673 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | 1 | 23.4018 | 0 | 0.16673 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.83 | 0 | 0.16673 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | 1 | 10.9057 | 0 | 0.16673 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.075734 | north | 1 | N | N | Nnorth | Nnorth | 1 | 23.4775 | 0 | 0.16673 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.0758 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.886 | 170 | 0.16679 | 28.355
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.0758 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 39.416 | 520 | 0.16679 | 86.733
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.075868 | north | 5 | N | N | Nnorth | Nnorth | 1 | 3.0347 | 0 | 0.16686 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.075868 | north | 5 | N | N | Nnorth | Nnorth | 1 | 3.0347 | 0 | 0.16686 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.075909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.8618 | 288 | 0.1669 | 48.0681
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.075909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.1586 | 147 | 0.1669 | 24.5348
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.075909 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.1586 | 147 | 0.1669 | 24.5348
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.07595 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.16694 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.07595 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.16694 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.075996 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 8.5495 | 0 | 0.16699 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.076168 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.4252 | 150 | 0.16716 | 25.0743
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.076168 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0934 | 80 | 0.16716 | 13.373
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.076301 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1673 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.076347 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.16734 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.076565 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.5939 | 60 | 0.16756 | 10.0536
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.076565 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.8236 | 63 | 0.16756 | 10.5562
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.077065 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3945 | 70 | 0.16806 | 11.7641
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.077065 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3175 | 69 | 0.16806 | 11.5961
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.077065 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.3175 | 69 | 0.16806 | 11.5961
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.077065 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.2404 | 68 | 0.16806 | 11.428
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.077179 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.1071 | 118 | 0.16817 | 19.8444
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.077179 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.8756 | 115 | 0.16817 | 19.3399
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.077179 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 42.9115 | 556 | 0.16817 | 93.5043
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.077514 | north | 3 | N | N | Nnorth | Nnorth | 1 | 89.6837 | 0 | 0.16851 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.077514 | north | 3 | N | N | Nnorth | Nnorth | 1 | 89.7612 | 0 | 0.16851 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.077524 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.16852 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.077524 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.16852 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.077524 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.16852 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.077906 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.929 | 217.3 | 0.1689 | 36.702
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.077906 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.9707 | 205 | 0.1689 | 34.6246
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.077906 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.2216 | 272.4 | 0.1689 | 46.0084
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.078104 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1691 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.078647 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.2127 | 168 | 0.16964 | 28.4997
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.078647 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.0782 | 90 | 0.16964 | 15.2677
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.079171 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 34.4394 | 435 | 0.17017 | 74.0219
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.079375 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.3531 | 395 | 0.17037 | 67.2959
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.079375 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 34.5281 | 435 | 0.17037 | 74.1106
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.083592 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.7246 | 224 | 0.17459 | 39.1073
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.083592 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.8918 | 226 | 0.17459 | 39.4565
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.083592 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.7215 | 212 | 0.17459 | 37.0123
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.083592 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.6379 | 211 | 0.17459 | 36.8377
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.08397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.1711 | 216.4 | 0.17496 | 37.8623
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.08397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.1459 | 216.1 | 0.17496 | 37.8098
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.098838 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.2037 | 255 | 0.18983 | 48.4072
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.098838 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.7269 | 149 | 0.18983 | 28.285
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.098838 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 15.1222 | 153 | 0.18983 | 29.0443
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.13567 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.22667 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.13567 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 106.7747 | 787 | 0.22667 | 178.3871

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
20
25
30
35
40
45
50
55
60
65
70
75
80
85
90
95
100
105
110
| 115 | 0
| Max | 750
| Min | 750
| Avg | 750