## test results
CRE test for: |  | 3650 ELGIN_SS 13430 SAND_TXU | [5 empty] | FAIL
Line Rating: |  | 247.95
Direcction |  | North | → | South |  | N-S
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3650 ELGIN_SS 13430 SAND_TXU
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.022286
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.025289
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.019821
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.0069746
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3650 ELGIN_SS 13430 SAND_TXU
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.023804
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.034557
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.019919
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.0064668
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3650 ELGIN_SS 13430 SAND_TXU
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.056842
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.0023665
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.028753
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.045208
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.018314
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.026288
PTDF tests
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.056842 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.056842 | -0.056842
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.086767
[6 empty] | Concentration |  | -1.5264 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.067738
[6 empty] | Concentration |  | -1.1917 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 95.2703
| Percent of line rating => | [6 empty] | 38.42% | FAIL
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -7.0709
[7 empty] | B1(N-S) | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B2 (N-W) | -0.00011958 | 0.016614 | 0.016733 | -0.00011958
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.015845 | 0.21915 | 0.20331 | 0.015845
[7 empty] | B4 (S-W) | -0.069923 | -0.38958 | -0.31966 | -0.069923
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.057549 | -0.18705 | -0.1295 | -0.057549
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.015914 | 0.20179 | 0.18588 | 0.015914
[7 empty] | test | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B1 | 0%
Deployment Error Percent | [6 empty] | B2 | -0.02975%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 3.942%
[7 empty] | B4 | -17.4%
[7 empty] | B5 | -14.32%
[7 empty] | B6 | 3.959%
[7 empty] | Max Abs Error | 17.4% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-S
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3650 ELGIN_SS 13430 SAND_TXU C:SANDOW__5-L_AUSTRO5_1Y C:L_AUSTRO5_1Y-SAND_TXU_59 [3429 - 7040 ckt1] and [7040 - 13429 ckt2] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3650 ELGIN_SS 13430 SAND_TXU C:SANDOW__5-L_AUSTRO5_1Y C:L_AUSTRO5_1Y-SAND_TXU_59 [3429 - 7040 ckt1] and [7040 - 13429 ckt2]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.031757 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -8.098
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.031757 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -4.7318
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.029433 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.4415
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.029433 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.4415
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.031757 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -4.8588
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.03064 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -4.596
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.03064 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -2.4512
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.023301 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -1.701
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.023301 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -2.7728
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.023301 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -4.7767
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.023301 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -2.3767
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.023301 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -2.2369
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.022698 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.27238
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.022698 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.27238
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.024326 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -4.0868
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.024326 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -2.1893
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.023199 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.41758
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.023199 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.41758
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.023199 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -0.88156
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.023058 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -6.6407
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.023058 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -3.3895
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.023058 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -3.3895
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.022924 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -2.5789
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.022863 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -0.91452
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.022851 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -1.8052
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.022851 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -2.4222
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.022851 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -3.3362
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.022851 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -1.7367
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.022981 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -1.3789
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.022981 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -1.4478
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.022832 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -0.45664
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.022832 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -0.5708
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.022832 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -0.93611
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.010702 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -4.955
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -1.284
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -1.2646
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -1.3035
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -1.3035
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -1.3035
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -2.2179
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.019455 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -10.0193
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -1.3338
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -1.3944
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -1.3944
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -1.354
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -1.354
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -1.3136
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.020096 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -1.4067
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.020096 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -1.475
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.020096 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -1.4148
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.020156 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -3.0234
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.020156 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -4.4343
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.020254 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -2.0051
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.020254 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -1.2355
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.020248 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -2.855
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.020254 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -0.50635
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.020254 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -0.92561
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.020254 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -0.92561
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.020248 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -2.4298
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.019918 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -0.51388
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.01985 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -1.9949
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.020037 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -2.4044
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.019845 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -1.151
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.019896 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -4.2617
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.020376 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -3.0564
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.019646 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -0.12966
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.019646 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -0.67386
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.020376 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -2.058
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.020046 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -2.4055
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | -0.02213 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | -8.0996
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.02215 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -5.3603
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.021175 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -8.47
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.021176 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -4.9975
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.021405 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -3.5318
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.022657 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -4.622
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.022657 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -4.5541
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.022657 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -5.483
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.022178 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.44356
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.022178 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.44356
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.022178 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.44356
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.022178 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -0.37703
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.022686 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -2.7223
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.022892 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -1.3735
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.022841 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -1.7131
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.022841 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -1.8181
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.022841 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -2.0191
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -3.656
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -3.5646
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -4.4786
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -3.5646
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -3.5875
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -4.5243
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.022872 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -3.8882
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.022872 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -11.8934
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022859 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -8.4578
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.022835 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -12.7419
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.022835 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -13.2215
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.022835 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -18.4507
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.023184 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -2.5966
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.023184 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -2.3184
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.023184 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -8.7636
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.023301 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -5.0633
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.023301 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -4.7767
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.023301 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -6.3472
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.02338 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -18.0026
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.023677 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -1.6574
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.023677 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -1.6337
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.023677 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -1.6337
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.023677 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -1.61
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.023239 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -26.8875
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.023239 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -26.9108
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.024283 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -5.4394
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.024283 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -5.488
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.024247 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -5.2471
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.024247 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -5.2398
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.024283 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -5.148
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.024283 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -5.1237
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.023531 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -9.2947
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.023506 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -10.2251
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.023531 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -10.236
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.022949 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -3.167
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.023125 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -2.7287
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.023125 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -2.6594
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.023125 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -12.8575
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.022841 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -8.8623
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.022841 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -11.7631
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.022219 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -17.4419
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.022219 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -17.6641
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.022219 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -17.3308
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.022121 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -4.026
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.022121 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -10.7066
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.023169 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -5.1899
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.022078 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -1.1039
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.022088 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -0.9277
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.020914 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -12.8621
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.020914 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -12.2765
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.033181 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -17.8182
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.033181 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -26.1134
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.033067 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -2.48
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.033067 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -7.3409
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.12216 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -69.5119
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.032064 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 6.7014
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.032064 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 6.9258
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.031989 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 13.0195
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.032064 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 1.4749
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.032064 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 1.507
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.032064 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 1.4749
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.032064 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 1.4749
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.032062 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 13.5943
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.032062 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 13.6264
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.031832 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 1.8463
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.031832 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 2.833
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.031832 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 1.4006
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.031832 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 1.4006
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.031832 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 1.3688
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.031832 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 1.4324
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.03208 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 13.217
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.03208 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 12.832
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.031755 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 17.3382
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.031755 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 23.8163
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.032165 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 1.9621
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.032165 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 3.0557
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.032165 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 4.8569
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.031901 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 4.9447
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.031901 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 5.4232
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.031901 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 4.9447
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.026289 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.57836
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.026289 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.28918
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.026289 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.28918
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.026573 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 1.2675
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.026573 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.99117
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.026573 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 1.2224
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.026573 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 1.2755
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.027318 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.32782
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.027318 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.3005
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.028499 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.68398
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.028499 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.68398
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.028499 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.65548
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.030121 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 11.9279
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.016409 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 21.8732
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.016409 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 21.7912
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.02691 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 1.0226
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.02691 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.51936
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.02691 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.40365
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.02691 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 1.2648
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.017365 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -1.3024
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.020552 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -3.0828
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.019469 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -3.3
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.008531 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -1.2796
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.020231 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -1.2746
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.021593 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -14.029
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.022884 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.91536
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.022884 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.91536
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.031906 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 13.4643
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.064481 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 8.5115
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.064481 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 8.6405
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.064481 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 20.8274
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.039065 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 6.1723
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.039065 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 6.2504
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.039065 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 6.8364
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.03682 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 21.5029
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.03682 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 21.9079
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.036779 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 15.9253
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.035192 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 7.8795
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.035192 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 7.9182
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.035192 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 7.9041
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.035192 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 7.978
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.046464 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.37171
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.046464 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.37171
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.027455 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.49419
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.027455 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.49419
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.027455 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.41182
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.028353 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.38844
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.035064 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.63115
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.035064 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.63115
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.042227 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 1.4779
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.042227 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 1.4357
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.042227 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 1.4779
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.032137 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.89984
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.032137 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.93197
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.019474 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -0.68159
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.019474 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -0.58422
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.049411 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 2.4705
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.049411 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 2.4705
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.049411 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 2.4705
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.049411 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 2.4705
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.037245 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.22347
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.035409 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.084982
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.035409 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.084982
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.035409 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.099145
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.034003 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.13601
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.036677 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.088025
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.036677 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.088025
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 4.8242
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 4.5289
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 4.5945
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 4.8242
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 5.9729
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 6.498
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.03983 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 6.0741
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.03983 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 5.9546
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.03983 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 9.2645
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.033998 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 4.8277
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.033998 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 4.9297
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.033998 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 5.1337
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.033998 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 9.8594
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.015927 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.52559
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.015927 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.39818
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.027318 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.32782
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.026749 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 1.9527
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 1.9662
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 2.0159
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.72313
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.18078
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 1.9662
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 1.991
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 1.9512
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.6222
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 1.1448
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.028015 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 17.6214
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.027079 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 3.8994
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.027079 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 5.0909
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.034605 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.41526
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.019834 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.119
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.026657 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 8.9568
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.026712 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 8.9218
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.026712 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 9.0821
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.026763 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 1.017
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.026732 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.6683
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.026732 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.6683
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.026751 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 1.0165
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.026861 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.77897
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.02666 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 3.9537
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.02666 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 3.9617
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.02666 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 4.079
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 4.1707
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 4.0387
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 2.6397
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 3.8276
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 3.8804
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 3.3524
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.027008 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 3.9567
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.027008 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 3.9945
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.027008 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 4.6724
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.026959 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 5.5805
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.026959 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 5.842
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.026959 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 6.5241
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.026958 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 3.882
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.026958 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 3.882
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.026958 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 4.6098
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.046657 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 14.4637
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.046657 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 19.2693
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.04825 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 2.0265
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.04825 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 2.123
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.04825 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 2.123
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.04825 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 2.2677
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 2.2256
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 2.0893
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 2.0893
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 2.1347
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.04542 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 6.9947
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.04542 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 6.7222
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 2.1802
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 2.1802
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -1.3881
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -1.3881
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -1.8402
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -1.5864
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -1.5864
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -2.2805
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -4.1278
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -2.8173
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -2.625
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -2.6963
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -2.9144
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -4.1635
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.020489 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -4.2822
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.020489 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -2.5919
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.020489 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -5.1018
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.020489 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -4.0363
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.020156 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -4.0312
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.020156 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -2.457
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.019538 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -2.9112
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.020105 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -3.6189
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.020105 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -3.6189
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.020085 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -4.5191
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.020353 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -2.5441
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.020353 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -2.5441
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -3.2003
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -3.2231
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -7.0634
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -3.2688
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -3.2917
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -7.0863
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.023589 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -4.6234
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.023589 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -2.6184
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.022961 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -3.6561
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -3.7243
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -3.7243
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -9.4015
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -3.6789
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -3.6561
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -3.7016
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -9.288
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.022894 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.022894 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.022137 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -3.2763
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.022137 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -2.8778
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.022137 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -3.2099
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.022137 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -8.8327
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.021119 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -3.1826
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.021119 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -3.189
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.021119 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -3.7465
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.021161 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -3.2059
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.021161 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -3.2228
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.021161 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -3.7561
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.12216 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -70.9779
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.016172 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -13.8271
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.016172 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -13.8271
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.017029 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.54493
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.019306 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -0.92669
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.019306 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -0.88808
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.017178 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.20614
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.017178 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -0.87608
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.017178 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.29203
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.017178 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.37792
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.017178 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.42945
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.019306 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -2.0271
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.020309 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -1.706
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.017328 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -1.3862
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.017308 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -2.5962
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.017308 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -2.5962
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007323 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 0.51847
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007323 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 0.48844
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007323 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 0.38812
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 1.1219
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 1.1241
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 1.1153
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 0.70301
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 1.7868
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007323 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 0.29292
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.007329 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 0.7351
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.007329 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 0.68086
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.007329 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 0.75269
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.007329 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 0.74756
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.007328 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 0.2345
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.007328 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 0.21984
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.011105 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 1.2327
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.011105 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 1.2327
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.011105 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 1.3215
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.011105 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 1.216
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.016172 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -2.463
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.016172 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -2.4743
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.005092 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 0.69251
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.008579 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.28311
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.005074 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.21311
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.005074 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.21311
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.005074 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.19281
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.005074 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.19281
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.011621 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 0.82509
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.011621 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.11621
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.008765 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.4287
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.008765 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.4287
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.008765 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 2.1474
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.005923 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.38499
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.005923 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 0.35538
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.005923 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.38499
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.005923 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.38499
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.00538 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 0.80162
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.00538 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 0.35024
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 0.55401
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 0.53331
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 0.52966
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 0.3318
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.074274
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.004387 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 3.2595
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.004666 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 3.4295
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.004302 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.73994
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.004302 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.73994
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.004302 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.73994
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00276 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 0.47748
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.005036 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 0.87123
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.005036 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 0.67986
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.004105 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 0.66829
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.004105 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 0.66255
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.004105 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 0.65228
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.004105 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 1.1051
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.005361 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 0.3431
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.005361 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 0.33882
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.005361 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 0.44282
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.005361 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 0.39457
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 0.90217
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 0.86845
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 0.87066
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 0.8679
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 1.487
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.022015
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 0.092463
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.008206 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -1.2654
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.008206 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -1.2801
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.008206 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -1.2801
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.008206 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -3.1183
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.004043 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 1.6091
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.2616
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.2616
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.2616
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.31278
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.31278
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 0.3071
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.018187 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -15.0406
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.018187 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -14.8952
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.008902 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.41038
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 1.2822
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 1.2822
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 1.7715
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 1.2485
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 1.2485
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 1.7208
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.005357 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 0.96426
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.005357 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 0.84962
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.005357 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 0.84105
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.005469 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 0.19142
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.006504 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 2.9853
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 0.28619
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 0.2906
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 0.30821
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 0.27739
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 0.27299
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 0.45791
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 0.25978
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00276 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 0.43056
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00276 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 0.42504
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00276 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 0.42504
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.00276 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 0.44712
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.00434 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 0.68138
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.005252 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 0.37289
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.005252 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 0.37814
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.005252 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 0.20483
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.005252 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 0.15756
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.005618 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 0.4382
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.005618 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 0.44944
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.005362 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 0.086864
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.005384 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 0.88836
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.00539 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 0.91091
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.005364 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 1.1425
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.005359 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 1.2219
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.005394 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.064728
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.005394 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 0.097092
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.006883 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 0.34415
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.49681
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.49681
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.25796
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.25318
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.25796
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.27229
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.25796
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.25796
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.27707
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.27707
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.00452 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.05424
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.21952
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.23128
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.21952
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.21952
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.23128
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.21952
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.015746 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 1.0392
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008543 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 1.3754
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008543 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 1.4181
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008543 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 2.1187
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008543 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 4.6645
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008543 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 5.4931
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.008783 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 5.7177
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.008783 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 4.9536
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.008783 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 5.2698
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.008543 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.11106
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.004395 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.05274
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 0.15637
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 0.15959
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 0.15039
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 0.21109
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 0.081402
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 0.09382
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 0.09152
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 0.16096
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 0.082782
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 0.39275
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 0.68065
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 0.76254
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 0.87815
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.55346
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 1.2422
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 1.0577
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 1.0823
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.61495
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.22138
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 1.1561
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 0.86093
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 0.77484
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 0.88553
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 0.79698
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 1.2422
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 1.193
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 1.2668
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 0.93472
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.98392
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.98392
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 2.1031
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.23675
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.016415 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -1.2557
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.017365 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -1.3892
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.017365 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -0.6946
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.017518 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -1.4014
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.017332 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -1.3866
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.016545 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -1.3236
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.016287 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -1.3681
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.017518 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -1.4014
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 3.7952
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.020077 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -2.4092
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.020077 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -4.6779
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.020077 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -3.4171
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 7.3906
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 6.1255
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 7.4572
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 3.8285
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 3.3291
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.020841 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -1.2505
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.016402 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.012179 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.018085 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -0.086808
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -0.76744
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -2.2
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -2.7628
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -2.4353
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -2.1488
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -1.6474
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.019835 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -2.9752
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.019756 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -2.2226
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.019756 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -2.9535
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.019756 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -3.6746
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.019756 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -4.2377
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.02691 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.020743 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.028287 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.69686
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 1.0851
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 1.8417
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 2.5278
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 1.1026
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 1.0219
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.51095
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 2.5278
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.96811
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 1.1564
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.59162
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 1.0072
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.38739
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.18078
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.38739
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 1.0072
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 1.0072
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 3.98
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 1.3446
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 1.4791
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 1.3446
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.026397 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.31676
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.026145 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.39217
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.026145 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.60133
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.025113 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 1.2054
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.025911 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.20729
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.026665 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 4.7997
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.026657 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 4.7983
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.026712 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 4.8082
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.026712 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 4.8082
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.02829 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 2.829
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.02829 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 2.829
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.66235
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.66235
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.66235
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.4239
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.66235
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.66235
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.66235
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.39741
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.02829 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.02829 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 14.145
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.02829 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 14.145
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.02829 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.028395 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.015927 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.027613 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.027337 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L:3650 ELGIN_SS 13430 SAND_TXU C:SANDOW__5-L_AUSTRO5_1Y C:L_AUSTRO5_1Y-SAND_TXU_59 [3429 - 7040 ckt1] and [7040 - 13429 ckt2] | [7 empty] | 95.2703
Number of Bus | Name of Bus | ID | Max MW | L:3650 ELGIN_SS 13430 SAND_TXU C:SANDOW__5-L_AUSTRO5_1Y C:L_AUSTRO5_1Y-SAND_TXU_59 [3429 - 7040 ckt1] and [7040 - 13429 ckt2] | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.031757 | north | -0.0094711 | -0.057046 | -0.011936 | -0.038732 | 0.0094711 | North | N | 0.0094711 | 0
239 | BOSQUESW | 1 | 149 | -0.031757 | north | -0.0094711 | -0.057046 | -0.011936 | -0.038732 | 0.0094711 | North | N | 0.0094711 | 0
244 | WHITNYDM | 1 | 15 | -0.029433 | north | -0.0071471 | -0.054722 | -0.0096116 | -0.036408 | 0.0071471 | North | N | 0.0071471 | 0
245 | WHITNYDM | 2 | 15 | -0.029433 | north | -0.0071471 | -0.054722 | -0.0096116 | -0.036408 | 0.0071471 | North | N | 0.0071471 | 0
247 | BOSQUESW | 2 | 153 | -0.031757 | north | -0.0094711 | -0.057046 | -0.011936 | -0.038732 | 0.0094711 | North | N | 0.0094711 | 0
251 | BOSQUESW | 2 | 150 | -0.03064 | north | -0.0083541 | -0.055929 | -0.010819 | -0.037615 | 0.0083541 | North | N | 0.0083541 | 0
253 | BOSQUESW | 2 | 80 | -0.03064 | north | -0.0083541 | -0.055929 | -0.010819 | -0.037615 | 0.0083541 | North | N | 0.0083541 | 0
332 | RWMILLER | 1 | 73 | -0.023301 | north | -0.0010151 | -0.04859 | -0.0034796 | -0.030276 | 0.0010151 | North | N | 0.0010151 | 0
333 | RWMILLER | 2 | 119 | -0.023301 | north | -0.0010151 | -0.04859 | -0.0034796 | -0.030276 | 0.0010151 | North | N | 0.0010151 | 0
334 | RWMILLER | 3 | 205 | -0.023301 | north | -0.0010151 | -0.04859 | -0.0034796 | -0.030276 | 0.0010151 | North | N | 0.0010151 | 0
335 | RWMILLER | 4 | 102 | -0.023301 | north | -0.0010151 | -0.04859 | -0.0034796 | -0.030276 | 0.0010151 | North | N | 0.0010151 | 0
336 | RWMILLER | 5 | 96 | -0.023301 | north | -0.0010151 | -0.04859 | -0.0034796 | -0.030276 | 0.0010151 | North | N | 0.0010151 | 0
344 | MRSSHPRD | 1 | 12 | -0.022698 | north | -0.0004121 | -0.047987 | -0.0028766 | -0.029673 | 0.0004121 | North | N | 0.0004121 | 0
345 | MRSSHPRD | 2 | 12 | -0.022698 | north | -0.0004121 | -0.047987 | -0.0028766 | -0.029673 | 0.0004121 | North | N | 0.0004121 | 0
366 | JNSNCNTY | 1 | 168 | -0.024326 | north | -0.0020401 | -0.049615 | -0.0045046 | -0.031301 | 0.0020401 | North | N | 0.0020401 | 0
367 | JNSNCNTY | 2 | 90 | -0.024326 | north | -0.0020401 | -0.049615 | -0.0045046 | -0.031301 | 0.0020401 | North | N | 0.0020401 | 0
503 | NTHTEXAS | 1 | 18 | -0.023199 | north | -0.0009131 | -0.048488 | -0.0033776 | -0.030174 | 0.0009131 | North | N | 0.0009131 | 0
504 | NTHTEXAS | 2 | 18 | -0.023199 | north | -0.0009131 | -0.048488 | -0.0033776 | -0.030174 | 0.0009131 | North | N | 0.0009131 | 0
505 | NTHTEXAS | 3 | 38 | -0.023199 | north | -0.0009131 | -0.048488 | -0.0033776 | -0.030174 | 0.0009131 | North | N | 0.0009131 | 0
580 | JCKCNTY8 | 1 | 288 | -0.023058 | north | -0.0007721 | -0.048347 | -0.0032366 | -0.030033 | 0.0007721 | North | N | 0.0007721 | 0
581 | JCKCNTY8 | 2 | 147 | -0.023058 | north | -0.0007721 | -0.048347 | -0.0032366 | -0.030033 | 0.0007721 | North | N | 0.0007721 | 0
582 | JCKCNTY8 | 3 | 147 | -0.023058 | north | -0.0007721 | -0.048347 | -0.0032366 | -0.030033 | 0.0007721 | North | N | 0.0007721 | 0
728 | WOLFRIDG | 1 | 112.5 | -0.022924 | north | -0.0006381 | -0.048213 | -0.0031026 | -0.029899 | 0.0006381 | North | N | 0.0006381 | 0
837 | NEWMAN_G | 1 | 40 | -0.022863 | north | -0.0005771 | -0.048152 | -0.0030416 | -0.029838 | 0.0005771 | North | N | 0.0005771 | 0
842 | OLINGER_ | 1 | 79 | -0.022851 | north | -0.0005651 | -0.04814 | -0.0030296 | -0.029826 | 0.0005651 | North | N | 0.0005651 | 0
843 | OLINGER_ | 1 | 106 | -0.022851 | north | -0.0005651 | -0.04814 | -0.0030296 | -0.029826 | 0.0005651 | North | N | 0.0005651 | 0
844 | OLINGER_ | 1 | 146 | -0.022851 | north | -0.0005651 | -0.04814 | -0.0030296 | -0.029826 | 0.0005651 | North | N | 0.0005651 | 0
845 | OLINGER_ | 1 | 76 | -0.022851 | north | -0.0005651 | -0.04814 | -0.0030296 | -0.029826 | 0.0005651 | North | N | 0.0005651 | 0
923 | SPENCER_ | 1 | 60 | -0.022981 | north | -0.0006951 | -0.04827 | -0.0031596 | -0.029956 | 0.0006951 | North | N | 0.0006951 | 0
924 | SPENCER_ | 1 | 63 | -0.022981 | north | -0.0006951 | -0.04827 | -0.0031596 | -0.029956 | 0.0006951 | North | N | 0.0006951 | 0
948 | STEAM1 | 1 | 20 | -0.022832 | north | -0.0005461 | -0.048121 | -0.0030106 | -0.029807 | 0.0005461 | North | N | 0.0005461 | 0
949 | STEAM2 | 1 | 25 | -0.022832 | north | -0.0005461 | -0.048121 | -0.0030106 | -0.029807 | 0.0005461 | North | N | 0.0005461 | 0
950 | STEAM3 | 1 | 41 | -0.022832 | north | -0.0005461 | -0.048121 | -0.0030106 | -0.029807 | 0.0005461 | North | N | 0.0005461 | 0
990 | GIBN_CRE | 1 | 463 | -0.010702 | north | 0.011584 | -0.035991 | 0.0091194 | -0.017677 | 0.0091194 | west | Y | 0.011584 | 1.1411
1002 | PBCTAGE_ | A | 66 | -0.019455 | west | 0.0028309 | -0.044744 | 0.00036638 | -0.02643 | 0.00036638 | west | N | 0.00036638 | 0
1003 | PBCTBGE_ | B | 65 | -0.019455 | west | 0.0028309 | -0.044744 | 0.00036638 | -0.02643 | 0.00036638 | west | N | 0.00036638 | 0
1004 | PBCTCGE_ | C | 67 | -0.019455 | west | 0.0028309 | -0.044744 | 0.00036638 | -0.02643 | 0.00036638 | west | N | 0.00036638 | 0
1005 | PBCTDGE_ | D | 67 | -0.019455 | west | 0.0028309 | -0.044744 | 0.00036638 | -0.02643 | 0.00036638 | west | N | 0.00036638 | 0
1006 | PBCTEGE_ | E | 67 | -0.019455 | west | 0.0028309 | -0.044744 | 0.00036638 | -0.02643 | 0.00036638 | west | N | 0.00036638 | 0
1007 | PB5GEN_6 | MB | 114 | -0.019455 | west | 0.0028309 | -0.044744 | 0.00036638 | -0.02643 | 0.00036638 | west | N | 0.00036638 | 0
1008 | PB6GEN_7 | MB | 515 | -0.019455 | west | 0.0028309 | -0.044744 | 0.00036638 | -0.02643 | 0.00036638 | west | N | 0.00036638 | 0
1039 | MRGNAG_1 | A | 66 | -0.020209 | west | 0.0020769 | -0.045498 | -0.00038762 | -0.027184 | 0.00038762 | west | N | 0.00038762 | 0
1040 | MRGNBG_2 | B | 69 | -0.020209 | west | 0.0020769 | -0.045498 | -0.00038762 | -0.027184 | 0.00038762 | west | N | 0.00038762 | 0
1041 | MRGNCG_3 | C | 69 | -0.020209 | west | 0.0020769 | -0.045498 | -0.00038762 | -0.027184 | 0.00038762 | west | N | 0.00038762 | 0
1042 | MRGNDG_4 | D | 67 | -0.020209 | west | 0.0020769 | -0.045498 | -0.00038762 | -0.027184 | 0.00038762 | west | N | 0.00038762 | 0
1043 | MRGNEG_5 | E | 67 | -0.020209 | west | 0.0020769 | -0.045498 | -0.00038762 | -0.027184 | 0.00038762 | west | N | 0.00038762 | 0
1044 | MRGNFG_6 | F | 65 | -0.020209 | west | 0.0020769 | -0.045498 | -0.00038762 | -0.027184 | 0.00038762 | west | N | 0.00038762 | 0
1045 | CALENG1G | 1 | 70 | -0.020096 | west | 0.0021899 | -0.045385 | -0.00027462 | -0.027071 | 0.00027462 | west | N | 0.00027462 | 0
1046 | CALENG2G | 2 | 73.4 | -0.020096 | west | 0.0021899 | -0.045385 | -0.00027462 | -0.027071 | 0.00027462 | west | N | 0.00027462 | 0
1047 | CALENG3G | 3 | 70.4 | -0.020096 | west | 0.0021899 | -0.045385 | -0.00027462 | -0.027071 | 0.00027462 | west | N | 0.00027462 | 0
1058 | LONGSHOR | 1 | 150 | -0.020156 | west | 0.0021299 | -0.045445 | -0.00033462 | -0.027131 | 0.00033462 | west | N | 0.00033462 | 0
1058 | LONGSHOR | 2 | 220 | -0.020156 | west | 0.0021299 | -0.045445 | -0.00033462 | -0.027131 | 0.00033462 | west | N | 0.00033462 | 0
1061 | CIELOGEN | 1 | 99 | -0.020254 | west | 0.0020319 | -0.045543 | -0.00043262 | -0.027229 | 0.00043262 | west | N | 0.00043262 | 0
1062 | CIELOGEN | 1 | 61 | -0.020254 | west | 0.0020319 | -0.045543 | -0.00043262 | -0.027229 | 0.00043262 | west | N | 0.00043262 | 0
1068 | SCURRYCW | 1 | 141 | -0.020248 | west | 0.0020379 | -0.045537 | -0.00042662 | -0.027223 | 0.00042662 | west | N | 0.00042662 | 0
1069 | KINDERMG | 1 | 25 | -0.020254 | west | 0.0020319 | -0.045543 | -0.00043262 | -0.027229 | 0.00043262 | west | N | 0.00043262 | 0
1070 | KINDERMG | 1 | 45.7 | -0.020254 | west | 0.0020319 | -0.045543 | -0.00043262 | -0.027229 | 0.00043262 | west | N | 0.00043262 | 0
1071 | KINDERMG | 1 | 45.7 | -0.020254 | west | 0.0020319 | -0.045543 | -0.00043262 | -0.027229 | 0.00043262 | west | N | 0.00043262 | 0
1073 | SCURRYCW | 2 | 120 | -0.020248 | west | 0.0020379 | -0.045537 | -0.00042662 | -0.027223 | 0.00042662 | west | N | 0.00042662 | 0
1320 | BSP 1 | 1 | 25.8 | -0.019918 | west | 0.0023679 | -0.045207 | -9.6621e-05 | -0.026893 | 9.6621e-05 | west | N | 9.6621e-05 | 0
1326 | STANTONW | 1 | 100.5 | -0.01985 | west | 0.0024359 | -0.045139 | -2.8621e-05 | -0.026825 | 2.8621e-05 | west | N | 2.8621e-05 | 0
1327 | WILDHRSE | 1 | 120 | -0.020037 | west | 0.0022489 | -0.045326 | -0.00021562 | -0.027012 | 0.00021562 | west | N | 0.00021562 | 0
1328 | OCOTILLO | 1 | 58 | -0.019845 | west | 0.0024409 | -0.045134 | -2.3621e-05 | -0.02682 | 2.3621e-05 | west | N | 2.3621e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.019896 | west | 0.0023899 | -0.045185 | -7.4621e-05 | -0.026871 | 7.4621e-05 | west | N | 7.4621e-05 | 0
1343 | TRENTIPP | 1 | 150 | -0.020376 | west | 0.0019099 | -0.045665 | -0.00055462 | -0.027351 | 0.00055462 | west | N | 0.00055462 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.019646 | west | 0.0026399 | -0.044935 | 0.00017538 | -0.026621 | 0.00017538 | west | N | 0.00017538 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.019646 | west | 0.0026399 | -0.044935 | 0.00017538 | -0.026621 | 0.00017538 | west | N | 0.00017538 | 0
1354 | AEPWIND_ | 1 | 101 | -0.020376 | west | 0.0019099 | -0.045665 | -0.00055462 | -0.027351 | 0.00055462 | west | N | 0.00055462 | 0
1360 | GUNSIGHT | 1 | 120 | -0.020046 | west | 0.0022399 | -0.045335 | -0.00022462 | -0.027021 | 0.00022462 | west | N | 0.00022462 | 0
1432 | GRHAMSES | 2 | 366 | -0.02213 | north | 0.0001559 | -0.047419 | -0.0023086 | -0.029105 | 0.0001559 | North | N | 0.0001559 | 0
1433 | GRHAMSES | 1 | 242 | -0.02215 | north | 0.0001359 | -0.047439 | -0.0023286 | -0.029125 | 0.0001359 | North | N | 0.0001359 | 0
1437 | MESQUITW | 1 | 400 | -0.021175 | west | 0.0011109 | -0.046464 | -0.0013536 | -0.02815 | 0.0011109 | North | Y | 0.0013536 | 0.09709
1438 | MESQUITW | 1 | 236 | -0.021176 | west | 0.0011099 | -0.046465 | -0.0013546 | -0.028151 | 0.0011099 | North | Y | 0.0013546 | 0.057755
1442 | COKFIELD | 1 | 165 | -0.021405 | west | 0.0008809 | -0.046694 | -0.0015836 | -0.02838 | 0.0008809 | North | Y | 0.0015836 | 0.11595
1453 | WCPWRCO_ | 1 | 204 | -0.022657 | north | -0.0003711 | -0.047946 | -0.0028356 | -0.029632 | 0.0003711 | North | N | 0.0003711 | 0
1454 | WCPWRCO_ | 2 | 201 | -0.022657 | north | -0.0003711 | -0.047946 | -0.0028356 | -0.029632 | 0.0003711 | North | N | 0.0003711 | 0
1455 | WCPWRCO_ | 3 | 242 | -0.022657 | north | -0.0003711 | -0.047946 | -0.0028356 | -0.029632 | 0.0003711 | North | N | 0.0003711 | 0
1479 | WFCOGEN_ | 1 | 20 | -0.022178 | west | 0.0001079 | -0.047467 | -0.0023566 | -0.029153 | 0.0001079 | North | Y | 0.0023566 | 0.044975
1479 | WFCOGEN_ | 2 | 20 | -0.022178 | west | 0.0001079 | -0.047467 | -0.0023566 | -0.029153 | 0.0001079 | North | Y | 0.0023566 | 0.044975
1482 | WFCOGEN_ | 1 | 20 | -0.022178 | west | 0.0001079 | -0.047467 | -0.0023566 | -0.029153 | 0.0001079 | North | Y | 0.0023566 | 0.044975
1482 | WFCOGEN_ | 2 | 17 | -0.022178 | west | 0.0001079 | -0.047467 | -0.0023566 | -0.029153 | 0.0001079 | North | Y | 0.0023566 | 0.038228
1600 | BARTNWND | 1 | 120 | -0.022686 | north | -0.0004001 | -0.047975 | -0.0028646 | -0.029661 | 0.0004001 | North | N | 0.0004001 | 0
1643 | SLSTR1PP | 1 | 60 | -0.022892 | north | -0.0006061 | -0.048181 | -0.0030706 | -0.029867 | 0.0006061 | North | N | 0.0006061 | 0
1675 | PEC_1G | 1 | 75 | -0.022841 | north | -0.0005551 | -0.04813 | -0.0030196 | -0.029816 | 0.0005551 | North | N | 0.0005551 | 0
1676 | PEC_2G | 2 | 79.6 | -0.022841 | north | -0.0005551 | -0.04813 | -0.0030196 | -0.029816 | 0.0005551 | North | N | 0.0005551 | 0
1677 | PEC_3G | 3 | 88.4 | -0.022841 | north | -0.0005551 | -0.04813 | -0.0030196 | -0.029816 | 0.0005551 | North | N | 0.0005551 | 0
1678 | LAMARPWR | 1 | 160 | -0.02285 | north | -0.0005641 | -0.048139 | -0.0030286 | -0.029825 | 0.0005641 | North | N | 0.0005641 | 0
1679 | LAMARPWR | 2 | 156 | -0.02285 | north | -0.0005641 | -0.048139 | -0.0030286 | -0.029825 | 0.0005641 | North | N | 0.0005641 | 0
1680 | LAMARPWR | 3 | 196 | -0.02285 | north | -0.0005641 | -0.048139 | -0.0030286 | -0.029825 | 0.0005641 | North | N | 0.0005641 | 0
1681 | LAMARPWR | 4 | 156 | -0.02285 | north | -0.0005641 | -0.048139 | -0.0030286 | -0.029825 | 0.0005641 | North | N | 0.0005641 | 0
1682 | LAMARPWR | 5 | 157 | -0.02285 | north | -0.0005641 | -0.048139 | -0.0030286 | -0.029825 | 0.0005641 | North | N | 0.0005641 | 0
1683 | LAMARPWR | 6 | 198 | -0.02285 | north | -0.0005641 | -0.048139 | -0.0030286 | -0.029825 | 0.0005641 | North | N | 0.0005641 | 0
1687 | VALLEY_1 | 1 | 170 | -0.022872 | north | -0.0005861 | -0.048161 | -0.0030506 | -0.029847 | 0.0005861 | North | N | 0.0005861 | 0
1688 | VALLEY_2 | 2 | 520 | -0.022872 | north | -0.0005861 | -0.048161 | -0.0030506 | -0.029847 | 0.0005861 | North | N | 0.0005861 | 0
1689 | VALLEY_3 | 3 | 370 | -0.022859 | north | -0.0005731 | -0.048148 | -0.0030376 | -0.029834 | 0.0005731 | North | N | 0.0005731 | 0
1701 | MOSES_1G | 1 | 558 | -0.022835 | north | -0.0005491 | -0.048124 | -0.0030136 | -0.02981 | 0.0005491 | North | N | 0.0005491 | 0
1702 | MOSES_2G | 2 | 579 | -0.022835 | north | -0.0005491 | -0.048124 | -0.0030136 | -0.02981 | 0.0005491 | North | N | 0.0005491 | 0
1703 | MOSES_3G | 3 | 808 | -0.022835 | north | -0.0005491 | -0.048124 | -0.0030136 | -0.02981 | 0.0005491 | North | N | 0.0005491 | 0
1861 | EAGLEMNT | MB | 112 | -0.023184 | north | -0.0008981 | -0.048473 | -0.0033626 | -0.030159 | 0.0008981 | North | N | 0.0008981 | 0
1862 | EAGLEMNT | MB | 100 | -0.023184 | north | -0.0008981 | -0.048473 | -0.0033626 | -0.030159 | 0.0008981 | North | N | 0.0008981 | 0
1863 | EAGLEMNT | MB | 378 | -0.023184 | north | -0.0008981 | -0.048473 | -0.0033626 | -0.030159 | 0.0008981 | North | N | 0.0008981 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.023301 | north | -0.0010151 | -0.04859 | -0.0034796 | -0.030276 | 0.0010151 | North | N | 0.0010151 | 0
1878 | WLFHOLW_ | 2 | 205 | -0.023301 | north | -0.0010151 | -0.04859 | -0.0034796 | -0.030276 | 0.0010151 | North | N | 0.0010151 | 0
1879 | WLFHOLW_ | 3 | 272.4 | -0.023301 | north | -0.0010151 | -0.04859 | -0.0034796 | -0.030276 | 0.0010151 | North | N | 0.0010151 | 0
1889 | DECRDOVA | MB | 770 | -0.02338 | north | -0.0010941 | -0.048669 | -0.0035586 | -0.030355 | 0.0010941 | North | N | 0.0010941 | 0
1892 | DECRDOVA | A | 70 | -0.023677 | north | -0.0013911 | -0.048966 | -0.0038556 | -0.030652 | 0.0013911 | North | N | 0.0013911 | 0
1893 | DECRDOVA | B | 69 | -0.023677 | north | -0.0013911 | -0.048966 | -0.0038556 | -0.030652 | 0.0013911 | North | N | 0.0013911 | 0
1894 | DECRDOVA | C | 69 | -0.023677 | north | -0.0013911 | -0.048966 | -0.0038556 | -0.030652 | 0.0013911 | North | N | 0.0013911 | 0
1895 | DECRDOVA | D | 68 | -0.023677 | north | -0.0013911 | -0.048966 | -0.0038556 | -0.030652 | 0.0013911 | North | N | 0.0013911 | 0
1898 | COMCHEPK | 1 | 1157 | -0.023239 | north | -0.0009531 | -0.048528 | -0.0034176 | -0.030214 | 0.0009531 | North | N | 0.0009531 | 0
1899 | COMCHEPK | 2 | 1158 | -0.023239 | north | -0.0009531 | -0.048528 | -0.0034176 | -0.030214 | 0.0009531 | North | N | 0.0009531 | 0
1937 | MDLTHELP | 5 | 224 | -0.024283 | north | -0.0019971 | -0.049572 | -0.0044616 | -0.031258 | 0.0019971 | North | N | 0.0019971 | 0
1938 | MDLTHELP | 6 | 226 | -0.024283 | north | -0.0019971 | -0.049572 | -0.0044616 | -0.031258 | 0.0019971 | North | N | 0.0019971 | 0
1941 | MDLTHELP | 1 | 216.4 | -0.024247 | north | -0.0019611 | -0.049536 | -0.0044256 | -0.031222 | 0.0019611 | North | N | 0.0019611 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.024247 | north | -0.0019611 | -0.049536 | -0.0044256 | -0.031222 | 0.0019611 | North | N | 0.0019611 | 0
1943 | MDLTHELP | 3 | 212 | -0.024283 | north | -0.0019971 | -0.049572 | -0.0044616 | -0.031258 | 0.0019971 | North | N | 0.0019971 | 0
1944 | MDLTHELP | 4 | 211 | -0.024283 | north | -0.0019971 | -0.049572 | -0.0044616 | -0.031258 | 0.0019971 | North | N | 0.0019971 | 0
1947 | HANDLEY_ | 3 | 395 | -0.023531 | north | -0.0012451 | -0.04882 | -0.0037096 | -0.030506 | 0.0012451 | North | N | 0.0012451 | 0
1948 | HANDLEY_ | 4 | 435 | -0.023506 | north | -0.0012201 | -0.048795 | -0.0036846 | -0.030481 | 0.0012201 | North | N | 0.0012201 | 0
1949 | HANDLEY_ | 5 | 435 | -0.023531 | north | -0.0012451 | -0.04882 | -0.0037096 | -0.030506 | 0.0012451 | North | N | 0.0012451 | 0
2371 | COLLIN_1 | MB | 138 | -0.022949 | north | -0.0006631 | -0.048238 | -0.0031276 | -0.029924 | 0.0006631 | North | N | 0.0006631 | 0
2413 | MTCK6_G | 6 | 118 | -0.023125 | north | -0.0008391 | -0.048414 | -0.0033036 | -0.0301 | 0.0008391 | North | N | 0.0008391 | 0
2414 | MTCK7_G | 7 | 115 | -0.023125 | north | -0.0008391 | -0.048414 | -0.0033036 | -0.0301 | 0.0008391 | North | N | 0.0008391 | 0
2417 | MTCK8_G | 8 | 556 | -0.023125 | north | -0.0008391 | -0.048414 | -0.0033036 | -0.0301 | 0.0008391 | North | N | 0.0008391 | 0
2451 | LKHB1_G | 1 | 388 | -0.022841 | north | -0.0005551 | -0.04813 | -0.0030196 | -0.029816 | 0.0005551 | North | N | 0.0005551 | 0
2452 | LKHB2_G | 2 | 515 | -0.022841 | north | -0.0005551 | -0.04813 | -0.0030196 | -0.029816 | 0.0005551 | North | N | 0.0005551 | 0
3097 | MARTLAKE | 1 | 785 | -0.022219 | north | 6.6896e-05 | -0.047508 | -0.0023976 | -0.029194 | 6.6896e-05 | North | N | 6.6896e-05 | 0
3098 | MARTLAKE | 2 | 795 | -0.022219 | north | 6.6896e-05 | -0.047508 | -0.0023976 | -0.029194 | 6.6896e-05 | North | N | 6.6896e-05 | 0
3099 | MARTLAKE | 3 | 780 | -0.022219 | north | 6.6896e-05 | -0.047508 | -0.0023976 | -0.029194 | 6.6896e-05 | North | N | 6.6896e-05 | 0
3107 | STRYKER_ | 1 | 182 | -0.022121 | north | 0.0001649 | -0.04741 | -0.0022996 | -0.029096 | 0.0001649 | North | N | 0.0001649 | 0
3108 | STRYKER_ | 2 | 484 | -0.022121 | north | 0.0001649 | -0.04741 | -0.0022996 | -0.029096 | 0.0001649 | North | N | 0.0001649 | 0
3126 | TRINIDAD | 1 | 224 | -0.023169 | north | -0.0008831 | -0.048458 | -0.0033476 | -0.030144 | 0.0008831 | North | N | 0.0008831 | 0
3309 | ASPN_G | 1 | 50 | -0.022078 | north | 0.0002079 | -0.047367 | -0.0022566 | -0.029053 | 0.0002079 | North | N | 0.0002079 | 0
3348 | CHAMPION | MB | 42 | -0.022088 | north | 0.0001979 | -0.047377 | -0.0022666 | -0.029063 | 0.0001979 | North | N | 0.0001979 | 0
3381 | BBRN_1G | 1 | 615 | -0.020914 | north | 0.0013719 | -0.046203 | -0.0010926 | -0.027889 | 0.0010926 | west | Y | 0.0013719 | 0.17175
3382 | BBRN_2G | 2 | 587 | -0.020914 | north | 0.0013719 | -0.046203 | -0.0010926 | -0.027889 | 0.0010926 | west | Y | 0.0013719 | 0.16393
3403 | THOUSE_1 | MB | 537 | -0.033181 | north | -0.010895 | -0.05847 | -0.01336 | -0.040156 | 0.010895 | North | N | 0.010895 | 0
3404 | THOUSE_2 | 2 | 787 | -0.033181 | north | -0.010895 | -0.05847 | -0.01336 | -0.040156 | 0.010895 | North | N | 0.010895 | 0
3416 | LAKE_CRK | MB | 75 | -0.033067 | north | -0.010781 | -0.058356 | -0.013246 | -0.040042 | 0.010781 | North | N | 0.010781 | 0
3417 | LAKE_CRK | MB | 222 | -0.033067 | north | -0.010781 | -0.058356 | -0.013246 | -0.040042 | 0.010781 | North | N | 0.010781 | 0
3432 | SANDOW_4 | 4 | 569 | -0.12216 | south | -0.099879 | -0.14745 | -0.10234 | -0.12914 | 0.099879 | North | Y | 0.14745 | 27.0699
5026 | BRAUNIG_ | 1 | 209 | 0.032064 | south | 0.05435 | 0.0067753 | 0.051885 | 0.025089 | 0.0067753 | south | N | 0.0067753 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.032064 | south | 0.05435 | 0.0067753 | 0.051885 | 0.025089 | 0.0067753 | south | N | 0.0067753 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.031989 | south | 0.054275 | 0.0067003 | 0.05181 | 0.025014 | 0.0067003 | south | N | 0.0067003 | 0
5031 | BRA_VHBC | 1 | 46 | 0.032064 | south | 0.05435 | 0.0067753 | 0.051885 | 0.025089 | 0.0067753 | south | N | 0.0067753 | 0
5032 | BRA_VHBC | 2 | 47 | 0.032064 | south | 0.05435 | 0.0067753 | 0.051885 | 0.025089 | 0.0067753 | south | N | 0.0067753 | 0
5033 | BRA_VHBC | 3 | 46 | 0.032064 | south | 0.05435 | 0.0067753 | 0.051885 | 0.025089 | 0.0067753 | south | N | 0.0067753 | 0
5034 | BRA_VHBC | 4 | 46 | 0.032064 | south | 0.05435 | 0.0067753 | 0.051885 | 0.025089 | 0.0067753 | south | N | 0.0067753 | 0
5111 | CALAVER_ | 1 | 424 | 0.032062 | south | 0.054348 | 0.0067733 | 0.051883 | 0.025087 | 0.0067733 | south | N | 0.0067733 | 0
5112 | CALAVER_ | 2 | 425 | 0.032062 | south | 0.054348 | 0.0067733 | 0.051883 | 0.025087 | 0.0067733 | south | N | 0.0067733 | 0
5264 | LEON_LCP | 3 | 58 | 0.031832 | south | 0.054118 | 0.0065433 | 0.051653 | 0.024857 | 0.0065433 | south | N | 0.0065433 | 0
5265 | LEON_LCP | 4 | 89 | 0.031832 | south | 0.054118 | 0.0065433 | 0.051653 | 0.024857 | 0.0065433 | south | N | 0.0065433 | 0
5266 | LEON_LCP | 1 | 44 | 0.031832 | south | 0.054118 | 0.0065433 | 0.051653 | 0.024857 | 0.0065433 | south | N | 0.0065433 | 0
5267 | LEON_LCP | 2 | 44 | 0.031832 | south | 0.054118 | 0.0065433 | 0.051653 | 0.024857 | 0.0065433 | south | N | 0.0065433 | 0
5268 | LEON_LCP | 3 | 43 | 0.031832 | south | 0.054118 | 0.0065433 | 0.051653 | 0.024857 | 0.0065433 | south | N | 0.0065433 | 0
5269 | LEON_LCP | 4 | 45 | 0.031832 | south | 0.054118 | 0.0065433 | 0.051653 | 0.024857 | 0.0065433 | south | N | 0.0065433 | 0
5396 | CALAVER_ | 1 | 412 | 0.03208 | south | 0.054366 | 0.0067913 | 0.051901 | 0.025105 | 0.0067913 | south | N | 0.0067913 | 0
5397 | CALAVER_ | 2 | 400 | 0.03208 | south | 0.054366 | 0.0067913 | 0.051901 | 0.025105 | 0.0067913 | south | N | 0.0067913 | 0
5401 | CALAVER_ | 1 | 546 | 0.031755 | south | 0.054041 | 0.0064663 | 0.051576 | 0.02478 | 0.0064663 | south | N | 0.0064663 | 0
5402 | CALAVER_ | 2 | 750 | 0.031755 | south | 0.054041 | 0.0064663 | 0.051576 | 0.02478 | 0.0064663 | south | N | 0.0064663 | 0
5436 | TUTTL_WB | MB | 61 | 0.032165 | south | 0.054451 | 0.0068763 | 0.051986 | 0.02519 | 0.0068763 | south | N | 0.0068763 | 0
5438 | TUTTL_WB | MB | 95 | 0.032165 | south | 0.054451 | 0.0068763 | 0.051986 | 0.02519 | 0.0068763 | south | N | 0.0068763 | 0
5439 | TUTTL_WB | MB | 151 | 0.032165 | south | 0.054451 | 0.0068763 | 0.051986 | 0.02519 | 0.0068763 | south | N | 0.0068763 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.031901 | south | 0.054187 | 0.0066123 | 0.051722 | 0.024926 | 0.0066123 | south | N | 0.0066123 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.031901 | south | 0.054187 | 0.0066123 | 0.051722 | 0.024926 | 0.0066123 | south | N | 0.0066123 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.031901 | south | 0.054187 | 0.0066123 | 0.051722 | 0.024926 | 0.0066123 | south | N | 0.0066123 | 0
5503 | RAYBURNG | 1 | 22 | 0.026289 | south | 0.048575 | 0.0010003 | 0.04611 | 0.019314 | 0.0010003 | south | N | 0.0010003 | 0
5505 | RAYBURNG | 1 | 11 | 0.026289 | south | 0.048575 | 0.0010003 | 0.04611 | 0.019314 | 0.0010003 | south | N | 0.0010003 | 0
5506 | RAYBURNG | 1 | 11 | 0.026289 | south | 0.048575 | 0.0010003 | 0.04611 | 0.019314 | 0.0010003 | south | N | 0.0010003 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.026573 | south | 0.048859 | 0.0012843 | 0.046394 | 0.019598 | 0.0012843 | south | N | 0.0012843 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.026573 | south | 0.048859 | 0.0012843 | 0.046394 | 0.019598 | 0.0012843 | south | N | 0.0012843 | 0
5511 | RAYBURNC | 1 | 46 | 0.026573 | south | 0.048859 | 0.0012843 | 0.046394 | 0.019598 | 0.0012843 | south | N | 0.0012843 | 0
5512 | RAYBURNC | 1 | 48 | 0.026573 | south | 0.048859 | 0.0012843 | 0.046394 | 0.019598 | 0.0012843 | south | N | 0.0012843 | 0
5728 | FALCONHY | 2 | 12 | 0.027318 | south | 0.049604 | 0.0020293 | 0.047139 | 0.020343 | 0.0020293 | south | N | 0.0020293 | 0
5729 | FALCONHY | 3 | 11 | 0.027318 | south | 0.049604 | 0.0020293 | 0.047139 | 0.020343 | 0.0020293 | south | N | 0.0020293 | 0
5890 | PEARSALL | 1 | 24 | 0.028499 | south | 0.050785 | 0.0032103 | 0.04832 | 0.021524 | 0.0032103 | south | N | 0.0032103 | 0
5891 | PEARSALL | 1 | 24 | 0.028499 | south | 0.050785 | 0.0032103 | 0.04832 | 0.021524 | 0.0032103 | south | N | 0.0032103 | 0
5892 | PEARSALL | 1 | 23 | 0.028499 | south | 0.050785 | 0.0032103 | 0.04832 | 0.021524 | 0.0032103 | south | N | 0.0032103 | 0
5903 | SANMIGUE | 1 | 396 | 0.030121 | south | 0.052407 | 0.0048323 | 0.049942 | 0.023146 | 0.0048323 | south | N | 0.0048323 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.016409 | houston | 0.038695 | -0.0088797 | 0.03623 | 0.0094344 | 0.0088797 | south | Y | 0.0094344 | 0.73938
5912 | STP_GN2_ | 2 | 1328 | 0.016409 | houston | 0.038695 | -0.0088797 | 0.03623 | 0.0094344 | 0.0088797 | south | Y | 0.0094344 | 0.73661
5920 | WELSHDC1 | EQ | 600 | 0 | north | 0.022286 | -0.025289 | 0.019821 | -0.0069746 | 0.0069746 | houston | Y | 0.022286 | 9.1868
5932 | SI_RAY9 | 9 | 38 | 0.02691 | south | 0.049196 | 0.0016213 | 0.046731 | 0.019935 | 0.0016213 | south | N | 0.0016213 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.02691 | south | 0.049196 | 0.0016213 | 0.046731 | 0.019935 | 0.0016213 | south | N | 0.0016213 | 0
5934 | SI_RAY5 | 5 | 15 | 0.02691 | south | 0.049196 | 0.0016213 | 0.046731 | 0.019935 | 0.0016213 | south | N | 0.0016213 | 0
5935 | SI_RAY10 | 10 | 47 | 0.02691 | south | 0.049196 | 0.0016213 | 0.046731 | 0.019935 | 0.0016213 | south | N | 0.0016213 | 0
6016 | SWMESA | 1 | 75 | -0.017365 | west | 0.0049209 | -0.042654 | 0.0024564 | -0.02434 | 0.0024564 | west | N | 0.0024564 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | 0.022286 | -0.025289 | 0.019821 | -0.0069746 | 0.0069746 | houston | Y | 0.019821 | 2.8263
6144 | MCADOO1A | 1 | 150 | -0.020552 | west | 0.0017339 | -0.045841 | -0.00073062 | -0.027527 | 0.00073062 | west | N | 0.00073062 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.019469 | west | 0.0028169 | -0.044758 | 0.00035238 | -0.026444 | 0.00035238 | west | N | 0.00035238 | 0
6476 | LANGFORD | 1 | 150 | -0.008531 | west | 0.013755 | -0.03382 | 0.01129 | -0.015506 | 0.01129 | west | N | 0.01129 | 0
6637 | SNYDERW1 | 1 | 63 | -0.020231 | west | 0.0020549 | -0.04552 | -0.00040962 | -0.027206 | 0.00040962 | west | N | 0.00040962 | 0
6752 | OKLA0A | 1 | 649.7 | -0.021593 | west | 0.0006929 | -0.046882 | -0.0017716 | -0.028568 | 0.0006929 | North | Y | 0.0017716 | 0.70085
6948 | DENISNDM | 1 | 40 | -0.022884 | north | -0.0005981 | -0.048173 | -0.0030626 | -0.029859 | 0.0005981 | North | N | 0.0005981 | 0
6948 | DENISNDM | 2 | 40 | -0.022884 | north | -0.0005981 | -0.048173 | -0.0030626 | -0.029859 | 0.0005981 | North | N | 0.0005981 | 0
7000 | L_FERGUS | 1 | 422 | 0.031906 | south | 0.054192 | 0.0066173 | 0.051727 | 0.024931 | 0.0066173 | south | N | 0.0066173 | 0
7004 | L_SIMGID | 1 | 132 | 0.064481 | south | 0.086767 | 0.039192 | 0.084302 | 0.057506 | 0.039192 | south | N | 0.039192 | 0
7005 | L_SIMGID | 2 | 134 | 0.064481 | south | 0.086767 | 0.039192 | 0.084302 | 0.057506 | 0.039192 | south | N | 0.039192 | 0
7006 | L_SIMGID | 3 | 323 | 0.064481 | south | 0.086767 | 0.039192 | 0.084302 | 0.057506 | 0.039192 | south | N | 0.039192 | 0
7007 | L_LOSTPI | 1 | 158 | 0.039065 | south | 0.061351 | 0.013776 | 0.058886 | 0.03209 | 0.013776 | south | N | 0.013776 | 0
7008 | L_LOSTPI | 2 | 160 | 0.039065 | south | 0.061351 | 0.013776 | 0.058886 | 0.03209 | 0.013776 | south | N | 0.013776 | 0
7009 | L_LOSTPI | 3 | 175 | 0.039065 | south | 0.061351 | 0.013776 | 0.058886 | 0.03209 | 0.013776 | south | N | 0.013776 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.03682 | south | 0.059106 | 0.011531 | 0.056641 | 0.029845 | 0.011531 | south | N | 0.011531 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.03682 | south | 0.059106 | 0.011531 | 0.056641 | 0.029845 | 0.011531 | south | N | 0.011531 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.036779 | south | 0.059065 | 0.01149 | 0.0566 | 0.029804 | 0.01149 | south | N | 0.01149 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.035192 | south | 0.057478 | 0.0099033 | 0.055013 | 0.028217 | 0.0099033 | south | N | 0.0099033 | 0
7015 | L_HAYSEN | 2 | 225 | 0.035192 | south | 0.057478 | 0.0099033 | 0.055013 | 0.028217 | 0.0099033 | south | N | 0.0099033 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.035192 | south | 0.057478 | 0.0099033 | 0.055013 | 0.028217 | 0.0099033 | south | N | 0.0099033 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.035192 | south | 0.057478 | 0.0099033 | 0.055013 | 0.028217 | 0.0099033 | south | N | 0.0099033 | 0
7020 | L_AUSTPL | 1 | 8 | 0.046464 | south | 0.06875 | 0.021175 | 0.066285 | 0.039489 | 0.021175 | south | N | 0.021175 | 0
7020 | L_AUSTPL | 2 | 8 | 0.046464 | south | 0.06875 | 0.021175 | 0.066285 | 0.039489 | 0.021175 | south | N | 0.021175 | 0
7022 | L_BUCHAN | 1 | 18 | 0.027455 | south | 0.049741 | 0.0021663 | 0.047276 | 0.02048 | 0.0021663 | south | N | 0.0021663 | 0
7023 | L_BUCHAN | 2 | 18 | 0.027455 | south | 0.049741 | 0.0021663 | 0.047276 | 0.02048 | 0.0021663 | south | N | 0.0021663 | 0
7024 | L_BUCHAN | 3 | 15 | 0.027455 | south | 0.049741 | 0.0021663 | 0.047276 | 0.02048 | 0.0021663 | south | N | 0.0021663 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.028353 | south | 0.050639 | 0.0030643 | 0.048174 | 0.021378 | 0.0030643 | south | N | 0.0030643 | 0
7028 | L_MARBFA | 1 | 18 | 0.035064 | south | 0.05735 | 0.0097753 | 0.054885 | 0.028089 | 0.0097753 | south | N | 0.0097753 | 0
7029 | L_MARBFA | 2 | 18 | 0.035064 | south | 0.05735 | 0.0097753 | 0.054885 | 0.028089 | 0.0097753 | south | N | 0.0097753 | 0
7031 | L_MARSFO | 1 | 35 | 0.042227 | south | 0.064513 | 0.016938 | 0.062048 | 0.035252 | 0.016938 | south | N | 0.016938 | 0
7032 | L_MARSFO | 2 | 34 | 0.042227 | south | 0.064513 | 0.016938 | 0.062048 | 0.035252 | 0.016938 | south | N | 0.016938 | 0
7033 | L_MARSFO | 3 | 35 | 0.042227 | south | 0.064513 | 0.016938 | 0.062048 | 0.035252 | 0.016938 | south | N | 0.016938 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.032137 | south | 0.054423 | 0.0068483 | 0.051958 | 0.025162 | 0.0068483 | south | N | 0.0068483 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.032137 | south | 0.054423 | 0.0068483 | 0.051958 | 0.025162 | 0.0068483 | south | N | 0.0068483 | 0
7038 | L_DELAWA | 1 | 35 | -0.019474 | west | 0.0028119 | -0.044763 | 0.00034738 | -0.026449 | 0.00034738 | west | N | 0.00034738 | 0
7038 | L_DELAWA | 2 | 30 | -0.019474 | west | 0.0028119 | -0.044763 | 0.00034738 | -0.026449 | 0.00034738 | west | N | 0.00034738 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.049411 | south | 0.071697 | 0.024122 | 0.069232 | 0.042436 | 0.024122 | south | N | 0.024122 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.049411 | south | 0.071697 | 0.024122 | 0.069232 | 0.042436 | 0.024122 | south | N | 0.024122 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.049411 | south | 0.071697 | 0.024122 | 0.069232 | 0.042436 | 0.024122 | south | N | 0.024122 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.049411 | south | 0.071697 | 0.024122 | 0.069232 | 0.042436 | 0.024122 | south | N | 0.024122 | 0
7487 | L_CANYHY | 1 | 6 | 0.037245 | south | 0.059531 | 0.011956 | 0.057066 | 0.03027 | 0.011956 | south | N | 0.011956 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.035409 | south | 0.057695 | 0.01012 | 0.05523 | 0.028434 | 0.01012 | south | N | 0.01012 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.035409 | south | 0.057695 | 0.01012 | 0.05523 | 0.028434 | 0.01012 | south | N | 0.01012 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.035409 | south | 0.057695 | 0.01012 | 0.05523 | 0.028434 | 0.01012 | south | N | 0.01012 | 0
7609 | L_SCHUMA | 1 | 4 | 0.034003 | south | 0.056289 | 0.0087143 | 0.053824 | 0.027028 | 0.0087143 | south | N | 0.0087143 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.036677 | south | 0.058963 | 0.011388 | 0.056498 | 0.029702 | 0.011388 | south | N | 0.011388 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.036677 | south | 0.058963 | 0.011388 | 0.056498 | 0.029702 | 0.011388 | south | N | 0.011388 | 0
7800 | L_GUADGE | 1 | 147 | 0.032818 | south | 0.055104 | 0.0075293 | 0.052639 | 0.025843 | 0.0075293 | south | N | 0.0075293 | 0
7801 | L_GUADGE | 2 | 138 | 0.032818 | south | 0.055104 | 0.0075293 | 0.052639 | 0.025843 | 0.0075293 | south | N | 0.0075293 | 0
7802 | L_GUADGE | 3 | 140 | 0.032818 | south | 0.055104 | 0.0075293 | 0.052639 | 0.025843 | 0.0075293 | south | N | 0.0075293 | 0
7803 | L_GUADGE | 4 | 147 | 0.032818 | south | 0.055104 | 0.0075293 | 0.052639 | 0.025843 | 0.0075293 | south | N | 0.0075293 | 0
7804 | L_GUADGE | 5 | 182 | 0.032818 | south | 0.055104 | 0.0075293 | 0.052639 | 0.025843 | 0.0075293 | south | N | 0.0075293 | 0
7805 | L_GUADGE | 6 | 198 | 0.032818 | south | 0.055104 | 0.0075293 | 0.052639 | 0.025843 | 0.0075293 | south | N | 0.0075293 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.03983 | south | 0.062116 | 0.014541 | 0.059651 | 0.032855 | 0.014541 | south | N | 0.014541 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.03983 | south | 0.062116 | 0.014541 | 0.059651 | 0.032855 | 0.014541 | south | N | 0.014541 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.03983 | south | 0.062116 | 0.014541 | 0.059651 | 0.032855 | 0.014541 | south | N | 0.014541 | 0
7810 | L_RIONOG | 1 | 142 | 0.033998 | south | 0.056284 | 0.0087093 | 0.053819 | 0.027023 | 0.0087093 | south | N | 0.0087093 | 0
7811 | L_RIONOG | 2 | 145 | 0.033998 | south | 0.056284 | 0.0087093 | 0.053819 | 0.027023 | 0.0087093 | south | N | 0.0087093 | 0
7812 | L_RIONOG | 3 | 151 | 0.033998 | south | 0.056284 | 0.0087093 | 0.053819 | 0.027023 | 0.0087093 | south | N | 0.0087093 | 0
7813 | L_RIONOG | 4 | 290 | 0.033998 | south | 0.056284 | 0.0087093 | 0.053819 | 0.027023 | 0.0087093 | south | N | 0.0087093 | 0
8032 | AMISTADH | 1 | 33 | 0.015927 | south | 0.038213 | -0.0093617 | 0.035748 | 0.0089524 | 0.0089524 | houston | Y | 0.0093617 | 0.013508
8033 | AMISTADH | 2 | 25 | 0.015927 | south | 0.038213 | -0.0093617 | 0.035748 | 0.0089524 | 0.0089524 | houston | Y | 0.0093617 | 0.010233
8048 | FALCONHY | 1 | 12 | 0.027318 | south | 0.049604 | 0.0020293 | 0.047139 | 0.020343 | 0.0020293 | south | N | 0.0020293 | 0
8066 | DUP1V#1 | 1 | 73 | 0.026749 | south | 0.049035 | 0.0014603 | 0.04657 | 0.019774 | 0.0014603 | south | N | 0.0014603 | 0
8134 | FOR69CG0 | 1 | 79 | 0.024888 | south | 0.047174 | -0.00040069 | 0.044709 | 0.017913 | 0.00040069 | south | N | 0.00040069 | 0
8138 | FOR69CG0 | 2 | 81 | 0.024888 | south | 0.047174 | -0.00040069 | 0.044709 | 0.017913 | 0.00040069 | south | N | 0.00040069 | 0
8139 | JOS #1 | MB | 255 | 0 | south | 0.022286 | -0.025289 | 0.019821 | -0.0069746 | 0.0069746 | houston | Y | 0.025289 | 4.6701
8147 | UCAR #2 | 10 | 28 | 0.025826 | south | 0.048112 | 0.00053731 | 0.045647 | 0.018851 | 0.00053731 | south | N | 0.00053731 | 0
8148 | UCAR #1 | 2 | 7 | 0.025826 | south | 0.048112 | 0.00053731 | 0.045647 | 0.018851 | 0.00053731 | south | N | 0.00053731 | 0
8153 | FOR69CG0 | 3 | 79 | 0.024888 | south | 0.047174 | -0.00040069 | 0.044709 | 0.017913 | 0.00040069 | south | N | 0.00040069 | 0
8154 | FOR69CG0 | 4 | 80 | 0.024888 | south | 0.047174 | -0.00040069 | 0.044709 | 0.017913 | 0.00040069 | south | N | 0.00040069 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.024888 | south | 0.047174 | -0.00040069 | 0.044709 | 0.017913 | 0.00040069 | south | N | 0.00040069 | 0
8156 | FOR69CG0 | 6 | 25 | 0.024888 | south | 0.047174 | -0.00040069 | 0.044709 | 0.017913 | 0.00040069 | south | N | 0.00040069 | 0
8157 | FOR69CG0 | 7 | 46 | 0.024888 | south | 0.047174 | -0.00040069 | 0.044709 | 0.017913 | 0.00040069 | south | N | 0.00040069 | 0
8161 | COLETOU1 | 1 | 629 | 0.028015 | south | 0.050301 | 0.0027263 | 0.047836 | 0.02104 | 0.0027263 | south | N | 0.0027263 | 0
8173 | VICEC51A | 5 | 144 | 0.027079 | south | 0.049365 | 0.0017903 | 0.0469 | 0.020104 | 0.0017903 | south | N | 0.0017903 | 0
8174 | VICEC61A | 6 | 188 | 0.027079 | south | 0.049365 | 0.0017903 | 0.0469 | 0.020104 | 0.0017903 | south | N | 0.0017903 | 0
8189 | CUERO 2 | 1 | 12 | 0.034605 | south | 0.056891 | 0.0093163 | 0.054426 | 0.02763 | 0.0093163 | south | N | 0.0093163 | 0
8262 | ELPS | 1 | 6 | 0.019834 | south | 0.04212 | -0.0054547 | 0.039655 | 0.012859 | 0.0054547 | south | N | 0.0054547 | 0
8285 | LAR #1 | MB | 32 | 0 | south | 0.022286 | -0.025289 | 0.019821 | -0.0069746 | 0.0069746 | houston | Y | 0.025289 | 0.58605
8287 | LAR #2 | MB | 32 | 0 | south | 0.022286 | -0.025289 | 0.019821 | -0.0069746 | 0.0069746 | houston | Y | 0.025289 | 0.58605
8288 | LAR #3 | MB | 105 | 0 | south | 0.022286 | -0.025289 | 0.019821 | -0.0069746 | 0.0069746 | houston | Y | 0.025289 | 1.923
8388 | BATES0A | MB | 70 | 0 | south | 0.022286 | -0.025289 | 0.019821 | -0.0069746 | 0.0069746 | houston | Y | 0.025289 | 1.282
8393 | BATES0B | MB | 110 | 0 | south | 0.022286 | -0.025289 | 0.019821 | -0.0069746 | 0.0069746 | houston | Y | 0.025289 | 2.0145
8442 | NBEC71A | 1 | 336 | 0.026657 | south | 0.048943 | 0.0013683 | 0.046478 | 0.019682 | 0.0013683 | south | N | 0.0013683 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | 0.022286 | -0.025289 | 0.019821 | -0.0069746 | 0.0069746 | houston | Y | 0.025289 | 0.36628
8457 | COSW#2 | 2 | 14 | 0 | south | 0.022286 | -0.025289 | 0.019821 | -0.0069746 | 0.0069746 | houston | Y | 0.025289 | 0.2564
8459 | B_DAVIS1 | 1 | 334 | 0.026712 | south | 0.048998 | 0.0014233 | 0.046533 | 0.019737 | 0.0014233 | south | N | 0.0014233 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.026712 | south | 0.048998 | 0.0014233 | 0.046533 | 0.019737 | 0.0014233 | south | N | 0.0014233 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.026763 | south | 0.049049 | 0.0014743 | 0.046584 | 0.019788 | 0.0014743 | south | N | 0.0014743 | 0
8506 | VAL #1 | 1 | 25 | 0.026732 | south | 0.049018 | 0.0014433 | 0.046553 | 0.019757 | 0.0014433 | south | N | 0.0014433 | 0
8507 | VAL #2 | 2 | 25 | 0.026732 | south | 0.049018 | 0.0014433 | 0.046553 | 0.019757 | 0.0014433 | south | N | 0.0014433 | 0
8511 | OXY_CC0A | 1 | 38 | 0.026751 | south | 0.049037 | 0.0014623 | 0.046572 | 0.019776 | 0.0014623 | south | N | 0.0014623 | 0
8517 | CELANEBI | 1 | 29 | 0.026861 | south | 0.049147 | 0.0015723 | 0.046682 | 0.019886 | 0.0015723 | south | N | 0.0015723 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.02666 | south | 0.048946 | 0.0013713 | 0.046481 | 0.019685 | 0.0013713 | south | N | 0.0013713 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.02666 | south | 0.048946 | 0.0013713 | 0.046481 | 0.019685 | 0.0013713 | south | N | 0.0013713 | 0
8562 | CNOPST1 | 3 | 153 | 0.02666 | south | 0.048946 | 0.0013713 | 0.046481 | 0.019685 | 0.0013713 | south | N | 0.0013713 | 0
8926 | LGE_GT10 | 1 | 158 | 0.026397 | south | 0.048683 | 0.0011083 | 0.046218 | 0.019422 | 0.0011083 | south | N | 0.0011083 | 0
8927 | LGE_GT20 | 2 | 153 | 0.026397 | south | 0.048683 | 0.0011083 | 0.046218 | 0.019422 | 0.0011083 | south | N | 0.0011083 | 0
8928 | LGE_STG0 | 3 | 100 | 0.026397 | south | 0.048683 | 0.0011083 | 0.046218 | 0.019422 | 0.0011083 | south | N | 0.0011083 | 0
8930 | ICPGN10A | 1 | 145 | 0.026397 | south | 0.048683 | 0.0011083 | 0.046218 | 0.019422 | 0.0011083 | south | N | 0.0011083 | 0
8931 | ICPGN20A | 2 | 147 | 0.026397 | south | 0.048683 | 0.0011083 | 0.046218 | 0.019422 | 0.0011083 | south | N | 0.0011083 | 0
8932 | ICPGN30A | 3 | 127 | 0.026397 | south | 0.048683 | 0.0011083 | 0.046218 | 0.019422 | 0.0011083 | south | N | 0.0011083 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.027008 | south | 0.049294 | 0.0017193 | 0.046829 | 0.020033 | 0.0017193 | south | N | 0.0017193 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.027008 | south | 0.049294 | 0.0017193 | 0.046829 | 0.020033 | 0.0017193 | south | N | 0.0017193 | 0
8935 | FGNTS201 | 3 | 173 | 0.027008 | south | 0.049294 | 0.0017193 | 0.046829 | 0.020033 | 0.0017193 | south | N | 0.0017193 | 0
8936 | MVGN#1 | 1 | 207 | 0.026959 | south | 0.049245 | 0.0016703 | 0.04678 | 0.019984 | 0.0016703 | south | N | 0.0016703 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.026959 | south | 0.049245 | 0.0016703 | 0.04678 | 0.019984 | 0.0016703 | south | N | 0.0016703 | 0
8938 | MVGN#3 | 3 | 242 | 0.026959 | south | 0.049245 | 0.0016703 | 0.04678 | 0.019984 | 0.0016703 | south | N | 0.0016703 | 0
8981 | HECN1 | 1 | 144 | 0.026958 | south | 0.049244 | 0.0016693 | 0.046779 | 0.019983 | 0.0016693 | south | N | 0.0016693 | 0
8982 | HECN2 | 2 | 144 | 0.026958 | south | 0.049244 | 0.0016693 | 0.046779 | 0.019983 | 0.0016693 | south | N | 0.0016693 | 0
8983 | HECN3 | 3 | 171 | 0.026958 | south | 0.049244 | 0.0016693 | 0.046779 | 0.019983 | 0.0016693 | south | N | 0.0016693 | 0
9000 | DECKR_G1 | 1 | 310 | 0.046657 | south | 0.068943 | 0.021368 | 0.066478 | 0.039682 | 0.021368 | south | N | 0.021368 | 0
9001 | DECKR_G2 | 2 | 413 | 0.046657 | south | 0.068943 | 0.021368 | 0.066478 | 0.039682 | 0.021368 | south | N | 0.021368 | 0
9002 | DECKR_G3 | 3 | 42 | 0.04825 | south | 0.070536 | 0.022961 | 0.068071 | 0.041275 | 0.022961 | south | N | 0.022961 | 0
9003 | DECKR_G4 | 4 | 44 | 0.04825 | south | 0.070536 | 0.022961 | 0.068071 | 0.041275 | 0.022961 | south | N | 0.022961 | 0
9004 | DECKR_G5 | 5 | 44 | 0.04825 | south | 0.070536 | 0.022961 | 0.068071 | 0.041275 | 0.022961 | south | N | 0.022961 | 0
9005 | DECKR_G6 | 6 | 47 | 0.04825 | south | 0.070536 | 0.022961 | 0.068071 | 0.041275 | 0.022961 | south | N | 0.022961 | 0
9016 | SANDH_G1 | 1 | 49 | 0.04542 | south | 0.067706 | 0.020131 | 0.065241 | 0.038445 | 0.020131 | south | N | 0.020131 | 0
9017 | SANDH_G2 | 2 | 46 | 0.04542 | south | 0.067706 | 0.020131 | 0.065241 | 0.038445 | 0.020131 | south | N | 0.020131 | 0
9018 | SANDH_G3 | 3 | 46 | 0.04542 | south | 0.067706 | 0.020131 | 0.065241 | 0.038445 | 0.020131 | south | N | 0.020131 | 0
9019 | SANDH_G4 | 4 | 47 | 0.04542 | south | 0.067706 | 0.020131 | 0.065241 | 0.038445 | 0.020131 | south | N | 0.020131 | 0
9020 | SANDHG5A | 5A | 154 | 0.04542 | south | 0.067706 | 0.020131 | 0.065241 | 0.038445 | 0.020131 | south | N | 0.020131 | 0
9021 | SANDHG5C | 5C | 148 | 0.04542 | south | 0.067706 | 0.020131 | 0.065241 | 0.038445 | 0.020131 | south | N | 0.020131 | 0
9022 | SANDH_G6 | 6 | 48 | 0.04542 | south | 0.067706 | 0.020131 | 0.065241 | 0.038445 | 0.020131 | south | N | 0.020131 | 0
9023 | SANDH_G7 | 7 | 48 | 0.04542 | south | 0.067706 | 0.020131 | 0.065241 | 0.038445 | 0.020131 | south | N | 0.020131 | 0
11001 | NAV1CT | 1 | 70 | -0.01983 | west | 0.0024559 | -0.045119 | -8.6214e-06 | -0.026805 | 8.6214e-06 | west | N | 8.6214e-06 | 0
11009 | NAV2CT | 1 | 70 | -0.01983 | west | 0.0024559 | -0.045119 | -8.6214e-06 | -0.026805 | 8.6214e-06 | west | N | 8.6214e-06 | 0
11011 | NAV3ST | 1 | 92.8 | -0.01983 | west | 0.0024559 | -0.045119 | -8.6214e-06 | -0.026805 | 8.6214e-06 | west | N | 8.6214e-06 | 0
11012 | NAV4CT | 1 | 80 | -0.01983 | west | 0.0024559 | -0.045119 | -8.6214e-06 | -0.026805 | 8.6214e-06 | west | N | 8.6214e-06 | 0
11013 | NAV5CT | 1 | 80 | -0.01983 | west | 0.0024559 | -0.045119 | -8.6214e-06 | -0.026805 | 8.6214e-06 | west | N | 8.6214e-06 | 0
11014 | NAV6ST | 1 | 115 | -0.01983 | west | 0.0024559 | -0.045119 | -8.6214e-06 | -0.026805 | 8.6214e-06 | west | N | 8.6214e-06 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.019826 | west | 0.0024599 | -0.045115 | -4.6214e-06 | -0.026801 | 4.6214e-06 | west | N | 4.6214e-06 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.019826 | west | 0.0024599 | -0.045115 | -4.6214e-06 | -0.026801 | 4.6214e-06 | west | N | 4.6214e-06 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.019826 | west | 0.0024599 | -0.045115 | -4.6214e-06 | -0.026801 | 4.6214e-06 | west | N | 4.6214e-06 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.019826 | west | 0.0024599 | -0.045115 | -4.6214e-06 | -0.026801 | 4.6214e-06 | west | N | 4.6214e-06 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.019826 | west | 0.0024599 | -0.045115 | -4.6214e-06 | -0.026801 | 4.6214e-06 | west | N | 4.6214e-06 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.019826 | west | 0.0024599 | -0.045115 | -4.6214e-06 | -0.026801 | 4.6214e-06 | west | N | 4.6214e-06 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.020489 | west | 0.0017969 | -0.045778 | -0.00066762 | -0.027464 | 0.00066762 | west | N | 0.00066762 | 0
11057 | CHAMPION | 1 | 126.5 | -0.020489 | west | 0.0017969 | -0.045778 | -0.00066762 | -0.027464 | 0.00066762 | west | N | 0.00066762 | 0
11058 | PYRON_1G | 1 | 249 | -0.020489 | west | 0.0017969 | -0.045778 | -0.00066762 | -0.027464 | 0.00066762 | west | N | 0.00066762 | 0
11059 | INADALE_ | 1 | 197 | -0.020489 | west | 0.0017969 | -0.045778 | -0.00066762 | -0.027464 | 0.00066762 | west | N | 0.00066762 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.020156 | west | 0.0021299 | -0.045445 | -0.00033462 | -0.027131 | 0.00033462 | west | N | 0.00033462 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.020156 | west | 0.0021299 | -0.045445 | -0.00033462 | -0.027131 | 0.00033462 | west | N | 0.00033462 | 0
11147 | NOTREES_ | 1 | 149 | -0.019538 | west | 0.0027479 | -0.044827 | 0.00028338 | -0.026513 | 0.00028338 | west | N | 0.00028338 | 0
11309 | BULLCREK | 1 | 180 | -0.020105 | west | 0.0021809 | -0.045394 | -0.00028362 | -0.02708 | 0.00028362 | west | N | 0.00028362 | 0
11310 | BULLCREK | 1 | 180 | -0.020105 | west | 0.0021809 | -0.045394 | -0.00028362 | -0.02708 | 0.00028362 | west | N | 0.00028362 | 0
11320 | COYOTE_1 | 1 | 225 | -0.020085 | west | 0.0022009 | -0.045374 | -0.00026362 | -0.02706 | 0.00026362 | west | N | 0.00026362 | 0
11415 | LORAINE_ | 1 | 125 | -0.020353 | west | 0.0019329 | -0.045642 | -0.00053162 | -0.027328 | 0.00053162 | west | N | 0.00053162 | 0
11416 | LORAINE_ | 1 | 125 | -0.020353 | west | 0.0019329 | -0.045642 | -0.00053162 | -0.027328 | 0.00053162 | west | N | 0.00053162 | 0
11691 | KMICHICT | 1 | 140 | -0.022859 | north | -0.0005731 | -0.048148 | -0.0030376 | -0.029834 | 0.0005731 | North | N | 0.0005731 | 0
11692 | KMICHICT | 2 | 141 | -0.022859 | north | -0.0005731 | -0.048148 | -0.0030376 | -0.029834 | 0.0005731 | North | N | 0.0005731 | 0
11693 | KMICHIST | 3 | 309 | -0.022859 | north | -0.0005731 | -0.048148 | -0.0030376 | -0.029834 | 0.0005731 | North | N | 0.0005731 | 0
11694 | KMICHICT | 4 | 143 | -0.022859 | north | -0.0005731 | -0.048148 | -0.0030376 | -0.029834 | 0.0005731 | North | N | 0.0005731 | 0
11695 | KMICHICT | 5 | 144 | -0.022859 | north | -0.0005731 | -0.048148 | -0.0030376 | -0.029834 | 0.0005731 | North | N | 0.0005731 | 0
11696 | KMICHIST | 6 | 310 | -0.022859 | north | -0.0005731 | -0.048148 | -0.0030376 | -0.029834 | 0.0005731 | North | N | 0.0005731 | 0
12322 | ENNSTRAC | 1 | 196 | -0.023589 | north | -0.0013031 | -0.048878 | -0.0037676 | -0.030564 | 0.0013031 | North | N | 0.0013031 | 0
12323 | ENNSTRAC | 2 | 111 | -0.023589 | north | -0.0013031 | -0.048878 | -0.0037676 | -0.030564 | 0.0013031 | North | N | 0.0013031 | 0
12357 | RNRTPL_1 | 1 | 0 | -0.022961 | north | -0.0006751 | -0.04825 | -0.0031396 | -0.029936 | 0.0006751 | North | N | 0.0006751 | 0
12411 | FPLEFR1A | 1 | 161 | -0.022709 | north | -0.0004231 | -0.047998 | -0.0028876 | -0.029684 | 0.0004231 | North | N | 0.0004231 | 0
12412 | FPLEFR1B | 2 | 164 | -0.022709 | north | -0.0004231 | -0.047998 | -0.0028876 | -0.029684 | 0.0004231 | North | N | 0.0004231 | 0
12413 | FPLEFR1C | 3 | 164 | -0.022709 | north | -0.0004231 | -0.047998 | -0.0028876 | -0.029684 | 0.0004231 | North | N | 0.0004231 | 0
12414 | FPLEFR1S | 4 | 414 | -0.022709 | north | -0.0004231 | -0.047998 | -0.0028876 | -0.029684 | 0.0004231 | North | N | 0.0004231 | 0
12421 | FPLEFR2A | 1 | 162 | -0.022709 | north | -0.0004231 | -0.047998 | -0.0028876 | -0.029684 | 0.0004231 | North | N | 0.0004231 | 0
12422 | FPLEFR2B | 2 | 161 | -0.022709 | north | -0.0004231 | -0.047998 | -0.0028876 | -0.029684 | 0.0004231 | North | N | 0.0004231 | 0
12423 | FPLEFR2C | 3 | 163 | -0.022709 | north | -0.0004231 | -0.047998 | -0.0028876 | -0.029684 | 0.0004231 | North | N | 0.0004231 | 0
12424 | FPLEFR2S | 4 | 409 | -0.022709 | north | -0.0004231 | -0.047998 | -0.0028876 | -0.029684 | 0.0004231 | North | N | 0.0004231 | 0
12440 | PARKD_1S | 1 | 0 | -0.022894 | north | -0.0006081 | -0.048183 | -0.0030726 | -0.029869 | 0.0006081 | North | N | 0.0006081 | 0
12449 | PARKD_2S | 1 | 0 | -0.022894 | north | -0.0006081 | -0.048183 | -0.0030726 | -0.029869 | 0.0006081 | North | N | 0.0006081 | 0
13116 | TGATEWAY | 1 | 148 | -0.022137 | north | 0.0001489 | -0.047426 | -0.0023156 | -0.029112 | 0.0001489 | North | N | 0.0001489 | 0
13117 | TGATEWAY | 2 | 130 | -0.022137 | north | 0.0001489 | -0.047426 | -0.0023156 | -0.029112 | 0.0001489 | North | N | 0.0001489 | 0
13118 | TGATEWAY | 3 | 145 | -0.022137 | north | 0.0001489 | -0.047426 | -0.0023156 | -0.029112 | 0.0001489 | North | N | 0.0001489 | 0
13119 | TGATEWAY | 4 | 399 | -0.022137 | north | 0.0001489 | -0.047426 | -0.0023156 | -0.029112 | 0.0001489 | North | N | 0.0001489 | 0
13131 | CALFREST | 1 | 150.7 | -0.021119 | north | 0.0011669 | -0.046408 | -0.0012976 | -0.028094 | 0.0011669 | North | N | 0.0011669 | 0
13132 | CALFREST | 2 | 151 | -0.021119 | north | 0.0011669 | -0.046408 | -0.0012976 | -0.028094 | 0.0011669 | North | N | 0.0011669 | 0
13133 | CALFREST | 3 | 177.4 | -0.021119 | north | 0.0011669 | -0.046408 | -0.0012976 | -0.028094 | 0.0011669 | North | N | 0.0011669 | 0
13134 | CALFREST | 4 | 151.5 | -0.021161 | north | 0.0011249 | -0.04645 | -0.0013396 | -0.028136 | 0.0011249 | North | N | 0.0011249 | 0
13135 | CALFREST | 5 | 152.3 | -0.021161 | north | 0.0011249 | -0.04645 | -0.0013396 | -0.028136 | 0.0011249 | North | N | 0.0011249 | 0
13136 | CALFREST | 6 | 177.5 | -0.021161 | north | 0.0011249 | -0.04645 | -0.0013396 | -0.028136 | 0.0011249 | North | N | 0.0011249 | 0
13432 | SANDOW_5 | 5 | 581 | -0.12216 | south | -0.099879 | -0.14745 | -0.10234 | -0.12914 | 0.099879 | North | Y | 0.14745 | 27.6408
13691 | OAKGROVE | 1 | 855 | -0.016172 | north | 0.0061139 | -0.041461 | 0.0036494 | -0.023147 | 0.0036494 | west | Y | 0.0061139 | 2.1072
13692 | OAKGROVE | 2 | 855 | -0.016172 | north | 0.0061139 | -0.041461 | 0.0036494 | -0.023147 | 0.0036494 | west | Y | 0.0061139 | 2.1072
32798 | BRYN_TAM | 1 | 32 | -0.017029 | north | 0.0052569 | -0.042318 | 0.0027924 | -0.024004 | 0.0027924 | west | Y | 0.0052569 | 0.078865
32883 | BRYN_DNS | 1 | 48 | -0.019306 | north | 0.0029799 | -0.044595 | 0.00051538 | -0.026281 | 0.00051538 | west | Y | 0.0029799 | 0.1183
32884 | BRYN_DNS | 1 | 46 | -0.019306 | north | 0.0029799 | -0.044595 | 0.00051538 | -0.026281 | 0.00051538 | west | Y | 0.0029799 | 0.11337
32886 | BRYN_ATK | MB | 12 | -0.017178 | north | 0.0051079 | -0.042467 | 0.0026434 | -0.024153 | 0.0026434 | west | Y | 0.0051079 | 0.029574
32887 | BRYN_ATK | MB | 51 | -0.017178 | north | 0.0051079 | -0.042467 | 0.0026434 | -0.024153 | 0.0026434 | west | Y | 0.0051079 | 0.12569
32888 | BRYN_ATK | 1 | 17 | -0.017178 | north | 0.0051079 | -0.042467 | 0.0026434 | -0.024153 | 0.0026434 | west | Y | 0.0051079 | 0.041897
32890 | BRYN_ATK | MB | 22 | -0.017178 | north | 0.0051079 | -0.042467 | 0.0026434 | -0.024153 | 0.0026434 | west | Y | 0.0051079 | 0.054219
32891 | BRYN_ATK | MB | 25 | -0.017178 | north | 0.0051079 | -0.042467 | 0.0026434 | -0.024153 | 0.0026434 | west | Y | 0.0051079 | 0.061613
32892 | BRYN_DNS | 1 | 105 | -0.019306 | north | 0.0029799 | -0.044595 | 0.00051538 | -0.026281 | 0.00051538 | west | Y | 0.0029799 | 0.25877
36998 | RDCNYNG1 | 1 | 84 | -0.020309 | west | 0.0019769 | -0.045598 | -0.00048762 | -0.027284 | 0.00048762 | west | N | 0.00048762 | 0
38332 | WDWRDU2 | 1 | 80 | -0.017328 | west | 0.0049579 | -0.042617 | 0.0024934 | -0.024303 | 0.0024934 | west | N | 0.0024934 | 0
38437 | TNSRBNMS | 1 | 150 | -0.017308 | west | 0.0049779 | -0.042597 | 0.0025134 | -0.024283 | 0.0025134 | west | N | 0.0025134 | 0
38438 | TNSRBNMS | 1 | 150 | -0.017308 | west | 0.0049779 | -0.042597 | 0.0025134 | -0.024283 | 0.0025134 | west | N | 0.0025134 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.007323 | houston | 0.029609 | -0.017966 | 0.027144 | 0.00034837 | 0.00034837 | houston | N | 0.00034837 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.007323 | houston | 0.029609 | -0.017966 | 0.027144 | 0.00034837 | 0.00034837 | houston | N | 0.00034837 | 0
38600 | TNBP_CGN | 5 | 53 | 0.007323 | houston | 0.029609 | -0.017966 | 0.027144 | 0.00034837 | 0.00034837 | houston | N | 0.00034837 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.007323 | houston | 0.029609 | -0.017966 | 0.027144 | 0.00034837 | 0.00034837 | houston | N | 0.00034837 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.007323 | houston | 0.029609 | -0.017966 | 0.027144 | 0.00034837 | 0.00034837 | houston | N | 0.00034837 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.007323 | houston | 0.029609 | -0.017966 | 0.027144 | 0.00034837 | 0.00034837 | houston | N | 0.00034837 | 0
38614 | TNBPAMCG | 4 | 96 | 0.007323 | houston | 0.029609 | -0.017966 | 0.027144 | 0.00034837 | 0.00034837 | houston | N | 0.00034837 | 0
38615 | TNBPAMCG | 1 | 244 | 0.007323 | houston | 0.029609 | -0.017966 | 0.027144 | 0.00034837 | 0.00034837 | houston | N | 0.00034837 | 0
38690 | TNBP_CGN | 3 | 40 | 0.007323 | houston | 0.029609 | -0.017966 | 0.027144 | 0.00034837 | 0.00034837 | houston | N | 0.00034837 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.007329 | houston | 0.029615 | -0.01796 | 0.02715 | 0.00035437 | 0.00035437 | houston | N | 0.00035437 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.007329 | houston | 0.029615 | -0.01796 | 0.02715 | 0.00035437 | 0.00035437 | houston | N | 0.00035437 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.007329 | houston | 0.029615 | -0.01796 | 0.02715 | 0.00035437 | 0.00035437 | houston | N | 0.00035437 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.007329 | houston | 0.029615 | -0.01796 | 0.02715 | 0.00035437 | 0.00035437 | houston | N | 0.00035437 | 0
39470 | TNDOWCGN | 1 | 32 | 0.007328 | houston | 0.029614 | -0.017961 | 0.027149 | 0.00035337 | 0.00035337 | houston | N | 0.00035337 | 0
39480 | TNDOWCGN | 1 | 30 | 0.007328 | houston | 0.029614 | -0.017961 | 0.027149 | 0.00035337 | 0.00035337 | houston | N | 0.00035337 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.011105 | houston | 0.033391 | -0.014184 | 0.030926 | 0.0041304 | 0.0041304 | houston | N | 0.0041304 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.011105 | houston | 0.033391 | -0.014184 | 0.030926 | 0.0041304 | 0.0041304 | houston | N | 0.0041304 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.011105 | houston | 0.033391 | -0.014184 | 0.030926 | 0.0041304 | 0.0041304 | houston | N | 0.0041304 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.011105 | houston | 0.033391 | -0.014184 | 0.030926 | 0.0041304 | 0.0041304 | houston | N | 0.0041304 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.016172 | north | 0.0061139 | -0.041461 | 0.0036494 | -0.023147 | 0.0036494 | west | Y | 0.0061139 | 0.37535
39970 | TNTNPONE | 1 | 153 | -0.016172 | north | 0.0061139 | -0.041461 | 0.0036494 | -0.023147 | 0.0036494 | west | Y | 0.0061139 | 0.37707
48500 | APD_GT1_ | 1 | 136 | 0.005092 | houston | 0.027378 | -0.020197 | 0.024913 | -0.0018826 | 0.0018826 | houston | N | 0.0018826 | 0
48510 | AK_GT1__ | 1 | 33 | 0.008579 | houston | 0.030865 | -0.01671 | 0.0284 | 0.0016044 | 0.0016044 | houston | N | 0.0016044 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.005074 | houston | 0.02736 | -0.020215 | 0.024895 | -0.0019006 | 0.0019006 | houston | N | 0.0019006 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.005074 | houston | 0.02736 | -0.020215 | 0.024895 | -0.0019006 | 0.0019006 | houston | N | 0.0019006 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.005074 | houston | 0.02736 | -0.020215 | 0.024895 | -0.0019006 | 0.0019006 | houston | N | 0.0019006 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.005074 | houston | 0.02736 | -0.020215 | 0.024895 | -0.0019006 | 0.0019006 | houston | N | 0.0019006 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.011621 | houston | 0.033907 | -0.013668 | 0.031442 | 0.0046464 | 0.0046464 | houston | N | 0.0046464 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.011621 | houston | 0.033907 | -0.013668 | 0.031442 | 0.0046464 | 0.0046464 | houston | N | 0.0046464 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.008765 | houston | 0.031051 | -0.016524 | 0.028586 | 0.0017904 | 0.0017904 | houston | N | 0.0017904 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.008765 | houston | 0.031051 | -0.016524 | 0.028586 | 0.0017904 | 0.0017904 | houston | N | 0.0017904 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.008765 | houston | 0.031051 | -0.016524 | 0.028586 | 0.0017904 | 0.0017904 | houston | N | 0.0017904 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.005923 | houston | 0.028209 | -0.019366 | 0.025744 | -0.0010516 | 0.0010516 | houston | N | 0.0010516 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.005923 | houston | 0.028209 | -0.019366 | 0.025744 | -0.0010516 | 0.0010516 | houston | N | 0.0010516 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.005923 | houston | 0.028209 | -0.019366 | 0.025744 | -0.0010516 | 0.0010516 | houston | N | 0.0010516 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.005923 | houston | 0.028209 | -0.019366 | 0.025744 | -0.0010516 | 0.0010516 | houston | N | 0.0010516 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.00538 | houston | 0.027666 | -0.019909 | 0.025201 | -0.0015946 | 0.0015946 | houston | N | 0.0015946 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.00538 | houston | 0.027666 | -0.019909 | 0.025201 | -0.0015946 | 0.0015946 | houston | N | 0.0015946 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.006088 | houston | 0.028374 | -0.019201 | 0.025909 | -0.00088663 | 0.00088663 | houston | N | 0.00088663 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.006088 | houston | 0.028374 | -0.019201 | 0.025909 | -0.00088663 | 0.00088663 | houston | N | 0.00088663 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.006088 | houston | 0.028374 | -0.019201 | 0.025909 | -0.00088663 | 0.00088663 | houston | N | 0.00088663 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.006088 | houston | 0.028374 | -0.019201 | 0.025909 | -0.00088663 | 0.00088663 | houston | N | 0.00088663 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.006088 | houston | 0.028374 | -0.019201 | 0.025909 | -0.00088663 | 0.00088663 | houston | N | 0.00088663 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.004387 | houston | 0.026673 | -0.020902 | 0.024208 | -0.0025876 | 0.0025876 | houston | N | 0.0025876 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.004666 | houston | 0.026952 | -0.020623 | 0.024487 | -0.0023086 | 0.0023086 | houston | N | 0.0023086 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.004302 | houston | 0.026588 | -0.020987 | 0.024123 | -0.0026726 | 0.0026726 | houston | N | 0.0026726 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.004302 | houston | 0.026588 | -0.020987 | 0.024123 | -0.0026726 | 0.0026726 | houston | N | 0.0026726 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.004302 | houston | 0.026588 | -0.020987 | 0.024123 | -0.0026726 | 0.0026726 | houston | N | 0.0026726 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.00276 | houston | 0.025046 | -0.022529 | 0.022581 | -0.0042146 | 0.0042146 | houston | N | 0.0042146 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.005036 | houston | 0.027322 | -0.020253 | 0.024857 | -0.0019386 | 0.0019386 | houston | N | 0.0019386 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.005036 | houston | 0.027322 | -0.020253 | 0.024857 | -0.0019386 | 0.0019386 | houston | N | 0.0019386 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.004105 | houston | 0.026391 | -0.021184 | 0.023926 | -0.0028696 | 0.0028696 | houston | N | 0.0028696 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.004105 | houston | 0.026391 | -0.021184 | 0.023926 | -0.0028696 | 0.0028696 | houston | N | 0.0028696 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.004105 | houston | 0.026391 | -0.021184 | 0.023926 | -0.0028696 | 0.0028696 | houston | N | 0.0028696 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.004105 | houston | 0.026391 | -0.021184 | 0.023926 | -0.0028696 | 0.0028696 | houston | N | 0.0028696 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.005361 | houston | 0.027647 | -0.019928 | 0.025182 | -0.0016136 | 0.0016136 | houston | N | 0.0016136 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.005361 | houston | 0.027647 | -0.019928 | 0.025182 | -0.0016136 | 0.0016136 | houston | N | 0.0016136 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.005361 | houston | 0.027647 | -0.019928 | 0.025182 | -0.0016136 | 0.0016136 | houston | N | 0.0016136 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.005361 | houston | 0.027647 | -0.019928 | 0.025182 | -0.0016136 | 0.0016136 | houston | N | 0.0016136 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.005528 | houston | 0.027814 | -0.019761 | 0.025349 | -0.0014466 | 0.0014466 | houston | N | 0.0014466 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.005528 | houston | 0.027814 | -0.019761 | 0.025349 | -0.0014466 | 0.0014466 | houston | N | 0.0014466 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.005528 | houston | 0.027814 | -0.019761 | 0.025349 | -0.0014466 | 0.0014466 | houston | N | 0.0014466 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.005528 | houston | 0.027814 | -0.019761 | 0.025349 | -0.0014466 | 0.0014466 | houston | N | 0.0014466 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.005528 | houston | 0.027814 | -0.019761 | 0.025349 | -0.0014466 | 0.0014466 | houston | N | 0.0014466 | 0
48651 | EP_1_2 | 1 | 5 | 0.004403 | houston | 0.026689 | -0.020886 | 0.024224 | -0.0025716 | 0.0025716 | houston | N | 0.0025716 | 0
48651 | EP_1_2 | 2 | 21 | 0.004403 | houston | 0.026689 | -0.020886 | 0.024224 | -0.0025716 | 0.0025716 | houston | N | 0.0025716 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.008206 | north | 0.01408 | -0.033495 | 0.011615 | -0.015181 | 0.011615 | west | Y | 0.01408 | 0.38003
48672 | FTR_GT2_ | 2 | 156 | -0.008206 | north | 0.01408 | -0.033495 | 0.011615 | -0.015181 | 0.011615 | west | Y | 0.01408 | 0.38446
48673 | FTR_GT3_ | 3 | 156 | -0.008206 | north | 0.01408 | -0.033495 | 0.011615 | -0.015181 | 0.011615 | west | Y | 0.01408 | 0.38446
48674 | FTR_CN4_ | 4 | 380 | -0.008206 | north | 0.01408 | -0.033495 | 0.011615 | -0.015181 | 0.011615 | west | Y | 0.01408 | 0.93652
48690 | GBY_GN5_ | 5 | 398 | 0.004043 | houston | 0.026329 | -0.021246 | 0.023864 | -0.0029316 | 0.0029316 | houston | N | 0.0029316 | 0
48691 | GBY_7374 | A | 46 | 0.005687 | houston | 0.027973 | -0.019602 | 0.025508 | -0.0012876 | 0.0012876 | houston | N | 0.0012876 | 0
48691 | GBY_7374 | B | 46 | 0.005687 | houston | 0.027973 | -0.019602 | 0.025508 | -0.0012876 | 0.0012876 | houston | N | 0.0012876 | 0
48692 | GBY_8182 | C | 46 | 0.005687 | houston | 0.027973 | -0.019602 | 0.025508 | -0.0012876 | 0.0012876 | houston | N | 0.0012876 | 0
48692 | GBY_8182 | D | 55 | 0.005687 | houston | 0.027973 | -0.019602 | 0.025508 | -0.0012876 | 0.0012876 | houston | N | 0.0012876 | 0
48693 | GBY_8384 | E | 55 | 0.005687 | houston | 0.027973 | -0.019602 | 0.025508 | -0.0012876 | 0.0012876 | houston | N | 0.0012876 | 0
48693 | GBY_8384 | F | 54 | 0.005687 | houston | 0.027973 | -0.019602 | 0.025508 | -0.0012876 | 0.0012876 | houston | N | 0.0012876 | 0
48721 | LEG_1___ | 1 | 827 | -0.018187 | north | 0.0040989 | -0.043476 | 0.0016344 | -0.025162 | 0.0016344 | west | Y | 0.0040989 | 2.0382
48722 | LEG_2___ | 2 | 819 | -0.018187 | north | 0.0040989 | -0.043476 | 0.0016344 | -0.025162 | 0.0016344 | west | Y | 0.0040989 | 2.0184
48730 | MNS_GT | 1 | 46.1 | 0.008902 | houston | 0.031188 | -0.016387 | 0.028723 | 0.0019274 | 0.0019274 | houston | N | 0.0019274 | 0
48731 | CBE_GT1 | 1 | 76 | 0.016871 | houston | 0.039157 | -0.0084177 | 0.036692 | 0.0098964 | 0.0084177 | south | Y | 0.0098964 | 0.11238
48732 | CBE_GT2 | 1 | 76 | 0.016871 | houston | 0.039157 | -0.0084177 | 0.036692 | 0.0098964 | 0.0084177 | south | Y | 0.0098964 | 0.11238
48733 | CBE_ST12 | 1 | 105 | 0.016871 | houston | 0.039157 | -0.0084177 | 0.036692 | 0.0098964 | 0.0084177 | south | Y | 0.0098964 | 0.15526
48734 | CBE_GT3 | 1 | 74 | 0.016871 | houston | 0.039157 | -0.0084177 | 0.036692 | 0.0098964 | 0.0084177 | south | Y | 0.0098964 | 0.10942
48735 | CBE_GT4 | 1 | 74 | 0.016871 | houston | 0.039157 | -0.0084177 | 0.036692 | 0.0098964 | 0.0084177 | south | Y | 0.0098964 | 0.10942
48736 | CBE_ST34 | 1 | 102 | 0.016871 | houston | 0.039157 | -0.0084177 | 0.036692 | 0.0098964 | 0.0084177 | south | Y | 0.0098964 | 0.15082
48740 | PSG_GN2_ | 1 | 180 | 0.005357 | houston | 0.027643 | -0.019932 | 0.025178 | -0.0016176 | 0.0016176 | houston | N | 0.0016176 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.005357 | houston | 0.027643 | -0.019932 | 0.025178 | -0.0016176 | 0.0016176 | houston | N | 0.0016176 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.005357 | houston | 0.027643 | -0.019932 | 0.025178 | -0.0016176 | 0.0016176 | houston | N | 0.0016176 | 0
48761 | PR_GT1__ | 1 | 35 | 0.005469 | houston | 0.027755 | -0.01982 | 0.02529 | -0.0015056 | 0.0015056 | houston | N | 0.0015056 | 0
48772 | PHR_GN2_ | MB | 459 | 0.006504 | houston | 0.02879 | -0.018785 | 0.026325 | -0.00047063 | 0.00047063 | houston | N | 0.00047063 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.004403 | houston | 0.026689 | -0.020886 | 0.024224 | -0.0025716 | 0.0025716 | houston | N | 0.0025716 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.004403 | houston | 0.026689 | -0.020886 | 0.024224 | -0.0025716 | 0.0025716 | houston | N | 0.0025716 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.004403 | houston | 0.026689 | -0.020886 | 0.024224 | -0.0025716 | 0.0025716 | houston | N | 0.0025716 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.004403 | houston | 0.026689 | -0.020886 | 0.024224 | -0.0025716 | 0.0025716 | houston | N | 0.0025716 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.004403 | houston | 0.026689 | -0.020886 | 0.024224 | -0.0025716 | 0.0025716 | houston | N | 0.0025716 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.004403 | houston | 0.026689 | -0.020886 | 0.024224 | -0.0025716 | 0.0025716 | houston | N | 0.0025716 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.004403 | houston | 0.026689 | -0.020886 | 0.024224 | -0.0025716 | 0.0025716 | houston | N | 0.0025716 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.00276 | houston | 0.025046 | -0.022529 | 0.022581 | -0.0042146 | 0.0042146 | houston | N | 0.0042146 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.00276 | houston | 0.025046 | -0.022529 | 0.022581 | -0.0042146 | 0.0042146 | houston | N | 0.0042146 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.00276 | houston | 0.025046 | -0.022529 | 0.022581 | -0.0042146 | 0.0042146 | houston | N | 0.0042146 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.00276 | houston | 0.025046 | -0.022529 | 0.022581 | -0.0042146 | 0.0042146 | houston | N | 0.0042146 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.00434 | houston | 0.026626 | -0.020949 | 0.024161 | -0.0026346 | 0.0026346 | houston | N | 0.0026346 | 0
48820 | SHELLG1_ | 1 | 71 | 0.005252 | houston | 0.027538 | -0.020037 | 0.025073 | -0.0017226 | 0.0017226 | houston | N | 0.0017226 | 0
48821 | SHELLG2 | 2 | 72 | 0.005252 | houston | 0.027538 | -0.020037 | 0.025073 | -0.0017226 | 0.0017226 | houston | N | 0.0017226 | 0
48822 | SHELLG3_ | 1 | 39 | 0.005252 | houston | 0.027538 | -0.020037 | 0.025073 | -0.0017226 | 0.0017226 | houston | N | 0.0017226 | 0
48822 | SHELLG3_ | 2 | 30 | 0.005252 | houston | 0.027538 | -0.020037 | 0.025073 | -0.0017226 | 0.0017226 | houston | N | 0.0017226 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.005618 | houston | 0.027904 | -0.019671 | 0.025439 | -0.0013566 | 0.0013566 | houston | N | 0.0013566 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.005618 | houston | 0.027904 | -0.019671 | 0.025439 | -0.0013566 | 0.0013566 | houston | N | 0.0013566 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.005362 | houston | 0.027648 | -0.019927 | 0.025183 | -0.0016126 | 0.0016126 | houston | N | 0.0016126 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.005384 | houston | 0.02767 | -0.019905 | 0.025205 | -0.0015906 | 0.0015906 | houston | N | 0.0015906 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.00539 | houston | 0.027676 | -0.019899 | 0.025211 | -0.0015846 | 0.0015846 | houston | N | 0.0015846 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.005364 | houston | 0.02765 | -0.019925 | 0.025185 | -0.0016106 | 0.0016106 | houston | N | 0.0016106 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.005359 | houston | 0.027645 | -0.01993 | 0.02518 | -0.0016156 | 0.0016156 | houston | N | 0.0016156 | 0
48855 | SRB_GT21 | B2 | 12 | 0.005394 | houston | 0.02768 | -0.019895 | 0.025215 | -0.0015806 | 0.0015806 | houston | N | 0.0015806 | 0
48855 | SRB_GT21 | MB | 18 | 0.005394 | houston | 0.02768 | -0.019895 | 0.025215 | -0.0015806 | 0.0015806 | houston | N | 0.0015806 | 0
48865 | TECO_GT1 | 1 | 50 | 0.006883 | houston | 0.029169 | -0.018406 | 0.026704 | -9.1633e-05 | 9.1633e-05 | houston | N | 9.1633e-05 | 0
48873 | THW_ST3_ | 3 | 104 | 0.004777 | houston | 0.027063 | -0.020512 | 0.024598 | -0.0021976 | 0.0021976 | houston | N | 0.0021976 | 0
48874 | THW_ST4_ | 4 | 104 | 0.004777 | houston | 0.027063 | -0.020512 | 0.024598 | -0.0021976 | 0.0021976 | houston | N | 0.0021976 | 0
48875 | THW_3132 | A | 54 | 0.004777 | houston | 0.027063 | -0.020512 | 0.024598 | -0.0021976 | 0.0021976 | houston | N | 0.0021976 | 0
48875 | THW_3132 | B | 53 | 0.004777 | houston | 0.027063 | -0.020512 | 0.024598 | -0.0021976 | 0.0021976 | houston | N | 0.0021976 | 0
48877 | THW_3334 | C | 54 | 0.004777 | houston | 0.027063 | -0.020512 | 0.024598 | -0.0021976 | 0.0021976 | houston | N | 0.0021976 | 0
48877 | THW_3334 | D | 57 | 0.004777 | houston | 0.027063 | -0.020512 | 0.024598 | -0.0021976 | 0.0021976 | houston | N | 0.0021976 | 0
48879 | THW_4142 | E | 54 | 0.004777 | houston | 0.027063 | -0.020512 | 0.024598 | -0.0021976 | 0.0021976 | houston | N | 0.0021976 | 0
48879 | THW_4142 | F | 54 | 0.004777 | houston | 0.027063 | -0.020512 | 0.024598 | -0.0021976 | 0.0021976 | houston | N | 0.0021976 | 0
48881 | THW_4344 | G | 58 | 0.004777 | houston | 0.027063 | -0.020512 | 0.024598 | -0.0021976 | 0.0021976 | houston | N | 0.0021976 | 0
48881 | THW_4344 | H | 58 | 0.004777 | houston | 0.027063 | -0.020512 | 0.024598 | -0.0021976 | 0.0021976 | houston | N | 0.0021976 | 0
48883 | THW_GT1_ | B2 | 12 | 0.00452 | houston | 0.026806 | -0.020769 | 0.024341 | -0.0024546 | 0.0024546 | houston | N | 0.0024546 | 0
48885 | THW_5152 | A | 56 | 0.00392 | houston | 0.026206 | -0.021369 | 0.023741 | -0.0030546 | 0.0030546 | houston | N | 0.0030546 | 0
48885 | THW_5152 | B | 59 | 0.00392 | houston | 0.026206 | -0.021369 | 0.023741 | -0.0030546 | 0.0030546 | houston | N | 0.0030546 | 0
48886 | THW_5354 | C | 56 | 0.00392 | houston | 0.026206 | -0.021369 | 0.023741 | -0.0030546 | 0.0030546 | houston | N | 0.0030546 | 0
48886 | THW_5354 | D | 56 | 0.00392 | houston | 0.026206 | -0.021369 | 0.023741 | -0.0030546 | 0.0030546 | houston | N | 0.0030546 | 0
48887 | THW_5556 | E | 59 | 0.00392 | houston | 0.026206 | -0.021369 | 0.023741 | -0.0030546 | 0.0030546 | houston | N | 0.0030546 | 0
48887 | THW_5556 | F | 56 | 0.00392 | houston | 0.026206 | -0.021369 | 0.023741 | -0.0030546 | 0.0030546 | houston | N | 0.0030546 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.015746 | houston | 0.038032 | -0.0095427 | 0.035567 | 0.0087714 | 0.0087714 | houston | N | 0.0087714 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.008543 | houston | 0.030829 | -0.016746 | 0.028364 | 0.0015684 | 0.0015684 | houston | N | 0.0015684 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.008543 | houston | 0.030829 | -0.016746 | 0.028364 | 0.0015684 | 0.0015684 | houston | N | 0.0015684 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.008543 | houston | 0.030829 | -0.016746 | 0.028364 | 0.0015684 | 0.0015684 | houston | N | 0.0015684 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.008543 | houston | 0.030829 | -0.016746 | 0.028364 | 0.0015684 | 0.0015684 | houston | N | 0.0015684 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.008543 | houston | 0.030829 | -0.016746 | 0.028364 | 0.0015684 | 0.0015684 | houston | N | 0.0015684 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.008783 | houston | 0.031069 | -0.016506 | 0.028604 | 0.0018084 | 0.0018084 | houston | N | 0.0018084 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.008783 | houston | 0.031069 | -0.016506 | 0.028604 | 0.0018084 | 0.0018084 | houston | N | 0.0018084 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.008783 | houston | 0.031069 | -0.016506 | 0.028604 | 0.0018084 | 0.0018084 | houston | N | 0.0018084 | 0
48929 | WAPGT21_ | B1 | 13 | 0.008543 | houston | 0.030829 | -0.016746 | 0.028364 | 0.0015684 | 0.0015684 | houston | N | 0.0015684 | 0
48940 | WARVUE_G | G1 | 12 | 0.004395 | houston | 0.026681 | -0.020894 | 0.024216 | -0.0025796 | 0.0025796 | houston | N | 0.0025796 | 0
49803 | EXN_15GT | 1 | 34 | 0.004599 | houston | 0.026885 | -0.02069 | 0.02442 | -0.0023756 | 0.0023756 | houston | N | 0.0023756 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.004599 | houston | 0.026885 | -0.02069 | 0.02442 | -0.0023756 | 0.0023756 | houston | N | 0.0023756 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.004599 | houston | 0.026885 | -0.02069 | 0.02442 | -0.0023756 | 0.0023756 | houston | N | 0.0023756 | 0
49826 | EXN938GT | 5 | 45.9 | 0.004599 | houston | 0.026885 | -0.02069 | 0.02442 | -0.0023756 | 0.0023756 | houston | N | 0.0023756 | 0
49828 | EXN941GT | 10 | 17.7 | 0.004599 | houston | 0.026885 | -0.02069 | 0.02442 | -0.0023756 | 0.0023756 | houston | N | 0.0023756 | 0
49829 | EXN942GT | 11 | 20.4 | 0.004599 | houston | 0.026885 | -0.02069 | 0.02442 | -0.0023756 | 0.0023756 | houston | N | 0.0023756 | 0
49830 | EXN943GT | 12 | 19.9 | 0.004599 | houston | 0.026885 | -0.02069 | 0.02442 | -0.0023756 | 0.0023756 | houston | N | 0.0023756 | 0
49831 | EXN944GT | 13 | 35 | 0.004599 | houston | 0.026885 | -0.02069 | 0.02442 | -0.0023756 | 0.0023756 | houston | N | 0.0023756 | 0
49832 | EXN945GT | 9 | 18 | 0.004599 | houston | 0.026885 | -0.02069 | 0.02442 | -0.0023756 | 0.0023756 | houston | N | 0.0023756 | 0
49837 | EXN_GT | 4 | 85.4 | 0.004599 | houston | 0.026885 | -0.02069 | 0.02442 | -0.0023756 | 0.0023756 | houston | N | 0.0023756 | 0
49838 | EXN_14GT | 14 | 148 | 0.004599 | houston | 0.026885 | -0.02069 | 0.02442 | -0.0023756 | 0.0023756 | houston | N | 0.0023756 | 0
49851 | DOW17000 | 37 | 62 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49858 | DOW38100 | 31 | 71.4 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49859 | DOW38200 | 33 | 45 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49860 | DOW38300 | 32 | 101 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49862 | DOW39100 | 36 | 86 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49863 | DOW39200 | 35 | 88 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49865 | DOW41000 | 41 | 50 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49866 | DOW42000 | 42 | 18 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49869 | DOW49000 | 45 | 94 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49870 | DOW61000 | 61 | 70 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49871 | DOW62000 | 62 | 63 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49872 | DOW63000 | 63 | 72 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49873 | DOW64000 | 64 | 64.8 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49876 | DOW65000 | 65 | 101 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49877 | DOW66000 | 66 | 97 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49878 | DOW67000 | 67 | 103 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49882 | DOW81000 | 81 | 76 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49884 | DOW82000 | 82 | 80 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49885 | DOW83000 | 83 | 80 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
49886 | DOW84000 | 84 | 171 | 0.012299 | houston | 0.034585 | -0.01299 | 0.03212 | 0.0053244 | 0.0053244 | houston | N | 0.0053244 | 0
58909 | PEARSALL | 1 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58909 | PEARSALL | 2 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58909 | PEARSALL | 3 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58909 | PEARSALL | 4 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58909 | PEARSALL | 5 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58909 | PEARSALL | 6 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58919 | PEARSALL | 1 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58919 | PEARSALL | 2 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58919 | PEARSALL | 3 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58919 | PEARSALL | 4 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58919 | PEARSALL | 5 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58919 | PEARSALL | 6 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58929 | PEARSALL | 1 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58929 | PEARSALL | 2 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58929 | PEARSALL | 3 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58929 | PEARSALL | 4 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58929 | PEARSALL | 5 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58929 | PEARSALL | 6 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58949 | PEARSALL | 1 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58949 | PEARSALL | 2 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58949 | PEARSALL | 3 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58949 | PEARSALL | 4 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58949 | PEARSALL | 5 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
58949 | PEARSALL | 6 | 8.4 | 0.028184 | south | 0.05047 | 0.0028953 | 0.048005 | 0.021209 | 0.0028953 | south | N | 0.0028953 | 0
60000 | DSKY2 | 1 | 76.5 | -0.016415 | west | 0.0058709 | -0.041704 | 0.0034064 | -0.02339 | 0.0034064 | west | N | 0.0034064 | 0
60003 | KING_NE1 | 1 | 80 | -0.017365 | west | 0.0049209 | -0.042654 | 0.0024564 | -0.02434 | 0.0024564 | west | N | 0.0024564 | 0
60005 | KING_SE1 | 1 | 40 | -0.017365 | west | 0.0049209 | -0.042654 | 0.0024564 | -0.02434 | 0.0024564 | west | N | 0.0024564 | 0
60007 | KING_SW1 | 1 | 80 | -0.017518 | west | 0.0047679 | -0.042807 | 0.0023034 | -0.024493 | 0.0023034 | west | N | 0.0023034 | 0
60016 | WOODWRD1 | 1 | 80 | -0.017332 | west | 0.0049539 | -0.042621 | 0.0024894 | -0.024307 | 0.0024894 | west | N | 0.0024894 | 0
60017 | ORNNWP1 | 1 | 80 | -0.016545 | west | 0.0057409 | -0.041834 | 0.0032764 | -0.02352 | 0.0032764 | west | N | 0.0032764 | 0
60018 | DSKY1 | 1 | 84 | -0.016287 | west | 0.0059989 | -0.041576 | 0.0035344 | -0.023262 | 0.0035344 | west | N | 0.0035344 | 0
60019 | KING_NW1 | 1 | 80 | -0.017518 | west | 0.0047679 | -0.042807 | 0.0023034 | -0.024493 | 0.0023034 | west | N | 0.0023034 | 0
60057 | CALLAHAN | 1 | 114 | 0.033291 | south | 0.055577 | 0.0080023 | 0.053112 | 0.026316 | 0.0080023 | south | N | 0.0080023 | 0
60058 | BUFF_GAP | 1 | 120 | -0.020077 | west | 0.0022089 | -0.045366 | -0.00025562 | -0.027052 | 0.00025562 | west | N | 0.00025562 | 0
60060 | CIRELLO | 1 | 233 | -0.020077 | west | 0.0022089 | -0.045366 | -0.00025562 | -0.027052 | 0.00025562 | west | N | 0.00025562 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.020077 | west | 0.0022089 | -0.045366 | -0.00025562 | -0.027052 | 0.00025562 | west | N | 0.00025562 | 0
60066 | H_HOLLOW | 1 | 222 | 0.033291 | south | 0.055577 | 0.0080023 | 0.053112 | 0.026316 | 0.0080023 | south | N | 0.0080023 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.033291 | south | 0.055577 | 0.0080023 | 0.053112 | 0.026316 | 0.0080023 | south | N | 0.0080023 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.033291 | south | 0.055577 | 0.0080023 | 0.053112 | 0.026316 | 0.0080023 | south | N | 0.0080023 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.033291 | south | 0.055577 | 0.0080023 | 0.053112 | 0.026316 | 0.0080023 | south | N | 0.0080023 | 0
60074 | HORSH5 | 1 | 100 | 0.033291 | south | 0.055577 | 0.0080023 | 0.053112 | 0.026316 | 0.0080023 | south | N | 0.0080023 | 0
60081 | WHRLWIND | 1 | 60 | -0.020841 | west | 0.0014449 | -0.04613 | -0.0010196 | -0.027816 | 0.0010196 | west | N | 0.0010196 | 0
60201 | RIO DRCS | F | 0 | 0.016402 | south | 0.038688 | -0.0088867 | 0.036223 | 0.0094274 | 0.0088867 | south | N | 0.0088867 | 0
60202 | FRIEND_R | F | 0 | -0.012179 | west | 0.010107 | -0.037468 | 0.0076424 | -0.019154 | 0.0076424 | west | N | 0.0076424 | 0
60203 | PRES0A | BT | 4.8 | -0.018085 | west | 0.0042009 | -0.043374 | 0.0017364 | -0.02506 | 0.0017364 | west | N | 0.0017364 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.020465 | west | 0.0018209 | -0.045754 | -0.00064362 | -0.02744 | 0.00064362 | west | N | 0.00064362 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.020465 | west | 0.0018209 | -0.045754 | -0.00064362 | -0.02744 | 0.00064362 | west | N | 0.00064362 | 0
71057 | L_SWEETW | W1 | 135 | -0.020465 | west | 0.0018209 | -0.045754 | -0.00064362 | -0.02744 | 0.00064362 | west | N | 0.00064362 | 0
71059 | L_SWEETW | W1 | 119 | -0.020465 | west | 0.0018209 | -0.045754 | -0.00064362 | -0.02744 | 0.00064362 | west | N | 0.00064362 | 0
71060 | L_SWEETW | W1 | 105 | -0.020465 | west | 0.0018209 | -0.045754 | -0.00064362 | -0.02744 | 0.00064362 | west | N | 0.00064362 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.020465 | west | 0.0018209 | -0.045754 | -0.00064362 | -0.02744 | 0.00064362 | west | N | 0.00064362 | 0
76031 | L_GASCCR | W1 | 150 | -0.019835 | west | 0.0024509 | -0.045124 | -1.3621e-05 | -0.02681 | 1.3621e-05 | west | N | 1.3621e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.019756 | west | 0.0025299 | -0.045045 | 6.5379e-05 | -0.026731 | 6.5379e-05 | west | N | 6.5379e-05 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.019756 | west | 0.0025299 | -0.045045 | 6.5379e-05 | -0.026731 | 6.5379e-05 | west | N | 6.5379e-05 | 0
76096 | L_CAPRSI | W1 | 186 | -0.019756 | west | 0.0025299 | -0.045045 | 6.5379e-05 | -0.026731 | 6.5379e-05 | west | N | 6.5379e-05 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.019756 | west | 0.0025299 | -0.045045 | 6.5379e-05 | -0.026731 | 6.5379e-05 | west | N | 6.5379e-05 | 0
80003 | MILHWYS | F | 0 | 0.02691 | south | 0.049196 | 0.0016213 | 0.046731 | 0.019935 | 0.0016213 | south | N | 0.0016213 | 0
80010 | EPLVT1 | F | 0 | 0.020743 | south | 0.043029 | -0.0045457 | 0.040564 | 0.013768 | 0.0045457 | south | N | 0.0045457 | 0
80012 | LAR | F | 0 | 0.028287 | south | 0.050573 | 0.0029983 | 0.048108 | 0.021312 | 0.0029983 | south | N | 0.0029983 | 0
80051 | FORPVCM0 | 8 | 28 | 0.024888 | south | 0.047174 | -0.00040069 | 0.044709 | 0.017913 | 0.00040069 | south | N | 0.00040069 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.024888 | south | 0.047174 | -0.00040069 | 0.044709 | 0.017913 | 0.00040069 | south | N | 0.00040069 | 0
80053 | FOR69CG0 | 10 | 74 | 0.024888 | south | 0.047174 | -0.00040069 | 0.044709 | 0.017913 | 0.00040069 | south | N | 0.00040069 | 0
80080 | GWINDT11 | 1 | 94 | 0.026892 | south | 0.049178 | 0.0016033 | 0.046713 | 0.019917 | 0.0016033 | south | N | 0.0016033 | 0
80080 | GWINDT11 | 2 | 41 | 0.026892 | south | 0.049178 | 0.0016033 | 0.046713 | 0.019917 | 0.0016033 | south | N | 0.0016033 | 0
80080 | GWINDT11 | 3 | 38 | 0.026892 | south | 0.049178 | 0.0016033 | 0.046713 | 0.019917 | 0.0016033 | south | N | 0.0016033 | 0
80080 | GWINDT11 | 4 | 19 | 0.026892 | south | 0.049178 | 0.0016033 | 0.046713 | 0.019917 | 0.0016033 | south | N | 0.0016033 | 0
80081 | GWINDT21 | 1 | 94 | 0.026892 | south | 0.049178 | 0.0016033 | 0.046713 | 0.019917 | 0.0016033 | south | N | 0.0016033 | 0
80081 | GWINDT21 | 2 | 36 | 0.026892 | south | 0.049178 | 0.0016033 | 0.046713 | 0.019917 | 0.0016033 | south | N | 0.0016033 | 0
80081 | GWINDT21 | 3 | 43 | 0.026892 | south | 0.049178 | 0.0016033 | 0.046713 | 0.019917 | 0.0016033 | south | N | 0.0016033 | 0
80081 | GWINDT21 | 4 | 22 | 0.026892 | south | 0.049178 | 0.0016033 | 0.046713 | 0.019917 | 0.0016033 | south | N | 0.0016033 | 0
80137 | CSDR89 | 8 | 39 | 0.025826 | south | 0.048112 | 0.00053731 | 0.045647 | 0.018851 | 0.00053731 | south | N | 0.00053731 | 0
80137 | CSDR89 | 9 | 15 | 0.025826 | south | 0.048112 | 0.00053731 | 0.045647 | 0.018851 | 0.00053731 | south | N | 0.00053731 | 0
80138 | CSDR7 | 7 | 7 | 0.025826 | south | 0.048112 | 0.00053731 | 0.045647 | 0.018851 | 0.00053731 | south | N | 0.00053731 | 0
80139 | CSDR56 | 5 | 15 | 0.025826 | south | 0.048112 | 0.00053731 | 0.045647 | 0.018851 | 0.00053731 | south | N | 0.00053731 | 0
80139 | CSDR56 | 6 | 39 | 0.025826 | south | 0.048112 | 0.00053731 | 0.045647 | 0.018851 | 0.00053731 | south | N | 0.00053731 | 0
80140 | CSDR11 | 11 | 39 | 0.025826 | south | 0.048112 | 0.00053731 | 0.045647 | 0.018851 | 0.00053731 | south | N | 0.00053731 | 0
80180 | PNSCALT1 | 1 | 148 | 0.026892 | south | 0.049178 | 0.0016033 | 0.046713 | 0.019917 | 0.0016033 | south | N | 0.0016033 | 0
80180 | PNSCALT1 | 2 | 50 | 0.026892 | south | 0.049178 | 0.0016033 | 0.046713 | 0.019917 | 0.0016033 | south | N | 0.0016033 | 0
80181 | PNSCALT2 | 1 | 55 | 0.026892 | south | 0.049178 | 0.0016033 | 0.046713 | 0.019917 | 0.0016033 | south | N | 0.0016033 | 0
80181 | PNSCALT2 | 2 | 50 | 0.026892 | south | 0.049178 | 0.0016033 | 0.046713 | 0.019917 | 0.0016033 | south | N | 0.0016033 | 0
80223 | REYSHR G | 1 | 12 | 0.026397 | south | 0.048683 | 0.0011083 | 0.046218 | 0.019422 | 0.0011083 | south | N | 0.0011083 | 0
80224 | VISTRONG | 1 | 15 | 0.026145 | south | 0.048431 | 0.00085631 | 0.045966 | 0.01917 | 0.00085631 | south | N | 0.00085631 | 0
80225 | VISTRONG | 2 | 23 | 0.026145 | south | 0.048431 | 0.00085631 | 0.045966 | 0.01917 | 0.00085631 | south | N | 0.00085631 | 0
80226 | ALCOA G | 1 | 48 | 0.025113 | south | 0.047399 | -0.00017569 | 0.044934 | 0.018138 | 0.00017569 | south | N | 0.00017569 | 0
80227 | AIRCO G | 1 | 8 | 0.025911 | south | 0.048197 | 0.00062231 | 0.045732 | 0.018936 | 0.00062231 | south | N | 0.00062231 | 0
80261 | NBEC81A | 1 | 180 | 0.026665 | south | 0.048951 | 0.0013763 | 0.046486 | 0.01969 | 0.0013763 | south | N | 0.0013763 | 0
80262 | NBEC91A | 1 | 180 | 0.026657 | south | 0.048943 | 0.0013683 | 0.046478 | 0.019682 | 0.0013683 | south | N | 0.0013683 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.026712 | south | 0.048998 | 0.0014233 | 0.046533 | 0.019737 | 0.0014233 | south | N | 0.0014233 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.026712 | south | 0.048998 | 0.0014233 | 0.046533 | 0.019737 | 0.0014233 | south | N | 0.0014233 | 0
80265 | LARECU40 | 4 | 100 | 0.02829 | south | 0.050576 | 0.0030013 | 0.048111 | 0.021315 | 0.0030013 | south | N | 0.0030013 | 0
80266 | LARECU50 | 5 | 100 | 0.02829 | south | 0.050576 | 0.0030013 | 0.048111 | 0.021315 | 0.0030013 | south | N | 0.0030013 | 0
80291 | PAPALOTE | 1 | 25 | 0.026494 | south | 0.04878 | 0.0012053 | 0.046315 | 0.019519 | 0.0012053 | south | N | 0.0012053 | 0
80291 | PAPALOTE | 2 | 25 | 0.026494 | south | 0.04878 | 0.0012053 | 0.046315 | 0.019519 | 0.0012053 | south | N | 0.0012053 | 0
80291 | PAPALOTE | 3 | 25 | 0.026494 | south | 0.04878 | 0.0012053 | 0.046315 | 0.019519 | 0.0012053 | south | N | 0.0012053 | 0
80291 | PAPALOTE | 4 | 16 | 0.026494 | south | 0.04878 | 0.0012053 | 0.046315 | 0.019519 | 0.0012053 | south | N | 0.0012053 | 0
80294 | PAPALOTE | 5 | 25 | 0.026494 | south | 0.04878 | 0.0012053 | 0.046315 | 0.019519 | 0.0012053 | south | N | 0.0012053 | 0
80294 | PAPALOTE | 6 | 25 | 0.026494 | south | 0.04878 | 0.0012053 | 0.046315 | 0.019519 | 0.0012053 | south | N | 0.0012053 | 0
80294 | PAPALOTE | 7 | 25 | 0.026494 | south | 0.04878 | 0.0012053 | 0.046315 | 0.019519 | 0.0012053 | south | N | 0.0012053 | 0
80294 | PAPALOTE | 8 | 15 | 0.026494 | south | 0.04878 | 0.0012053 | 0.046315 | 0.019519 | 0.0012053 | south | N | 0.0012053 | 0
86104 | CID-138 | EQ | 0 | 0.02829 | south | 0.050576 | 0.0030013 | 0.048111 | 0.021315 | 0.0030013 | south | N | 0.0030013 | 0
86105 | CID-230 | EQ | 500 | 0.02829 | south | 0.050576 | 0.0030013 | 0.048111 | 0.021315 | 0.0030013 | south | N | 0.0030013 | 0
86106 | CUF-230 | EQ | 500 | 0.02829 | south | 0.050576 | 0.0030013 | 0.048111 | 0.021315 | 0.0030013 | south | N | 0.0030013 | 0
86107 | CUF-138 | EQ | 0 | 0.02829 | south | 0.050576 | 0.0030013 | 0.048111 | 0.021315 | 0.0030013 | south | N | 0.0030013 | 0
88198 | BEEVILLE | F | 0 | 0.028395 | south | 0.050681 | 0.0031063 | 0.048216 | 0.02142 | 0.0031063 | south | N | 0.0031063 | 0
88253 | HAMILTON | F | 0 | 0.015927 | south | 0.038213 | -0.0093617 | 0.035748 | 0.0089524 | 0.0089524 | houston | Y | 0.0093617 | 0
88299 | ZAPATA | F | 0 | 0.027613 | south | 0.049899 | 0.0023243 | 0.047434 | 0.020638 | 0.0023243 | south | N | 0.0023243 | 0
88508 | FALFURRI | F | 0 | 0.027337 | south | 0.049623 | 0.0020483 | 0.047158 | 0.020362 | 0.0020483 | south | N | 0.0020483 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3650 ELGIN_SS 13430 SAND_TXU C:SANDOW__5-L_AUSTRO5_1Y C:L_AUSTRO5_1Y-SAND_TXU_59 [3429 - 7040 ckt1] and [7040 - 13429 ckt2] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.064481 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.5115 | 132 | 0.086767 | 11.4532 | 132 | 11.4532
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.064481 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.6405 | 134 | 0.086767 | 11.6268 | 266 | 23.08
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.064481 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 20.8274 | 323 | 0.086767 | 28.0257
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.049411 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4705 | 50 | 0.071697 | 3.5848 |  |  | Weighted Shift Factors
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.049411 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4705 | 50 | 0.071697 | 3.5848 |  |  | North | -0.022286
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.049411 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4705 | 50 | 0.071697 | 3.5848 |  |  | South | 0.034557
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.049411 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4705 | 50 | 0.071697 | 3.5848 |  |  |  | -0.056842
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.04825 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.0265 | 42 | 0.070536 | 2.9625
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.04825 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.123 | 44 | 0.070536 | 3.1036 |  |  | Line Rating | 247.95
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.04825 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.123 | 44 | 0.070536 | 3.1036 |  |  | Conc Gen | 266
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.04825 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.2677 | 47 | 0.070536 | 3.3152 |  |  | Weighted Imp. | 23.08
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.046657 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 14.4637 | 310 | 0.068943 | 21.3723 |  |  | PTDF | 0.086767
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.046657 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 19.2693 | 413 | 0.068943 | 28.4734
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.046464 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.37171 | 0 | 0.06875 | 0 |  |  | Concentration | -1.5264
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.046464 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.37171 | 0 | 0.06875 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.2256 | 49 | 0.067706 | 3.3176
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.0893 | 46 | 0.067706 | 3.1145
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.0893 | 46 | 0.067706 | 3.1145
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.1347 | 47 | 0.067706 | 3.1822
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.04542 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.9947 | 154 | 0.067706 | 10.4267
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.04542 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.7222 | 148 | 0.067706 | 10.0205
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.1802 | 48 | 0.067706 | 3.2499
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.1802 | 48 | 0.067706 | 3.2499
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.042227 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.4779 | 0 | 0.064513 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.042227 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.4357 | 0 | 0.064513 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.042227 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.4779 | 0 | 0.064513 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.03983 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.0741 | 152.5 | 0.062116 | 9.4727
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.03983 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.9546 | 149.5 | 0.062116 | 9.2863
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.03983 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.2645 | 232.6 | 0.062116 | 14.4482
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.039065 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.1723 | 158 | 0.061351 | 9.6934
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.039065 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.2504 | 160 | 0.061351 | 9.8161
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.039065 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.8364 | 175 | 0.061351 | 10.7364
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.037245 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22347 | 0 | 0.059531 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.03682 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 21.5029 | 584 | 0.059106 | 34.5178
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.03682 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 21.9079 | 595 | 0.059106 | 35.168
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.036779 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 15.9253 | 433 | 0.059065 | 25.5751
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.036677 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.088025 | 0 | 0.058963 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.036677 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.088025 | 0 | 0.058963 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.035409 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.084982 | 0 | 0.057695 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.035409 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.084982 | 0 | 0.057695 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.035409 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.099145 | 0 | 0.057695 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.035192 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.8795 | 223.9 | 0.057478 | 12.8693
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.035192 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.9182 | 225 | 0.057478 | 12.9325
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.035192 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.9041 | 224.6 | 0.057478 | 12.9095
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.035192 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.978 | 226.7 | 0.057478 | 13.0302
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.035064 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.63115 | 0 | 0.05735 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.035064 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.63115 | 0 | 0.05735 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.034605 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.41526 | 0 | 0.056891 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.034003 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13601 | 0 | 0.056289 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.033998 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8277 | 142 | 0.056284 | 7.9923
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.033998 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.9297 | 145 | 0.056284 | 8.1612
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.033998 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.1337 | 151 | 0.056284 | 8.4989
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.033998 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.8594 | 290 | 0.056284 | 16.3223
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.7952 | 114 | 0.055577 | 6.3358
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.3906 | 222 | 0.055577 | 12.3381
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 6.1255 | 184 | 0.055577 | 10.2261
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.4572 | 224 | 0.055577 | 12.4492
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.8285 | 115 | 0.055577 | 6.3913
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8242 | 147 | 0.055104 | 8.1003
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.5289 | 138 | 0.055104 | 7.6043
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.5945 | 140 | 0.055104 | 7.7145
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8242 | 147 | 0.055104 | 8.1003
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.9729 | 182 | 0.055104 | 10.0289
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.498 | 198 | 0.055104 | 10.9106
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.032165 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.054451 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.032165 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.054451 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.032165 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.054451 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.032137 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.89984 | 0 | 0.054423 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.032137 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.93197 | 0 | 0.054423 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.03208 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 13.217 | 412 | 0.054366 | 22.3987
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.03208 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 12.832 | 400 | 0.054366 | 21.7464
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.032064 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.7014 | 209 | 0.05435 | 11.3591
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.032064 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.9258 | 216 | 0.05435 | 11.7396
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.032064 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4749 | 46 | 0.05435 | 2.5001
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.032064 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.507 | 47 | 0.05435 | 2.5544
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.032064 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4749 | 46 | 0.05435 | 2.5001
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.032064 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4749 | 46 | 0.05435 | 2.5001
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.032062 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 13.5943 | 424 | 0.054348 | 23.0435
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.032062 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 13.6264 | 425 | 0.054348 | 23.0979
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.031989 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 13.0195 | 407 | 0.054275 | 22.0899
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.031906 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 13.4643 | 422 | 0.054192 | 22.869
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.031901 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.9447 | 155 | 0.054187 | 8.399
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.031901 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.4232 | 170 | 0.054187 | 9.2118
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.031901 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.9447 | 155 | 0.054187 | 8.399
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.031832 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8463 | 58 | 0.054118 | 3.1388
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.031832 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.833 | 89 | 0.054118 | 4.8165
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.031832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4006 | 44 | 0.054118 | 2.3812
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.031832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4006 | 44 | 0.054118 | 2.3812
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.031832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.3688 | 43 | 0.054118 | 2.3271
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.031832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4324 | 45 | 0.054118 | 2.4353
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.031755 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 17.3382 | 546 | 0.054041 | 29.5063
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.031755 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 23.8163 | 750 | 0.054041 | 40.5307
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.030121 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.9279 | 396 | 0.052407 | 20.7531
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.028499 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.68398 | 24 | 0.050785 | 1.2188
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.028499 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.68398 | 24 | 0.050785 | 1.2188
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.028499 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.65548 | 23 | 0.050785 | 1.1681
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.028395 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050681 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.028353 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.38844 | 0 | 0.050639 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.02829 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.829 | 100 | 0.050576 | 5.0576
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.02829 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.829 | 100 | 0.050576 | 5.0576
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.02829 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050576 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.02829 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050576 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.02829 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050576 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.02829 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050576 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.028287 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050573 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.028015 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 17.6214 | 629 | 0.050301 | 31.6393
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.027613 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.049899 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.027455 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.49419 | 0 | 0.049741 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.027455 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.49419 | 0 | 0.049741 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.027455 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.41182 | 0 | 0.049741 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.027337 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.049623 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.027318 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.32782 | 0 | 0.049604 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.027318 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3005 | 0 | 0.049604 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.027318 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.32782 | 0 | 0.049604 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.027079 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8994 | 144 | 0.049365 | 7.1085
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.027079 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.0909 | 188 | 0.049365 | 9.2806
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.027008 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9567 | 146.5 | 0.049294 | 7.2216
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.027008 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9945 | 147.9 | 0.049294 | 7.2906
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.027008 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.6724 | 173 | 0.049294 | 8.5278
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.026959 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.5805 | 207 | 0.049245 | 10.1937
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.026959 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.842 | 216.7 | 0.049245 | 10.6714
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.026959 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.5241 | 242 | 0.049245 | 11.9173
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.026958 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.882 | 144 | 0.049244 | 7.0911
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.026958 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.882 | 144 | 0.049244 | 7.0911
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.026958 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.6098 | 171 | 0.049244 | 8.4207
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.02691 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.049196 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.02691 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0226 | 38 | 0.049196 | 1.8694
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.02691 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.51936 | 19.3 | 0.049196 | 0.94948
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.02691 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.40365 | 15 | 0.049196 | 0.73794
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.02691 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2648 | 47 | 0.049196 | 2.3122
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.5278 | 94 | 0.049178 | 4.6227
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.1026 | 41 | 0.049178 | 2.0163
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.0219 | 38 | 0.049178 | 1.8688
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.51095 | 19 | 0.049178 | 0.93438
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.5278 | 94 | 0.049178 | 4.6227
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.96811 | 36 | 0.049178 | 1.7704
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.1564 | 43 | 0.049178 | 2.1146
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.59162 | 22 | 0.049178 | 1.0819
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.98 | 148 | 0.049178 | 7.2783
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.3446 | 50 | 0.049178 | 2.4589
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.4791 | 55 | 0.049178 | 2.7048
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.3446 | 50 | 0.049178 | 2.4589
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.026861 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.77897 | 0 | 0.049147 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.026763 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.017 | 0 | 0.049049 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.026751 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0165 | 0 | 0.049037 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.026749 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9527 | 0 | 0.049035 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.026732 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.6683 | 0 | 0.049018 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.026732 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.6683 | 0 | 0.049018 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.026712 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.9218 | 334 | 0.048998 | 16.3653
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.026712 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 9.0821 | 340 | 0.048998 | 16.6593
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.026712 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8082 | 180 | 0.048998 | 8.8196
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.026712 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8082 | 180 | 0.048998 | 8.8196
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.026665 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7997 | 180 | 0.048951 | 8.8112
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.02666 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.9537 | 0 | 0.048946 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.02666 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.9617 | 0 | 0.048946 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.02666 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.079 | 0 | 0.048946 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.026657 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.9568 | 336 | 0.048943 | 16.4448
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.026657 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7983 | 180 | 0.048943 | 8.8097
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.026573 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.2675 | 47.7 | 0.048859 | 2.3306
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.026573 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.99117 | 37.3 | 0.048859 | 1.8224
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.026573 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.2224 | 46 | 0.048859 | 2.2475
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.026573 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.2755 | 48 | 0.048859 | 2.3452
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66235 | 25 | 0.04878 | 1.2195
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66235 | 25 | 0.04878 | 1.2195
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66235 | 25 | 0.04878 | 1.2195
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4239 | 16 | 0.04878 | 0.78048
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66235 | 25 | 0.04878 | 1.2195
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66235 | 25 | 0.04878 | 1.2195
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66235 | 25 | 0.04878 | 1.2195
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.39741 | 15 | 0.04878 | 0.7317
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.1707 | 0 | 0.048683 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.0387 | 0 | 0.048683 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6397 | 0 | 0.048683 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.8276 | 0 | 0.048683 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.8804 | 0 | 0.048683 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.3524 | 0 | 0.048683 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.026397 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.31676 | 0 | 0.048683 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.026289 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.57836 | 22 | 0.048575 | 1.0686
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.026289 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28918 | 11 | 0.048575 | 0.53432
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.026289 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28918 | 11 | 0.048575 | 0.53432
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.026145 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.39217 | 0 | 0.048431 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.026145 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.60133 | 0 | 0.048431 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.025911 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.20729 | 0 | 0.048197 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.72313 | 0 | 0.048112 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.18078 | 0 | 0.048112 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0072 | 0 | 0.048112 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.38739 | 0 | 0.048112 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.18078 | 0 | 0.048112 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.38739 | 0 | 0.048112 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0072 | 0 | 0.048112 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0072 | 0 | 0.048112 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.025113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2054 | 0 | 0.047399 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9662 | 0 | 0.047174 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.0159 | 0 | 0.047174 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9662 | 0 | 0.047174 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.991 | 0 | 0.047174 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9512 | 0 | 0.047174 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.6222 | 0 | 0.047174 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1448 | 0 | 0.047174 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.69686 | 0 | 0.047174 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0851 | 0 | 0.047174 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8417 | 0 | 0.047174 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.020743 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.043029 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.019834 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.119 | 0 | 0.04212 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.2822 | 76 | 0.039157 | 2.9759
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.2822 | 76 | 0.039157 | 2.9759
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.7715 | 105 | 0.039157 | 4.1115
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.2485 | 74 | 0.039157 | 2.8976
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.2485 | 74 | 0.039157 | 2.8976
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.7208 | 102 | 0.039157 | 3.994
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.016409 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 21.8732 | 0 | 0.038695 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.016409 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 21.7912 | 0 | 0.038695 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.015927 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.52559 | 0 | 0.038213 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.015927 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.39818 | 0 | 0.038213 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.015927 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.038213 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.015746 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.0392 | 66 | 0.038032 | 2.5101
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.76254 | 0 | 0.034585 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.87815 | 0 | 0.034585 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55346 | 0 | 0.034585 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2422 | 0 | 0.034585 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0577 | 0 | 0.034585 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0823 | 0 | 0.034585 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61495 | 0 | 0.034585 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22138 | 0 | 0.034585 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1561 | 0 | 0.034585 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.86093 | 0 | 0.034585 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77484 | 0 | 0.034585 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.88553 | 0 | 0.034585 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79698 | 0 | 0.034585 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2422 | 0 | 0.034585 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.193 | 0 | 0.034585 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2668 | 0 | 0.034585 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.93472 | 0 | 0.034585 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.98392 | 0 | 0.034585 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.98392 | 0 | 0.034585 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.1031 | 0 | 0.034585 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.011621 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.82509 | 0 | 0.033907 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.011621 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11621 | 0 | 0.033907 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.011105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2327 | 0 | 0.033391 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.011105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2327 | 0 | 0.033391 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.011105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3215 | 0 | 0.033391 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.011105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.216 | 0 | 0.033391 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.008902 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.41038 | 0 | 0.031188 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.008783 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.7177 | 651 | 0.031069 | 20.2259
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.008783 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.9536 | 564 | 0.031069 | 17.5229
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.008783 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.2698 | 600 | 0.031069 | 18.6413
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.008765 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4287 | 0 | 0.031051 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.008765 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4287 | 0 | 0.031051 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.008765 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.1474 | 0 | 0.031051 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.008579 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28311 | 0 | 0.030865 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.008543 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.3754 | 161 | 0.030829 | 4.9635
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.008543 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.4181 | 166 | 0.030829 | 5.1176
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.008543 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.1187 | 248 | 0.030829 | 7.6456
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.008543 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 4.6645 | 546 | 0.030829 | 16.8326
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.008543 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 5.4931 | 0 | 0.030829 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.008543 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11106 | 13 | 0.030829 | 0.40078
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.007329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.7351 | 0 | 0.029615 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.007329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.68086 | 0 | 0.029615 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.007329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.75269 | 0 | 0.029615 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.007329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.74756 | 0 | 0.029615 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.007328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2345 | 0 | 0.029614 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.007328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21984 | 0 | 0.029614 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.007323 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.51847 | 0 | 0.029609 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.007323 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.48844 | 0 | 0.029609 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.007323 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.38812 | 0 | 0.029609 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1219 | 0 | 0.029609 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1241 | 0 | 0.029609 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1153 | 0 | 0.029609 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.70301 | 0 | 0.029609 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7868 | 0 | 0.029609 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.007323 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29292 | 0 | 0.029609 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.006883 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.34415 | 50 | 0.029169 | 1.4584
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.006504 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.02879 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55401 | 0 | 0.028374 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.53331 | 0 | 0.028374 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52966 | 0 | 0.028374 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3318 | 0 | 0.028374 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.074274 | 0 | 0.028374 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.005923 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38499 | 0 | 0.028209 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.005923 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.35538 | 0 | 0.028209 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.005923 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38499 | 0 | 0.028209 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.005923 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38499 | 0 | 0.028209 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.2616 | 46 | 0.027973 | 1.2868
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.2616 | 46 | 0.027973 | 1.2868
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.2616 | 46 | 0.027973 | 1.2868
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.31278 | 55 | 0.027973 | 1.5385
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.31278 | 55 | 0.027973 | 1.5385
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.3071 | 54 | 0.027973 | 1.5105
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.005618 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.4382 | 0 | 0.027904 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.005618 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.44944 | 0 | 0.027904 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90217 | 0 | 0.027814 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.86845 | 0 | 0.027814 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.87066 | 0 | 0.027814 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.8679 | 0 | 0.027814 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.487 | 0 | 0.027814 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.005469 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19142 | 0 | 0.027755 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.005394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.064728 | 12 | 0.02768 | 0.33216
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.005394 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.02768 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.00539 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.91091 | 169 | 0.027676 | 4.6772
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.005384 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.88836 | 165 | 0.02767 | 4.5655
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.00538 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80162 | 0 | 0.027666 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.00538 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35024 | 0 | 0.027666 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.005364 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.1425 | 213 | 0.02765 | 5.8894
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.005362 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.086864 | 0 | 0.027648 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.005361 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3431 | 0 | 0.027647 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.005361 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33882 | 0 | 0.027647 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.005361 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.44282 | 0 | 0.027647 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.005361 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39457 | 0 | 0.027647 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.005359 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.2219 | 228 | 0.027645 | 6.303
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.005357 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.96426 | 0 | 0.027643 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.005357 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.84962 | 0 | 0.027643 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.005357 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.84105 | 0 | 0.027643 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.005252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.37289 | 0 | 0.027538 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.005252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.37814 | 0 | 0.027538 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.005252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20483 | 0 | 0.027538 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.005252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15756 | 0 | 0.027538 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.005092 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.69251 | 0 | 0.027378 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.005074 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21311 | 42 | 0.02736 | 1.1491
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.005074 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21311 | 42 | 0.02736 | 1.1491
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.005074 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.19281 | 38 | 0.02736 | 1.0397
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.005074 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.19281 | 38 | 0.02736 | 1.0397
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.005036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.87123 | 0 | 0.027322 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.005036 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.67986 | 0 | 0.027322 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.49681 | 104 | 0.027063 | 2.8145
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.49681 | 104 | 0.027063 | 2.8145
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25796 | 54 | 0.027063 | 1.4614
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25318 | 53 | 0.027063 | 1.4343
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25796 | 54 | 0.027063 | 1.4614
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27229 | 57 | 0.027063 | 1.5426
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25796 | 54 | 0.027063 | 1.4614
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25796 | 54 | 0.027063 | 1.4614
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27707 | 58 | 0.027063 | 1.5696
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27707 | 58 | 0.027063 | 1.5696
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.004666 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 3.4295 | 735 | 0.026952 | 19.8096
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15637 | 0 | 0.026885 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15959 | 0 | 0.026885 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15039 | 0 | 0.026885 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21109 | 0 | 0.026885 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.081402 | 0 | 0.026885 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.09382 | 0 | 0.026885 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.09152 | 0 | 0.026885 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16096 | 0 | 0.026885 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.082782 | 0 | 0.026885 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39275 | 0 | 0.026885 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68065 | 0 | 0.026885 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.00452 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.05424 | 12 | 0.026806 | 0.32167
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28619 | 0 | 0.026689 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2906 | 0 | 0.026689 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30821 | 0 | 0.026689 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27739 | 0 | 0.026689 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27299 | 0 | 0.026689 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.45791 | 0 | 0.026689 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25978 | 0 | 0.026689 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.022015 | 0 | 0.026689 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.092463 | 0 | 0.026689 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.004395 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.05274 | 12 | 0.026681 | 0.32017
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.004387 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 3.2595 | 743 | 0.026673 | 19.818
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.00434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.68138 | 0 | 0.026626 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.004302 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.73994 | 172 | 0.026588 | 4.5731
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.004302 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.73994 | 172 | 0.026588 | 4.5731
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.004302 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.73994 | 172 | 0.026588 | 4.5731
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.004105 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.66829 | 0 | 0.026391 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.004105 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.66255 | 0 | 0.026391 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.004105 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.65228 | 0 | 0.026391 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.004105 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1051 | 0 | 0.026391 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.004043 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.6091 | 398 | 0.026329 | 10.4789
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21952 | 56 | 0.026206 | 1.4675
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.23128 | 59 | 0.026206 | 1.5461
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21952 | 56 | 0.026206 | 1.4675
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21952 | 56 | 0.026206 | 1.4675
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.23128 | 59 | 0.026206 | 1.5461
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21952 | 56 | 0.026206 | 1.4675
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.00276 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.47748 | 0 | 0.025046 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.00276 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.43056 | 0 | 0.025046 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.00276 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.42504 | 0 | 0.025046 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.00276 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.42504 | 0 | 0.025046 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.00276 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.44712 | 0 | 0.025046 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.022286 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.022286 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.022286 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.022286 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.022286 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.022286 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022286 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022286 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 3.3291 | 100 | -0.0012656 | -0.12656
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.016402 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.018155 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.034557 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.034557 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.008206 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.2654 | 0 | -0.042763 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.008206 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.2801 | 0 | -0.042763 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.008206 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.2801 | 0 | -0.042763 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.008206 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.1183 | 0 | -0.042763 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.008531 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2796 | 150 | -0.043088 | -6.4631
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.010702 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.955 | 463 | -0.045259 | -20.9547
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.012179 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.046736 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.016172 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.8271 | 855 | -0.050729 | -43.3729
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.016172 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.8271 | 855 | -0.050729 | -43.3729
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.016172 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.463 | 152.3 | -0.050729 | -7.726
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.016172 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.4743 | 153 | -0.050729 | -7.7615
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.016287 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3681 | 84 | -0.050844 | -4.2709
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.016415 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2557 | 76.5 | -0.050972 | -3.8993
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.016545 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3236 | 80 | -0.051102 | -4.0881
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.017029 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.54493 | 0 | -0.051586 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.017178 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.051735 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.017178 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.051735 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.017178 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.29203 | 17 | -0.051735 | -0.87949
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.017178 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.051735 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.017178 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.051735 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.017308 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5962 | 150 | -0.051865 | -7.7797
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.017308 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5962 | 150 | -0.051865 | -7.7797
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.017328 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3862 | 80 | -0.051885 | -4.1508
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.017332 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3866 | 80 | -0.051889 | -4.1511
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.017365 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3024 | 75 | -0.051922 | -3.8941
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.017365 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3892 | 80 | -0.051922 | -4.1537
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.017365 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.6946 | 40 | -0.051922 | -2.0769
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.017518 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4014 | 80 | -0.052075 | -4.166
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.017518 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4014 | 80 | -0.052075 | -4.166
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.018085 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.086808 | 0 | -0.052642 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.018187 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.0406 | 827 | -0.052744 | -43.6189
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.018187 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -14.8952 | 819 | -0.052744 | -43.197
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.019306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.92669 | 48 | -0.053863 | -2.5854
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.019306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.88808 | 46 | -0.053863 | -2.4777
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.019306 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.0271 | 105 | -0.053863 | -5.6556
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.284 | 66 | -0.054012 | -3.5648
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.2646 | 65 | -0.054012 | -3.5108
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3035 | 67 | -0.054012 | -3.6188
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3035 | 67 | -0.054012 | -3.6188
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3035 | 67 | -0.054012 | -3.6188
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.019455 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.054012 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.019455 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.054012 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.019469 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.3 | 169.5 | -0.054026 | -9.1573
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.019474 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.68159 | 35 | -0.054031 | -1.8911
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.019474 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.58422 | 30 | -0.054031 | -1.6209
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.019538 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9112 | 149 | -0.054095 | -8.0601
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.019646 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.12966 | 6.6 | -0.054203 | -0.35774
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.019646 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.67386 | 34.3 | -0.054203 | -1.8591
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.019756 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2226 | 112.5 | -0.054313 | -6.1102
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.019756 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9535 | 149.5 | -0.054313 | -8.1197
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.019756 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6746 | 186 | -0.054313 | -10.1021
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.019756 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2377 | 214.5 | -0.054313 | -11.65
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.1278 | 208.2 | -0.054383 | -11.3224
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.8173 | 142.1 | -0.054383 | -7.7278
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.625 | 132.4 | -0.054383 | -7.2002
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.6963 | 136 | -0.054383 | -7.396
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.9144 | 147 | -0.054383 | -7.9942
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.1635 | 210 | -0.054383 | -11.4203
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3881 | 70 | -0.054387 | -3.8071
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3881 | 70 | -0.054387 | -3.8071
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.8402 | 92.8 | -0.054387 | -5.0471
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.5864 | 80 | -0.054387 | -4.3509
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.5864 | 80 | -0.054387 | -4.3509
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.2805 | 115 | -0.054387 | -6.2545
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.019835 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9752 | 150 | -0.054392 | -8.1587
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.019845 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.151 | 58 | -0.054402 | -3.1553
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.01985 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.9949 | 100.5 | -0.054407 | -5.4679
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.019896 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2617 | 214.2 | -0.054453 | -11.6637
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.019918 | west | 8 | N | N | Nwest | Nwest | 1 | -0.51388 | 0 | -0.054475 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.020037 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4044 | 120 | -0.054594 | -6.5512
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.020046 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4055 | 120 | -0.054603 | -6.5523
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.020077 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4092 | 120 | -0.054634 | -6.556
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.020077 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.6779 | 233 | -0.054634 | -12.7296
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.020077 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4171 | 170.2 | -0.054634 | -9.2986
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.020085 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5191 | 225 | -0.054642 | -12.2943
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.020096 | west | 8 | N | N | Nwest | Nwest | 1 | -1.4067 | 0 | -0.054653 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.020096 | west | 8 | N | N | Nwest | Nwest | 1 | -1.475 | 0 | -0.054653 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.020096 | west | 8 | N | N | Nwest | Nwest | 1 | -1.4148 | 0 | -0.054653 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.020105 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6189 | 180 | -0.054662 | -9.8391
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.020105 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6189 | 180 | -0.054662 | -9.8391
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.020156 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.0234 | 150 | -0.054713 | -8.2069
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.020156 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4343 | 220 | -0.054713 | -12.0368
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.020156 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0312 | 200 | -0.054713 | -10.9425
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.020156 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.457 | 121.9 | -0.054713 | -6.6695
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3338 | 66 | -0.054766 | -3.6145
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3944 | 69 | -0.054766 | -3.7788
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3944 | 69 | -0.054766 | -3.7788
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.354 | 67 | -0.054766 | -3.6693
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.354 | 67 | -0.054766 | -3.6693
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3136 | 65 | -0.054766 | -3.5598
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.020231 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2746 | 63 | -0.054788 | -3.4516
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.020248 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.855 | 141 | -0.054805 | -7.7274
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.020248 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4298 | 120 | -0.054805 | -6.5765
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.020254 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0051 | 99 | -0.054811 | -5.4262
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.020254 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2355 | 61 | -0.054811 | -3.3434
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.020254 | west | 7 | N | N | Nwest | Nwest | 1 | -0.50635 | 0 | -0.054811 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.020254 | west | 7 | N | N | Nwest | Nwest | 1 | -0.92561 | 0 | -0.054811 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.020254 | west | 7 | N | N | Nwest | Nwest | 1 | -0.92561 | 0 | -0.054811 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.020309 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.706 | 84 | -0.054866 | -4.6087
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.020353 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5441 | 125 | -0.05491 | -6.8637
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.020353 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5441 | 125 | -0.05491 | -6.8637
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.020376 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.0564 | 150 | -0.054933 | -8.2399
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.020376 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.058 | 101 | -0.054933 | -5.5482
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.76744 | 37.5 | -0.055022 | -2.0633
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2 | 107.5 | -0.055022 | -5.9148
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7628 | 135 | -0.055022 | -7.4279
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4353 | 119 | -0.055022 | -6.5476
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.1488 | 105 | -0.055022 | -5.7773
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.6474 | 80.5 | -0.055022 | -4.4292
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.020489 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2822 | 209 | -0.055046 | -11.5045
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.020489 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5919 | 126.5 | -0.055046 | -6.9633
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.020489 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.1018 | 249 | -0.055046 | -13.7063
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.020489 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0363 | 197 | -0.055046 | -10.844
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.020552 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.0828 | 150 | -0.055109 | -8.2663
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.020841 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2505 | 60 | -0.055398 | -3.3239
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.020914 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.8621 | 615 | -0.055471 | -34.1144
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.020914 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.2765 | 587 | -0.055471 | -32.5612
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.021119 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.1826 | 150.7 | -0.055676 | -8.3903
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.021119 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.189 | 151 | -0.055676 | -8.407
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.021119 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7465 | 177.4 | -0.055676 | -9.8768
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.021161 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2059 | 151.5 | -0.055718 | -8.4412
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.021161 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2228 | 152.3 | -0.055718 | -8.4858
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.021161 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7561 | 177.5 | -0.055718 | -9.8899
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.021175 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.47 | 400 | -0.055732 | -22.2926
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.021176 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.9975 | 236 | -0.055733 | -13.1529
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.021405 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.5318 | 165 | -0.055962 | -9.2337
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.021593 | west | 4 | Y | N | Ywest | Nwest | 1 | -14.029 | 649.7 | -0.05615 | -36.4804
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.022078 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.1039 | 50 | -0.056635 | -2.8317
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.022088 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.056645 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.022121 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.026 | 182 | -0.056678 | -10.3153
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.022121 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.7066 | 484 | -0.056678 | -27.4319
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.02213 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.0996 | 366 | -0.056687 | -20.7473
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.022137 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2763 | 0 | -0.056694 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.022137 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.8778 | 0 | -0.056694 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.022137 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2099 | 0 | -0.056694 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.022137 | north | 1 | N | N | Nnorth | Nnorth | 1 | -8.8327 | 0 | -0.056694 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.02215 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.3603 | 242 | -0.056707 | -13.723
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.022178 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.44356 | 20 | -0.056735 | -1.1347
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.022178 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.44356 | 20 | -0.056735 | -1.1347
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.022178 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.44356 | 20 | -0.056735 | -1.1347
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.022178 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.37703 | 17 | -0.056735 | -0.96449
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.022219 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.4419 | 785 | -0.056776 | -44.5688
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.022219 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.6641 | 795 | -0.056776 | -45.1366
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.022219 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.3308 | 780 | -0.056776 | -44.2849
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.022657 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.622 | 204 | -0.057214 | -11.6716
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.022657 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.5541 | 201 | -0.057214 | -11.4999
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.022657 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.483 | 242 | -0.057214 | -13.8457
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.022686 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.7223 | 120 | -0.057243 | -6.8691
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.022698 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27238 | 0 | -0.057255 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.022698 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27238 | 0 | -0.057255 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.6561 | 161 | -0.057266 | -9.2198
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7243 | 164 | -0.057266 | -9.3916
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7243 | 164 | -0.057266 | -9.3916
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.4015 | 414 | -0.057266 | -23.7079
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.6789 | 162 | -0.057266 | -9.277
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.6561 | 161 | -0.057266 | -9.2198
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7016 | 163 | -0.057266 | -9.3343
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.288 | 409 | -0.057266 | -23.4216
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.022832 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.45664 | 20 | -0.057389 | -1.1478
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.022832 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.5708 | 25 | -0.057389 | -1.4347
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.022832 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.93611 | 41 | -0.057389 | -2.3529
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.022835 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.7419 | 558 | -0.057392 | -32.0245
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.022835 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.2215 | 579 | -0.057392 | -33.2297
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.022835 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -18.4507 | 808 | -0.057392 | -46.3724
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.022841 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.8623 | 388 | -0.057398 | -22.2703
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.022841 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.7631 | 515 | -0.057398 | -29.5597
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.022841 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.7131 | 0 | -0.057398 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.022841 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.8181 | 0 | -0.057398 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.022841 | north | 8 | N | N | Nnorth | Nnorth | 1 | -2.0191 | 0 | -0.057398 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.656 | 160 | -0.057407 | -9.185
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5646 | 156 | -0.057407 | -8.9554
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.4786 | 196 | -0.057407 | -11.2517
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5646 | 156 | -0.057407 | -8.9554
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5875 | 157 | -0.057407 | -9.0128
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.5243 | 198 | -0.057407 | -11.3665
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.022851 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.8052 | 79 | -0.057408 | -4.5352
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.022851 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.4222 | 106 | -0.057408 | -6.0852
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.022851 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.3362 | 146 | -0.057408 | -8.3815
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.022851 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.7367 | 76 | -0.057408 | -4.363
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.022859 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.4578 | 370 | -0.057416 | -21.2438
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2003 | 0 | -0.057416 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2231 | 0 | -0.057416 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.0634 | 0 | -0.057416 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2688 | 0 | -0.057416 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2917 | 0 | -0.057416 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.0863 | 0 | -0.057416 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.022863 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.91452 | 40 | -0.05742 | -2.2968
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.022872 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.8882 | 170 | -0.057429 | -9.7629
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.022872 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.8934 | 520 | -0.057429 | -29.8628
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.022884 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.91536 | 0 | -0.057441 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.022884 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.91536 | 0 | -0.057441 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.022892 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.3735 | 60 | -0.057449 | -3.4469
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.022894 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.057451 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.022894 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.057451 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.022924 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.5789 | 112.5 | -0.057481 | -6.4666
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.022949 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.057506 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.022961 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.057518 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.022981 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.3789 | 60 | -0.057538 | -3.4523
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.022981 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4478 | 63 | -0.057538 | -3.6249
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.023058 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.6407 | 288 | -0.057615 | -16.593
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.023058 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.3895 | 147 | -0.057615 | -8.4693
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.023058 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.3895 | 147 | -0.057615 | -8.4693
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.023125 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.7287 | 118 | -0.057682 | -6.8064
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.023125 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.6594 | 115 | -0.057682 | -6.6334
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.023125 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -12.8575 | 556 | -0.057682 | -32.0709
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.023169 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.1899 | 224 | -0.057726 | -12.9305
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.023184 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.057741 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.023184 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.057741 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.023184 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.057741 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.023199 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.41758 | 18 | -0.057756 | -1.0396
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.023199 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.41758 | 18 | -0.057756 | -1.0396
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.023199 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.88156 | 38 | -0.057756 | -2.1947
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.023239 | north | 3 | N | N | Nnorth | Nnorth | 1 | -26.8875 | 0 | -0.057796 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.023239 | north | 3 | N | N | Nnorth | Nnorth | 1 | -26.9108 | 0 | -0.057796 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.023301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.0633 | 217.3 | -0.057858 | -12.5724
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.023301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.7767 | 205 | -0.057858 | -11.8608
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.023301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3472 | 272.4 | -0.057858 | -15.7604
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.023301 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.701 | 73 | -0.057858 | -4.2236
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.023301 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.7728 | 119 | -0.057858 | -6.885
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.023301 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.7767 | 205 | -0.057858 | -11.8608
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.023301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.3767 | 102 | -0.057858 | -5.9015
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.023301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.2369 | 96 | -0.057858 | -5.5543
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.02338 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.057937 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.023506 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -10.2251 | 435 | -0.058063 | -25.2572
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.023531 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.2947 | 395 | -0.058088 | -22.9446
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.023531 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -10.236 | 435 | -0.058088 | -25.2681
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.023589 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.6234 | 196 | -0.058146 | -11.3965
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.023589 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.6184 | 111 | -0.058146 | -6.4542
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.023677 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6574 | 70 | -0.058234 | -4.0763
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.023677 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6337 | 69 | -0.058234 | -4.0181
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.023677 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6337 | 69 | -0.058234 | -4.0181
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.023677 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.61 | 68 | -0.058234 | -3.9599
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.024247 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.2471 | 216.4 | -0.058804 | -12.7251
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.024247 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.2398 | 216.1 | -0.058804 | -12.7074
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.024283 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4394 | 224 | -0.05884 | -13.1801
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.024283 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.488 | 226 | -0.05884 | -13.2977
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.024283 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.148 | 212 | -0.05884 | -12.474
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.024283 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.1237 | 211 | -0.05884 | -12.4151
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.024326 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.0868 | 168 | -0.058883 | -9.8923
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.024326 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.1893 | 90 | -0.058883 | -5.2994
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.029433 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.4415 | 0 | -0.06399 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.029433 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.4415 | 0 | -0.06399 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.03064 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.596 | 150 | -0.065197 | -9.7795
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.03064 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.4512 | 80 | -0.065197 | -5.2157
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.031757 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.098 | 255 | -0.066314 | -16.91
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.031757 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -4.7318 | 149 | -0.066314 | -9.8807
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.031757 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -4.8588 | 153 | -0.066314 | -10.146
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.033067 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.067624 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.033067 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.067624 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.033181 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.067738 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.033181 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -26.1134 | 787 | -0.067738 | -53.3095
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.12216 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -69.5119 | 569 | -0.099879 | -56.8312
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.12216 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -70.9779 | 581 | -0.099879 | -58.0298

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3650 ELGIN_SS 13430 SAND_TXU C:SANDOW__5-L_AUSTRO5_1Y C:L_AUSTRO5_1Y-SAND_TXU_59 [3429 - 7040 ckt1] and [7040 - 13429 ckt2] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.12216 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -69.5119 | 0 | -0.099879 | 0 | 0 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.12216 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -70.9779 | 0 | -0.099879 | 0 | 0 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.033181 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.067738 | 0 | 0 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.033181 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -26.1134 | 787 | -0.067738 | -53.3095 | 787 | 53.3095 | Weighted Shift Factors
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.033067 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.067624 | 0 |  |  | North | -0.022286
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.033067 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.067624 | 0 |  |  | South | 0.034557
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.031757 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.098 | 255 | -0.066314 | -16.91 |  |  |  | -0.056842
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.031757 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -4.7318 | 149 | -0.066314 | -9.8807
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.031757 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -4.8588 | 153 | -0.066314 | -10.146 |  |  | Line Rating | 247.95
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.03064 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.596 | 150 | -0.065197 | -9.7795 |  |  | Conc Gen | 787
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.03064 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.4512 | 80 | -0.065197 | -5.2157 |  |  | Weighted Imp. | 53.3095
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.029433 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.4415 | 0 | -0.06399 | 0 |  |  | PTDF | 0.067738
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.029433 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.4415 | 0 | -0.06399 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.024326 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.0868 | 168 | -0.058883 | -9.8923 |  |  | Concentration | -1.1917
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.024326 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.1893 | 90 | -0.058883 | -5.2994
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.024283 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4394 | 224 | -0.05884 | -13.1801
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.024283 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.488 | 226 | -0.05884 | -13.2977
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.024283 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.148 | 212 | -0.05884 | -12.474
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.024283 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.1237 | 211 | -0.05884 | -12.4151
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.024247 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.2471 | 216.4 | -0.058804 | -12.7251
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.024247 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.2398 | 216.1 | -0.058804 | -12.7074
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.023677 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6574 | 70 | -0.058234 | -4.0763
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.023677 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6337 | 69 | -0.058234 | -4.0181
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.023677 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6337 | 69 | -0.058234 | -4.0181
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.023677 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.61 | 68 | -0.058234 | -3.9599
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.023589 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.6234 | 196 | -0.058146 | -11.3965
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.023589 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.6184 | 111 | -0.058146 | -6.4542
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.023531 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.2947 | 395 | -0.058088 | -22.9446
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.023531 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -10.236 | 435 | -0.058088 | -25.2681
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.023506 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -10.2251 | 435 | -0.058063 | -25.2572
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.02338 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.057937 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.023301 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.701 | 73 | -0.057858 | -4.2236
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.023301 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.7728 | 119 | -0.057858 | -6.885
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.023301 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.7767 | 205 | -0.057858 | -11.8608
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.023301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.3767 | 102 | -0.057858 | -5.9015
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.023301 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.2369 | 96 | -0.057858 | -5.5543
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.023301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.0633 | 217.3 | -0.057858 | -12.5724
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.023301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.7767 | 205 | -0.057858 | -11.8608
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.023301 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3472 | 272.4 | -0.057858 | -15.7604
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.023239 | north | 3 | N | N | Nnorth | Nnorth | 1 | -26.8875 | 0 | -0.057796 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.023239 | north | 3 | N | N | Nnorth | Nnorth | 1 | -26.9108 | 0 | -0.057796 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.023199 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.41758 | 18 | -0.057756 | -1.0396
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.023199 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.41758 | 18 | -0.057756 | -1.0396
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.023199 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.88156 | 38 | -0.057756 | -2.1947
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.023184 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.057741 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.023184 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.057741 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.023184 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.057741 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.023169 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.1899 | 224 | -0.057726 | -12.9305
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.023125 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.7287 | 118 | -0.057682 | -6.8064
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.023125 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.6594 | 115 | -0.057682 | -6.6334
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.023125 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -12.8575 | 556 | -0.057682 | -32.0709
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.023058 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.6407 | 288 | -0.057615 | -16.593
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.023058 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.3895 | 147 | -0.057615 | -8.4693
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.023058 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.3895 | 147 | -0.057615 | -8.4693
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.022981 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.3789 | 60 | -0.057538 | -3.4523
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.022981 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4478 | 63 | -0.057538 | -3.6249
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.022961 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.057518 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.022949 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.057506 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.022924 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.5789 | 0 | -0.057481 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.022894 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.057451 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.022894 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.057451 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.022892 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.3735 | 0 | -0.057449 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.022884 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.91536 | 0 | -0.057441 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.022884 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.91536 | 0 | -0.057441 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.022872 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.8882 | 170 | -0.057429 | -9.7629
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.022872 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.8934 | 520 | -0.057429 | -29.8628
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.022863 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.91452 | 40 | -0.05742 | -2.2968
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.022859 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.4578 | 370 | -0.057416 | -21.2438
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2003 | 0 | -0.057416 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2231 | 0 | -0.057416 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.0634 | 0 | -0.057416 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2688 | 0 | -0.057416 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2917 | 0 | -0.057416 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.022859 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.0863 | 0 | -0.057416 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.022851 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.8052 | 79 | -0.057408 | -4.5352
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.022851 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.4222 | 106 | -0.057408 | -6.0852
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.022851 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.3362 | 146 | -0.057408 | -8.3815
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.022851 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.7367 | 76 | -0.057408 | -4.363
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.656 | 160 | -0.057407 | -9.185
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5646 | 156 | -0.057407 | -8.9554
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.4786 | 196 | -0.057407 | -11.2517
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5646 | 156 | -0.057407 | -8.9554
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5875 | 157 | -0.057407 | -9.0128
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.02285 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.5243 | 198 | -0.057407 | -11.3665
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.022841 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.7131 | 0 | -0.057398 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.022841 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.8181 | 0 | -0.057398 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.022841 | north | 8 | N | N | Nnorth | Nnorth | 1 | -2.0191 | 0 | -0.057398 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.022841 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.8623 | 388 | -0.057398 | -22.2703
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.022841 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.7631 | 515 | -0.057398 | -29.5597
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.022835 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.7419 | 0 | -0.057392 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.022835 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.2215 | 0 | -0.057392 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.022835 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -18.4507 | 0 | -0.057392 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.022832 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.45664 | 20 | -0.057389 | -1.1478
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.022832 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.5708 | 25 | -0.057389 | -1.4347
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.022832 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.93611 | 41 | -0.057389 | -2.3529
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.6561 | 161 | -0.057266 | -9.2198
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7243 | 164 | -0.057266 | -9.3916
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7243 | 164 | -0.057266 | -9.3916
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.4015 | 414 | -0.057266 | -23.7079
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.6789 | 162 | -0.057266 | -9.277
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.6561 | 161 | -0.057266 | -9.2198
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7016 | 163 | -0.057266 | -9.3343
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.022709 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.288 | 409 | -0.057266 | -23.4216
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.022698 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27238 | 0 | -0.057255 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.022698 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27238 | 0 | -0.057255 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.022686 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.7223 | 0 | -0.057243 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.022657 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.622 | 204 | -0.057214 | -11.6716
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.022657 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.5541 | 201 | -0.057214 | -11.4999
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.022657 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.483 | 242 | -0.057214 | -13.8457
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.022219 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.4419 | 0 | -0.056776 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.022219 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.6641 | 0 | -0.056776 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.022219 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -17.3308 | 0 | -0.056776 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.022178 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.44356 | 20 | -0.056735 | -1.1347
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.022178 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.44356 | 20 | -0.056735 | -1.1347
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.022178 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.44356 | 20 | -0.056735 | -1.1347
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.022178 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.37703 | 17 | -0.056735 | -0.96449
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.02215 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.3603 | 242 | -0.056707 | -13.723
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.022137 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2763 | 0 | -0.056694 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.022137 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.8778 | 0 | -0.056694 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.022137 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2099 | 0 | -0.056694 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.022137 | north | 1 | N | N | Nnorth | Nnorth | 1 | -8.8327 | 0 | -0.056694 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.02213 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.0996 | 366 | -0.056687 | -20.7473
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.022121 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.026 | 182 | -0.056678 | -10.3153
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.022121 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.7066 | 484 | -0.056678 | -27.4319
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.022088 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.056645 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.022078 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.1039 | 0 | -0.056635 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.021593 | west | 4 | Y | N | Ywest | Nwest | 1 | -14.029 | 0 | -0.05615 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.021405 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.5318 | 0 | -0.055962 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.021176 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.9975 | 0 | -0.055733 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.021175 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.47 | 0 | -0.055732 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.021161 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2059 | 151.5 | -0.055718 | -8.4412
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.021161 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2228 | 152.3 | -0.055718 | -8.4858
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.021161 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7561 | 177.5 | -0.055718 | -9.8899
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.021119 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.1826 | 150.7 | -0.055676 | -8.3903
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.021119 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.189 | 151 | -0.055676 | -8.407
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.021119 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7465 | 177.4 | -0.055676 | -9.8768
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.020914 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.8621 | 0 | -0.055471 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.020914 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.2765 | 0 | -0.055471 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.020841 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2505 | 0 | -0.055398 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.020552 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.0828 | 0 | -0.055109 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.020489 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2822 | 0 | -0.055046 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.020489 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5919 | 0 | -0.055046 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.020489 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.1018 | 0 | -0.055046 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.020489 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0363 | 0 | -0.055046 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.76744 | 0 | -0.055022 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2 | 0 | -0.055022 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.7628 | 0 | -0.055022 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4353 | 0 | -0.055022 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.1488 | 0 | -0.055022 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.020465 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.6474 | 0 | -0.055022 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.020376 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.0564 | 0 | -0.054933 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.020376 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.058 | 0 | -0.054933 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.020353 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5441 | 0 | -0.05491 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.020353 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5441 | 0 | -0.05491 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.020309 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.706 | 0 | -0.054866 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.020254 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0051 | 0 | -0.054811 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.020254 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2355 | 0 | -0.054811 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.020254 | west | 7 | N | N | Nwest | Nwest | 1 | -0.50635 | 0 | -0.054811 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.020254 | west | 7 | N | N | Nwest | Nwest | 1 | -0.92561 | 0 | -0.054811 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.020254 | west | 7 | N | N | Nwest | Nwest | 1 | -0.92561 | 0 | -0.054811 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.020248 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.855 | 0 | -0.054805 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.020248 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4298 | 0 | -0.054805 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.020231 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2746 | 0 | -0.054788 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3338 | 66 | -0.054766 | -3.6145
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3944 | 69 | -0.054766 | -3.7788
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3944 | 69 | -0.054766 | -3.7788
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.354 | 67 | -0.054766 | -3.6693
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.354 | 67 | -0.054766 | -3.6693
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.020209 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3136 | 65 | -0.054766 | -3.5598
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.020156 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.0234 | 0 | -0.054713 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.020156 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4343 | 0 | -0.054713 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.020156 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0312 | 0 | -0.054713 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.020156 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.457 | 0 | -0.054713 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.020105 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6189 | 0 | -0.054662 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.020105 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6189 | 0 | -0.054662 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.020096 | west | 8 | N | N | Nwest | Nwest | 1 | -1.4067 | 0 | -0.054653 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.020096 | west | 8 | N | N | Nwest | Nwest | 1 | -1.475 | 0 | -0.054653 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.020096 | west | 8 | N | N | Nwest | Nwest | 1 | -1.4148 | 0 | -0.054653 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.020085 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5191 | 0 | -0.054642 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.020077 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4092 | 0 | -0.054634 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.020077 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.6779 | 0 | -0.054634 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.020077 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4171 | 0 | -0.054634 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.020046 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4055 | 0 | -0.054603 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.020037 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.4044 | 0 | -0.054594 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.019918 | west | 8 | N | N | Nwest | Nwest | 1 | -0.51388 | 0 | -0.054475 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.019896 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2617 | 0 | -0.054453 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.01985 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.9949 | 0 | -0.054407 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.019845 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.151 | 0 | -0.054402 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.019835 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9752 | 0 | -0.054392 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3881 | 70 | -0.054387 | -3.8071
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.3881 | 70 | -0.054387 | -3.8071
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.8402 | 92.8 | -0.054387 | -5.0471
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.5864 | 80 | -0.054387 | -4.3509
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 1 | -1.5864 | 80 | -0.054387 | -4.3509
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.01983 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.2805 | 115 | -0.054387 | -6.2545
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.1278 | 208.2 | -0.054383 | -11.3224
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.8173 | 142.1 | -0.054383 | -7.7278
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.625 | 132.4 | -0.054383 | -7.2002
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.6963 | 136 | -0.054383 | -7.396
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.9144 | 147 | -0.054383 | -7.9942
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.019826 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.1635 | 210 | -0.054383 | -11.4203
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.019756 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2226 | 0 | -0.054313 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.019756 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9535 | 0 | -0.054313 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.019756 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.6746 | 0 | -0.054313 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.019756 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2377 | 0 | -0.054313 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.019646 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.12966 | 0 | -0.054203 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.019646 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.67386 | 0 | -0.054203 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.019538 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9112 | 0 | -0.054095 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.019474 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.68159 | 0 | -0.054031 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.019474 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.58422 | 0 | -0.054031 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.019469 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.3 | 0 | -0.054026 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.284 | 66 | -0.054012 | -3.5648
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.2646 | 65 | -0.054012 | -3.5108
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3035 | 67 | -0.054012 | -3.6188
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3035 | 67 | -0.054012 | -3.6188
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.019455 | west | 13 | Y | Y | Ywest | Ywest | 1 | -1.3035 | 67 | -0.054012 | -3.6188
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.019455 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.054012 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.019455 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.054012 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.019306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.92669 | 48 | -0.053863 | -2.5854
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.019306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.88808 | 46 | -0.053863 | -2.4777
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.019306 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.0271 | 105 | -0.053863 | -5.6556
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.018187 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.0406 | 0 | -0.052744 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.018187 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -14.8952 | 0 | -0.052744 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.018085 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.086808 | 0 | -0.052642 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.017518 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4014 | 0 | -0.052075 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.017518 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4014 | 0 | -0.052075 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.017365 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3024 | 0 | -0.051922 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.017365 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3892 | 0 | -0.051922 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.017365 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.6946 | 0 | -0.051922 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.017332 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3866 | 0 | -0.051889 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.017328 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3862 | 0 | -0.051885 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.017308 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5962 | 0 | -0.051865 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.017308 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5962 | 0 | -0.051865 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.017178 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.051735 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.017178 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.051735 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.017178 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.29203 | 17 | -0.051735 | -0.87949
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.017178 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.051735 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.017178 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.051735 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.017029 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.54493 | 0 | -0.051586 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.016545 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3236 | 0 | -0.051102 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.016415 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2557 | 0 | -0.050972 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.016287 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3681 | 0 | -0.050844 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.016172 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.8271 | 0 | -0.050729 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.016172 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.8271 | 0 | -0.050729 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.016172 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.463 | 0 | -0.050729 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.016172 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.4743 | 0 | -0.050729 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.012179 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.046736 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.010702 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -4.955 | 0 | -0.045259 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.008531 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.2796 | 0 | -0.043088 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.008206 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.2654 | 0 | -0.042763 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.008206 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.2801 | 0 | -0.042763 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.008206 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.2801 | 0 | -0.042763 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.008206 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.1183 | 0 | -0.042763 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.034557 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.034557 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.016402 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.018155 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 3.3291 | 0 | -0.0012656 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.022286 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.022286 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.022286 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.022286 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.022286 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.022286 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022286 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022286 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.00276 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.47748 | 0 | 0.025046 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.00276 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.43056 | 0 | 0.025046 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.00276 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.42504 | 0 | 0.025046 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.00276 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.42504 | 0 | 0.025046 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.00276 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.44712 | 0 | 0.025046 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21952 | 56 | 0.026206 | 1.4675
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.23128 | 59 | 0.026206 | 1.5461
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21952 | 56 | 0.026206 | 1.4675
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21952 | 56 | 0.026206 | 1.4675
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.23128 | 59 | 0.026206 | 1.5461
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.00392 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21952 | 56 | 0.026206 | 1.4675
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.004043 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.6091 | 398 | 0.026329 | 10.4789
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.004105 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.66829 | 0 | 0.026391 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.004105 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.66255 | 0 | 0.026391 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.004105 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.65228 | 0 | 0.026391 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.004105 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1051 | 0 | 0.026391 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.004302 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.73994 | 172 | 0.026588 | 4.5731
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.004302 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.73994 | 172 | 0.026588 | 4.5731
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.004302 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.73994 | 172 | 0.026588 | 4.5731
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.00434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.68138 | 0 | 0.026626 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.004387 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 3.2595 | 743 | 0.026673 | 19.818
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.004395 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.05274 | 0 | 0.026681 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.022015 | 0 | 0.026689 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.092463 | 0 | 0.026689 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28619 | 0 | 0.026689 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2906 | 0 | 0.026689 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30821 | 0 | 0.026689 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27739 | 0 | 0.026689 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27299 | 0 | 0.026689 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.45791 | 0 | 0.026689 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.004403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25978 | 0 | 0.026689 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.00452 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.05424 | 12 | 0.026806 | 0.32167
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15637 | 0 | 0.026885 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15959 | 0 | 0.026885 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15039 | 0 | 0.026885 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21109 | 0 | 0.026885 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.081402 | 0 | 0.026885 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.09382 | 0 | 0.026885 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.09152 | 0 | 0.026885 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16096 | 0 | 0.026885 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.082782 | 0 | 0.026885 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39275 | 0 | 0.026885 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.004599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68065 | 0 | 0.026885 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.004666 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 3.4295 | 735 | 0.026952 | 19.8096
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.49681 | 104 | 0.027063 | 2.8145
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.49681 | 104 | 0.027063 | 2.8145
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25796 | 54 | 0.027063 | 1.4614
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25318 | 53 | 0.027063 | 1.4343
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25796 | 54 | 0.027063 | 1.4614
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27229 | 57 | 0.027063 | 1.5426
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25796 | 54 | 0.027063 | 1.4614
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25796 | 54 | 0.027063 | 1.4614
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27707 | 58 | 0.027063 | 1.5696
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.004777 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.27707 | 58 | 0.027063 | 1.5696
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.005036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.87123 | 0 | 0.027322 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.005036 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.67986 | 0 | 0.027322 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.005074 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21311 | 42 | 0.02736 | 1.1491
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.005074 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21311 | 42 | 0.02736 | 1.1491
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.005074 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.19281 | 38 | 0.02736 | 1.0397
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.005074 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.19281 | 38 | 0.02736 | 1.0397
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.005092 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.69251 | 0 | 0.027378 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.005252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.37289 | 0 | 0.027538 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.005252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.37814 | 0 | 0.027538 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.005252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20483 | 0 | 0.027538 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.005252 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15756 | 0 | 0.027538 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.005357 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.96426 | 0 | 0.027643 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.005357 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.84962 | 0 | 0.027643 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.005357 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.84105 | 0 | 0.027643 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.005359 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.2219 | 228 | 0.027645 | 6.303
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.005361 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3431 | 0 | 0.027647 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.005361 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33882 | 0 | 0.027647 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.005361 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.44282 | 0 | 0.027647 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.005361 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39457 | 0 | 0.027647 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.005362 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.086864 | 0 | 0.027648 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.005364 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.1425 | 213 | 0.02765 | 5.8894
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.00538 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80162 | 0 | 0.027666 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.00538 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35024 | 0 | 0.027666 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.005384 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.88836 | 165 | 0.02767 | 4.5655
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.00539 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.91091 | 169 | 0.027676 | 4.6772
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.005394 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.064728 | 12 | 0.02768 | 0.33216
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.005394 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.02768 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.005469 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19142 | 0 | 0.027755 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90217 | 0 | 0.027814 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.86845 | 0 | 0.027814 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.87066 | 0 | 0.027814 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.8679 | 0 | 0.027814 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.005528 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.487 | 0 | 0.027814 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.005618 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.4382 | 0 | 0.027904 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.005618 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.44944 | 0 | 0.027904 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.2616 | 46 | 0.027973 | 1.2868
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.2616 | 46 | 0.027973 | 1.2868
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.2616 | 46 | 0.027973 | 1.2868
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.31278 | 55 | 0.027973 | 1.5385
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.31278 | 55 | 0.027973 | 1.5385
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.005687 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.3071 | 54 | 0.027973 | 1.5105
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.005923 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38499 | 0 | 0.028209 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.005923 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.35538 | 0 | 0.028209 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.005923 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38499 | 0 | 0.028209 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.005923 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.38499 | 0 | 0.028209 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55401 | 0 | 0.028374 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.53331 | 0 | 0.028374 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52966 | 0 | 0.028374 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3318 | 0 | 0.028374 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.006088 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.074274 | 0 | 0.028374 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.006504 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.02879 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.006883 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.34415 | 50 | 0.029169 | 1.4584
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.007323 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.51847 | 0 | 0.029609 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.007323 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.48844 | 0 | 0.029609 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.007323 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.38812 | 0 | 0.029609 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1219 | 0 | 0.029609 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1241 | 0 | 0.029609 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1153 | 0 | 0.029609 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.70301 | 0 | 0.029609 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.007323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7868 | 0 | 0.029609 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.007323 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29292 | 0 | 0.029609 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.007328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2345 | 0 | 0.029614 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.007328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21984 | 0 | 0.029614 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.007329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.7351 | 0 | 0.029615 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.007329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.68086 | 0 | 0.029615 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.007329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.75269 | 0 | 0.029615 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.007329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.74756 | 0 | 0.029615 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.008543 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.3754 | 161 | 0.030829 | 4.9635
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.008543 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.4181 | 166 | 0.030829 | 5.1176
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.008543 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.1187 | 248 | 0.030829 | 7.6456
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.008543 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 4.6645 | 546 | 0.030829 | 16.8326
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.008543 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 5.4931 | 0 | 0.030829 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.008543 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11106 | 13 | 0.030829 | 0.40078
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.008579 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28311 | 0 | 0.030865 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.008765 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4287 | 0 | 0.031051 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.008765 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4287 | 0 | 0.031051 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.008765 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.1474 | 0 | 0.031051 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.008783 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.7177 | 0 | 0.031069 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.008783 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.9536 | 0 | 0.031069 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.008783 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.2698 | 0 | 0.031069 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.008902 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.41038 | 0 | 0.031188 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.011105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2327 | 0 | 0.033391 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.011105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2327 | 0 | 0.033391 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.011105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3215 | 0 | 0.033391 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.011105 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.216 | 0 | 0.033391 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.011621 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.82509 | 0 | 0.033907 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.011621 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11621 | 0 | 0.033907 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.76254 | 0 | 0.034585 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.87815 | 0 | 0.034585 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55346 | 0 | 0.034585 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2422 | 0 | 0.034585 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0577 | 0 | 0.034585 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0823 | 0 | 0.034585 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61495 | 0 | 0.034585 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22138 | 0 | 0.034585 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1561 | 0 | 0.034585 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.86093 | 0 | 0.034585 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77484 | 0 | 0.034585 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.88553 | 0 | 0.034585 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79698 | 0 | 0.034585 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2422 | 0 | 0.034585 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.193 | 0 | 0.034585 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2668 | 0 | 0.034585 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.93472 | 0 | 0.034585 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.98392 | 0 | 0.034585 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.98392 | 0 | 0.034585 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.012299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.1031 | 0 | 0.034585 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.015746 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.0392 | 66 | 0.038032 | 2.5101
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.015927 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.52559 | 0 | 0.038213 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.015927 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.39818 | 0 | 0.038213 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.015927 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.038213 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.016409 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 21.8732 | 0 | 0.038695 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.016409 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 21.7912 | 0 | 0.038695 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.2822 | 76 | 0.039157 | 2.9759
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.2822 | 76 | 0.039157 | 2.9759
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.7715 | 105 | 0.039157 | 4.1115
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.2485 | 74 | 0.039157 | 2.8976
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.2485 | 74 | 0.039157 | 2.8976
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.016871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.7208 | 102 | 0.039157 | 3.994
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.019834 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.119 | 0 | 0.04212 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.020743 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.043029 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9662 | 0 | 0.047174 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.0159 | 0 | 0.047174 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9662 | 0 | 0.047174 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.991 | 0 | 0.047174 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9512 | 0 | 0.047174 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.6222 | 0 | 0.047174 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1448 | 0 | 0.047174 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.69686 | 0 | 0.047174 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0851 | 0 | 0.047174 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.024888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8417 | 0 | 0.047174 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.025113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2054 | 0 | 0.047399 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.72313 | 0 | 0.048112 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.18078 | 0 | 0.048112 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0072 | 0 | 0.048112 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.38739 | 0 | 0.048112 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.18078 | 0 | 0.048112 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.38739 | 0 | 0.048112 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0072 | 0 | 0.048112 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.025826 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0072 | 0 | 0.048112 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.025911 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.20729 | 0 | 0.048197 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.026145 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.39217 | 0 | 0.048431 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.026145 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.60133 | 0 | 0.048431 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.026289 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.57836 | 22 | 0.048575 | 1.0686
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.026289 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28918 | 11 | 0.048575 | 0.53432
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.026289 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.28918 | 11 | 0.048575 | 0.53432
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.1707 | 0 | 0.048683 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.0387 | 0 | 0.048683 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -1 | 2.6397 | 0 | 0.048683 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.8276 | 0 | 0.048683 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.8804 | 0 | 0.048683 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.026397 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.3524 | 0 | 0.048683 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.026397 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.31676 | 0 | 0.048683 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66235 | 0 | 0.04878 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66235 | 0 | 0.04878 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66235 | 0 | 0.04878 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.4239 | 0 | 0.04878 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66235 | 0 | 0.04878 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66235 | 0 | 0.04878 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.66235 | 0 | 0.04878 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.026494 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.39741 | 0 | 0.04878 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.026573 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.2675 | 47.7 | 0.048859 | 2.3306
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.026573 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.99117 | 37.3 | 0.048859 | 1.8224
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.026573 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.2224 | 46 | 0.048859 | 2.2475
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.026573 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.2755 | 48 | 0.048859 | 2.3452
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.026657 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.9568 | 336 | 0.048943 | 16.4448
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.026657 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7983 | 180 | 0.048943 | 8.8097
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.02666 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.9537 | 0 | 0.048946 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.02666 | south | 8 | N | N | Nsouth | Nsouth | -1 | 3.9617 | 0 | 0.048946 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.02666 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.079 | 0 | 0.048946 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.026665 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.7997 | 180 | 0.048951 | 8.8112
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.026712 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.9218 | 334 | 0.048998 | 16.3653
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.026712 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 9.0821 | 340 | 0.048998 | 16.6593
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.026712 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8082 | 180 | 0.048998 | 8.8196
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.026712 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8082 | 180 | 0.048998 | 8.8196
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.026732 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.6683 | 0 | 0.049018 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.026732 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.6683 | 0 | 0.049018 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.026749 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9527 | 0 | 0.049035 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.026751 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0165 | 0 | 0.049037 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.026763 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.017 | 0 | 0.049049 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.026861 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.77897 | 0 | 0.049147 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.5278 | 0 | 0.049178 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.1026 | 0 | 0.049178 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.0219 | 0 | 0.049178 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.51095 | 0 | 0.049178 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.5278 | 0 | 0.049178 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.96811 | 0 | 0.049178 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.1564 | 0 | 0.049178 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.59162 | 0 | 0.049178 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.98 | 0 | 0.049178 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.3446 | 0 | 0.049178 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.4791 | 0 | 0.049178 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.026892 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.3446 | 0 | 0.049178 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.02691 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0226 | 38 | 0.049196 | 1.8694
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.02691 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.51936 | 19.3 | 0.049196 | 0.94948
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.02691 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.40365 | 15 | 0.049196 | 0.73794
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.02691 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.2648 | 47 | 0.049196 | 2.3122
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.02691 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.049196 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.026958 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.882 | 144 | 0.049244 | 7.0911
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.026958 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.882 | 144 | 0.049244 | 7.0911
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.026958 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.6098 | 171 | 0.049244 | 8.4207
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.026959 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.5805 | 207 | 0.049245 | 10.1937
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.026959 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.842 | 216.7 | 0.049245 | 10.6714
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.026959 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.5241 | 242 | 0.049245 | 11.9173
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.027008 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9567 | 146.5 | 0.049294 | 7.2216
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.027008 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.9945 | 147.9 | 0.049294 | 7.2906
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.027008 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.6724 | 173 | 0.049294 | 8.5278
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.027079 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 3.8994 | 144 | 0.049365 | 7.1085
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.027079 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.0909 | 188 | 0.049365 | 9.2806
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.027318 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.32782 | 0 | 0.049604 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.027318 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.3005 | 0 | 0.049604 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.027318 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.32782 | 0 | 0.049604 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.027337 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.049623 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.027455 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.49419 | 0 | 0.049741 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.027455 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.49419 | 0 | 0.049741 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.027455 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.41182 | 0 | 0.049741 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.027613 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.049899 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.028015 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 17.6214 | 0 | 0.050301 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.028184 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.23675 | 8.4 | 0.05047 | 0.42395
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.028287 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050573 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.02829 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.829 | 100 | 0.050576 | 5.0576
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.02829 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.829 | 100 | 0.050576 | 5.0576
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.02829 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050576 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.02829 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050576 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.02829 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050576 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.02829 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050576 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.028353 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.38844 | 0 | 0.050639 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.028395 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.050681 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.028499 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.68398 | 24 | 0.050785 | 1.2188
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.028499 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.68398 | 24 | 0.050785 | 1.2188
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.028499 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.65548 | 23 | 0.050785 | 1.1681
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.030121 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 11.9279 | 0 | 0.052407 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.031755 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 17.3382 | 0 | 0.054041 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.031755 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 23.8163 | 0 | 0.054041 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.031832 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8463 | 58 | 0.054118 | 3.1388
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.031832 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.833 | 89 | 0.054118 | 4.8165
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.031832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4006 | 44 | 0.054118 | 2.3812
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.031832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4006 | 44 | 0.054118 | 2.3812
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.031832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.3688 | 43 | 0.054118 | 2.3271
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.031832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4324 | 45 | 0.054118 | 2.4353
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.031901 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.9447 | 155 | 0.054187 | 8.399
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.031901 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.4232 | 170 | 0.054187 | 9.2118
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.031901 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.9447 | 155 | 0.054187 | 8.399
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.031906 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 13.4643 | 422 | 0.054192 | 22.869
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.031989 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 13.0195 | 407 | 0.054275 | 22.0899
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.032062 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 13.5943 | 0 | 0.054348 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.032062 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 13.6264 | 0 | 0.054348 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.032064 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.7014 | 209 | 0.05435 | 11.3591
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.032064 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 6.9258 | 216 | 0.05435 | 11.7396
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.032064 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4749 | 46 | 0.05435 | 2.5001
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.032064 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.507 | 47 | 0.05435 | 2.5544
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.032064 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4749 | 46 | 0.05435 | 2.5001
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.032064 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 1.4749 | 46 | 0.05435 | 2.5001
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.03208 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 13.217 | 412 | 0.054366 | 22.3987
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.03208 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 12.832 | 400 | 0.054366 | 21.7464
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.032137 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.89984 | 0 | 0.054423 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.032137 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.93197 | 0 | 0.054423 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.032165 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.054451 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.032165 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.054451 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.032165 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.054451 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8242 | 147 | 0.055104 | 8.1003
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.5289 | 138 | 0.055104 | 7.6043
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.5945 | 140 | 0.055104 | 7.7145
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8242 | 147 | 0.055104 | 8.1003
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.9729 | 182 | 0.055104 | 10.0289
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.032818 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.498 | 198 | 0.055104 | 10.9106
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.7952 | 0 | 0.055577 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.3906 | 0 | 0.055577 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 6.1255 | 0 | 0.055577 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.4572 | 0 | 0.055577 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.033291 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 3.8285 | 0 | 0.055577 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.033998 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.8277 | 142 | 0.056284 | 7.9923
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.033998 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 4.9297 | 145 | 0.056284 | 8.1612
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.033998 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.1337 | 151 | 0.056284 | 8.4989
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.033998 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.8594 | 290 | 0.056284 | 16.3223
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.034003 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13601 | 0 | 0.056289 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.034605 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.41526 | 0 | 0.056891 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.035064 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.63115 | 0 | 0.05735 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.035064 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.63115 | 0 | 0.05735 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.035192 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.8795 | 223.9 | 0.057478 | 12.8693
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.035192 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.9182 | 225 | 0.057478 | 12.9325
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.035192 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.9041 | 224.6 | 0.057478 | 12.9095
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.035192 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.978 | 226.7 | 0.057478 | 13.0302
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.035409 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.084982 | 0 | 0.057695 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.035409 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.084982 | 0 | 0.057695 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.035409 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.099145 | 0 | 0.057695 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.036677 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.088025 | 0 | 0.058963 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.036677 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.088025 | 0 | 0.058963 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.036779 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 15.9253 | 0 | 0.059065 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.03682 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 21.5029 | 0 | 0.059106 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.03682 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 21.9079 | 0 | 0.059106 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.037245 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22347 | 0 | 0.059531 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.039065 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.1723 | 158 | 0.061351 | 9.6934
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.039065 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.2504 | 160 | 0.061351 | 9.8161
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.039065 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.8364 | 175 | 0.061351 | 10.7364
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.03983 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.0741 | 152.5 | 0.062116 | 9.4727
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.03983 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 5.9546 | 149.5 | 0.062116 | 9.2863
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.03983 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.2645 | 232.6 | 0.062116 | 14.4482
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.042227 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.4779 | 0 | 0.064513 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.042227 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.4357 | 0 | 0.064513 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.042227 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.4779 | 0 | 0.064513 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.2256 | 49 | 0.067706 | 3.3176
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.0893 | 46 | 0.067706 | 3.1145
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.0893 | 46 | 0.067706 | 3.1145
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.1347 | 47 | 0.067706 | 3.1822
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.04542 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.9947 | 154 | 0.067706 | 10.4267
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.04542 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.7222 | 148 | 0.067706 | 10.0205
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.1802 | 48 | 0.067706 | 3.2499
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.04542 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.1802 | 48 | 0.067706 | 3.2499
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.046464 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.37171 | 0 | 0.06875 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.046464 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.37171 | 0 | 0.06875 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.046657 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 14.4637 | 310 | 0.068943 | 21.3723
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.046657 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 19.2693 | 413 | 0.068943 | 28.4734
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.04825 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.0265 | 42 | 0.070536 | 2.9625
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.04825 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.123 | 44 | 0.070536 | 3.1036
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.04825 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.123 | 44 | 0.070536 | 3.1036
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.04825 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.2677 | 47 | 0.070536 | 3.3152
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.049411 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4705 | 50 | 0.071697 | 3.5848
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.049411 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4705 | 50 | 0.071697 | 3.5848
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.049411 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4705 | 50 | 0.071697 | 3.5848
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.049411 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.4705 | 50 | 0.071697 | 3.5848
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.064481 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.5115 | 132 | 0.086767 | 11.4532
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.064481 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.6405 | 134 | 0.086767 | 11.6268
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.064481 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 20.8274 | 323 | 0.086767 | 28.0257

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 268
| 25 | 268
| 30 | 268
| 35 | 268
| 40 | 268
| 45 | 268
| 50 | 268
| 55 | 268
| 60 | 267
| 65 | 261
| 70 | 256
| 75 | 250
| 80 | 245
| 85 | 239
| 90 | 233
| 95 | 226
| 100 | 220
| 105 | 213
| 110 | 206
| 115 | 199
| Max | 268
| Min | 199
| Avg | 247.95