## test results
CRE test for: |  | 3409 LAKE_CRK 3414 TEMP_SS_ctg2 | [5 empty] | PASS
Line Rating: |  | 1239.6
Direcction |  | North | → | South |  | N-S
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3409 LAKE_CRK 3414 TEMP_SS_ctg2
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.13953
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.1892
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.12426
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.038241
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3409 LAKE_CRK 3414 TEMP_SS_ctg2
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.15001
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.1857
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.12486
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.035353
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3409 LAKE_CRK 3414 TEMP_SS_ctg2
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.32523
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.014674
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.17488
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.31405
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.15096
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.15961
PTDF tests
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.32523 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.32523 | 0.32523
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.37627
[6 empty] | Concentration |  | 1.1569 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.37421
[6 empty] | Concentration |  | 1.1506 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 269.5269
| Percent of line rating => | [6 empty] | 21.74% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 1.2358
[7 empty] | B1(N-S) | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B2 (N-W) | -0.0015206 | 0.016614 | 0.018134 | -0.0015206
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.0030271 | 0.21915 | 0.21612 | 0.0030271
[7 empty] | B4 (S-W) | -0.0014702 | -0.38958 | -0.38811 | -0.0014702
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.00049079 | -0.18705 | -0.18656 | -0.00049079
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.0045448 | 0.20179 | 0.19725 | 0.0045448
[7 empty] | test | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B1 | 0%
Deployment Error Percent | [6 empty] | B2 | -0.3783%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0.7532%
[7 empty] | B4 | -0.3658%
[7 empty] | B5 | -0.1221%
[7 empty] | B6 | 1.131%
[7 empty] | Max Abs Error | 1.131% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-S
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3409 LAKE_CRK 3414 TEMP_SS_ctg2 C:THOUSE__5-LAKE_CRK1_5 C:THOUSE__5-AEP_PEC__59 [3405 - 3409] and [3405 - 3412] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3409 LAKE_CRK 3414 TEMP_SS_ctg2 C:THOUSE__5-LAKE_CRK1_5 C:THOUSE__5-AEP_PEC__59 [3405 - 3409] and [3405 - 3412]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.19162 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 48.8641
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.19162 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 28.552
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.15871 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.3807
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.15871 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.3807
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.19162 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 29.3185
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.1621 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 24.3154
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.1621 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 12.9682
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14271 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 10.4176
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14271 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 16.9821
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14271 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 29.2549
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14271 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 14.5561
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.14271 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 13.6999
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.14161 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.6993
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.14161 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.6993
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.15096 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 25.3604
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.15096 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 13.586
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.1446 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.6029
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.1446 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.6029
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.1446 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 5.495
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.14494 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 41.7436
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.14494 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 21.3066
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.14494 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 21.3066
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.14494 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 16.306
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.14477 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 5.7909
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14476 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 11.4364
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14476 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 15.345
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14476 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 21.1355
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.14476 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 11.0021
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.14589 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 8.7536
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.14589 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 9.1913
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.1446 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 2.892
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.1446 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 3.615
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.1446 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 5.9286
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.055959 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 25.909
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 8.0523
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 7.9303
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.1743
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.1743
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 8.1743
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.122 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 13.9085
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.122 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 62.8321
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 8.3511
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.7307
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.7307
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.4776
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 8.4776
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 8.2246
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12589 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 8.8125
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12589 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 9.2405
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.12589 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 8.8629
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12626 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 18.9392
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12626 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 27.7774
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12678 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 12.5515
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12678 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 7.7338
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.12675 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 17.8712
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12678 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 3.1696
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12678 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.794
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.12678 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.794
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.12675 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 15.2095
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.12464 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 3.2157
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.12435 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 12.4974
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.12545 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 15.0534
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.12433 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 7.2113
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.12464 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 26.6979
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.12717 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 19.0759
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12275 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.81013
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.12275 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 4.2102
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.12717 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 12.8445
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.1255 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 15.0599
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.13969 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 51.1269
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.13884 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 33.5988
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.13303 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 53.212
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.13304 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 31.3972
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.13464 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 22.2149
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.14352 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 29.2787
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.14352 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 28.8481
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.14352 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 34.7326
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13978 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.7956
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13978 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.7956
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13978 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.7956
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.13978 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 2.3762
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.14144 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 16.973
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.13623 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 8.1737
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.14477 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 10.8577
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.14477 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 11.5236
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.14477 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 12.7976
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 23.1782
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 22.5988
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 28.3933
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 22.5988
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 22.7436
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 28.6831
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.14503 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 24.6553
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.14503 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 75.4161
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14495 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 53.6315
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14474 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 80.7638
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14474 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 83.8033
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.14474 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 116.9483
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.1473 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 16.498
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.1473 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 14.7304
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.1473 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 55.6809
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.14773 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 32.1009
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.14773 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 30.2838
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.14773 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 40.2406
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.14821 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 114.1186
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.14754 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 10.3279
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.14754 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 10.1804
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.14754 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 10.1804
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.14754 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 10.0329
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.14707 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 170.1623
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.14707 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 170.3094
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.15691 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 35.1469
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.15691 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 35.4608
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.15739 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 34.0594
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.15739 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 34.0122
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.15691 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 33.2641
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.15691 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 33.1072
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.15033 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 59.3815
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.15007 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 65.28
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.15033 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 65.3949
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.14572 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 20.1096
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14722 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 17.3718
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14722 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 16.9302
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.14722 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 81.8538
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.14484 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 56.1968
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.14484 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 74.5911
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.13954 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 109.5405
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.13954 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 110.9359
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.13954 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 108.8428
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.13753 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 25.0305
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.13753 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 66.5645
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.14118 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 31.6236
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.13826 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 6.9129
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.13829 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 5.8083
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.13196 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 81.1536
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.13196 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 77.4588
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.23563 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 126.5322
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.23563 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 185.4392
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.1779 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 13.3423
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.1779 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 39.4931
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.28306 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -161.0583
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18036 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -37.6957
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18036 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -38.9582
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.18028 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -73.3756
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18036 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -8.2967
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18036 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -8.477
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18036 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -8.2967
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.18036 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -8.2967
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.1807 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -76.6181
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.1807 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -76.7988
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.17927 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -10.3975
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.17927 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -15.9548
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.17927 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -7.8877
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.17927 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -7.8877
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.17927 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -7.7085
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.17927 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -8.067
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.18057 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -74.3948
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.18057 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -72.228
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.17898 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -97.7225
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.17898 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -134.2343
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.18122 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -11.0547
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.18122 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -17.2163
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.18122 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -27.3648
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.17991 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -27.8861
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.17991 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -30.5847
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.17991 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -27.8861
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.14405 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -3.1691
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.14405 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.5846
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.14405 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.5846
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.14541 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -6.9361
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.14541 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -5.4238
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.14541 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -6.6889
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.14541 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -6.9797
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.15224 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.8268
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.15224 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -1.6746
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.15942 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.8261
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.15942 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.8261
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.15942 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -3.6667
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.16909 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -66.9596
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.091159 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -121.5149
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.091159 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -121.0592
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.14971 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -5.6889
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.14971 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -2.8894
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.14971 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -2.2456
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.14971 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -7.0363
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.10939 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 8.2043
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.12855 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 19.2827
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.12135 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 20.5685
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.055321 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 8.2981
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.12664 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 7.9782
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.13584 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 88.2539
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.14512 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.8047
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.14512 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.8047
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.2028 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -85.5799
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.22729 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -30.0023
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.22729 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -30.4569
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.22729 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -73.4147
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.22987 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -36.3195
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.22987 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -36.7792
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.22987 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -40.2272
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.2042 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -119.2505
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.2042 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -121.4966
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.20399 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -88.3272
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.19955 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -44.6783
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.19955 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -44.8978
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.19955 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -44.818
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.19955 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -45.2371
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.23658 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.8926
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.23658 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.8926
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.20109 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -3.6197
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.20109 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -3.6197
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.20109 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -3.0164
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.19826 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -2.7162
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.21066 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -3.7918
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.21066 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -3.7918
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.22849 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -7.997
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.22849 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -7.7686
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.22849 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -7.997
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.20433 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -5.7211
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.20433 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -5.9254
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.12212 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 4.2741
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.12212 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 3.6635
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.20642 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -10.3211
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.20642 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -10.3211
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.20642 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -10.3211
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.20642 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -10.3211
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.20459 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -1.2275
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.19302 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.46325
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.19302 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.46325
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.19302 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.54045
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.19019 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.76074
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.19032 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.45678
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.19032 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.45678
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -27.242
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -25.5742
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -25.9448
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -27.242
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -33.7282
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -36.6934
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.23152 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -35.3073
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.23152 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -34.6127
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.23152 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -53.8522
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.19225 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -27.2992
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.19225 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -27.876
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.19225 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -29.0294
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.19225 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -55.7519
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.086262 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -2.8466
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.086262 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -2.1566
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.15224 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.8268
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.14573 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -10.638
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -10.7308
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -11.0025
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -3.9503
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.98757
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -10.7308
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -10.8666
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -10.6493
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -3.3958
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -6.2483
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.15466 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -97.2805
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.14742 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -21.2283
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.14742 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -27.7148
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.1785 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -2.142
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.109 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.65402
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.14806 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -49.7472
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.14841 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -49.5683
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.14841 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -50.4587
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.14863 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -5.6478
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.14846 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.7116
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.14846 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.7116
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.14861 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -5.6474
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.14936 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -4.3314
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.14808 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -21.9595
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.14808 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -22.0039
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.14808 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -22.6555
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -23.1432
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -22.4108
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -14.6476
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -21.239
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -21.532
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -18.6025
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.15032 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -22.0216
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.15032 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -22.232
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.15032 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -26.005
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -31.0523
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -32.5074
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -36.3027
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -21.6009
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -21.6009
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -25.651
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.23759 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -73.6538
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.23759 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -98.1259
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.24016 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -10.0867
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.24016 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -10.567
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.24016 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -10.567
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.24016 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -11.2875
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -11.5108
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -10.8061
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -10.8061
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -11.041
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23492 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -36.1769
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23492 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -34.7674
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -11.2759
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -11.2759
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.6996
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.6996
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 11.5332
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 9.9424
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 9.9424
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 14.2922
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 25.8705
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 17.6571
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 16.4518
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 16.8991
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 18.2659
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 26.0942
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12847 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 26.8504
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12847 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 16.2516
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12847 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 31.9893
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.12847 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 25.3088
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12626 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 25.2522
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.12626 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 15.3912
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.1225 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 18.2526
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12589 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 22.6597
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.12589 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 22.6597
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.12577 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 28.2976
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.12752 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 15.9406
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.12752 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 15.9406
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 20.293
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 20.438
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 44.7895
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 20.7279
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 20.8728
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 44.9345
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.14664 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 28.742
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.14664 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 16.2774
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.14583 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 23.1489
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 23.5802
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 23.5802
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 59.5257
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 23.2927
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 23.1489
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 23.4365
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 58.8068
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.14535 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.14535 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13903 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 20.5767
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13903 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 18.0742
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13903 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 20.1596
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.13903 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 55.4738
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.13327 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 20.0841
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.13327 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 20.1241
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.13327 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 23.6425
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.13344 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 20.2163
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.13344 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 20.3231
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.13344 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 23.6858
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.28306 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -164.455
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.094903 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 81.1421
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.094903 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 81.1421
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.046607 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 1.4914
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.042415 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 2.0359
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.042415 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 1.9511
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.046689 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.56027
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.046689 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 2.3811
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.046689 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.79371
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.046689 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 1.0272
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.046689 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 1.1672
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.042415 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 4.4536
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.12711 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 10.6773
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.10916 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 8.7332
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.10905 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 16.3572
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.10905 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 16.3572
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040414 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -2.8613
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040414 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -2.6956
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040414 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -2.1419
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -6.1914
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -6.2035
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -6.1551
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -3.8797
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -9.861
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040414 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -1.6166
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.040447 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -4.0568
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.040447 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -3.7575
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.040447 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -4.1539
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.040447 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -4.1256
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.040446 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -1.2943
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.040446 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -1.2134
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.060736 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -6.7417
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.060736 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -6.7417
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.060736 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -7.2276
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.060736 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -6.6506
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.094903 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 14.4537
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.094903 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 14.5202
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.028047 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -3.8144
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.047183 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -1.557
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.027975 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.1749
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.027975 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.1749
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.027975 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.0631
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.027975 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.0631
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.063994 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -4.5436
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.063994 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.63994
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.048419 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -7.8923
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.048419 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -7.8923
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.048419 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -11.8627
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.032665 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.1232
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.032665 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -1.9599
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.032665 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.1232
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.032665 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.1232
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.029653 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -4.4183
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.029653 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -1.9304
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -3.0551
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -2.9409
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -2.9208
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -1.8297
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.40958
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.024196 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -17.9776
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.02573 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -18.9115
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.023734 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.0822
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.023734 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.0822
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.023734 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.0822
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.015225 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -2.6339
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.027743 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -4.7995
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.027743 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -3.7453
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.02265 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -3.6874
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.02265 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -3.6557
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.02265 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -3.5991
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.02265 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -6.0974
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.029553 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -1.8914
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.029553 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -1.8677
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.029553 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -2.4411
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.029553 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -2.1751
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -4.9799
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -4.7937
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -4.806
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -4.7907
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -8.2083
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.024277 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.12139
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.024277 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.50982
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.044771 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 6.9037
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.044771 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 6.9843
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.044771 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 6.9843
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.044771 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 17.013
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.022274 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -8.8651
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.4405
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.4405
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.4405
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -1.7224
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -1.7224
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -1.6911
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.11176 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 92.423
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.11176 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 91.529
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.048944 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -2.2563
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -6.8802
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -6.8802
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -9.5055
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -6.6991
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -6.6991
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -9.234
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.029524 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -5.3143
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.029524 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -4.6825
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.029524 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -4.6353
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.030137 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -1.0548
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.035886 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -16.4717
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -1.5774
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -1.6016
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -1.6987
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -1.5288
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -1.5046
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -2.5238
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -1.4318
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.015225 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -2.3751
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.015225 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -2.3447
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.015225 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -2.3447
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.015225 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -2.4665
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.023916 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -3.7548
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.028953 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -2.0557
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.028953 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -2.0846
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.028953 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -1.1292
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.028953 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.86859
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.030979 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -2.4164
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.030979 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -2.4783
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.02956 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.47887
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.029678 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -4.8969
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.02971 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -5.021
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.02957 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -6.2984
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.029538 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -6.7347
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.029732 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.35678
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.029732 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.53518
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.03787 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -1.8935
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.7341
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.7341
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4196
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -1.3933
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4196
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -1.4985
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4196
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4196
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.5248
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.5248
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.024881 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.29857
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.2103
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.2752
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.2103
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.2103
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.2752
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.2103
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.085133 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -5.6188
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.046651 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -7.5108
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.046651 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -7.7441
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.046651 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -11.5694
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.046651 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -25.4714
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.046651 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -29.9966
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.048518 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -31.5852
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.048518 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -27.3642
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.048518 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -29.1108
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.046651 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.60646
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.024238 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.29086
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.86214
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.87989
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.82917
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -1.1639
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.44882
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.51728
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.5046
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.8875
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.45643
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -2.1655
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -3.7528
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -4.2233
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -4.8636
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -3.0653
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -6.8798
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -5.8581
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -5.9943
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -3.4059
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -1.2261
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -6.403
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -4.7682
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -4.2914
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -4.9044
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -4.414
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -6.8798
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -6.6073
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -7.0161
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -5.1769
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.4494
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.4494
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -11.648
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.3239
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.10365 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 7.9295
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.10939 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 8.7513
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.10939 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 4.3756
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.11031 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 8.8247
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.10919 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 8.7354
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.10446 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 8.3565
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.10291 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 8.6442
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.11031 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 8.8247
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -21.562
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12529 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 15.0353
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12529 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 29.1935
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.12529 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 21.325
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -41.9891
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -34.8018
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -42.3674
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -21.7511
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -18.914
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.1304 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 7.824
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.099921 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.078216 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.11374 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.54593
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 4.8066
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 13.779
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 17.3039
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 15.2531
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 13.4586
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 10.3182
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.12389 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 18.5838
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12333 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 13.8742
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12333 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 18.4372
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12333 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 22.9386
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.12333 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 26.4534
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.14971 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.11429 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.15819 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -3.8033
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -5.9223
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -10.0516
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -14.0627
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -6.1337
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -5.6849
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -2.8425
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -14.0627
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -5.3857
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -6.4329
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -3.2913
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.5022
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -2.1162
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.98757
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -2.1162
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.5022
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.5022
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -22.1412
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -7.4802
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -8.2282
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -7.4802
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.14648 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -1.7577
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.14276 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -2.1414
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.14276 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -3.2835
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.13707 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -6.5793
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.14168 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -1.1334
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.1481 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -26.6589
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.14806 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -26.6503
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.14841 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -26.7134
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.14841 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -26.7134
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1582 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -15.8202
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1582 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -15.8202
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.6775
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.6775
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.6775
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -2.3536
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.6775
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.6775
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.6775
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -2.2065
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1582 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1582 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -79.101
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1582 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -79.101
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1582 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.15679 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.086262 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.15407 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.15224 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L:3409 LAKE_CRK 3414 TEMP_SS_ctg2 C:THOUSE__5-LAKE_CRK1_5 C:THOUSE__5-AEP_PEC__59 [3405 - 3409] and [3405 - 3412] | [7 empty] | 269.5269
Number of Bus | Name of Bus | ID | Max MW | L:3409 LAKE_CRK 3414 TEMP_SS_ctg2 C:THOUSE__5-LAKE_CRK1_5 C:THOUSE__5-AEP_PEC__59 [3405 - 3409] and [3405 - 3412] | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.19162 | north | 0.052093 | 0.38082 | 0.067367 | 0.22986 | 0.052093 | North | N | 0.052093 | 0
239 | BOSQUESW | 1 | 149 | 0.19162 | north | 0.052093 | 0.38082 | 0.067367 | 0.22986 | 0.052093 | North | N | 0.052093 | 0
244 | WHITNYDM | 1 | 15 | 0.15871 | north | 0.019182 | 0.34791 | 0.034456 | 0.19695 | 0.019182 | North | N | 0.019182 | 0
245 | WHITNYDM | 2 | 15 | 0.15871 | north | 0.019182 | 0.34791 | 0.034456 | 0.19695 | 0.019182 | North | N | 0.019182 | 0
247 | BOSQUESW | 2 | 153 | 0.19162 | north | 0.052093 | 0.38082 | 0.067367 | 0.22986 | 0.052093 | North | N | 0.052093 | 0
251 | BOSQUESW | 2 | 150 | 0.1621 | north | 0.022572 | 0.3513 | 0.037846 | 0.20034 | 0.022572 | North | N | 0.022572 | 0
253 | BOSQUESW | 2 | 80 | 0.1621 | north | 0.022572 | 0.3513 | 0.037846 | 0.20034 | 0.022572 | North | N | 0.022572 | 0
332 | RWMILLER | 1 | 73 | 0.14271 | north | 0.0031762 | 0.3319 | 0.01845 | 0.18095 | 0.0031762 | North | N | 0.0031762 | 0
333 | RWMILLER | 2 | 119 | 0.14271 | north | 0.0031762 | 0.3319 | 0.01845 | 0.18095 | 0.0031762 | North | N | 0.0031762 | 0
334 | RWMILLER | 3 | 205 | 0.14271 | north | 0.0031762 | 0.3319 | 0.01845 | 0.18095 | 0.0031762 | North | N | 0.0031762 | 0
335 | RWMILLER | 4 | 102 | 0.14271 | north | 0.0031762 | 0.3319 | 0.01845 | 0.18095 | 0.0031762 | North | N | 0.0031762 | 0
336 | RWMILLER | 5 | 96 | 0.14271 | north | 0.0031762 | 0.3319 | 0.01845 | 0.18095 | 0.0031762 | North | N | 0.0031762 | 0
344 | MRSSHPRD | 1 | 12 | 0.14161 | north | 0.0020812 | 0.33081 | 0.017355 | 0.17985 | 0.0020812 | North | N | 0.0020812 | 0
345 | MRSSHPRD | 2 | 12 | 0.14161 | north | 0.0020812 | 0.33081 | 0.017355 | 0.17985 | 0.0020812 | North | N | 0.0020812 | 0
366 | JNSNCNTY | 1 | 168 | 0.15096 | north | 0.011424 | 0.34015 | 0.026698 | 0.1892 | 0.011424 | North | N | 0.011424 | 0
367 | JNSNCNTY | 2 | 90 | 0.15096 | north | 0.011424 | 0.34015 | 0.026698 | 0.1892 | 0.011424 | North | N | 0.011424 | 0
503 | NTHTEXAS | 1 | 18 | 0.1446 | north | 0.0050732 | 0.3338 | 0.020347 | 0.18284 | 0.0050732 | North | N | 0.0050732 | 0
504 | NTHTEXAS | 2 | 18 | 0.1446 | north | 0.0050732 | 0.3338 | 0.020347 | 0.18284 | 0.0050732 | North | N | 0.0050732 | 0
505 | NTHTEXAS | 3 | 38 | 0.1446 | north | 0.0050732 | 0.3338 | 0.020347 | 0.18284 | 0.0050732 | North | N | 0.0050732 | 0
580 | JCKCNTY8 | 1 | 288 | 0.14494 | north | 0.0054122 | 0.33414 | 0.020686 | 0.18318 | 0.0054122 | North | N | 0.0054122 | 0
581 | JCKCNTY8 | 2 | 147 | 0.14494 | north | 0.0054122 | 0.33414 | 0.020686 | 0.18318 | 0.0054122 | North | N | 0.0054122 | 0
582 | JCKCNTY8 | 3 | 147 | 0.14494 | north | 0.0054122 | 0.33414 | 0.020686 | 0.18318 | 0.0054122 | North | N | 0.0054122 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.14494 | north | 0.0054112 | 0.33414 | 0.020685 | 0.18318 | 0.0054112 | North | N | 0.0054112 | 0
837 | NEWMAN_G | 1 | 40 | 0.14477 | north | 0.0052412 | 0.33397 | 0.020515 | 0.18301 | 0.0052412 | North | N | 0.0052412 | 0
842 | OLINGER_ | 1 | 79 | 0.14476 | north | 0.0052332 | 0.33396 | 0.020507 | 0.183 | 0.0052332 | North | N | 0.0052332 | 0
843 | OLINGER_ | 1 | 106 | 0.14476 | north | 0.0052332 | 0.33396 | 0.020507 | 0.183 | 0.0052332 | North | N | 0.0052332 | 0
844 | OLINGER_ | 1 | 146 | 0.14476 | north | 0.0052332 | 0.33396 | 0.020507 | 0.183 | 0.0052332 | North | N | 0.0052332 | 0
845 | OLINGER_ | 1 | 76 | 0.14476 | north | 0.0052332 | 0.33396 | 0.020507 | 0.183 | 0.0052332 | North | N | 0.0052332 | 0
923 | SPENCER_ | 1 | 60 | 0.14589 | north | 0.0063622 | 0.33509 | 0.021636 | 0.18413 | 0.0063622 | North | N | 0.0063622 | 0
924 | SPENCER_ | 1 | 63 | 0.14589 | north | 0.0063622 | 0.33509 | 0.021636 | 0.18413 | 0.0063622 | North | N | 0.0063622 | 0
948 | STEAM1 | 1 | 20 | 0.1446 | north | 0.0050692 | 0.3338 | 0.020343 | 0.18284 | 0.0050692 | North | N | 0.0050692 | 0
949 | STEAM2 | 1 | 25 | 0.1446 | north | 0.0050702 | 0.3338 | 0.020344 | 0.18284 | 0.0050702 | North | N | 0.0050702 | 0
950 | STEAM3 | 1 | 41 | 0.1446 | north | 0.0050702 | 0.3338 | 0.020344 | 0.18284 | 0.0050702 | North | N | 0.0050702 | 0
990 | GIBN_CRE | 1 | 463 | 0.055959 | north | -0.083572 | 0.24516 | -0.068298 | 0.0942 | 0.068298 | west | Y | 0.083572 | 7.0717
1002 | PBCTAGE_ | A | 66 | 0.122 | west | -0.017527 | 0.3112 | -0.0022531 | 0.16024 | 0.0022531 | west | N | 0.0022531 | 0
1003 | PBCTBGE_ | B | 65 | 0.122 | west | -0.017527 | 0.3112 | -0.0022531 | 0.16024 | 0.0022531 | west | N | 0.0022531 | 0
1004 | PBCTCGE_ | C | 67 | 0.122 | west | -0.017527 | 0.3112 | -0.0022531 | 0.16024 | 0.0022531 | west | N | 0.0022531 | 0
1005 | PBCTDGE_ | D | 67 | 0.122 | west | -0.017527 | 0.3112 | -0.0022531 | 0.16024 | 0.0022531 | west | N | 0.0022531 | 0
1006 | PBCTEGE_ | E | 67 | 0.122 | west | -0.017527 | 0.3112 | -0.0022531 | 0.16024 | 0.0022531 | west | N | 0.0022531 | 0
1007 | PB5GEN_6 | MB | 114 | 0.122 | west | -0.017527 | 0.3112 | -0.0022531 | 0.16024 | 0.0022531 | west | N | 0.0022531 | 0
1008 | PB6GEN_7 | MB | 515 | 0.122 | west | -0.017527 | 0.3112 | -0.0022531 | 0.16024 | 0.0022531 | west | N | 0.0022531 | 0
1039 | MRGNAG_1 | A | 66 | 0.12653 | west | -0.012999 | 0.31573 | 0.0022749 | 0.16477 | 0.0022749 | west | N | 0.0022749 | 0
1040 | MRGNBG_2 | B | 69 | 0.12653 | west | -0.012999 | 0.31573 | 0.0022749 | 0.16477 | 0.0022749 | west | N | 0.0022749 | 0
1041 | MRGNCG_3 | C | 69 | 0.12653 | west | -0.012999 | 0.31573 | 0.0022749 | 0.16477 | 0.0022749 | west | N | 0.0022749 | 0
1042 | MRGNDG_4 | D | 67 | 0.12653 | west | -0.012999 | 0.31573 | 0.0022749 | 0.16477 | 0.0022749 | west | N | 0.0022749 | 0
1043 | MRGNEG_5 | E | 67 | 0.12653 | west | -0.012999 | 0.31573 | 0.0022749 | 0.16477 | 0.0022749 | west | N | 0.0022749 | 0
1044 | MRGNFG_6 | F | 65 | 0.12653 | west | -0.012999 | 0.31573 | 0.0022749 | 0.16477 | 0.0022749 | west | N | 0.0022749 | 0
1045 | CALENG1G | 1 | 70 | 0.12589 | west | -0.013638 | 0.31509 | 0.0016359 | 0.16413 | 0.0016359 | west | N | 0.0016359 | 0
1046 | CALENG2G | 2 | 73.4 | 0.12589 | west | -0.013638 | 0.31509 | 0.0016359 | 0.16413 | 0.0016359 | west | N | 0.0016359 | 0
1047 | CALENG3G | 3 | 70.4 | 0.12589 | west | -0.013638 | 0.31509 | 0.0016359 | 0.16413 | 0.0016359 | west | N | 0.0016359 | 0
1058 | LONGSHOR | 1 | 150 | 0.12626 | west | -0.01327 | 0.31546 | 0.0020039 | 0.1645 | 0.0020039 | west | N | 0.0020039 | 0
1058 | LONGSHOR | 2 | 220 | 0.12626 | west | -0.01327 | 0.31546 | 0.0020039 | 0.1645 | 0.0020039 | west | N | 0.0020039 | 0
1061 | CIELOGEN | 1 | 99 | 0.12678 | west | -0.012748 | 0.31598 | 0.0025259 | 0.16502 | 0.0025259 | west | N | 0.0025259 | 0
1062 | CIELOGEN | 1 | 61 | 0.12678 | west | -0.012748 | 0.31598 | 0.0025259 | 0.16502 | 0.0025259 | west | N | 0.0025259 | 0
1068 | SCURRYCW | 1 | 141 | 0.12675 | west | -0.012785 | 0.31594 | 0.0024889 | 0.16499 | 0.0024889 | west | N | 0.0024889 | 0
1069 | KINDERMG | 1 | 25 | 0.12678 | west | -0.012748 | 0.31598 | 0.0025259 | 0.16502 | 0.0025259 | west | N | 0.0025259 | 0
1070 | KINDERMG | 1 | 45.7 | 0.12678 | west | -0.012748 | 0.31598 | 0.0025259 | 0.16502 | 0.0025259 | west | N | 0.0025259 | 0
1071 | KINDERMG | 1 | 45.7 | 0.12678 | west | -0.012748 | 0.31598 | 0.0025259 | 0.16502 | 0.0025259 | west | N | 0.0025259 | 0
1073 | SCURRYCW | 2 | 120 | 0.12675 | west | -0.012785 | 0.31594 | 0.0024889 | 0.16499 | 0.0024889 | west | N | 0.0024889 | 0
1320 | BSP 1 | 1 | 25.8 | 0.12464 | west | -0.014893 | 0.31384 | 0.00038091 | 0.16288 | 0.00038091 | west | N | 0.00038091 | 0
1326 | STANTONW | 1 | 100.5 | 0.12435 | west | -0.015179 | 0.31355 | 9.4909e-05 | 0.16259 | 9.4909e-05 | west | N | 9.4909e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.12545 | west | -0.014086 | 0.31464 | 0.0011879 | 0.16369 | 0.0011879 | west | N | 0.0011879 | 0
1328 | OCOTILLO | 1 | 58 | 0.12433 | west | -0.015199 | 0.31353 | 7.4909e-05 | 0.16257 | 7.4909e-05 | west | N | 7.4909e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.12464 | west | -0.014891 | 0.31384 | 0.00038291 | 0.16288 | 0.00038291 | west | N | 0.00038291 | 0
1343 | TRENTIPP | 1 | 150 | 0.12717 | west | -0.012358 | 0.31637 | 0.0029159 | 0.16541 | 0.0029159 | west | N | 0.0029159 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.12275 | west | -0.016784 | 0.31194 | -0.0015101 | 0.16099 | 0.0015101 | west | N | 0.0015101 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.12275 | west | -0.016784 | 0.31194 | -0.0015101 | 0.16099 | 0.0015101 | west | N | 0.0015101 | 0
1354 | AEPWIND_ | 1 | 101 | 0.12717 | west | -0.012358 | 0.31637 | 0.0029159 | 0.16541 | 0.0029159 | west | N | 0.0029159 | 0
1360 | GUNSIGHT | 1 | 120 | 0.1255 | west | -0.014032 | 0.3147 | 0.0012419 | 0.16374 | 0.0012419 | west | N | 0.0012419 | 0
1432 | GRHAMSES | 2 | 366 | 0.13969 | north | 0.00016019 | 0.32889 | 0.015434 | 0.17793 | 0.00016019 | North | N | 0.00016019 | 0
1433 | GRHAMSES | 1 | 242 | 0.13884 | north | -0.00069281 | 0.32804 | 0.014581 | 0.17708 | 0.00069281 | North | N | 0.00069281 | 0
1437 | MESQUITW | 1 | 400 | 0.13303 | west | -0.0065008 | 0.32223 | 0.0087729 | 0.17127 | 0.0065008 | North | Y | 0.0087729 | 0.90884
1438 | MESQUITW | 1 | 236 | 0.13304 | west | -0.0064918 | 0.32224 | 0.0087819 | 0.17128 | 0.0064918 | North | Y | 0.0087819 | 0.54046
1442 | COKFIELD | 1 | 165 | 0.13464 | west | -0.0048948 | 0.32383 | 0.010379 | 0.17288 | 0.0048948 | North | Y | 0.010379 | 0.90488
1453 | WCPWRCO_ | 1 | 204 | 0.14352 | north | 0.0039922 | 0.33272 | 0.019266 | 0.18176 | 0.0039922 | North | N | 0.0039922 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.14352 | north | 0.0039922 | 0.33272 | 0.019266 | 0.18176 | 0.0039922 | North | N | 0.0039922 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.14352 | north | 0.0039922 | 0.33272 | 0.019266 | 0.18176 | 0.0039922 | North | N | 0.0039922 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.13978 | west | 0.00024819 | 0.32898 | 0.015522 | 0.17802 | 0.00024819 | North | Y | 0.015522 | 0.30547
1479 | WFCOGEN_ | 2 | 20 | 0.13978 | west | 0.00024819 | 0.32898 | 0.015522 | 0.17802 | 0.00024819 | North | Y | 0.015522 | 0.30547
1482 | WFCOGEN_ | 1 | 20 | 0.13978 | west | 0.00024819 | 0.32898 | 0.015522 | 0.17802 | 0.00024819 | North | Y | 0.015522 | 0.30547
1482 | WFCOGEN_ | 2 | 17 | 0.13978 | west | 0.00024819 | 0.32898 | 0.015522 | 0.17802 | 0.00024819 | North | Y | 0.015522 | 0.25965
1600 | BARTNWND | 1 | 120 | 0.14144 | north | 0.0019112 | 0.33064 | 0.017185 | 0.17968 | 0.0019112 | North | N | 0.0019112 | 0
1643 | SLSTR1PP | 1 | 60 | 0.13623 | north | -0.0033018 | 0.32543 | 0.011972 | 0.17447 | 0.0033018 | North | N | 0.0033018 | 0
1675 | PEC_1G | 1 | 75 | 0.14477 | north | 0.0052382 | 0.33397 | 0.020512 | 0.18301 | 0.0052382 | North | N | 0.0052382 | 0
1676 | PEC_2G | 2 | 79.6 | 0.14477 | north | 0.0052382 | 0.33397 | 0.020512 | 0.18301 | 0.0052382 | North | N | 0.0052382 | 0
1677 | PEC_3G | 3 | 88.4 | 0.14477 | north | 0.0052382 | 0.33397 | 0.020512 | 0.18301 | 0.0052382 | North | N | 0.0052382 | 0
1678 | LAMARPWR | 1 | 160 | 0.14486 | north | 0.0053332 | 0.33406 | 0.020607 | 0.1831 | 0.0053332 | North | N | 0.0053332 | 0
1679 | LAMARPWR | 2 | 156 | 0.14486 | north | 0.0053332 | 0.33406 | 0.020607 | 0.1831 | 0.0053332 | North | N | 0.0053332 | 0
1680 | LAMARPWR | 3 | 196 | 0.14486 | north | 0.0053332 | 0.33406 | 0.020607 | 0.1831 | 0.0053332 | North | N | 0.0053332 | 0
1681 | LAMARPWR | 4 | 156 | 0.14486 | north | 0.0053332 | 0.33406 | 0.020607 | 0.1831 | 0.0053332 | North | N | 0.0053332 | 0
1682 | LAMARPWR | 5 | 157 | 0.14486 | north | 0.0053332 | 0.33406 | 0.020607 | 0.1831 | 0.0053332 | North | N | 0.0053332 | 0
1683 | LAMARPWR | 6 | 198 | 0.14486 | north | 0.0053332 | 0.33406 | 0.020607 | 0.1831 | 0.0053332 | North | N | 0.0053332 | 0
1687 | VALLEY_1 | 1 | 170 | 0.14503 | north | 0.0055002 | 0.33423 | 0.020774 | 0.18327 | 0.0055002 | North | N | 0.0055002 | 0
1688 | VALLEY_2 | 2 | 520 | 0.14503 | north | 0.0055002 | 0.33423 | 0.020774 | 0.18327 | 0.0055002 | North | N | 0.0055002 | 0
1689 | VALLEY_3 | 3 | 370 | 0.14495 | north | 0.0054192 | 0.33415 | 0.020693 | 0.18319 | 0.0054192 | North | N | 0.0054192 | 0
1701 | MOSES_1G | 1 | 558 | 0.14474 | north | 0.0052072 | 0.33394 | 0.020481 | 0.18298 | 0.0052072 | North | N | 0.0052072 | 0
1702 | MOSES_2G | 2 | 579 | 0.14474 | north | 0.0052072 | 0.33394 | 0.020481 | 0.18298 | 0.0052072 | North | N | 0.0052072 | 0
1703 | MOSES_3G | 3 | 808 | 0.14474 | north | 0.0052072 | 0.33394 | 0.020481 | 0.18298 | 0.0052072 | North | N | 0.0052072 | 0
1861 | EAGLEMNT | MB | 112 | 0.1473 | north | 0.0077732 | 0.3365 | 0.023047 | 0.18554 | 0.0077732 | North | N | 0.0077732 | 0
1862 | EAGLEMNT | MB | 100 | 0.1473 | north | 0.0077732 | 0.3365 | 0.023047 | 0.18554 | 0.0077732 | North | N | 0.0077732 | 0
1863 | EAGLEMNT | MB | 378 | 0.1473 | north | 0.0077732 | 0.3365 | 0.023047 | 0.18554 | 0.0077732 | North | N | 0.0077732 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.14773 | north | 0.0081952 | 0.33692 | 0.023469 | 0.18597 | 0.0081952 | North | N | 0.0081952 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.14773 | north | 0.0081952 | 0.33692 | 0.023469 | 0.18597 | 0.0081952 | North | N | 0.0081952 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.14773 | north | 0.0081952 | 0.33692 | 0.023469 | 0.18597 | 0.0081952 | North | N | 0.0081952 | 0
1889 | DECRDOVA | MB | 770 | 0.14821 | north | 0.0086752 | 0.3374 | 0.023949 | 0.18645 | 0.0086752 | North | N | 0.0086752 | 0
1892 | DECRDOVA | A | 70 | 0.14754 | north | 0.0080112 | 0.33674 | 0.023285 | 0.18578 | 0.0080112 | North | N | 0.0080112 | 0
1893 | DECRDOVA | B | 69 | 0.14754 | north | 0.0080112 | 0.33674 | 0.023285 | 0.18578 | 0.0080112 | North | N | 0.0080112 | 0
1894 | DECRDOVA | C | 69 | 0.14754 | north | 0.0080112 | 0.33674 | 0.023285 | 0.18578 | 0.0080112 | North | N | 0.0080112 | 0
1895 | DECRDOVA | D | 68 | 0.14754 | north | 0.0080112 | 0.33674 | 0.023285 | 0.18578 | 0.0080112 | North | N | 0.0080112 | 0
1898 | COMCHEPK | 1 | 1157 | 0.14707 | north | 0.0075412 | 0.33627 | 0.022815 | 0.18531 | 0.0075412 | North | N | 0.0075412 | 0
1899 | COMCHEPK | 2 | 1158 | 0.14707 | north | 0.0075412 | 0.33627 | 0.022815 | 0.18531 | 0.0075412 | North | N | 0.0075412 | 0
1937 | MDLTHELP | 5 | 224 | 0.15691 | north | 0.017375 | 0.3461 | 0.032649 | 0.19515 | 0.017375 | North | N | 0.017375 | 0
1938 | MDLTHELP | 6 | 226 | 0.15691 | north | 0.017375 | 0.3461 | 0.032649 | 0.19515 | 0.017375 | North | N | 0.017375 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.15739 | north | 0.01786 | 0.34659 | 0.033134 | 0.19563 | 0.01786 | North | N | 0.01786 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.15739 | north | 0.01786 | 0.34659 | 0.033134 | 0.19563 | 0.01786 | North | N | 0.01786 | 0
1943 | MDLTHELP | 3 | 212 | 0.15691 | north | 0.017375 | 0.3461 | 0.032649 | 0.19515 | 0.017375 | North | N | 0.017375 | 0
1944 | MDLTHELP | 4 | 211 | 0.15691 | north | 0.017375 | 0.3461 | 0.032649 | 0.19515 | 0.017375 | North | N | 0.017375 | 0
1947 | HANDLEY_ | 3 | 395 | 0.15033 | north | 0.010802 | 0.33953 | 0.026076 | 0.18857 | 0.010802 | North | N | 0.010802 | 0
1948 | HANDLEY_ | 4 | 435 | 0.15007 | north | 0.010538 | 0.33927 | 0.025812 | 0.18831 | 0.010538 | North | N | 0.010538 | 0
1949 | HANDLEY_ | 5 | 435 | 0.15033 | north | 0.010802 | 0.33953 | 0.026076 | 0.18857 | 0.010802 | North | N | 0.010802 | 0
2371 | COLLIN_1 | MB | 138 | 0.14572 | north | 0.0061912 | 0.33492 | 0.021465 | 0.18396 | 0.0061912 | North | N | 0.0061912 | 0
2413 | MTCK6_G | 6 | 118 | 0.14722 | north | 0.0076882 | 0.33642 | 0.022962 | 0.18546 | 0.0076882 | North | N | 0.0076882 | 0
2414 | MTCK7_G | 7 | 115 | 0.14722 | north | 0.0076882 | 0.33642 | 0.022962 | 0.18546 | 0.0076882 | North | N | 0.0076882 | 0
2417 | MTCK8_G | 8 | 556 | 0.14722 | north | 0.0076882 | 0.33642 | 0.022962 | 0.18546 | 0.0076882 | North | N | 0.0076882 | 0
2451 | LKHB1_G | 1 | 388 | 0.14484 | north | 0.0053062 | 0.33403 | 0.02058 | 0.18308 | 0.0053062 | North | N | 0.0053062 | 0
2452 | LKHB2_G | 2 | 515 | 0.14484 | north | 0.0053062 | 0.33403 | 0.02058 | 0.18308 | 0.0053062 | North | N | 0.0053062 | 0
3097 | MARTLAKE | 1 | 785 | 0.13954 | north | 1.1192e-05 | 0.32874 | 0.015285 | 0.17778 | 1.1192e-05 | North | N | 1.1192e-05 | 0
3098 | MARTLAKE | 2 | 795 | 0.13954 | north | 1.1192e-05 | 0.32874 | 0.015285 | 0.17778 | 1.1192e-05 | North | N | 1.1192e-05 | 0
3099 | MARTLAKE | 3 | 780 | 0.13954 | north | 1.1192e-05 | 0.32874 | 0.015285 | 0.17778 | 1.1192e-05 | North | N | 1.1192e-05 | 0
3107 | STRYKER_ | 1 | 182 | 0.13753 | north | -0.0020008 | 0.32673 | 0.013273 | 0.17577 | 0.0020008 | North | N | 0.0020008 | 0
3108 | STRYKER_ | 2 | 484 | 0.13753 | north | -0.0020008 | 0.32673 | 0.013273 | 0.17577 | 0.0020008 | North | N | 0.0020008 | 0
3126 | TRINIDAD | 1 | 224 | 0.14118 | north | 0.0016462 | 0.33037 | 0.01692 | 0.17942 | 0.0016462 | North | N | 0.0016462 | 0
3309 | ASPN_G | 1 | 50 | 0.13826 | north | -0.0012728 | 0.32746 | 0.014001 | 0.1765 | 0.0012728 | North | N | 0.0012728 | 0
3348 | CHAMPION | MB | 42 | 0.13829 | north | -0.0012378 | 0.32749 | 0.014036 | 0.17653 | 0.0012378 | North | N | 0.0012378 | 0
3381 | BBRN_1G | 1 | 615 | 0.13196 | north | -0.0075738 | 0.32115 | 0.0076999 | 0.1702 | 0.0075738 | North | N | 0.0075738 | 0
3382 | BBRN_2G | 2 | 587 | 0.13196 | north | -0.0075738 | 0.32115 | 0.0076999 | 0.1702 | 0.0075738 | North | N | 0.0075738 | 0
3403 | THOUSE_1 | MB | 537 | 0.23563 | north | 0.096097 | 0.42483 | 0.11137 | 0.27387 | 0.096097 | North | N | 0.096097 | 0
3404 | THOUSE_2 | 2 | 787 | 0.23563 | north | 0.096097 | 0.42483 | 0.11137 | 0.27387 | 0.096097 | North | N | 0.096097 | 0
3416 | LAKE_CRK | MB | 75 | 0.1779 | north | 0.038366 | 0.36709 | 0.05364 | 0.21614 | 0.038366 | North | N | 0.038366 | 0
3417 | LAKE_CRK | MB | 222 | 0.1779 | north | 0.038366 | 0.36709 | 0.05364 | 0.21614 | 0.038366 | North | N | 0.038366 | 0
3432 | SANDOW_4 | 4 | 569 | -0.28306 | south | -0.42259 | -0.093857 | -0.40731 | -0.24481 | 0.093857 | south | N | 0.093857 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.18036 | south | -0.31989 | 0.0088358 | -0.30462 | -0.14212 | 0.0088358 | south | N | 0.0088358 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.18036 | south | -0.31989 | 0.0088358 | -0.30462 | -0.14212 | 0.0088358 | south | N | 0.0088358 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.18028 | south | -0.31981 | 0.0089138 | -0.30454 | -0.14204 | 0.0089138 | south | N | 0.0089138 | 0
5031 | BRA_VHBC | 1 | 46 | -0.18036 | south | -0.31989 | 0.0088358 | -0.30462 | -0.14212 | 0.0088358 | south | N | 0.0088358 | 0
5032 | BRA_VHBC | 2 | 47 | -0.18036 | south | -0.31989 | 0.0088358 | -0.30462 | -0.14212 | 0.0088358 | south | N | 0.0088358 | 0
5033 | BRA_VHBC | 3 | 46 | -0.18036 | south | -0.31989 | 0.0088358 | -0.30462 | -0.14212 | 0.0088358 | south | N | 0.0088358 | 0
5034 | BRA_VHBC | 4 | 46 | -0.18036 | south | -0.31989 | 0.0088358 | -0.30462 | -0.14212 | 0.0088358 | south | N | 0.0088358 | 0
5111 | CALAVER_ | 1 | 424 | -0.1807 | south | -0.32023 | 0.0084948 | -0.30496 | -0.14246 | 0.0084948 | south | N | 0.0084948 | 0
5112 | CALAVER_ | 2 | 425 | -0.1807 | south | -0.32023 | 0.0084948 | -0.30496 | -0.14246 | 0.0084948 | south | N | 0.0084948 | 0
5264 | LEON_LCP | 3 | 58 | -0.17927 | south | -0.3188 | 0.0099308 | -0.30352 | -0.14103 | 0.0099308 | south | N | 0.0099308 | 0
5265 | LEON_LCP | 4 | 89 | -0.17927 | south | -0.3188 | 0.0099308 | -0.30352 | -0.14103 | 0.0099308 | south | N | 0.0099308 | 0
5266 | LEON_LCP | 1 | 44 | -0.17927 | south | -0.3188 | 0.0099308 | -0.30352 | -0.14103 | 0.0099308 | south | N | 0.0099308 | 0
5267 | LEON_LCP | 2 | 44 | -0.17927 | south | -0.3188 | 0.0099308 | -0.30352 | -0.14103 | 0.0099308 | south | N | 0.0099308 | 0
5268 | LEON_LCP | 3 | 43 | -0.17927 | south | -0.3188 | 0.0099308 | -0.30352 | -0.14103 | 0.0099308 | south | N | 0.0099308 | 0
5269 | LEON_LCP | 4 | 45 | -0.17927 | south | -0.3188 | 0.0099308 | -0.30352 | -0.14103 | 0.0099308 | south | N | 0.0099308 | 0
5396 | CALAVER_ | 1 | 412 | -0.18057 | south | -0.3201 | 0.0086278 | -0.30483 | -0.14233 | 0.0086278 | south | N | 0.0086278 | 0
5397 | CALAVER_ | 2 | 400 | -0.18057 | south | -0.3201 | 0.0086278 | -0.30483 | -0.14233 | 0.0086278 | south | N | 0.0086278 | 0
5401 | CALAVER_ | 1 | 546 | -0.17898 | south | -0.31851 | 0.010219 | -0.30324 | -0.14074 | 0.010219 | south | N | 0.010219 | 0
5402 | CALAVER_ | 2 | 750 | -0.17898 | south | -0.31851 | 0.010219 | -0.30324 | -0.14074 | 0.010219 | south | N | 0.010219 | 0
5436 | TUTTL_WB | MB | 61 | -0.18122 | south | -0.32075 | 0.0079738 | -0.30548 | -0.14298 | 0.0079738 | south | N | 0.0079738 | 0
5438 | TUTTL_WB | MB | 95 | -0.18122 | south | -0.32075 | 0.0079738 | -0.30548 | -0.14298 | 0.0079738 | south | N | 0.0079738 | 0
5439 | TUTTL_WB | MB | 151 | -0.18122 | south | -0.32075 | 0.0079738 | -0.30548 | -0.14298 | 0.0079738 | south | N | 0.0079738 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.17991 | south | -0.31944 | 0.0092878 | -0.30417 | -0.14167 | 0.0092878 | south | N | 0.0092878 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.17991 | south | -0.31944 | 0.0092878 | -0.30417 | -0.14167 | 0.0092878 | south | N | 0.0092878 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.17991 | south | -0.31944 | 0.0092878 | -0.30417 | -0.14167 | 0.0092878 | south | N | 0.0092878 | 0
5503 | RAYBURNG | 1 | 22 | -0.14405 | south | -0.28358 | 0.045146 | -0.26831 | -0.10581 | 0.045146 | south | N | 0.045146 | 0
5505 | RAYBURNG | 1 | 11 | -0.14405 | south | -0.28358 | 0.045146 | -0.26831 | -0.10581 | 0.045146 | south | N | 0.045146 | 0
5506 | RAYBURNG | 1 | 11 | -0.14405 | south | -0.28358 | 0.045146 | -0.26831 | -0.10581 | 0.045146 | south | N | 0.045146 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.14541 | south | -0.28494 | 0.043788 | -0.26967 | -0.10717 | 0.043788 | south | N | 0.043788 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.14541 | south | -0.28494 | 0.043788 | -0.26967 | -0.10717 | 0.043788 | south | N | 0.043788 | 0
5511 | RAYBURNC | 1 | 46 | -0.14541 | south | -0.28494 | 0.043788 | -0.26967 | -0.10717 | 0.043788 | south | N | 0.043788 | 0
5512 | RAYBURNC | 1 | 48 | -0.14541 | south | -0.28494 | 0.043788 | -0.26967 | -0.10717 | 0.043788 | south | N | 0.043788 | 0
5728 | FALCONHY | 2 | 12 | -0.15224 | south | -0.29177 | 0.036963 | -0.27649 | -0.11399 | 0.036963 | south | N | 0.036963 | 0
5729 | FALCONHY | 3 | 11 | -0.15224 | south | -0.29177 | 0.036963 | -0.27649 | -0.11399 | 0.036963 | south | N | 0.036963 | 0
5890 | PEARSALL | 1 | 24 | -0.15942 | south | -0.29895 | 0.029776 | -0.28368 | -0.12118 | 0.029776 | south | N | 0.029776 | 0
5891 | PEARSALL | 1 | 24 | -0.15942 | south | -0.29895 | 0.029776 | -0.28368 | -0.12118 | 0.029776 | south | N | 0.029776 | 0
5892 | PEARSALL | 1 | 23 | -0.15942 | south | -0.29895 | 0.029776 | -0.28368 | -0.12118 | 0.029776 | south | N | 0.029776 | 0
5903 | SANMIGUE | 1 | 396 | -0.16909 | south | -0.30862 | 0.020108 | -0.29335 | -0.13085 | 0.020108 | south | N | 0.020108 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.091159 | houston | -0.23069 | 0.098039 | -0.21542 | -0.052918 | 0.052918 | houston | N | 0.052918 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.091159 | houston | -0.23069 | 0.098039 | -0.21542 | -0.052918 | 0.052918 | houston | N | 0.052918 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | -0.13953 | 0.1892 | -0.12426 | 0.038241 | 0.038241 | houston | Y | 0.13953 | 60.774
5932 | SI_RAY9 | 9 | 38 | -0.14971 | south | -0.28924 | 0.03949 | -0.27397 | -0.11147 | 0.03949 | south | N | 0.03949 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.14971 | south | -0.28924 | 0.03949 | -0.27397 | -0.11147 | 0.03949 | south | N | 0.03949 | 0
5934 | SI_RAY5 | 5 | 15 | -0.14971 | south | -0.28924 | 0.03949 | -0.27397 | -0.11147 | 0.03949 | south | N | 0.03949 | 0
5935 | SI_RAY10 | 10 | 47 | -0.14971 | south | -0.28924 | 0.03949 | -0.27397 | -0.11147 | 0.03949 | south | N | 0.03949 | 0
6016 | SWMESA | 1 | 75 | 0.10939 | west | -0.03014 | 0.29859 | -0.014866 | 0.14763 | 0.014866 | west | N | 0.014866 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | -0.13953 | 0.1892 | -0.12426 | 0.038241 | 0.038241 | houston | Y | 0.12426 | 18.9236
6144 | MCADOO1A | 1 | 150 | 0.12855 | west | -0.01098 | 0.31775 | 0.0042939 | 0.16679 | 0.0042939 | west | N | 0.0042939 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.12135 | west | -0.018183 | 0.31055 | -0.0029091 | 0.15959 | 0.0029091 | west | N | 0.0029091 | 0
6476 | LANGFORD | 1 | 150 | 0.055321 | west | -0.08421 | 0.24452 | -0.068936 | 0.093562 | 0.068936 | west | N | 0.068936 | 0
6637 | SNYDERW1 | 1 | 63 | 0.12664 | west | -0.012893 | 0.31584 | 0.0023809 | 0.16488 | 0.0023809 | west | N | 0.0023809 | 0
6752 | OKLA0A | 1 | 649.7 | 0.13584 | west | -0.0036928 | 0.32504 | 0.011581 | 0.17408 | 0.0036928 | North | Y | 0.011581 | 5.1249
6948 | DENISNDM | 1 | 40 | 0.14512 | north | 0.0055872 | 0.33432 | 0.020861 | 0.18336 | 0.0055872 | North | N | 0.0055872 | 0
6948 | DENISNDM | 2 | 40 | 0.14512 | north | 0.0055872 | 0.33432 | 0.020861 | 0.18336 | 0.0055872 | North | N | 0.0055872 | 0
7000 | L_FERGUS | 1 | 422 | -0.2028 | south | -0.34233 | -0.013598 | -0.32705 | -0.16456 | 0.013598 | south | N | 0.013598 | 0
7004 | L_SIMGID | 1 | 132 | -0.22729 | south | -0.36682 | -0.038092 | -0.35155 | -0.18905 | 0.038092 | south | N | 0.038092 | 0
7005 | L_SIMGID | 2 | 134 | -0.22729 | south | -0.36682 | -0.038092 | -0.35155 | -0.18905 | 0.038092 | south | N | 0.038092 | 0
7006 | L_SIMGID | 3 | 323 | -0.22729 | south | -0.36682 | -0.038092 | -0.35155 | -0.18905 | 0.038092 | south | N | 0.038092 | 0
7007 | L_LOSTPI | 1 | 158 | -0.22987 | south | -0.3694 | -0.040672 | -0.35413 | -0.19163 | 0.040672 | south | N | 0.040672 | 0
7008 | L_LOSTPI | 2 | 160 | -0.22987 | south | -0.3694 | -0.040672 | -0.35413 | -0.19163 | 0.040672 | south | N | 0.040672 | 0
7009 | L_LOSTPI | 3 | 175 | -0.22987 | south | -0.3694 | -0.040672 | -0.35413 | -0.19163 | 0.040672 | south | N | 0.040672 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.2042 | south | -0.34373 | -0.014998 | -0.32845 | -0.16596 | 0.014998 | south | N | 0.014998 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.2042 | south | -0.34373 | -0.014998 | -0.32845 | -0.16596 | 0.014998 | south | N | 0.014998 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.20399 | south | -0.34352 | -0.014791 | -0.32825 | -0.16575 | 0.014791 | south | N | 0.014791 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.19955 | south | -0.33908 | -0.010348 | -0.3238 | -0.16131 | 0.010348 | south | N | 0.010348 | 0
7015 | L_HAYSEN | 2 | 225 | -0.19955 | south | -0.33908 | -0.010348 | -0.3238 | -0.16131 | 0.010348 | south | N | 0.010348 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.19955 | south | -0.33908 | -0.010348 | -0.3238 | -0.16131 | 0.010348 | south | N | 0.010348 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.19955 | south | -0.33908 | -0.010348 | -0.3238 | -0.16131 | 0.010348 | south | N | 0.010348 | 0
7020 | L_AUSTPL | 1 | 8 | -0.23658 | south | -0.37611 | -0.047383 | -0.36084 | -0.19834 | 0.047383 | south | N | 0.047383 | 0
7020 | L_AUSTPL | 2 | 8 | -0.23658 | south | -0.37611 | -0.047383 | -0.36084 | -0.19834 | 0.047383 | south | N | 0.047383 | 0
7022 | L_BUCHAN | 1 | 18 | -0.20109 | south | -0.34062 | -0.011895 | -0.32535 | -0.16285 | 0.011895 | south | N | 0.011895 | 0
7023 | L_BUCHAN | 2 | 18 | -0.20109 | south | -0.34062 | -0.011895 | -0.32535 | -0.16285 | 0.011895 | south | N | 0.011895 | 0
7024 | L_BUCHAN | 3 | 15 | -0.20109 | south | -0.34062 | -0.011895 | -0.32535 | -0.16285 | 0.011895 | south | N | 0.011895 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.19826 | south | -0.33779 | -0.0090652 | -0.32252 | -0.16002 | 0.0090652 | south | N | 0.0090652 | 0
7028 | L_MARBFA | 1 | 18 | -0.21066 | south | -0.35019 | -0.02146 | -0.33492 | -0.17242 | 0.02146 | south | N | 0.02146 | 0
7029 | L_MARBFA | 2 | 18 | -0.21066 | south | -0.35019 | -0.02146 | -0.33492 | -0.17242 | 0.02146 | south | N | 0.02146 | 0
7031 | L_MARSFO | 1 | 35 | -0.22849 | south | -0.36802 | -0.039289 | -0.35274 | -0.19025 | 0.039289 | south | N | 0.039289 | 0
7032 | L_MARSFO | 2 | 34 | -0.22849 | south | -0.36802 | -0.039289 | -0.35274 | -0.19025 | 0.039289 | south | N | 0.039289 | 0
7033 | L_MARSFO | 3 | 35 | -0.22849 | south | -0.36802 | -0.039289 | -0.35274 | -0.19025 | 0.039289 | south | N | 0.039289 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.20433 | south | -0.34386 | -0.015127 | -0.32858 | -0.16608 | 0.015127 | south | N | 0.015127 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.20433 | south | -0.34386 | -0.015127 | -0.32858 | -0.16608 | 0.015127 | south | N | 0.015127 | 0
7038 | L_DELAWA | 1 | 35 | 0.12212 | west | -0.017414 | 0.31131 | -0.0021401 | 0.16036 | 0.0021401 | west | N | 0.0021401 | 0
7038 | L_DELAWA | 2 | 30 | 0.12212 | west | -0.017414 | 0.31131 | -0.0021401 | 0.16036 | 0.0021401 | west | N | 0.0021401 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.20642 | south | -0.34595 | -0.017225 | -0.33068 | -0.16818 | 0.017225 | south | N | 0.017225 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.20642 | south | -0.34595 | -0.017225 | -0.33068 | -0.16818 | 0.017225 | south | N | 0.017225 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.20642 | south | -0.34595 | -0.017225 | -0.33068 | -0.16818 | 0.017225 | south | N | 0.017225 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.20642 | south | -0.34595 | -0.017225 | -0.33068 | -0.16818 | 0.017225 | south | N | 0.017225 | 0
7487 | L_CANYHY | 1 | 6 | -0.20459 | south | -0.34412 | -0.015391 | -0.32885 | -0.16635 | 0.015391 | south | N | 0.015391 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.19302 | south | -0.33255 | -0.0038212 | -0.31728 | -0.15478 | 0.0038212 | south | N | 0.0038212 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.19302 | south | -0.33255 | -0.0038212 | -0.31728 | -0.15478 | 0.0038212 | south | N | 0.0038212 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.19302 | south | -0.33255 | -0.0038212 | -0.31728 | -0.15478 | 0.0038212 | south | N | 0.0038212 | 0
7609 | L_SCHUMA | 1 | 4 | -0.19019 | south | -0.32972 | -0.00098822 | -0.31444 | -0.15195 | 0.00098822 | south | N | 0.00098822 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.19032 | south | -0.32985 | -0.0011262 | -0.31458 | -0.15208 | 0.0011262 | south | N | 0.0011262 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.19032 | south | -0.32985 | -0.0011262 | -0.31458 | -0.15208 | 0.0011262 | south | N | 0.0011262 | 0
7800 | L_GUADGE | 1 | 147 | -0.18532 | south | -0.32485 | 0.0038778 | -0.30958 | -0.14708 | 0.0038778 | south | N | 0.0038778 | 0
7801 | L_GUADGE | 2 | 138 | -0.18532 | south | -0.32485 | 0.0038778 | -0.30958 | -0.14708 | 0.0038778 | south | N | 0.0038778 | 0
7802 | L_GUADGE | 3 | 140 | -0.18532 | south | -0.32485 | 0.0038778 | -0.30958 | -0.14708 | 0.0038778 | south | N | 0.0038778 | 0
7803 | L_GUADGE | 4 | 147 | -0.18532 | south | -0.32485 | 0.0038778 | -0.30958 | -0.14708 | 0.0038778 | south | N | 0.0038778 | 0
7804 | L_GUADGE | 5 | 182 | -0.18532 | south | -0.32485 | 0.0038778 | -0.30958 | -0.14708 | 0.0038778 | south | N | 0.0038778 | 0
7805 | L_GUADGE | 6 | 198 | -0.18532 | south | -0.32485 | 0.0038778 | -0.30958 | -0.14708 | 0.0038778 | south | N | 0.0038778 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.23152 | south | -0.37105 | -0.042325 | -0.35578 | -0.19328 | 0.042325 | south | N | 0.042325 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.23152 | south | -0.37105 | -0.042325 | -0.35578 | -0.19328 | 0.042325 | south | N | 0.042325 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.23152 | south | -0.37105 | -0.042325 | -0.35578 | -0.19328 | 0.042325 | south | N | 0.042325 | 0
7810 | L_RIONOG | 1 | 142 | -0.19225 | south | -0.33178 | -0.0030502 | -0.31651 | -0.15401 | 0.0030502 | south | N | 0.0030502 | 0
7811 | L_RIONOG | 2 | 145 | -0.19225 | south | -0.33178 | -0.0030502 | -0.31651 | -0.15401 | 0.0030502 | south | N | 0.0030502 | 0
7812 | L_RIONOG | 3 | 151 | -0.19225 | south | -0.33178 | -0.0030502 | -0.31651 | -0.15401 | 0.0030502 | south | N | 0.0030502 | 0
7813 | L_RIONOG | 4 | 290 | -0.19225 | south | -0.33178 | -0.0030502 | -0.31651 | -0.15401 | 0.0030502 | south | N | 0.0030502 | 0
8032 | AMISTADH | 1 | 33 | -0.086262 | south | -0.22579 | 0.10294 | -0.21052 | -0.048021 | 0.048021 | houston | Y | 0.10294 | 1.8122
8033 | AMISTADH | 2 | 25 | -0.086262 | south | -0.22579 | 0.10294 | -0.21052 | -0.048021 | 0.048021 | houston | Y | 0.10294 | 1.3729
8048 | FALCONHY | 1 | 12 | -0.15224 | south | -0.29177 | 0.036963 | -0.27649 | -0.11399 | 0.036963 | south | N | 0.036963 | 0
8066 | DUP1V#1 | 1 | 73 | -0.14573 | south | -0.28526 | 0.043472 | -0.26998 | -0.10749 | 0.043472 | south | N | 0.043472 | 0
8134 | FOR69CG0 | 1 | 79 | -0.13583 | south | -0.27536 | 0.053365 | -0.26009 | -0.097592 | 0.053365 | south | N | 0.053365 | 0
8138 | FOR69CG0 | 2 | 81 | -0.13583 | south | -0.27536 | 0.053365 | -0.26009 | -0.097592 | 0.053365 | south | N | 0.053365 | 0
8139 | JOS #1 | MB | 255 | 0 | south | -0.13953 | 0.1892 | -0.12426 | 0.038241 | 0.038241 | houston | Y | 0.1892 | 38.494
8147 | UCAR #2 | 10 | 28 | -0.14108 | south | -0.28061 | 0.048117 | -0.26534 | -0.10284 | 0.048117 | south | N | 0.048117 | 0
8148 | UCAR #1 | 2 | 7 | -0.14108 | south | -0.28061 | 0.048117 | -0.26534 | -0.10284 | 0.048117 | south | N | 0.048117 | 0
8153 | FOR69CG0 | 3 | 79 | -0.13583 | south | -0.27536 | 0.053365 | -0.26009 | -0.097592 | 0.053365 | south | N | 0.053365 | 0
8154 | FOR69CG0 | 4 | 80 | -0.13583 | south | -0.27536 | 0.053365 | -0.26009 | -0.097592 | 0.053365 | south | N | 0.053365 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.13583 | south | -0.27536 | 0.053365 | -0.26009 | -0.097592 | 0.053365 | south | N | 0.053365 | 0
8156 | FOR69CG0 | 6 | 25 | -0.13583 | south | -0.27536 | 0.053365 | -0.26009 | -0.097592 | 0.053365 | south | N | 0.053365 | 0
8157 | FOR69CG0 | 7 | 46 | -0.13583 | south | -0.27536 | 0.053365 | -0.26009 | -0.097592 | 0.053365 | south | N | 0.053365 | 0
8161 | COLETOU1 | 1 | 629 | -0.15466 | south | -0.29419 | 0.034539 | -0.27892 | -0.11642 | 0.034539 | south | N | 0.034539 | 0
8173 | VICEC51A | 5 | 144 | -0.14742 | south | -0.28695 | 0.041779 | -0.27168 | -0.10918 | 0.041779 | south | N | 0.041779 | 0
8174 | VICEC61A | 6 | 188 | -0.14742 | south | -0.28695 | 0.041779 | -0.27168 | -0.10918 | 0.041779 | south | N | 0.041779 | 0
8189 | CUERO 2 | 1 | 12 | -0.1785 | south | -0.31803 | 0.010697 | -0.30276 | -0.14026 | 0.010697 | south | N | 0.010697 | 0
8262 | ELPS | 1 | 6 | -0.109 | south | -0.24853 | 0.080194 | -0.23326 | -0.070763 | 0.070763 | houston | Y | 0.080194 | 0.056584
8285 | LAR #1 | MB | 32 | 0 | south | -0.13953 | 0.1892 | -0.12426 | 0.038241 | 0.038241 | houston | Y | 0.1892 | 4.8306
8287 | LAR #2 | MB | 32 | 0 | south | -0.13953 | 0.1892 | -0.12426 | 0.038241 | 0.038241 | houston | Y | 0.1892 | 4.8306
8288 | LAR #3 | MB | 105 | 0 | south | -0.13953 | 0.1892 | -0.12426 | 0.038241 | 0.038241 | houston | Y | 0.1892 | 15.8505
8388 | BATES0A | MB | 70 | 0 | south | -0.13953 | 0.1892 | -0.12426 | 0.038241 | 0.038241 | houston | Y | 0.1892 | 10.567
8393 | BATES0B | MB | 110 | 0 | south | -0.13953 | 0.1892 | -0.12426 | 0.038241 | 0.038241 | houston | Y | 0.1892 | 16.6053
8442 | NBEC71A | 1 | 336 | -0.14806 | south | -0.28759 | 0.041141 | -0.27231 | -0.10982 | 0.041141 | south | N | 0.041141 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | -0.13953 | 0.1892 | -0.12426 | 0.038241 | 0.038241 | houston | Y | 0.1892 | 3.0191
8457 | COSW#2 | 2 | 14 | 0 | south | -0.13953 | 0.1892 | -0.12426 | 0.038241 | 0.038241 | houston | Y | 0.1892 | 2.1134
8459 | B_DAVIS1 | 1 | 334 | -0.14841 | south | -0.28794 | 0.04079 | -0.27267 | -0.11017 | 0.04079 | south | N | 0.04079 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.14841 | south | -0.28794 | 0.04079 | -0.27267 | -0.11017 | 0.04079 | south | N | 0.04079 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.14863 | south | -0.28816 | 0.040572 | -0.27288 | -0.11039 | 0.040572 | south | N | 0.040572 | 0
8506 | VAL #1 | 1 | 25 | -0.14846 | south | -0.28799 | 0.040735 | -0.27272 | -0.11022 | 0.040735 | south | N | 0.040735 | 0
8507 | VAL #2 | 2 | 25 | -0.14846 | south | -0.28799 | 0.040735 | -0.27272 | -0.11022 | 0.040735 | south | N | 0.040735 | 0
8511 | OXY_CC0A | 1 | 38 | -0.14861 | south | -0.28815 | 0.040583 | -0.27287 | -0.11037 | 0.040583 | south | N | 0.040583 | 0
8517 | CELANEBI | 1 | 29 | -0.14936 | south | -0.28889 | 0.039841 | -0.27361 | -0.11112 | 0.039841 | south | N | 0.039841 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.14808 | south | -0.28761 | 0.041123 | -0.27233 | -0.10983 | 0.041123 | south | N | 0.041123 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.14808 | south | -0.28761 | 0.041123 | -0.27233 | -0.10983 | 0.041123 | south | N | 0.041123 | 0
8562 | CNOPST1 | 3 | 153 | -0.14808 | south | -0.28761 | 0.041123 | -0.27233 | -0.10983 | 0.041123 | south | N | 0.041123 | 0
8926 | LGE_GT10 | 1 | 158 | -0.14648 | south | -0.28601 | 0.042722 | -0.27073 | -0.10824 | 0.042722 | south | N | 0.042722 | 0
8927 | LGE_GT20 | 2 | 153 | -0.14648 | south | -0.28601 | 0.042722 | -0.27073 | -0.10824 | 0.042722 | south | N | 0.042722 | 0
8928 | LGE_STG0 | 3 | 100 | -0.14648 | south | -0.28601 | 0.042722 | -0.27073 | -0.10824 | 0.042722 | south | N | 0.042722 | 0
8930 | ICPGN10A | 1 | 145 | -0.14648 | south | -0.28601 | 0.042722 | -0.27073 | -0.10824 | 0.042722 | south | N | 0.042722 | 0
8931 | ICPGN20A | 2 | 147 | -0.14648 | south | -0.28601 | 0.042722 | -0.27073 | -0.10824 | 0.042722 | south | N | 0.042722 | 0
8932 | ICPGN30A | 3 | 127 | -0.14648 | south | -0.28601 | 0.042722 | -0.27073 | -0.10824 | 0.042722 | south | N | 0.042722 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.15032 | south | -0.28985 | 0.03888 | -0.27458 | -0.11208 | 0.03888 | south | N | 0.03888 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.15032 | south | -0.28985 | 0.03888 | -0.27458 | -0.11208 | 0.03888 | south | N | 0.03888 | 0
8935 | FGNTS201 | 3 | 173 | -0.15032 | south | -0.28985 | 0.03888 | -0.27458 | -0.11208 | 0.03888 | south | N | 0.03888 | 0
8936 | MVGN#1 | 1 | 207 | -0.15001 | south | -0.28954 | 0.039187 | -0.27427 | -0.11177 | 0.039187 | south | N | 0.039187 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.15001 | south | -0.28954 | 0.039187 | -0.27427 | -0.11177 | 0.039187 | south | N | 0.039187 | 0
8938 | MVGN#3 | 3 | 242 | -0.15001 | south | -0.28954 | 0.039187 | -0.27427 | -0.11177 | 0.039187 | south | N | 0.039187 | 0
8981 | HECN1 | 1 | 144 | -0.15001 | south | -0.28954 | 0.039192 | -0.27426 | -0.11177 | 0.039192 | south | N | 0.039192 | 0
8982 | HECN2 | 2 | 144 | -0.15001 | south | -0.28954 | 0.039192 | -0.27426 | -0.11177 | 0.039192 | south | N | 0.039192 | 0
8983 | HECN3 | 3 | 171 | -0.15001 | south | -0.28954 | 0.039192 | -0.27426 | -0.11177 | 0.039192 | south | N | 0.039192 | 0
9000 | DECKR_G1 | 1 | 310 | -0.23759 | south | -0.37712 | -0.048395 | -0.36185 | -0.19935 | 0.048395 | south | N | 0.048395 | 0
9001 | DECKR_G2 | 2 | 413 | -0.23759 | south | -0.37712 | -0.048395 | -0.36185 | -0.19935 | 0.048395 | south | N | 0.048395 | 0
9002 | DECKR_G3 | 3 | 42 | -0.24016 | south | -0.37969 | -0.050962 | -0.36442 | -0.20192 | 0.050962 | south | N | 0.050962 | 0
9003 | DECKR_G4 | 4 | 44 | -0.24016 | south | -0.37969 | -0.050962 | -0.36442 | -0.20192 | 0.050962 | south | N | 0.050962 | 0
9004 | DECKR_G5 | 5 | 44 | -0.24016 | south | -0.37969 | -0.050962 | -0.36442 | -0.20192 | 0.050962 | south | N | 0.050962 | 0
9005 | DECKR_G6 | 6 | 47 | -0.24016 | south | -0.37969 | -0.050962 | -0.36442 | -0.20192 | 0.050962 | south | N | 0.050962 | 0
9016 | SANDH_G1 | 1 | 49 | -0.23492 | south | -0.37445 | -0.045717 | -0.35917 | -0.19667 | 0.045717 | south | N | 0.045717 | 0
9017 | SANDH_G2 | 2 | 46 | -0.23492 | south | -0.37445 | -0.045717 | -0.35917 | -0.19667 | 0.045717 | south | N | 0.045717 | 0
9018 | SANDH_G3 | 3 | 46 | -0.23492 | south | -0.37445 | -0.045717 | -0.35917 | -0.19667 | 0.045717 | south | N | 0.045717 | 0
9019 | SANDH_G4 | 4 | 47 | -0.23492 | south | -0.37445 | -0.045717 | -0.35917 | -0.19667 | 0.045717 | south | N | 0.045717 | 0
9020 | SANDHG5A | 5A | 154 | -0.23492 | south | -0.37445 | -0.045717 | -0.35917 | -0.19667 | 0.045717 | south | N | 0.045717 | 0
9021 | SANDHG5C | 5C | 148 | -0.23492 | south | -0.37445 | -0.045717 | -0.35917 | -0.19667 | 0.045717 | south | N | 0.045717 | 0
9022 | SANDH_G6 | 6 | 48 | -0.23492 | south | -0.37445 | -0.045717 | -0.35917 | -0.19667 | 0.045717 | south | N | 0.045717 | 0
9023 | SANDH_G7 | 7 | 48 | -0.23492 | south | -0.37445 | -0.045717 | -0.35917 | -0.19667 | 0.045717 | south | N | 0.045717 | 0
11001 | NAV1CT | 1 | 70 | 0.12428 | west | -0.015251 | 0.31348 | 2.2909e-05 | 0.16252 | 2.2909e-05 | west | N | 2.2909e-05 | 0
11009 | NAV2CT | 1 | 70 | 0.12428 | west | -0.015251 | 0.31348 | 2.2909e-05 | 0.16252 | 2.2909e-05 | west | N | 2.2909e-05 | 0
11011 | NAV3ST | 1 | 92.8 | 0.12428 | west | -0.015251 | 0.31348 | 2.2909e-05 | 0.16252 | 2.2909e-05 | west | N | 2.2909e-05 | 0
11012 | NAV4CT | 1 | 80 | 0.12428 | west | -0.015251 | 0.31348 | 2.2909e-05 | 0.16252 | 2.2909e-05 | west | N | 2.2909e-05 | 0
11013 | NAV5CT | 1 | 80 | 0.12428 | west | -0.015251 | 0.31348 | 2.2909e-05 | 0.16252 | 2.2909e-05 | west | N | 2.2909e-05 | 0
11014 | NAV6ST | 1 | 115 | 0.12428 | west | -0.015251 | 0.31348 | 2.2909e-05 | 0.16252 | 2.2909e-05 | west | N | 2.2909e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.12426 | west | -0.015273 | 0.31346 | 9.0909e-07 | 0.1625 | 9.0909e-07 | west | N | 9.0909e-07 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.12426 | west | -0.015273 | 0.31346 | 9.0909e-07 | 0.1625 | 9.0909e-07 | west | N | 9.0909e-07 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.12426 | west | -0.015273 | 0.31346 | 9.0909e-07 | 0.1625 | 9.0909e-07 | west | N | 9.0909e-07 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.12426 | west | -0.015273 | 0.31346 | 9.0909e-07 | 0.1625 | 9.0909e-07 | west | N | 9.0909e-07 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.12426 | west | -0.015273 | 0.31346 | 9.0909e-07 | 0.1625 | 9.0909e-07 | west | N | 9.0909e-07 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.12426 | west | -0.015273 | 0.31346 | 9.0909e-07 | 0.1625 | 9.0909e-07 | west | N | 9.0909e-07 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.12847 | west | -0.01106 | 0.31767 | 0.0042139 | 0.16671 | 0.0042139 | west | N | 0.0042139 | 0
11057 | CHAMPION | 1 | 126.5 | 0.12847 | west | -0.01106 | 0.31767 | 0.0042139 | 0.16671 | 0.0042139 | west | N | 0.0042139 | 0
11058 | PYRON_1G | 1 | 249 | 0.12847 | west | -0.01106 | 0.31767 | 0.0042139 | 0.16671 | 0.0042139 | west | N | 0.0042139 | 0
11059 | INADALE_ | 1 | 197 | 0.12847 | west | -0.01106 | 0.31767 | 0.0042139 | 0.16671 | 0.0042139 | west | N | 0.0042139 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.12626 | west | -0.01327 | 0.31546 | 0.0020039 | 0.1645 | 0.0020039 | west | N | 0.0020039 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.12626 | west | -0.01327 | 0.31546 | 0.0020039 | 0.1645 | 0.0020039 | west | N | 0.0020039 | 0
11147 | NOTREES_ | 1 | 149 | 0.1225 | west | -0.01703 | 0.3117 | -0.0017561 | 0.16074 | 0.0017561 | west | N | 0.0017561 | 0
11309 | BULLCREK | 1 | 180 | 0.12589 | west | -0.013644 | 0.31508 | 0.0016299 | 0.16413 | 0.0016299 | west | N | 0.0016299 | 0
11310 | BULLCREK | 1 | 180 | 0.12589 | west | -0.013644 | 0.31508 | 0.0016299 | 0.16413 | 0.0016299 | west | N | 0.0016299 | 0
11320 | COYOTE_1 | 1 | 225 | 0.12577 | west | -0.013764 | 0.31496 | 0.0015099 | 0.16401 | 0.0015099 | west | N | 0.0015099 | 0
11415 | LORAINE_ | 1 | 125 | 0.12752 | west | -0.012006 | 0.31672 | 0.0032679 | 0.16577 | 0.0032679 | west | N | 0.0032679 | 0
11416 | LORAINE_ | 1 | 125 | 0.12752 | west | -0.012006 | 0.31672 | 0.0032679 | 0.16577 | 0.0032679 | west | N | 0.0032679 | 0
11691 | KMICHICT | 1 | 140 | 0.14495 | north | 0.0054192 | 0.33415 | 0.020693 | 0.18319 | 0.0054192 | North | N | 0.0054192 | 0
11692 | KMICHICT | 2 | 141 | 0.14495 | north | 0.0054192 | 0.33415 | 0.020693 | 0.18319 | 0.0054192 | North | N | 0.0054192 | 0
11693 | KMICHIST | 3 | 309 | 0.14495 | north | 0.0054192 | 0.33415 | 0.020693 | 0.18319 | 0.0054192 | North | N | 0.0054192 | 0
11694 | KMICHICT | 4 | 143 | 0.14495 | north | 0.0054192 | 0.33415 | 0.020693 | 0.18319 | 0.0054192 | North | N | 0.0054192 | 0
11695 | KMICHICT | 5 | 144 | 0.14495 | north | 0.0054192 | 0.33415 | 0.020693 | 0.18319 | 0.0054192 | North | N | 0.0054192 | 0
11696 | KMICHIST | 6 | 310 | 0.14495 | north | 0.0054192 | 0.33415 | 0.020693 | 0.18319 | 0.0054192 | North | N | 0.0054192 | 0
12322 | ENNSTRAC | 1 | 196 | 0.14664 | north | 0.0071122 | 0.33584 | 0.022386 | 0.18488 | 0.0071122 | North | N | 0.0071122 | 0
12323 | ENNSTRAC | 2 | 111 | 0.14664 | north | 0.0071122 | 0.33584 | 0.022386 | 0.18488 | 0.0071122 | North | N | 0.0071122 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.14583 | north | 0.0063042 | 0.33503 | 0.021578 | 0.18408 | 0.0063042 | North | N | 0.0063042 | 0
12411 | FPLEFR1A | 1 | 161 | 0.14378 | north | 0.0042512 | 0.33298 | 0.019525 | 0.18202 | 0.0042512 | North | N | 0.0042512 | 0
12412 | FPLEFR1B | 2 | 164 | 0.14378 | north | 0.0042512 | 0.33298 | 0.019525 | 0.18202 | 0.0042512 | North | N | 0.0042512 | 0
12413 | FPLEFR1C | 3 | 164 | 0.14378 | north | 0.0042512 | 0.33298 | 0.019525 | 0.18202 | 0.0042512 | North | N | 0.0042512 | 0
12414 | FPLEFR1S | 4 | 414 | 0.14378 | north | 0.0042512 | 0.33298 | 0.019525 | 0.18202 | 0.0042512 | North | N | 0.0042512 | 0
12421 | FPLEFR2A | 1 | 162 | 0.14378 | north | 0.0042512 | 0.33298 | 0.019525 | 0.18202 | 0.0042512 | North | N | 0.0042512 | 0
12422 | FPLEFR2B | 2 | 161 | 0.14378 | north | 0.0042512 | 0.33298 | 0.019525 | 0.18202 | 0.0042512 | North | N | 0.0042512 | 0
12423 | FPLEFR2C | 3 | 163 | 0.14378 | north | 0.0042512 | 0.33298 | 0.019525 | 0.18202 | 0.0042512 | North | N | 0.0042512 | 0
12424 | FPLEFR2S | 4 | 409 | 0.14378 | north | 0.0042512 | 0.33298 | 0.019525 | 0.18202 | 0.0042512 | North | N | 0.0042512 | 0
12440 | PARKD_1S | 1 | 0 | 0.14535 | north | 0.0058202 | 0.33455 | 0.021094 | 0.18359 | 0.0058202 | North | N | 0.0058202 | 0
12449 | PARKD_2S | 1 | 0 | 0.14535 | north | 0.0058202 | 0.33455 | 0.021094 | 0.18359 | 0.0058202 | North | N | 0.0058202 | 0
13116 | TGATEWAY | 1 | 148 | 0.13903 | north | -0.00049881 | 0.32823 | 0.014775 | 0.17727 | 0.00049881 | North | N | 0.00049881 | 0
13117 | TGATEWAY | 2 | 130 | 0.13903 | north | -0.00049881 | 0.32823 | 0.014775 | 0.17727 | 0.00049881 | North | N | 0.00049881 | 0
13118 | TGATEWAY | 3 | 145 | 0.13903 | north | -0.00049881 | 0.32823 | 0.014775 | 0.17727 | 0.00049881 | North | N | 0.00049881 | 0
13119 | TGATEWAY | 4 | 399 | 0.13903 | north | -0.00049881 | 0.32823 | 0.014775 | 0.17727 | 0.00049881 | North | N | 0.00049881 | 0
13131 | CALFREST | 1 | 150.7 | 0.13327 | north | -0.0062588 | 0.32247 | 0.0090149 | 0.17151 | 0.0062588 | North | N | 0.0062588 | 0
13132 | CALFREST | 2 | 151 | 0.13327 | north | -0.0062588 | 0.32247 | 0.0090149 | 0.17151 | 0.0062588 | North | N | 0.0062588 | 0
13133 | CALFREST | 3 | 177.4 | 0.13327 | north | -0.0062588 | 0.32247 | 0.0090149 | 0.17151 | 0.0062588 | North | N | 0.0062588 | 0
13134 | CALFREST | 4 | 151.5 | 0.13344 | north | -0.0060898 | 0.32264 | 0.0091839 | 0.17168 | 0.0060898 | North | N | 0.0060898 | 0
13135 | CALFREST | 5 | 152.3 | 0.13344 | north | -0.0060898 | 0.32264 | 0.0091839 | 0.17168 | 0.0060898 | North | N | 0.0060898 | 0
13136 | CALFREST | 6 | 177.5 | 0.13344 | north | -0.0060898 | 0.32264 | 0.0091839 | 0.17168 | 0.0060898 | North | N | 0.0060898 | 0
13432 | SANDOW_5 | 5 | 581 | -0.28306 | south | -0.42259 | -0.093857 | -0.40731 | -0.24481 | 0.093857 | south | N | 0.093857 | 0
13691 | OAKGROVE | 1 | 855 | 0.094903 | north | -0.044628 | 0.2841 | -0.029354 | 0.13314 | 0.029354 | west | Y | 0.044628 | 13.059
13692 | OAKGROVE | 2 | 855 | 0.094903 | north | -0.044628 | 0.2841 | -0.029354 | 0.13314 | 0.029354 | west | Y | 0.044628 | 13.059
32798 | BRYN_TAM | 1 | 32 | 0.046607 | north | -0.092924 | 0.2358 | -0.07765 | 0.084848 | 0.07765 | west | Y | 0.092924 | 0.48876
32883 | BRYN_DNS | 1 | 48 | 0.042415 | north | -0.097116 | 0.23161 | -0.081842 | 0.080656 | 0.080656 | houston | Y | 0.097116 | 0.79008
32884 | BRYN_DNS | 1 | 46 | 0.042415 | north | -0.097116 | 0.23161 | -0.081842 | 0.080656 | 0.080656 | houston | Y | 0.097116 | 0.75716
32886 | BRYN_ATK | MB | 12 | 0.046689 | north | -0.092842 | 0.23589 | -0.077568 | 0.08493 | 0.077568 | west | Y | 0.092842 | 0.18328
32887 | BRYN_ATK | MB | 51 | 0.046689 | north | -0.092842 | 0.23589 | -0.077568 | 0.08493 | 0.077568 | west | Y | 0.092842 | 0.77896
32888 | BRYN_ATK | 1 | 17 | 0.046689 | north | -0.092842 | 0.23589 | -0.077568 | 0.08493 | 0.077568 | west | Y | 0.092842 | 0.25965
32890 | BRYN_ATK | MB | 22 | 0.046689 | north | -0.092842 | 0.23589 | -0.077568 | 0.08493 | 0.077568 | west | Y | 0.092842 | 0.33602
32891 | BRYN_ATK | MB | 25 | 0.046689 | north | -0.092842 | 0.23589 | -0.077568 | 0.08493 | 0.077568 | west | Y | 0.092842 | 0.38184
32892 | BRYN_DNS | 1 | 105 | 0.042415 | north | -0.097116 | 0.23161 | -0.081842 | 0.080656 | 0.080656 | houston | Y | 0.097116 | 1.7283
36998 | RDCNYNG1 | 1 | 84 | 0.12711 | west | -0.01242 | 0.31631 | 0.0028539 | 0.16535 | 0.0028539 | west | N | 0.0028539 | 0
38332 | WDWRDU2 | 1 | 80 | 0.10916 | west | -0.030366 | 0.29836 | -0.015092 | 0.14741 | 0.015092 | west | N | 0.015092 | 0
38437 | TNSRBNMS | 1 | 150 | 0.10905 | west | -0.030483 | 0.29825 | -0.015209 | 0.14729 | 0.015209 | west | N | 0.015209 | 0
38438 | TNSRBNMS | 1 | 150 | 0.10905 | west | -0.030483 | 0.29825 | -0.015209 | 0.14729 | 0.015209 | west | N | 0.015209 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.040414 | houston | -0.17994 | 0.14878 | -0.16467 | -0.0021732 | 0.0021732 | houston | N | 0.0021732 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.040414 | houston | -0.17994 | 0.14878 | -0.16467 | -0.0021732 | 0.0021732 | houston | N | 0.0021732 | 0
38600 | TNBP_CGN | 5 | 53 | -0.040414 | houston | -0.17994 | 0.14878 | -0.16467 | -0.0021732 | 0.0021732 | houston | N | 0.0021732 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.040414 | houston | -0.17994 | 0.14878 | -0.16467 | -0.0021732 | 0.0021732 | houston | N | 0.0021732 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.040414 | houston | -0.17994 | 0.14878 | -0.16467 | -0.0021732 | 0.0021732 | houston | N | 0.0021732 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.040414 | houston | -0.17994 | 0.14878 | -0.16467 | -0.0021732 | 0.0021732 | houston | N | 0.0021732 | 0
38614 | TNBPAMCG | 4 | 96 | -0.040414 | houston | -0.17994 | 0.14878 | -0.16467 | -0.0021732 | 0.0021732 | houston | N | 0.0021732 | 0
38615 | TNBPAMCG | 1 | 244 | -0.040414 | houston | -0.17994 | 0.14878 | -0.16467 | -0.0021732 | 0.0021732 | houston | N | 0.0021732 | 0
38690 | TNBP_CGN | 3 | 40 | -0.040414 | houston | -0.17994 | 0.14878 | -0.16467 | -0.0021732 | 0.0021732 | houston | N | 0.0021732 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.040447 | houston | -0.17998 | 0.14875 | -0.1647 | -0.0022062 | 0.0022062 | houston | N | 0.0022062 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.040447 | houston | -0.17998 | 0.14875 | -0.1647 | -0.0022062 | 0.0022062 | houston | N | 0.0022062 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.040447 | houston | -0.17998 | 0.14875 | -0.1647 | -0.0022062 | 0.0022062 | houston | N | 0.0022062 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.040447 | houston | -0.17998 | 0.14875 | -0.1647 | -0.0022062 | 0.0022062 | houston | N | 0.0022062 | 0
39470 | TNDOWCGN | 1 | 32 | -0.040446 | houston | -0.17998 | 0.14875 | -0.1647 | -0.0022052 | 0.0022052 | houston | N | 0.0022052 | 0
39480 | TNDOWCGN | 1 | 30 | -0.040446 | houston | -0.17998 | 0.14875 | -0.1647 | -0.0022052 | 0.0022052 | houston | N | 0.0022052 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.060736 | houston | -0.20027 | 0.12846 | -0.18499 | -0.022495 | 0.022495 | houston | N | 0.022495 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.060736 | houston | -0.20027 | 0.12846 | -0.18499 | -0.022495 | 0.022495 | houston | N | 0.022495 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.060736 | houston | -0.20027 | 0.12846 | -0.18499 | -0.022495 | 0.022495 | houston | N | 0.022495 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.060736 | houston | -0.20027 | 0.12846 | -0.18499 | -0.022495 | 0.022495 | houston | N | 0.022495 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.094903 | north | -0.044628 | 0.2841 | -0.029354 | 0.13314 | 0.029354 | west | Y | 0.044628 | 2.3262
39970 | TNTNPONE | 1 | 153 | 0.094903 | north | -0.044628 | 0.2841 | -0.029354 | 0.13314 | 0.029354 | west | Y | 0.044628 | 2.3369
48500 | APD_GT1_ | 1 | 136 | -0.028047 | houston | -0.16758 | 0.16115 | -0.1523 | 0.010194 | 0.010194 | houston | N | 0.010194 | 0
48510 | AK_GT1__ | 1 | 33 | -0.047183 | houston | -0.18671 | 0.14201 | -0.17144 | -0.0089422 | 0.0089422 | houston | N | 0.0089422 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.027975 | houston | -0.16751 | 0.16122 | -0.15223 | 0.010266 | 0.010266 | houston | N | 0.010266 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.027975 | houston | -0.16751 | 0.16122 | -0.15223 | 0.010266 | 0.010266 | houston | N | 0.010266 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.027975 | houston | -0.16751 | 0.16122 | -0.15223 | 0.010266 | 0.010266 | houston | N | 0.010266 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.027975 | houston | -0.16751 | 0.16122 | -0.15223 | 0.010266 | 0.010266 | houston | N | 0.010266 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.063994 | houston | -0.20352 | 0.1252 | -0.18825 | -0.025753 | 0.025753 | houston | N | 0.025753 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.063994 | houston | -0.20352 | 0.1252 | -0.18825 | -0.025753 | 0.025753 | houston | N | 0.025753 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.048419 | houston | -0.18795 | 0.14078 | -0.17268 | -0.010178 | 0.010178 | houston | N | 0.010178 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.048419 | houston | -0.18795 | 0.14078 | -0.17268 | -0.010178 | 0.010178 | houston | N | 0.010178 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.048419 | houston | -0.18795 | 0.14078 | -0.17268 | -0.010178 | 0.010178 | houston | N | 0.010178 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.032665 | houston | -0.1722 | 0.15653 | -0.15692 | 0.0055758 | 0.0055758 | houston | N | 0.0055758 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.032665 | houston | -0.1722 | 0.15653 | -0.15692 | 0.0055758 | 0.0055758 | houston | N | 0.0055758 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.032665 | houston | -0.1722 | 0.15653 | -0.15692 | 0.0055758 | 0.0055758 | houston | N | 0.0055758 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.032665 | houston | -0.1722 | 0.15653 | -0.15692 | 0.0055758 | 0.0055758 | houston | N | 0.0055758 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.029653 | houston | -0.16918 | 0.15954 | -0.15391 | 0.0085878 | 0.0085878 | houston | N | 0.0085878 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.029653 | houston | -0.16918 | 0.15954 | -0.15391 | 0.0085878 | 0.0085878 | houston | N | 0.0085878 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.033572 | houston | -0.1731 | 0.15563 | -0.15783 | 0.0046688 | 0.0046688 | houston | N | 0.0046688 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.033572 | houston | -0.1731 | 0.15563 | -0.15783 | 0.0046688 | 0.0046688 | houston | N | 0.0046688 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.033572 | houston | -0.1731 | 0.15563 | -0.15783 | 0.0046688 | 0.0046688 | houston | N | 0.0046688 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.033572 | houston | -0.1731 | 0.15563 | -0.15783 | 0.0046688 | 0.0046688 | houston | N | 0.0046688 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.033572 | houston | -0.1731 | 0.15563 | -0.15783 | 0.0046688 | 0.0046688 | houston | N | 0.0046688 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.024196 | houston | -0.16373 | 0.165 | -0.14845 | 0.014045 | 0.014045 | houston | N | 0.014045 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.02573 | houston | -0.16526 | 0.16347 | -0.14999 | 0.012511 | 0.012511 | houston | N | 0.012511 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.023734 | houston | -0.16326 | 0.16546 | -0.14799 | 0.014507 | 0.014507 | houston | N | 0.014507 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.023734 | houston | -0.16326 | 0.16546 | -0.14799 | 0.014507 | 0.014507 | houston | N | 0.014507 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.023734 | houston | -0.16326 | 0.16546 | -0.14799 | 0.014507 | 0.014507 | houston | N | 0.014507 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.015225 | houston | -0.15476 | 0.17397 | -0.13948 | 0.023016 | 0.023016 | houston | N | 0.023016 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.027743 | houston | -0.16727 | 0.16145 | -0.152 | 0.010498 | 0.010498 | houston | N | 0.010498 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.027743 | houston | -0.16727 | 0.16145 | -0.152 | 0.010498 | 0.010498 | houston | N | 0.010498 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.02265 | houston | -0.16218 | 0.16655 | -0.14691 | 0.015591 | 0.015591 | houston | N | 0.015591 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.02265 | houston | -0.16218 | 0.16655 | -0.14691 | 0.015591 | 0.015591 | houston | N | 0.015591 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.02265 | houston | -0.16218 | 0.16655 | -0.14691 | 0.015591 | 0.015591 | houston | N | 0.015591 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.02265 | houston | -0.16218 | 0.16655 | -0.14691 | 0.015591 | 0.015591 | houston | N | 0.015591 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.029553 | houston | -0.16908 | 0.15964 | -0.15381 | 0.0086878 | 0.0086878 | houston | N | 0.0086878 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.029553 | houston | -0.16908 | 0.15964 | -0.15381 | 0.0086878 | 0.0086878 | houston | N | 0.0086878 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.029553 | houston | -0.16908 | 0.15964 | -0.15381 | 0.0086878 | 0.0086878 | houston | N | 0.0086878 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.029553 | houston | -0.16908 | 0.15964 | -0.15381 | 0.0086878 | 0.0086878 | houston | N | 0.0086878 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.030514 | houston | -0.17004 | 0.15868 | -0.15477 | 0.0077268 | 0.0077268 | houston | N | 0.0077268 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.030514 | houston | -0.17004 | 0.15868 | -0.15477 | 0.0077268 | 0.0077268 | houston | N | 0.0077268 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.030514 | houston | -0.17004 | 0.15868 | -0.15477 | 0.0077268 | 0.0077268 | houston | N | 0.0077268 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.030514 | houston | -0.17004 | 0.15868 | -0.15477 | 0.0077268 | 0.0077268 | houston | N | 0.0077268 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.030514 | houston | -0.17004 | 0.15868 | -0.15477 | 0.0077268 | 0.0077268 | houston | N | 0.0077268 | 0
48651 | EP_1_2 | 1 | 5 | -0.024277 | houston | -0.16381 | 0.16492 | -0.14853 | 0.013964 | 0.013964 | houston | N | 0.013964 | 0
48651 | EP_1_2 | 2 | 21 | -0.024277 | houston | -0.16381 | 0.16492 | -0.14853 | 0.013964 | 0.013964 | houston | N | 0.013964 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.044771 | north | -0.09476 | 0.23397 | -0.079486 | 0.083012 | 0.079486 | west | Y | 0.09476 | 2.3552
48672 | FTR_GT2_ | 2 | 156 | 0.044771 | north | -0.09476 | 0.23397 | -0.079486 | 0.083012 | 0.079486 | west | Y | 0.09476 | 2.3827
48673 | FTR_GT3_ | 3 | 156 | 0.044771 | north | -0.09476 | 0.23397 | -0.079486 | 0.083012 | 0.079486 | west | Y | 0.09476 | 2.3827
48674 | FTR_CN4_ | 4 | 380 | 0.044771 | north | -0.09476 | 0.23397 | -0.079486 | 0.083012 | 0.079486 | west | Y | 0.09476 | 5.804
48690 | GBY_GN5_ | 5 | 398 | -0.022274 | houston | -0.1618 | 0.16692 | -0.14653 | 0.015967 | 0.015967 | houston | N | 0.015967 | 0
48691 | GBY_7374 | A | 46 | -0.031316 | houston | -0.17085 | 0.15788 | -0.15557 | 0.0069248 | 0.0069248 | houston | N | 0.0069248 | 0
48691 | GBY_7374 | B | 46 | -0.031316 | houston | -0.17085 | 0.15788 | -0.15557 | 0.0069248 | 0.0069248 | houston | N | 0.0069248 | 0
48692 | GBY_8182 | C | 46 | -0.031316 | houston | -0.17085 | 0.15788 | -0.15557 | 0.0069248 | 0.0069248 | houston | N | 0.0069248 | 0
48692 | GBY_8182 | D | 55 | -0.031316 | houston | -0.17085 | 0.15788 | -0.15557 | 0.0069248 | 0.0069248 | houston | N | 0.0069248 | 0
48693 | GBY_8384 | E | 55 | -0.031316 | houston | -0.17085 | 0.15788 | -0.15557 | 0.0069248 | 0.0069248 | houston | N | 0.0069248 | 0
48693 | GBY_8384 | F | 54 | -0.031316 | houston | -0.17085 | 0.15788 | -0.15557 | 0.0069248 | 0.0069248 | houston | N | 0.0069248 | 0
48721 | LEG_1___ | 1 | 827 | 0.11176 | north | -0.027774 | 0.30095 | -0.0125 | 0.15 | 0.0125 | west | Y | 0.027774 | 12.6314
48722 | LEG_2___ | 2 | 819 | 0.11176 | north | -0.027774 | 0.30095 | -0.0125 | 0.15 | 0.0125 | west | Y | 0.027774 | 12.5092
48730 | MNS_GT | 1 | 46.1 | -0.048944 | houston | -0.18847 | 0.14025 | -0.1732 | -0.010703 | 0.010703 | houston | N | 0.010703 | 0
48731 | CBE_GT1 | 1 | 76 | -0.090529 | houston | -0.23006 | 0.098669 | -0.21479 | -0.052288 | 0.052288 | houston | N | 0.052288 | 0
48732 | CBE_GT2 | 1 | 76 | -0.090529 | houston | -0.23006 | 0.098669 | -0.21479 | -0.052288 | 0.052288 | houston | N | 0.052288 | 0
48733 | CBE_ST12 | 1 | 105 | -0.090529 | houston | -0.23006 | 0.098669 | -0.21479 | -0.052288 | 0.052288 | houston | N | 0.052288 | 0
48734 | CBE_GT3 | 1 | 74 | -0.090529 | houston | -0.23006 | 0.098669 | -0.21479 | -0.052288 | 0.052288 | houston | N | 0.052288 | 0
48735 | CBE_GT4 | 1 | 74 | -0.090529 | houston | -0.23006 | 0.098669 | -0.21479 | -0.052288 | 0.052288 | houston | N | 0.052288 | 0
48736 | CBE_ST34 | 1 | 102 | -0.090529 | houston | -0.23006 | 0.098669 | -0.21479 | -0.052288 | 0.052288 | houston | N | 0.052288 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.029524 | houston | -0.16905 | 0.15967 | -0.15378 | 0.0087168 | 0.0087168 | houston | N | 0.0087168 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.029524 | houston | -0.16905 | 0.15967 | -0.15378 | 0.0087168 | 0.0087168 | houston | N | 0.0087168 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.029524 | houston | -0.16905 | 0.15967 | -0.15378 | 0.0087168 | 0.0087168 | houston | N | 0.0087168 | 0
48761 | PR_GT1__ | 1 | 35 | -0.030137 | houston | -0.16967 | 0.15906 | -0.15439 | 0.0081038 | 0.0081038 | houston | N | 0.0081038 | 0
48772 | PHR_GN2_ | MB | 459 | -0.035886 | houston | -0.17542 | 0.15331 | -0.16014 | 0.0023548 | 0.0023548 | houston | N | 0.0023548 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.024267 | houston | -0.1638 | 0.16493 | -0.14852 | 0.013974 | 0.013974 | houston | N | 0.013974 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.024267 | houston | -0.1638 | 0.16493 | -0.14852 | 0.013974 | 0.013974 | houston | N | 0.013974 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.024267 | houston | -0.1638 | 0.16493 | -0.14852 | 0.013974 | 0.013974 | houston | N | 0.013974 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.024267 | houston | -0.1638 | 0.16493 | -0.14852 | 0.013974 | 0.013974 | houston | N | 0.013974 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.024267 | houston | -0.1638 | 0.16493 | -0.14852 | 0.013974 | 0.013974 | houston | N | 0.013974 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.024267 | houston | -0.1638 | 0.16493 | -0.14852 | 0.013974 | 0.013974 | houston | N | 0.013974 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.024267 | houston | -0.1638 | 0.16493 | -0.14852 | 0.013974 | 0.013974 | houston | N | 0.013974 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.015225 | houston | -0.15476 | 0.17397 | -0.13948 | 0.023016 | 0.023016 | houston | N | 0.023016 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.015225 | houston | -0.15476 | 0.17397 | -0.13948 | 0.023016 | 0.023016 | houston | N | 0.023016 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.015225 | houston | -0.15476 | 0.17397 | -0.13948 | 0.023016 | 0.023016 | houston | N | 0.023016 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.015225 | houston | -0.15476 | 0.17397 | -0.13948 | 0.023016 | 0.023016 | houston | N | 0.023016 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.023916 | houston | -0.16345 | 0.16528 | -0.14817 | 0.014325 | 0.014325 | houston | N | 0.014325 | 0
48820 | SHELLG1_ | 1 | 71 | -0.028953 | houston | -0.16848 | 0.16024 | -0.15321 | 0.0092878 | 0.0092878 | houston | N | 0.0092878 | 0
48821 | SHELLG2 | 2 | 72 | -0.028953 | houston | -0.16848 | 0.16024 | -0.15321 | 0.0092878 | 0.0092878 | houston | N | 0.0092878 | 0
48822 | SHELLG3_ | 1 | 39 | -0.028953 | houston | -0.16848 | 0.16024 | -0.15321 | 0.0092878 | 0.0092878 | houston | N | 0.0092878 | 0
48822 | SHELLG3_ | 2 | 30 | -0.028953 | houston | -0.16848 | 0.16024 | -0.15321 | 0.0092878 | 0.0092878 | houston | N | 0.0092878 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.030979 | houston | -0.17051 | 0.15822 | -0.15524 | 0.0072618 | 0.0072618 | houston | N | 0.0072618 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.030979 | houston | -0.17051 | 0.15822 | -0.15524 | 0.0072618 | 0.0072618 | houston | N | 0.0072618 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.02956 | houston | -0.16909 | 0.15964 | -0.15382 | 0.0086808 | 0.0086808 | houston | N | 0.0086808 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.029678 | houston | -0.16921 | 0.15952 | -0.15394 | 0.0085628 | 0.0085628 | houston | N | 0.0085628 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.02971 | houston | -0.16924 | 0.15949 | -0.15397 | 0.0085308 | 0.0085308 | houston | N | 0.0085308 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.02957 | houston | -0.1691 | 0.15963 | -0.15383 | 0.0086708 | 0.0086708 | houston | N | 0.0086708 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.029538 | houston | -0.16907 | 0.15966 | -0.1538 | 0.0087028 | 0.0087028 | houston | N | 0.0087028 | 0
48855 | SRB_GT21 | B2 | 12 | -0.029732 | houston | -0.16926 | 0.15947 | -0.15399 | 0.0085088 | 0.0085088 | houston | N | 0.0085088 | 0
48855 | SRB_GT21 | MB | 18 | -0.029732 | houston | -0.16926 | 0.15947 | -0.15399 | 0.0085088 | 0.0085088 | houston | N | 0.0085088 | 0
48865 | TECO_GT1 | 1 | 50 | -0.03787 | houston | -0.1774 | 0.15133 | -0.16213 | 0.00037085 | 0.00037085 | houston | N | 0.00037085 | 0
48873 | THW_ST3_ | 3 | 104 | -0.026289 | houston | -0.16582 | 0.16291 | -0.15055 | 0.011952 | 0.011952 | houston | N | 0.011952 | 0
48874 | THW_ST4_ | 4 | 104 | -0.026289 | houston | -0.16582 | 0.16291 | -0.15055 | 0.011952 | 0.011952 | houston | N | 0.011952 | 0
48875 | THW_3132 | A | 54 | -0.026289 | houston | -0.16582 | 0.16291 | -0.15055 | 0.011952 | 0.011952 | houston | N | 0.011952 | 0
48875 | THW_3132 | B | 53 | -0.026289 | houston | -0.16582 | 0.16291 | -0.15055 | 0.011952 | 0.011952 | houston | N | 0.011952 | 0
48877 | THW_3334 | C | 54 | -0.026289 | houston | -0.16582 | 0.16291 | -0.15055 | 0.011952 | 0.011952 | houston | N | 0.011952 | 0
48877 | THW_3334 | D | 57 | -0.026289 | houston | -0.16582 | 0.16291 | -0.15055 | 0.011952 | 0.011952 | houston | N | 0.011952 | 0
48879 | THW_4142 | E | 54 | -0.026289 | houston | -0.16582 | 0.16291 | -0.15055 | 0.011952 | 0.011952 | houston | N | 0.011952 | 0
48879 | THW_4142 | F | 54 | -0.026289 | houston | -0.16582 | 0.16291 | -0.15055 | 0.011952 | 0.011952 | houston | N | 0.011952 | 0
48881 | THW_4344 | G | 58 | -0.026289 | houston | -0.16582 | 0.16291 | -0.15055 | 0.011952 | 0.011952 | houston | N | 0.011952 | 0
48881 | THW_4344 | H | 58 | -0.026289 | houston | -0.16582 | 0.16291 | -0.15055 | 0.011952 | 0.011952 | houston | N | 0.011952 | 0
48883 | THW_GT1_ | B2 | 12 | -0.024881 | houston | -0.16441 | 0.16432 | -0.14914 | 0.01336 | 0.01336 | houston | N | 0.01336 | 0
48885 | THW_5152 | A | 56 | -0.021613 | houston | -0.16114 | 0.16758 | -0.14587 | 0.016628 | 0.016628 | houston | N | 0.016628 | 0
48885 | THW_5152 | B | 59 | -0.021613 | houston | -0.16114 | 0.16758 | -0.14587 | 0.016628 | 0.016628 | houston | N | 0.016628 | 0
48886 | THW_5354 | C | 56 | -0.021613 | houston | -0.16114 | 0.16758 | -0.14587 | 0.016628 | 0.016628 | houston | N | 0.016628 | 0
48886 | THW_5354 | D | 56 | -0.021613 | houston | -0.16114 | 0.16758 | -0.14587 | 0.016628 | 0.016628 | houston | N | 0.016628 | 0
48887 | THW_5556 | E | 59 | -0.021613 | houston | -0.16114 | 0.16758 | -0.14587 | 0.016628 | 0.016628 | houston | N | 0.016628 | 0
48887 | THW_5556 | F | 56 | -0.021613 | houston | -0.16114 | 0.16758 | -0.14587 | 0.016628 | 0.016628 | houston | N | 0.016628 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.085133 | houston | -0.22466 | 0.10406 | -0.20939 | -0.046892 | 0.046892 | houston | N | 0.046892 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.046651 | houston | -0.18618 | 0.14255 | -0.17091 | -0.0084102 | 0.0084102 | houston | N | 0.0084102 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.046651 | houston | -0.18618 | 0.14255 | -0.17091 | -0.0084102 | 0.0084102 | houston | N | 0.0084102 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.046651 | houston | -0.18618 | 0.14255 | -0.17091 | -0.0084102 | 0.0084102 | houston | N | 0.0084102 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.046651 | houston | -0.18618 | 0.14255 | -0.17091 | -0.0084102 | 0.0084102 | houston | N | 0.0084102 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.046651 | houston | -0.18618 | 0.14255 | -0.17091 | -0.0084102 | 0.0084102 | houston | N | 0.0084102 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.048518 | houston | -0.18805 | 0.14068 | -0.17278 | -0.010277 | 0.010277 | houston | N | 0.010277 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.048518 | houston | -0.18805 | 0.14068 | -0.17278 | -0.010277 | 0.010277 | houston | N | 0.010277 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.048518 | houston | -0.18805 | 0.14068 | -0.17278 | -0.010277 | 0.010277 | houston | N | 0.010277 | 0
48929 | WAPGT21_ | B1 | 13 | -0.046651 | houston | -0.18618 | 0.14255 | -0.17091 | -0.0084102 | 0.0084102 | houston | N | 0.0084102 | 0
48940 | WARVUE_G | G1 | 12 | -0.024238 | houston | -0.16377 | 0.16496 | -0.1485 | 0.014003 | 0.014003 | houston | N | 0.014003 | 0
49803 | EXN_15GT | 1 | 34 | -0.025357 | houston | -0.16489 | 0.16384 | -0.14961 | 0.012884 | 0.012884 | houston | N | 0.012884 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.025357 | houston | -0.16489 | 0.16384 | -0.14961 | 0.012884 | 0.012884 | houston | N | 0.012884 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.025357 | houston | -0.16489 | 0.16384 | -0.14961 | 0.012884 | 0.012884 | houston | N | 0.012884 | 0
49826 | EXN938GT | 5 | 45.9 | -0.025357 | houston | -0.16489 | 0.16384 | -0.14961 | 0.012884 | 0.012884 | houston | N | 0.012884 | 0
49828 | EXN941GT | 10 | 17.7 | -0.025357 | houston | -0.16489 | 0.16384 | -0.14961 | 0.012884 | 0.012884 | houston | N | 0.012884 | 0
49829 | EXN942GT | 11 | 20.4 | -0.025357 | houston | -0.16489 | 0.16384 | -0.14961 | 0.012884 | 0.012884 | houston | N | 0.012884 | 0
49830 | EXN943GT | 12 | 19.9 | -0.025357 | houston | -0.16489 | 0.16384 | -0.14961 | 0.012884 | 0.012884 | houston | N | 0.012884 | 0
49831 | EXN944GT | 13 | 35 | -0.025357 | houston | -0.16489 | 0.16384 | -0.14961 | 0.012884 | 0.012884 | houston | N | 0.012884 | 0
49832 | EXN945GT | 9 | 18 | -0.025357 | houston | -0.16489 | 0.16384 | -0.14961 | 0.012884 | 0.012884 | houston | N | 0.012884 | 0
49837 | EXN_GT | 4 | 85.4 | -0.025357 | houston | -0.16489 | 0.16384 | -0.14961 | 0.012884 | 0.012884 | houston | N | 0.012884 | 0
49838 | EXN_14GT | 14 | 148 | -0.025357 | houston | -0.16489 | 0.16384 | -0.14961 | 0.012884 | 0.012884 | houston | N | 0.012884 | 0
49851 | DOW17000 | 37 | 62 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49858 | DOW38100 | 31 | 71.4 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49859 | DOW38200 | 33 | 45 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49860 | DOW38300 | 32 | 101 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49862 | DOW39100 | 36 | 86 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49863 | DOW39200 | 35 | 88 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49865 | DOW41000 | 41 | 50 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49866 | DOW42000 | 42 | 18 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49869 | DOW49000 | 45 | 94 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49870 | DOW61000 | 61 | 70 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49871 | DOW62000 | 62 | 63 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49872 | DOW63000 | 63 | 72 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49873 | DOW64000 | 64 | 64.8 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49876 | DOW65000 | 65 | 101 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49877 | DOW66000 | 66 | 97 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49878 | DOW67000 | 67 | 103 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49882 | DOW81000 | 81 | 76 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49884 | DOW82000 | 82 | 80 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49885 | DOW83000 | 83 | 80 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
49886 | DOW84000 | 84 | 171 | -0.068117 | houston | -0.20765 | 0.12108 | -0.19237 | -0.029876 | 0.029876 | houston | N | 0.029876 | 0
58909 | PEARSALL | 1 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58909 | PEARSALL | 2 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58909 | PEARSALL | 3 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58909 | PEARSALL | 4 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58909 | PEARSALL | 5 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58909 | PEARSALL | 6 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58919 | PEARSALL | 1 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58919 | PEARSALL | 2 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58919 | PEARSALL | 3 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58919 | PEARSALL | 4 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58919 | PEARSALL | 5 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58919 | PEARSALL | 6 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58929 | PEARSALL | 1 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58929 | PEARSALL | 2 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58929 | PEARSALL | 3 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58929 | PEARSALL | 4 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58929 | PEARSALL | 5 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58929 | PEARSALL | 6 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58949 | PEARSALL | 1 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58949 | PEARSALL | 2 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58949 | PEARSALL | 3 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58949 | PEARSALL | 4 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58949 | PEARSALL | 5 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
58949 | PEARSALL | 6 | 8.4 | -0.15761 | south | -0.29714 | 0.031591 | -0.28186 | -0.11937 | 0.031591 | south | N | 0.031591 | 0
60000 | DSKY2 | 1 | 76.5 | 0.10365 | west | -0.035877 | 0.29285 | -0.020603 | 0.14189 | 0.020603 | west | N | 0.020603 | 0
60003 | KING_NE1 | 1 | 80 | 0.10939 | west | -0.03014 | 0.29859 | -0.014866 | 0.14763 | 0.014866 | west | N | 0.014866 | 0
60005 | KING_SE1 | 1 | 40 | 0.10939 | west | -0.03014 | 0.29859 | -0.014866 | 0.14763 | 0.014866 | west | N | 0.014866 | 0
60007 | KING_SW1 | 1 | 80 | 0.11031 | west | -0.029222 | 0.29951 | -0.013948 | 0.14855 | 0.013948 | west | N | 0.013948 | 0
60016 | WOODWRD1 | 1 | 80 | 0.10919 | west | -0.030339 | 0.29839 | -0.015065 | 0.14743 | 0.015065 | west | N | 0.015065 | 0
60017 | ORNNWP1 | 1 | 80 | 0.10446 | west | -0.035075 | 0.29365 | -0.019801 | 0.1427 | 0.019801 | west | N | 0.019801 | 0
60018 | DSKY1 | 1 | 84 | 0.10291 | west | -0.036624 | 0.2921 | -0.02135 | 0.14115 | 0.02135 | west | N | 0.02135 | 0
60019 | KING_NW1 | 1 | 80 | 0.11031 | west | -0.029222 | 0.29951 | -0.013948 | 0.14855 | 0.013948 | west | N | 0.013948 | 0
60057 | CALLAHAN | 1 | 114 | -0.18914 | south | -0.32867 | 5.7783e-05 | -0.3134 | -0.1509 | 5.7783e-05 | south | N | 5.7783e-05 | 0
60058 | BUFF_GAP | 1 | 120 | 0.12529 | west | -0.014237 | 0.31449 | 0.0010369 | 0.16353 | 0.0010369 | west | N | 0.0010369 | 0
60060 | CIRELLO | 1 | 233 | 0.12529 | west | -0.014237 | 0.31449 | 0.0010369 | 0.16353 | 0.0010369 | west | N | 0.0010369 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.12529 | west | -0.014237 | 0.31449 | 0.0010369 | 0.16353 | 0.0010369 | west | N | 0.0010369 | 0
60066 | H_HOLLOW | 1 | 222 | -0.18914 | south | -0.32867 | 5.7783e-05 | -0.3134 | -0.1509 | 5.7783e-05 | south | N | 5.7783e-05 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.18914 | south | -0.32867 | 5.7783e-05 | -0.3134 | -0.1509 | 5.7783e-05 | south | N | 5.7783e-05 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.18914 | south | -0.32867 | 5.7783e-05 | -0.3134 | -0.1509 | 5.7783e-05 | south | N | 5.7783e-05 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.18914 | south | -0.32867 | 5.7783e-05 | -0.3134 | -0.1509 | 5.7783e-05 | south | N | 5.7783e-05 | 0
60074 | HORSH5 | 1 | 100 | -0.18914 | south | -0.32867 | 5.7783e-05 | -0.3134 | -0.1509 | 5.7783e-05 | south | N | 5.7783e-05 | 0
60081 | WHRLWIND | 1 | 60 | 0.1304 | west | -0.0091308 | 0.3196 | 0.0061429 | 0.16864 | 0.0061429 | west | N | 0.0061429 | 0
60201 | RIO DRCS | F | 0 | -0.099921 | south | -0.23945 | 0.089277 | -0.22418 | -0.06168 | 0.06168 | houston | Y | 0.089277 | 0
60202 | FRIEND_R | F | 0 | 0.078216 | west | -0.061315 | 0.26741 | -0.046041 | 0.11646 | 0.046041 | west | N | 0.046041 | 0
60203 | PRES0A | BT | 4.8 | 0.11374 | west | -0.025795 | 0.30293 | -0.010521 | 0.15198 | 0.010521 | west | N | 0.010521 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.12818 | west | -0.011354 | 0.31737 | 0.0039199 | 0.16642 | 0.0039199 | west | N | 0.0039199 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.12818 | west | -0.011354 | 0.31737 | 0.0039199 | 0.16642 | 0.0039199 | west | N | 0.0039199 | 0
71057 | L_SWEETW | W1 | 135 | 0.12818 | west | -0.011354 | 0.31737 | 0.0039199 | 0.16642 | 0.0039199 | west | N | 0.0039199 | 0
71059 | L_SWEETW | W1 | 119 | 0.12818 | west | -0.011354 | 0.31737 | 0.0039199 | 0.16642 | 0.0039199 | west | N | 0.0039199 | 0
71060 | L_SWEETW | W1 | 105 | 0.12818 | west | -0.011354 | 0.31737 | 0.0039199 | 0.16642 | 0.0039199 | west | N | 0.0039199 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.12818 | west | -0.011354 | 0.31737 | 0.0039199 | 0.16642 | 0.0039199 | west | N | 0.0039199 | 0
76031 | L_GASCCR | W1 | 150 | 0.12389 | west | -0.015639 | 0.31309 | -0.00036509 | 0.16213 | 0.00036509 | west | N | 0.00036509 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.12333 | west | -0.016205 | 0.31252 | -0.00093109 | 0.16157 | 0.00093109 | west | N | 0.00093109 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.12333 | west | -0.016205 | 0.31252 | -0.00093109 | 0.16157 | 0.00093109 | west | N | 0.00093109 | 0
76096 | L_CAPRSI | W1 | 186 | 0.12333 | west | -0.016205 | 0.31252 | -0.00093109 | 0.16157 | 0.00093109 | west | N | 0.00093109 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.12333 | west | -0.016205 | 0.31252 | -0.00093109 | 0.16157 | 0.00093109 | west | N | 0.00093109 | 0
80003 | MILHWYS | F | 0 | -0.14971 | south | -0.28924 | 0.03949 | -0.27397 | -0.11147 | 0.03949 | south | N | 0.03949 | 0
80010 | EPLVT1 | F | 0 | -0.11429 | south | -0.25382 | 0.074904 | -0.23855 | -0.076053 | 0.074904 | south | N | 0.074904 | 0
80012 | LAR | F | 0 | -0.15819 | south | -0.29772 | 0.03101 | -0.28245 | -0.11995 | 0.03101 | south | N | 0.03101 | 0
80051 | FORPVCM0 | 8 | 28 | -0.13583 | south | -0.27536 | 0.053365 | -0.26009 | -0.097592 | 0.053365 | south | N | 0.053365 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.13583 | south | -0.27536 | 0.053365 | -0.26009 | -0.097592 | 0.053365 | south | N | 0.053365 | 0
80053 | FOR69CG0 | 10 | 74 | -0.13583 | south | -0.27536 | 0.053365 | -0.26009 | -0.097592 | 0.053365 | south | N | 0.053365 | 0
80080 | GWINDT11 | 1 | 94 | -0.1496 | south | -0.28913 | 0.039595 | -0.27386 | -0.11136 | 0.039595 | south | N | 0.039595 | 0
80080 | GWINDT11 | 2 | 41 | -0.1496 | south | -0.28913 | 0.039595 | -0.27386 | -0.11136 | 0.039595 | south | N | 0.039595 | 0
80080 | GWINDT11 | 3 | 38 | -0.1496 | south | -0.28913 | 0.039595 | -0.27386 | -0.11136 | 0.039595 | south | N | 0.039595 | 0
80080 | GWINDT11 | 4 | 19 | -0.1496 | south | -0.28913 | 0.039595 | -0.27386 | -0.11136 | 0.039595 | south | N | 0.039595 | 0
80081 | GWINDT21 | 1 | 94 | -0.1496 | south | -0.28913 | 0.039595 | -0.27386 | -0.11136 | 0.039595 | south | N | 0.039595 | 0
80081 | GWINDT21 | 2 | 36 | -0.1496 | south | -0.28913 | 0.039595 | -0.27386 | -0.11136 | 0.039595 | south | N | 0.039595 | 0
80081 | GWINDT21 | 3 | 43 | -0.1496 | south | -0.28913 | 0.039595 | -0.27386 | -0.11136 | 0.039595 | south | N | 0.039595 | 0
80081 | GWINDT21 | 4 | 22 | -0.1496 | south | -0.28913 | 0.039595 | -0.27386 | -0.11136 | 0.039595 | south | N | 0.039595 | 0
80137 | CSDR89 | 8 | 39 | -0.14108 | south | -0.28061 | 0.048117 | -0.26534 | -0.10284 | 0.048117 | south | N | 0.048117 | 0
80137 | CSDR89 | 9 | 15 | -0.14108 | south | -0.28061 | 0.048117 | -0.26534 | -0.10284 | 0.048117 | south | N | 0.048117 | 0
80138 | CSDR7 | 7 | 7 | -0.14108 | south | -0.28061 | 0.048117 | -0.26534 | -0.10284 | 0.048117 | south | N | 0.048117 | 0
80139 | CSDR56 | 5 | 15 | -0.14108 | south | -0.28061 | 0.048117 | -0.26534 | -0.10284 | 0.048117 | south | N | 0.048117 | 0
80139 | CSDR56 | 6 | 39 | -0.14108 | south | -0.28061 | 0.048117 | -0.26534 | -0.10284 | 0.048117 | south | N | 0.048117 | 0
80140 | CSDR11 | 11 | 39 | -0.14108 | south | -0.28061 | 0.048117 | -0.26534 | -0.10284 | 0.048117 | south | N | 0.048117 | 0
80180 | PNSCALT1 | 1 | 148 | -0.1496 | south | -0.28913 | 0.039595 | -0.27386 | -0.11136 | 0.039595 | south | N | 0.039595 | 0
80180 | PNSCALT1 | 2 | 50 | -0.1496 | south | -0.28913 | 0.039595 | -0.27386 | -0.11136 | 0.039595 | south | N | 0.039595 | 0
80181 | PNSCALT2 | 1 | 55 | -0.1496 | south | -0.28913 | 0.039595 | -0.27386 | -0.11136 | 0.039595 | south | N | 0.039595 | 0
80181 | PNSCALT2 | 2 | 50 | -0.1496 | south | -0.28913 | 0.039595 | -0.27386 | -0.11136 | 0.039595 | south | N | 0.039595 | 0
80223 | REYSHR G | 1 | 12 | -0.14648 | south | -0.28601 | 0.042722 | -0.27073 | -0.10824 | 0.042722 | south | N | 0.042722 | 0
80224 | VISTRONG | 1 | 15 | -0.14276 | south | -0.28229 | 0.046435 | -0.26702 | -0.10452 | 0.046435 | south | N | 0.046435 | 0
80225 | VISTRONG | 2 | 23 | -0.14276 | south | -0.28229 | 0.046435 | -0.26702 | -0.10452 | 0.046435 | south | N | 0.046435 | 0
80226 | ALCOA G | 1 | 48 | -0.13707 | south | -0.2766 | 0.052129 | -0.26133 | -0.098828 | 0.052129 | south | N | 0.052129 | 0
80227 | AIRCO G | 1 | 8 | -0.14168 | south | -0.28121 | 0.04752 | -0.26594 | -0.10344 | 0.04752 | south | N | 0.04752 | 0
80261 | NBEC81A | 1 | 180 | -0.1481 | south | -0.28764 | 0.041093 | -0.27236 | -0.10986 | 0.041093 | south | N | 0.041093 | 0
80262 | NBEC91A | 1 | 180 | -0.14806 | south | -0.28759 | 0.041141 | -0.27231 | -0.10982 | 0.041141 | south | N | 0.041141 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.14841 | south | -0.28794 | 0.04079 | -0.27267 | -0.11017 | 0.04079 | south | N | 0.04079 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.14841 | south | -0.28794 | 0.04079 | -0.27267 | -0.11017 | 0.04079 | south | N | 0.04079 | 0
80265 | LARECU40 | 4 | 100 | -0.1582 | south | -0.29773 | 0.030996 | -0.28246 | -0.11996 | 0.030996 | south | N | 0.030996 | 0
80266 | LARECU50 | 5 | 100 | -0.1582 | south | -0.29773 | 0.030996 | -0.28246 | -0.11996 | 0.030996 | south | N | 0.030996 | 0
80291 | PAPALOTE | 1 | 25 | -0.1471 | south | -0.28663 | 0.042099 | -0.27136 | -0.10886 | 0.042099 | south | N | 0.042099 | 0
80291 | PAPALOTE | 2 | 25 | -0.1471 | south | -0.28663 | 0.042099 | -0.27136 | -0.10886 | 0.042099 | south | N | 0.042099 | 0
80291 | PAPALOTE | 3 | 25 | -0.1471 | south | -0.28663 | 0.042099 | -0.27136 | -0.10886 | 0.042099 | south | N | 0.042099 | 0
80291 | PAPALOTE | 4 | 16 | -0.1471 | south | -0.28663 | 0.042099 | -0.27136 | -0.10886 | 0.042099 | south | N | 0.042099 | 0
80294 | PAPALOTE | 5 | 25 | -0.1471 | south | -0.28663 | 0.042099 | -0.27136 | -0.10886 | 0.042099 | south | N | 0.042099 | 0
80294 | PAPALOTE | 6 | 25 | -0.1471 | south | -0.28663 | 0.042099 | -0.27136 | -0.10886 | 0.042099 | south | N | 0.042099 | 0
80294 | PAPALOTE | 7 | 25 | -0.1471 | south | -0.28663 | 0.042099 | -0.27136 | -0.10886 | 0.042099 | south | N | 0.042099 | 0
80294 | PAPALOTE | 8 | 15 | -0.1471 | south | -0.28663 | 0.042099 | -0.27136 | -0.10886 | 0.042099 | south | N | 0.042099 | 0
86104 | CID-138 | EQ | 0 | -0.1582 | south | -0.29773 | 0.030996 | -0.28246 | -0.11996 | 0.030996 | south | N | 0.030996 | 0
86105 | CID-230 | EQ | 500 | -0.1582 | south | -0.29773 | 0.030996 | -0.28246 | -0.11996 | 0.030996 | south | N | 0.030996 | 0
86106 | CUF-230 | EQ | 500 | -0.1582 | south | -0.29773 | 0.030996 | -0.28246 | -0.11996 | 0.030996 | south | N | 0.030996 | 0
86107 | CUF-138 | EQ | 0 | -0.1582 | south | -0.29773 | 0.030996 | -0.28246 | -0.11996 | 0.030996 | south | N | 0.030996 | 0
88198 | BEEVILLE | F | 0 | -0.15679 | south | -0.29632 | 0.032411 | -0.28104 | -0.11855 | 0.032411 | south | N | 0.032411 | 0
88253 | HAMILTON | F | 0 | -0.086262 | south | -0.22579 | 0.10294 | -0.21052 | -0.048021 | 0.048021 | houston | Y | 0.10294 | 0
88299 | ZAPATA | F | 0 | -0.15407 | south | -0.2936 | 0.035129 | -0.27833 | -0.11583 | 0.035129 | south | N | 0.035129 | 0
88508 | FALFURRI | F | 0 | -0.15224 | south | -0.29177 | 0.036957 | -0.2765 | -0.114 | 0.036957 | south | N | 0.036957 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3409 LAKE_CRK 3414 TEMP_SS_ctg2 C:THOUSE__5-LAKE_CRK1_5 C:THOUSE__5-AEP_PEC__59 [3405 - 3409] and [3405 - 3412] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.23563 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.42133 | 0 | 0 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.23563 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 185.4392 | 787 | 0.42133 | 331.5855 | 787 | 331.5855
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.19162 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 48.8641 | 255 | 0.37732 | 96.2177 | 1042 | 427.8032
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.19162 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 28.552 | 149 | 0.37732 | 56.2213 | 1191 | 484.0246 | Weighted Shift Factors
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.19162 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 29.3185 | 153 | 0.37732 | 57.7306 | 1344 | 541.7552 | North | 0.13953
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.1779 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3636 | 0 | 1344 | 541.7552 | South | -0.1857
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.1779 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3636 | 0 | 1344 | 541.7552 |  | 0.32523
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.1621 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.3154 | 150 | 0.3478 | 52.1705 | 1494 | 593.9257
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.1621 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.9682 | 80 | 0.3478 | 27.8243 | 1574 | 621.75 | Line Rating | 1239.6
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.15871 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3807 | 0 | 0.34441 | 0 | 1574 | 621.75 | Conc Gen | 2456.5
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.15871 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3807 | 0 | 0.34441 | 0 | 1574 | 621.75 | Weighted Imp. | 924.31
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.15739 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.0594 | 216.4 | 0.34309 | 74.245 | 1790.4 | 695.995 | PTDF | 0.37627
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.15739 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.0122 | 216.1 | 0.34309 | 74.1421 | 2006.5 | 770.1371
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.15691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.1469 | 224 | 0.34261 | 76.7438 | 2230.5 | 846.8809 | Concentration | 1.1569
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.15691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.4608 | 226 | 0.34261 | 77.4291 | 2456.5 | 924.31
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.15691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.2641 | 212 | 0.34261 | 72.6326
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.15691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.1072 | 211 | 0.34261 | 72.29
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.15096 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.3604 | 168 | 0.33666 | 56.5581
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.15096 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.586 | 90 | 0.33666 | 30.299
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.15033 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 59.3815 | 395 | 0.33603 | 132.7332
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.15033 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 65.3949 | 435 | 0.33603 | 146.1746
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.15007 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 65.28 | 435 | 0.33577 | 146.0597
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.14821 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33391 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.14773 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.1009 | 217.3 | 0.33343 | 72.4536
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.14773 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.2838 | 205 | 0.33343 | 68.3524
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.14773 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 40.2406 | 272.4 | 0.33343 | 90.8254
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.14754 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.3279 | 70 | 0.33324 | 23.327
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.14754 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.1804 | 69 | 0.33324 | 22.9937
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.14754 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.1804 | 69 | 0.33324 | 22.9937
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.14754 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.0329 | 68 | 0.33324 | 22.6605
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.1473 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.333 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.1473 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.333 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.1473 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.333 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.14722 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 17.3718 | 118 | 0.33292 | 39.2845
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.14722 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 16.9302 | 115 | 0.33292 | 38.2857
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.14722 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 81.8538 | 556 | 0.33292 | 185.1032
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.14707 | north | 3 | N | N | Nnorth | Nnorth | 1 | 170.1623 | 0 | 0.33277 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.14707 | north | 3 | N | N | Nnorth | Nnorth | 1 | 170.3094 | 0 | 0.33277 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.14664 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.742 | 196 | 0.33234 | 65.1393
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.14664 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.2774 | 111 | 0.33234 | 36.8901
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.14589 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.7536 | 60 | 0.33159 | 19.8956
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.14589 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.1913 | 63 | 0.33159 | 20.8904
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.14583 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.33154 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.14572 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33142 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14535 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.33105 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14535 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.33105 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.14512 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.8047 | 0 | 0.33082 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.14512 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.8047 | 0 | 0.33082 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.14503 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 24.6553 | 170 | 0.33073 | 56.2243
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.14503 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.4161 | 520 | 0.33073 | 171.9804
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.14495 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 53.6315 | 370 | 0.33065 | 122.3407
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.293 | 0 | 0.33065 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.438 | 0 | 0.33065 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | 1 | 44.7895 | 0 | 0.33065 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.7279 | 0 | 0.33065 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.8728 | 0 | 0.33065 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | 1 | 44.9345 | 0 | 0.33065 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.14494 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 41.7436 | 288 | 0.33064 | 95.2253
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.14494 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3066 | 147 | 0.33064 | 48.6046
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.14494 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3066 | 147 | 0.33064 | 48.6046
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.14494 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 16.306 | 112.5 | 0.33064 | 37.1973
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1782 | 160 | 0.33056 | 52.8903
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.5988 | 156 | 0.33056 | 51.5681
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.3933 | 196 | 0.33056 | 64.7906
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.5988 | 156 | 0.33056 | 51.5681
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7436 | 157 | 0.33056 | 51.8986
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.6831 | 198 | 0.33056 | 65.4518
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.14484 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 56.1968 | 388 | 0.33054 | 128.2485
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.14484 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 74.5911 | 515 | 0.33054 | 170.2268
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.14477 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.7909 | 40 | 0.33047 | 13.2189
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.14477 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.8577 | 0 | 0.33047 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.14477 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.5236 | 0 | 0.33047 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.14477 | north | 8 | N | N | Nnorth | Nnorth | 1 | 12.7976 | 0 | 0.33047 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.14476 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.4364 | 79 | 0.33046 | 26.1067
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.14476 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.345 | 106 | 0.33046 | 35.0292
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.14476 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 21.1355 | 146 | 0.33046 | 48.2478
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.14476 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.0021 | 76 | 0.33046 | 25.1153
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.14474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.7638 | 558 | 0.33044 | 184.3847
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.14474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 83.8033 | 579 | 0.33044 | 191.3239
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.14474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 116.9483 | 808 | 0.33044 | 266.9943
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.1446 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.6029 | 18 | 0.3303 | 5.9455
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.1446 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.6029 | 18 | 0.3303 | 5.9455
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.1446 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.495 | 38 | 0.3303 | 12.5516
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.1446 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.615 | 25 | 0.3303 | 8.2575
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.1446 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.9286 | 41 | 0.3303 | 13.5424
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.1446 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.892 | 20 | 0.3303 | 6.606
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1489 | 161 | 0.32948 | 53.0467
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5802 | 164 | 0.32948 | 54.0351
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5802 | 164 | 0.32948 | 54.0351
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 59.5257 | 414 | 0.32948 | 136.4057
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2927 | 162 | 0.32948 | 53.3762
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1489 | 161 | 0.32948 | 53.0467
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.4365 | 163 | 0.32948 | 53.7056
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 58.8068 | 409 | 0.32948 | 134.7583
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.14352 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.2787 | 204 | 0.32922 | 67.1616
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.14352 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.8481 | 201 | 0.32922 | 66.1739
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.14352 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.7326 | 242 | 0.32922 | 79.6721
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.14271 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.4176 | 73 | 0.32841 | 23.9737
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.14271 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.9821 | 119 | 0.32841 | 39.0805
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.14271 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.2549 | 205 | 0.32841 | 67.3235
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.14271 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.5561 | 102 | 0.32841 | 33.4976
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.14271 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.6999 | 96 | 0.32841 | 31.5271
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.14161 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6993 | 0 | 0.32731 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.14161 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6993 | 0 | 0.32731 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.14144 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 16.973 | 120 | 0.32714 | 39.2571
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.14118 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.6236 | 224 | 0.32688 | 73.2206
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13978 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7956 | 20 | 0.32548 | 6.5096
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.13978 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7956 | 20 | 0.32548 | 6.5096
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13978 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7956 | 20 | 0.32548 | 6.5096
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.13978 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3762 | 17 | 0.32548 | 5.5332
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.13969 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 51.1269 | 366 | 0.32539 | 119.0933
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.13954 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 109.5405 | 785 | 0.32524 | 255.3153
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.13954 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 110.9359 | 795 | 0.32524 | 258.5678
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.13954 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 108.8428 | 780 | 0.32524 | 253.6891
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.13903 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.5767 | 0 | 0.32473 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.13903 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.0742 | 0 | 0.32473 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.13903 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.1596 | 0 | 0.32473 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.13903 | north | 1 | N | N | Nnorth | Nnorth | 1 | 55.4738 | 0 | 0.32473 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.13884 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 33.5988 | 242 | 0.32454 | 78.5383
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.13829 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.32399 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.13826 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.9129 | 50 | 0.32396 | 16.1979
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.13753 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.0305 | 182 | 0.32323 | 58.8279
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.13753 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 66.5645 | 484 | 0.32323 | 156.4435
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.13623 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 8.1737 | 60 | 0.32193 | 19.3158
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.13584 | west | 4 | Y | N | Ywest | Nwest | 1 | 88.2539 | 649.7 | 0.32154 | 208.9035
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.13464 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.2149 | 165 | 0.32034 | 52.8555
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.13344 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.2163 | 151.5 | 0.31914 | 48.3499
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.13344 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.3231 | 152.3 | 0.31914 | 48.6052
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.13344 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.6858 | 177.5 | 0.31914 | 56.6476
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.13327 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.0841 | 150.7 | 0.31897 | 48.0691
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.13327 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.1241 | 151 | 0.31897 | 48.1648
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.13327 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.6425 | 177.4 | 0.31897 | 56.5857
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.13304 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.3972 | 236 | 0.31874 | 75.2225
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.13303 | west | 6 | Y | N | Ywest | Nwest | 1 | 53.212 | 400 | 0.31873 | 127.4922
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.13196 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.1536 | 615 | 0.31766 | 195.3593
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.13196 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 77.4588 | 587 | 0.31766 | 186.4649
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.1304 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.824 | 60 | 0.3161 | 18.966
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12855 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.2827 | 150 | 0.31425 | 47.1377
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.12847 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.8504 | 209 | 0.31417 | 65.6618
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.12847 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.2516 | 126.5 | 0.31417 | 39.7427
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.12847 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.9893 | 249 | 0.31417 | 78.2287
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.12847 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.3088 | 197 | 0.31417 | 61.8918
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8066 | 37.5 | 0.31388 | 11.7704
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.779 | 107.5 | 0.31388 | 33.7418
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.3039 | 135 | 0.31388 | 42.3735
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.2531 | 119 | 0.31388 | 37.3514
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.4586 | 105 | 0.31388 | 32.9571
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.3182 | 80.5 | 0.31388 | 25.2671
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12752 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9406 | 125 | 0.31323 | 39.1532
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12752 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9406 | 125 | 0.31323 | 39.1532
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.12717 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.0759 | 150 | 0.31287 | 46.931
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.12717 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.8445 | 101 | 0.31287 | 31.6002
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.12711 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6773 | 84 | 0.31281 | 26.2762
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.12678 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5515 | 99 | 0.31248 | 30.9359
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.12678 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7338 | 61 | 0.31248 | 19.0615
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.12678 | west | 7 | N | N | Nwest | Nwest | 1 | 3.1696 | 0 | 0.31248 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12678 | west | 7 | N | N | Nwest | Nwest | 1 | 5.794 | 0 | 0.31248 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12678 | west | 7 | N | N | Nwest | Nwest | 1 | 5.794 | 0 | 0.31248 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.12675 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8712 | 141 | 0.31245 | 44.055
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.12675 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.2095 | 120 | 0.31245 | 37.4936
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.12664 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9782 | 63 | 0.31234 | 19.6773
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3511 | 66 | 0.31223 | 20.6073
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7307 | 69 | 0.31223 | 21.544
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7307 | 69 | 0.31223 | 21.544
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.4776 | 67 | 0.31223 | 20.9196
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.4776 | 67 | 0.31223 | 20.9196
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2246 | 65 | 0.31223 | 20.2951
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12626 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.9392 | 150 | 0.31196 | 46.7942
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12626 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.7774 | 220 | 0.31196 | 68.6315
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12626 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.2522 | 200 | 0.31196 | 62.3923
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12626 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3912 | 121.9 | 0.31196 | 38.0281
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12589 | west | 8 | N | N | Nwest | Nwest | 1 | 8.8125 | 0 | 0.31159 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12589 | west | 8 | N | N | Nwest | Nwest | 1 | 9.2405 | 0 | 0.31159 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12589 | west | 8 | N | N | Nwest | Nwest | 1 | 8.8629 | 0 | 0.31159 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12589 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6597 | 180 | 0.31159 | 56.0857
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12589 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6597 | 180 | 0.31159 | 56.0857
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.12577 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.2976 | 225 | 0.31147 | 70.0802
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.1255 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0599 | 120 | 0.3112 | 37.3439
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.12545 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0534 | 120 | 0.31115 | 37.3375
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12529 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0353 | 120 | 0.31099 | 37.3193
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12529 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.1935 | 233 | 0.31099 | 72.4617
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12529 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.325 | 170.2 | 0.31099 | 52.9313
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.12464 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.6979 | 214.2 | 0.31034 | 66.4749
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.12464 | west | 8 | N | N | Nwest | Nwest | 1 | 3.2157 | 0 | 0.31034 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12435 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.4974 | 100.5 | 0.31005 | 31.1603
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.12433 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2113 | 58 | 0.31003 | 17.9819
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.6996 | 70 | 0.30998 | 21.6986
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.6996 | 70 | 0.30998 | 21.6986
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.5332 | 92.8 | 0.30998 | 28.7662
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.9424 | 80 | 0.30998 | 24.7984
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.9424 | 80 | 0.30998 | 24.7984
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.2922 | 115 | 0.30998 | 35.6478
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.8705 | 208.2 | 0.30996 | 64.5334
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.6571 | 142.1 | 0.30996 | 44.0451
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.4518 | 132.4 | 0.30996 | 41.0385
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.8991 | 136 | 0.30996 | 42.1544
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.2659 | 147 | 0.30996 | 45.5639
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.0942 | 210 | 0.30996 | 65.0913
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.12389 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.5838 | 150 | 0.30959 | 46.4389
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12333 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.8742 | 112.5 | 0.30903 | 34.7655
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12333 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.4372 | 149.5 | 0.30903 | 46.1995
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12333 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.9386 | 186 | 0.30903 | 57.4789
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12333 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.4534 | 214.5 | 0.30903 | 66.2862
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12275 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.81013 | 6.6 | 0.30845 | 2.0358
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12275 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2102 | 34.3 | 0.30845 | 10.5797
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.1225 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.2526 | 149 | 0.3082 | 45.922
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.12212 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2741 | 35 | 0.30782 | 10.7736
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.12212 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6635 | 30 | 0.30782 | 9.2345
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.0523 | 66 | 0.3077 | 20.3085
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.9303 | 65 | 0.3077 | 20.0008
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1743 | 67 | 0.3077 | 20.6162
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1743 | 67 | 0.3077 | 20.6162
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1743 | 67 | 0.3077 | 20.6162
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.122 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3077 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.122 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3077 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.12135 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.5685 | 169.5 | 0.30705 | 52.0447
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.11374 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.54593 | 0 | 0.29944 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.11176 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 92.423 | 827 | 0.29746 | 245.9973
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.11176 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 91.529 | 819 | 0.29746 | 243.6177
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11031 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8247 | 80 | 0.29601 | 23.6808
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11031 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8247 | 80 | 0.29601 | 23.6808
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.10939 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2043 | 75 | 0.29509 | 22.1319
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10939 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7513 | 80 | 0.29509 | 23.6073
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.10939 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3756 | 40 | 0.29509 | 11.8037
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10919 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7354 | 80 | 0.29489 | 23.5914
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.10916 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7332 | 80 | 0.29487 | 23.5892
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.10905 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.3572 | 150 | 0.29475 | 44.2123
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.10905 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.3572 | 150 | 0.29475 | 44.2123
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10446 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3565 | 80 | 0.29016 | 23.2125
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.10365 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9295 | 76.5 | 0.28935 | 22.1356
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.10291 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6442 | 84 | 0.28861 | 24.243
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.094903 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.1421 | 855 | 0.2806 | 239.916
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.094903 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.1421 | 855 | 0.2806 | 239.916
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.094903 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.4537 | 152.3 | 0.2806 | 42.7359
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.094903 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.5202 | 153 | 0.2806 | 42.9323
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.078216 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.26392 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.055959 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 25.909 | 463 | 0.24166 | 111.8883
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.055321 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2981 | 150 | 0.24102 | 36.1532
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.046689 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23239 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.046689 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23239 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.046689 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.79371 | 17 | 0.23239 | 3.9506
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.046689 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23239 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.046689 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23239 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.046607 | north | 7 | N | N | Nnorth | Nnorth | 1 | 1.4914 | 0 | 0.23231 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.044771 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.9037 | 0 | 0.23047 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.044771 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.9843 | 0 | 0.23047 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.044771 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.9843 | 0 | 0.23047 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.044771 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.013 | 0 | 0.23047 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.042415 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.0359 | 48 | 0.22812 | 10.9495
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.042415 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.9511 | 46 | 0.22812 | 10.4933
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.042415 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.4536 | 105 | 0.22812 | 23.9521
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.1857 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.1857 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.099921 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.085779 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -18.914 | 100 | -0.0034395 | -0.34395
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13953 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13953 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13953 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13953 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13953 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13953 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13953 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13953 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.015225 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6339 | 0 | -0.15476 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.015225 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3751 | 0 | -0.15476 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.015225 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3447 | 0 | -0.15476 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.015225 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3447 | 0 | -0.15476 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.015225 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4665 | 0 | -0.15476 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2103 | 56 | -0.16114 | -9.0241
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2752 | 59 | -0.16114 | -9.5075
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2103 | 56 | -0.16114 | -9.0241
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2103 | 56 | -0.16114 | -9.0241
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2752 | 59 | -0.16114 | -9.5075
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2103 | 56 | -0.16114 | -9.0241
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.022274 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.8651 | 398 | -0.1618 | -64.3983
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.02265 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6874 | 0 | -0.16218 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.02265 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6557 | 0 | -0.16218 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.02265 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5991 | 0 | -0.16218 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.02265 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0974 | 0 | -0.16218 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.023734 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.0822 | 172 | -0.16326 | -28.0815
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.023734 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.0822 | 172 | -0.16326 | -28.0815
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.023734 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.0822 | 172 | -0.16326 | -28.0815
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.023916 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7548 | 0 | -0.16345 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.024196 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -17.9776 | 743 | -0.16373 | -121.649
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.024238 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.29086 | 12 | -0.16377 | -1.9652
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5774 | 0 | -0.1638 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6016 | 0 | -0.1638 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6987 | 0 | -0.1638 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5288 | 0 | -0.1638 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5046 | 0 | -0.1638 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5238 | 0 | -0.1638 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4318 | 0 | -0.1638 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.024277 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12139 | 0 | -0.16381 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.024277 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50982 | 0 | -0.16381 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.024881 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.29857 | 12 | -0.16441 | -1.9729
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86214 | 0 | -0.16489 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.87989 | 0 | -0.16489 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.82917 | 0 | -0.16489 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1639 | 0 | -0.16489 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.44882 | 0 | -0.16489 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51728 | 0 | -0.16489 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5046 | 0 | -0.16489 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8875 | 0 | -0.16489 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45643 | 0 | -0.16489 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1655 | 0 | -0.16489 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7528 | 0 | -0.16489 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.02573 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -18.9115 | 735 | -0.16526 | -121.4667
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.7341 | 104 | -0.16582 | -17.2453
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.7341 | 104 | -0.16582 | -17.2453
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4196 | 54 | -0.16582 | -8.9543
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.3933 | 53 | -0.16582 | -8.7884
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4196 | 54 | -0.16582 | -8.9543
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4985 | 57 | -0.16582 | -9.4517
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4196 | 54 | -0.16582 | -8.9543
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4196 | 54 | -0.16582 | -8.9543
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5248 | 58 | -0.16582 | -9.6175
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5248 | 58 | -0.16582 | -9.6175
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.027743 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7995 | 0 | -0.16727 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.027743 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7453 | 0 | -0.16727 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.027975 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1749 | 42 | -0.16751 | -7.0352
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.027975 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1749 | 42 | -0.16751 | -7.0352
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.027975 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0631 | 38 | -0.16751 | -6.3652
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.027975 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0631 | 38 | -0.16751 | -6.3652
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.028047 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8144 | 0 | -0.16758 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.028953 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0557 | 0 | -0.16848 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.028953 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0846 | 0 | -0.16848 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.028953 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1292 | 0 | -0.16848 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.028953 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86859 | 0 | -0.16848 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.029524 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.3143 | 0 | -0.16905 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.029524 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.6825 | 0 | -0.16905 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.029524 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.6353 | 0 | -0.16905 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.029538 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.7347 | 228 | -0.16907 | -38.5477
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.029553 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8914 | 0 | -0.16908 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.029553 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8677 | 0 | -0.16908 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.029553 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4411 | 0 | -0.16908 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.029553 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1751 | 0 | -0.16908 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.02956 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47887 | 0 | -0.16909 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.02957 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.2984 | 213 | -0.1691 | -36.0185
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.029653 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4183 | 0 | -0.16918 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.029653 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9304 | 0 | -0.16918 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.029678 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.8969 | 165 | -0.16921 | -27.9195
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.02971 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.021 | 169 | -0.16924 | -28.6017
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.029732 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.35678 | 12 | -0.16926 | -2.0312
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.029732 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16926 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.030137 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0548 | 0 | -0.16967 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9799 | 0 | -0.17004 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.7937 | 0 | -0.17004 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.806 | 0 | -0.17004 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.7907 | 0 | -0.17004 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.2083 | 0 | -0.17004 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.030979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4164 | 0 | -0.17051 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.030979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4783 | 0 | -0.17051 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4405 | 46 | -0.17085 | -7.859
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4405 | 46 | -0.17085 | -7.859
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4405 | 46 | -0.17085 | -7.859
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7224 | 55 | -0.17085 | -9.3966
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7224 | 55 | -0.17085 | -9.3966
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6911 | 54 | -0.17085 | -9.2257
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.032665 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1232 | 0 | -0.1722 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.032665 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9599 | 0 | -0.1722 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.032665 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1232 | 0 | -0.1722 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.032665 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1232 | 0 | -0.1722 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0551 | 0 | -0.1731 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9409 | 0 | -0.1731 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9208 | 0 | -0.1731 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8297 | 0 | -0.1731 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40958 | 0 | -0.1731 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.035886 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.17542 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.03787 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8935 | 50 | -0.1774 | -8.87
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.040414 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8613 | 0 | -0.17994 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.040414 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6956 | 0 | -0.17994 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.040414 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1419 | 0 | -0.17994 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1914 | 0 | -0.17994 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.2035 | 0 | -0.17994 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1551 | 0 | -0.17994 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8797 | 0 | -0.17994 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.861 | 0 | -0.17994 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.040414 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6166 | 0 | -0.17994 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.040446 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2943 | 0 | -0.17998 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.040446 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2134 | 0 | -0.17998 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.040447 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0568 | 0 | -0.17998 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.040447 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7575 | 0 | -0.17998 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.040447 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1539 | 0 | -0.17998 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.040447 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1256 | 0 | -0.17998 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.046651 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.5108 | 161 | -0.18618 | -29.9753
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.046651 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.7441 | 166 | -0.18618 | -30.9062
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.046651 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.5694 | 248 | -0.18618 | -46.1731
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.046651 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -25.4714 | 546 | -0.18618 | -101.6553
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.046651 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -29.9966 | 0 | -0.18618 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.046651 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.60646 | 13 | -0.18618 | -2.4204
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.047183 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.557 | 0 | -0.18671 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.048419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.8923 | 0 | -0.18795 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.048419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.8923 | 0 | -0.18795 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.048419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.8627 | 0 | -0.18795 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.048518 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -31.5852 | 651 | -0.18805 | -122.4198
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.048518 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -27.3642 | 564 | -0.18805 | -106.0595
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.048518 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -29.1108 | 600 | -0.18805 | -112.8293
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.048944 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2563 | 0 | -0.18847 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.060736 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.7417 | 0 | -0.20027 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.060736 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.7417 | 0 | -0.20027 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.060736 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.2276 | 0 | -0.20027 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.060736 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.6506 | 0 | -0.20027 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.063994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5436 | 0 | -0.20352 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.063994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63994 | 0 | -0.20352 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2233 | 0 | -0.20765 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8636 | 0 | -0.20765 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0653 | 0 | -0.20765 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8798 | 0 | -0.20765 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8581 | 0 | -0.20765 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9943 | 0 | -0.20765 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4059 | 0 | -0.20765 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2261 | 0 | -0.20765 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.403 | 0 | -0.20765 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7682 | 0 | -0.20765 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2914 | 0 | -0.20765 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9044 | 0 | -0.20765 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.414 | 0 | -0.20765 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8798 | 0 | -0.20765 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6073 | 0 | -0.20765 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0161 | 0 | -0.20765 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.1769 | 0 | -0.20765 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4494 | 0 | -0.20765 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4494 | 0 | -0.20765 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.648 | 0 | -0.20765 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.085133 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.6188 | 66 | -0.22466 | -14.8278
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.086262 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.8466 | 0 | -0.22579 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.086262 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.1566 | 0 | -0.22579 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.086262 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.22579 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.8802 | 76 | -0.23006 | -17.4845
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.8802 | 76 | -0.23006 | -17.4845
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5055 | 105 | -0.23006 | -24.1563
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6991 | 74 | -0.23006 | -17.0244
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6991 | 74 | -0.23006 | -17.0244
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.234 | 102 | -0.23006 | -23.4661
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.091159 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -121.5149 | 0 | -0.23069 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.091159 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -121.0592 | 0 | -0.23069 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.109 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.65402 | 0 | -0.24853 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.11429 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25382 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.7308 | 0 | -0.27536 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.0025 | 0 | -0.27536 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.7308 | 0 | -0.27536 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.8666 | 0 | -0.27536 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.6493 | 0 | -0.27536 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3958 | 0 | -0.27536 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.2483 | 0 | -0.27536 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8033 | 0 | -0.27536 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9223 | 0 | -0.27536 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.0516 | 0 | -0.27536 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.13707 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.5793 | 0 | -0.2766 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.9503 | 0 | -0.28061 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.98757 | 0 | -0.28061 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5022 | 0 | -0.28061 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1162 | 0 | -0.28061 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.98757 | 0 | -0.28061 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1162 | 0 | -0.28061 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5022 | 0 | -0.28061 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5022 | 0 | -0.28061 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.14168 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1334 | 0 | -0.28121 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.14276 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1414 | 0 | -0.28229 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.14276 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2835 | 0 | -0.28229 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.14405 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.1691 | 22 | -0.28358 | -6.2388
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.14405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5846 | 11 | -0.28358 | -3.1194
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.14405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5846 | 11 | -0.28358 | -3.1194
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.14541 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9361 | 47.7 | -0.28494 | -13.5917
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.14541 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4238 | 37.3 | -0.28494 | -10.6283
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.14541 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6889 | 46 | -0.28494 | -13.1073
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.14541 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9797 | 48 | -0.28494 | -13.6772
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.14573 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.638 | 0 | -0.28526 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -23.1432 | 0 | -0.28601 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.4108 | 0 | -0.28601 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -14.6476 | 0 | -0.28601 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.239 | 0 | -0.28601 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.532 | 0 | -0.28601 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -18.6025 | 0 | -0.28601 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.14648 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7577 | 0 | -0.28601 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6775 | 25 | -0.28663 | -7.1657
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6775 | 25 | -0.28663 | -7.1657
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6775 | 25 | -0.28663 | -7.1657
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.3536 | 16 | -0.28663 | -4.5861
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6775 | 25 | -0.28663 | -7.1657
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6775 | 25 | -0.28663 | -7.1657
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6775 | 25 | -0.28663 | -7.1657
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2065 | 15 | -0.28663 | -4.2994
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.14742 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.2283 | 144 | -0.28695 | -41.3208
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.14742 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.7148 | 188 | -0.28695 | -53.9466
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.14806 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -49.7472 | 336 | -0.28759 | -96.6295
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.14806 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6503 | 180 | -0.28759 | -51.7658
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.14808 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.9595 | 0 | -0.28761 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.14808 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.0039 | 0 | -0.28761 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.14808 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.6555 | 0 | -0.28761 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.1481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6589 | 180 | -0.28764 | -51.7744
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.14841 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -49.5683 | 334 | -0.28794 | -96.1716
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.14841 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -50.4587 | 340 | -0.28794 | -97.8992
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.14841 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.7134 | 180 | -0.28794 | -51.829
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.14841 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.7134 | 180 | -0.28794 | -51.829
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.14846 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7116 | 0 | -0.28799 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.14846 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7116 | 0 | -0.28799 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.14861 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6474 | 0 | -0.28815 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.14863 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6478 | 0 | -0.28816 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.14936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.3314 | 0 | -0.28889 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -14.0627 | 94 | -0.28913 | -27.1786
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.1337 | 41 | -0.28913 | -11.8545
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.6849 | 38 | -0.28913 | -10.9871
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8425 | 19 | -0.28913 | -5.4935
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -14.0627 | 94 | -0.28913 | -27.1786
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.3857 | 36 | -0.28913 | -10.4088
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.4329 | 43 | -0.28913 | -12.4328
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2913 | 22 | -0.28913 | -6.3609
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -22.1412 | 148 | -0.28913 | -42.7918
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.4802 | 50 | -0.28913 | -14.4567
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.2282 | 55 | -0.28913 | -15.9024
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.4802 | 50 | -0.28913 | -14.4567
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.14971 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28924 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.14971 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.6889 | 38 | -0.28924 | -10.9911
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.14971 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8894 | 19.3 | -0.28924 | -5.5823
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.14971 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2456 | 15 | -0.28924 | -4.3386
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.14971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.0363 | 47 | -0.28924 | -13.5942
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.6009 | 144 | -0.28954 | -41.6933
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.6009 | 144 | -0.28954 | -41.6933
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.651 | 171 | -0.28954 | -49.5108
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.0523 | 207 | -0.28954 | -59.9352
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.5074 | 216.7 | -0.28954 | -62.7437
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.3027 | 242 | -0.28954 | -70.0691
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.15032 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.0216 | 146.5 | -0.28985 | -42.4629
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.15032 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.232 | 147.9 | -0.28985 | -42.8686
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.15032 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.005 | 173 | -0.28985 | -50.1438
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.15224 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8268 | 0 | -0.29177 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.15224 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6746 | 0 | -0.29177 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.15224 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8268 | 0 | -0.29177 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.15224 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29177 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.15407 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.2936 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.15466 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -97.2805 | 629 | -0.29419 | -185.0454
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.15679 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29632 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.15819 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29772 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.1582 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -15.8202 | 100 | -0.29773 | -29.7733
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.1582 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -15.8202 | 100 | -0.29773 | -29.7733
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.1582 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29773 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.1582 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29773 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.1582 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29773 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.1582 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29773 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.15942 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.8261 | 24 | -0.29895 | -7.1749
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.15942 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.8261 | 24 | -0.29895 | -7.1749
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.15942 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.6667 | 23 | -0.29895 | -6.8759
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.16909 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -66.9596 | 396 | -0.30862 | -122.2138
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.1785 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.142 | 0 | -0.31803 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.17898 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -97.7225 | 546 | -0.31851 | -173.9064
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.17898 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -134.2343 | 750 | -0.31851 | -238.8824
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.17927 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.3975 | 58 | -0.3188 | -18.4903
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.17927 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.9548 | 89 | -0.3188 | -28.373
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.17927 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8877 | 44 | -0.3188 | -14.0271
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.17927 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8877 | 44 | -0.3188 | -14.0271
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.17927 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7085 | 43 | -0.3188 | -13.7083
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.17927 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.067 | 45 | -0.3188 | -14.3459
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.17991 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.8861 | 155 | -0.31944 | -49.5133
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.17991 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -30.5847 | 170 | -0.31944 | -54.3049
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.17991 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.8861 | 155 | -0.31944 | -49.5133
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.18028 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -73.3756 | 407 | -0.31981 | -130.1646
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.18036 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -37.6957 | 209 | -0.31989 | -66.8576
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.18036 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -38.9582 | 216 | -0.31989 | -69.0968
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.18036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.2967 | 46 | -0.31989 | -14.7151
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.18036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.477 | 47 | -0.31989 | -15.035
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.18036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.2967 | 46 | -0.31989 | -14.7151
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.18036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.2967 | 46 | -0.31989 | -14.7151
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.18057 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -74.3948 | 412 | -0.3201 | -131.8815
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.18057 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -72.228 | 400 | -0.3201 | -128.0403
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.1807 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -76.6181 | 424 | -0.32023 | -135.7791
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.1807 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -76.7988 | 425 | -0.32023 | -136.0994
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.18122 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32075 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.18122 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32075 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.18122 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32075 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.242 | 147 | -0.32485 | -47.7531
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.5742 | 138 | -0.32485 | -44.8294
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.9448 | 140 | -0.32485 | -45.4791
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.242 | 147 | -0.32485 | -47.7531
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -33.7282 | 182 | -0.32485 | -59.1228
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.6934 | 198 | -0.32485 | -64.3205
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -21.562 | 114 | -0.32867 | -37.4685
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -41.9891 | 222 | -0.32867 | -72.9649
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -34.8018 | 184 | -0.32867 | -60.4754
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -42.3674 | 224 | -0.32867 | -73.6223
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -21.7511 | 115 | -0.32867 | -37.7971
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.19019 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.76074 | 0 | -0.32972 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.19032 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.45678 | 0 | -0.32985 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.19032 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.45678 | 0 | -0.32985 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.19225 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.2992 | 142 | -0.33178 | -47.1126
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.19225 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.876 | 145 | -0.33178 | -48.1079
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.19225 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.0294 | 151 | -0.33178 | -50.0986
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.19225 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -55.7519 | 290 | -0.33178 | -96.2159
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.19302 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46325 | 0 | -0.33255 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.19302 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46325 | 0 | -0.33255 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.19302 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54045 | 0 | -0.33255 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.19826 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.7162 | 0 | -0.33779 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.19955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -44.6783 | 223.9 | -0.33908 | -75.9193
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.19955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -44.8978 | 225 | -0.33908 | -76.2923
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.19955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -44.818 | 224.6 | -0.33908 | -76.1567
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.19955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.2371 | 226.7 | -0.33908 | -76.8687
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.20109 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.6197 | 0 | -0.34062 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.20109 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.6197 | 0 | -0.34062 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.20109 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.0164 | 0 | -0.34062 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.2028 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -85.5799 | 422 | -0.34233 | -144.4619
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.20399 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -88.3272 | 433 | -0.34352 | -148.7441
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.2042 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -119.2505 | 584 | -0.34373 | -200.7365
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.2042 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -121.4966 | 595 | -0.34373 | -204.5175
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.20433 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.7211 | 0 | -0.34386 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.20433 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.9254 | 0 | -0.34386 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.20459 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.2275 | 0 | -0.34412 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.20642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.3211 | 50 | -0.34595 | -17.2977
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.20642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.3211 | 50 | -0.34595 | -17.2977
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.20642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.3211 | 50 | -0.34595 | -17.2977
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.20642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.3211 | 50 | -0.34595 | -17.2977
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.21066 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.7918 | 0 | -0.35019 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.21066 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.7918 | 0 | -0.35019 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.22729 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.0023 | 132 | -0.36682 | -48.4203
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.22729 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.4569 | 134 | -0.36682 | -49.154
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.22729 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -73.4147 | 323 | -0.36682 | -118.4831
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.22849 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.997 | 0 | -0.36802 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.22849 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.7686 | 0 | -0.36802 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.22849 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.997 | 0 | -0.36802 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.22987 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.3195 | 158 | -0.3694 | -58.3653
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.22987 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.7792 | 160 | -0.3694 | -59.1041
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.22987 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -40.2272 | 175 | -0.3694 | -64.6451
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.23152 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.3073 | 152.5 | -0.37105 | -56.5857
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.23152 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.6127 | 149.5 | -0.37105 | -55.4725
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.23152 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -53.8522 | 232.6 | -0.37105 | -86.3071
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.5108 | 49 | -0.37445 | -18.3478
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.8061 | 46 | -0.37445 | -17.2245
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.8061 | 46 | -0.37445 | -17.2245
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.041 | 47 | -0.37445 | -17.599
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.23492 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.1769 | 154 | -0.37445 | -57.6647
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.23492 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.7674 | 148 | -0.37445 | -55.418
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.2759 | 48 | -0.37445 | -17.9734
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.2759 | 48 | -0.37445 | -17.9734
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.23658 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8926 | 0 | -0.37611 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.23658 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8926 | 0 | -0.37611 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.23759 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -73.6538 | 310 | -0.37712 | -116.9084
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.23759 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -98.1259 | 413 | -0.37712 | -155.7521
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.24016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.0867 | 42 | -0.37969 | -15.947
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.24016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.567 | 44 | -0.37969 | -16.7064
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.24016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.567 | 44 | -0.37969 | -16.7064
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.24016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.2875 | 47 | -0.37969 | -17.8455
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.28306 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -161.0583 | 569 | -0.42259 | -240.4513
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.28306 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -164.455 | 581 | -0.42259 | -245.5224

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3409 LAKE_CRK 3414 TEMP_SS_ctg2 C:THOUSE__5-LAKE_CRK1_5 C:THOUSE__5-AEP_PEC__59 [3405 - 3409] and [3405 - 3412] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.28306 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -161.0583 | 0 | -0.42259 | 0 | 0 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.28306 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -164.455 | 0 | -0.42259 | 0 | 0 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.24016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.0867 | 42 | -0.37969 | -15.947 | 42 | 15.947
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.24016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.567 | 44 | -0.37969 | -16.7064 | 86 | 32.6534 | Weighted Shift Factors
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.24016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.567 | 44 | -0.37969 | -16.7064 | 130 | 49.3598 | North | 0.13953
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.24016 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.2875 | 47 | -0.37969 | -17.8455 | 177 | 67.2053 | South | -0.1857
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.23759 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -73.6538 | 310 | -0.37712 | -116.9084 | 487 | 184.1137 |  | 0.32523
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.23759 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -98.1259 | 413 | -0.37712 | -155.7521 | 900 | 339.8658
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.23658 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8926 | 0 | -0.37611 | 0 | 900 | 339.8658 | Line Rating | 1239.6
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.23658 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8926 | 0 | -0.37611 | 0 | 900 | 339.8658 | Conc Gen | 2338.6
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.5108 | 49 | -0.37445 | -18.3478 | 949 | 358.2136 | Weighted Imp. | 875.1259
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.8061 | 46 | -0.37445 | -17.2245 | 995 | 375.4381 | PTDF | 0.37421
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.8061 | 46 | -0.37445 | -17.2245 | 1041 | 392.6626
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.041 | 47 | -0.37445 | -17.599 | 1088 | 410.2616 | Concentration | 1.1506
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.23492 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.1769 | 154 | -0.37445 | -57.6647 | 1242 | 467.9263
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.23492 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.7674 | 148 | -0.37445 | -55.418 | 1390 | 523.3442
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.2759 | 48 | -0.37445 | -17.9734 | 1438 | 541.3176
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.23492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -11.2759 | 48 | -0.37445 | -17.9734 | 1486 | 559.291
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.23152 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.3073 | 152.5 | -0.37105 | -56.5857 | 1638.5 | 615.8767
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.23152 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.6127 | 149.5 | -0.37105 | -55.4725 | 1788 | 671.3493
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.23152 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -53.8522 | 232.6 | -0.37105 | -86.3071 | 2020.6 | 757.6564
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.22987 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.3195 | 158 | -0.3694 | -58.3653 | 2178.6 | 816.0217
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.22987 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.7792 | 160 | -0.3694 | -59.1041 | 2338.6 | 875.1259
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.22987 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -40.2272 | 175 | -0.3694 | -64.6451
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.22849 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.997 | 0 | -0.36802 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.22849 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.7686 | 0 | -0.36802 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.22849 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.997 | 0 | -0.36802 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.22729 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.0023 | 132 | -0.36682 | -48.4203
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.22729 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -30.4569 | 134 | -0.36682 | -49.154
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.22729 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -73.4147 | 323 | -0.36682 | -118.4831
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.21066 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.7918 | 0 | -0.35019 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.21066 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.7918 | 0 | -0.35019 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.20642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.3211 | 50 | -0.34595 | -17.2977
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.20642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.3211 | 50 | -0.34595 | -17.2977
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.20642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.3211 | 50 | -0.34595 | -17.2977
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.20642 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.3211 | 50 | -0.34595 | -17.2977
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.20459 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.2275 | 0 | -0.34412 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.20433 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.7211 | 0 | -0.34386 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.20433 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.9254 | 0 | -0.34386 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.2042 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -119.2505 | 0 | -0.34373 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.2042 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -121.4966 | 0 | -0.34373 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.20399 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -88.3272 | 0 | -0.34352 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.2028 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -85.5799 | 422 | -0.34233 | -144.4619
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.20109 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.6197 | 0 | -0.34062 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.20109 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.6197 | 0 | -0.34062 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.20109 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.0164 | 0 | -0.34062 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.19955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -44.6783 | 223.9 | -0.33908 | -75.9193
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.19955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -44.8978 | 225 | -0.33908 | -76.2923
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.19955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -44.818 | 224.6 | -0.33908 | -76.1567
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.19955 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -45.2371 | 226.7 | -0.33908 | -76.8687
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.19826 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.7162 | 0 | -0.33779 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.19302 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46325 | 0 | -0.33255 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.19302 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.46325 | 0 | -0.33255 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.19302 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54045 | 0 | -0.33255 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.19225 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.2992 | 142 | -0.33178 | -47.1126
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.19225 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.876 | 145 | -0.33178 | -48.1079
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.19225 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.0294 | 151 | -0.33178 | -50.0986
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.19225 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -55.7519 | 290 | -0.33178 | -96.2159
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.19032 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.45678 | 0 | -0.32985 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.19032 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.45678 | 0 | -0.32985 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.19019 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.76074 | 0 | -0.32972 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -21.562 | 0 | -0.32867 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -41.9891 | 0 | -0.32867 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -34.8018 | 0 | -0.32867 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -42.3674 | 0 | -0.32867 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -21.7511 | 0 | -0.32867 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.242 | 147 | -0.32485 | -47.7531
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.5742 | 138 | -0.32485 | -44.8294
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.9448 | 140 | -0.32485 | -45.4791
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.242 | 147 | -0.32485 | -47.7531
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -33.7282 | 182 | -0.32485 | -59.1228
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.18532 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.6934 | 198 | -0.32485 | -64.3205
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.18122 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32075 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.18122 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32075 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.18122 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.32075 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.1807 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -76.6181 | 0 | -0.32023 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.1807 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -76.7988 | 0 | -0.32023 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.18057 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -74.3948 | 412 | -0.3201 | -131.8815
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.18057 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -72.228 | 400 | -0.3201 | -128.0403
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.18036 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -37.6957 | 209 | -0.31989 | -66.8576
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.18036 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -38.9582 | 216 | -0.31989 | -69.0968
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.18036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.2967 | 46 | -0.31989 | -14.7151
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.18036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.477 | 47 | -0.31989 | -15.035
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.18036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.2967 | 46 | -0.31989 | -14.7151
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.18036 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.2967 | 46 | -0.31989 | -14.7151
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.18028 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -73.3756 | 407 | -0.31981 | -130.1646
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.17991 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.8861 | 155 | -0.31944 | -49.5133
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.17991 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -30.5847 | 170 | -0.31944 | -54.3049
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.17991 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.8861 | 155 | -0.31944 | -49.5133
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.17927 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -10.3975 | 58 | -0.3188 | -18.4903
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.17927 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.9548 | 89 | -0.3188 | -28.373
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.17927 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8877 | 44 | -0.3188 | -14.0271
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.17927 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8877 | 44 | -0.3188 | -14.0271
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.17927 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7085 | 43 | -0.3188 | -13.7083
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.17927 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.067 | 45 | -0.3188 | -14.3459
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.17898 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -97.7225 | 0 | -0.31851 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.17898 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -134.2343 | 0 | -0.31851 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.1785 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.142 | 0 | -0.31803 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.16909 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -66.9596 | 0 | -0.30862 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.15942 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.8261 | 24 | -0.29895 | -7.1749
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.15942 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.8261 | 24 | -0.29895 | -7.1749
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.15942 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.6667 | 23 | -0.29895 | -6.8759
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.1582 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -15.8202 | 100 | -0.29773 | -29.7733
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.1582 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -15.8202 | 100 | -0.29773 | -29.7733
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.1582 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29773 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.1582 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29773 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.1582 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29773 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.1582 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29773 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.15819 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29772 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.15761 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.3239 | 8.4 | -0.29714 | -2.496
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.15679 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29632 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.15466 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -97.2805 | 0 | -0.29419 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.15407 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.2936 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.15224 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.29177 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.15224 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8268 | 0 | -0.29177 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.15224 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6746 | 0 | -0.29177 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.15224 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8268 | 0 | -0.29177 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.15032 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.0216 | 146.5 | -0.28985 | -42.4629
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.15032 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.232 | 147.9 | -0.28985 | -42.8686
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.15032 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.005 | 173 | -0.28985 | -50.1438
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.0523 | 207 | -0.28954 | -59.9352
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.5074 | 216.7 | -0.28954 | -62.7437
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -36.3027 | 242 | -0.28954 | -70.0691
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.6009 | 144 | -0.28954 | -41.6933
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.6009 | 144 | -0.28954 | -41.6933
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.15001 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.651 | 171 | -0.28954 | -49.5108
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.14971 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.6889 | 38 | -0.28924 | -10.9911
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.14971 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8894 | 19.3 | -0.28924 | -5.5823
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.14971 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2456 | 15 | -0.28924 | -4.3386
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.14971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.0363 | 47 | -0.28924 | -13.5942
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.14971 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.28924 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -14.0627 | 0 | -0.28913 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.1337 | 0 | -0.28913 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.6849 | 0 | -0.28913 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8425 | 0 | -0.28913 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -14.0627 | 0 | -0.28913 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.3857 | 0 | -0.28913 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.4329 | 0 | -0.28913 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2913 | 0 | -0.28913 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -22.1412 | 0 | -0.28913 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.4802 | 0 | -0.28913 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.2282 | 0 | -0.28913 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.1496 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.4802 | 0 | -0.28913 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.14936 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.3314 | 0 | -0.28889 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.14863 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6478 | 0 | -0.28816 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.14861 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6474 | 0 | -0.28815 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.14846 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7116 | 0 | -0.28799 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.14846 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7116 | 0 | -0.28799 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.14841 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -49.5683 | 334 | -0.28794 | -96.1716
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.14841 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -50.4587 | 340 | -0.28794 | -97.8992
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.14841 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.7134 | 180 | -0.28794 | -51.829
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.14841 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.7134 | 180 | -0.28794 | -51.829
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.1481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6589 | 180 | -0.28764 | -51.7744
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.14808 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.9595 | 0 | -0.28761 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.14808 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.0039 | 0 | -0.28761 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.14808 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.6555 | 0 | -0.28761 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.14806 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -49.7472 | 336 | -0.28759 | -96.6295
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.14806 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.6503 | 180 | -0.28759 | -51.7658
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.14742 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.2283 | 144 | -0.28695 | -41.3208
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.14742 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.7148 | 188 | -0.28695 | -53.9466
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6775 | 0 | -0.28663 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6775 | 0 | -0.28663 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6775 | 0 | -0.28663 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.3536 | 0 | -0.28663 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6775 | 0 | -0.28663 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6775 | 0 | -0.28663 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6775 | 0 | -0.28663 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.1471 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2065 | 0 | -0.28663 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -23.1432 | 0 | -0.28601 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.4108 | 0 | -0.28601 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -14.6476 | 0 | -0.28601 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.239 | 0 | -0.28601 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.532 | 0 | -0.28601 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.14648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -18.6025 | 0 | -0.28601 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.14648 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7577 | 0 | -0.28601 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.14573 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.638 | 0 | -0.28526 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.14541 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9361 | 47.7 | -0.28494 | -13.5917
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.14541 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4238 | 37.3 | -0.28494 | -10.6283
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.14541 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6889 | 46 | -0.28494 | -13.1073
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.14541 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9797 | 48 | -0.28494 | -13.6772
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.14405 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.1691 | 22 | -0.28358 | -6.2388
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.14405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5846 | 11 | -0.28358 | -3.1194
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.14405 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5846 | 11 | -0.28358 | -3.1194
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.14276 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1414 | 0 | -0.28229 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.14276 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2835 | 0 | -0.28229 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.14168 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1334 | 0 | -0.28121 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.9503 | 0 | -0.28061 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.98757 | 0 | -0.28061 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5022 | 0 | -0.28061 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1162 | 0 | -0.28061 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.98757 | 0 | -0.28061 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1162 | 0 | -0.28061 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5022 | 0 | -0.28061 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.14108 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5022 | 0 | -0.28061 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.13707 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.5793 | 0 | -0.2766 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.7308 | 0 | -0.27536 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -11.0025 | 0 | -0.27536 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.7308 | 0 | -0.27536 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.8666 | 0 | -0.27536 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.6493 | 0 | -0.27536 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3958 | 0 | -0.27536 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.2483 | 0 | -0.27536 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8033 | 0 | -0.27536 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9223 | 0 | -0.27536 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.13583 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.0516 | 0 | -0.27536 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.11429 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25382 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.109 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.65402 | 0 | -0.24853 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.091159 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -121.5149 | 0 | -0.23069 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.091159 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -121.0592 | 0 | -0.23069 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.8802 | 76 | -0.23006 | -17.4845
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.8802 | 76 | -0.23006 | -17.4845
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.5055 | 105 | -0.23006 | -24.1563
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6991 | 74 | -0.23006 | -17.0244
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6991 | 74 | -0.23006 | -17.0244
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.090529 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.234 | 102 | -0.23006 | -23.4661
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.086262 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.8466 | 0 | -0.22579 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.086262 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.1566 | 0 | -0.22579 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.086262 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.22579 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.085133 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.6188 | 66 | -0.22466 | -14.8278
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2233 | 0 | -0.20765 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8636 | 0 | -0.20765 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0653 | 0 | -0.20765 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8798 | 0 | -0.20765 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8581 | 0 | -0.20765 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9943 | 0 | -0.20765 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4059 | 0 | -0.20765 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2261 | 0 | -0.20765 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.403 | 0 | -0.20765 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7682 | 0 | -0.20765 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2914 | 0 | -0.20765 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9044 | 0 | -0.20765 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.414 | 0 | -0.20765 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8798 | 0 | -0.20765 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6073 | 0 | -0.20765 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0161 | 0 | -0.20765 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.1769 | 0 | -0.20765 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4494 | 0 | -0.20765 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4494 | 0 | -0.20765 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.068117 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.648 | 0 | -0.20765 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.063994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5436 | 0 | -0.20352 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.063994 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63994 | 0 | -0.20352 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.060736 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.7417 | 0 | -0.20027 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.060736 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.7417 | 0 | -0.20027 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.060736 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.2276 | 0 | -0.20027 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.060736 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.6506 | 0 | -0.20027 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.048944 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2563 | 0 | -0.18847 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.048518 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -31.5852 | 0 | -0.18805 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.048518 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -27.3642 | 0 | -0.18805 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.048518 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -29.1108 | 0 | -0.18805 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.048419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.8923 | 0 | -0.18795 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.048419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.8923 | 0 | -0.18795 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.048419 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.8627 | 0 | -0.18795 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.047183 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.557 | 0 | -0.18671 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.046651 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.5108 | 161 | -0.18618 | -29.9753
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.046651 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.7441 | 166 | -0.18618 | -30.9062
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.046651 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.5694 | 248 | -0.18618 | -46.1731
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.046651 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -25.4714 | 546 | -0.18618 | -101.6553
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.046651 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -29.9966 | 0 | -0.18618 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.046651 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.60646 | 13 | -0.18618 | -2.4204
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.040447 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0568 | 0 | -0.17998 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.040447 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7575 | 0 | -0.17998 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.040447 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1539 | 0 | -0.17998 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.040447 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1256 | 0 | -0.17998 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.040446 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2943 | 0 | -0.17998 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.040446 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2134 | 0 | -0.17998 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.040414 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8613 | 0 | -0.17994 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.040414 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6956 | 0 | -0.17994 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.040414 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1419 | 0 | -0.17994 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1914 | 0 | -0.17994 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.2035 | 0 | -0.17994 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1551 | 0 | -0.17994 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8797 | 0 | -0.17994 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.040414 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.861 | 0 | -0.17994 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.040414 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6166 | 0 | -0.17994 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.03787 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8935 | 50 | -0.1774 | -8.87
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.035886 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.17542 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0551 | 0 | -0.1731 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9409 | 0 | -0.1731 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9208 | 0 | -0.1731 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8297 | 0 | -0.1731 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.033572 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40958 | 0 | -0.1731 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.032665 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1232 | 0 | -0.1722 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.032665 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9599 | 0 | -0.1722 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.032665 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1232 | 0 | -0.1722 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.032665 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1232 | 0 | -0.1722 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4405 | 46 | -0.17085 | -7.859
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4405 | 46 | -0.17085 | -7.859
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4405 | 46 | -0.17085 | -7.859
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7224 | 55 | -0.17085 | -9.3966
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7224 | 55 | -0.17085 | -9.3966
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.031316 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6911 | 54 | -0.17085 | -9.2257
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.030979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4164 | 0 | -0.17051 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.030979 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4783 | 0 | -0.17051 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9799 | 0 | -0.17004 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.7937 | 0 | -0.17004 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.806 | 0 | -0.17004 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.7907 | 0 | -0.17004 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.030514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.2083 | 0 | -0.17004 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.030137 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0548 | 0 | -0.16967 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.029732 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.35678 | 12 | -0.16926 | -2.0312
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.029732 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16926 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.02971 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.021 | 169 | -0.16924 | -28.6017
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.029678 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.8969 | 165 | -0.16921 | -27.9195
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.029653 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4183 | 0 | -0.16918 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.029653 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9304 | 0 | -0.16918 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.02957 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.2984 | 213 | -0.1691 | -36.0185
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.02956 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47887 | 0 | -0.16909 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.029553 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8914 | 0 | -0.16908 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.029553 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8677 | 0 | -0.16908 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.029553 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4411 | 0 | -0.16908 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.029553 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1751 | 0 | -0.16908 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.029538 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.7347 | 228 | -0.16907 | -38.5477
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.029524 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.3143 | 0 | -0.16905 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.029524 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.6825 | 0 | -0.16905 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.029524 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.6353 | 0 | -0.16905 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.028953 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0557 | 0 | -0.16848 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.028953 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0846 | 0 | -0.16848 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.028953 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1292 | 0 | -0.16848 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.028953 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86859 | 0 | -0.16848 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.028047 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8144 | 0 | -0.16758 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.027975 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1749 | 42 | -0.16751 | -7.0352
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.027975 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1749 | 42 | -0.16751 | -7.0352
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.027975 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0631 | 38 | -0.16751 | -6.3652
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.027975 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0631 | 38 | -0.16751 | -6.3652
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.027743 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7995 | 0 | -0.16727 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.027743 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7453 | 0 | -0.16727 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.7341 | 104 | -0.16582 | -17.2453
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.7341 | 104 | -0.16582 | -17.2453
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4196 | 54 | -0.16582 | -8.9543
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.3933 | 53 | -0.16582 | -8.7884
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4196 | 54 | -0.16582 | -8.9543
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4985 | 57 | -0.16582 | -9.4517
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4196 | 54 | -0.16582 | -8.9543
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4196 | 54 | -0.16582 | -8.9543
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5248 | 58 | -0.16582 | -9.6175
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.026289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5248 | 58 | -0.16582 | -9.6175
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.02573 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -18.9115 | 735 | -0.16526 | -121.4667
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86214 | 0 | -0.16489 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.87989 | 0 | -0.16489 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.82917 | 0 | -0.16489 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1639 | 0 | -0.16489 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.44882 | 0 | -0.16489 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51728 | 0 | -0.16489 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5046 | 0 | -0.16489 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8875 | 0 | -0.16489 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45643 | 0 | -0.16489 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1655 | 0 | -0.16489 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.025357 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7528 | 0 | -0.16489 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.024881 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.29857 | 12 | -0.16441 | -1.9729
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.024277 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12139 | 0 | -0.16381 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.024277 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50982 | 0 | -0.16381 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5774 | 0 | -0.1638 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6016 | 0 | -0.1638 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6987 | 0 | -0.1638 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5288 | 0 | -0.1638 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5046 | 0 | -0.1638 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5238 | 0 | -0.1638 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.024267 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4318 | 0 | -0.1638 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.024238 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.29086 | 0 | -0.16377 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.024196 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -17.9776 | 743 | -0.16373 | -121.649
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.023916 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7548 | 0 | -0.16345 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.023734 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.0822 | 172 | -0.16326 | -28.0815
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.023734 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.0822 | 172 | -0.16326 | -28.0815
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.023734 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.0822 | 172 | -0.16326 | -28.0815
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.02265 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6874 | 0 | -0.16218 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.02265 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6557 | 0 | -0.16218 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.02265 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5991 | 0 | -0.16218 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.02265 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0974 | 0 | -0.16218 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.022274 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.8651 | 398 | -0.1618 | -64.3983
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2103 | 56 | -0.16114 | -9.0241
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2752 | 59 | -0.16114 | -9.5075
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2103 | 56 | -0.16114 | -9.0241
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2103 | 56 | -0.16114 | -9.0241
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2752 | 59 | -0.16114 | -9.5075
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.021613 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2103 | 56 | -0.16114 | -9.0241
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.015225 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6339 | 0 | -0.15476 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.015225 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3751 | 0 | -0.15476 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.015225 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3447 | 0 | -0.15476 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.015225 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3447 | 0 | -0.15476 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.015225 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4665 | 0 | -0.15476 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13953 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13953 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13953 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13953 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13953 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.13953 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13953 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13953 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.18914 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -18.914 | 0 | -0.0034395 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.099921 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.085779 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.1857 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.1857 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.042415 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.0359 | 48 | 0.22812 | 10.9495
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.042415 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.9511 | 46 | 0.22812 | 10.4933
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.042415 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.4536 | 105 | 0.22812 | 23.9521
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.044771 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.9037 | 0 | 0.23047 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.044771 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.9843 | 0 | 0.23047 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.044771 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.9843 | 0 | 0.23047 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.044771 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.013 | 0 | 0.23047 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.046607 | north | 7 | N | N | Nnorth | Nnorth | 1 | 1.4914 | 0 | 0.23231 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.046689 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23239 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.046689 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23239 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.046689 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.79371 | 17 | 0.23239 | 3.9506
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.046689 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23239 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.046689 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.23239 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.055321 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2981 | 0 | 0.24102 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.055959 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 25.909 | 0 | 0.24166 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.078216 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.26392 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.094903 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.1421 | 0 | 0.2806 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.094903 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.1421 | 0 | 0.2806 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.094903 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.4537 | 0 | 0.2806 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.094903 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.5202 | 0 | 0.2806 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.10291 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6442 | 0 | 0.28861 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.10365 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9295 | 0 | 0.28935 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10446 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3565 | 0 | 0.29016 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.10905 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.3572 | 0 | 0.29475 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.10905 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.3572 | 0 | 0.29475 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.10916 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7332 | 0 | 0.29487 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10919 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7354 | 0 | 0.29489 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.10939 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2043 | 0 | 0.29509 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10939 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7513 | 0 | 0.29509 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.10939 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3756 | 0 | 0.29509 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11031 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8247 | 0 | 0.29601 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.11031 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8247 | 0 | 0.29601 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.11176 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 92.423 | 0 | 0.29746 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.11176 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 91.529 | 0 | 0.29746 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.11374 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.54593 | 0 | 0.29944 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.12135 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.5685 | 0 | 0.30705 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.0523 | 66 | 0.3077 | 20.3085
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.9303 | 65 | 0.3077 | 20.0008
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1743 | 67 | 0.3077 | 20.6162
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1743 | 67 | 0.3077 | 20.6162
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.122 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.1743 | 67 | 0.3077 | 20.6162
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.122 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3077 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.122 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3077 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.12212 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2741 | 0 | 0.30782 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.12212 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6635 | 0 | 0.30782 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.1225 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.2526 | 0 | 0.3082 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.12275 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.81013 | 0 | 0.30845 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.12275 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2102 | 0 | 0.30845 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.12333 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.8742 | 0 | 0.30903 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.12333 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.4372 | 0 | 0.30903 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.12333 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.9386 | 0 | 0.30903 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.12333 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.4534 | 0 | 0.30903 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.12389 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.5838 | 0 | 0.30959 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 1 | 25.8705 | 208.2 | 0.30996 | 64.5334
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 1 | 17.6571 | 142.1 | 0.30996 | 44.0451
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.4518 | 132.4 | 0.30996 | 41.0385
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.8991 | 136 | 0.30996 | 42.1544
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 1 | 18.2659 | 147 | 0.30996 | 45.5639
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.12426 | west | 9 | Y | Y | Ywest | Ywest | 1 | 26.0942 | 210 | 0.30996 | 65.0913
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.6996 | 70 | 0.30998 | 21.6986
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.6996 | 70 | 0.30998 | 21.6986
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.5332 | 92.8 | 0.30998 | 28.7662
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.9424 | 80 | 0.30998 | 24.7984
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.9424 | 80 | 0.30998 | 24.7984
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.12428 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.2922 | 115 | 0.30998 | 35.6478
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.12433 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2113 | 0 | 0.31003 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.12435 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.4974 | 0 | 0.31005 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.12464 | west | 8 | N | N | Nwest | Nwest | 1 | 3.2157 | 0 | 0.31034 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.12464 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.6979 | 0 | 0.31034 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.12529 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0353 | 0 | 0.31099 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.12529 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.1935 | 0 | 0.31099 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.12529 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.325 | 0 | 0.31099 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.12545 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0534 | 0 | 0.31115 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.1255 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0599 | 0 | 0.3112 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.12577 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.2976 | 0 | 0.31147 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12589 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6597 | 0 | 0.31159 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.12589 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6597 | 0 | 0.31159 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.12589 | west | 8 | N | N | Nwest | Nwest | 1 | 8.8125 | 0 | 0.31159 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.12589 | west | 8 | N | N | Nwest | Nwest | 1 | 9.2405 | 0 | 0.31159 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.12589 | west | 8 | N | N | Nwest | Nwest | 1 | 8.8629 | 0 | 0.31159 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.12626 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.9392 | 0 | 0.31196 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.12626 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.7774 | 0 | 0.31196 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.12626 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.2522 | 0 | 0.31196 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.12626 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3912 | 0 | 0.31196 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.3511 | 66 | 0.31223 | 20.6073
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7307 | 69 | 0.31223 | 21.544
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.7307 | 69 | 0.31223 | 21.544
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.4776 | 67 | 0.31223 | 20.9196
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.4776 | 67 | 0.31223 | 20.9196
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.12653 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.2246 | 65 | 0.31223 | 20.2951
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.12664 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9782 | 0 | 0.31234 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.12675 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8712 | 0 | 0.31245 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.12675 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.2095 | 0 | 0.31245 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.12678 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5515 | 0 | 0.31248 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.12678 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7338 | 0 | 0.31248 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.12678 | west | 7 | N | N | Nwest | Nwest | 1 | 3.1696 | 0 | 0.31248 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12678 | west | 7 | N | N | Nwest | Nwest | 1 | 5.794 | 0 | 0.31248 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.12678 | west | 7 | N | N | Nwest | Nwest | 1 | 5.794 | 0 | 0.31248 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.12711 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6773 | 0 | 0.31281 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.12717 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.0759 | 0 | 0.31287 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.12717 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.8445 | 0 | 0.31287 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12752 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9406 | 0 | 0.31323 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.12752 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9406 | 0 | 0.31323 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8066 | 0 | 0.31388 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.779 | 0 | 0.31388 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.3039 | 0 | 0.31388 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.2531 | 0 | 0.31388 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.4586 | 0 | 0.31388 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.12818 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.3182 | 0 | 0.31388 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.12847 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.8504 | 0 | 0.31417 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.12847 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.2516 | 0 | 0.31417 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.12847 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.9893 | 0 | 0.31417 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.12847 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.3088 | 0 | 0.31417 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.12855 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.2827 | 0 | 0.31425 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.1304 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.824 | 0 | 0.3161 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.13196 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.1536 | 0 | 0.31766 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.13196 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 77.4588 | 0 | 0.31766 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.13303 | west | 6 | Y | N | Ywest | Nwest | 1 | 53.212 | 0 | 0.31873 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.13304 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.3972 | 0 | 0.31874 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.13327 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.0841 | 150.7 | 0.31897 | 48.0691
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.13327 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.1241 | 151 | 0.31897 | 48.1648
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.13327 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.6425 | 177.4 | 0.31897 | 56.5857
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.13344 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.2163 | 151.5 | 0.31914 | 48.3499
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.13344 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.3231 | 152.3 | 0.31914 | 48.6052
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.13344 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.6858 | 177.5 | 0.31914 | 56.6476
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.13464 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.2149 | 0 | 0.32034 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.13584 | west | 4 | Y | N | Ywest | Nwest | 1 | 88.2539 | 0 | 0.32154 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.13623 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 8.1737 | 0 | 0.32193 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.13753 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.0305 | 182 | 0.32323 | 58.8279
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.13753 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 66.5645 | 484 | 0.32323 | 156.4435
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.13826 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.9129 | 0 | 0.32396 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.13829 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.32399 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.13884 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 33.5988 | 242 | 0.32454 | 78.5383
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.13903 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.5767 | 0 | 0.32473 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.13903 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.0742 | 0 | 0.32473 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.13903 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.1596 | 0 | 0.32473 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.13903 | north | 1 | N | N | Nnorth | Nnorth | 1 | 55.4738 | 0 | 0.32473 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.13954 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 109.5405 | 0 | 0.32524 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.13954 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 110.9359 | 0 | 0.32524 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.13954 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 108.8428 | 0 | 0.32524 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.13969 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 51.1269 | 366 | 0.32539 | 119.0933
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13978 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7956 | 20 | 0.32548 | 6.5096
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.13978 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7956 | 20 | 0.32548 | 6.5096
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.13978 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7956 | 20 | 0.32548 | 6.5096
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.13978 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3762 | 17 | 0.32548 | 5.5332
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.14118 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.6236 | 224 | 0.32688 | 73.2206
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.14144 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 16.973 | 0 | 0.32714 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.14161 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6993 | 0 | 0.32731 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.14161 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6993 | 0 | 0.32731 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.14271 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.4176 | 73 | 0.32841 | 23.9737
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.14271 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.9821 | 119 | 0.32841 | 39.0805
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.14271 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.2549 | 205 | 0.32841 | 67.3235
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.14271 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.5561 | 102 | 0.32841 | 33.4976
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.14271 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.6999 | 96 | 0.32841 | 31.5271
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.14352 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.2787 | 204 | 0.32922 | 67.1616
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.14352 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.8481 | 201 | 0.32922 | 66.1739
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.14352 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.7326 | 242 | 0.32922 | 79.6721
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1489 | 161 | 0.32948 | 53.0467
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5802 | 164 | 0.32948 | 54.0351
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5802 | 164 | 0.32948 | 54.0351
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 59.5257 | 414 | 0.32948 | 136.4057
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2927 | 162 | 0.32948 | 53.3762
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1489 | 161 | 0.32948 | 53.0467
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.4365 | 163 | 0.32948 | 53.7056
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.14378 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 58.8068 | 409 | 0.32948 | 134.7583
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.1446 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.892 | 20 | 0.3303 | 6.606
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.1446 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.615 | 25 | 0.3303 | 8.2575
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.1446 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.9286 | 41 | 0.3303 | 13.5424
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.1446 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.6029 | 18 | 0.3303 | 5.9455
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.1446 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.6029 | 18 | 0.3303 | 5.9455
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.1446 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.495 | 38 | 0.3303 | 12.5516
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.14474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.7638 | 0 | 0.33044 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.14474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 83.8033 | 0 | 0.33044 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.14474 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 116.9483 | 0 | 0.33044 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.14476 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.4364 | 79 | 0.33046 | 26.1067
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.14476 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.345 | 106 | 0.33046 | 35.0292
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.14476 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 21.1355 | 146 | 0.33046 | 48.2478
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.14476 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.0021 | 76 | 0.33046 | 25.1153
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.14477 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.8577 | 0 | 0.33047 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.14477 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.5236 | 0 | 0.33047 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.14477 | north | 8 | N | N | Nnorth | Nnorth | 1 | 12.7976 | 0 | 0.33047 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.14477 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.7909 | 40 | 0.33047 | 13.2189
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.14484 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 56.1968 | 388 | 0.33054 | 128.2485
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.14484 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 74.5911 | 515 | 0.33054 | 170.2268
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1782 | 160 | 0.33056 | 52.8903
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.5988 | 156 | 0.33056 | 51.5681
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.3933 | 196 | 0.33056 | 64.7906
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.5988 | 156 | 0.33056 | 51.5681
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.7436 | 157 | 0.33056 | 51.8986
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.6831 | 198 | 0.33056 | 65.4518
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.14494 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 16.306 | 0 | 0.33064 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.14494 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 41.7436 | 288 | 0.33064 | 95.2253
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.14494 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3066 | 147 | 0.33064 | 48.6046
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.14494 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3066 | 147 | 0.33064 | 48.6046
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.14495 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 53.6315 | 370 | 0.33065 | 122.3407
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.293 | 0 | 0.33065 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.438 | 0 | 0.33065 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | 1 | 44.7895 | 0 | 0.33065 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.7279 | 0 | 0.33065 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | 1 | 20.8728 | 0 | 0.33065 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.14495 | north | 1 | N | N | Nnorth | Nnorth | 1 | 44.9345 | 0 | 0.33065 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.14503 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 24.6553 | 170 | 0.33073 | 56.2243
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.14503 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.4161 | 520 | 0.33073 | 171.9804
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.14512 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.8047 | 0 | 0.33082 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.14512 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.8047 | 0 | 0.33082 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14535 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.33105 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.14535 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.33105 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.14572 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33142 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.14583 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.33154 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.14589 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.7536 | 60 | 0.33159 | 19.8956
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.14589 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.1913 | 63 | 0.33159 | 20.8904
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.14664 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.742 | 196 | 0.33234 | 65.1393
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.14664 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.2774 | 111 | 0.33234 | 36.8901
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.14707 | north | 3 | N | N | Nnorth | Nnorth | 1 | 170.1623 | 0 | 0.33277 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.14707 | north | 3 | N | N | Nnorth | Nnorth | 1 | 170.3094 | 0 | 0.33277 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.14722 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 17.3718 | 118 | 0.33292 | 39.2845
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.14722 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 16.9302 | 115 | 0.33292 | 38.2857
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.14722 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 81.8538 | 556 | 0.33292 | 185.1032
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.1473 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.333 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.1473 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.333 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.1473 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.333 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.14754 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.3279 | 70 | 0.33324 | 23.327
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.14754 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.1804 | 69 | 0.33324 | 22.9937
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.14754 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.1804 | 69 | 0.33324 | 22.9937
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.14754 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.0329 | 68 | 0.33324 | 22.6605
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.14773 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.1009 | 217.3 | 0.33343 | 72.4536
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.14773 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.2838 | 205 | 0.33343 | 68.3524
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.14773 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 40.2406 | 272.4 | 0.33343 | 90.8254
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.14821 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.33391 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.15007 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 65.28 | 435 | 0.33577 | 146.0597
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.15033 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 59.3815 | 395 | 0.33603 | 132.7332
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.15033 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 65.3949 | 435 | 0.33603 | 146.1746
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.15096 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.3604 | 168 | 0.33666 | 56.5581
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.15096 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.586 | 90 | 0.33666 | 30.299
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.15691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.1469 | 224 | 0.34261 | 76.7438
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.15691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 35.4608 | 226 | 0.34261 | 77.4291
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.15691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.2641 | 212 | 0.34261 | 72.6326
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.15691 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 33.1072 | 211 | 0.34261 | 72.29
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.15739 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.0594 | 216.4 | 0.34309 | 74.245
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.15739 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 34.0122 | 216.1 | 0.34309 | 74.1421
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.15871 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3807 | 0 | 0.34441 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.15871 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3807 | 0 | 0.34441 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.1621 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.3154 | 150 | 0.3478 | 52.1705
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.1621 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.9682 | 80 | 0.3478 | 27.8243
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.1779 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3636 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.1779 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.3636 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.19162 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 48.8641 | 255 | 0.37732 | 96.2177
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.19162 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 28.552 | 149 | 0.37732 | 56.2213
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.19162 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 29.3185 | 153 | 0.37732 | 57.7306
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.23563 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.42133 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.23563 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 185.4392 | 787 | 0.42133 | 331.5855

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 1340
| 25 | 1340
| 30 | 1340
| 35 | 1340
| 40 | 1340
| 45 | 1340
| 50 | 1340
| 55 | 1340
| 60 | 1334
| 65 | 1307
| 70 | 1280
| 75 | 1251
| 80 | 1223
| 85 | 1194
| 90 | 1163
| 95 | 1132
| 100 | 1098
| 105 | 1065
| 110 | 1031
| 115 | 994
| Max | 1340
| Min | 994
| Avg | 1239.6