## test results
CRE test for: |  | GRHAMSES - COKFIELD 345kV [1430 - 1442] | [5 empty] | PASS
Line Rating: |  | 1340
Direcction |  | north | → | west |  | n-w
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | GRHAMSES - COKFIELD 345kV [1430 - 1442]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.022225
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.0031072
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.27708
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.010921
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | GRHAMSES - COKFIELD 345kV [1430 - 1442]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.023486
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.0026731
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.26804
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.011053
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | GRHAMSES - COKFIELD 345kV [1430 - 1442]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.019552
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.29026 | PASS
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.011172
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.27115
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.0078137
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.28813
PTDF tests
north | → | west | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.29026 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.29026 | 0.019552
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.147
[6 empty] | Concentration |  | 0.50643 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.033489
[6 empty] | Concentration |  | 0.11537 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 170.2791
| Percent of line rating => | [6 empty] | 12.71% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 2.807
[7 empty] | B1(N-S) | -0.014755 | 0.040127 | 0.054882 | -0.014755
[7 empty] | B2 (N-W) | 0 | 0.81477 | 0.81477 | 0
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.012385 | 0.018975 | 0.031359 | -0.012385
[7 empty] | B4 (S-W) | 0.014665 | 0.77577 | 0.7611 | 0.014665
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.0019089 | -0.020024 | -0.021933 | 0.0019089
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.01585 | -0.79294 | -0.80879 | 0.01585
[7 empty] | test | 0 | 0.81477 | 0.81477 | 0
[7 empty] | B1 | -1.811%
Deployment Error Percent | [6 empty] | B2 | 0%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -1.52%
[7 empty] | B4 | 1.8%
[7 empty] | B5 | 0.2343%
[7 empty] | B6 | 1.945%
[7 empty] | Max Abs Error | 1.945% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | 6
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: GRHAMSES - COKFIELD 345kV [1430 - 1442] C: GRHAMSES - LONGCREK 345kV [1430 - 1435] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: GRHAMSES - COKFIELD 345kV [1430 - 1442] C: GRHAMSES - LONGCREK 345kV [1430 - 1435]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.013614 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 3.4716
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.013614 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 2.0285
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.013005 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.19507
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.013005 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.19507
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.013614 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 2.0829
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.012594 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 1.8891
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.012594 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 1.0075
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.007647 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 0.55823
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.007647 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 0.90999
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.007647 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 1.5676
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.007647 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 0.77999
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.007647 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 0.73411
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.008485 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.10182
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.008485 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.10182
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.015384 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 2.5845
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.015384 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 1.3846
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.017001 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.30602
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.017001 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.30602
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.017001 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 0.64604
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.02109 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 6.0739
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.02109 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 3.1002
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.02109 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 3.1002
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.024015 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 2.7017
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.024707 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.98828
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.024818 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 1.9606
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.024818 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 2.6307
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.024818 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 3.6234
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.024818 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 1.8862
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.029502 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 1.7701
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.029502 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 1.8586
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.024713 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.49426
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.024713 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.61782
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.024713 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 1.0132
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.015254 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 7.0626
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -18.1543
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -17.8792
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -18.4294
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -18.4294
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -18.4294
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27507 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -31.3574
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27507 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -141.6585
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -18.3381
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -19.1716
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -19.1716
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -18.616
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -18.616
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -18.0602
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.28097 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -19.6678
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.28097 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -20.6231
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.28097 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -19.7801
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.28162 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -42.243
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.28162 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -61.9564
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.26828 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -26.5596
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.26828 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -16.365
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.26853 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -37.8629
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.26828 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -6.707
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.26828 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -12.2604
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.26828 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -12.2604
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.26853 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -32.2237
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.27349 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -7.056
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.27614 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -27.7525
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.27429 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -32.9149
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.2763 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -16.0256
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.27652 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -59.2306
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.27471 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -41.2068
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.26963 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -1.7795
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.26963 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -9.2482
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.27471 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -27.7459
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.27364 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -32.8367
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.086971 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 31.8314
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.021412 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 5.1817
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.46966 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -187.8628
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.47077 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -111.1027
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.57691 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -95.19
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.046657 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 9.518
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.046657 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 9.3781
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.046657 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 11.291
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.015834 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.31668
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.015834 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.31668
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.015834 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.31668
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.015834 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.26918
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.017015 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 2.0418
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.032089 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -1.9253
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.025291 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 1.8968
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.025291 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 2.0132
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.025291 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 2.2357
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 4.0573
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 3.9558
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 4.9702
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 3.9558
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 3.9812
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 5.0209
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.025552 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 4.3438
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.025552 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 13.287
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.02544 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 9.4128
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.02522 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 14.0728
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.02522 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 14.6024
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.02522 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 20.3778
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.029267 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 3.2779
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.029267 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 2.9267
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.029267 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 11.0629
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.014331 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 3.1141
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.014331 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 2.9379
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.014331 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 3.9038
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.018993 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 14.6246
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.014334 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 1.0034
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.014334 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.98905
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.014334 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.98905
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.014334 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 0.97471
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.012869 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 14.8894
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.012869 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 14.9023
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.020852 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 4.6708
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.020852 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 4.7126
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.021993 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 4.7593
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.021993 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 4.7527
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.020852 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 4.4206
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.020852 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 4.3998
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.024925 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 9.8454
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.024872 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 10.8193
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.024925 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 10.8424
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.026388 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 3.6415
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.023645 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 2.7901
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.023645 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 2.7192
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.023645 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 13.1466
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.024229 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 9.4009
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.024229 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 12.4779
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.022533 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 17.6884
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.022533 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 17.9137
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.022533 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 17.5757
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.022081 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 4.0187
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.022081 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 10.6872
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.021193 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 4.7472
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.022119 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 1.1059
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.022139 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.92984
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.019873 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 12.2219
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.019873 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 11.6655
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.014917 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 8.0104
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.014917 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 11.7397
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.014167 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 1.0625
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.014167 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 3.1451
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.008535 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 4.8564
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001617 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 0.33795
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001617 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 0.34927
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.001456 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 0.59259
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001617 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.074382
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001617 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 0.075999
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001617 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.074382
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001617 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.074382
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.001701 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 0.72122
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.001701 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 0.72293
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000988 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 0.057304
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000988 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 0.087932
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000988 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.043472
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000988 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.043472
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000988 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 0.042484
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000988 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 0.04446
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.00162 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 0.66744
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.00162 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 0.648
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.002308 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 1.2602
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.002308 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 1.731
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.002047 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 0.12487
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.002047 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 0.19446
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.002047 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 0.3091
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.002149 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.33309
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.002149 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 0.36533
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.002149 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.33309
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.003718 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.081796
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.003718 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.040898
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.003718 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.040898
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003907 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 0.18636
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003907 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.14573
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003907 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 0.17972
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003907 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 0.18754
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000106 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.001272
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000106 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.001166
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.008099 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.19438
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.008099 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.19438
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.008099 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.18628
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.001564 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 0.61934
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.008266 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 11.0186
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.008266 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 10.9772
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.002716 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.10321
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.002716 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.052419
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.002716 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.04074
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.002716 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 0.12765
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.25993 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -19.4947
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.23853 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -35.7801
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.28626 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -48.5219
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.19857 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -29.7861
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.27089 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -17.0661
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.11692 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -75.9629
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.025653 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 1.0261
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.025653 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 1.0261
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.006908 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -2.9152
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.005605 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 0.73986
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.005605 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 0.75107
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.005605 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 1.8104
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.006149 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 0.97154
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.006149 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 0.98384
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.006149 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 1.0761
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.00621 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 3.6266
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.00621 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 3.6949
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.006208 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 2.6881
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003574 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 0.80022
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003574 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 0.80415
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003574 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 0.80272
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003574 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 0.81023
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.004596 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.036768
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.004596 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.036768
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.00736 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.13248
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.00736 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.13248
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.00736 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.1104
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.010469 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.14343
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.004226 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.076068
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.004226 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.076068
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.001857 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.064995
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.001857 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.063138
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.001857 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.064995
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.006234 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -0.17455
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.006234 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -0.18079
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.2749 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -9.6216
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.2749 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -8.2471
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005978 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.2989
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005978 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.2989
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005978 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.2989
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005978 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.2989
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.002929 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.017574
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.003306 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0079344
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.003306 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0079344
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.003306 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.0092568
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.002877 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.011508
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.003753 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0090072
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.003753 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0090072
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.4482
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 0.42076
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 0.42686
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.4482
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 0.55492
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 0.6037
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.005636 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 0.85949
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.005636 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 0.84258
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.005636 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 1.3109
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.003315 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 0.47073
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.003315 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 0.48068
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.003315 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 0.50057
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.003315 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 0.96135
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.074039 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -2.4433
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.074039 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -1.851
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000106 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.001272
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.004093 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 0.29879
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.38038
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 0.39002
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.12146
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.030366
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.38038
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 0.3852
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 0.3775
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.12037
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.22149
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.003103 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 1.9518
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.003989 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 0.57442
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.003989 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 0.74993
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.003773 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.045276
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.053081 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.31849
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.003092 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 1.0389
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003052 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 1.0194
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003052 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 1.0377
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.003002 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.11408
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.003028 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.0757
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.003028 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.0757
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.003025 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.11495
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.002896 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.083984
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.00309 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 0.45825
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.00309 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 0.45917
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.00309 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 0.47277
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 0.52077
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 0.50429
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 0.3296
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 0.47792
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 0.48451
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 0.41859
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.002167 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 0.31747
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.002167 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 0.3205
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.002167 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 0.37489
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.002509 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 0.51936
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.002509 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 0.5437
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.002509 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 0.60718
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.00251 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.36144
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.00251 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.36144
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.00251 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 0.42921
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.004854 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 1.5047
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.004854 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 2.0047
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00507 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.21294
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00507 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.22308
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00507 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.22308
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00507 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.23829
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.23466
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.22029
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.22029
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.22508
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004789 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 0.73751
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004789 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 0.70877
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.22987
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.22987
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -19.4991
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -19.4991
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -25.8502
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -22.2846
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -22.2846
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -32.0342
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -57.9889
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -39.5784
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -36.8767
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -37.8794
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -40.9432
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -58.4903
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.2344 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -48.9892
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.2344 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -29.6513
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.2344 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -58.3651
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.2344 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -46.1764
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.28162 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -56.324
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.28162 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -34.3295
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.27471 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -40.9316
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.27162 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -48.8914
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.27162 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -48.8914
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.27176 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -61.1467
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.3045 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -38.0629
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.3045 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -38.0629
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 3.5616
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 3.587
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 7.861
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 3.6379
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 3.6634
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 7.8864
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.021413 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 4.1969
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.021413 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 2.3768
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.025808 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 3.8807
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 3.9531
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 3.9531
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 9.9791
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 3.9048
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 3.8807
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 3.929
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 9.8585
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.024079 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.024079 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.02232 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 3.3034
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.02232 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 2.9016
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.02232 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 3.2364
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.02232 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 8.9057
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.020234 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 3.0493
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.020234 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 3.0553
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.020234 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 3.5895
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.020308 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 3.0767
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.020308 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 3.0929
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.020308 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 3.6047
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.008535 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 4.9588
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.017091 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 14.6128
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.017091 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 14.6128
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.015227 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.48726
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.015188 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.72902
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.015188 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.69865
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.015239 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.18287
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.015239 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.77719
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.015239 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.25906
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.015239 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.33526
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.015239 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.38098
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.015188 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 1.5947
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.26276 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -22.0715
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.25968 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -20.7746
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.25954 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -38.9313
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.25954 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -38.9313
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010808 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 0.76521
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010808 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 0.72089
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010808 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 0.57282
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 1.6558
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 1.659
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 1.6461
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 1.0376
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 2.6372
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010808 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 0.43232
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.010806 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 1.0838
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.010806 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 1.0039
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.010806 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 1.1098
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.010806 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 1.1022
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.010806 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 0.34579
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.010806 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 0.32418
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.009822 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 1.0902
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.009822 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 1.0902
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.009822 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 1.1688
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.009822 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 1.0755
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.017091 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 2.603
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.017091 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 2.6149
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.011396 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 1.5499
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.01048 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.34584
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.011395 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.47859
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.011395 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.47859
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.011395 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.43301
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.011395 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.43301
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.009644 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 0.68472
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.009644 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.09644
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.010455 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.7042
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.010455 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.7042
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.010455 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 2.5615
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.011174 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.72631
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.011174 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 0.67044
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.011174 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.72631
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.011174 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.72631
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.011317 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 1.6862
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.011317 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 0.73674
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 1.013
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 0.97516
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 0.96848
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 0.60669
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.13581
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.01157 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 8.5965
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.011498 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 8.451
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.01159 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.9935
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.01159 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.9935
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.01159 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.9935
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011987 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 2.0738
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.01141 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 1.9739
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.01141 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 1.5404
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.011641 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 1.8952
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.011641 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 1.8789
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.011641 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 1.8498
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.011641 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 3.1338
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 0.72454
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 0.71549
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 0.93511
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 0.83323
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 1.8394
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 1.7707
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 1.7752
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 1.7695
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 3.0319
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.011567 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.057835
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.011567 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 0.24291
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.014698 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 2.2664
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.014698 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 2.2929
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.014698 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 2.2929
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.014698 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 5.5852
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.011663 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 4.6419
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.51745
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.51745
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.51745
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.61869
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.61869
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 0.60745
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.017827 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 14.7429
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.017827 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 14.6003
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.010394 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.47916
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.64022
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.64022
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 0.88452
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.62338
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.62338
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 0.85925
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.011323 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 2.0381
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.011323 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 1.7958
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.011323 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 1.7777
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.011295 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 0.39532
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.011021 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 5.0586
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 0.75199
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 0.76355
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 0.80983
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 0.72885
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 0.71728
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 1.2032
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 0.68257
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011987 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 1.87
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011987 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.846
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011987 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.846
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011987 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 1.9419
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.011586 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 1.819
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 0.80578
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 0.81713
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 0.44261
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 0.34047
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.011253 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 0.87773
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.011253 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 0.90024
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 0.1834
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.011315 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 1.867
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.011314 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 1.9121
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.01132 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 2.4112
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.011322 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 2.5814
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.011313 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.13576
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.011313 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 0.20363
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.010946 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 0.5473
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 1.1945
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 1.1945
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.62024
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.60876
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.62024
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.6547
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.62024
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.62024
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.66619
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.66619
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.011549 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.13859
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.65498
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.69006
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.65498
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.65498
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.69006
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.65498
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.008561 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 0.56503
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.010562 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 1.7005
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.010562 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 1.7533
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.010562 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 2.6194
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.010562 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 5.7669
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.010562 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 6.7914
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.01045 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 6.803
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.01045 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 5.8938
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.01045 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 6.27
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.010562 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.13731
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.011568 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.13882
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 0.39154
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 0.39961
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 0.37657
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 0.52858
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 0.20383
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 0.23493
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 0.22917
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 0.40306
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 0.20729
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 0.98347
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 1.7044
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 0.58491
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 0.67359
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.42453
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.95283
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 0.81132
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 0.83019
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.4717
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.16981
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 0.8868
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 0.66038
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 0.59434
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 0.67925
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 0.61132
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.95283
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 0.9151
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 0.9717
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 0.71698
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.75472
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.75472
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 1.6132
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084806
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.25291 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -19.3473
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.25993 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -20.7943
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.25993 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -10.3972
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.26097 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -20.8773
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.25971 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -20.7771
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.25425 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -20.3402
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.25247 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -21.2071
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.26097 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -20.8773
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 0.070794
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.30173 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -36.2078
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.30173 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -70.3036
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.30173 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -51.3548
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 0.13786
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 0.11426
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 0.1391
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 0.071415
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 0.0621
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.20609 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -12.3655
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.079135 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.22424 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.26516 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -1.2728
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -11.8351
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -33.9273
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -42.6064
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -37.5568
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -33.1383
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -25.406
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.26859 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -40.2884
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.26589 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -29.9125
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.26589 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -39.7504
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.26589 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -49.4554
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.26589 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -57.0332
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.002716 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.048206 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.004132 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.13482
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.20993
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 0.35631
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.26292
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.11468
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.10629
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.053143
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.26292
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.10069
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 0.12027
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.061534
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.16918
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.06507
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.030366
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.06507
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.16918
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.16918
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 0.41396
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.13985
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 0.15383
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.13985
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003296 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.039552
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.004234 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.06351
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.004234 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.097382
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.004714 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.22627
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.004265 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.03412
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.003086 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 0.55548
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.003092 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 0.55656
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003052 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.54936
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003052 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.54936
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.004128 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.4128
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.004128 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.4128
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.08025
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.08025
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.08025
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.05136
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.08025
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.08025
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.08025
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.04815
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.004128 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.004128 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -2.064
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.004128 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -2.064
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.004128 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.001915 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.074039 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.001865 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.001732 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L: GRHAMSES - COKFIELD 345kV [1430 - 1442] C: GRHAMSES - LONGCREK 345kV [1430 - 1435] | [7 empty] | 170.2791
Number of Bus | Name of Bus | ID | Max MW | L: GRHAMSES - COKFIELD 345kV [1430 - 1442] C: GRHAMSES - LONGCREK 345kV [1430 - 1435] | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.013614 | north | -0.0086112 | 0.010507 | 0.29069 | 0.0026931 | 0.0026931 | houston | Y | 0.0086112 | 1.5091
239 | BOSQUESW | 1 | 149 | 0.013614 | north | -0.0086112 | 0.010507 | 0.29069 | 0.0026931 | 0.0026931 | houston | Y | 0.0086112 | 0.8818
244 | WHITNYDM | 1 | 15 | 0.013005 | north | -0.0092202 | 0.0098978 | 0.29009 | 0.0020841 | 0.0020841 | houston | Y | 0.0092202 | 0.10704
245 | WHITNYDM | 2 | 15 | 0.013005 | north | -0.0092202 | 0.0098978 | 0.29009 | 0.0020841 | 0.0020841 | houston | Y | 0.0092202 | 0.10704
247 | BOSQUESW | 2 | 153 | 0.013614 | north | -0.0086112 | 0.010507 | 0.29069 | 0.0026931 | 0.0026931 | houston | Y | 0.0086112 | 0.90547
251 | BOSQUESW | 2 | 150 | 0.012594 | north | -0.0096312 | 0.0094868 | 0.28967 | 0.0016731 | 0.0016731 | houston | Y | 0.0096312 | 1.1937
253 | BOSQUESW | 2 | 80 | 0.012594 | north | -0.0096312 | 0.0094868 | 0.28967 | 0.0016731 | 0.0016731 | houston | Y | 0.0096312 | 0.63665
332 | RWMILLER | 1 | 73 | 0.007647 | north | -0.014578 | 0.0045398 | 0.28473 | -0.0032739 | 0.0032739 | houston | Y | 0.014578 | 0.82521
333 | RWMILLER | 2 | 119 | 0.007647 | north | -0.014578 | 0.0045398 | 0.28473 | -0.0032739 | 0.0032739 | houston | Y | 0.014578 | 1.3452
334 | RWMILLER | 3 | 205 | 0.007647 | north | -0.014578 | 0.0045398 | 0.28473 | -0.0032739 | 0.0032739 | houston | Y | 0.014578 | 2.3174
335 | RWMILLER | 4 | 102 | 0.007647 | north | -0.014578 | 0.0045398 | 0.28473 | -0.0032739 | 0.0032739 | houston | Y | 0.014578 | 1.153
336 | RWMILLER | 5 | 96 | 0.007647 | north | -0.014578 | 0.0045398 | 0.28473 | -0.0032739 | 0.0032739 | houston | Y | 0.014578 | 1.0852
344 | MRSSHPRD | 1 | 12 | 0.008485 | north | -0.01374 | 0.0053778 | 0.28557 | -0.0024359 | 0.0024359 | houston | Y | 0.01374 | 0.13565
345 | MRSSHPRD | 2 | 12 | 0.008485 | north | -0.01374 | 0.0053778 | 0.28557 | -0.0024359 | 0.0024359 | houston | Y | 0.01374 | 0.13565
366 | JNSNCNTY | 1 | 168 | 0.015384 | north | -0.0068412 | 0.012277 | 0.29246 | 0.0044631 | 0.0044631 | houston | Y | 0.0068412 | 0.39952
367 | JNSNCNTY | 2 | 90 | 0.015384 | north | -0.0068412 | 0.012277 | 0.29246 | 0.0044631 | 0.0044631 | houston | Y | 0.0068412 | 0.21403
503 | NTHTEXAS | 1 | 18 | 0.017001 | north | -0.0052242 | 0.013894 | 0.29408 | 0.0060801 | 0.0052242 | North | N | 0.0052242 | 0
504 | NTHTEXAS | 2 | 18 | 0.017001 | north | -0.0052242 | 0.013894 | 0.29408 | 0.0060801 | 0.0052242 | North | N | 0.0052242 | 0
505 | NTHTEXAS | 3 | 38 | 0.017001 | north | -0.0052242 | 0.013894 | 0.29408 | 0.0060801 | 0.0052242 | North | N | 0.0052242 | 0
580 | JCKCNTY8 | 1 | 288 | 0.02109 | north | -0.0011352 | 0.017983 | 0.29817 | 0.010169 | 0.0011352 | North | N | 0.0011352 | 0
581 | JCKCNTY8 | 2 | 147 | 0.02109 | north | -0.0011352 | 0.017983 | 0.29817 | 0.010169 | 0.0011352 | North | N | 0.0011352 | 0
582 | JCKCNTY8 | 3 | 147 | 0.02109 | north | -0.0011352 | 0.017983 | 0.29817 | 0.010169 | 0.0011352 | North | N | 0.0011352 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.024015 | north | 0.0017898 | 0.020908 | 0.3011 | 0.013094 | 0.0017898 | North | N | 0.0017898 | 0
837 | NEWMAN_G | 1 | 40 | 0.024707 | north | 0.0024818 | 0.0216 | 0.30179 | 0.013786 | 0.0024818 | North | N | 0.0024818 | 0
842 | OLINGER_ | 1 | 79 | 0.024818 | north | 0.0025928 | 0.021711 | 0.3019 | 0.013897 | 0.0025928 | North | N | 0.0025928 | 0
843 | OLINGER_ | 1 | 106 | 0.024818 | north | 0.0025928 | 0.021711 | 0.3019 | 0.013897 | 0.0025928 | North | N | 0.0025928 | 0
844 | OLINGER_ | 1 | 146 | 0.024818 | north | 0.0025928 | 0.021711 | 0.3019 | 0.013897 | 0.0025928 | North | N | 0.0025928 | 0
845 | OLINGER_ | 1 | 76 | 0.024818 | north | 0.0025928 | 0.021711 | 0.3019 | 0.013897 | 0.0025928 | North | N | 0.0025928 | 0
923 | SPENCER_ | 1 | 60 | 0.029502 | north | 0.0072768 | 0.026395 | 0.30658 | 0.018581 | 0.0072768 | North | N | 0.0072768 | 0
924 | SPENCER_ | 1 | 63 | 0.029502 | north | 0.0072768 | 0.026395 | 0.30658 | 0.018581 | 0.0072768 | North | N | 0.0072768 | 0
948 | STEAM1 | 1 | 20 | 0.024713 | north | 0.0024878 | 0.021606 | 0.30179 | 0.013792 | 0.0024878 | North | N | 0.0024878 | 0
949 | STEAM2 | 1 | 25 | 0.024713 | north | 0.0024878 | 0.021606 | 0.30179 | 0.013792 | 0.0024878 | North | N | 0.0024878 | 0
950 | STEAM3 | 1 | 41 | 0.024713 | north | 0.0024878 | 0.021606 | 0.30179 | 0.013792 | 0.0024878 | North | N | 0.0024878 | 0
990 | GIBN_CRE | 1 | 463 | 0.015254 | north | -0.0069712 | 0.012147 | 0.29233 | 0.0043331 | 0.0043331 | houston | Y | 0.0069712 | 1.2214
1002 | PBCTAGE_ | A | 66 | -0.27507 | west | -0.29729 | -0.27817 | 0.0020158 | -0.28599 | 0.0020158 | west | N | 0.0020158 | 0
1003 | PBCTBGE_ | B | 65 | -0.27507 | west | -0.29729 | -0.27817 | 0.0020158 | -0.28599 | 0.0020158 | west | N | 0.0020158 | 0
1004 | PBCTCGE_ | C | 67 | -0.27507 | west | -0.29729 | -0.27817 | 0.0020158 | -0.28599 | 0.0020158 | west | N | 0.0020158 | 0
1005 | PBCTDGE_ | D | 67 | -0.27507 | west | -0.29729 | -0.27817 | 0.0020158 | -0.28599 | 0.0020158 | west | N | 0.0020158 | 0
1006 | PBCTEGE_ | E | 67 | -0.27507 | west | -0.29729 | -0.27817 | 0.0020158 | -0.28599 | 0.0020158 | west | N | 0.0020158 | 0
1007 | PB5GEN_6 | MB | 114 | -0.27507 | west | -0.29729 | -0.27817 | 0.0020158 | -0.28599 | 0.0020158 | west | N | 0.0020158 | 0
1008 | PB6GEN_7 | MB | 515 | -0.27507 | west | -0.29729 | -0.27817 | 0.0020158 | -0.28599 | 0.0020158 | west | N | 0.0020158 | 0
1039 | MRGNAG_1 | A | 66 | -0.27785 | west | -0.30008 | -0.28096 | -0.00076916 | -0.28877 | 0.00076916 | west | N | 0.00076916 | 0
1040 | MRGNBG_2 | B | 69 | -0.27785 | west | -0.30008 | -0.28096 | -0.00076916 | -0.28877 | 0.00076916 | west | N | 0.00076916 | 0
1041 | MRGNCG_3 | C | 69 | -0.27785 | west | -0.30008 | -0.28096 | -0.00076916 | -0.28877 | 0.00076916 | west | N | 0.00076916 | 0
1042 | MRGNDG_4 | D | 67 | -0.27785 | west | -0.30008 | -0.28096 | -0.00076916 | -0.28877 | 0.00076916 | west | N | 0.00076916 | 0
1043 | MRGNEG_5 | E | 67 | -0.27785 | west | -0.30008 | -0.28096 | -0.00076916 | -0.28877 | 0.00076916 | west | N | 0.00076916 | 0
1044 | MRGNFG_6 | F | 65 | -0.27785 | west | -0.30008 | -0.28096 | -0.00076916 | -0.28877 | 0.00076916 | west | N | 0.00076916 | 0
1045 | CALENG1G | 1 | 70 | -0.28097 | west | -0.30319 | -0.28408 | -0.0038872 | -0.29189 | 0.0038872 | west | N | 0.0038872 | 0
1046 | CALENG2G | 2 | 73.4 | -0.28097 | west | -0.30319 | -0.28408 | -0.0038872 | -0.29189 | 0.0038872 | west | N | 0.0038872 | 0
1047 | CALENG3G | 3 | 70.4 | -0.28097 | west | -0.30319 | -0.28408 | -0.0038872 | -0.29189 | 0.0038872 | west | N | 0.0038872 | 0
1058 | LONGSHOR | 1 | 150 | -0.28162 | west | -0.30385 | -0.28473 | -0.0045392 | -0.29254 | 0.0045392 | west | N | 0.0045392 | 0
1058 | LONGSHOR | 2 | 220 | -0.28162 | west | -0.30385 | -0.28473 | -0.0045392 | -0.29254 | 0.0045392 | west | N | 0.0045392 | 0
1061 | CIELOGEN | 1 | 99 | -0.26828 | west | -0.2905 | -0.27139 | 0.0088018 | -0.2792 | 0.0088018 | west | N | 0.0088018 | 0
1062 | CIELOGEN | 1 | 61 | -0.26828 | west | -0.2905 | -0.27139 | 0.0088018 | -0.2792 | 0.0088018 | west | N | 0.0088018 | 0
1068 | SCURRYCW | 1 | 141 | -0.26853 | west | -0.29076 | -0.27164 | 0.0085498 | -0.27945 | 0.0085498 | west | N | 0.0085498 | 0
1069 | KINDERMG | 1 | 25 | -0.26828 | west | -0.2905 | -0.27139 | 0.0088018 | -0.2792 | 0.0088018 | west | N | 0.0088018 | 0
1070 | KINDERMG | 1 | 45.7 | -0.26828 | west | -0.2905 | -0.27139 | 0.0088018 | -0.2792 | 0.0088018 | west | N | 0.0088018 | 0
1071 | KINDERMG | 1 | 45.7 | -0.26828 | west | -0.2905 | -0.27139 | 0.0088018 | -0.2792 | 0.0088018 | west | N | 0.0088018 | 0
1073 | SCURRYCW | 2 | 120 | -0.26853 | west | -0.29076 | -0.27164 | 0.0085498 | -0.27945 | 0.0085498 | west | N | 0.0085498 | 0
1320 | BSP 1 | 1 | 25.8 | -0.27349 | west | -0.29571 | -0.2766 | 0.0035918 | -0.28441 | 0.0035918 | west | N | 0.0035918 | 0
1326 | STANTONW | 1 | 100.5 | -0.27614 | west | -0.29837 | -0.27925 | 0.00093684 | -0.28706 | 0.00093684 | west | N | 0.00093684 | 0
1327 | WILDHRSE | 1 | 120 | -0.27429 | west | -0.29652 | -0.2774 | 0.0027898 | -0.28521 | 0.0027898 | west | N | 0.0027898 | 0
1328 | OCOTILLO | 1 | 58 | -0.2763 | west | -0.29853 | -0.27941 | 0.00077784 | -0.28722 | 0.00077784 | west | N | 0.00077784 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.27652 | west | -0.29875 | -0.27963 | 0.00056084 | -0.28744 | 0.00056084 | west | N | 0.00056084 | 0
1343 | TRENTIPP | 1 | 150 | -0.27471 | west | -0.29694 | -0.27782 | 0.0023688 | -0.28563 | 0.0023688 | west | N | 0.0023688 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.26963 | west | -0.29185 | -0.27273 | 0.0074548 | -0.28055 | 0.0074548 | west | N | 0.0074548 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.26963 | west | -0.29185 | -0.27273 | 0.0074548 | -0.28055 | 0.0074548 | west | N | 0.0074548 | 0
1354 | AEPWIND_ | 1 | 101 | -0.27471 | west | -0.29694 | -0.27782 | 0.0023688 | -0.28563 | 0.0023688 | west | N | 0.0023688 | 0
1360 | GUNSIGHT | 1 | 120 | -0.27364 | west | -0.29586 | -0.27675 | 0.0034418 | -0.28456 | 0.0034418 | west | N | 0.0034418 | 0
1432 | GRHAMSES | 2 | 366 | 0.086971 | north | 0.064746 | 0.083864 | 0.36405 | 0.07605 | 0.064746 | North | N | 0.064746 | 0
1433 | GRHAMSES | 1 | 242 | 0.021412 | north | -0.00081318 | 0.018305 | 0.29849 | 0.010491 | 0.00081318 | North | N | 0.00081318 | 0
1437 | MESQUITW | 1 | 400 | -0.46966 | west | -0.49188 | -0.47276 | -0.19258 | -0.48058 | 0.19258 | west | N | 0.19258 | 0
1438 | MESQUITW | 1 | 236 | -0.47077 | west | -0.493 | -0.47388 | -0.19369 | -0.48169 | 0.19369 | west | N | 0.19369 | 0
1442 | COKFIELD | 1 | 165 | -0.57691 | west | -0.59913 | -0.58002 | -0.29983 | -0.58783 | 0.29983 | west | N | 0.29983 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.046657 | north | 0.024432 | 0.04355 | 0.32374 | 0.035736 | 0.024432 | North | N | 0.024432 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.046657 | north | 0.024432 | 0.04355 | 0.32374 | 0.035736 | 0.024432 | North | N | 0.024432 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.046657 | north | 0.024432 | 0.04355 | 0.32374 | 0.035736 | 0.024432 | North | N | 0.024432 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.015834 | west | -0.0063912 | 0.012727 | 0.29291 | 0.0049131 | 0.0049131 | houston | Y | 0.29291 | 5.76
1479 | WFCOGEN_ | 2 | 20 | 0.015834 | west | -0.0063912 | 0.012727 | 0.29291 | 0.0049131 | 0.0049131 | houston | Y | 0.29291 | 5.76
1482 | WFCOGEN_ | 1 | 20 | 0.015834 | west | -0.0063912 | 0.012727 | 0.29291 | 0.0049131 | 0.0049131 | houston | Y | 0.29291 | 5.76
1482 | WFCOGEN_ | 2 | 17 | 0.015834 | west | -0.0063912 | 0.012727 | 0.29291 | 0.0049131 | 0.0049131 | houston | Y | 0.29291 | 4.896
1600 | BARTNWND | 1 | 120 | 0.017015 | north | -0.0052102 | 0.013908 | 0.2941 | 0.0060941 | 0.0052102 | North | N | 0.0052102 | 0
1643 | SLSTR1PP | 1 | 60 | -0.032089 | north | -0.054314 | -0.035196 | 0.24499 | -0.04301 | 0.035196 | south | Y | 0.054314 | 1.1471
1675 | PEC_1G | 1 | 75 | 0.025291 | north | 0.0030658 | 0.022184 | 0.30237 | 0.01437 | 0.0030658 | North | N | 0.0030658 | 0
1676 | PEC_2G | 2 | 79.6 | 0.025291 | north | 0.0030658 | 0.022184 | 0.30237 | 0.01437 | 0.0030658 | North | N | 0.0030658 | 0
1677 | PEC_3G | 3 | 88.4 | 0.025291 | north | 0.0030658 | 0.022184 | 0.30237 | 0.01437 | 0.0030658 | North | N | 0.0030658 | 0
1678 | LAMARPWR | 1 | 160 | 0.025358 | north | 0.0031328 | 0.022251 | 0.30244 | 0.014437 | 0.0031328 | North | N | 0.0031328 | 0
1679 | LAMARPWR | 2 | 156 | 0.025358 | north | 0.0031328 | 0.022251 | 0.30244 | 0.014437 | 0.0031328 | North | N | 0.0031328 | 0
1680 | LAMARPWR | 3 | 196 | 0.025358 | north | 0.0031328 | 0.022251 | 0.30244 | 0.014437 | 0.0031328 | North | N | 0.0031328 | 0
1681 | LAMARPWR | 4 | 156 | 0.025358 | north | 0.0031328 | 0.022251 | 0.30244 | 0.014437 | 0.0031328 | North | N | 0.0031328 | 0
1682 | LAMARPWR | 5 | 157 | 0.025358 | north | 0.0031328 | 0.022251 | 0.30244 | 0.014437 | 0.0031328 | North | N | 0.0031328 | 0
1683 | LAMARPWR | 6 | 198 | 0.025358 | north | 0.0031328 | 0.022251 | 0.30244 | 0.014437 | 0.0031328 | North | N | 0.0031328 | 0
1687 | VALLEY_1 | 1 | 170 | 0.025552 | north | 0.0033268 | 0.022445 | 0.30263 | 0.014631 | 0.0033268 | North | N | 0.0033268 | 0
1688 | VALLEY_2 | 2 | 520 | 0.025552 | north | 0.0033268 | 0.022445 | 0.30263 | 0.014631 | 0.0033268 | North | N | 0.0033268 | 0
1689 | VALLEY_3 | 3 | 370 | 0.02544 | north | 0.0032148 | 0.022333 | 0.30252 | 0.014519 | 0.0032148 | North | N | 0.0032148 | 0
1701 | MOSES_1G | 1 | 558 | 0.02522 | north | 0.0029948 | 0.022113 | 0.3023 | 0.014299 | 0.0029948 | North | N | 0.0029948 | 0
1702 | MOSES_2G | 2 | 579 | 0.02522 | north | 0.0029948 | 0.022113 | 0.3023 | 0.014299 | 0.0029948 | North | N | 0.0029948 | 0
1703 | MOSES_3G | 3 | 808 | 0.02522 | north | 0.0029948 | 0.022113 | 0.3023 | 0.014299 | 0.0029948 | North | N | 0.0029948 | 0
1861 | EAGLEMNT | MB | 112 | 0.029267 | north | 0.0070418 | 0.02616 | 0.30635 | 0.018346 | 0.0070418 | North | N | 0.0070418 | 0
1862 | EAGLEMNT | MB | 100 | 0.029267 | north | 0.0070418 | 0.02616 | 0.30635 | 0.018346 | 0.0070418 | North | N | 0.0070418 | 0
1863 | EAGLEMNT | MB | 378 | 0.029267 | north | 0.0070418 | 0.02616 | 0.30635 | 0.018346 | 0.0070418 | North | N | 0.0070418 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.014331 | north | -0.0078942 | 0.011224 | 0.29141 | 0.0034101 | 0.0034101 | houston | Y | 0.0078942 | 0.9744
1878 | WLFHOLW_ | 2 | 205 | 0.014331 | north | -0.0078942 | 0.011224 | 0.29141 | 0.0034101 | 0.0034101 | houston | Y | 0.0078942 | 0.91924
1879 | WLFHOLW_ | 3 | 272.4 | 0.014331 | north | -0.0078942 | 0.011224 | 0.29141 | 0.0034101 | 0.0034101 | houston | Y | 0.0078942 | 1.2215
1889 | DECRDOVA | MB | 770 | 0.018993 | north | -0.0032322 | 0.015886 | 0.29607 | 0.0080721 | 0.0032322 | North | N | 0.0032322 | 0
1892 | DECRDOVA | A | 70 | 0.014334 | north | -0.0078912 | 0.011227 | 0.29141 | 0.0034131 | 0.0034131 | houston | Y | 0.0078912 | 0.31347
1893 | DECRDOVA | B | 69 | 0.014334 | north | -0.0078912 | 0.011227 | 0.29141 | 0.0034131 | 0.0034131 | houston | Y | 0.0078912 | 0.30899
1894 | DECRDOVA | C | 69 | 0.014334 | north | -0.0078912 | 0.011227 | 0.29141 | 0.0034131 | 0.0034131 | houston | Y | 0.0078912 | 0.30899
1895 | DECRDOVA | D | 68 | 0.014334 | north | -0.0078912 | 0.011227 | 0.29141 | 0.0034131 | 0.0034131 | houston | Y | 0.0078912 | 0.30451
1898 | COMCHEPK | 1 | 1157 | 0.012869 | north | -0.0093562 | 0.0097618 | 0.28995 | 0.0019481 | 0.0019481 | houston | Y | 0.0093562 | 8.5712
1899 | COMCHEPK | 2 | 1158 | 0.012869 | north | -0.0093562 | 0.0097618 | 0.28995 | 0.0019481 | 0.0019481 | houston | Y | 0.0093562 | 8.5786
1937 | MDLTHELP | 5 | 224 | 0.020852 | north | -0.0013732 | 0.017745 | 0.29793 | 0.0099311 | 0.0013732 | North | N | 0.0013732 | 0
1938 | MDLTHELP | 6 | 226 | 0.020852 | north | -0.0013732 | 0.017745 | 0.29793 | 0.0099311 | 0.0013732 | North | N | 0.0013732 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.021993 | north | -0.00023218 | 0.018886 | 0.29907 | 0.011072 | 0.00023218 | North | N | 0.00023218 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.021993 | north | -0.00023218 | 0.018886 | 0.29907 | 0.011072 | 0.00023218 | North | N | 0.00023218 | 0
1943 | MDLTHELP | 3 | 212 | 0.020852 | north | -0.0013732 | 0.017745 | 0.29793 | 0.0099311 | 0.0013732 | North | N | 0.0013732 | 0
1944 | MDLTHELP | 4 | 211 | 0.020852 | north | -0.0013732 | 0.017745 | 0.29793 | 0.0099311 | 0.0013732 | North | N | 0.0013732 | 0
1947 | HANDLEY_ | 3 | 395 | 0.024925 | north | 0.0026998 | 0.021818 | 0.30201 | 0.014004 | 0.0026998 | North | N | 0.0026998 | 0
1948 | HANDLEY_ | 4 | 435 | 0.024872 | north | 0.0026468 | 0.021765 | 0.30195 | 0.013951 | 0.0026468 | North | N | 0.0026468 | 0
1949 | HANDLEY_ | 5 | 435 | 0.024925 | north | 0.0026998 | 0.021818 | 0.30201 | 0.014004 | 0.0026998 | North | N | 0.0026998 | 0
2371 | COLLIN_1 | MB | 138 | 0.026388 | north | 0.0041628 | 0.023281 | 0.30347 | 0.015467 | 0.0041628 | North | N | 0.0041628 | 0
2413 | MTCK6_G | 6 | 118 | 0.023645 | north | 0.0014198 | 0.020538 | 0.30073 | 0.012724 | 0.0014198 | North | N | 0.0014198 | 0
2414 | MTCK7_G | 7 | 115 | 0.023645 | north | 0.0014198 | 0.020538 | 0.30073 | 0.012724 | 0.0014198 | North | N | 0.0014198 | 0
2417 | MTCK8_G | 8 | 556 | 0.023645 | north | 0.0014198 | 0.020538 | 0.30073 | 0.012724 | 0.0014198 | North | N | 0.0014198 | 0
2451 | LKHB1_G | 1 | 388 | 0.024229 | north | 0.0020038 | 0.021122 | 0.30131 | 0.013308 | 0.0020038 | North | N | 0.0020038 | 0
2452 | LKHB2_G | 2 | 515 | 0.024229 | north | 0.0020038 | 0.021122 | 0.30131 | 0.013308 | 0.0020038 | North | N | 0.0020038 | 0
3097 | MARTLAKE | 1 | 785 | 0.022533 | north | 0.00030782 | 0.019426 | 0.29961 | 0.011612 | 0.00030782 | North | N | 0.00030782 | 0
3098 | MARTLAKE | 2 | 795 | 0.022533 | north | 0.00030782 | 0.019426 | 0.29961 | 0.011612 | 0.00030782 | North | N | 0.00030782 | 0
3099 | MARTLAKE | 3 | 780 | 0.022533 | north | 0.00030782 | 0.019426 | 0.29961 | 0.011612 | 0.00030782 | North | N | 0.00030782 | 0
3107 | STRYKER_ | 1 | 182 | 0.022081 | north | -0.00014418 | 0.018974 | 0.29916 | 0.01116 | 0.00014418 | North | N | 0.00014418 | 0
3108 | STRYKER_ | 2 | 484 | 0.022081 | north | -0.00014418 | 0.018974 | 0.29916 | 0.01116 | 0.00014418 | North | N | 0.00014418 | 0
3126 | TRINIDAD | 1 | 224 | 0.021193 | north | -0.0010322 | 0.018086 | 0.29827 | 0.010272 | 0.0010322 | North | N | 0.0010322 | 0
3309 | ASPN_G | 1 | 50 | 0.022119 | north | -0.00010618 | 0.019012 | 0.2992 | 0.011198 | 0.00010618 | North | N | 0.00010618 | 0
3348 | CHAMPION | MB | 42 | 0.022139 | north | -8.6177e-05 | 0.019032 | 0.29922 | 0.011218 | 8.6177e-05 | North | N | 8.6177e-05 | 0
3381 | BBRN_1G | 1 | 615 | 0.019873 | north | -0.0023522 | 0.016766 | 0.29695 | 0.0089521 | 0.0023522 | North | N | 0.0023522 | 0
3382 | BBRN_2G | 2 | 587 | 0.019873 | north | -0.0023522 | 0.016766 | 0.29695 | 0.0089521 | 0.0023522 | North | N | 0.0023522 | 0
3403 | THOUSE_1 | MB | 537 | 0.014917 | north | -0.0073082 | 0.01181 | 0.292 | 0.0039961 | 0.0039961 | houston | Y | 0.0073082 | 1.7786
3404 | THOUSE_2 | 2 | 787 | 0.014917 | north | -0.0073082 | 0.01181 | 0.292 | 0.0039961 | 0.0039961 | houston | Y | 0.0073082 | 2.6066
3416 | LAKE_CRK | MB | 75 | 0.014167 | north | -0.0080582 | 0.01106 | 0.29125 | 0.0032461 | 0.0032461 | houston | Y | 0.0080582 | 0.36091
3417 | LAKE_CRK | MB | 222 | 0.014167 | north | -0.0080582 | 0.01106 | 0.29125 | 0.0032461 | 0.0032461 | houston | Y | 0.0080582 | 1.0683
3432 | SANDOW_4 | 4 | 569 | 0.008535 | south | -0.01369 | 0.0054278 | 0.28562 | -0.0023859 | 0.0023859 | houston | Y | 0.0054278 | 1.7308
5026 | BRAUNIG_ | 1 | 209 | 0.001617 | south | -0.020608 | -0.0014902 | 0.2787 | -0.0093039 | 0.0014902 | south | N | 0.0014902 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.001617 | south | -0.020608 | -0.0014902 | 0.2787 | -0.0093039 | 0.0014902 | south | N | 0.0014902 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.001456 | south | -0.020769 | -0.0016512 | 0.27854 | -0.0094649 | 0.0016512 | south | N | 0.0016512 | 0
5031 | BRA_VHBC | 1 | 46 | 0.001617 | south | -0.020608 | -0.0014902 | 0.2787 | -0.0093039 | 0.0014902 | south | N | 0.0014902 | 0
5032 | BRA_VHBC | 2 | 47 | 0.001617 | south | -0.020608 | -0.0014902 | 0.2787 | -0.0093039 | 0.0014902 | south | N | 0.0014902 | 0
5033 | BRA_VHBC | 3 | 46 | 0.001617 | south | -0.020608 | -0.0014902 | 0.2787 | -0.0093039 | 0.0014902 | south | N | 0.0014902 | 0
5034 | BRA_VHBC | 4 | 46 | 0.001617 | south | -0.020608 | -0.0014902 | 0.2787 | -0.0093039 | 0.0014902 | south | N | 0.0014902 | 0
5111 | CALAVER_ | 1 | 424 | 0.001701 | south | -0.020524 | -0.0014062 | 0.27878 | -0.0092199 | 0.0014062 | south | N | 0.0014062 | 0
5112 | CALAVER_ | 2 | 425 | 0.001701 | south | -0.020524 | -0.0014062 | 0.27878 | -0.0092199 | 0.0014062 | south | N | 0.0014062 | 0
5264 | LEON_LCP | 3 | 58 | 0.000988 | south | -0.021237 | -0.0021192 | 0.27807 | -0.0099329 | 0.0021192 | south | N | 0.0021192 | 0
5265 | LEON_LCP | 4 | 89 | 0.000988 | south | -0.021237 | -0.0021192 | 0.27807 | -0.0099329 | 0.0021192 | south | N | 0.0021192 | 0
5266 | LEON_LCP | 1 | 44 | 0.000988 | south | -0.021237 | -0.0021192 | 0.27807 | -0.0099329 | 0.0021192 | south | N | 0.0021192 | 0
5267 | LEON_LCP | 2 | 44 | 0.000988 | south | -0.021237 | -0.0021192 | 0.27807 | -0.0099329 | 0.0021192 | south | N | 0.0021192 | 0
5268 | LEON_LCP | 3 | 43 | 0.000988 | south | -0.021237 | -0.0021192 | 0.27807 | -0.0099329 | 0.0021192 | south | N | 0.0021192 | 0
5269 | LEON_LCP | 4 | 45 | 0.000988 | south | -0.021237 | -0.0021192 | 0.27807 | -0.0099329 | 0.0021192 | south | N | 0.0021192 | 0
5396 | CALAVER_ | 1 | 412 | 0.00162 | south | -0.020605 | -0.0014872 | 0.2787 | -0.0093009 | 0.0014872 | south | N | 0.0014872 | 0
5397 | CALAVER_ | 2 | 400 | 0.00162 | south | -0.020605 | -0.0014872 | 0.2787 | -0.0093009 | 0.0014872 | south | N | 0.0014872 | 0
5401 | CALAVER_ | 1 | 546 | 0.002308 | south | -0.019917 | -0.00079921 | 0.27939 | -0.0086129 | 0.00079921 | south | N | 0.00079921 | 0
5402 | CALAVER_ | 2 | 750 | 0.002308 | south | -0.019917 | -0.00079921 | 0.27939 | -0.0086129 | 0.00079921 | south | N | 0.00079921 | 0
5436 | TUTTL_WB | MB | 61 | 0.002047 | south | -0.020178 | -0.0010602 | 0.27913 | -0.0088739 | 0.0010602 | south | N | 0.0010602 | 0
5438 | TUTTL_WB | MB | 95 | 0.002047 | south | -0.020178 | -0.0010602 | 0.27913 | -0.0088739 | 0.0010602 | south | N | 0.0010602 | 0
5439 | TUTTL_WB | MB | 151 | 0.002047 | south | -0.020178 | -0.0010602 | 0.27913 | -0.0088739 | 0.0010602 | south | N | 0.0010602 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.002149 | south | -0.020076 | -0.00095821 | 0.27923 | -0.0087719 | 0.00095821 | south | N | 0.00095821 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.002149 | south | -0.020076 | -0.00095821 | 0.27923 | -0.0087719 | 0.00095821 | south | N | 0.00095821 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.002149 | south | -0.020076 | -0.00095821 | 0.27923 | -0.0087719 | 0.00095821 | south | N | 0.00095821 | 0
5503 | RAYBURNG | 1 | 22 | 0.003718 | south | -0.018507 | 0.00061079 | 0.2808 | -0.0072029 | 0.00061079 | south | N | 0.00061079 | 0
5505 | RAYBURNG | 1 | 11 | 0.003718 | south | -0.018507 | 0.00061079 | 0.2808 | -0.0072029 | 0.00061079 | south | N | 0.00061079 | 0
5506 | RAYBURNG | 1 | 11 | 0.003718 | south | -0.018507 | 0.00061079 | 0.2808 | -0.0072029 | 0.00061079 | south | N | 0.00061079 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.003907 | south | -0.018318 | 0.00079979 | 0.28099 | -0.0070139 | 0.00079979 | south | N | 0.00079979 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.003907 | south | -0.018318 | 0.00079979 | 0.28099 | -0.0070139 | 0.00079979 | south | N | 0.00079979 | 0
5511 | RAYBURNC | 1 | 46 | 0.003907 | south | -0.018318 | 0.00079979 | 0.28099 | -0.0070139 | 0.00079979 | south | N | 0.00079979 | 0
5512 | RAYBURNC | 1 | 48 | 0.003907 | south | -0.018318 | 0.00079979 | 0.28099 | -0.0070139 | 0.00079979 | south | N | 0.00079979 | 0
5728 | FALCONHY | 2 | 12 | 0.000106 | south | -0.022119 | -0.0030012 | 0.27719 | -0.010815 | 0.0030012 | south | N | 0.0030012 | 0
5729 | FALCONHY | 3 | 11 | 0.000106 | south | -0.022119 | -0.0030012 | 0.27719 | -0.010815 | 0.0030012 | south | N | 0.0030012 | 0
5890 | PEARSALL | 1 | 24 | -0.008099 | south | -0.030324 | -0.011206 | 0.26898 | -0.01902 | 0.011206 | south | N | 0.011206 | 0
5891 | PEARSALL | 1 | 24 | -0.008099 | south | -0.030324 | -0.011206 | 0.26898 | -0.01902 | 0.011206 | south | N | 0.011206 | 0
5892 | PEARSALL | 1 | 23 | -0.008099 | south | -0.030324 | -0.011206 | 0.26898 | -0.01902 | 0.011206 | south | N | 0.011206 | 0
5903 | SANMIGUE | 1 | 396 | 0.001564 | south | -0.020661 | -0.0015432 | 0.27864 | -0.0093569 | 0.0015432 | south | N | 0.0015432 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.008266 | houston | -0.013959 | 0.0051588 | 0.28535 | -0.0026549 | 0.0026549 | houston | N | 0.0026549 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.008266 | houston | -0.013959 | 0.0051588 | 0.28535 | -0.0026549 | 0.0026549 | houston | N | 0.0026549 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | -0.022225 | -0.0031072 | 0.27708 | -0.010921 | 0.0031072 | south | Y | 0.022225 | 11.4708
5932 | SI_RAY9 | 9 | 38 | 0.002716 | south | -0.019509 | -0.00039121 | 0.2798 | -0.0082049 | 0.00039121 | south | N | 0.00039121 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.002716 | south | -0.019509 | -0.00039121 | 0.2798 | -0.0082049 | 0.00039121 | south | N | 0.00039121 | 0
5934 | SI_RAY5 | 5 | 15 | 0.002716 | south | -0.019509 | -0.00039121 | 0.2798 | -0.0082049 | 0.00039121 | south | N | 0.00039121 | 0
5935 | SI_RAY10 | 10 | 47 | 0.002716 | south | -0.019509 | -0.00039121 | 0.2798 | -0.0082049 | 0.00039121 | south | N | 0.00039121 | 0
6016 | SWMESA | 1 | 75 | -0.25993 | west | -0.28215 | -0.26304 | 0.017152 | -0.27085 | 0.017152 | west | N | 0.017152 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | -0.022225 | -0.0031072 | 0.27708 | -0.010921 | 0.0031072 | south | Y | 0.27708 | 60.2742
6144 | MCADOO1A | 1 | 150 | -0.23853 | west | -0.26076 | -0.24164 | 0.038547 | -0.24945 | 0.038547 | west | N | 0.038547 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.28626 | west | -0.30849 | -0.28937 | -0.0091842 | -0.29719 | 0.0091842 | west | N | 0.0091842 | 0
6476 | LANGFORD | 1 | 150 | -0.19857 | west | -0.2208 | -0.20168 | 0.078507 | -0.20949 | 0.078507 | west | N | 0.078507 | 0
6637 | SNYDERW1 | 1 | 63 | -0.27089 | west | -0.29312 | -0.274 | 0.0061908 | -0.28181 | 0.0061908 | west | N | 0.0061908 | 0
6752 | OKLA0A | 1 | 649.7 | -0.11692 | west | -0.13915 | -0.12003 | 0.16016 | -0.12784 | 0.12003 | south | Y | 0.16016 | 26.0748
6948 | DENISNDM | 1 | 40 | 0.025653 | north | 0.0034278 | 0.022546 | 0.30273 | 0.014732 | 0.0034278 | North | N | 0.0034278 | 0
6948 | DENISNDM | 2 | 40 | 0.025653 | north | 0.0034278 | 0.022546 | 0.30273 | 0.014732 | 0.0034278 | North | N | 0.0034278 | 0
7000 | L_FERGUS | 1 | 422 | -0.006908 | south | -0.029133 | -0.010015 | 0.27017 | -0.017829 | 0.010015 | south | N | 0.010015 | 0
7004 | L_SIMGID | 1 | 132 | 0.005605 | south | -0.01662 | 0.0024978 | 0.28269 | -0.0053159 | 0.0024978 | south | N | 0.0024978 | 0
7005 | L_SIMGID | 2 | 134 | 0.005605 | south | -0.01662 | 0.0024978 | 0.28269 | -0.0053159 | 0.0024978 | south | N | 0.0024978 | 0
7006 | L_SIMGID | 3 | 323 | 0.005605 | south | -0.01662 | 0.0024978 | 0.28269 | -0.0053159 | 0.0024978 | south | N | 0.0024978 | 0
7007 | L_LOSTPI | 1 | 158 | 0.006149 | south | -0.016076 | 0.0030418 | 0.28323 | -0.0047719 | 0.0030418 | south | N | 0.0030418 | 0
7008 | L_LOSTPI | 2 | 160 | 0.006149 | south | -0.016076 | 0.0030418 | 0.28323 | -0.0047719 | 0.0030418 | south | N | 0.0030418 | 0
7009 | L_LOSTPI | 3 | 175 | 0.006149 | south | -0.016076 | 0.0030418 | 0.28323 | -0.0047719 | 0.0030418 | south | N | 0.0030418 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.00621 | south | -0.016015 | 0.0031028 | 0.28329 | -0.0047109 | 0.0031028 | south | N | 0.0031028 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.00621 | south | -0.016015 | 0.0031028 | 0.28329 | -0.0047109 | 0.0031028 | south | N | 0.0031028 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.006208 | south | -0.016017 | 0.0031008 | 0.28329 | -0.0047129 | 0.0031008 | south | N | 0.0031008 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.003574 | south | -0.018651 | 0.00046679 | 0.28065 | -0.0073469 | 0.00046679 | south | N | 0.00046679 | 0
7015 | L_HAYSEN | 2 | 225 | 0.003574 | south | -0.018651 | 0.00046679 | 0.28065 | -0.0073469 | 0.00046679 | south | N | 0.00046679 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.003574 | south | -0.018651 | 0.00046679 | 0.28065 | -0.0073469 | 0.00046679 | south | N | 0.00046679 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.003574 | south | -0.018651 | 0.00046679 | 0.28065 | -0.0073469 | 0.00046679 | south | N | 0.00046679 | 0
7020 | L_AUSTPL | 1 | 8 | 0.004596 | south | -0.017629 | 0.0014888 | 0.28168 | -0.0063249 | 0.0014888 | south | N | 0.0014888 | 0
7020 | L_AUSTPL | 2 | 8 | 0.004596 | south | -0.017629 | 0.0014888 | 0.28168 | -0.0063249 | 0.0014888 | south | N | 0.0014888 | 0
7022 | L_BUCHAN | 1 | 18 | -0.00736 | south | -0.029585 | -0.010467 | 0.26972 | -0.018281 | 0.010467 | south | N | 0.010467 | 0
7023 | L_BUCHAN | 2 | 18 | -0.00736 | south | -0.029585 | -0.010467 | 0.26972 | -0.018281 | 0.010467 | south | N | 0.010467 | 0
7024 | L_BUCHAN | 3 | 15 | -0.00736 | south | -0.029585 | -0.010467 | 0.26972 | -0.018281 | 0.010467 | south | N | 0.010467 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.010469 | south | -0.032694 | -0.013576 | 0.26661 | -0.02139 | 0.013576 | south | N | 0.013576 | 0
7028 | L_MARBFA | 1 | 18 | -0.004226 | south | -0.026451 | -0.0073332 | 0.27285 | -0.015147 | 0.0073332 | south | N | 0.0073332 | 0
7029 | L_MARBFA | 2 | 18 | -0.004226 | south | -0.026451 | -0.0073332 | 0.27285 | -0.015147 | 0.0073332 | south | N | 0.0073332 | 0
7031 | L_MARSFO | 1 | 35 | 0.001857 | south | -0.020368 | -0.0012502 | 0.27894 | -0.0090639 | 0.0012502 | south | N | 0.0012502 | 0
7032 | L_MARSFO | 2 | 34 | 0.001857 | south | -0.020368 | -0.0012502 | 0.27894 | -0.0090639 | 0.0012502 | south | N | 0.0012502 | 0
7033 | L_MARSFO | 3 | 35 | 0.001857 | south | -0.020368 | -0.0012502 | 0.27894 | -0.0090639 | 0.0012502 | south | N | 0.0012502 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.006234 | south | -0.028459 | -0.0093412 | 0.27085 | -0.017155 | 0.0093412 | south | N | 0.0093412 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.006234 | south | -0.028459 | -0.0093412 | 0.27085 | -0.017155 | 0.0093412 | south | N | 0.0093412 | 0
7038 | L_DELAWA | 1 | 35 | -0.2749 | west | -0.29713 | -0.27801 | 0.0021788 | -0.28582 | 0.0021788 | west | N | 0.0021788 | 0
7038 | L_DELAWA | 2 | 30 | -0.2749 | west | -0.29713 | -0.27801 | 0.0021788 | -0.28582 | 0.0021788 | west | N | 0.0021788 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.005978 | south | -0.016247 | 0.0028708 | 0.28306 | -0.0049429 | 0.0028708 | south | N | 0.0028708 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.005978 | south | -0.016247 | 0.0028708 | 0.28306 | -0.0049429 | 0.0028708 | south | N | 0.0028708 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.005978 | south | -0.016247 | 0.0028708 | 0.28306 | -0.0049429 | 0.0028708 | south | N | 0.0028708 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.005978 | south | -0.016247 | 0.0028708 | 0.28306 | -0.0049429 | 0.0028708 | south | N | 0.0028708 | 0
7487 | L_CANYHY | 1 | 6 | 0.002929 | south | -0.019296 | -0.00017821 | 0.28001 | -0.0079919 | 0.00017821 | south | N | 0.00017821 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.003306 | south | -0.018919 | 0.00019879 | 0.28039 | -0.0076149 | 0.00019879 | south | N | 0.00019879 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.003306 | south | -0.018919 | 0.00019879 | 0.28039 | -0.0076149 | 0.00019879 | south | N | 0.00019879 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.003306 | south | -0.018919 | 0.00019879 | 0.28039 | -0.0076149 | 0.00019879 | south | N | 0.00019879 | 0
7609 | L_SCHUMA | 1 | 4 | 0.002877 | south | -0.019348 | -0.00023021 | 0.27996 | -0.0080439 | 0.00023021 | south | N | 0.00023021 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.003753 | south | -0.018472 | 0.00064579 | 0.28083 | -0.0071679 | 0.00064579 | south | N | 0.00064579 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.003753 | south | -0.018472 | 0.00064579 | 0.28083 | -0.0071679 | 0.00064579 | south | N | 0.00064579 | 0
7800 | L_GUADGE | 1 | 147 | 0.003049 | south | -0.019176 | -5.8211e-05 | 0.28013 | -0.0078719 | 5.8211e-05 | south | N | 5.8211e-05 | 0
7801 | L_GUADGE | 2 | 138 | 0.003049 | south | -0.019176 | -5.8211e-05 | 0.28013 | -0.0078719 | 5.8211e-05 | south | N | 5.8211e-05 | 0
7802 | L_GUADGE | 3 | 140 | 0.003049 | south | -0.019176 | -5.8211e-05 | 0.28013 | -0.0078719 | 5.8211e-05 | south | N | 5.8211e-05 | 0
7803 | L_GUADGE | 4 | 147 | 0.003049 | south | -0.019176 | -5.8211e-05 | 0.28013 | -0.0078719 | 5.8211e-05 | south | N | 5.8211e-05 | 0
7804 | L_GUADGE | 5 | 182 | 0.003049 | south | -0.019176 | -5.8211e-05 | 0.28013 | -0.0078719 | 5.8211e-05 | south | N | 5.8211e-05 | 0
7805 | L_GUADGE | 6 | 198 | 0.003049 | south | -0.019176 | -5.8211e-05 | 0.28013 | -0.0078719 | 5.8211e-05 | south | N | 5.8211e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.005636 | south | -0.016589 | 0.0025288 | 0.28272 | -0.0052849 | 0.0025288 | south | N | 0.0025288 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.005636 | south | -0.016589 | 0.0025288 | 0.28272 | -0.0052849 | 0.0025288 | south | N | 0.0025288 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.005636 | south | -0.016589 | 0.0025288 | 0.28272 | -0.0052849 | 0.0025288 | south | N | 0.0025288 | 0
7810 | L_RIONOG | 1 | 142 | 0.003315 | south | -0.01891 | 0.00020779 | 0.2804 | -0.0076059 | 0.00020779 | south | N | 0.00020779 | 0
7811 | L_RIONOG | 2 | 145 | 0.003315 | south | -0.01891 | 0.00020779 | 0.2804 | -0.0076059 | 0.00020779 | south | N | 0.00020779 | 0
7812 | L_RIONOG | 3 | 151 | 0.003315 | south | -0.01891 | 0.00020779 | 0.2804 | -0.0076059 | 0.00020779 | south | N | 0.00020779 | 0
7813 | L_RIONOG | 4 | 290 | 0.003315 | south | -0.01891 | 0.00020779 | 0.2804 | -0.0076059 | 0.00020779 | south | N | 0.00020779 | 0
8032 | AMISTADH | 1 | 33 | -0.074039 | south | -0.096264 | -0.077146 | 0.20304 | -0.08496 | 0.077146 | south | N | 0.077146 | 0
8033 | AMISTADH | 2 | 25 | -0.074039 | south | -0.096264 | -0.077146 | 0.20304 | -0.08496 | 0.077146 | south | N | 0.077146 | 0
8048 | FALCONHY | 1 | 12 | 0.000106 | south | -0.022119 | -0.0030012 | 0.27719 | -0.010815 | 0.0030012 | south | N | 0.0030012 | 0
8066 | DUP1V#1 | 1 | 73 | 0.004093 | south | -0.018132 | 0.00098579 | 0.28117 | -0.0068279 | 0.00098579 | south | N | 0.00098579 | 0
8134 | FOR69CG0 | 1 | 79 | 0.004815 | south | -0.01741 | 0.0017078 | 0.2819 | -0.0061059 | 0.0017078 | south | N | 0.0017078 | 0
8138 | FOR69CG0 | 2 | 81 | 0.004815 | south | -0.01741 | 0.0017078 | 0.2819 | -0.0061059 | 0.0017078 | south | N | 0.0017078 | 0
8139 | JOS #1 | MB | 255 | 0 | south | -0.022225 | -0.0031072 | 0.27708 | -0.010921 | 0.0031072 | south | N | 0.0031072 | 0
8147 | UCAR #2 | 10 | 28 | 0.004338 | south | -0.017887 | 0.0012308 | 0.28142 | -0.0065829 | 0.0012308 | south | N | 0.0012308 | 0
8148 | UCAR #1 | 2 | 7 | 0.004338 | south | -0.017887 | 0.0012308 | 0.28142 | -0.0065829 | 0.0012308 | south | N | 0.0012308 | 0
8153 | FOR69CG0 | 3 | 79 | 0.004815 | south | -0.01741 | 0.0017078 | 0.2819 | -0.0061059 | 0.0017078 | south | N | 0.0017078 | 0
8154 | FOR69CG0 | 4 | 80 | 0.004815 | south | -0.01741 | 0.0017078 | 0.2819 | -0.0061059 | 0.0017078 | south | N | 0.0017078 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.004815 | south | -0.01741 | 0.0017078 | 0.2819 | -0.0061059 | 0.0017078 | south | N | 0.0017078 | 0
8156 | FOR69CG0 | 6 | 25 | 0.004815 | south | -0.01741 | 0.0017078 | 0.2819 | -0.0061059 | 0.0017078 | south | N | 0.0017078 | 0
8157 | FOR69CG0 | 7 | 46 | 0.004815 | south | -0.01741 | 0.0017078 | 0.2819 | -0.0061059 | 0.0017078 | south | N | 0.0017078 | 0
8161 | COLETOU1 | 1 | 629 | 0.003103 | south | -0.019122 | -4.2107e-06 | 0.28018 | -0.0078179 | 4.2107e-06 | south | N | 4.2107e-06 | 0
8173 | VICEC51A | 5 | 144 | 0.003989 | south | -0.018236 | 0.00088179 | 0.28107 | -0.0069319 | 0.00088179 | south | N | 0.00088179 | 0
8174 | VICEC61A | 6 | 188 | 0.003989 | south | -0.018236 | 0.00088179 | 0.28107 | -0.0069319 | 0.00088179 | south | N | 0.00088179 | 0
8189 | CUERO 2 | 1 | 12 | 0.003773 | south | -0.018452 | 0.00066579 | 0.28085 | -0.0071479 | 0.00066579 | south | N | 0.00066579 | 0
8262 | ELPS | 1 | 6 | -0.053081 | south | -0.075306 | -0.056188 | 0.224 | -0.064002 | 0.056188 | south | N | 0.056188 | 0
8285 | LAR #1 | MB | 32 | 0 | south | -0.022225 | -0.0031072 | 0.27708 | -0.010921 | 0.0031072 | south | N | 0.0031072 | 0
8287 | LAR #2 | MB | 32 | 0 | south | -0.022225 | -0.0031072 | 0.27708 | -0.010921 | 0.0031072 | south | N | 0.0031072 | 0
8288 | LAR #3 | MB | 105 | 0 | south | -0.022225 | -0.0031072 | 0.27708 | -0.010921 | 0.0031072 | south | N | 0.0031072 | 0
8388 | BATES0A | MB | 70 | 0 | south | -0.022225 | -0.0031072 | 0.27708 | -0.010921 | 0.0031072 | south | N | 0.0031072 | 0
8393 | BATES0B | MB | 110 | 0 | south | -0.022225 | -0.0031072 | 0.27708 | -0.010921 | 0.0031072 | south | N | 0.0031072 | 0
8442 | NBEC71A | 1 | 336 | 0.003092 | south | -0.019133 | -1.5211e-05 | 0.28017 | -0.0078289 | 1.5211e-05 | south | N | 1.5211e-05 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | -0.022225 | -0.0031072 | 0.27708 | -0.010921 | 0.0031072 | south | N | 0.0031072 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | -0.022225 | -0.0031072 | 0.27708 | -0.010921 | 0.0031072 | south | N | 0.0031072 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.003052 | south | -0.019173 | -5.5211e-05 | 0.28013 | -0.0078689 | 5.5211e-05 | south | N | 5.5211e-05 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.003052 | south | -0.019173 | -5.5211e-05 | 0.28013 | -0.0078689 | 5.5211e-05 | south | N | 5.5211e-05 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.003002 | south | -0.019223 | -0.00010521 | 0.28008 | -0.0079189 | 0.00010521 | south | N | 0.00010521 | 0
8506 | VAL #1 | 1 | 25 | 0.003028 | south | -0.019197 | -7.9211e-05 | 0.28011 | -0.0078929 | 7.9211e-05 | south | N | 7.9211e-05 | 0
8507 | VAL #2 | 2 | 25 | 0.003028 | south | -0.019197 | -7.9211e-05 | 0.28011 | -0.0078929 | 7.9211e-05 | south | N | 7.9211e-05 | 0
8511 | OXY_CC0A | 1 | 38 | 0.003025 | south | -0.0192 | -8.2211e-05 | 0.28011 | -0.0078959 | 8.2211e-05 | south | N | 8.2211e-05 | 0
8517 | CELANEBI | 1 | 29 | 0.002896 | south | -0.019329 | -0.00021121 | 0.27998 | -0.0080249 | 0.00021121 | south | N | 0.00021121 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.00309 | south | -0.019135 | -1.7211e-05 | 0.28017 | -0.0078309 | 1.7211e-05 | south | N | 1.7211e-05 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.00309 | south | -0.019135 | -1.7211e-05 | 0.28017 | -0.0078309 | 1.7211e-05 | south | N | 1.7211e-05 | 0
8562 | CNOPST1 | 3 | 153 | 0.00309 | south | -0.019135 | -1.7211e-05 | 0.28017 | -0.0078309 | 1.7211e-05 | south | N | 1.7211e-05 | 0
8926 | LGE_GT10 | 1 | 158 | 0.003296 | south | -0.018929 | 0.00018879 | 0.28038 | -0.0076249 | 0.00018879 | south | N | 0.00018879 | 0
8927 | LGE_GT20 | 2 | 153 | 0.003296 | south | -0.018929 | 0.00018879 | 0.28038 | -0.0076249 | 0.00018879 | south | N | 0.00018879 | 0
8928 | LGE_STG0 | 3 | 100 | 0.003296 | south | -0.018929 | 0.00018879 | 0.28038 | -0.0076249 | 0.00018879 | south | N | 0.00018879 | 0
8930 | ICPGN10A | 1 | 145 | 0.003296 | south | -0.018929 | 0.00018879 | 0.28038 | -0.0076249 | 0.00018879 | south | N | 0.00018879 | 0
8931 | ICPGN20A | 2 | 147 | 0.003296 | south | -0.018929 | 0.00018879 | 0.28038 | -0.0076249 | 0.00018879 | south | N | 0.00018879 | 0
8932 | ICPGN30A | 3 | 127 | 0.003296 | south | -0.018929 | 0.00018879 | 0.28038 | -0.0076249 | 0.00018879 | south | N | 0.00018879 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.002167 | south | -0.020058 | -0.00094021 | 0.27925 | -0.0087539 | 0.00094021 | south | N | 0.00094021 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.002167 | south | -0.020058 | -0.00094021 | 0.27925 | -0.0087539 | 0.00094021 | south | N | 0.00094021 | 0
8935 | FGNTS201 | 3 | 173 | 0.002167 | south | -0.020058 | -0.00094021 | 0.27925 | -0.0087539 | 0.00094021 | south | N | 0.00094021 | 0
8936 | MVGN#1 | 1 | 207 | 0.002509 | south | -0.019716 | -0.00059821 | 0.27959 | -0.0084119 | 0.00059821 | south | N | 0.00059821 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.002509 | south | -0.019716 | -0.00059821 | 0.27959 | -0.0084119 | 0.00059821 | south | N | 0.00059821 | 0
8938 | MVGN#3 | 3 | 242 | 0.002509 | south | -0.019716 | -0.00059821 | 0.27959 | -0.0084119 | 0.00059821 | south | N | 0.00059821 | 0
8981 | HECN1 | 1 | 144 | 0.00251 | south | -0.019715 | -0.00059721 | 0.27959 | -0.0084109 | 0.00059721 | south | N | 0.00059721 | 0
8982 | HECN2 | 2 | 144 | 0.00251 | south | -0.019715 | -0.00059721 | 0.27959 | -0.0084109 | 0.00059721 | south | N | 0.00059721 | 0
8983 | HECN3 | 3 | 171 | 0.00251 | south | -0.019715 | -0.00059721 | 0.27959 | -0.0084109 | 0.00059721 | south | N | 0.00059721 | 0
9000 | DECKR_G1 | 1 | 310 | 0.004854 | south | -0.017371 | 0.0017468 | 0.28193 | -0.0060669 | 0.0017468 | south | N | 0.0017468 | 0
9001 | DECKR_G2 | 2 | 413 | 0.004854 | south | -0.017371 | 0.0017468 | 0.28193 | -0.0060669 | 0.0017468 | south | N | 0.0017468 | 0
9002 | DECKR_G3 | 3 | 42 | 0.00507 | south | -0.017155 | 0.0019628 | 0.28215 | -0.0058509 | 0.0019628 | south | N | 0.0019628 | 0
9003 | DECKR_G4 | 4 | 44 | 0.00507 | south | -0.017155 | 0.0019628 | 0.28215 | -0.0058509 | 0.0019628 | south | N | 0.0019628 | 0
9004 | DECKR_G5 | 5 | 44 | 0.00507 | south | -0.017155 | 0.0019628 | 0.28215 | -0.0058509 | 0.0019628 | south | N | 0.0019628 | 0
9005 | DECKR_G6 | 6 | 47 | 0.00507 | south | -0.017155 | 0.0019628 | 0.28215 | -0.0058509 | 0.0019628 | south | N | 0.0019628 | 0
9016 | SANDH_G1 | 1 | 49 | 0.004789 | south | -0.017436 | 0.0016818 | 0.28187 | -0.0061319 | 0.0016818 | south | N | 0.0016818 | 0
9017 | SANDH_G2 | 2 | 46 | 0.004789 | south | -0.017436 | 0.0016818 | 0.28187 | -0.0061319 | 0.0016818 | south | N | 0.0016818 | 0
9018 | SANDH_G3 | 3 | 46 | 0.004789 | south | -0.017436 | 0.0016818 | 0.28187 | -0.0061319 | 0.0016818 | south | N | 0.0016818 | 0
9019 | SANDH_G4 | 4 | 47 | 0.004789 | south | -0.017436 | 0.0016818 | 0.28187 | -0.0061319 | 0.0016818 | south | N | 0.0016818 | 0
9020 | SANDHG5A | 5A | 154 | 0.004789 | south | -0.017436 | 0.0016818 | 0.28187 | -0.0061319 | 0.0016818 | south | N | 0.0016818 | 0
9021 | SANDHG5C | 5C | 148 | 0.004789 | south | -0.017436 | 0.0016818 | 0.28187 | -0.0061319 | 0.0016818 | south | N | 0.0016818 | 0
9022 | SANDH_G6 | 6 | 48 | 0.004789 | south | -0.017436 | 0.0016818 | 0.28187 | -0.0061319 | 0.0016818 | south | N | 0.0016818 | 0
9023 | SANDH_G7 | 7 | 48 | 0.004789 | south | -0.017436 | 0.0016818 | 0.28187 | -0.0061319 | 0.0016818 | south | N | 0.0016818 | 0
11001 | NAV1CT | 1 | 70 | -0.27856 | west | -0.30078 | -0.28167 | -0.0014772 | -0.28948 | 0.0014772 | west | N | 0.0014772 | 0
11009 | NAV2CT | 1 | 70 | -0.27856 | west | -0.30078 | -0.28167 | -0.0014772 | -0.28948 | 0.0014772 | west | N | 0.0014772 | 0
11011 | NAV3ST | 1 | 92.8 | -0.27856 | west | -0.30078 | -0.28167 | -0.0014772 | -0.28948 | 0.0014772 | west | N | 0.0014772 | 0
11012 | NAV4CT | 1 | 80 | -0.27856 | west | -0.30078 | -0.28167 | -0.0014772 | -0.28948 | 0.0014772 | west | N | 0.0014772 | 0
11013 | NAV5CT | 1 | 80 | -0.27856 | west | -0.30078 | -0.28167 | -0.0014772 | -0.28948 | 0.0014772 | west | N | 0.0014772 | 0
11014 | NAV6ST | 1 | 115 | -0.27856 | west | -0.30078 | -0.28167 | -0.0014772 | -0.28948 | 0.0014772 | west | N | 0.0014772 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.27853 | west | -0.30075 | -0.28163 | -0.0014442 | -0.28945 | 0.0014442 | west | N | 0.0014442 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.27853 | west | -0.30075 | -0.28163 | -0.0014442 | -0.28945 | 0.0014442 | west | N | 0.0014442 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.27853 | west | -0.30075 | -0.28163 | -0.0014442 | -0.28945 | 0.0014442 | west | N | 0.0014442 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.27853 | west | -0.30075 | -0.28163 | -0.0014442 | -0.28945 | 0.0014442 | west | N | 0.0014442 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.27853 | west | -0.30075 | -0.28163 | -0.0014442 | -0.28945 | 0.0014442 | west | N | 0.0014442 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.27853 | west | -0.30075 | -0.28163 | -0.0014442 | -0.28945 | 0.0014442 | west | N | 0.0014442 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.2344 | west | -0.25662 | -0.23751 | 0.042683 | -0.24532 | 0.042683 | west | N | 0.042683 | 0
11057 | CHAMPION | 1 | 126.5 | -0.2344 | west | -0.25662 | -0.23751 | 0.042683 | -0.24532 | 0.042683 | west | N | 0.042683 | 0
11058 | PYRON_1G | 1 | 249 | -0.2344 | west | -0.25662 | -0.23751 | 0.042683 | -0.24532 | 0.042683 | west | N | 0.042683 | 0
11059 | INADALE_ | 1 | 197 | -0.2344 | west | -0.25662 | -0.23751 | 0.042683 | -0.24532 | 0.042683 | west | N | 0.042683 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.28162 | west | -0.30385 | -0.28473 | -0.0045392 | -0.29254 | 0.0045392 | west | N | 0.0045392 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.28162 | west | -0.30385 | -0.28473 | -0.0045392 | -0.29254 | 0.0045392 | west | N | 0.0045392 | 0
11147 | NOTREES_ | 1 | 149 | -0.27471 | west | -0.29693 | -0.27782 | 0.0023718 | -0.28563 | 0.0023718 | west | N | 0.0023718 | 0
11309 | BULLCREK | 1 | 180 | -0.27162 | west | -0.29384 | -0.27473 | 0.0054618 | -0.28254 | 0.0054618 | west | N | 0.0054618 | 0
11310 | BULLCREK | 1 | 180 | -0.27162 | west | -0.29384 | -0.27473 | 0.0054618 | -0.28254 | 0.0054618 | west | N | 0.0054618 | 0
11320 | COYOTE_1 | 1 | 225 | -0.27176 | west | -0.29399 | -0.27487 | 0.0053178 | -0.28268 | 0.0053178 | west | N | 0.0053178 | 0
11415 | LORAINE_ | 1 | 125 | -0.3045 | west | -0.32673 | -0.30761 | -0.027422 | -0.31542 | 0.027422 | west | N | 0.027422 | 0
11416 | LORAINE_ | 1 | 125 | -0.3045 | west | -0.32673 | -0.30761 | -0.027422 | -0.31542 | 0.027422 | west | N | 0.027422 | 0
11691 | KMICHICT | 1 | 140 | 0.02544 | north | 0.0032148 | 0.022333 | 0.30252 | 0.014519 | 0.0032148 | North | N | 0.0032148 | 0
11692 | KMICHICT | 2 | 141 | 0.02544 | north | 0.0032148 | 0.022333 | 0.30252 | 0.014519 | 0.0032148 | North | N | 0.0032148 | 0
11693 | KMICHIST | 3 | 309 | 0.02544 | north | 0.0032148 | 0.022333 | 0.30252 | 0.014519 | 0.0032148 | North | N | 0.0032148 | 0
11694 | KMICHICT | 4 | 143 | 0.02544 | north | 0.0032148 | 0.022333 | 0.30252 | 0.014519 | 0.0032148 | North | N | 0.0032148 | 0
11695 | KMICHICT | 5 | 144 | 0.02544 | north | 0.0032148 | 0.022333 | 0.30252 | 0.014519 | 0.0032148 | North | N | 0.0032148 | 0
11696 | KMICHIST | 6 | 310 | 0.02544 | north | 0.0032148 | 0.022333 | 0.30252 | 0.014519 | 0.0032148 | North | N | 0.0032148 | 0
12322 | ENNSTRAC | 1 | 196 | 0.021413 | north | -0.00081218 | 0.018306 | 0.29849 | 0.010492 | 0.00081218 | North | N | 0.00081218 | 0
12323 | ENNSTRAC | 2 | 111 | 0.021413 | north | -0.00081218 | 0.018306 | 0.29849 | 0.010492 | 0.00081218 | North | N | 0.00081218 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.025808 | north | 0.0035828 | 0.022701 | 0.30289 | 0.014887 | 0.0035828 | North | N | 0.0035828 | 0
12411 | FPLEFR1A | 1 | 161 | 0.024104 | north | 0.0018788 | 0.020997 | 0.30118 | 0.013183 | 0.0018788 | North | N | 0.0018788 | 0
12412 | FPLEFR1B | 2 | 164 | 0.024104 | north | 0.0018788 | 0.020997 | 0.30118 | 0.013183 | 0.0018788 | North | N | 0.0018788 | 0
12413 | FPLEFR1C | 3 | 164 | 0.024104 | north | 0.0018788 | 0.020997 | 0.30118 | 0.013183 | 0.0018788 | North | N | 0.0018788 | 0
12414 | FPLEFR1S | 4 | 414 | 0.024104 | north | 0.0018788 | 0.020997 | 0.30118 | 0.013183 | 0.0018788 | North | N | 0.0018788 | 0
12421 | FPLEFR2A | 1 | 162 | 0.024104 | north | 0.0018788 | 0.020997 | 0.30118 | 0.013183 | 0.0018788 | North | N | 0.0018788 | 0
12422 | FPLEFR2B | 2 | 161 | 0.024104 | north | 0.0018788 | 0.020997 | 0.30118 | 0.013183 | 0.0018788 | North | N | 0.0018788 | 0
12423 | FPLEFR2C | 3 | 163 | 0.024104 | north | 0.0018788 | 0.020997 | 0.30118 | 0.013183 | 0.0018788 | North | N | 0.0018788 | 0
12424 | FPLEFR2S | 4 | 409 | 0.024104 | north | 0.0018788 | 0.020997 | 0.30118 | 0.013183 | 0.0018788 | North | N | 0.0018788 | 0
12440 | PARKD_1S | 1 | 0 | 0.024079 | north | 0.0018538 | 0.020972 | 0.30116 | 0.013158 | 0.0018538 | North | N | 0.0018538 | 0
12449 | PARKD_2S | 1 | 0 | 0.024079 | north | 0.0018538 | 0.020972 | 0.30116 | 0.013158 | 0.0018538 | North | N | 0.0018538 | 0
13116 | TGATEWAY | 1 | 148 | 0.02232 | north | 9.4823e-05 | 0.019213 | 0.2994 | 0.011399 | 9.4823e-05 | North | N | 9.4823e-05 | 0
13117 | TGATEWAY | 2 | 130 | 0.02232 | north | 9.4823e-05 | 0.019213 | 0.2994 | 0.011399 | 9.4823e-05 | North | N | 9.4823e-05 | 0
13118 | TGATEWAY | 3 | 145 | 0.02232 | north | 9.4823e-05 | 0.019213 | 0.2994 | 0.011399 | 9.4823e-05 | North | N | 9.4823e-05 | 0
13119 | TGATEWAY | 4 | 399 | 0.02232 | north | 9.4823e-05 | 0.019213 | 0.2994 | 0.011399 | 9.4823e-05 | North | N | 9.4823e-05 | 0
13131 | CALFREST | 1 | 150.7 | 0.020234 | north | -0.0019912 | 0.017127 | 0.29731 | 0.0093131 | 0.0019912 | North | N | 0.0019912 | 0
13132 | CALFREST | 2 | 151 | 0.020234 | north | -0.0019912 | 0.017127 | 0.29731 | 0.0093131 | 0.0019912 | North | N | 0.0019912 | 0
13133 | CALFREST | 3 | 177.4 | 0.020234 | north | -0.0019912 | 0.017127 | 0.29731 | 0.0093131 | 0.0019912 | North | N | 0.0019912 | 0
13134 | CALFREST | 4 | 151.5 | 0.020308 | north | -0.0019172 | 0.017201 | 0.29739 | 0.0093871 | 0.0019172 | North | N | 0.0019172 | 0
13135 | CALFREST | 5 | 152.3 | 0.020308 | north | -0.0019172 | 0.017201 | 0.29739 | 0.0093871 | 0.0019172 | North | N | 0.0019172 | 0
13136 | CALFREST | 6 | 177.5 | 0.020308 | north | -0.0019172 | 0.017201 | 0.29739 | 0.0093871 | 0.0019172 | North | N | 0.0019172 | 0
13432 | SANDOW_5 | 5 | 581 | 0.008535 | south | -0.01369 | 0.0054278 | 0.28562 | -0.0023859 | 0.0023859 | houston | Y | 0.0054278 | 1.7673
13691 | OAKGROVE | 1 | 855 | 0.017091 | north | -0.0051342 | 0.013984 | 0.29417 | 0.0061701 | 0.0051342 | North | N | 0.0051342 | 0
13692 | OAKGROVE | 2 | 855 | 0.017091 | north | -0.0051342 | 0.013984 | 0.29417 | 0.0061701 | 0.0051342 | North | N | 0.0051342 | 0
32798 | BRYN_TAM | 1 | 32 | 0.015227 | north | -0.0069982 | 0.01212 | 0.29231 | 0.0043061 | 0.0043061 | houston | Y | 0.0069982 | 0.086147
32883 | BRYN_DNS | 1 | 48 | 0.015188 | north | -0.0070372 | 0.012081 | 0.29227 | 0.0042671 | 0.0042671 | houston | Y | 0.0070372 | 0.13297
32884 | BRYN_DNS | 1 | 46 | 0.015188 | north | -0.0070372 | 0.012081 | 0.29227 | 0.0042671 | 0.0042671 | houston | Y | 0.0070372 | 0.12742
32886 | BRYN_ATK | MB | 12 | 0.015239 | north | -0.0069862 | 0.012132 | 0.29232 | 0.0043181 | 0.0043181 | houston | Y | 0.0069862 | 0.032017
32887 | BRYN_ATK | MB | 51 | 0.015239 | north | -0.0069862 | 0.012132 | 0.29232 | 0.0043181 | 0.0043181 | houston | Y | 0.0069862 | 0.13607
32888 | BRYN_ATK | 1 | 17 | 0.015239 | north | -0.0069862 | 0.012132 | 0.29232 | 0.0043181 | 0.0043181 | houston | Y | 0.0069862 | 0.045358
32890 | BRYN_ATK | MB | 22 | 0.015239 | north | -0.0069862 | 0.012132 | 0.29232 | 0.0043181 | 0.0043181 | houston | Y | 0.0069862 | 0.058698
32891 | BRYN_ATK | MB | 25 | 0.015239 | north | -0.0069862 | 0.012132 | 0.29232 | 0.0043181 | 0.0043181 | houston | Y | 0.0069862 | 0.066703
32892 | BRYN_DNS | 1 | 105 | 0.015188 | north | -0.0070372 | 0.012081 | 0.29227 | 0.0042671 | 0.0042671 | houston | Y | 0.0070372 | 0.29086
36998 | RDCNYNG1 | 1 | 84 | -0.26276 | west | -0.28498 | -0.26586 | 0.014325 | -0.27368 | 0.014325 | west | N | 0.014325 | 0
38332 | WDWRDU2 | 1 | 80 | -0.25968 | west | -0.28191 | -0.26279 | 0.017399 | -0.2706 | 0.017399 | west | N | 0.017399 | 0
38437 | TNSRBNMS | 1 | 150 | -0.25954 | west | -0.28177 | -0.26265 | 0.017539 | -0.27046 | 0.017539 | west | N | 0.017539 | 0
38438 | TNSRBNMS | 1 | 150 | -0.25954 | west | -0.28177 | -0.26265 | 0.017539 | -0.27046 | 0.017539 | west | N | 0.017539 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.010808 | houston | -0.011417 | 0.0077008 | 0.28789 | -0.00011293 | 0.00011293 | houston | N | 0.00011293 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.010808 | houston | -0.011417 | 0.0077008 | 0.28789 | -0.00011293 | 0.00011293 | houston | N | 0.00011293 | 0
38600 | TNBP_CGN | 5 | 53 | 0.010808 | houston | -0.011417 | 0.0077008 | 0.28789 | -0.00011293 | 0.00011293 | houston | N | 0.00011293 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.010808 | houston | -0.011417 | 0.0077008 | 0.28789 | -0.00011293 | 0.00011293 | houston | N | 0.00011293 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.010808 | houston | -0.011417 | 0.0077008 | 0.28789 | -0.00011293 | 0.00011293 | houston | N | 0.00011293 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.010808 | houston | -0.011417 | 0.0077008 | 0.28789 | -0.00011293 | 0.00011293 | houston | N | 0.00011293 | 0
38614 | TNBPAMCG | 4 | 96 | 0.010808 | houston | -0.011417 | 0.0077008 | 0.28789 | -0.00011293 | 0.00011293 | houston | N | 0.00011293 | 0
38615 | TNBPAMCG | 1 | 244 | 0.010808 | houston | -0.011417 | 0.0077008 | 0.28789 | -0.00011293 | 0.00011293 | houston | N | 0.00011293 | 0
38690 | TNBP_CGN | 3 | 40 | 0.010808 | houston | -0.011417 | 0.0077008 | 0.28789 | -0.00011293 | 0.00011293 | houston | N | 0.00011293 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.010806 | houston | -0.011419 | 0.0076988 | 0.28789 | -0.00011493 | 0.00011493 | houston | N | 0.00011493 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.010806 | houston | -0.011419 | 0.0076988 | 0.28789 | -0.00011493 | 0.00011493 | houston | N | 0.00011493 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.010806 | houston | -0.011419 | 0.0076988 | 0.28789 | -0.00011493 | 0.00011493 | houston | N | 0.00011493 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.010806 | houston | -0.011419 | 0.0076988 | 0.28789 | -0.00011493 | 0.00011493 | houston | N | 0.00011493 | 0
39470 | TNDOWCGN | 1 | 32 | 0.010806 | houston | -0.011419 | 0.0076988 | 0.28789 | -0.00011493 | 0.00011493 | houston | N | 0.00011493 | 0
39480 | TNDOWCGN | 1 | 30 | 0.010806 | houston | -0.011419 | 0.0076988 | 0.28789 | -0.00011493 | 0.00011493 | houston | N | 0.00011493 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.009822 | houston | -0.012403 | 0.0067148 | 0.2869 | -0.0010989 | 0.0010989 | houston | N | 0.0010989 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.009822 | houston | -0.012403 | 0.0067148 | 0.2869 | -0.0010989 | 0.0010989 | houston | N | 0.0010989 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.009822 | houston | -0.012403 | 0.0067148 | 0.2869 | -0.0010989 | 0.0010989 | houston | N | 0.0010989 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.009822 | houston | -0.012403 | 0.0067148 | 0.2869 | -0.0010989 | 0.0010989 | houston | N | 0.0010989 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.017091 | north | -0.0051342 | 0.013984 | 0.29417 | 0.0061701 | 0.0051342 | North | N | 0.0051342 | 0
39970 | TNTNPONE | 1 | 153 | 0.017091 | north | -0.0051342 | 0.013984 | 0.29417 | 0.0061701 | 0.0051342 | North | N | 0.0051342 | 0
48500 | APD_GT1_ | 1 | 136 | 0.011396 | houston | -0.010829 | 0.0082888 | 0.28848 | 0.00047507 | 0.00047507 | houston | N | 0.00047507 | 0
48510 | AK_GT1__ | 1 | 33 | 0.01048 | houston | -0.011745 | 0.0073728 | 0.28756 | -0.00044093 | 0.00044093 | houston | N | 0.00044093 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.011395 | houston | -0.01083 | 0.0082878 | 0.28848 | 0.00047407 | 0.00047407 | houston | N | 0.00047407 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.011395 | houston | -0.01083 | 0.0082878 | 0.28848 | 0.00047407 | 0.00047407 | houston | N | 0.00047407 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.011395 | houston | -0.01083 | 0.0082878 | 0.28848 | 0.00047407 | 0.00047407 | houston | N | 0.00047407 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.011395 | houston | -0.01083 | 0.0082878 | 0.28848 | 0.00047407 | 0.00047407 | houston | N | 0.00047407 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.009644 | houston | -0.012581 | 0.0065368 | 0.28672 | -0.0012769 | 0.0012769 | houston | N | 0.0012769 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.009644 | houston | -0.012581 | 0.0065368 | 0.28672 | -0.0012769 | 0.0012769 | houston | N | 0.0012769 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.010455 | houston | -0.01177 | 0.0073478 | 0.28754 | -0.00046593 | 0.00046593 | houston | N | 0.00046593 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.010455 | houston | -0.01177 | 0.0073478 | 0.28754 | -0.00046593 | 0.00046593 | houston | N | 0.00046593 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.010455 | houston | -0.01177 | 0.0073478 | 0.28754 | -0.00046593 | 0.00046593 | houston | N | 0.00046593 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.011174 | houston | -0.011051 | 0.0080668 | 0.28825 | 0.00025307 | 0.00025307 | houston | N | 0.00025307 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.011174 | houston | -0.011051 | 0.0080668 | 0.28825 | 0.00025307 | 0.00025307 | houston | N | 0.00025307 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.011174 | houston | -0.011051 | 0.0080668 | 0.28825 | 0.00025307 | 0.00025307 | houston | N | 0.00025307 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.011174 | houston | -0.011051 | 0.0080668 | 0.28825 | 0.00025307 | 0.00025307 | houston | N | 0.00025307 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.011317 | houston | -0.010908 | 0.0082098 | 0.2884 | 0.00039607 | 0.00039607 | houston | N | 0.00039607 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.011317 | houston | -0.010908 | 0.0082098 | 0.2884 | 0.00039607 | 0.00039607 | houston | N | 0.00039607 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.011132 | houston | -0.011093 | 0.0080248 | 0.28821 | 0.00021107 | 0.00021107 | houston | N | 0.00021107 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.011132 | houston | -0.011093 | 0.0080248 | 0.28821 | 0.00021107 | 0.00021107 | houston | N | 0.00021107 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.011132 | houston | -0.011093 | 0.0080248 | 0.28821 | 0.00021107 | 0.00021107 | houston | N | 0.00021107 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.011132 | houston | -0.011093 | 0.0080248 | 0.28821 | 0.00021107 | 0.00021107 | houston | N | 0.00021107 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.011132 | houston | -0.011093 | 0.0080248 | 0.28821 | 0.00021107 | 0.00021107 | houston | N | 0.00021107 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.01157 | houston | -0.010655 | 0.0084628 | 0.28865 | 0.00064907 | 0.00064907 | houston | N | 0.00064907 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.011498 | houston | -0.010727 | 0.0083908 | 0.28858 | 0.00057707 | 0.00057707 | houston | N | 0.00057707 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.01159 | houston | -0.010635 | 0.0084828 | 0.28867 | 0.00066907 | 0.00066907 | houston | N | 0.00066907 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.01159 | houston | -0.010635 | 0.0084828 | 0.28867 | 0.00066907 | 0.00066907 | houston | N | 0.00066907 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.01159 | houston | -0.010635 | 0.0084828 | 0.28867 | 0.00066907 | 0.00066907 | houston | N | 0.00066907 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.011987 | houston | -0.010238 | 0.0088798 | 0.28907 | 0.0010661 | 0.0010661 | houston | N | 0.0010661 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.01141 | houston | -0.010815 | 0.0083028 | 0.28849 | 0.00048907 | 0.00048907 | houston | N | 0.00048907 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.01141 | houston | -0.010815 | 0.0083028 | 0.28849 | 0.00048907 | 0.00048907 | houston | N | 0.00048907 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.011641 | houston | -0.010584 | 0.0085338 | 0.28872 | 0.00072007 | 0.00072007 | houston | N | 0.00072007 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.011641 | houston | -0.010584 | 0.0085338 | 0.28872 | 0.00072007 | 0.00072007 | houston | N | 0.00072007 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.011641 | houston | -0.010584 | 0.0085338 | 0.28872 | 0.00072007 | 0.00072007 | houston | N | 0.00072007 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.011641 | houston | -0.010584 | 0.0085338 | 0.28872 | 0.00072007 | 0.00072007 | houston | N | 0.00072007 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.011321 | houston | -0.010904 | 0.0082138 | 0.2884 | 0.00040007 | 0.00040007 | houston | N | 0.00040007 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.011321 | houston | -0.010904 | 0.0082138 | 0.2884 | 0.00040007 | 0.00040007 | houston | N | 0.00040007 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.011321 | houston | -0.010904 | 0.0082138 | 0.2884 | 0.00040007 | 0.00040007 | houston | N | 0.00040007 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.011321 | houston | -0.010904 | 0.0082138 | 0.2884 | 0.00040007 | 0.00040007 | houston | N | 0.00040007 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.011271 | houston | -0.010954 | 0.0081638 | 0.28835 | 0.00035007 | 0.00035007 | houston | N | 0.00035007 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.011271 | houston | -0.010954 | 0.0081638 | 0.28835 | 0.00035007 | 0.00035007 | houston | N | 0.00035007 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.011271 | houston | -0.010954 | 0.0081638 | 0.28835 | 0.00035007 | 0.00035007 | houston | N | 0.00035007 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.011271 | houston | -0.010954 | 0.0081638 | 0.28835 | 0.00035007 | 0.00035007 | houston | N | 0.00035007 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.011271 | houston | -0.010954 | 0.0081638 | 0.28835 | 0.00035007 | 0.00035007 | houston | N | 0.00035007 | 0
48651 | EP_1_2 | 1 | 5 | 0.011567 | houston | -0.010658 | 0.0084598 | 0.28865 | 0.00064607 | 0.00064607 | houston | N | 0.00064607 | 0
48651 | EP_1_2 | 2 | 21 | 0.011567 | houston | -0.010658 | 0.0084598 | 0.28865 | 0.00064607 | 0.00064607 | houston | N | 0.00064607 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.014698 | north | -0.0075272 | 0.011591 | 0.29178 | 0.0037771 | 0.0037771 | houston | Y | 0.0075272 | 0.57827
48672 | FTR_GT2_ | 2 | 156 | 0.014698 | north | -0.0075272 | 0.011591 | 0.29178 | 0.0037771 | 0.0037771 | houston | Y | 0.0075272 | 0.58502
48673 | FTR_GT3_ | 3 | 156 | 0.014698 | north | -0.0075272 | 0.011591 | 0.29178 | 0.0037771 | 0.0037771 | houston | Y | 0.0075272 | 0.58502
48674 | FTR_CN4_ | 4 | 380 | 0.014698 | north | -0.0075272 | 0.011591 | 0.29178 | 0.0037771 | 0.0037771 | houston | Y | 0.0075272 | 1.425
48690 | GBY_GN5_ | 5 | 398 | 0.011663 | houston | -0.010562 | 0.0085558 | 0.28874 | 0.00074207 | 0.00074207 | houston | N | 0.00074207 | 0
48691 | GBY_7374 | A | 46 | 0.011249 | houston | -0.010976 | 0.0081418 | 0.28833 | 0.00032807 | 0.00032807 | houston | N | 0.00032807 | 0
48691 | GBY_7374 | B | 46 | 0.011249 | houston | -0.010976 | 0.0081418 | 0.28833 | 0.00032807 | 0.00032807 | houston | N | 0.00032807 | 0
48692 | GBY_8182 | C | 46 | 0.011249 | houston | -0.010976 | 0.0081418 | 0.28833 | 0.00032807 | 0.00032807 | houston | N | 0.00032807 | 0
48692 | GBY_8182 | D | 55 | 0.011249 | houston | -0.010976 | 0.0081418 | 0.28833 | 0.00032807 | 0.00032807 | houston | N | 0.00032807 | 0
48693 | GBY_8384 | E | 55 | 0.011249 | houston | -0.010976 | 0.0081418 | 0.28833 | 0.00032807 | 0.00032807 | houston | N | 0.00032807 | 0
48693 | GBY_8384 | F | 54 | 0.011249 | houston | -0.010976 | 0.0081418 | 0.28833 | 0.00032807 | 0.00032807 | houston | N | 0.00032807 | 0
48721 | LEG_1___ | 1 | 827 | 0.017827 | north | -0.0043982 | 0.01472 | 0.29491 | 0.0069061 | 0.0043982 | North | N | 0.0043982 | 0
48722 | LEG_2___ | 2 | 819 | 0.017827 | north | -0.0043982 | 0.01472 | 0.29491 | 0.0069061 | 0.0043982 | North | N | 0.0043982 | 0
48730 | MNS_GT | 1 | 46.1 | 0.010394 | houston | -0.011831 | 0.0072868 | 0.28747 | -0.00052693 | 0.00052693 | houston | N | 0.00052693 | 0
48731 | CBE_GT1 | 1 | 76 | 0.008424 | houston | -0.013801 | 0.0053168 | 0.2855 | -0.0024969 | 0.0024969 | houston | N | 0.0024969 | 0
48732 | CBE_GT2 | 1 | 76 | 0.008424 | houston | -0.013801 | 0.0053168 | 0.2855 | -0.0024969 | 0.0024969 | houston | N | 0.0024969 | 0
48733 | CBE_ST12 | 1 | 105 | 0.008424 | houston | -0.013801 | 0.0053168 | 0.2855 | -0.0024969 | 0.0024969 | houston | N | 0.0024969 | 0
48734 | CBE_GT3 | 1 | 74 | 0.008424 | houston | -0.013801 | 0.0053168 | 0.2855 | -0.0024969 | 0.0024969 | houston | N | 0.0024969 | 0
48735 | CBE_GT4 | 1 | 74 | 0.008424 | houston | -0.013801 | 0.0053168 | 0.2855 | -0.0024969 | 0.0024969 | houston | N | 0.0024969 | 0
48736 | CBE_ST34 | 1 | 102 | 0.008424 | houston | -0.013801 | 0.0053168 | 0.2855 | -0.0024969 | 0.0024969 | houston | N | 0.0024969 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.011323 | houston | -0.010902 | 0.0082158 | 0.2884 | 0.00040207 | 0.00040207 | houston | N | 0.00040207 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.011323 | houston | -0.010902 | 0.0082158 | 0.2884 | 0.00040207 | 0.00040207 | houston | N | 0.00040207 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.011323 | houston | -0.010902 | 0.0082158 | 0.2884 | 0.00040207 | 0.00040207 | houston | N | 0.00040207 | 0
48761 | PR_GT1__ | 1 | 35 | 0.011295 | houston | -0.01093 | 0.0081878 | 0.28838 | 0.00037407 | 0.00037407 | houston | N | 0.00037407 | 0
48772 | PHR_GN2_ | MB | 459 | 0.011021 | houston | -0.011204 | 0.0079138 | 0.2881 | 0.00010007 | 0.00010007 | houston | N | 0.00010007 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.011569 | houston | -0.010656 | 0.0084618 | 0.28865 | 0.00064807 | 0.00064807 | houston | N | 0.00064807 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.011569 | houston | -0.010656 | 0.0084618 | 0.28865 | 0.00064807 | 0.00064807 | houston | N | 0.00064807 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.011569 | houston | -0.010656 | 0.0084618 | 0.28865 | 0.00064807 | 0.00064807 | houston | N | 0.00064807 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.011569 | houston | -0.010656 | 0.0084618 | 0.28865 | 0.00064807 | 0.00064807 | houston | N | 0.00064807 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.011569 | houston | -0.010656 | 0.0084618 | 0.28865 | 0.00064807 | 0.00064807 | houston | N | 0.00064807 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.011569 | houston | -0.010656 | 0.0084618 | 0.28865 | 0.00064807 | 0.00064807 | houston | N | 0.00064807 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.011569 | houston | -0.010656 | 0.0084618 | 0.28865 | 0.00064807 | 0.00064807 | houston | N | 0.00064807 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.011987 | houston | -0.010238 | 0.0088798 | 0.28907 | 0.0010661 | 0.0010661 | houston | N | 0.0010661 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.011987 | houston | -0.010238 | 0.0088798 | 0.28907 | 0.0010661 | 0.0010661 | houston | N | 0.0010661 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.011987 | houston | -0.010238 | 0.0088798 | 0.28907 | 0.0010661 | 0.0010661 | houston | N | 0.0010661 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.011987 | houston | -0.010238 | 0.0088798 | 0.28907 | 0.0010661 | 0.0010661 | houston | N | 0.0010661 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.011586 | houston | -0.010639 | 0.0084788 | 0.28867 | 0.00066507 | 0.00066507 | houston | N | 0.00066507 | 0
48820 | SHELLG1_ | 1 | 71 | 0.011349 | houston | -0.010876 | 0.0082418 | 0.28843 | 0.00042807 | 0.00042807 | houston | N | 0.00042807 | 0
48821 | SHELLG2 | 2 | 72 | 0.011349 | houston | -0.010876 | 0.0082418 | 0.28843 | 0.00042807 | 0.00042807 | houston | N | 0.00042807 | 0
48822 | SHELLG3_ | 1 | 39 | 0.011349 | houston | -0.010876 | 0.0082418 | 0.28843 | 0.00042807 | 0.00042807 | houston | N | 0.00042807 | 0
48822 | SHELLG3_ | 2 | 30 | 0.011349 | houston | -0.010876 | 0.0082418 | 0.28843 | 0.00042807 | 0.00042807 | houston | N | 0.00042807 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.011253 | houston | -0.010972 | 0.0081458 | 0.28833 | 0.00033207 | 0.00033207 | houston | N | 0.00033207 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.011253 | houston | -0.010972 | 0.0081458 | 0.28833 | 0.00033207 | 0.00033207 | houston | N | 0.00033207 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.011321 | houston | -0.010904 | 0.0082138 | 0.2884 | 0.00040007 | 0.00040007 | houston | N | 0.00040007 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.011315 | houston | -0.01091 | 0.0082078 | 0.2884 | 0.00039407 | 0.00039407 | houston | N | 0.00039407 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.011314 | houston | -0.010911 | 0.0082068 | 0.28839 | 0.00039307 | 0.00039307 | houston | N | 0.00039307 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.01132 | houston | -0.010905 | 0.0082128 | 0.2884 | 0.00039907 | 0.00039907 | houston | N | 0.00039907 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.011322 | houston | -0.010903 | 0.0082148 | 0.2884 | 0.00040107 | 0.00040107 | houston | N | 0.00040107 | 0
48855 | SRB_GT21 | B2 | 12 | 0.011313 | houston | -0.010912 | 0.0082058 | 0.28839 | 0.00039207 | 0.00039207 | houston | N | 0.00039207 | 0
48855 | SRB_GT21 | MB | 18 | 0.011313 | houston | -0.010912 | 0.0082058 | 0.28839 | 0.00039207 | 0.00039207 | houston | N | 0.00039207 | 0
48865 | TECO_GT1 | 1 | 50 | 0.010946 | houston | -0.011279 | 0.0078388 | 0.28803 | 2.5072e-05 | 2.5072e-05 | houston | N | 2.5072e-05 | 0
48873 | THW_ST3_ | 3 | 104 | 0.011486 | houston | -0.010739 | 0.0083788 | 0.28857 | 0.00056507 | 0.00056507 | houston | N | 0.00056507 | 0
48874 | THW_ST4_ | 4 | 104 | 0.011486 | houston | -0.010739 | 0.0083788 | 0.28857 | 0.00056507 | 0.00056507 | houston | N | 0.00056507 | 0
48875 | THW_3132 | A | 54 | 0.011486 | houston | -0.010739 | 0.0083788 | 0.28857 | 0.00056507 | 0.00056507 | houston | N | 0.00056507 | 0
48875 | THW_3132 | B | 53 | 0.011486 | houston | -0.010739 | 0.0083788 | 0.28857 | 0.00056507 | 0.00056507 | houston | N | 0.00056507 | 0
48877 | THW_3334 | C | 54 | 0.011486 | houston | -0.010739 | 0.0083788 | 0.28857 | 0.00056507 | 0.00056507 | houston | N | 0.00056507 | 0
48877 | THW_3334 | D | 57 | 0.011486 | houston | -0.010739 | 0.0083788 | 0.28857 | 0.00056507 | 0.00056507 | houston | N | 0.00056507 | 0
48879 | THW_4142 | E | 54 | 0.011486 | houston | -0.010739 | 0.0083788 | 0.28857 | 0.00056507 | 0.00056507 | houston | N | 0.00056507 | 0
48879 | THW_4142 | F | 54 | 0.011486 | houston | -0.010739 | 0.0083788 | 0.28857 | 0.00056507 | 0.00056507 | houston | N | 0.00056507 | 0
48881 | THW_4344 | G | 58 | 0.011486 | houston | -0.010739 | 0.0083788 | 0.28857 | 0.00056507 | 0.00056507 | houston | N | 0.00056507 | 0
48881 | THW_4344 | H | 58 | 0.011486 | houston | -0.010739 | 0.0083788 | 0.28857 | 0.00056507 | 0.00056507 | houston | N | 0.00056507 | 0
48883 | THW_GT1_ | B2 | 12 | 0.011549 | houston | -0.010676 | 0.0084418 | 0.28863 | 0.00062807 | 0.00062807 | houston | N | 0.00062807 | 0
48885 | THW_5152 | A | 56 | 0.011696 | houston | -0.010529 | 0.0085888 | 0.28878 | 0.00077507 | 0.00077507 | houston | N | 0.00077507 | 0
48885 | THW_5152 | B | 59 | 0.011696 | houston | -0.010529 | 0.0085888 | 0.28878 | 0.00077507 | 0.00077507 | houston | N | 0.00077507 | 0
48886 | THW_5354 | C | 56 | 0.011696 | houston | -0.010529 | 0.0085888 | 0.28878 | 0.00077507 | 0.00077507 | houston | N | 0.00077507 | 0
48886 | THW_5354 | D | 56 | 0.011696 | houston | -0.010529 | 0.0085888 | 0.28878 | 0.00077507 | 0.00077507 | houston | N | 0.00077507 | 0
48887 | THW_5556 | E | 59 | 0.011696 | houston | -0.010529 | 0.0085888 | 0.28878 | 0.00077507 | 0.00077507 | houston | N | 0.00077507 | 0
48887 | THW_5556 | F | 56 | 0.011696 | houston | -0.010529 | 0.0085888 | 0.28878 | 0.00077507 | 0.00077507 | houston | N | 0.00077507 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.008561 | houston | -0.013664 | 0.0054538 | 0.28564 | -0.0023599 | 0.0023599 | houston | N | 0.0023599 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.010562 | houston | -0.011663 | 0.0074548 | 0.28764 | -0.00035893 | 0.00035893 | houston | N | 0.00035893 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.010562 | houston | -0.011663 | 0.0074548 | 0.28764 | -0.00035893 | 0.00035893 | houston | N | 0.00035893 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.010562 | houston | -0.011663 | 0.0074548 | 0.28764 | -0.00035893 | 0.00035893 | houston | N | 0.00035893 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.010562 | houston | -0.011663 | 0.0074548 | 0.28764 | -0.00035893 | 0.00035893 | houston | N | 0.00035893 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.010562 | houston | -0.011663 | 0.0074548 | 0.28764 | -0.00035893 | 0.00035893 | houston | N | 0.00035893 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.01045 | houston | -0.011775 | 0.0073428 | 0.28753 | -0.00047093 | 0.00047093 | houston | N | 0.00047093 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.01045 | houston | -0.011775 | 0.0073428 | 0.28753 | -0.00047093 | 0.00047093 | houston | N | 0.00047093 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.01045 | houston | -0.011775 | 0.0073428 | 0.28753 | -0.00047093 | 0.00047093 | houston | N | 0.00047093 | 0
48929 | WAPGT21_ | B1 | 13 | 0.010562 | houston | -0.011663 | 0.0074548 | 0.28764 | -0.00035893 | 0.00035893 | houston | N | 0.00035893 | 0
48940 | WARVUE_G | G1 | 12 | 0.011568 | houston | -0.010657 | 0.0084608 | 0.28865 | 0.00064707 | 0.00064707 | houston | N | 0.00064707 | 0
49803 | EXN_15GT | 1 | 34 | 0.011516 | houston | -0.010709 | 0.0084088 | 0.2886 | 0.00059507 | 0.00059507 | houston | N | 0.00059507 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.011516 | houston | -0.010709 | 0.0084088 | 0.2886 | 0.00059507 | 0.00059507 | houston | N | 0.00059507 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.011516 | houston | -0.010709 | 0.0084088 | 0.2886 | 0.00059507 | 0.00059507 | houston | N | 0.00059507 | 0
49826 | EXN938GT | 5 | 45.9 | 0.011516 | houston | -0.010709 | 0.0084088 | 0.2886 | 0.00059507 | 0.00059507 | houston | N | 0.00059507 | 0
49828 | EXN941GT | 10 | 17.7 | 0.011516 | houston | -0.010709 | 0.0084088 | 0.2886 | 0.00059507 | 0.00059507 | houston | N | 0.00059507 | 0
49829 | EXN942GT | 11 | 20.4 | 0.011516 | houston | -0.010709 | 0.0084088 | 0.2886 | 0.00059507 | 0.00059507 | houston | N | 0.00059507 | 0
49830 | EXN943GT | 12 | 19.9 | 0.011516 | houston | -0.010709 | 0.0084088 | 0.2886 | 0.00059507 | 0.00059507 | houston | N | 0.00059507 | 0
49831 | EXN944GT | 13 | 35 | 0.011516 | houston | -0.010709 | 0.0084088 | 0.2886 | 0.00059507 | 0.00059507 | houston | N | 0.00059507 | 0
49832 | EXN945GT | 9 | 18 | 0.011516 | houston | -0.010709 | 0.0084088 | 0.2886 | 0.00059507 | 0.00059507 | houston | N | 0.00059507 | 0
49837 | EXN_GT | 4 | 85.4 | 0.011516 | houston | -0.010709 | 0.0084088 | 0.2886 | 0.00059507 | 0.00059507 | houston | N | 0.00059507 | 0
49838 | EXN_14GT | 14 | 148 | 0.011516 | houston | -0.010709 | 0.0084088 | 0.2886 | 0.00059507 | 0.00059507 | houston | N | 0.00059507 | 0
49851 | DOW17000 | 37 | 62 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49858 | DOW38100 | 31 | 71.4 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49859 | DOW38200 | 33 | 45 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49860 | DOW38300 | 32 | 101 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49862 | DOW39100 | 36 | 86 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49863 | DOW39200 | 35 | 88 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49865 | DOW41000 | 41 | 50 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49866 | DOW42000 | 42 | 18 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49869 | DOW49000 | 45 | 94 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49870 | DOW61000 | 61 | 70 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49871 | DOW62000 | 62 | 63 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49872 | DOW63000 | 63 | 72 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49873 | DOW64000 | 64 | 64.8 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49876 | DOW65000 | 65 | 101 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49877 | DOW66000 | 66 | 97 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49878 | DOW67000 | 67 | 103 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49882 | DOW81000 | 81 | 76 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49884 | DOW82000 | 82 | 80 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49885 | DOW83000 | 83 | 80 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
49886 | DOW84000 | 84 | 171 | 0.009434 | houston | -0.012791 | 0.0063268 | 0.28651 | -0.0014869 | 0.0014869 | houston | N | 0.0014869 | 0
58909 | PEARSALL | 1 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58909 | PEARSALL | 2 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58909 | PEARSALL | 3 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58909 | PEARSALL | 4 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58909 | PEARSALL | 5 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58909 | PEARSALL | 6 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58919 | PEARSALL | 1 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58919 | PEARSALL | 2 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58919 | PEARSALL | 3 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58919 | PEARSALL | 4 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58919 | PEARSALL | 5 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58919 | PEARSALL | 6 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58929 | PEARSALL | 1 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58929 | PEARSALL | 2 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58929 | PEARSALL | 3 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58929 | PEARSALL | 4 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58929 | PEARSALL | 5 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58929 | PEARSALL | 6 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58949 | PEARSALL | 1 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58949 | PEARSALL | 2 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58949 | PEARSALL | 3 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58949 | PEARSALL | 4 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58949 | PEARSALL | 5 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
58949 | PEARSALL | 6 | 8.4 | -0.010096 | south | -0.032321 | -0.013203 | 0.26698 | -0.021017 | 0.013203 | south | N | 0.013203 | 0
60000 | DSKY2 | 1 | 76.5 | -0.25291 | west | -0.27513 | -0.25601 | 0.024175 | -0.26383 | 0.024175 | west | N | 0.024175 | 0
60003 | KING_NE1 | 1 | 80 | -0.25993 | west | -0.28215 | -0.26304 | 0.017152 | -0.27085 | 0.017152 | west | N | 0.017152 | 0
60005 | KING_SE1 | 1 | 40 | -0.25993 | west | -0.28215 | -0.26304 | 0.017152 | -0.27085 | 0.017152 | west | N | 0.017152 | 0
60007 | KING_SW1 | 1 | 80 | -0.26097 | west | -0.28319 | -0.26407 | 0.016115 | -0.27189 | 0.016115 | west | N | 0.016115 | 0
60016 | WOODWRD1 | 1 | 80 | -0.25971 | west | -0.28194 | -0.26282 | 0.017367 | -0.27063 | 0.017367 | west | N | 0.017367 | 0
60017 | ORNNWP1 | 1 | 80 | -0.25425 | west | -0.27648 | -0.25736 | 0.022829 | -0.26517 | 0.022829 | west | N | 0.022829 | 0
60018 | DSKY1 | 1 | 84 | -0.25247 | west | -0.27469 | -0.25557 | 0.024615 | -0.26339 | 0.024615 | west | N | 0.024615 | 0
60019 | KING_NW1 | 1 | 80 | -0.26097 | west | -0.28319 | -0.26407 | 0.016115 | -0.27189 | 0.016115 | west | N | 0.016115 | 0
60057 | CALLAHAN | 1 | 114 | 0.000621 | south | -0.021604 | -0.0024862 | 0.2777 | -0.0103 | 0.0024862 | south | N | 0.0024862 | 0
60058 | BUFF_GAP | 1 | 120 | -0.30173 | west | -0.32396 | -0.30484 | -0.024651 | -0.31265 | 0.024651 | west | N | 0.024651 | 0
60060 | CIRELLO | 1 | 233 | -0.30173 | west | -0.32396 | -0.30484 | -0.024651 | -0.31265 | 0.024651 | west | N | 0.024651 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.30173 | west | -0.32396 | -0.30484 | -0.024651 | -0.31265 | 0.024651 | west | N | 0.024651 | 0
60066 | H_HOLLOW | 1 | 222 | 0.000621 | south | -0.021604 | -0.0024862 | 0.2777 | -0.0103 | 0.0024862 | south | N | 0.0024862 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.000621 | south | -0.021604 | -0.0024862 | 0.2777 | -0.0103 | 0.0024862 | south | N | 0.0024862 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.000621 | south | -0.021604 | -0.0024862 | 0.2777 | -0.0103 | 0.0024862 | south | N | 0.0024862 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.000621 | south | -0.021604 | -0.0024862 | 0.2777 | -0.0103 | 0.0024862 | south | N | 0.0024862 | 0
60074 | HORSH5 | 1 | 100 | 0.000621 | south | -0.021604 | -0.0024862 | 0.2777 | -0.0103 | 0.0024862 | south | N | 0.0024862 | 0
60081 | WHRLWIND | 1 | 60 | -0.20609 | west | -0.22832 | -0.2092 | 0.070989 | -0.21701 | 0.070989 | west | N | 0.070989 | 0
60201 | RIO DRCS | F | 0 | -0.079135 | south | -0.10136 | -0.082242 | 0.19795 | -0.090056 | 0.082242 | south | N | 0.082242 | 0
60202 | FRIEND_R | F | 0 | -0.22424 | west | -0.24647 | -0.22735 | 0.052838 | -0.23516 | 0.052838 | west | N | 0.052838 | 0
60203 | PRES0A | BT | 4.8 | -0.26516 | west | -0.28738 | -0.26827 | 0.011923 | -0.27608 | 0.011923 | west | N | 0.011923 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.3156 | west | -0.33783 | -0.31871 | -0.038522 | -0.32652 | 0.038522 | west | N | 0.038522 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.3156 | west | -0.33783 | -0.31871 | -0.038522 | -0.32652 | 0.038522 | west | N | 0.038522 | 0
71057 | L_SWEETW | W1 | 135 | -0.3156 | west | -0.33783 | -0.31871 | -0.038522 | -0.32652 | 0.038522 | west | N | 0.038522 | 0
71059 | L_SWEETW | W1 | 119 | -0.3156 | west | -0.33783 | -0.31871 | -0.038522 | -0.32652 | 0.038522 | west | N | 0.038522 | 0
71060 | L_SWEETW | W1 | 105 | -0.3156 | west | -0.33783 | -0.31871 | -0.038522 | -0.32652 | 0.038522 | west | N | 0.038522 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.3156 | west | -0.33783 | -0.31871 | -0.038522 | -0.32652 | 0.038522 | west | N | 0.038522 | 0
76031 | L_GASCCR | W1 | 150 | -0.26859 | west | -0.29081 | -0.2717 | 0.0084918 | -0.27951 | 0.0084918 | west | N | 0.0084918 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.26589 | west | -0.28811 | -0.269 | 0.011192 | -0.27681 | 0.011192 | west | N | 0.011192 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.26589 | west | -0.28811 | -0.269 | 0.011192 | -0.27681 | 0.011192 | west | N | 0.011192 | 0
76096 | L_CAPRSI | W1 | 186 | -0.26589 | west | -0.28811 | -0.269 | 0.011192 | -0.27681 | 0.011192 | west | N | 0.011192 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.26589 | west | -0.28811 | -0.269 | 0.011192 | -0.27681 | 0.011192 | west | N | 0.011192 | 0
80003 | MILHWYS | F | 0 | 0.002716 | south | -0.019509 | -0.00039121 | 0.2798 | -0.0082049 | 0.00039121 | south | N | 0.00039121 | 0
80010 | EPLVT1 | F | 0 | -0.048206 | south | -0.070431 | -0.051313 | 0.22887 | -0.059127 | 0.051313 | south | N | 0.051313 | 0
80012 | LAR | F | 0 | -0.004132 | south | -0.026357 | -0.0072392 | 0.27295 | -0.015053 | 0.0072392 | south | N | 0.0072392 | 0
80051 | FORPVCM0 | 8 | 28 | 0.004815 | south | -0.01741 | 0.0017078 | 0.2819 | -0.0061059 | 0.0017078 | south | N | 0.0017078 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.004815 | south | -0.01741 | 0.0017078 | 0.2819 | -0.0061059 | 0.0017078 | south | N | 0.0017078 | 0
80053 | FOR69CG0 | 10 | 74 | 0.004815 | south | -0.01741 | 0.0017078 | 0.2819 | -0.0061059 | 0.0017078 | south | N | 0.0017078 | 0
80080 | GWINDT11 | 1 | 94 | 0.002797 | south | -0.019428 | -0.00031021 | 0.27988 | -0.0081239 | 0.00031021 | south | N | 0.00031021 | 0
80080 | GWINDT11 | 2 | 41 | 0.002797 | south | -0.019428 | -0.00031021 | 0.27988 | -0.0081239 | 0.00031021 | south | N | 0.00031021 | 0
80080 | GWINDT11 | 3 | 38 | 0.002797 | south | -0.019428 | -0.00031021 | 0.27988 | -0.0081239 | 0.00031021 | south | N | 0.00031021 | 0
80080 | GWINDT11 | 4 | 19 | 0.002797 | south | -0.019428 | -0.00031021 | 0.27988 | -0.0081239 | 0.00031021 | south | N | 0.00031021 | 0
80081 | GWINDT21 | 1 | 94 | 0.002797 | south | -0.019428 | -0.00031021 | 0.27988 | -0.0081239 | 0.00031021 | south | N | 0.00031021 | 0
80081 | GWINDT21 | 2 | 36 | 0.002797 | south | -0.019428 | -0.00031021 | 0.27988 | -0.0081239 | 0.00031021 | south | N | 0.00031021 | 0
80081 | GWINDT21 | 3 | 43 | 0.002797 | south | -0.019428 | -0.00031021 | 0.27988 | -0.0081239 | 0.00031021 | south | N | 0.00031021 | 0
80081 | GWINDT21 | 4 | 22 | 0.002797 | south | -0.019428 | -0.00031021 | 0.27988 | -0.0081239 | 0.00031021 | south | N | 0.00031021 | 0
80137 | CSDR89 | 8 | 39 | 0.004338 | south | -0.017887 | 0.0012308 | 0.28142 | -0.0065829 | 0.0012308 | south | N | 0.0012308 | 0
80137 | CSDR89 | 9 | 15 | 0.004338 | south | -0.017887 | 0.0012308 | 0.28142 | -0.0065829 | 0.0012308 | south | N | 0.0012308 | 0
80138 | CSDR7 | 7 | 7 | 0.004338 | south | -0.017887 | 0.0012308 | 0.28142 | -0.0065829 | 0.0012308 | south | N | 0.0012308 | 0
80139 | CSDR56 | 5 | 15 | 0.004338 | south | -0.017887 | 0.0012308 | 0.28142 | -0.0065829 | 0.0012308 | south | N | 0.0012308 | 0
80139 | CSDR56 | 6 | 39 | 0.004338 | south | -0.017887 | 0.0012308 | 0.28142 | -0.0065829 | 0.0012308 | south | N | 0.0012308 | 0
80140 | CSDR11 | 11 | 39 | 0.004338 | south | -0.017887 | 0.0012308 | 0.28142 | -0.0065829 | 0.0012308 | south | N | 0.0012308 | 0
80180 | PNSCALT1 | 1 | 148 | 0.002797 | south | -0.019428 | -0.00031021 | 0.27988 | -0.0081239 | 0.00031021 | south | N | 0.00031021 | 0
80180 | PNSCALT1 | 2 | 50 | 0.002797 | south | -0.019428 | -0.00031021 | 0.27988 | -0.0081239 | 0.00031021 | south | N | 0.00031021 | 0
80181 | PNSCALT2 | 1 | 55 | 0.002797 | south | -0.019428 | -0.00031021 | 0.27988 | -0.0081239 | 0.00031021 | south | N | 0.00031021 | 0
80181 | PNSCALT2 | 2 | 50 | 0.002797 | south | -0.019428 | -0.00031021 | 0.27988 | -0.0081239 | 0.00031021 | south | N | 0.00031021 | 0
80223 | REYSHR G | 1 | 12 | 0.003296 | south | -0.018929 | 0.00018879 | 0.28038 | -0.0076249 | 0.00018879 | south | N | 0.00018879 | 0
80224 | VISTRONG | 1 | 15 | 0.004234 | south | -0.017991 | 0.0011268 | 0.28131 | -0.0066869 | 0.0011268 | south | N | 0.0011268 | 0
80225 | VISTRONG | 2 | 23 | 0.004234 | south | -0.017991 | 0.0011268 | 0.28131 | -0.0066869 | 0.0011268 | south | N | 0.0011268 | 0
80226 | ALCOA G | 1 | 48 | 0.004714 | south | -0.017511 | 0.0016068 | 0.28179 | -0.0062069 | 0.0016068 | south | N | 0.0016068 | 0
80227 | AIRCO G | 1 | 8 | 0.004265 | south | -0.01796 | 0.0011578 | 0.28135 | -0.0066559 | 0.0011578 | south | N | 0.0011578 | 0
80261 | NBEC81A | 1 | 180 | 0.003086 | south | -0.019139 | -2.1211e-05 | 0.28017 | -0.0078349 | 2.1211e-05 | south | N | 2.1211e-05 | 0
80262 | NBEC91A | 1 | 180 | 0.003092 | south | -0.019133 | -1.5211e-05 | 0.28017 | -0.0078289 | 1.5211e-05 | south | N | 1.5211e-05 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.003052 | south | -0.019173 | -5.5211e-05 | 0.28013 | -0.0078689 | 5.5211e-05 | south | N | 5.5211e-05 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.003052 | south | -0.019173 | -5.5211e-05 | 0.28013 | -0.0078689 | 5.5211e-05 | south | N | 5.5211e-05 | 0
80265 | LARECU40 | 4 | 100 | -0.004128 | south | -0.026353 | -0.0072352 | 0.27295 | -0.015049 | 0.0072352 | south | N | 0.0072352 | 0
80266 | LARECU50 | 5 | 100 | -0.004128 | south | -0.026353 | -0.0072352 | 0.27295 | -0.015049 | 0.0072352 | south | N | 0.0072352 | 0
80291 | PAPALOTE | 1 | 25 | 0.00321 | south | -0.019015 | 0.00010279 | 0.28029 | -0.0077109 | 0.00010279 | south | N | 0.00010279 | 0
80291 | PAPALOTE | 2 | 25 | 0.00321 | south | -0.019015 | 0.00010279 | 0.28029 | -0.0077109 | 0.00010279 | south | N | 0.00010279 | 0
80291 | PAPALOTE | 3 | 25 | 0.00321 | south | -0.019015 | 0.00010279 | 0.28029 | -0.0077109 | 0.00010279 | south | N | 0.00010279 | 0
80291 | PAPALOTE | 4 | 16 | 0.00321 | south | -0.019015 | 0.00010279 | 0.28029 | -0.0077109 | 0.00010279 | south | N | 0.00010279 | 0
80294 | PAPALOTE | 5 | 25 | 0.00321 | south | -0.019015 | 0.00010279 | 0.28029 | -0.0077109 | 0.00010279 | south | N | 0.00010279 | 0
80294 | PAPALOTE | 6 | 25 | 0.00321 | south | -0.019015 | 0.00010279 | 0.28029 | -0.0077109 | 0.00010279 | south | N | 0.00010279 | 0
80294 | PAPALOTE | 7 | 25 | 0.00321 | south | -0.019015 | 0.00010279 | 0.28029 | -0.0077109 | 0.00010279 | south | N | 0.00010279 | 0
80294 | PAPALOTE | 8 | 15 | 0.00321 | south | -0.019015 | 0.00010279 | 0.28029 | -0.0077109 | 0.00010279 | south | N | 0.00010279 | 0
86104 | CID-138 | EQ | 0 | -0.004128 | south | -0.026353 | -0.0072352 | 0.27295 | -0.015049 | 0.0072352 | south | N | 0.0072352 | 0
86105 | CID-230 | EQ | 500 | -0.004128 | south | -0.026353 | -0.0072352 | 0.27295 | -0.015049 | 0.0072352 | south | N | 0.0072352 | 0
86106 | CUF-230 | EQ | 500 | -0.004128 | south | -0.026353 | -0.0072352 | 0.27295 | -0.015049 | 0.0072352 | south | N | 0.0072352 | 0
86107 | CUF-138 | EQ | 0 | -0.004128 | south | -0.026353 | -0.0072352 | 0.27295 | -0.015049 | 0.0072352 | south | N | 0.0072352 | 0
88198 | BEEVILLE | F | 0 | 0.001915 | south | -0.02031 | -0.0011922 | 0.279 | -0.0090059 | 0.0011922 | south | N | 0.0011922 | 0
88253 | HAMILTON | F | 0 | -0.074039 | south | -0.096264 | -0.077146 | 0.20304 | -0.08496 | 0.077146 | south | N | 0.077146 | 0
88299 | ZAPATA | F | 0 | -0.001865 | south | -0.02409 | -0.0049722 | 0.27522 | -0.012786 | 0.0049722 | south | N | 0.0049722 | 0
88508 | FALFURRI | F | 0 | 0.001732 | south | -0.020493 | -0.0013752 | 0.27881 | -0.0091889 | 0.0013752 | south | N | 0.0013752 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: GRHAMSES - COKFIELD 345kV [1430 - 1442] C: GRHAMSES - LONGCREK 345kV [1430 - 1435] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.086971 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.8314 | 366 | 0.35501 | 129.9338 | 366 | 129.9338
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.046657 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.518 | 204 | 0.3147 | 64.1981 | 570 | 194.1319
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.046657 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3781 | 201 | 0.3147 | 63.254 | 771 | 257.3859
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.046657 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.291 | 242 | 0.3147 | 76.1565 | 1013 | 333.5424 | Weighted Shift Factors
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.011987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.0738 | 0 | -0.010238 | 0 | 1013 | 333.5424 | north | 0.022225
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.011987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.87 | 0 | -0.010238 | 0 | 1013 | 333.5424 | west | -0.26804
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.011987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.846 | 0 | -0.010238 | 0 | 1013 | 333.5424 |  | 0.29026
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.011987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.846 | 0 | -0.010238 | 0 | 1013 | 333.5424
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.011987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9419 | 0 | -0.010238 | 0 | 1013 | 333.5424 | Line Rating | 1340
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65498 | 56 | -0.010529 | -0.58963 | 1069 | 332.9528 | Conc Gen | 2269
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.69006 | 59 | -0.010529 | -0.62122 | 1128 | 332.3316 | Weighted Imp. | 333.5424
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65498 | 56 | -0.010529 | -0.58963 | 1184 | 331.7419 | PTDF | 0.147
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65498 | 56 | -0.010529 | -0.58963 | 1240 | 331.1523
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.69006 | 59 | -0.010529 | -0.62122 | 1299 | 330.5311 | Concentration | 0.50643
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65498 | 56 | -0.010529 | -0.58963 | 1355 | 329.9414
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.011663 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.6419 | 398 | -0.010562 | -4.2037 | 1753 | 325.7377
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.011641 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8952 | 0 | -0.010584 | 0 | 1753 | 325.7377
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.011641 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8789 | 0 | -0.010584 | 0 | 1753 | 325.7377
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.011641 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8498 | 0 | -0.010584 | 0 | 1753 | 325.7377
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.011641 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1338 | 0 | -0.010584 | 0 | 1753 | 325.7377
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.01159 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.9935 | 172 | -0.010635 | -1.8293 | 1925 | 323.9084
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.01159 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.9935 | 172 | -0.010635 | -1.8293 | 2097 | 322.0792
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.01159 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.9935 | 172 | -0.010635 | -1.8293 | 2269 | 320.2499
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.011586 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.819 | 0 | -0.010639 | 0 | 2269 | 320.2499
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.01157 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 8.5965 | 743 | -0.010655 | -7.9168
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75199 | 0 | -0.010656 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.76355 | 0 | -0.010656 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80983 | 0 | -0.010656 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72885 | 0 | -0.010656 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71728 | 0 | -0.010656 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2032 | 0 | -0.010656 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68257 | 0 | -0.010656 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.011568 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.13882 | 12 | -0.010657 | -0.12789
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.011567 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.057835 | 0 | -0.010658 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.011567 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.24291 | 0 | -0.010658 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.011549 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13859 | 12 | -0.010676 | -0.12811
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39154 | 0 | -0.010709 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39961 | 0 | -0.010709 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.37657 | 0 | -0.010709 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52858 | 0 | -0.010709 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20383 | 0 | -0.010709 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23493 | 0 | -0.010709 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22917 | 0 | -0.010709 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.40306 | 0 | -0.010709 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20729 | 0 | -0.010709 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.98347 | 0 | -0.010709 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.7044 | 0 | -0.010709 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.011498 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 8.451 | 735 | -0.010727 | -7.8845
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1945 | 104 | -0.010739 | -1.1169
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1945 | 104 | -0.010739 | -1.1169
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62024 | 54 | -0.010739 | -0.57992
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.60876 | 53 | -0.010739 | -0.56918
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62024 | 54 | -0.010739 | -0.57992
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.6547 | 57 | -0.010739 | -0.61213
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62024 | 54 | -0.010739 | -0.57992
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62024 | 54 | -0.010739 | -0.57992
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.66619 | 58 | -0.010739 | -0.62287
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.66619 | 58 | -0.010739 | -0.62287
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.01141 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9739 | 0 | -0.010815 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.01141 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5404 | 0 | -0.010815 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.011396 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5499 | 0 | -0.010829 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.011395 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.47859 | 42 | -0.01083 | -0.45487
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.011395 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.47859 | 42 | -0.01083 | -0.45487
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.011395 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.43301 | 38 | -0.01083 | -0.41155
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.011395 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.43301 | 38 | -0.01083 | -0.41155
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80578 | 0 | -0.010876 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.81713 | 0 | -0.010876 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.44261 | 0 | -0.010876 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34047 | 0 | -0.010876 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.011323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.0381 | 0 | -0.010902 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.011323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7958 | 0 | -0.010902 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.011323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7777 | 0 | -0.010902 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.011322 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.5814 | 228 | -0.010903 | -2.4859
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1834 | 0 | -0.010904 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72454 | 0 | -0.010904 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71549 | 0 | -0.010904 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.93511 | 0 | -0.010904 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.83323 | 0 | -0.010904 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.01132 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.4112 | 213 | -0.010905 | -2.3228
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.011317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6862 | 0 | -0.010908 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.011317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.73674 | 0 | -0.010908 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.011315 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.867 | 165 | -0.01091 | -1.8002
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.011314 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.9121 | 169 | -0.010911 | -1.844
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.011313 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13576 | 12 | -0.010912 | -0.13095
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.011313 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.010912 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.011295 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39532 | 0 | -0.01093 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8394 | 0 | -0.010954 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7707 | 0 | -0.010954 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7752 | 0 | -0.010954 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7695 | 0 | -0.010954 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.0319 | 0 | -0.010954 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.011253 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.87773 | 0 | -0.010972 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.011253 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90024 | 0 | -0.010972 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.51745 | 46 | -0.010976 | -0.5049
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.51745 | 46 | -0.010976 | -0.5049
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.51745 | 46 | -0.010976 | -0.5049
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.61869 | 55 | -0.010976 | -0.60369
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.61869 | 55 | -0.010976 | -0.60369
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.60745 | 54 | -0.010976 | -0.59271
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.011174 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72631 | 0 | -0.011051 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.011174 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.67044 | 0 | -0.011051 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.011174 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72631 | 0 | -0.011051 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.011174 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72631 | 0 | -0.011051 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.013 | 0 | -0.011093 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.97516 | 0 | -0.011093 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.96848 | 0 | -0.011093 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60669 | 0 | -0.011093 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13581 | 0 | -0.011093 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.011021 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.011204 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.010946 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.5473 | 50 | -0.011279 | -0.56396
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.010808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.76521 | 0 | -0.011417 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.010808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72089 | 0 | -0.011417 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.010808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57282 | 0 | -0.011417 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6558 | 0 | -0.011417 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.659 | 0 | -0.011417 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6461 | 0 | -0.011417 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0376 | 0 | -0.011417 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.6372 | 0 | -0.011417 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.010808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.43232 | 0 | -0.011417 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.010806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0838 | 0 | -0.011419 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.010806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0039 | 0 | -0.011419 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.010806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1098 | 0 | -0.011419 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.010806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1022 | 0 | -0.011419 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.010806 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34579 | 0 | -0.011419 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.010806 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32418 | 0 | -0.011419 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.010562 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.7005 | 161 | -0.011663 | -1.8778
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.010562 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.7533 | 166 | -0.011663 | -1.9361
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.010562 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.6194 | 248 | -0.011663 | -2.8925
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.010562 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 5.7669 | 546 | -0.011663 | -6.3681
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.010562 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 6.7914 | 0 | -0.011663 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.010562 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13731 | 13 | -0.011663 | -0.15162
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.01048 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34584 | 0 | -0.011745 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.010455 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7042 | 0 | -0.01177 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.010455 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7042 | 0 | -0.01177 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.010455 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.5615 | 0 | -0.01177 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.01045 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 6.803 | 651 | -0.011775 | -7.6656
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.01045 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.8938 | 564 | -0.011775 | -6.6412
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.01045 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 6.27 | 600 | -0.011775 | -7.0651
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.010394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.47916 | 0 | -0.011831 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.009822 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0902 | 0 | -0.012403 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.009822 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0902 | 0 | -0.012403 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.009822 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1688 | 0 | -0.012403 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.009822 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0755 | 0 | -0.012403 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.009644 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68472 | 0 | -0.012581 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.009644 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.09644 | 0 | -0.012581 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58491 | 0 | -0.012791 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67359 | 0 | -0.012791 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42453 | 0 | -0.012791 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95283 | 0 | -0.012791 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.81132 | 0 | -0.012791 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.83019 | 0 | -0.012791 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4717 | 0 | -0.012791 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16981 | 0 | -0.012791 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.8868 | 0 | -0.012791 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.66038 | 0 | -0.012791 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59434 | 0 | -0.012791 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67925 | 0 | -0.012791 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61132 | 0 | -0.012791 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95283 | 0 | -0.012791 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.9151 | 0 | -0.012791 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.9717 | 0 | -0.012791 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71698 | 0 | -0.012791 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75472 | 0 | -0.012791 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75472 | 0 | -0.012791 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6132 | 0 | -0.012791 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.029502 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.7701 | 60 | 0.29754 | 17.8525
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.029502 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8586 | 63 | 0.29754 | 18.7451
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.029267 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29731 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.029267 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29731 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.029267 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29731 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.008561 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.56503 | 66 | -0.013664 | -0.90184
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.008535 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.8564 | 569 | -0.01369 | -7.7897
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.008535 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.9588 | 581 | -0.01369 | -7.954
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.64022 | 76 | -0.013801 | -1.0489
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.64022 | 76 | -0.013801 | -1.0489
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.88452 | 105 | -0.013801 | -1.4491
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62338 | 74 | -0.013801 | -1.0213
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62338 | 74 | -0.013801 | -1.0213
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.85925 | 102 | -0.013801 | -1.4077
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.008266 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 11.0186 | 0 | -0.013959 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.008266 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 10.9772 | 0 | -0.013959 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.00621 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.6266 | 584 | -0.016015 | -9.3529
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.00621 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.6949 | 595 | -0.016015 | -9.529
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.006208 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.6881 | 433 | -0.016017 | -6.9354
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.006149 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.97154 | 158 | -0.016076 | -2.54
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.006149 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.98384 | 160 | -0.016076 | -2.5722
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.006149 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0761 | 175 | -0.016076 | -2.8133
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.026388 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29443 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.005978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2989 | 50 | -0.016247 | -0.81236
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.005978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2989 | 50 | -0.016247 | -0.81236
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.005978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2989 | 50 | -0.016247 | -0.81236
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.005978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2989 | 50 | -0.016247 | -0.81236
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.005636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.85949 | 152.5 | -0.016589 | -2.5298
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.005636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.84258 | 149.5 | -0.016589 | -2.4801
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.005636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.3109 | 232.6 | -0.016589 | -3.8586
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.005605 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.73986 | 132 | -0.01662 | -2.1939
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.005605 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.75107 | 134 | -0.01662 | -2.2271
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.005605 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8104 | 323 | -0.01662 | -5.3683
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.025808 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.29385 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.025653 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0261 | 0 | 0.29369 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.025653 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0261 | 0 | 0.29369 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.025552 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.3438 | 170 | 0.29359 | 49.9105
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.025552 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.287 | 520 | 0.29359 | 152.6675
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.00507 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.21294 | 42 | -0.017155 | -0.72052
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.00507 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22308 | 44 | -0.017155 | -0.75483
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.00507 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22308 | 44 | -0.017155 | -0.75483
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.00507 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23829 | 47 | -0.017155 | -0.80629
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.02544 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.4128 | 370 | 0.29348 | 108.5874
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.5616 | 0 | 0.29348 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.587 | 0 | 0.29348 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.861 | 0 | 0.29348 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.6379 | 0 | 0.29348 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.6634 | 0 | 0.29348 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.8864 | 0 | 0.29348 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0573 | 160 | 0.2934 | 46.9436
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9558 | 156 | 0.2934 | 45.77
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.9702 | 196 | 0.2934 | 57.5059
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9558 | 156 | 0.2934 | 45.77
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9812 | 157 | 0.2934 | 46.0634
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.0209 | 198 | 0.2934 | 58.0927
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.025291 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.8968 | 0 | 0.29333 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.025291 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.0132 | 0 | 0.29333 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.025291 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.2357 | 0 | 0.29333 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.004854 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.5047 | 310 | -0.017371 | -5.3851
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.004854 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.0047 | 413 | -0.017371 | -7.1743
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.02522 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.0728 | 558 | 0.29326 | 163.6388
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.02522 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.6024 | 579 | 0.29326 | 169.7972
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.02522 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 20.3778 | 808 | 0.29326 | 236.9536
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.38038 | 0 | -0.01741 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.39002 | 0 | -0.01741 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.38038 | 0 | -0.01741 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3852 | 0 | -0.01741 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3775 | 0 | -0.01741 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12037 | 0 | -0.01741 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.22149 | 0 | -0.01741 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13482 | 0 | -0.01741 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.20993 | 0 | -0.01741 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.35631 | 0 | -0.01741 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23466 | 49 | -0.017436 | -0.85437
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22029 | 46 | -0.017436 | -0.80206
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22029 | 46 | -0.017436 | -0.80206
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22508 | 47 | -0.017436 | -0.8195
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.004789 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.73751 | 154 | -0.017436 | -2.6852
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.004789 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.70877 | 148 | -0.017436 | -2.5806
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22987 | 48 | -0.017436 | -0.83694
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22987 | 48 | -0.017436 | -0.83694
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.004714 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.22627 | 0 | -0.017511 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.004596 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.036768 | 0 | -0.017629 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.004596 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.036768 | 0 | -0.017629 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.024925 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.8454 | 395 | 0.29296 | 115.7209
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.024925 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.8424 | 435 | 0.29296 | 127.4395
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.024872 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.8193 | 435 | 0.29291 | 127.4165
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.024818 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.9606 | 79 | 0.29286 | 23.1357
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.024818 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.6307 | 106 | 0.29286 | 31.0429
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.024818 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.6234 | 146 | 0.29286 | 42.7572
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.024818 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.8862 | 76 | 0.29286 | 22.2572
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12146 | 0 | -0.017887 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.030366 | 0 | -0.017887 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16918 | 0 | -0.017887 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06507 | 0 | -0.017887 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.030366 | 0 | -0.017887 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06507 | 0 | -0.017887 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16918 | 0 | -0.017887 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16918 | 0 | -0.017887 | 0
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.024713 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.49426 | 20 | 0.29275 | 5.855
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.024713 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.61782 | 25 | 0.29275 | 7.3188
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.024713 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.0132 | 41 | 0.29275 | 12.0028
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.024707 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.98828 | 40 | 0.29275 | 11.7099
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.004265 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.03412 | 0 | -0.01796 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.004234 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06351 | 0 | -0.017991 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.004234 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.097382 | 0 | -0.017991 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.004093 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.29879 | 0 | -0.018132 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.003989 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57442 | 144 | -0.018236 | -2.626
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.003989 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.74993 | 188 | -0.018236 | -3.4284
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.003907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18636 | 47.7 | -0.018318 | -0.87378
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.003907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14573 | 37.3 | -0.018318 | -0.68327
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.003907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.17972 | 46 | -0.018318 | -0.84264
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.003907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18754 | 48 | -0.018318 | -0.87927
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.024229 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.4009 | 388 | 0.29227 | 113.4002
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.024229 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.4779 | 515 | 0.29227 | 150.5182
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.003773 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.045276 | 0 | -0.018452 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003753 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0090072 | 0 | -0.018472 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003753 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0090072 | 0 | -0.018472 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8807 | 161 | 0.29214 | 47.0351
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9531 | 164 | 0.29214 | 47.9115
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9531 | 164 | 0.29214 | 47.9115
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.9791 | 414 | 0.29214 | 120.9474
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9048 | 162 | 0.29214 | 47.3272
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8807 | 161 | 0.29214 | 47.0351
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.929 | 163 | 0.29214 | 47.6194
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.8585 | 409 | 0.29214 | 119.4867
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.003718 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.081796 | 22 | -0.018507 | -0.40716
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003718 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.040898 | 11 | -0.018507 | -0.20358
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003718 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.040898 | 11 | -0.018507 | -0.20358
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.024079 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.29212 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.024079 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.29212 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.024015 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.7017 | 112.5 | 0.29205 | 32.8561
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.003574 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.80022 | 223.9 | -0.018651 | -4.176
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.003574 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.80415 | 225 | -0.018651 | -4.1965
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.003574 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.80272 | 224.6 | -0.018651 | -4.1891
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.003574 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.81023 | 226.7 | -0.018651 | -4.2282
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.003315 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.47073 | 142 | -0.01891 | -2.6852
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.003315 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48068 | 145 | -0.01891 | -2.742
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.003315 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.50057 | 151 | -0.01891 | -2.8554
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.003315 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.96135 | 290 | -0.01891 | -5.484
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003306 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0079344 | 0 | -0.018919 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003306 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0079344 | 0 | -0.018919 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.003306 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0092568 | 0 | -0.018919 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.52077 | 0 | -0.018929 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.50429 | 0 | -0.018929 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.3296 | 0 | -0.018929 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47792 | 0 | -0.018929 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.48451 | 0 | -0.018929 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.41859 | 0 | -0.018929 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.003296 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.039552 | 0 | -0.018929 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.023645 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.7901 | 118 | 0.29168 | 34.4188
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.023645 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.7192 | 115 | 0.29168 | 33.5437
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.023645 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.1466 | 556 | 0.29168 | 162.1765
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08025 | 25 | -0.019015 | -0.47538
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08025 | 25 | -0.019015 | -0.47538
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08025 | 25 | -0.019015 | -0.47538
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05136 | 16 | -0.019015 | -0.30424
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08025 | 25 | -0.019015 | -0.47538
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08025 | 25 | -0.019015 | -0.47538
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08025 | 25 | -0.019015 | -0.47538
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.04815 | 15 | -0.019015 | -0.28523
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.003103 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.9518 | 629 | -0.019122 | -12.0278
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.003092 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0389 | 336 | -0.019133 | -6.4287
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.003092 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55656 | 180 | -0.019133 | -3.444
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.00309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.45825 | 0 | -0.019135 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.00309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.45917 | 0 | -0.019135 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.00309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47277 | 0 | -0.019135 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.003086 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55548 | 180 | -0.019139 | -3.4451
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.003052 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0194 | 334 | -0.019173 | -6.4038
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.003052 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0377 | 340 | -0.019173 | -6.5189
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.003052 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54936 | 180 | -0.019173 | -3.4512
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.003052 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54936 | 180 | -0.019173 | -3.4512
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4482 | 147 | -0.019176 | -2.8189
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42076 | 138 | -0.019176 | -2.6463
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42686 | 140 | -0.019176 | -2.6847
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4482 | 147 | -0.019176 | -2.8189
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55492 | 182 | -0.019176 | -3.4901
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.6037 | 198 | -0.019176 | -3.7969
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.003028 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0757 | 0 | -0.019197 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.003028 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0757 | 0 | -0.019197 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.003025 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.11495 | 0 | -0.0192 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.003002 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.11408 | 0 | -0.019223 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.002929 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.017574 | 0 | -0.019296 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.002896 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.083984 | 0 | -0.019329 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.002877 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011508 | 0 | -0.019348 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.26292 | 94 | -0.019428 | -1.8262
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11468 | 41 | -0.019428 | -0.79656
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10629 | 38 | -0.019428 | -0.73827
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.053143 | 19 | -0.019428 | -0.36914
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.26292 | 94 | -0.019428 | -1.8262
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10069 | 36 | -0.019428 | -0.69941
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.12027 | 43 | -0.019428 | -0.83541
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.061534 | 22 | -0.019428 | -0.42742
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.41396 | 148 | -0.019428 | -2.8754
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13985 | 50 | -0.019428 | -0.97141
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15383 | 55 | -0.019428 | -1.0685
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13985 | 50 | -0.019428 | -0.97141
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.002716 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.019509 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.002716 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.10321 | 38 | -0.019509 | -0.74135
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.002716 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.052419 | 19.3 | -0.019509 | -0.37653
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.002716 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.04074 | 15 | -0.019509 | -0.29264
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.002716 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12765 | 47 | -0.019509 | -0.91693
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.00251 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36144 | 144 | -0.019715 | -2.839
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.00251 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36144 | 144 | -0.019715 | -2.839
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.00251 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42921 | 171 | -0.019715 | -3.3713
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.002509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.51936 | 207 | -0.019716 | -4.0812
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.002509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.5437 | 216.7 | -0.019716 | -4.2725
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.002509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.60718 | 242 | -0.019716 | -4.7713
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.002308 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.2602 | 546 | -0.019917 | -10.8748
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.002308 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.731 | 750 | -0.019917 | -14.9379
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.002167 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31747 | 146.5 | -0.020058 | -2.9385
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.002167 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.3205 | 147.9 | -0.020058 | -2.9666
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.002167 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.37489 | 173 | -0.020058 | -3.4701
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.022533 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.6884 | 785 | 0.29057 | 228.0994
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.022533 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.9137 | 795 | 0.29057 | 231.0051
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.022533 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.5757 | 780 | 0.29057 | 226.6465
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.002149 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33309 | 155 | -0.020076 | -3.1118
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.002149 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36533 | 170 | -0.020076 | -3.413
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.002149 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33309 | 155 | -0.020076 | -3.1118
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.002047 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.020178 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.002047 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.020178 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.002047 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.020178 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.02232 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.3034 | 0 | 0.29036 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.02232 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.9016 | 0 | 0.29036 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.02232 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.2364 | 0 | 0.29036 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.02232 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.9057 | 0 | 0.29036 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.001915 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.02031 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.001857 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.064995 | 0 | -0.020368 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.001857 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.063138 | 0 | -0.020368 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.001857 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.064995 | 0 | -0.020368 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.022139 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.29018 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.022119 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.1059 | 50 | 0.29016 | 14.5079
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.001732 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.020493 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.022081 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.0187 | 182 | 0.29012 | 52.8019
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.022081 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.6872 | 484 | 0.29012 | 140.4183
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.001701 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.72122 | 424 | -0.020524 | -8.7023
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.001701 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.72293 | 425 | -0.020524 | -8.7228
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.00162 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.66744 | 412 | -0.020605 | -8.4893
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.00162 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.648 | 400 | -0.020605 | -8.2421
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.001617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.33795 | 209 | -0.020608 | -4.3071
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.001617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34927 | 216 | -0.020608 | -4.4514
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.001617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074382 | 46 | -0.020608 | -0.94798
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.001617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.075999 | 47 | -0.020608 | -0.96858
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.001617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074382 | 46 | -0.020608 | -0.94798
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.001617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074382 | 46 | -0.020608 | -0.94798
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.021993 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7593 | 216.4 | 0.29003 | 62.763
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.021993 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7527 | 216.1 | 0.29003 | 62.676
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.001564 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.61934 | 396 | -0.020661 | -8.1818
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.001456 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.59259 | 407 | -0.020769 | -8.4531
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.021413 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1969 | 196 | 0.28945 | 56.7327
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.021413 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3768 | 111 | 0.28945 | 32.1292
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.021412 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.1817 | 242 | 0.28945 | 70.0472
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.000988 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.057304 | 58 | -0.021237 | -1.2318
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.000988 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.087932 | 89 | -0.021237 | -1.8901
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.000988 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.043472 | 44 | -0.021237 | -0.93444
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.000988 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.043472 | 44 | -0.021237 | -0.93444
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.000988 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.042484 | 43 | -0.021237 | -0.9132
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.000988 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.04446 | 45 | -0.021237 | -0.95567
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.021193 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.7472 | 224 | 0.28923 | 64.7881
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.02109 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0739 | 288 | 0.28913 | 83.2693
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.02109 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1002 | 147 | 0.28913 | 42.502
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.02109 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1002 | 147 | 0.28913 | 42.502
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070794 | 114 | -0.021604 | -2.4629
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13786 | 222 | -0.021604 | -4.7961
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11426 | 184 | -0.021604 | -3.9752
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1391 | 224 | -0.021604 | -4.8393
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.071415 | 115 | -0.021604 | -2.4845
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.020852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6708 | 224 | 0.28889 | 64.7117
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.020852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7126 | 226 | 0.28889 | 65.2895
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.020852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4206 | 212 | 0.28889 | 61.245
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.020852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.3998 | 211 | 0.28889 | 60.9561
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.000106 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001272 | 0 | -0.022119 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.000106 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001166 | 0 | -0.022119 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000106 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001272 | 0 | -0.022119 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.022225 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.022225 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.022225 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.022225 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.022225 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.022225 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.022225 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.022225 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.020308 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0767 | 151.5 | 0.28835 | 43.6846
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.020308 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0929 | 152.3 | 0.28835 | 43.9153
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.020308 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.6047 | 177.5 | 0.28835 | 51.1817
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.020234 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0493 | 150.7 | 0.28827 | 43.4428
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.020234 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0553 | 151 | 0.28827 | 43.5293
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.020234 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5895 | 177.4 | 0.28827 | 51.1397
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.019873 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.2219 | 615 | 0.28791 | 177.0661
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.019873 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.6655 | 587 | 0.28791 | 169.0046
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.018993 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28703 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.001865 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.02409 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.017827 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.7429 | 827 | 0.28587 | 236.4115
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.017827 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.6003 | 819 | 0.28587 | 234.1246
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.017091 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.6128 | 855 | 0.28513 | 243.7865
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.017091 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.6128 | 855 | 0.28513 | 243.7865
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.017091 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.603 | 152.3 | 0.28513 | 43.4254
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.017091 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.6149 | 153 | 0.28513 | 43.625
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.017015 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.0418 | 120 | 0.28505 | 34.2065
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.017001 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.30602 | 18 | 0.28504 | 5.1307
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.017001 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.30602 | 18 | 0.28504 | 5.1307
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.017001 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.64604 | 38 | 0.28504 | 10.8315
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.004128 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.4128 | 100 | -0.026353 | -2.6353
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.004128 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.4128 | 100 | -0.026353 | -2.6353
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.004128 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.026353 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.004128 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.026353 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.004128 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.026353 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.004128 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.026353 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.004132 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.026357 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004226 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.076068 | 0 | -0.026451 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004226 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.076068 | 0 | -0.026451 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.015834 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.31668 | 20 | 0.28387 | 5.6775
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.015834 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.31668 | 20 | 0.28387 | 5.6775
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.015834 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.31668 | 20 | 0.28387 | 5.6775
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.015834 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.26918 | 17 | 0.28387 | 4.8258
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.015384 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5845 | 168 | 0.28342 | 47.6151
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.015384 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3846 | 90 | 0.28342 | 25.5081
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.015254 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0626 | 463 | 0.28329 | 131.1649
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.015239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28328 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.015239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28328 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.015239 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.25906 | 17 | 0.28328 | 4.8157
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.015239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28328 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.015239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28328 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.015227 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.48726 | 0 | 0.28327 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.015188 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.72902 | 48 | 0.28323 | 13.5949
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.015188 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.69865 | 46 | 0.28323 | 13.0285
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.015188 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.5947 | 105 | 0.28323 | 29.7389
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.014917 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28296 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.014917 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 11.7397 | 787 | 0.28296 | 222.6867
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.014698 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2664 | 0 | 0.28274 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.014698 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2929 | 0 | 0.28274 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.014698 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2929 | 0 | 0.28274 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.014698 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.5852 | 0 | 0.28274 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.014334 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0034 | 70 | 0.28237 | 19.7661
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.014334 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.98905 | 69 | 0.28237 | 19.4838
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.014334 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.98905 | 69 | 0.28237 | 19.4838
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.014334 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.97471 | 68 | 0.28237 | 19.2014
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.014331 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1141 | 217.3 | 0.28237 | 61.3591
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.014331 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.9379 | 205 | 0.28237 | 57.8859
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.014331 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9038 | 272.4 | 0.28237 | 76.9177
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.014167 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28221 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.014167 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28221 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.006234 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17455 | 0 | -0.028459 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.006234 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18079 | 0 | -0.028459 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.013614 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4716 | 255 | 0.28165 | 71.8216
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.013614 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.0285 | 149 | 0.28165 | 41.9664
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.013614 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.0829 | 153 | 0.28165 | 43.093
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.006908 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.9152 | 422 | -0.029133 | -12.2942
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.00736 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13248 | 0 | -0.029585 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.00736 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13248 | 0 | -0.029585 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.00736 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1104 | 0 | -0.029585 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.013005 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.19507 | 0 | 0.28104 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.013005 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.19507 | 0 | 0.28104 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.012869 | north | 3 | N | N | Nnorth | Nnorth | 1 | 14.8894 | 0 | 0.28091 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.012869 | north | 3 | N | N | Nnorth | Nnorth | 1 | 14.9023 | 0 | 0.28091 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.012594 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8891 | 150 | 0.28063 | 42.095
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.012594 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0075 | 80 | 0.28063 | 22.4507
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.008099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.19438 | 24 | -0.030324 | -0.72778
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.008099 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.19438 | 24 | -0.030324 | -0.72778
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.008099 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.18628 | 23 | -0.030324 | -0.69746
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.010469 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.14343 | 0 | -0.032694 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.008485 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.10182 | 0 | 0.27652 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.008485 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.10182 | 0 | 0.27652 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.007647 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.55823 | 73 | 0.27569 | 20.1251
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.007647 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.90999 | 119 | 0.27569 | 32.8067
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.007647 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.5676 | 205 | 0.27569 | 56.5157
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.007647 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.77999 | 102 | 0.27569 | 28.12
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.007647 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.73411 | 96 | 0.27569 | 26.4659
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0621 | 100 | 0.26866 | 26.866
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.26804 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.26804 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.048206 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.070431 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.032089 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.9253 | 60 | 0.23595 | 14.157
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.053081 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.31849 | 0 | -0.075306 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.074039 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.4433 | 0 | -0.096264 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.074039 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.851 | 0 | -0.096264 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.074039 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.096264 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.079135 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.1889 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.11692 | west | 4 | Y | N | Ywest | Nwest | 1 | -75.9629 | 649.7 | 0.15112 | 98.1823
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.19857 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.7861 | 150 | 0.069465 | 10.4198
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.20609 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.3655 | 60 | 0.061947 | 3.7168
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.22424 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.043796 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.2344 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.9892 | 209 | 0.033641 | 7.0311
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.2344 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.6513 | 126.5 | 0.033641 | 4.2556
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.2344 | west | 6 | Y | N | Ywest | Nwest | 1 | -58.3651 | 249 | 0.033641 | 8.3767
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.2344 | west | 6 | Y | N | Ywest | Nwest | 1 | -46.1764 | 197 | 0.033641 | 6.6274
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.23853 | west | 6 | Y | N | Ywest | Nwest | 1 | -35.7801 | 150 | 0.029505 | 4.4258
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.25247 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.2071 | 84 | 0.015573 | 1.3082
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.25291 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.3473 | 76.5 | 0.015133 | 1.1577
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.25425 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.3402 | 80 | 0.013787 | 1.103
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.25954 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.9313 | 150 | 0.0084974 | 1.2746
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.25954 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.9313 | 150 | 0.0084974 | 1.2746
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.25968 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7746 | 80 | 0.0083574 | 0.66859
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.25971 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7771 | 80 | 0.0083254 | 0.66603
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.25993 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.4947 | 75 | 0.0081104 | 0.60828
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.25993 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7943 | 80 | 0.0081104 | 0.64883
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.25993 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.3972 | 40 | 0.0081104 | 0.32442
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.26097 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.8773 | 80 | 0.0070734 | 0.56587
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.26097 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.8773 | 80 | 0.0070734 | 0.56587
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.26276 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.0715 | 84 | 0.0052834 | 0.44381
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.26516 | west | #N/A | N | N | Nwest | Nwest | 1 | -1.2728 | 0 | 0.0028814 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.26589 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.9125 | 112.5 | 0.0021504 | 0.24192
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.26589 | west | 6 | Y | N | Ywest | Nwest | 1 | -39.7504 | 149.5 | 0.0021504 | 0.32149
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.26589 | west | 6 | Y | N | Ywest | Nwest | 1 | -49.4554 | 186 | 0.0021504 | 0.39998
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.26589 | west | 6 | Y | N | Ywest | Nwest | 1 | -57.0332 | 214.5 | 0.0021504 | 0.46127
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.26828 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.5596 | 99 | -0.00023957 | -0.023718
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.26828 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.365 | 61 | -0.00023957 | -0.014614
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.26828 | west | 7 | N | N | Nwest | Nwest | 1 | -6.707 | 0 | -0.00023957 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.26828 | west | 7 | N | N | Nwest | Nwest | 1 | -12.2604 | 0 | -0.00023957 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.26828 | west | 7 | N | N | Nwest | Nwest | 1 | -12.2604 | 0 | -0.00023957 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.26853 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.8629 | 141 | -0.00049157 | -0.069312
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.26853 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.2237 | 120 | -0.00049157 | -0.058989
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.26859 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.2884 | 150 | -0.00054957 | -0.082436
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.26963 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.7795 | 6.6 | -0.0015866 | -0.010471
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.26963 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.2482 | 34.3 | -0.0015866 | -0.054419
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.27089 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.0661 | 63 | -0.0028506 | -0.17959
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.27162 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.8914 | 180 | -0.0035796 | -0.64432
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.27162 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.8914 | 180 | -0.0035796 | -0.64432
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.27176 | west | 6 | Y | N | Ywest | Nwest | 1 | -61.1467 | 225 | -0.0037236 | -0.8378
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.27349 | west | 8 | N | N | Nwest | Nwest | 1 | -7.056 | 0 | -0.0054496 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.27364 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.8367 | 120 | -0.0055996 | -0.67195
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.27429 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.9149 | 120 | -0.0062516 | -0.75019
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.27471 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.9316 | 149 | -0.0066696 | -0.99377
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.27471 | west | 6 | Y | N | Ywest | Nwest | 1 | -41.2068 | 150 | -0.0066726 | -1.0009
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.27471 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.7459 | 101 | -0.0066726 | -0.67393
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.2749 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.6216 | 35 | -0.0068626 | -0.24019
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.2749 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2471 | 30 | -0.0068626 | -0.20588
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.1543 | 66 | -0.0070256 | -0.46369
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -17.8792 | 65 | -0.0070256 | -0.45666
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.4294 | 67 | -0.0070256 | -0.47071
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.4294 | 67 | -0.0070256 | -0.47071
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.4294 | 67 | -0.0070256 | -0.47071
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.27507 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0070256 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.27507 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0070256 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.27614 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.7525 | 100.5 | -0.0081046 | -0.81451
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.2763 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.0256 | 58 | -0.0082636 | -0.47929
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.27652 | west | 6 | Y | N | Ywest | Nwest | 1 | -59.2306 | 214.2 | -0.0084806 | -1.8165
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.3381 | 66 | -0.0098106 | -0.6475
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 1 | -19.1716 | 69 | -0.0098106 | -0.67693
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 1 | -19.1716 | 69 | -0.0098106 | -0.67693
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.616 | 67 | -0.0098106 | -0.65731
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.616 | 67 | -0.0098106 | -0.65731
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.0602 | 65 | -0.0098106 | -0.63769
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 1 | -57.9889 | 208.2 | -0.010486 | -2.1831
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 1 | -39.5784 | 142.1 | -0.010486 | -1.49
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 1 | -36.8767 | 132.4 | -0.010486 | -1.3883
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 1 | -37.8794 | 136 | -0.010486 | -1.426
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 1 | -40.9432 | 147 | -0.010486 | -1.5414
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 1 | -58.4903 | 210 | -0.010486 | -2.202
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 1 | -19.4991 | 70 | -0.010519 | -0.7363
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 1 | -19.4991 | 70 | -0.010519 | -0.7363
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 1 | -25.8502 | 92.8 | -0.010519 | -0.97612
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 1 | -22.2846 | 80 | -0.010519 | -0.84149
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 1 | -22.2846 | 80 | -0.010519 | -0.84149
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 1 | -32.0342 | 115 | -0.010519 | -1.2096
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.28097 | west | 8 | N | N | Nwest | Nwest | 1 | -19.6678 | 0 | -0.012929 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.28097 | west | 8 | N | N | Nwest | Nwest | 1 | -20.6231 | 0 | -0.012929 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.28097 | west | 8 | N | N | Nwest | Nwest | 1 | -19.7801 | 0 | -0.012929 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.28162 | west | 6 | Y | N | Ywest | Nwest | 1 | -42.243 | 150 | -0.013581 | -2.0371
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.28162 | west | 6 | Y | N | Ywest | Nwest | 1 | -61.9564 | 220 | -0.013581 | -2.9877
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.28162 | west | 6 | Y | N | Ywest | Nwest | 1 | -56.324 | 200 | -0.013581 | -2.7161
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.28162 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.3295 | 121.9 | -0.013581 | -1.6555
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.28626 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.5219 | 169.5 | -0.018226 | -3.0892
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.30173 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.2078 | 120 | -0.033693 | -4.0431
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.30173 | west | 6 | Y | N | Ywest | Nwest | 1 | -70.3036 | 233 | -0.033693 | -7.8504
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.30173 | west | 6 | Y | N | Ywest | Nwest | 1 | -51.3548 | 170.2 | -0.033693 | -5.7345
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.3045 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.0629 | 125 | -0.036464 | -4.5579
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.3045 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.0629 | 125 | -0.036464 | -4.5579
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8351 | 37.5 | -0.047564 | -1.7836
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 1 | -33.9273 | 107.5 | -0.047564 | -5.1131
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 1 | -42.6064 | 135 | -0.047564 | -6.4211
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.5568 | 119 | -0.047564 | -5.6601
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 1 | -33.1383 | 105 | -0.047564 | -4.9942
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.406 | 80.5 | -0.047564 | -3.8289
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.46966 | west | 6 | Y | N | Ywest | Nwest | 1 | -187.8628 | 400 | -0.20162 | -80.647
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.47077 | west | 6 | Y | N | Ywest | Nwest | 1 | -111.1027 | 236 | -0.20273 | -47.8454
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.57691 | west | 6 | Y | N | Ywest | Nwest | 1 | -95.19 | 165 | -0.30887 | -50.9635

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: GRHAMSES - COKFIELD 345kV [1430 - 1442] C: GRHAMSES - LONGCREK 345kV [1430 - 1435] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.57691 | west | 6 | Y | N | Ywest | Nwest | 1 | -95.19 | 0 | -0.30887 | 0 | 0 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.47077 | west | 6 | Y | N | Ywest | Nwest | 1 | -111.1027 | 0 | -0.20273 | 0 | 0 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.46966 | west | 6 | Y | N | Ywest | Nwest | 1 | -187.8628 | 0 | -0.20162 | 0 | 0 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8351 | 0 | -0.047564 | 0 | 0 | 0 | Weighted Shift Factors
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 1 | -33.9273 | 0 | -0.047564 | 0 | 0 | 0 | north | 0.022225
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 1 | -42.6064 | 0 | -0.047564 | 0 | 0 | 0 | west | -0.26804
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.5568 | 0 | -0.047564 | 0 | 0 | 0 |  | 0.29026
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 1 | -33.1383 | 0 | -0.047564 | 0 | 0 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.3156 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.406 | 0 | -0.047564 | 0 | 0 | 0 | Line Rating | 1340
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.3045 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.0629 | 0 | -0.036464 | 0 | 0 | 0 | Conc Gen | 2615.5
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.3045 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.0629 | 0 | -0.036464 | 0 | 0 | 0 | Weighted Imp. | 87.5893
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.30173 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.2078 | 0 | -0.033693 | 0 | 0 | 0 | PTDF | 0.033489
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.30173 | west | 6 | Y | N | Ywest | Nwest | 1 | -70.3036 | 0 | -0.033693 | 0 | 0 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.30173 | west | 6 | Y | N | Ywest | Nwest | 1 | -51.3548 | 0 | -0.033693 | 0 | 0 | 0 | Concentration | 0.11537
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.28626 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.5219 | 0 | -0.018226 | 0 | 0 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.28162 | west | 6 | Y | N | Ywest | Nwest | 1 | -42.243 | 0 | -0.013581 | 0 | 0 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.28162 | west | 6 | Y | N | Ywest | Nwest | 1 | -61.9564 | 0 | -0.013581 | 0 | 0 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.28162 | west | 6 | Y | N | Ywest | Nwest | 1 | -56.324 | 0 | -0.013581 | 0 | 0 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.28162 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.3295 | 0 | -0.013581 | 0 | 0 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.28097 | west | 8 | N | N | Nwest | Nwest | 1 | -19.6678 | 0 | -0.012929 | 0 | 0 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.28097 | west | 8 | N | N | Nwest | Nwest | 1 | -20.6231 | 0 | -0.012929 | 0 | 0 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.28097 | west | 8 | N | N | Nwest | Nwest | 1 | -19.7801 | 0 | -0.012929 | 0 | 0 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 1 | -19.4991 | 70 | -0.010519 | -0.7363 | 70 | 0.7363
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 1 | -19.4991 | 70 | -0.010519 | -0.7363 | 140 | 1.4726
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 1 | -25.8502 | 92.8 | -0.010519 | -0.97612 | 232.8 | 2.4487
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 1 | -22.2846 | 80 | -0.010519 | -0.84149 | 312.8 | 3.2902
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 1 | -22.2846 | 80 | -0.010519 | -0.84149 | 392.8 | 4.1317
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.27856 | west | 9 | Y | Y | Ywest | Ywest | 1 | -32.0342 | 115 | -0.010519 | -1.2096 | 507.8 | 5.3413
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 1 | -57.9889 | 208.2 | -0.010486 | -2.1831 | 716 | 7.5244
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 1 | -39.5784 | 142.1 | -0.010486 | -1.49 | 858.1 | 9.0144
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 1 | -36.8767 | 132.4 | -0.010486 | -1.3883 | 990.5 | 10.4027
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 1 | -37.8794 | 136 | -0.010486 | -1.426 | 1126.5 | 11.8288
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 1 | -40.9432 | 147 | -0.010486 | -1.5414 | 1273.5 | 13.3701
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.27853 | west | 9 | Y | Y | Ywest | Ywest | 1 | -58.4903 | 210 | -0.010486 | -2.202 | 1483.5 | 15.5721
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.3381 | 66 | -0.0098106 | -0.6475 | 1549.5 | 16.2196
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 1 | -19.1716 | 69 | -0.0098106 | -0.67693 | 1618.5 | 16.8965
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 1 | -19.1716 | 69 | -0.0098106 | -0.67693 | 1687.5 | 17.5735
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.616 | 67 | -0.0098106 | -0.65731 | 1754.5 | 18.2308
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.616 | 67 | -0.0098106 | -0.65731 | 1821.5 | 18.8881
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.27785 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.0602 | 65 | -0.0098106 | -0.63769 | 1886.5 | 19.5258
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.27652 | west | 6 | Y | N | Ywest | Nwest | 1 | -59.2306 | 0 | -0.0084806 | 0 | 1886.5 | 19.5258
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.2763 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.0256 | 0 | -0.0082636 | 0 | 1886.5 | 19.5258
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.27614 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.7525 | 0 | -0.0081046 | 0 | 1886.5 | 19.5258
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.1543 | 66 | -0.0070256 | -0.46369 | 1952.5 | 19.9895
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -17.8792 | 65 | -0.0070256 | -0.45666 | 2017.5 | 20.4461
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.4294 | 67 | -0.0070256 | -0.47071 | 2084.5 | 20.9168
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.4294 | 67 | -0.0070256 | -0.47071 | 2151.5 | 21.3875
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.27507 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.4294 | 67 | -0.0070256 | -0.47071 | 2218.5 | 21.8583
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.27507 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0070256 | 0 | 2218.5 | 21.8583
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.27507 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0070256 | 0 | 2218.5 | 21.8583
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.2749 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.6216 | 0 | -0.0068626 | 0 | 2218.5 | 21.8583
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.2749 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2471 | 0 | -0.0068626 | 0 | 2218.5 | 21.8583
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.27471 | west | 6 | Y | N | Ywest | Nwest | 1 | -41.2068 | 0 | -0.0066726 | 0 | 2218.5 | 21.8583
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.27471 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.7459 | 0 | -0.0066726 | 0 | 2218.5 | 21.8583
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.27471 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.9316 | 0 | -0.0066696 | 0 | 2218.5 | 21.8583
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.27429 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.9149 | 0 | -0.0062516 | 0 | 2218.5 | 21.8583
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.27364 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.8367 | 0 | -0.0055996 | 0 | 2218.5 | 21.8583
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.27349 | west | 8 | N | N | Nwest | Nwest | 1 | -7.056 | 0 | -0.0054496 | 0 | 2218.5 | 21.8583
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.27176 | west | 6 | Y | N | Ywest | Nwest | 1 | -61.1467 | 0 | -0.0037236 | 0 | 2218.5 | 21.8583
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.27162 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.8914 | 0 | -0.0035796 | 0 | 2218.5 | 21.8583
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.27162 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.8914 | 0 | -0.0035796 | 0 | 2218.5 | 21.8583
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.27089 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.0661 | 0 | -0.0028506 | 0 | 2218.5 | 21.8583
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.26963 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.7795 | 0 | -0.0015866 | 0 | 2218.5 | 21.8583
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.26963 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.2482 | 0 | -0.0015866 | 0 | 2218.5 | 21.8583
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.26859 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.2884 | 0 | -0.00054957 | 0 | 2218.5 | 21.8583
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.26853 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.8629 | 0 | -0.00049157 | 0 | 2218.5 | 21.8583
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.26853 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.2237 | 0 | -0.00049157 | 0 | 2218.5 | 21.8583
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.26828 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.5596 | 0 | -0.00023957 | 0 | 2218.5 | 21.8583
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.26828 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.365 | 0 | -0.00023957 | 0 | 2218.5 | 21.8583
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.26828 | west | 7 | N | N | Nwest | Nwest | 1 | -6.707 | 0 | -0.00023957 | 0 | 2218.5 | 21.8583
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.26828 | west | 7 | N | N | Nwest | Nwest | 1 | -12.2604 | 0 | -0.00023957 | 0 | 2218.5 | 21.8583
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.26828 | west | 7 | N | N | Nwest | Nwest | 1 | -12.2604 | 0 | -0.00023957 | 0 | 2218.5 | 21.8583
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.26589 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.9125 | 0 | 0.0021504 | 0 | 2218.5 | 21.8583
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.26589 | west | 6 | Y | N | Ywest | Nwest | 1 | -39.7504 | 0 | 0.0021504 | 0 | 2218.5 | 21.8583
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.26589 | west | 6 | Y | N | Ywest | Nwest | 1 | -49.4554 | 0 | 0.0021504 | 0 | 2218.5 | 21.8583
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.26589 | west | 6 | Y | N | Ywest | Nwest | 1 | -57.0332 | 0 | 0.0021504 | 0 | 2218.5 | 21.8583
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.26516 | west | #N/A | N | N | Nwest | Nwest | 1 | -1.2728 | 0 | 0.0028814 | 0 | 2218.5 | 21.8583
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.26276 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.0715 | 0 | 0.0052834 | 0 | 2218.5 | 21.8583
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.26097 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.8773 | 0 | 0.0070734 | 0 | 2218.5 | 21.8583
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.26097 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.8773 | 0 | 0.0070734 | 0 | 2218.5 | 21.8583
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.25993 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.4947 | 0 | 0.0081104 | 0 | 2218.5 | 21.8583
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.25993 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7943 | 0 | 0.0081104 | 0 | 2218.5 | 21.8583
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.25993 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.3972 | 0 | 0.0081104 | 0 | 2218.5 | 21.8583
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.25971 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7771 | 0 | 0.0083254 | 0 | 2218.5 | 21.8583
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.25968 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7746 | 0 | 0.0083574 | 0 | 2218.5 | 21.8583
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.25954 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.9313 | 0 | 0.0084974 | 0 | 2218.5 | 21.8583
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.25954 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.9313 | 0 | 0.0084974 | 0 | 2218.5 | 21.8583
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.25425 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.3402 | 0 | 0.013787 | 0 | 2218.5 | 21.8583
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.25291 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.3473 | 0 | 0.015133 | 0 | 2218.5 | 21.8583
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.25247 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.2071 | 0 | 0.015573 | 0 | 2218.5 | 21.8583
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.23853 | west | 6 | Y | N | Ywest | Nwest | 1 | -35.7801 | 0 | 0.029505 | 0 | 2218.5 | 21.8583
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.2344 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.9892 | 0 | 0.033641 | 0 | 2218.5 | 21.8583
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.2344 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.6513 | 0 | 0.033641 | 0 | 2218.5 | 21.8583
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.2344 | west | 6 | Y | N | Ywest | Nwest | 1 | -58.3651 | 0 | 0.033641 | 0 | 2218.5 | 21.8583
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.2344 | west | 6 | Y | N | Ywest | Nwest | 1 | -46.1764 | 0 | 0.033641 | 0 | 2218.5 | 21.8583
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.22424 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.043796 | 0 | 2218.5 | 21.8583
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.20609 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.3655 | 0 | 0.061947 | 0 | 2218.5 | 21.8583
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.19857 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.7861 | 0 | 0.069465 | 0 | 2218.5 | 21.8583
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.11692 | west | 4 | Y | N | Ywest | Nwest | 1 | -75.9629 | 0 | 0.15112 | 0 | 2218.5 | 21.8583
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.079135 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.1889 | 0 | 2218.5 | 21.8583
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.074039 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.4433 | 0 | -0.096264 | 0 | 2218.5 | 21.8583
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.074039 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.851 | 0 | -0.096264 | 0 | 2218.5 | 21.8583
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.074039 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.096264 | 0 | 2218.5 | 21.8583
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.053081 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.31849 | 0 | -0.075306 | 0 | 2218.5 | 21.8583
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.032089 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.9253 | 0 | 0.23595 | 0 | 2218.5 | 21.8583
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.048206 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.070431 | 0 | 2218.5 | 21.8583
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.26804 | 0 | 2218.5 | 21.8583
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.26804 | 0 | 2218.5 | 21.8583
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0621 | 0 | 0.26866 | 0 | 2218.5 | 21.8583
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.007647 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.55823 | 73 | 0.27569 | 20.1251 | 2291.5 | 1.7331
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.007647 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.90999 | 119 | 0.27569 | 32.8067 | 2410.5 | 31.0735
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.007647 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.5676 | 205 | 0.27569 | 56.5157 | 2615.5 | 87.5893
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.007647 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.77999 | 102 | 0.27569 | 28.12
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.007647 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.73411 | 96 | 0.27569 | 26.4659
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.008485 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.10182 | 0 | 0.27652 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.008485 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.10182 | 0 | 0.27652 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.010469 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.14343 | 0 | -0.032694 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.010096 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084806 | 8.4 | -0.032321 | -0.2715
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.008099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.19438 | 24 | -0.030324 | -0.72778
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.008099 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.19438 | 24 | -0.030324 | -0.72778
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.008099 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.18628 | 23 | -0.030324 | -0.69746
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.012594 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8891 | 150 | 0.28063 | 42.095
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.012594 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0075 | 80 | 0.28063 | 22.4507
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.012869 | north | 3 | N | N | Nnorth | Nnorth | 1 | 14.8894 | 0 | 0.28091 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.012869 | north | 3 | N | N | Nnorth | Nnorth | 1 | 14.9023 | 0 | 0.28091 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.013005 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.19507 | 0 | 0.28104 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.013005 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.19507 | 0 | 0.28104 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.00736 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13248 | 0 | -0.029585 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.00736 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13248 | 0 | -0.029585 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.00736 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1104 | 0 | -0.029585 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.006908 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.9152 | 422 | -0.029133 | -12.2942
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.013614 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4716 | 255 | 0.28165 | 71.8216
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.013614 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.0285 | 149 | 0.28165 | 41.9664
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.013614 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.0829 | 153 | 0.28165 | 43.093
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.006234 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17455 | 0 | -0.028459 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.006234 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18079 | 0 | -0.028459 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.014167 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28221 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.014167 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28221 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.014331 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1141 | 217.3 | 0.28237 | 61.3591
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.014331 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.9379 | 205 | 0.28237 | 57.8859
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.014331 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9038 | 272.4 | 0.28237 | 76.9177
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.014334 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0034 | 70 | 0.28237 | 19.7661
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.014334 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.98905 | 69 | 0.28237 | 19.4838
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.014334 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.98905 | 69 | 0.28237 | 19.4838
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.014334 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.97471 | 68 | 0.28237 | 19.2014
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.014698 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2664 | 0 | 0.28274 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.014698 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2929 | 0 | 0.28274 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.014698 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2929 | 0 | 0.28274 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.014698 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.5852 | 0 | 0.28274 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.014917 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28296 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.014917 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 11.7397 | 787 | 0.28296 | 222.6867
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.015188 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.72902 | 48 | 0.28323 | 13.5949
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.015188 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.69865 | 46 | 0.28323 | 13.0285
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.015188 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.5947 | 105 | 0.28323 | 29.7389
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.015227 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.48726 | 0 | 0.28327 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.015239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28328 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.015239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28328 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.015239 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.25906 | 17 | 0.28328 | 4.8157
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.015239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28328 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.015239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28328 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.015254 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0626 | 0 | 0.28329 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.015384 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5845 | 168 | 0.28342 | 47.6151
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.015384 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3846 | 90 | 0.28342 | 25.5081
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.015834 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.31668 | 20 | 0.28387 | 5.6775
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.015834 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.31668 | 20 | 0.28387 | 5.6775
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.015834 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.31668 | 20 | 0.28387 | 5.6775
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.015834 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.26918 | 17 | 0.28387 | 4.8258
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004226 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.076068 | 0 | -0.026451 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004226 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.076068 | 0 | -0.026451 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.004132 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.026357 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.004128 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.4128 | 100 | -0.026353 | -2.6353
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.004128 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.4128 | 100 | -0.026353 | -2.6353
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.004128 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.026353 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.004128 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.026353 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.004128 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.026353 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.004128 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.026353 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.017001 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.30602 | 18 | 0.28504 | 5.1307
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.017001 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.30602 | 18 | 0.28504 | 5.1307
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.017001 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.64604 | 38 | 0.28504 | 10.8315
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.017015 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.0418 | 0 | 0.28505 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.017091 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.6128 | 0 | 0.28513 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.017091 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.6128 | 0 | 0.28513 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.017091 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.603 | 0 | 0.28513 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.017091 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.6149 | 0 | 0.28513 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.017827 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.7429 | 0 | 0.28587 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.017827 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.6003 | 0 | 0.28587 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.001865 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.02409 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.018993 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.28703 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.019873 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.2219 | 0 | 0.28791 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.019873 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.6655 | 0 | 0.28791 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.020234 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0493 | 150.7 | 0.28827 | 43.4428
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.020234 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0553 | 151 | 0.28827 | 43.5293
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.020234 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5895 | 177.4 | 0.28827 | 51.1397
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.020308 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0767 | 151.5 | 0.28835 | 43.6846
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.020308 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0929 | 152.3 | 0.28835 | 43.9153
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.020308 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.6047 | 177.5 | 0.28835 | 51.1817
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.022225 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.022225 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.022225 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.022225 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.022225 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.022225 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.022225 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.022225 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.000106 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001272 | 0 | -0.022119 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.000106 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001166 | 0 | -0.022119 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000106 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001272 | 0 | -0.022119 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.020852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6708 | 224 | 0.28889 | 64.7117
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.020852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7126 | 226 | 0.28889 | 65.2895
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.020852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4206 | 212 | 0.28889 | 61.245
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.020852 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.3998 | 211 | 0.28889 | 60.9561
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070794 | 0 | -0.021604 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13786 | 0 | -0.021604 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11426 | 0 | -0.021604 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1391 | 0 | -0.021604 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000621 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.071415 | 0 | -0.021604 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.02109 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0739 | 288 | 0.28913 | 83.2693
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.02109 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1002 | 147 | 0.28913 | 42.502
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.02109 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1002 | 147 | 0.28913 | 42.502
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.021193 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.7472 | 224 | 0.28923 | 64.7881
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.000988 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.057304 | 58 | -0.021237 | -1.2318
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.000988 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.087932 | 89 | -0.021237 | -1.8901
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.000988 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.043472 | 44 | -0.021237 | -0.93444
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.000988 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.043472 | 44 | -0.021237 | -0.93444
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.000988 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.042484 | 43 | -0.021237 | -0.9132
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.000988 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.04446 | 45 | -0.021237 | -0.95567
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.021412 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.1817 | 242 | 0.28945 | 70.0472
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.021413 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1969 | 196 | 0.28945 | 56.7327
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.021413 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3768 | 111 | 0.28945 | 32.1292
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.001456 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.59259 | 407 | -0.020769 | -8.4531
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.001564 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.61934 | 0 | -0.020661 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.021993 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7593 | 216.4 | 0.29003 | 62.763
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.021993 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7527 | 216.1 | 0.29003 | 62.676
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.001617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.33795 | 209 | -0.020608 | -4.3071
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.001617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34927 | 216 | -0.020608 | -4.4514
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.001617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074382 | 46 | -0.020608 | -0.94798
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.001617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.075999 | 47 | -0.020608 | -0.96858
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.001617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074382 | 46 | -0.020608 | -0.94798
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.001617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074382 | 46 | -0.020608 | -0.94798
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.00162 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.66744 | 412 | -0.020605 | -8.4893
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.00162 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.648 | 400 | -0.020605 | -8.2421
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.001701 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.72122 | 0 | -0.020524 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.001701 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.72293 | 0 | -0.020524 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.022081 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.0187 | 182 | 0.29012 | 52.8019
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.022081 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.6872 | 484 | 0.29012 | 140.4183
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.001732 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.020493 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.022119 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.1059 | 0 | 0.29016 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.022139 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.29018 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.001857 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.064995 | 0 | -0.020368 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.001857 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.063138 | 0 | -0.020368 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.001857 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.064995 | 0 | -0.020368 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.001915 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.02031 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.02232 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.3034 | 0 | 0.29036 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.02232 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.9016 | 0 | 0.29036 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.02232 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.2364 | 0 | 0.29036 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.02232 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.9057 | 0 | 0.29036 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.002047 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.020178 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.002047 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.020178 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.002047 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.020178 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.002149 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33309 | 155 | -0.020076 | -3.1118
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.002149 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36533 | 170 | -0.020076 | -3.413
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.002149 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33309 | 155 | -0.020076 | -3.1118
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.022533 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.6884 | 0 | 0.29057 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.022533 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.9137 | 0 | 0.29057 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.022533 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.5757 | 0 | 0.29057 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.002167 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31747 | 146.5 | -0.020058 | -2.9385
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.002167 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.3205 | 147.9 | -0.020058 | -2.9666
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.002167 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.37489 | 173 | -0.020058 | -3.4701
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.002308 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.2602 | 0 | -0.019917 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.002308 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.731 | 0 | -0.019917 | 0
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.002509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.51936 | 207 | -0.019716 | -4.0812
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.002509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.5437 | 216.7 | -0.019716 | -4.2725
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.002509 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.60718 | 242 | -0.019716 | -4.7713
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.00251 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36144 | 144 | -0.019715 | -2.839
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.00251 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36144 | 144 | -0.019715 | -2.839
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.00251 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42921 | 171 | -0.019715 | -3.3713
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.002716 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.10321 | 38 | -0.019509 | -0.74135
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.002716 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.052419 | 19.3 | -0.019509 | -0.37653
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.002716 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.04074 | 15 | -0.019509 | -0.29264
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.002716 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12765 | 47 | -0.019509 | -0.91693
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.002716 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.019509 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.26292 | 0 | -0.019428 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11468 | 0 | -0.019428 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10629 | 0 | -0.019428 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.053143 | 0 | -0.019428 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.26292 | 0 | -0.019428 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10069 | 0 | -0.019428 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.12027 | 0 | -0.019428 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.061534 | 0 | -0.019428 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.41396 | 0 | -0.019428 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13985 | 0 | -0.019428 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15383 | 0 | -0.019428 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.002797 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13985 | 0 | -0.019428 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.002877 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011508 | 0 | -0.019348 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.002896 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.083984 | 0 | -0.019329 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.002929 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.017574 | 0 | -0.019296 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.003002 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.11408 | 0 | -0.019223 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.003025 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.11495 | 0 | -0.0192 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.003028 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0757 | 0 | -0.019197 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.003028 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0757 | 0 | -0.019197 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4482 | 147 | -0.019176 | -2.8189
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42076 | 138 | -0.019176 | -2.6463
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42686 | 140 | -0.019176 | -2.6847
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4482 | 147 | -0.019176 | -2.8189
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55492 | 182 | -0.019176 | -3.4901
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.003049 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.6037 | 198 | -0.019176 | -3.7969
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.003052 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0194 | 334 | -0.019173 | -6.4038
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.003052 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0377 | 340 | -0.019173 | -6.5189
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.003052 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54936 | 180 | -0.019173 | -3.4512
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.003052 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54936 | 180 | -0.019173 | -3.4512
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.003086 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55548 | 180 | -0.019139 | -3.4451
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.00309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.45825 | 0 | -0.019135 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.00309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.45917 | 0 | -0.019135 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.00309 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47277 | 0 | -0.019135 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.003092 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0389 | 336 | -0.019133 | -6.4287
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.003092 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55656 | 180 | -0.019133 | -3.444
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.003103 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.9518 | 0 | -0.019122 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08025 | 0 | -0.019015 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08025 | 0 | -0.019015 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08025 | 0 | -0.019015 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05136 | 0 | -0.019015 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08025 | 0 | -0.019015 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08025 | 0 | -0.019015 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08025 | 0 | -0.019015 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.00321 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.04815 | 0 | -0.019015 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.023645 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.7901 | 118 | 0.29168 | 34.4188
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.023645 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.7192 | 115 | 0.29168 | 33.5437
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.023645 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.1466 | 556 | 0.29168 | 162.1765
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.52077 | 0 | -0.018929 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.50429 | 0 | -0.018929 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.3296 | 0 | -0.018929 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47792 | 0 | -0.018929 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.48451 | 0 | -0.018929 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.003296 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.41859 | 0 | -0.018929 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.003296 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.039552 | 0 | -0.018929 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003306 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0079344 | 0 | -0.018919 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003306 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0079344 | 0 | -0.018919 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.003306 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0092568 | 0 | -0.018919 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.003315 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.47073 | 142 | -0.01891 | -2.6852
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.003315 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48068 | 145 | -0.01891 | -2.742
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.003315 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.50057 | 151 | -0.01891 | -2.8554
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.003315 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.96135 | 290 | -0.01891 | -5.484
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.003574 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.80022 | 223.9 | -0.018651 | -4.176
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.003574 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.80415 | 225 | -0.018651 | -4.1965
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.003574 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.80272 | 224.6 | -0.018651 | -4.1891
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.003574 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.81023 | 226.7 | -0.018651 | -4.2282
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.024015 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.7017 | 0 | 0.29205 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.024079 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.29212 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.024079 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.29212 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.003718 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.081796 | 22 | -0.018507 | -0.40716
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003718 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.040898 | 11 | -0.018507 | -0.20358
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003718 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.040898 | 11 | -0.018507 | -0.20358
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8807 | 161 | 0.29214 | 47.0351
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9531 | 164 | 0.29214 | 47.9115
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9531 | 164 | 0.29214 | 47.9115
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.9791 | 414 | 0.29214 | 120.9474
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9048 | 162 | 0.29214 | 47.3272
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8807 | 161 | 0.29214 | 47.0351
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.929 | 163 | 0.29214 | 47.6194
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.024104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.8585 | 409 | 0.29214 | 119.4867
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003753 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0090072 | 0 | -0.018472 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003753 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0090072 | 0 | -0.018472 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.003773 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.045276 | 0 | -0.018452 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.024229 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.4009 | 388 | 0.29227 | 113.4002
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.024229 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.4779 | 515 | 0.29227 | 150.5182
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.003907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18636 | 47.7 | -0.018318 | -0.87378
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.003907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14573 | 37.3 | -0.018318 | -0.68327
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.003907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.17972 | 46 | -0.018318 | -0.84264
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.003907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18754 | 48 | -0.018318 | -0.87927
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.003989 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57442 | 144 | -0.018236 | -2.626
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.003989 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.74993 | 188 | -0.018236 | -3.4284
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.004093 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.29879 | 0 | -0.018132 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.004234 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06351 | 0 | -0.017991 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.004234 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.097382 | 0 | -0.017991 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.004265 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.03412 | 0 | -0.01796 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.024707 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.98828 | 40 | 0.29275 | 11.7099
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.024713 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.49426 | 20 | 0.29275 | 5.855
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.024713 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.61782 | 25 | 0.29275 | 7.3188
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.024713 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.0132 | 41 | 0.29275 | 12.0028
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12146 | 0 | -0.017887 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.030366 | 0 | -0.017887 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16918 | 0 | -0.017887 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06507 | 0 | -0.017887 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.030366 | 0 | -0.017887 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06507 | 0 | -0.017887 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16918 | 0 | -0.017887 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.004338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16918 | 0 | -0.017887 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.024818 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.9606 | 79 | 0.29286 | 23.1357
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.024818 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.6307 | 106 | 0.29286 | 31.0429
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.024818 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.6234 | 146 | 0.29286 | 42.7572
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.024818 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.8862 | 76 | 0.29286 | 22.2572
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.024872 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.8193 | 435 | 0.29291 | 127.4165
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.024925 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.8454 | 395 | 0.29296 | 115.7209
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.024925 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.8424 | 435 | 0.29296 | 127.4395
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.004596 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.036768 | 0 | -0.017629 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.004596 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.036768 | 0 | -0.017629 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.004714 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.22627 | 0 | -0.017511 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23466 | 49 | -0.017436 | -0.85437
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22029 | 46 | -0.017436 | -0.80206
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22029 | 46 | -0.017436 | -0.80206
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22508 | 47 | -0.017436 | -0.8195
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.004789 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.73751 | 154 | -0.017436 | -2.6852
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.004789 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.70877 | 148 | -0.017436 | -2.5806
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22987 | 48 | -0.017436 | -0.83694
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.004789 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22987 | 48 | -0.017436 | -0.83694
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.38038 | 0 | -0.01741 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.39002 | 0 | -0.01741 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.38038 | 0 | -0.01741 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3852 | 0 | -0.01741 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3775 | 0 | -0.01741 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12037 | 0 | -0.01741 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.22149 | 0 | -0.01741 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13482 | 0 | -0.01741 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.20993 | 0 | -0.01741 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.004815 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.35631 | 0 | -0.01741 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.02522 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.0728 | 0 | 0.29326 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.02522 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.6024 | 0 | 0.29326 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.02522 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 20.3778 | 0 | 0.29326 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.004854 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.5047 | 310 | -0.017371 | -5.3851
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.004854 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.0047 | 413 | -0.017371 | -7.1743
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.025291 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.8968 | 0 | 0.29333 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.025291 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.0132 | 0 | 0.29333 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.025291 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.2357 | 0 | 0.29333 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0573 | 160 | 0.2934 | 46.9436
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9558 | 156 | 0.2934 | 45.77
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.9702 | 196 | 0.2934 | 57.5059
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9558 | 156 | 0.2934 | 45.77
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9812 | 157 | 0.2934 | 46.0634
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.025358 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.0209 | 198 | 0.2934 | 58.0927
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.02544 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.4128 | 370 | 0.29348 | 108.5874
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.5616 | 0 | 0.29348 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.587 | 0 | 0.29348 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.861 | 0 | 0.29348 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.6379 | 0 | 0.29348 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.6634 | 0 | 0.29348 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.02544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.8864 | 0 | 0.29348 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.00507 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.21294 | 42 | -0.017155 | -0.72052
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.00507 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22308 | 44 | -0.017155 | -0.75483
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.00507 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22308 | 44 | -0.017155 | -0.75483
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.00507 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23829 | 47 | -0.017155 | -0.80629
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.025552 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.3438 | 170 | 0.29359 | 49.9105
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.025552 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.287 | 520 | 0.29359 | 152.6675
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.025653 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0261 | 0 | 0.29369 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.025653 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0261 | 0 | 0.29369 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.025808 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.29385 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.005605 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.73986 | 132 | -0.01662 | -2.1939
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.005605 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.75107 | 134 | -0.01662 | -2.2271
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.005605 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8104 | 323 | -0.01662 | -5.3683
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.005636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.85949 | 152.5 | -0.016589 | -2.5298
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.005636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.84258 | 149.5 | -0.016589 | -2.4801
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.005636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.3109 | 232.6 | -0.016589 | -3.8586
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.005978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2989 | 50 | -0.016247 | -0.81236
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.005978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2989 | 50 | -0.016247 | -0.81236
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.005978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2989 | 50 | -0.016247 | -0.81236
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.005978 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2989 | 50 | -0.016247 | -0.81236
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.026388 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29443 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.006149 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.97154 | 158 | -0.016076 | -2.54
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.006149 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.98384 | 160 | -0.016076 | -2.5722
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.006149 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0761 | 175 | -0.016076 | -2.8133
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.006208 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.6881 | 0 | -0.016017 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.00621 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.6266 | 0 | -0.016015 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.00621 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.6949 | 0 | -0.016015 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.008266 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 11.0186 | 0 | -0.013959 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.008266 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 10.9772 | 0 | -0.013959 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.64022 | 76 | -0.013801 | -1.0489
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.64022 | 76 | -0.013801 | -1.0489
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.88452 | 105 | -0.013801 | -1.4491
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62338 | 74 | -0.013801 | -1.0213
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62338 | 74 | -0.013801 | -1.0213
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.008424 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.85925 | 102 | -0.013801 | -1.4077
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.008535 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.8564 | 0 | -0.01369 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.008535 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.9588 | 0 | -0.01369 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.008561 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.56503 | 66 | -0.013664 | -0.90184
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.029267 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29731 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.029267 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29731 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.029267 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.29731 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.029502 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.7701 | 60 | 0.29754 | 17.8525
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.029502 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8586 | 63 | 0.29754 | 18.7451
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58491 | 0 | -0.012791 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67359 | 0 | -0.012791 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42453 | 0 | -0.012791 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95283 | 0 | -0.012791 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.81132 | 0 | -0.012791 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.83019 | 0 | -0.012791 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4717 | 0 | -0.012791 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16981 | 0 | -0.012791 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.8868 | 0 | -0.012791 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.66038 | 0 | -0.012791 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59434 | 0 | -0.012791 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67925 | 0 | -0.012791 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61132 | 0 | -0.012791 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95283 | 0 | -0.012791 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.9151 | 0 | -0.012791 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.9717 | 0 | -0.012791 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71698 | 0 | -0.012791 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75472 | 0 | -0.012791 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75472 | 0 | -0.012791 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.009434 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6132 | 0 | -0.012791 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.009644 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68472 | 0 | -0.012581 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.009644 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.09644 | 0 | -0.012581 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.009822 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0902 | 0 | -0.012403 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.009822 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0902 | 0 | -0.012403 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.009822 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1688 | 0 | -0.012403 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.009822 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0755 | 0 | -0.012403 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.010394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.47916 | 0 | -0.011831 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.01045 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 6.803 | 0 | -0.011775 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.01045 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.8938 | 0 | -0.011775 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.01045 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 6.27 | 0 | -0.011775 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.010455 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7042 | 0 | -0.01177 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.010455 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7042 | 0 | -0.01177 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.010455 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.5615 | 0 | -0.01177 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.01048 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34584 | 0 | -0.011745 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.010562 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.7005 | 161 | -0.011663 | -1.8778
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.010562 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.7533 | 166 | -0.011663 | -1.9361
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.010562 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.6194 | 248 | -0.011663 | -2.8925
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.010562 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 5.7669 | 546 | -0.011663 | -6.3681
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.010562 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 6.7914 | 0 | -0.011663 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.010562 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13731 | 13 | -0.011663 | -0.15162
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.010806 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34579 | 0 | -0.011419 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.010806 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32418 | 0 | -0.011419 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.010806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0838 | 0 | -0.011419 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.010806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0039 | 0 | -0.011419 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.010806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1098 | 0 | -0.011419 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.010806 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1022 | 0 | -0.011419 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.010808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.76521 | 0 | -0.011417 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.010808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72089 | 0 | -0.011417 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.010808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57282 | 0 | -0.011417 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6558 | 0 | -0.011417 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.659 | 0 | -0.011417 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6461 | 0 | -0.011417 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0376 | 0 | -0.011417 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.010808 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.6372 | 0 | -0.011417 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.010808 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.43232 | 0 | -0.011417 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.010946 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.5473 | 50 | -0.011279 | -0.56396
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.011021 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.011204 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.013 | 0 | -0.011093 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.97516 | 0 | -0.011093 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.96848 | 0 | -0.011093 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60669 | 0 | -0.011093 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.011132 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13581 | 0 | -0.011093 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.011174 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72631 | 0 | -0.011051 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.011174 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.67044 | 0 | -0.011051 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.011174 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72631 | 0 | -0.011051 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.011174 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72631 | 0 | -0.011051 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.51745 | 46 | -0.010976 | -0.5049
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.51745 | 46 | -0.010976 | -0.5049
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.51745 | 46 | -0.010976 | -0.5049
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.61869 | 55 | -0.010976 | -0.60369
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.61869 | 55 | -0.010976 | -0.60369
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.011249 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.60745 | 54 | -0.010976 | -0.59271
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.011253 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.87773 | 0 | -0.010972 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.011253 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90024 | 0 | -0.010972 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8394 | 0 | -0.010954 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7707 | 0 | -0.010954 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7752 | 0 | -0.010954 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7695 | 0 | -0.010954 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.011271 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.0319 | 0 | -0.010954 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.011295 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39532 | 0 | -0.01093 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.011313 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13576 | 12 | -0.010912 | -0.13095
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.011313 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.010912 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.011314 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.9121 | 169 | -0.010911 | -1.844
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.011315 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.867 | 165 | -0.01091 | -1.8002
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.011317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6862 | 0 | -0.010908 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.011317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.73674 | 0 | -0.010908 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.01132 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.4112 | 213 | -0.010905 | -2.3228
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72454 | 0 | -0.010904 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71549 | 0 | -0.010904 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.93511 | 0 | -0.010904 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.83323 | 0 | -0.010904 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1834 | 0 | -0.010904 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.011322 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.5814 | 228 | -0.010903 | -2.4859
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.011323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.0381 | 0 | -0.010902 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.011323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7958 | 0 | -0.010902 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.011323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7777 | 0 | -0.010902 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80578 | 0 | -0.010876 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.81713 | 0 | -0.010876 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.44261 | 0 | -0.010876 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34047 | 0 | -0.010876 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.011395 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.47859 | 42 | -0.01083 | -0.45487
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.011395 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.47859 | 42 | -0.01083 | -0.45487
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.011395 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.43301 | 38 | -0.01083 | -0.41155
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.011395 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.43301 | 38 | -0.01083 | -0.41155
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.011396 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5499 | 0 | -0.010829 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.01141 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9739 | 0 | -0.010815 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.01141 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5404 | 0 | -0.010815 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1945 | 104 | -0.010739 | -1.1169
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1945 | 104 | -0.010739 | -1.1169
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62024 | 54 | -0.010739 | -0.57992
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.60876 | 53 | -0.010739 | -0.56918
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62024 | 54 | -0.010739 | -0.57992
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.6547 | 57 | -0.010739 | -0.61213
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62024 | 54 | -0.010739 | -0.57992
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62024 | 54 | -0.010739 | -0.57992
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.66619 | 58 | -0.010739 | -0.62287
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.011486 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.66619 | 58 | -0.010739 | -0.62287
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.011498 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 8.451 | 735 | -0.010727 | -7.8845
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39154 | 0 | -0.010709 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39961 | 0 | -0.010709 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.37657 | 0 | -0.010709 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52858 | 0 | -0.010709 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20383 | 0 | -0.010709 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23493 | 0 | -0.010709 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22917 | 0 | -0.010709 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.40306 | 0 | -0.010709 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20729 | 0 | -0.010709 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.98347 | 0 | -0.010709 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.011516 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.7044 | 0 | -0.010709 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.011549 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13859 | 12 | -0.010676 | -0.12811
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.011567 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.057835 | 0 | -0.010658 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.011567 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.24291 | 0 | -0.010658 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.011568 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.13882 | 0 | -0.010657 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75199 | 0 | -0.010656 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.76355 | 0 | -0.010656 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80983 | 0 | -0.010656 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72885 | 0 | -0.010656 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71728 | 0 | -0.010656 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2032 | 0 | -0.010656 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.011569 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68257 | 0 | -0.010656 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.01157 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 8.5965 | 743 | -0.010655 | -7.9168
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.011586 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.819 | 0 | -0.010639 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.01159 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.9935 | 172 | -0.010635 | -1.8293
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.01159 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.9935 | 172 | -0.010635 | -1.8293
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.01159 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.9935 | 172 | -0.010635 | -1.8293
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.011641 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8952 | 0 | -0.010584 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.011641 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8789 | 0 | -0.010584 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.011641 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8498 | 0 | -0.010584 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.011641 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1338 | 0 | -0.010584 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.011663 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.6419 | 398 | -0.010562 | -4.2037
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65498 | 56 | -0.010529 | -0.58963
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.69006 | 59 | -0.010529 | -0.62122
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65498 | 56 | -0.010529 | -0.58963
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65498 | 56 | -0.010529 | -0.58963
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.69006 | 59 | -0.010529 | -0.62122
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.011696 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65498 | 56 | -0.010529 | -0.58963
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.011987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.0738 | 0 | -0.010238 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.011987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.87 | 0 | -0.010238 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.011987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.846 | 0 | -0.010238 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.011987 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.846 | 0 | -0.010238 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.011987 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9419 | 0 | -0.010238 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.046657 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.518 | 204 | 0.3147 | 64.1981
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.046657 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3781 | 201 | 0.3147 | 63.254
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.046657 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.291 | 242 | 0.3147 | 76.1565
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.086971 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.8314 | 366 | 0.35501 | 129.9338

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
Average line rating
| Temp | graham-cokfield
| 20 | 1340
| 25 | 1340
| 30 | 1340
| 35 | 1340
| 40 | 1340
| 45 | 1340
| 50 | 1340
| 55 | 1340
| 60 | 1334
| 65 | 1307
| 70 | 1280
| 75 | 1251
| 80 | 1223
| 85 | 1194
| 90 | 1163
| 95 | 1132
| 100 | 1098
| 105 | 1065
| 110 | 1031
| 115 | 994
| total | 24792
| avg | 1239.6