## test results
CRE test for: |  | Longcreek - Cookfield 345kV [1439-1442] | [5 empty] | PASS
Line Rating: |  | 1240
Direcction |  | North | → | West |  | N-W
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Longcreek - Cookfield 345kV [1439-1442]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.016565
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.0021903
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.19934
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.0080181
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Longcreek - Cookfield 345kV [1439-1442]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.017506
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.0018675
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.19667
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.0081167
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | Longcreek - Cookfield 345kV [1439-1442]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.014697
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.21324 | PASS
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.008448
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.19886
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.0058278
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.20745
PTDF tests
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.21324 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.21324 | -0.014697
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.06347
[6 empty] | Concentration |  | -0.29765 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.22708
[6 empty] | Concentration |  | -1.0649 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 144.6727
| Percent of line rating => | [6 empty] | 11.67% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -3.821
[7 empty] | B1(N-S) | -0.01603 | 0.040127 | 0.056157 | -0.01603
[7 empty] | B2 (N-W) | 0 | 0.81477 | 0.81477 | 0
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.013305 | 0.018975 | 0.032279 | -0.013305
[7 empty] | B4 (S-W) | 0.015925 | 0.77577 | 0.75984 | 0.015925
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.0022436 | -0.020024 | -0.022268 | 0.0022436
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.00026867 | -0.79294 | -0.79267 | -0.00026867
[7 empty] | test | 0 | 0.81477 | 0.81477 | 0
[7 empty] | B1 | -1.967%
Deployment Error Percent | [6 empty] | B2 | 0%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -1.633%
[7 empty] | B4 | 1.955%
[7 empty] | B5 | 0.2754%
[7 empty] | B6 | -0.03298%
[7 empty] | Max Abs Error | 1.967% | PASS

## Generation_sensitivity
Generator Sensitivities
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: Longcreek - Cookfield 345kV [1439-1442] C: Fisher Road - Oklaunion 345kV [1425-6100] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: Longcreek - Cookfield 345kV [1439-1442] C: Fisher Road - Oklaunion 345kV [1425-6100]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.009989 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -2.5472
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.009989 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -1.4884
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.009568 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.14352
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.009568 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.14352
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.009989 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -1.5283
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.00923 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -1.3845
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.00923 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -0.7384
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.006188 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -0.45172
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.006188 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -0.73637
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.006188 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -1.2685
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.006188 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -0.63118
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.006188 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -0.59405
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.008206 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.098472
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.008206 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.098472
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.011279 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -1.8949
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.011279 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -1.0151
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.2477
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.2477
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -0.52292
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -5.4138
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -2.7633
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -2.7633
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.021754 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -2.4473
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.018459 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -0.73836
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -1.4654
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -1.9662
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -2.7082
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.018549 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -1.4097
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.022646 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -1.3588
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.022646 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -1.4267
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.018466 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -0.36932
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.018467 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -0.46168
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.018467 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -0.75715
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.011251 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -5.2092
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 13.3814
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 13.1787
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 13.5842
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 13.5842
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 13.5842
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.20275 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 23.1134
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.20275 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 104.4157
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 13.5724
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 14.1893
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 14.1893
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 13.778
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 13.778
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 13.3667
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.20665 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 14.4657
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.20665 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 15.1683
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.20665 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 14.5484
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.20706 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 31.0598
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.20706 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 45.5543
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.20142 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 19.9409
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.20142 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 12.2868
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.20152 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 28.4142
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.20142 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 5.0356
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.20142 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 9.205
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.20142 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 9.205
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.20152 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 24.1823
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.20284 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 5.2332
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.204 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 20.5022
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.20355 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 24.4259
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.20414 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 11.8401
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.20435 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 43.7716
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.20738 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 31.1072
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.20008 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 1.3205
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.20008 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 6.8626
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.20738 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 20.9455
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.20327 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 24.3926
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | -0.057392 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | -21.0055
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.016465 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -3.9845
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.32331 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 129.322
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.32518 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 76.7427
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.52665 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -86.8964
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -7.5402
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -7.4294
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -8.9448
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.03761 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.7522
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.03761 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.7522
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.03761 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.7522
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.03761 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -0.63937
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.013587 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -1.6304
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.02441 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 1.4646
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.018969 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -1.4227
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.018969 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -1.5099
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.018969 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -1.6769
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -3.0421
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -2.966
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -3.7265
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -2.966
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -2.985
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -3.7646
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.01925 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -3.2725
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.01925 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -10.01
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019084 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -7.0611
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.018884 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -10.5373
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.018884 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -10.9338
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.018884 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -15.2583
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.021865 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -2.4489
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.021865 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -2.1865
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.021865 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -8.265
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -2.2351
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -2.1086
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -2.8019
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.013748 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -10.586
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -0.73129
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.72084
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.72084
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -0.7104
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.009179 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -10.6201
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.009179 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -10.6293
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -3.4321
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -3.4628
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.016216 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -3.5091
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.016216 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -3.5043
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -3.2483
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -3.2329
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.018377 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -7.2589
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.018366 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -7.9892
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.018377 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -7.994
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.019856 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -2.7401
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.017557 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -2.0717
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.017557 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -2.0191
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.017557 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -9.7617
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.018068 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -7.0104
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.018068 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -9.305
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.016756 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -13.1535
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.016756 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -13.321
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.016756 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -13.0697
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.016407 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -2.9861
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.016407 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -7.941
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.015721 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -3.5215
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.016434 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -0.8217
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.01645 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -0.6909
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.014695 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -9.0374
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.014695 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -8.626
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.010958 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -5.8844
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.010958 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -8.6239
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.010406 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -0.78045
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.010406 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -2.3101
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.006219 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -3.5386
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.001084 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -0.22656
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.001084 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -0.23414
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.000964 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -0.39235
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.049864
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -0.050948
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.049864
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.049864
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.001147 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -0.48633
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.001147 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -0.48747
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.000617 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -0.035786
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.000617 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -0.054913
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.027148
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.027148
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -0.026531
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -0.027765
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.001086 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -0.44743
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.001086 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -0.4344
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.001597 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -0.87196
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.001597 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -1.1978
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.001403 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -0.085583
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -0.13328
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.001403 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -0.21185
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.22925
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -0.25143
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.22925
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.002652 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.058344
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.002652 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.029172
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.002652 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.029172
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -0.13318
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -0.10414
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -0.12843
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -0.13402
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 3e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.00036
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 3e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.00033
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.006121 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.1469
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.006121 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.1469
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.006121 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.14078
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.001048 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -0.41501
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.006038 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -8.0487
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.006038 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -8.0185
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -0.072466
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.036805
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.028605
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.001907 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -0.089629
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.19187 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 14.3906
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.1889 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 28.3358
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.21461 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 36.3764
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.14784 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 22.176
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.20257 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 12.762
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.24757 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 160.8469
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.019381 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.77524
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.019381 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.77524
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.0053 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 2.2366
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -0.53341
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -0.54149
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -1.3052
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -0.70278
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -0.71168
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -0.7784
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.004496 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -2.6257
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.004496 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -2.6751
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.004494 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -1.9459
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -0.56759
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -0.57037
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -0.56936
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -0.57468
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.003287 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.026296
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.003287 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.026296
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.005652 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.10174
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.005652 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.10174
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.005652 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.08478
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.00796 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.10905
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.059364
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.059364
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.001242 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.04347
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.001242 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -0.042228
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.001242 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.04347
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.004798 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.13434
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.004798 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.13914
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.20272 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 7.095
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.20272 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 6.0815
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.2161
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.2161
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.2161
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.2161
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.002052 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.012312
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.002337 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.0056088
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.002337 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.0056088
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.002337 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.0065436
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.002018 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.008072
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.00267 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.006408
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.00267 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.006408
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.31561
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -0.29629
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -0.30058
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.31561
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -0.39075
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -0.42511
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -0.62006
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -0.60787
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -0.94575
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -0.33285
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -0.33988
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -0.35394
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -0.67976
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.055041 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 1.8164
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.055041 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 1.376
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 3e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.00036
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.00293 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -0.21389
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.27397
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -0.28091
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -0.087164
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.021791
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.27397
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -0.27744
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -0.27189
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -0.0867
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -0.15953
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.002193 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -1.3794
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.002853 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -0.41083
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.002853 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -0.53636
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.002687 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.032244
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.039493 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.23696
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.002186 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -0.7345
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.002157 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -0.72044
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.002157 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -0.73338
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.002119 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -0.080522
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.002139 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.053475
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.002139 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.053475
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.002137 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -0.081206
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.002041 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -0.059189
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.002185 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -0.32404
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.002185 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -0.32469
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.002185 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -0.33431
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -0.3694
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -0.35771
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -0.2338
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -0.33901
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -0.34369
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -0.29693
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -0.2196
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -0.2217
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -0.25933
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -0.36308
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -0.38009
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -0.42447
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.25258
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.25258
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -0.29993
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.003479 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -1.0785
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.003479 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -1.4368
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -0.15288
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.16016
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.16016
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -0.17108
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.16817
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.15787
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.15787
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.1613
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -0.52853
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -0.50794
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.16474
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.16474
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 14.3534
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 14.3534
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 19.0285
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 16.4039
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 16.4039
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 23.5806
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 42.6866
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 29.1343
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 27.1456
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 27.8837
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 30.139
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 43.0557
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.17314 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 36.1867
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.17314 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 21.9025
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.17314 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 43.1124
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.17314 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 34.109
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.20706 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 41.413
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.20706 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 25.2412
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.20276 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 30.2109
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.20255 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 36.4585
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.20255 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 36.4585
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.20257 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 45.578
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.22138 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 27.6724
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.22138 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 27.6724
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -2.6718
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -2.6908
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -5.897
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -2.729
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -2.7481
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -5.916
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.015849 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -3.1064
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.015849 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -1.7592
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.019332 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -2.8951
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -2.949
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -2.949
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -7.4445
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -2.9131
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -2.8951
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -2.9311
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -7.3546
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.017938 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.017938 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.01659 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -2.4553
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.01659 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -2.1567
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.01659 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -2.4055
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.01659 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -6.6194
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -2.2561
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -2.2606
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -2.6559
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -2.2772
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -2.2892
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -2.668
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.006219 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -3.6132
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.012623 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -10.7927
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.012623 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -10.7927
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.01123 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.35936
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.0112 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -0.5376
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.0112 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -0.5152
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.011239 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.13487
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.011239 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -0.57319
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.011239 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.19106
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.011239 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.24726
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.011239 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.28097
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.0112 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -1.176
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.1991 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 16.7243
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.1917 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 15.3358
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.1916 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 28.7394
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.1916 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 28.7394
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.56173
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.5292
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.4205
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -1.2155
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -1.2179
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -1.2083
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.76166
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -1.9359
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.31736
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -0.79568
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.73698
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -0.81472
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -0.80917
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.007933 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.25386
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.007933 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.23799
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.79909
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.79909
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -0.85668
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -0.78829
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.012623 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -1.9225
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.012623 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -1.9313
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.008373 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -1.1387
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.007689 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.25374
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.35162
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.35162
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.31814
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.31814
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.007066 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.50169
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.007066 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.07066
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.2502
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.2502
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -1.8792
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.53346
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.49242
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.53346
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.53346
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.008313 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -1.2386
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.008313 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.54118
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.74392
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.71613
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.71122
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.44554
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.099735
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.008502 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -6.317
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.008449 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -6.21
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.4649
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.4649
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.4649
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -1.5248
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.008383 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -1.4503
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.008383 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -1.1317
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -1.3928
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -1.3808
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -1.3594
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -2.303
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.53229
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.52563
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.68698
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.61213
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -1.3511
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -1.3006
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -1.3039
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -1.2998
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -2.2271
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.0085 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.0425
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.0085 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.1785
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.010836 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -1.6709
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.010836 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -1.6904
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.010836 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -1.6904
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.010836 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -4.1177
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.008572 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -3.4117
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.3801
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.3801
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.3801
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.45447
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.45447
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.4462
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.013173 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -10.8941
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.013173 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -10.7887
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.007625 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.35151
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.46786
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.46786
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -0.64638
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.45554
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.45554
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -0.62791
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -1.4972
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -1.3192
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -1.3059
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.008297 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.2904
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.008093 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -3.7147
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.55263
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.56113
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.59514
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.53563
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.52712
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -0.88421
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.50162
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -1.375
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -1.3574
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -1.3574
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.008814 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -1.4279
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.008514 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -1.3367
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.592
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.60034
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.32518
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.25014
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.008266 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.64475
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.008266 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.66128
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.008316 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.13472
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.008312 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -1.3715
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.008311 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -1.4046
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.008316 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -1.7713
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.008317 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -1.8963
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.008311 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.099732
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.008311 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.1496
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.008037 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.40185
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.87766
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.87766
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.45571
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.44727
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.45571
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.48102
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.45571
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.45571
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.48946
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.48946
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.008487 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.10184
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.48138
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.50716
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.48138
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.48138
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.50716
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.48138
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.006258 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -0.41303
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -1.2477
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -1.2865
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -1.922
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.00775 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -4.2315
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.00775 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -4.9832
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -4.9912
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -4.3242
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -4.6002
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.00775 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.10075
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.008501 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.10201
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.28771
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.29363
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.27671
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.38841
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.14978
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.17262
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.16839
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.29617
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.15232
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.72265
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -1.2524
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.42836
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -0.4933
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.3109
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.69781
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -0.59417
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -0.60799
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.34545
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.12436
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -0.64945
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -0.48363
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.43527
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -0.49745
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.4477
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.69781
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -0.67017
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -0.71163
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -0.52508
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.55272
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.55272
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -1.1814
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.063865
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.18684 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 14.2935
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.19187 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 15.35
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.19187 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 7.675
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.19262 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 15.4098
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.19172 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 15.3376
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.18779 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 15.0229
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.1865 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 15.666
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.19262 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 15.4098
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -0.038418
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.22648 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 27.1782
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.22648 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 52.771
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.22648 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 38.5477
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -0.074814
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -0.062008
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -0.075488
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -0.038755
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -0.0337
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.18556 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 11.1337
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.059084 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.16616 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.19563 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.93903
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 8.8034
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 25.2363
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 31.6921
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 27.936
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 24.6494
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 18.8979
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.19833 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 29.7498
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.19652 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 22.109
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.19652 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 29.3803
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.19652 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 36.5535
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.19652 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 42.1544
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.001907 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.035876 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.003177 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -0.097104
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -0.1512
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -0.25663
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.1849
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -0.080647
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -0.074746
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.037373
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.1849
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -0.070812
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -0.084581
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.043274
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.12141
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.046695
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.021791
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.046695
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.12141
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.12141
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -0.29112
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.09835
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -0.10819
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.09835
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.002338 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.028056
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.003035 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.045525
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.003035 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.069805
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.003392 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -0.16282
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.003059 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.024472
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.002182 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -0.39276
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.002186 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -0.39348
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.002157 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.38826
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.002157 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.38826
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.003174 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.3174
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.003174 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.3174
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.05685
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.05685
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.05685
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.036384
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.05685
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.05685
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.05685
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.03411
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.003174 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.003174 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 1.587
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.003174 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 1.587
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.003174 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.001311 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.055041 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.001494 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.001176 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L: Longcreek - Cookfield 345kV [1439-1442] C: Fisher Road - Oklaunion 345kV [1425-6100] | [7 empty] | 144.6727
Number of Bus | Name of Bus | ID | Max MW | L: Longcreek - Cookfield 345kV [1439-1442] C: Fisher Road - Oklaunion 345kV [1425-6100] | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.009989 | north | 0.0065757 | -0.0077987 | -0.20932 | -0.0019709 | 0.0019709 | houston | Y | 0.0065757 | 1.1742
239 | BOSQUESW | 1 | 149 | -0.009989 | north | 0.0065757 | -0.0077987 | -0.20932 | -0.0019709 | 0.0019709 | houston | Y | 0.0065757 | 0.68611
244 | WHITNYDM | 1 | 15 | -0.009568 | north | 0.0069967 | -0.0073777 | -0.2089 | -0.0015499 | 0.0015499 | houston | Y | 0.0069967 | 0.081702
245 | WHITNYDM | 2 | 15 | -0.009568 | north | 0.0069967 | -0.0073777 | -0.2089 | -0.0015499 | 0.0015499 | houston | Y | 0.0069967 | 0.081702
247 | BOSQUESW | 2 | 153 | -0.009989 | north | 0.0065757 | -0.0077987 | -0.20932 | -0.0019709 | 0.0019709 | houston | Y | 0.0065757 | 0.70453
251 | BOSQUESW | 2 | 150 | -0.00923 | north | 0.0073347 | -0.0070397 | -0.20857 | -0.0012119 | 0.0012119 | houston | Y | 0.0073347 | 0.91842
253 | BOSQUESW | 2 | 80 | -0.00923 | north | 0.0073347 | -0.0070397 | -0.20857 | -0.0012119 | 0.0012119 | houston | Y | 0.0073347 | 0.48982
332 | RWMILLER | 1 | 73 | -0.006188 | north | 0.010377 | -0.0039977 | -0.20552 | 0.0018301 | 0.0018301 | houston | Y | 0.010377 | 0.6239
333 | RWMILLER | 2 | 119 | -0.006188 | north | 0.010377 | -0.0039977 | -0.20552 | 0.0018301 | 0.0018301 | houston | Y | 0.010377 | 1.017
334 | RWMILLER | 3 | 205 | -0.006188 | north | 0.010377 | -0.0039977 | -0.20552 | 0.0018301 | 0.0018301 | houston | Y | 0.010377 | 1.7521
335 | RWMILLER | 4 | 102 | -0.006188 | north | 0.010377 | -0.0039977 | -0.20552 | 0.0018301 | 0.0018301 | houston | Y | 0.010377 | 0.87175
336 | RWMILLER | 5 | 96 | -0.006188 | north | 0.010377 | -0.0039977 | -0.20552 | 0.0018301 | 0.0018301 | houston | Y | 0.010377 | 0.82047
344 | MRSSHPRD | 1 | 12 | -0.008206 | north | 0.0083587 | -0.0060157 | -0.20754 | -0.00018791 | 0.00018791 | houston | Y | 0.0083587 | 0.098049
345 | MRSSHPRD | 2 | 12 | -0.008206 | north | 0.0083587 | -0.0060157 | -0.20754 | -0.00018791 | 0.00018791 | houston | Y | 0.0083587 | 0.098049
366 | JNSNCNTY | 1 | 168 | -0.011279 | north | 0.0052857 | -0.0090887 | -0.21061 | -0.0032609 | 0.0032609 | houston | Y | 0.0052857 | 0.34016
367 | JNSNCNTY | 2 | 90 | -0.011279 | north | 0.0052857 | -0.0090887 | -0.21061 | -0.0032609 | 0.0032609 | houston | Y | 0.0052857 | 0.18223
503 | NTHTEXAS | 1 | 18 | -0.013761 | north | 0.0028037 | -0.011571 | -0.2131 | -0.0057429 | 0.0028037 | North | N | 0.0028037 | 0
504 | NTHTEXAS | 2 | 18 | -0.013761 | north | 0.0028037 | -0.011571 | -0.2131 | -0.0057429 | 0.0028037 | North | N | 0.0028037 | 0
505 | NTHTEXAS | 3 | 38 | -0.013761 | north | 0.0028037 | -0.011571 | -0.2131 | -0.0057429 | 0.0028037 | North | N | 0.0028037 | 0
580 | JCKCNTY8 | 1 | 288 | -0.018798 | north | -0.0022333 | -0.016608 | -0.21813 | -0.01078 | 0.0022333 | North | N | 0.0022333 | 0
581 | JCKCNTY8 | 2 | 147 | -0.018798 | north | -0.0022333 | -0.016608 | -0.21813 | -0.01078 | 0.0022333 | North | N | 0.0022333 | 0
582 | JCKCNTY8 | 3 | 147 | -0.018798 | north | -0.0022333 | -0.016608 | -0.21813 | -0.01078 | 0.0022333 | North | N | 0.0022333 | 0
728 | WOLFRIDG | 1 | 112.5 | -0.021754 | north | -0.0051893 | -0.019564 | -0.22109 | -0.013736 | 0.0051893 | North | N | 0.0051893 | 0
837 | NEWMAN_G | 1 | 40 | -0.018459 | north | -0.0018943 | -0.016269 | -0.21779 | -0.010441 | 0.0018943 | North | N | 0.0018943 | 0
842 | OLINGER_ | 1 | 79 | -0.018549 | north | -0.0019843 | -0.016359 | -0.21788 | -0.010531 | 0.0019843 | North | N | 0.0019843 | 0
843 | OLINGER_ | 1 | 106 | -0.018549 | north | -0.0019843 | -0.016359 | -0.21788 | -0.010531 | 0.0019843 | North | N | 0.0019843 | 0
844 | OLINGER_ | 1 | 146 | -0.018549 | north | -0.0019843 | -0.016359 | -0.21788 | -0.010531 | 0.0019843 | North | N | 0.0019843 | 0
845 | OLINGER_ | 1 | 76 | -0.018549 | north | -0.0019843 | -0.016359 | -0.21788 | -0.010531 | 0.0019843 | North | N | 0.0019843 | 0
923 | SPENCER_ | 1 | 60 | -0.022646 | north | -0.0060813 | -0.020456 | -0.22198 | -0.014628 | 0.0060813 | North | N | 0.0060813 | 0
924 | SPENCER_ | 1 | 63 | -0.022646 | north | -0.0060813 | -0.020456 | -0.22198 | -0.014628 | 0.0060813 | North | N | 0.0060813 | 0
948 | STEAM1 | 1 | 20 | -0.018466 | north | -0.0019013 | -0.016276 | -0.2178 | -0.010448 | 0.0019013 | North | N | 0.0019013 | 0
949 | STEAM2 | 1 | 25 | -0.018467 | north | -0.0019023 | -0.016277 | -0.2178 | -0.010449 | 0.0019023 | North | N | 0.0019023 | 0
950 | STEAM3 | 1 | 41 | -0.018467 | north | -0.0019023 | -0.016277 | -0.2178 | -0.010449 | 0.0019023 | North | N | 0.0019023 | 0
990 | GIBN_CRE | 1 | 463 | -0.011251 | north | 0.0053137 | -0.0090607 | -0.21059 | -0.0032329 | 0.0032329 | houston | Y | 0.0053137 | 0.9634
1002 | PBCTAGE_ | A | 66 | 0.20275 | west | 0.21931 | 0.20494 | 0.0034133 | 0.21077 | 0.0034133 | west | N | 0.0034133 | 0
1003 | PBCTBGE_ | B | 65 | 0.20275 | west | 0.21931 | 0.20494 | 0.0034133 | 0.21077 | 0.0034133 | west | N | 0.0034133 | 0
1004 | PBCTCGE_ | C | 67 | 0.20275 | west | 0.21931 | 0.20494 | 0.0034133 | 0.21077 | 0.0034133 | west | N | 0.0034133 | 0
1005 | PBCTDGE_ | D | 67 | 0.20275 | west | 0.21931 | 0.20494 | 0.0034133 | 0.21077 | 0.0034133 | west | N | 0.0034133 | 0
1006 | PBCTEGE_ | E | 67 | 0.20275 | west | 0.21931 | 0.20494 | 0.0034133 | 0.21077 | 0.0034133 | west | N | 0.0034133 | 0
1007 | PB5GEN_6 | MB | 114 | 0.20275 | west | 0.21931 | 0.20494 | 0.0034133 | 0.21077 | 0.0034133 | west | N | 0.0034133 | 0
1008 | PB6GEN_7 | MB | 515 | 0.20275 | west | 0.21931 | 0.20494 | 0.0034133 | 0.21077 | 0.0034133 | west | N | 0.0034133 | 0
1039 | MRGNAG_1 | A | 66 | 0.20564 | west | 0.22221 | 0.20783 | 0.0063063 | 0.21366 | 0.0063063 | west | N | 0.0063063 | 0
1040 | MRGNBG_2 | B | 69 | 0.20564 | west | 0.22221 | 0.20783 | 0.0063063 | 0.21366 | 0.0063063 | west | N | 0.0063063 | 0
1041 | MRGNCG_3 | C | 69 | 0.20564 | west | 0.22221 | 0.20783 | 0.0063063 | 0.21366 | 0.0063063 | west | N | 0.0063063 | 0
1042 | MRGNDG_4 | D | 67 | 0.20564 | west | 0.22221 | 0.20783 | 0.0063063 | 0.21366 | 0.0063063 | west | N | 0.0063063 | 0
1043 | MRGNEG_5 | E | 67 | 0.20564 | west | 0.22221 | 0.20783 | 0.0063063 | 0.21366 | 0.0063063 | west | N | 0.0063063 | 0
1044 | MRGNFG_6 | F | 65 | 0.20564 | west | 0.22221 | 0.20783 | 0.0063063 | 0.21366 | 0.0063063 | west | N | 0.0063063 | 0
1045 | CALENG1G | 1 | 70 | 0.20665 | west | 0.22322 | 0.20884 | 0.0073173 | 0.21467 | 0.0073173 | west | N | 0.0073173 | 0
1046 | CALENG2G | 2 | 73.4 | 0.20665 | west | 0.22322 | 0.20884 | 0.0073173 | 0.21467 | 0.0073173 | west | N | 0.0073173 | 0
1047 | CALENG3G | 3 | 70.4 | 0.20665 | west | 0.22322 | 0.20884 | 0.0073173 | 0.21467 | 0.0073173 | west | N | 0.0073173 | 0
1058 | LONGSHOR | 1 | 150 | 0.20706 | west | 0.22363 | 0.20926 | 0.0077293 | 0.21508 | 0.0077293 | west | N | 0.0077293 | 0
1058 | LONGSHOR | 2 | 220 | 0.20706 | west | 0.22363 | 0.20926 | 0.0077293 | 0.21508 | 0.0077293 | west | N | 0.0077293 | 0
1061 | CIELOGEN | 1 | 99 | 0.20142 | west | 0.21799 | 0.20361 | 0.0020873 | 0.20944 | 0.0020873 | west | N | 0.0020873 | 0
1062 | CIELOGEN | 1 | 61 | 0.20142 | west | 0.21799 | 0.20361 | 0.0020873 | 0.20944 | 0.0020873 | west | N | 0.0020873 | 0
1068 | SCURRYCW | 1 | 141 | 0.20152 | west | 0.21808 | 0.20371 | 0.0021833 | 0.20954 | 0.0021833 | west | N | 0.0021833 | 0
1069 | KINDERMG | 1 | 25 | 0.20142 | west | 0.21799 | 0.20361 | 0.0020873 | 0.20944 | 0.0020873 | west | N | 0.0020873 | 0
1070 | KINDERMG | 1 | 45.7 | 0.20142 | west | 0.21799 | 0.20361 | 0.0020873 | 0.20944 | 0.0020873 | west | N | 0.0020873 | 0
1071 | KINDERMG | 1 | 45.7 | 0.20142 | west | 0.21799 | 0.20361 | 0.0020873 | 0.20944 | 0.0020873 | west | N | 0.0020873 | 0
1073 | SCURRYCW | 2 | 120 | 0.20152 | west | 0.21808 | 0.20371 | 0.0021833 | 0.20954 | 0.0021833 | west | N | 0.0021833 | 0
1320 | BSP 1 | 1 | 25.8 | 0.20284 | west | 0.2194 | 0.20503 | 0.0035023 | 0.21086 | 0.0035023 | west | N | 0.0035023 | 0
1326 | STANTONW | 1 | 100.5 | 0.204 | west | 0.22057 | 0.20619 | 0.0046663 | 0.21202 | 0.0046663 | west | N | 0.0046663 | 0
1327 | WILDHRSE | 1 | 120 | 0.20355 | west | 0.22011 | 0.20574 | 0.0042133 | 0.21157 | 0.0042133 | west | N | 0.0042133 | 0
1328 | OCOTILLO | 1 | 58 | 0.20414 | west | 0.2207 | 0.20633 | 0.0048033 | 0.21216 | 0.0048033 | west | N | 0.0048033 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.20435 | west | 0.22091 | 0.20654 | 0.0050133 | 0.21237 | 0.0050133 | west | N | 0.0050133 | 0
1343 | TRENTIPP | 1 | 150 | 0.20738 | west | 0.22395 | 0.20957 | 0.0080453 | 0.2154 | 0.0080453 | west | N | 0.0080453 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.20008 | west | 0.21664 | 0.20227 | 0.00074128 | 0.2081 | 0.00074128 | west | N | 0.00074128 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.20008 | west | 0.21664 | 0.20227 | 0.00074128 | 0.2081 | 0.00074128 | west | N | 0.00074128 | 0
1354 | AEPWIND_ | 1 | 101 | 0.20738 | west | 0.22395 | 0.20957 | 0.0080453 | 0.2154 | 0.0080453 | west | N | 0.0080453 | 0
1360 | GUNSIGHT | 1 | 120 | 0.20327 | west | 0.21984 | 0.20546 | 0.0039363 | 0.21129 | 0.0039363 | west | N | 0.0039363 | 0
1432 | GRHAMSES | 2 | 366 | -0.057392 | north | -0.040827 | -0.055202 | -0.25673 | -0.049374 | 0.040827 | North | N | 0.040827 | 0
1433 | GRHAMSES | 1 | 242 | -0.016465 | north | 9.9679e-05 | -0.014275 | -0.2158 | -0.0084469 | 9.9679e-05 | North | N | 9.9679e-05 | 0
1437 | MESQUITW | 1 | 400 | 0.32331 | west | 0.33987 | 0.3255 | 0.12397 | 0.33132 | 0.12397 | west | N | 0.12397 | 0
1438 | MESQUITW | 1 | 236 | 0.32518 | west | 0.34175 | 0.32737 | 0.12585 | 0.3332 | 0.12585 | west | N | 0.12585 | 0
1442 | COKFIELD | 1 | 165 | -0.52665 | west | -0.51008 | -0.52445 | -0.72598 | -0.51863 | 0.51008 | North | Y | 0.72598 | 35.6236
1453 | WCPWRCO_ | 1 | 204 | -0.036962 | north | -0.020397 | -0.034772 | -0.2363 | -0.028944 | 0.020397 | North | N | 0.020397 | 0
1454 | WCPWRCO_ | 2 | 201 | -0.036962 | north | -0.020397 | -0.034772 | -0.2363 | -0.028944 | 0.020397 | North | N | 0.020397 | 0
1455 | WCPWRCO_ | 3 | 242 | -0.036962 | north | -0.020397 | -0.034772 | -0.2363 | -0.028944 | 0.020397 | North | N | 0.020397 | 0
1479 | WFCOGEN_ | 1 | 20 | -0.03761 | west | -0.021045 | -0.03542 | -0.23695 | -0.029592 | 0.021045 | North | Y | 0.23695 | 4.318
1479 | WFCOGEN_ | 2 | 20 | -0.03761 | west | -0.021045 | -0.03542 | -0.23695 | -0.029592 | 0.021045 | North | Y | 0.23695 | 4.318
1482 | WFCOGEN_ | 1 | 20 | -0.03761 | west | -0.021045 | -0.03542 | -0.23695 | -0.029592 | 0.021045 | North | Y | 0.23695 | 4.318
1482 | WFCOGEN_ | 2 | 17 | -0.03761 | west | -0.021045 | -0.03542 | -0.23695 | -0.029592 | 0.021045 | North | Y | 0.23695 | 3.6703
1600 | BARTNWND | 1 | 120 | -0.013587 | north | 0.0029777 | -0.011397 | -0.21292 | -0.0055689 | 0.0029777 | North | N | 0.0029777 | 0
1643 | SLSTR1PP | 1 | 60 | 0.02441 | north | 0.040975 | 0.0266 | -0.17493 | 0.032428 | 0.0266 | south | Y | 0.040975 | 0.86246
1675 | PEC_1G | 1 | 75 | -0.018969 | north | -0.0024043 | -0.016779 | -0.2183 | -0.010951 | 0.0024043 | North | N | 0.0024043 | 0
1676 | PEC_2G | 2 | 79.6 | -0.018969 | north | -0.0024043 | -0.016779 | -0.2183 | -0.010951 | 0.0024043 | North | N | 0.0024043 | 0
1677 | PEC_3G | 3 | 88.4 | -0.018969 | north | -0.0024043 | -0.016779 | -0.2183 | -0.010951 | 0.0024043 | North | N | 0.0024043 | 0
1678 | LAMARPWR | 1 | 160 | -0.019013 | north | -0.0024483 | -0.016823 | -0.21835 | -0.010995 | 0.0024483 | North | N | 0.0024483 | 0
1679 | LAMARPWR | 2 | 156 | -0.019013 | north | -0.0024483 | -0.016823 | -0.21835 | -0.010995 | 0.0024483 | North | N | 0.0024483 | 0
1680 | LAMARPWR | 3 | 196 | -0.019013 | north | -0.0024483 | -0.016823 | -0.21835 | -0.010995 | 0.0024483 | North | N | 0.0024483 | 0
1681 | LAMARPWR | 4 | 156 | -0.019013 | north | -0.0024483 | -0.016823 | -0.21835 | -0.010995 | 0.0024483 | North | N | 0.0024483 | 0
1682 | LAMARPWR | 5 | 157 | -0.019013 | north | -0.0024483 | -0.016823 | -0.21835 | -0.010995 | 0.0024483 | North | N | 0.0024483 | 0
1683 | LAMARPWR | 6 | 198 | -0.019013 | north | -0.0024483 | -0.016823 | -0.21835 | -0.010995 | 0.0024483 | North | N | 0.0024483 | 0
1687 | VALLEY_1 | 1 | 170 | -0.01925 | north | -0.0026853 | -0.01706 | -0.21859 | -0.011232 | 0.0026853 | North | N | 0.0026853 | 0
1688 | VALLEY_2 | 2 | 520 | -0.01925 | north | -0.0026853 | -0.01706 | -0.21859 | -0.011232 | 0.0026853 | North | N | 0.0026853 | 0
1689 | VALLEY_3 | 3 | 370 | -0.019084 | north | -0.0025193 | -0.016894 | -0.21842 | -0.011066 | 0.0025193 | North | N | 0.0025193 | 0
1701 | MOSES_1G | 1 | 558 | -0.018884 | north | -0.0023193 | -0.016694 | -0.21822 | -0.010866 | 0.0023193 | North | N | 0.0023193 | 0
1702 | MOSES_2G | 2 | 579 | -0.018884 | north | -0.0023193 | -0.016694 | -0.21822 | -0.010866 | 0.0023193 | North | N | 0.0023193 | 0
1703 | MOSES_3G | 3 | 808 | -0.018884 | north | -0.0023193 | -0.016694 | -0.21822 | -0.010866 | 0.0023193 | North | N | 0.0023193 | 0
1861 | EAGLEMNT | MB | 112 | -0.021865 | north | -0.0053003 | -0.019675 | -0.2212 | -0.013847 | 0.0053003 | North | N | 0.0053003 | 0
1862 | EAGLEMNT | MB | 100 | -0.021865 | north | -0.0053003 | -0.019675 | -0.2212 | -0.013847 | 0.0053003 | North | N | 0.0053003 | 0
1863 | EAGLEMNT | MB | 378 | -0.021865 | north | -0.0053003 | -0.019675 | -0.2212 | -0.013847 | 0.0053003 | North | N | 0.0053003 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.010286 | north | 0.0062787 | -0.0080957 | -0.20962 | -0.0022679 | 0.0022679 | houston | Y | 0.0062787 | 0.87154
1878 | WLFHOLW_ | 2 | 205 | -0.010286 | north | 0.0062787 | -0.0080957 | -0.20962 | -0.0022679 | 0.0022679 | houston | Y | 0.0062787 | 0.82221
1879 | WLFHOLW_ | 3 | 272.4 | -0.010286 | north | 0.0062787 | -0.0080957 | -0.20962 | -0.0022679 | 0.0022679 | houston | Y | 0.0062787 | 1.0925
1889 | DECRDOVA | MB | 770 | -0.013748 | north | 0.0028167 | -0.011558 | -0.21308 | -0.0057299 | 0.0028167 | North | N | 0.0028167 | 0
1892 | DECRDOVA | A | 70 | -0.010447 | north | 0.0061177 | -0.0082567 | -0.20978 | -0.0024289 | 0.0024289 | houston | Y | 0.0061177 | 0.25821
1893 | DECRDOVA | B | 69 | -0.010447 | north | 0.0061177 | -0.0082567 | -0.20978 | -0.0024289 | 0.0024289 | houston | Y | 0.0061177 | 0.25452
1894 | DECRDOVA | C | 69 | -0.010447 | north | 0.0061177 | -0.0082567 | -0.20978 | -0.0024289 | 0.0024289 | houston | Y | 0.0061177 | 0.25452
1895 | DECRDOVA | D | 68 | -0.010447 | north | 0.0061177 | -0.0082567 | -0.20978 | -0.0024289 | 0.0024289 | houston | Y | 0.0061177 | 0.25084
1898 | COMCHEPK | 1 | 1157 | -0.009179 | north | 0.0073857 | -0.0069887 | -0.20851 | -0.0011609 | 0.0011609 | houston | Y | 0.0073857 | 7.2021
1899 | COMCHEPK | 2 | 1158 | -0.009179 | north | 0.0073857 | -0.0069887 | -0.20851 | -0.0011609 | 0.0011609 | houston | Y | 0.0073857 | 7.2083
1937 | MDLTHELP | 5 | 224 | -0.015322 | north | 0.0012427 | -0.013132 | -0.21466 | -0.0073039 | 0.0012427 | North | N | 0.0012427 | 0
1938 | MDLTHELP | 6 | 226 | -0.015322 | north | 0.0012427 | -0.013132 | -0.21466 | -0.0073039 | 0.0012427 | North | N | 0.0012427 | 0
1941 | MDLTHELP | 1 | 216.4 | -0.016216 | north | 0.00034868 | -0.014026 | -0.21555 | -0.0081979 | 0.00034868 | North | N | 0.00034868 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.016216 | north | 0.00034868 | -0.014026 | -0.21555 | -0.0081979 | 0.00034868 | North | N | 0.00034868 | 0
1943 | MDLTHELP | 3 | 212 | -0.015322 | north | 0.0012427 | -0.013132 | -0.21466 | -0.0073039 | 0.0012427 | North | N | 0.0012427 | 0
1944 | MDLTHELP | 4 | 211 | -0.015322 | north | 0.0012427 | -0.013132 | -0.21466 | -0.0073039 | 0.0012427 | North | N | 0.0012427 | 0
1947 | HANDLEY_ | 3 | 395 | -0.018377 | north | -0.0018123 | -0.016187 | -0.21771 | -0.010359 | 0.0018123 | North | N | 0.0018123 | 0
1948 | HANDLEY_ | 4 | 435 | -0.018366 | north | -0.0018013 | -0.016176 | -0.2177 | -0.010348 | 0.0018013 | North | N | 0.0018013 | 0
1949 | HANDLEY_ | 5 | 435 | -0.018377 | north | -0.0018123 | -0.016187 | -0.21771 | -0.010359 | 0.0018123 | North | N | 0.0018123 | 0
2371 | COLLIN_1 | MB | 138 | -0.019856 | north | -0.0032913 | -0.017666 | -0.21919 | -0.011838 | 0.0032913 | North | N | 0.0032913 | 0
2413 | MTCK6_G | 6 | 118 | -0.017557 | north | -0.00099232 | -0.015367 | -0.21689 | -0.0095389 | 0.00099232 | North | N | 0.00099232 | 0
2414 | MTCK7_G | 7 | 115 | -0.017557 | north | -0.00099232 | -0.015367 | -0.21689 | -0.0095389 | 0.00099232 | North | N | 0.00099232 | 0
2417 | MTCK8_G | 8 | 556 | -0.017557 | north | -0.00099232 | -0.015367 | -0.21689 | -0.0095389 | 0.00099232 | North | N | 0.00099232 | 0
2451 | LKHB1_G | 1 | 388 | -0.018068 | north | -0.0015033 | -0.015878 | -0.2174 | -0.01005 | 0.0015033 | North | N | 0.0015033 | 0
2452 | LKHB2_G | 2 | 515 | -0.018068 | north | -0.0015033 | -0.015878 | -0.2174 | -0.01005 | 0.0015033 | North | N | 0.0015033 | 0
3097 | MARTLAKE | 1 | 785 | -0.016756 | north | -0.00019132 | -0.014566 | -0.21609 | -0.0087379 | 0.00019132 | North | N | 0.00019132 | 0
3098 | MARTLAKE | 2 | 795 | -0.016756 | north | -0.00019132 | -0.014566 | -0.21609 | -0.0087379 | 0.00019132 | North | N | 0.00019132 | 0
3099 | MARTLAKE | 3 | 780 | -0.016756 | north | -0.00019132 | -0.014566 | -0.21609 | -0.0087379 | 0.00019132 | North | N | 0.00019132 | 0
3107 | STRYKER_ | 1 | 182 | -0.016407 | north | 0.00015768 | -0.014217 | -0.21574 | -0.0083889 | 0.00015768 | North | N | 0.00015768 | 0
3108 | STRYKER_ | 2 | 484 | -0.016407 | north | 0.00015768 | -0.014217 | -0.21574 | -0.0083889 | 0.00015768 | North | N | 0.00015768 | 0
3126 | TRINIDAD | 1 | 224 | -0.015721 | north | 0.00084368 | -0.013531 | -0.21506 | -0.0077029 | 0.00084368 | North | N | 0.00084368 | 0
3309 | ASPN_G | 1 | 50 | -0.016434 | north | 0.00013068 | -0.014244 | -0.21577 | -0.0084159 | 0.00013068 | North | N | 0.00013068 | 0
3348 | CHAMPION | MB | 42 | -0.01645 | north | 0.00011468 | -0.01426 | -0.21579 | -0.0084319 | 0.00011468 | North | N | 0.00011468 | 0
3381 | BBRN_1G | 1 | 615 | -0.014695 | north | 0.0018697 | -0.012505 | -0.21403 | -0.0066769 | 0.0018697 | North | N | 0.0018697 | 0
3382 | BBRN_2G | 2 | 587 | -0.014695 | north | 0.0018697 | -0.012505 | -0.21403 | -0.0066769 | 0.0018697 | North | N | 0.0018697 | 0
3403 | THOUSE_1 | MB | 537 | -0.010958 | north | 0.0056067 | -0.0087677 | -0.21029 | -0.0029399 | 0.0029399 | houston | Y | 0.0056067 | 1.4321
3404 | THOUSE_2 | 2 | 787 | -0.010958 | north | 0.0056067 | -0.0087677 | -0.21029 | -0.0029399 | 0.0029399 | houston | Y | 0.0056067 | 2.0987
3416 | LAKE_CRK | MB | 75 | -0.010406 | north | 0.0061587 | -0.0082157 | -0.20974 | -0.0023879 | 0.0023879 | houston | Y | 0.0061587 | 0.28281
3417 | LAKE_CRK | MB | 222 | -0.010406 | north | 0.0061587 | -0.0082157 | -0.20974 | -0.0023879 | 0.0023879 | houston | Y | 0.0061587 | 0.83711
3432 | SANDOW_4 | 4 | 569 | -0.006219 | south | 0.010346 | -0.0040287 | -0.20555 | 0.0017991 | 0.0017991 | houston | Y | 0.0040287 | 1.2686
5026 | BRAUNIG_ | 1 | 209 | -0.001084 | south | 0.015481 | 0.0011063 | -0.20042 | 0.0069341 | 0.0011063 | south | N | 0.0011063 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.001084 | south | 0.015481 | 0.0011063 | -0.20042 | 0.0069341 | 0.0011063 | south | N | 0.0011063 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.000964 | south | 0.015601 | 0.0012263 | -0.2003 | 0.0070541 | 0.0012263 | south | N | 0.0012263 | 0
5031 | BRA_VHBC | 1 | 46 | -0.001084 | south | 0.015481 | 0.0011063 | -0.20042 | 0.0069341 | 0.0011063 | south | N | 0.0011063 | 0
5032 | BRA_VHBC | 2 | 47 | -0.001084 | south | 0.015481 | 0.0011063 | -0.20042 | 0.0069341 | 0.0011063 | south | N | 0.0011063 | 0
5033 | BRA_VHBC | 3 | 46 | -0.001084 | south | 0.015481 | 0.0011063 | -0.20042 | 0.0069341 | 0.0011063 | south | N | 0.0011063 | 0
5034 | BRA_VHBC | 4 | 46 | -0.001084 | south | 0.015481 | 0.0011063 | -0.20042 | 0.0069341 | 0.0011063 | south | N | 0.0011063 | 0
5111 | CALAVER_ | 1 | 424 | -0.001147 | south | 0.015418 | 0.0010433 | -0.20048 | 0.0068711 | 0.0010433 | south | N | 0.0010433 | 0
5112 | CALAVER_ | 2 | 425 | -0.001147 | south | 0.015418 | 0.0010433 | -0.20048 | 0.0068711 | 0.0010433 | south | N | 0.0010433 | 0
5264 | LEON_LCP | 3 | 58 | -0.000617 | south | 0.015948 | 0.0015733 | -0.19995 | 0.0074011 | 0.0015733 | south | N | 0.0015733 | 0
5265 | LEON_LCP | 4 | 89 | -0.000617 | south | 0.015948 | 0.0015733 | -0.19995 | 0.0074011 | 0.0015733 | south | N | 0.0015733 | 0
5266 | LEON_LCP | 1 | 44 | -0.000617 | south | 0.015948 | 0.0015733 | -0.19995 | 0.0074011 | 0.0015733 | south | N | 0.0015733 | 0
5267 | LEON_LCP | 2 | 44 | -0.000617 | south | 0.015948 | 0.0015733 | -0.19995 | 0.0074011 | 0.0015733 | south | N | 0.0015733 | 0
5268 | LEON_LCP | 3 | 43 | -0.000617 | south | 0.015948 | 0.0015733 | -0.19995 | 0.0074011 | 0.0015733 | south | N | 0.0015733 | 0
5269 | LEON_LCP | 4 | 45 | -0.000617 | south | 0.015948 | 0.0015733 | -0.19995 | 0.0074011 | 0.0015733 | south | N | 0.0015733 | 0
5396 | CALAVER_ | 1 | 412 | -0.001086 | south | 0.015479 | 0.0011043 | -0.20042 | 0.0069321 | 0.0011043 | south | N | 0.0011043 | 0
5397 | CALAVER_ | 2 | 400 | -0.001086 | south | 0.015479 | 0.0011043 | -0.20042 | 0.0069321 | 0.0011043 | south | N | 0.0011043 | 0
5401 | CALAVER_ | 1 | 546 | -0.001597 | south | 0.014968 | 0.00059332 | -0.20093 | 0.0064211 | 0.00059332 | south | N | 0.00059332 | 0
5402 | CALAVER_ | 2 | 750 | -0.001597 | south | 0.014968 | 0.00059332 | -0.20093 | 0.0064211 | 0.00059332 | south | N | 0.00059332 | 0
5436 | TUTTL_WB | MB | 61 | -0.001403 | south | 0.015162 | 0.00078732 | -0.20074 | 0.0066151 | 0.00078732 | south | N | 0.00078732 | 0
5438 | TUTTL_WB | MB | 95 | -0.001403 | south | 0.015162 | 0.00078732 | -0.20074 | 0.0066151 | 0.00078732 | south | N | 0.00078732 | 0
5439 | TUTTL_WB | MB | 151 | -0.001403 | south | 0.015162 | 0.00078732 | -0.20074 | 0.0066151 | 0.00078732 | south | N | 0.00078732 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.001479 | south | 0.015086 | 0.00071132 | -0.20081 | 0.0065391 | 0.00071132 | south | N | 0.00071132 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.001479 | south | 0.015086 | 0.00071132 | -0.20081 | 0.0065391 | 0.00071132 | south | N | 0.00071132 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.001479 | south | 0.015086 | 0.00071132 | -0.20081 | 0.0065391 | 0.00071132 | south | N | 0.00071132 | 0
5503 | RAYBURNG | 1 | 22 | -0.002652 | south | 0.013913 | -0.00046168 | -0.20199 | 0.0053661 | 0.00046168 | south | N | 0.00046168 | 0
5505 | RAYBURNG | 1 | 11 | -0.002652 | south | 0.013913 | -0.00046168 | -0.20199 | 0.0053661 | 0.00046168 | south | N | 0.00046168 | 0
5506 | RAYBURNG | 1 | 11 | -0.002652 | south | 0.013913 | -0.00046168 | -0.20199 | 0.0053661 | 0.00046168 | south | N | 0.00046168 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.002792 | south | 0.013773 | -0.00060168 | -0.20213 | 0.0052261 | 0.00060168 | south | N | 0.00060168 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.002792 | south | 0.013773 | -0.00060168 | -0.20213 | 0.0052261 | 0.00060168 | south | N | 0.00060168 | 0
5511 | RAYBURNC | 1 | 46 | -0.002792 | south | 0.013773 | -0.00060168 | -0.20213 | 0.0052261 | 0.00060168 | south | N | 0.00060168 | 0
5512 | RAYBURNC | 1 | 48 | -0.002792 | south | 0.013773 | -0.00060168 | -0.20213 | 0.0052261 | 0.00060168 | south | N | 0.00060168 | 0
5728 | FALCONHY | 2 | 12 | 3e-05 | south | 0.016595 | 0.0022203 | -0.19931 | 0.0080481 | 0.0022203 | south | N | 0.0022203 | 0
5729 | FALCONHY | 3 | 11 | 3e-05 | south | 0.016595 | 0.0022203 | -0.19931 | 0.0080481 | 0.0022203 | south | N | 0.0022203 | 0
5890 | PEARSALL | 1 | 24 | 0.006121 | south | 0.022686 | 0.0083113 | -0.19321 | 0.014139 | 0.0083113 | south | N | 0.0083113 | 0
5891 | PEARSALL | 1 | 24 | 0.006121 | south | 0.022686 | 0.0083113 | -0.19321 | 0.014139 | 0.0083113 | south | N | 0.0083113 | 0
5892 | PEARSALL | 1 | 23 | 0.006121 | south | 0.022686 | 0.0083113 | -0.19321 | 0.014139 | 0.0083113 | south | N | 0.0083113 | 0
5903 | SANMIGUE | 1 | 396 | -0.001048 | south | 0.015517 | 0.0011423 | -0.20038 | 0.0069701 | 0.0011423 | south | N | 0.0011423 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.006038 | houston | 0.010527 | -0.0038477 | -0.20537 | 0.0019801 | 0.0019801 | houston | N | 0.0019801 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.006038 | houston | 0.010527 | -0.0038477 | -0.20537 | 0.0019801 | 0.0019801 | houston | N | 0.0019801 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | 0.016565 | 0.0021903 | -0.19934 | 0.0080181 | 0.0021903 | south | Y | 0.016565 | 8.6246
5932 | SI_RAY9 | 9 | 38 | -0.001907 | south | 0.014658 | 0.00028332 | -0.20124 | 0.0061111 | 0.00028332 | south | N | 0.00028332 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.001907 | south | 0.014658 | 0.00028332 | -0.20124 | 0.0061111 | 0.00028332 | south | N | 0.00028332 | 0
5934 | SI_RAY5 | 5 | 15 | -0.001907 | south | 0.014658 | 0.00028332 | -0.20124 | 0.0061111 | 0.00028332 | south | N | 0.00028332 | 0
5935 | SI_RAY10 | 10 | 47 | -0.001907 | south | 0.014658 | 0.00028332 | -0.20124 | 0.0061111 | 0.00028332 | south | N | 0.00028332 | 0
6016 | SWMESA | 1 | 75 | 0.19187 | west | 0.20844 | 0.19407 | -0.0074607 | 0.19989 | 0.0074607 | west | N | 0.0074607 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | 0.016565 | 0.0021903 | -0.19934 | 0.0080181 | 0.0021903 | south | Y | 0.19934 | 43.372
6144 | MCADOO1A | 1 | 150 | 0.1889 | west | 0.20547 | 0.1911 | -0.010431 | 0.19692 | 0.010431 | west | N | 0.010431 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.21461 | west | 0.23117 | 0.2168 | 0.015274 | 0.22263 | 0.015274 | west | N | 0.015274 | 0
6476 | LANGFORD | 1 | 150 | 0.14784 | west | 0.1644 | 0.15003 | -0.051496 | 0.15586 | 0.051496 | west | N | 0.051496 | 0
6637 | SNYDERW1 | 1 | 63 | 0.20257 | west | 0.21914 | 0.20476 | 0.0032363 | 0.21059 | 0.0032363 | west | N | 0.0032363 | 0
6752 | OKLA0A | 1 | 649.7 | 0.24757 | west | 0.26414 | 0.24976 | 0.048235 | 0.25559 | 0.048235 | west | N | 0.048235 | 0
6948 | DENISNDM | 1 | 40 | -0.019381 | north | -0.0028163 | -0.017191 | -0.21872 | -0.011363 | 0.0028163 | North | N | 0.0028163 | 0
6948 | DENISNDM | 2 | 40 | -0.019381 | north | -0.0028163 | -0.017191 | -0.21872 | -0.011363 | 0.0028163 | North | N | 0.0028163 | 0
7000 | L_FERGUS | 1 | 422 | 0.0053 | south | 0.021865 | 0.0074903 | -0.19404 | 0.013318 | 0.0074903 | south | N | 0.0074903 | 0
7004 | L_SIMGID | 1 | 132 | -0.004041 | south | 0.012524 | -0.0018507 | -0.20338 | 0.0039771 | 0.0018507 | south | N | 0.0018507 | 0
7005 | L_SIMGID | 2 | 134 | -0.004041 | south | 0.012524 | -0.0018507 | -0.20338 | 0.0039771 | 0.0018507 | south | N | 0.0018507 | 0
7006 | L_SIMGID | 3 | 323 | -0.004041 | south | 0.012524 | -0.0018507 | -0.20338 | 0.0039771 | 0.0018507 | south | N | 0.0018507 | 0
7007 | L_LOSTPI | 1 | 158 | -0.004448 | south | 0.012117 | -0.0022577 | -0.20378 | 0.0035701 | 0.0022577 | south | N | 0.0022577 | 0
7008 | L_LOSTPI | 2 | 160 | -0.004448 | south | 0.012117 | -0.0022577 | -0.20378 | 0.0035701 | 0.0022577 | south | N | 0.0022577 | 0
7009 | L_LOSTPI | 3 | 175 | -0.004448 | south | 0.012117 | -0.0022577 | -0.20378 | 0.0035701 | 0.0022577 | south | N | 0.0022577 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.004496 | south | 0.012069 | -0.0023057 | -0.20383 | 0.0035221 | 0.0023057 | south | N | 0.0023057 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.004496 | south | 0.012069 | -0.0023057 | -0.20383 | 0.0035221 | 0.0023057 | south | N | 0.0023057 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.004494 | south | 0.012071 | -0.0023037 | -0.20383 | 0.0035241 | 0.0023037 | south | N | 0.0023037 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.002535 | south | 0.01403 | -0.00034468 | -0.20187 | 0.0054831 | 0.00034468 | south | N | 0.00034468 | 0
7015 | L_HAYSEN | 2 | 225 | -0.002535 | south | 0.01403 | -0.00034468 | -0.20187 | 0.0054831 | 0.00034468 | south | N | 0.00034468 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.002535 | south | 0.01403 | -0.00034468 | -0.20187 | 0.0054831 | 0.00034468 | south | N | 0.00034468 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.002535 | south | 0.01403 | -0.00034468 | -0.20187 | 0.0054831 | 0.00034468 | south | N | 0.00034468 | 0
7020 | L_AUSTPL | 1 | 8 | -0.003287 | south | 0.013278 | -0.0010967 | -0.20262 | 0.0047311 | 0.0010967 | south | N | 0.0010967 | 0
7020 | L_AUSTPL | 2 | 8 | -0.003287 | south | 0.013278 | -0.0010967 | -0.20262 | 0.0047311 | 0.0010967 | south | N | 0.0010967 | 0
7022 | L_BUCHAN | 1 | 18 | 0.005652 | south | 0.022217 | 0.0078423 | -0.19368 | 0.01367 | 0.0078423 | south | N | 0.0078423 | 0
7023 | L_BUCHAN | 2 | 18 | 0.005652 | south | 0.022217 | 0.0078423 | -0.19368 | 0.01367 | 0.0078423 | south | N | 0.0078423 | 0
7024 | L_BUCHAN | 3 | 15 | 0.005652 | south | 0.022217 | 0.0078423 | -0.19368 | 0.01367 | 0.0078423 | south | N | 0.0078423 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.00796 | south | 0.024525 | 0.01015 | -0.19138 | 0.015978 | 0.01015 | south | N | 0.01015 | 0
7028 | L_MARBFA | 1 | 18 | 0.003298 | south | 0.019863 | 0.0054883 | -0.19604 | 0.011316 | 0.0054883 | south | N | 0.0054883 | 0
7029 | L_MARBFA | 2 | 18 | 0.003298 | south | 0.019863 | 0.0054883 | -0.19604 | 0.011316 | 0.0054883 | south | N | 0.0054883 | 0
7031 | L_MARSFO | 1 | 35 | -0.001242 | south | 0.015323 | 0.00094832 | -0.20058 | 0.0067761 | 0.00094832 | south | N | 0.00094832 | 0
7032 | L_MARSFO | 2 | 34 | -0.001242 | south | 0.015323 | 0.00094832 | -0.20058 | 0.0067761 | 0.00094832 | south | N | 0.00094832 | 0
7033 | L_MARSFO | 3 | 35 | -0.001242 | south | 0.015323 | 0.00094832 | -0.20058 | 0.0067761 | 0.00094832 | south | N | 0.00094832 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.004798 | south | 0.021363 | 0.0069883 | -0.19454 | 0.012816 | 0.0069883 | south | N | 0.0069883 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.004798 | south | 0.021363 | 0.0069883 | -0.19454 | 0.012816 | 0.0069883 | south | N | 0.0069883 | 0
7038 | L_DELAWA | 1 | 35 | 0.20272 | west | 0.21928 | 0.20491 | 0.0033793 | 0.21073 | 0.0033793 | west | N | 0.0033793 | 0
7038 | L_DELAWA | 2 | 30 | 0.20272 | west | 0.21928 | 0.20491 | 0.0033793 | 0.21073 | 0.0033793 | west | N | 0.0033793 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.004322 | south | 0.012243 | -0.0021317 | -0.20366 | 0.0036961 | 0.0021317 | south | N | 0.0021317 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.004322 | south | 0.012243 | -0.0021317 | -0.20366 | 0.0036961 | 0.0021317 | south | N | 0.0021317 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.004322 | south | 0.012243 | -0.0021317 | -0.20366 | 0.0036961 | 0.0021317 | south | N | 0.0021317 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.004322 | south | 0.012243 | -0.0021317 | -0.20366 | 0.0036961 | 0.0021317 | south | N | 0.0021317 | 0
7487 | L_CANYHY | 1 | 6 | -0.002052 | south | 0.014513 | 0.00013832 | -0.20139 | 0.0059661 | 0.00013832 | south | N | 0.00013832 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.002337 | south | 0.014228 | -0.00014668 | -0.20167 | 0.0056811 | 0.00014668 | south | N | 0.00014668 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.002337 | south | 0.014228 | -0.00014668 | -0.20167 | 0.0056811 | 0.00014668 | south | N | 0.00014668 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.002337 | south | 0.014228 | -0.00014668 | -0.20167 | 0.0056811 | 0.00014668 | south | N | 0.00014668 | 0
7609 | L_SCHUMA | 1 | 4 | -0.002018 | south | 0.014547 | 0.00017232 | -0.20135 | 0.0060001 | 0.00017232 | south | N | 0.00017232 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.00267 | south | 0.013895 | -0.00047968 | -0.20201 | 0.0053481 | 0.00047968 | south | N | 0.00047968 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.00267 | south | 0.013895 | -0.00047968 | -0.20201 | 0.0053481 | 0.00047968 | south | N | 0.00047968 | 0
7800 | L_GUADGE | 1 | 147 | -0.002147 | south | 0.014418 | 4.3315e-05 | -0.20148 | 0.0058711 | 4.3315e-05 | south | N | 4.3315e-05 | 0
7801 | L_GUADGE | 2 | 138 | -0.002147 | south | 0.014418 | 4.3315e-05 | -0.20148 | 0.0058711 | 4.3315e-05 | south | N | 4.3315e-05 | 0
7802 | L_GUADGE | 3 | 140 | -0.002147 | south | 0.014418 | 4.3315e-05 | -0.20148 | 0.0058711 | 4.3315e-05 | south | N | 4.3315e-05 | 0
7803 | L_GUADGE | 4 | 147 | -0.002147 | south | 0.014418 | 4.3315e-05 | -0.20148 | 0.0058711 | 4.3315e-05 | south | N | 4.3315e-05 | 0
7804 | L_GUADGE | 5 | 182 | -0.002147 | south | 0.014418 | 4.3315e-05 | -0.20148 | 0.0058711 | 4.3315e-05 | south | N | 4.3315e-05 | 0
7805 | L_GUADGE | 6 | 198 | -0.002147 | south | 0.014418 | 4.3315e-05 | -0.20148 | 0.0058711 | 4.3315e-05 | south | N | 4.3315e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.004066 | south | 0.012499 | -0.0018757 | -0.2034 | 0.0039521 | 0.0018757 | south | N | 0.0018757 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.004066 | south | 0.012499 | -0.0018757 | -0.2034 | 0.0039521 | 0.0018757 | south | N | 0.0018757 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.004066 | south | 0.012499 | -0.0018757 | -0.2034 | 0.0039521 | 0.0018757 | south | N | 0.0018757 | 0
7810 | L_RIONOG | 1 | 142 | -0.002344 | south | 0.014221 | -0.00015368 | -0.20168 | 0.0056741 | 0.00015368 | south | N | 0.00015368 | 0
7811 | L_RIONOG | 2 | 145 | -0.002344 | south | 0.014221 | -0.00015368 | -0.20168 | 0.0056741 | 0.00015368 | south | N | 0.00015368 | 0
7812 | L_RIONOG | 3 | 151 | -0.002344 | south | 0.014221 | -0.00015368 | -0.20168 | 0.0056741 | 0.00015368 | south | N | 0.00015368 | 0
7813 | L_RIONOG | 4 | 290 | -0.002344 | south | 0.014221 | -0.00015368 | -0.20168 | 0.0056741 | 0.00015368 | south | N | 0.00015368 | 0
8032 | AMISTADH | 1 | 33 | 0.055041 | south | 0.071606 | 0.057231 | -0.14429 | 0.063059 | 0.057231 | south | N | 0.057231 | 0
8033 | AMISTADH | 2 | 25 | 0.055041 | south | 0.071606 | 0.057231 | -0.14429 | 0.063059 | 0.057231 | south | N | 0.057231 | 0
8048 | FALCONHY | 1 | 12 | 3e-05 | south | 0.016595 | 0.0022203 | -0.19931 | 0.0080481 | 0.0022203 | south | N | 0.0022203 | 0
8066 | DUP1V#1 | 1 | 73 | -0.00293 | south | 0.013635 | -0.00073968 | -0.20227 | 0.0050881 | 0.00073968 | south | N | 0.00073968 | 0
8134 | FOR69CG0 | 1 | 79 | -0.003468 | south | 0.013097 | -0.0012777 | -0.2028 | 0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8138 | FOR69CG0 | 2 | 81 | -0.003468 | south | 0.013097 | -0.0012777 | -0.2028 | 0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8139 | JOS #1 | MB | 255 | 0 | south | 0.016565 | 0.0021903 | -0.19934 | 0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8147 | UCAR #2 | 10 | 28 | -0.003113 | south | 0.013452 | -0.00092268 | -0.20245 | 0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
8148 | UCAR #1 | 2 | 7 | -0.003113 | south | 0.013452 | -0.00092268 | -0.20245 | 0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
8153 | FOR69CG0 | 3 | 79 | -0.003468 | south | 0.013097 | -0.0012777 | -0.2028 | 0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8154 | FOR69CG0 | 4 | 80 | -0.003468 | south | 0.013097 | -0.0012777 | -0.2028 | 0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.003468 | south | 0.013097 | -0.0012777 | -0.2028 | 0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8156 | FOR69CG0 | 6 | 25 | -0.003468 | south | 0.013097 | -0.0012777 | -0.2028 | 0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8157 | FOR69CG0 | 7 | 46 | -0.003468 | south | 0.013097 | -0.0012777 | -0.2028 | 0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8161 | COLETOU1 | 1 | 629 | -0.002193 | south | 0.014372 | -2.6848e-06 | -0.20153 | 0.0058251 | 2.6848e-06 | south | N | 2.6848e-06 | 0
8173 | VICEC51A | 5 | 144 | -0.002853 | south | 0.013712 | -0.00066268 | -0.20219 | 0.0051651 | 0.00066268 | south | N | 0.00066268 | 0
8174 | VICEC61A | 6 | 188 | -0.002853 | south | 0.013712 | -0.00066268 | -0.20219 | 0.0051651 | 0.00066268 | south | N | 0.00066268 | 0
8189 | CUERO 2 | 1 | 12 | -0.002687 | south | 0.013878 | -0.00049668 | -0.20202 | 0.0053311 | 0.00049668 | south | N | 0.00049668 | 0
8262 | ELPS | 1 | 6 | 0.039493 | south | 0.056058 | 0.041683 | -0.15984 | 0.047511 | 0.041683 | south | N | 0.041683 | 0
8285 | LAR #1 | MB | 32 | 0 | south | 0.016565 | 0.0021903 | -0.19934 | 0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8287 | LAR #2 | MB | 32 | 0 | south | 0.016565 | 0.0021903 | -0.19934 | 0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8288 | LAR #3 | MB | 105 | 0 | south | 0.016565 | 0.0021903 | -0.19934 | 0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8388 | BATES0A | MB | 70 | 0 | south | 0.016565 | 0.0021903 | -0.19934 | 0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8393 | BATES0B | MB | 110 | 0 | south | 0.016565 | 0.0021903 | -0.19934 | 0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8442 | NBEC71A | 1 | 336 | -0.002186 | south | 0.014379 | 4.3152e-06 | -0.20152 | 0.0058321 | 4.3152e-06 | south | N | 4.3152e-06 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | 0.016565 | 0.0021903 | -0.19934 | 0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | 0.016565 | 0.0021903 | -0.19934 | 0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.002157 | south | 0.014408 | 3.3315e-05 | -0.20149 | 0.0058611 | 3.3315e-05 | south | N | 3.3315e-05 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.002157 | south | 0.014408 | 3.3315e-05 | -0.20149 | 0.0058611 | 3.3315e-05 | south | N | 3.3315e-05 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.002119 | south | 0.014446 | 7.1315e-05 | -0.20145 | 0.0058991 | 7.1315e-05 | south | N | 7.1315e-05 | 0
8506 | VAL #1 | 1 | 25 | -0.002139 | south | 0.014426 | 5.1315e-05 | -0.20147 | 0.0058791 | 5.1315e-05 | south | N | 5.1315e-05 | 0
8507 | VAL #2 | 2 | 25 | -0.002139 | south | 0.014426 | 5.1315e-05 | -0.20147 | 0.0058791 | 5.1315e-05 | south | N | 5.1315e-05 | 0
8511 | OXY_CC0A | 1 | 38 | -0.002137 | south | 0.014428 | 5.3315e-05 | -0.20147 | 0.0058811 | 5.3315e-05 | south | N | 5.3315e-05 | 0
8517 | CELANEBI | 1 | 29 | -0.002041 | south | 0.014524 | 0.00014932 | -0.20138 | 0.0059771 | 0.00014932 | south | N | 0.00014932 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.002185 | south | 0.01438 | 5.3152e-06 | -0.20152 | 0.0058331 | 5.3152e-06 | south | N | 5.3152e-06 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.002185 | south | 0.01438 | 5.3152e-06 | -0.20152 | 0.0058331 | 5.3152e-06 | south | N | 5.3152e-06 | 0
8562 | CNOPST1 | 3 | 153 | -0.002185 | south | 0.01438 | 5.3152e-06 | -0.20152 | 0.0058331 | 5.3152e-06 | south | N | 5.3152e-06 | 0
8926 | LGE_GT10 | 1 | 158 | -0.002338 | south | 0.014227 | -0.00014768 | -0.20167 | 0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
8927 | LGE_GT20 | 2 | 153 | -0.002338 | south | 0.014227 | -0.00014768 | -0.20167 | 0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
8928 | LGE_STG0 | 3 | 100 | -0.002338 | south | 0.014227 | -0.00014768 | -0.20167 | 0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
8930 | ICPGN10A | 1 | 145 | -0.002338 | south | 0.014227 | -0.00014768 | -0.20167 | 0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
8931 | ICPGN20A | 2 | 147 | -0.002338 | south | 0.014227 | -0.00014768 | -0.20167 | 0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
8932 | ICPGN30A | 3 | 127 | -0.002338 | south | 0.014227 | -0.00014768 | -0.20167 | 0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.001499 | south | 0.015066 | 0.00069132 | -0.20083 | 0.0065191 | 0.00069132 | south | N | 0.00069132 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.001499 | south | 0.015066 | 0.00069132 | -0.20083 | 0.0065191 | 0.00069132 | south | N | 0.00069132 | 0
8935 | FGNTS201 | 3 | 173 | -0.001499 | south | 0.015066 | 0.00069132 | -0.20083 | 0.0065191 | 0.00069132 | south | N | 0.00069132 | 0
8936 | MVGN#1 | 1 | 207 | -0.001754 | south | 0.014811 | 0.00043632 | -0.20109 | 0.0062641 | 0.00043632 | south | N | 0.00043632 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.001754 | south | 0.014811 | 0.00043632 | -0.20109 | 0.0062641 | 0.00043632 | south | N | 0.00043632 | 0
8938 | MVGN#3 | 3 | 242 | -0.001754 | south | 0.014811 | 0.00043632 | -0.20109 | 0.0062641 | 0.00043632 | south | N | 0.00043632 | 0
8981 | HECN1 | 1 | 144 | -0.001754 | south | 0.014811 | 0.00043632 | -0.20109 | 0.0062641 | 0.00043632 | south | N | 0.00043632 | 0
8982 | HECN2 | 2 | 144 | -0.001754 | south | 0.014811 | 0.00043632 | -0.20109 | 0.0062641 | 0.00043632 | south | N | 0.00043632 | 0
8983 | HECN3 | 3 | 171 | -0.001754 | south | 0.014811 | 0.00043632 | -0.20109 | 0.0062641 | 0.00043632 | south | N | 0.00043632 | 0
9000 | DECKR_G1 | 1 | 310 | -0.003479 | south | 0.013086 | -0.0012887 | -0.20281 | 0.0045391 | 0.0012887 | south | N | 0.0012887 | 0
9001 | DECKR_G2 | 2 | 413 | -0.003479 | south | 0.013086 | -0.0012887 | -0.20281 | 0.0045391 | 0.0012887 | south | N | 0.0012887 | 0
9002 | DECKR_G3 | 3 | 42 | -0.00364 | south | 0.012925 | -0.0014497 | -0.20298 | 0.0043781 | 0.0014497 | south | N | 0.0014497 | 0
9003 | DECKR_G4 | 4 | 44 | -0.00364 | south | 0.012925 | -0.0014497 | -0.20298 | 0.0043781 | 0.0014497 | south | N | 0.0014497 | 0
9004 | DECKR_G5 | 5 | 44 | -0.00364 | south | 0.012925 | -0.0014497 | -0.20298 | 0.0043781 | 0.0014497 | south | N | 0.0014497 | 0
9005 | DECKR_G6 | 6 | 47 | -0.00364 | south | 0.012925 | -0.0014497 | -0.20298 | 0.0043781 | 0.0014497 | south | N | 0.0014497 | 0
9016 | SANDH_G1 | 1 | 49 | -0.003432 | south | 0.013133 | -0.0012417 | -0.20277 | 0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9017 | SANDH_G2 | 2 | 46 | -0.003432 | south | 0.013133 | -0.0012417 | -0.20277 | 0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9018 | SANDH_G3 | 3 | 46 | -0.003432 | south | 0.013133 | -0.0012417 | -0.20277 | 0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9019 | SANDH_G4 | 4 | 47 | -0.003432 | south | 0.013133 | -0.0012417 | -0.20277 | 0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9020 | SANDHG5A | 5A | 154 | -0.003432 | south | 0.013133 | -0.0012417 | -0.20277 | 0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9021 | SANDHG5C | 5C | 148 | -0.003432 | south | 0.013133 | -0.0012417 | -0.20277 | 0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9022 | SANDH_G6 | 6 | 48 | -0.003432 | south | 0.013133 | -0.0012417 | -0.20277 | 0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9023 | SANDH_G7 | 7 | 48 | -0.003432 | south | 0.013133 | -0.0012417 | -0.20277 | 0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
11001 | NAV1CT | 1 | 70 | 0.20505 | west | 0.22161 | 0.20724 | 0.0057133 | 0.21307 | 0.0057133 | west | N | 0.0057133 | 0
11009 | NAV2CT | 1 | 70 | 0.20505 | west | 0.22161 | 0.20724 | 0.0057133 | 0.21307 | 0.0057133 | west | N | 0.0057133 | 0
11011 | NAV3ST | 1 | 92.8 | 0.20505 | west | 0.22161 | 0.20724 | 0.0057133 | 0.21307 | 0.0057133 | west | N | 0.0057133 | 0
11012 | NAV4CT | 1 | 80 | 0.20505 | west | 0.22161 | 0.20724 | 0.0057133 | 0.21307 | 0.0057133 | west | N | 0.0057133 | 0
11013 | NAV5CT | 1 | 80 | 0.20505 | west | 0.22161 | 0.20724 | 0.0057133 | 0.21307 | 0.0057133 | west | N | 0.0057133 | 0
11014 | NAV6ST | 1 | 115 | 0.20505 | west | 0.22161 | 0.20724 | 0.0057133 | 0.21307 | 0.0057133 | west | N | 0.0057133 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.20503 | west | 0.22159 | 0.20722 | 0.0056913 | 0.21305 | 0.0056913 | west | N | 0.0056913 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.20503 | west | 0.22159 | 0.20722 | 0.0056913 | 0.21305 | 0.0056913 | west | N | 0.0056913 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.20503 | west | 0.22159 | 0.20722 | 0.0056913 | 0.21305 | 0.0056913 | west | N | 0.0056913 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.20503 | west | 0.22159 | 0.20722 | 0.0056913 | 0.21305 | 0.0056913 | west | N | 0.0056913 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.20503 | west | 0.22159 | 0.20722 | 0.0056913 | 0.21305 | 0.0056913 | west | N | 0.0056913 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.20503 | west | 0.22159 | 0.20722 | 0.0056913 | 0.21305 | 0.0056913 | west | N | 0.0056913 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.17314 | west | 0.18971 | 0.17533 | -0.026194 | 0.18116 | 0.026194 | west | N | 0.026194 | 0
11057 | CHAMPION | 1 | 126.5 | 0.17314 | west | 0.18971 | 0.17533 | -0.026194 | 0.18116 | 0.026194 | west | N | 0.026194 | 0
11058 | PYRON_1G | 1 | 249 | 0.17314 | west | 0.18971 | 0.17533 | -0.026194 | 0.18116 | 0.026194 | west | N | 0.026194 | 0
11059 | INADALE_ | 1 | 197 | 0.17314 | west | 0.18971 | 0.17533 | -0.026194 | 0.18116 | 0.026194 | west | N | 0.026194 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.20706 | west | 0.22363 | 0.20926 | 0.0077293 | 0.21508 | 0.0077293 | west | N | 0.0077293 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.20706 | west | 0.22363 | 0.20926 | 0.0077293 | 0.21508 | 0.0077293 | west | N | 0.0077293 | 0
11147 | NOTREES_ | 1 | 149 | 0.20276 | west | 0.21932 | 0.20495 | 0.0034223 | 0.21078 | 0.0034223 | west | N | 0.0034223 | 0
11309 | BULLCREK | 1 | 180 | 0.20255 | west | 0.21911 | 0.20474 | 0.0032113 | 0.21057 | 0.0032113 | west | N | 0.0032113 | 0
11310 | BULLCREK | 1 | 180 | 0.20255 | west | 0.21911 | 0.20474 | 0.0032113 | 0.21057 | 0.0032113 | west | N | 0.0032113 | 0
11320 | COYOTE_1 | 1 | 225 | 0.20257 | west | 0.21913 | 0.20476 | 0.0032333 | 0.21059 | 0.0032333 | west | N | 0.0032333 | 0
11415 | LORAINE_ | 1 | 125 | 0.22138 | west | 0.23794 | 0.22357 | 0.022043 | 0.2294 | 0.022043 | west | N | 0.022043 | 0
11416 | LORAINE_ | 1 | 125 | 0.22138 | west | 0.23794 | 0.22357 | 0.022043 | 0.2294 | 0.022043 | west | N | 0.022043 | 0
11691 | KMICHICT | 1 | 140 | -0.019084 | north | -0.0025193 | -0.016894 | -0.21842 | -0.011066 | 0.0025193 | North | N | 0.0025193 | 0
11692 | KMICHICT | 2 | 141 | -0.019084 | north | -0.0025193 | -0.016894 | -0.21842 | -0.011066 | 0.0025193 | North | N | 0.0025193 | 0
11693 | KMICHIST | 3 | 309 | -0.019084 | north | -0.0025193 | -0.016894 | -0.21842 | -0.011066 | 0.0025193 | North | N | 0.0025193 | 0
11694 | KMICHICT | 4 | 143 | -0.019084 | north | -0.0025193 | -0.016894 | -0.21842 | -0.011066 | 0.0025193 | North | N | 0.0025193 | 0
11695 | KMICHICT | 5 | 144 | -0.019084 | north | -0.0025193 | -0.016894 | -0.21842 | -0.011066 | 0.0025193 | North | N | 0.0025193 | 0
11696 | KMICHIST | 6 | 310 | -0.019084 | north | -0.0025193 | -0.016894 | -0.21842 | -0.011066 | 0.0025193 | North | N | 0.0025193 | 0
12322 | ENNSTRAC | 1 | 196 | -0.015849 | north | 0.00071568 | -0.013659 | -0.21518 | -0.0078309 | 0.00071568 | North | N | 0.00071568 | 0
12323 | ENNSTRAC | 2 | 111 | -0.015849 | north | 0.00071568 | -0.013659 | -0.21518 | -0.0078309 | 0.00071568 | North | N | 0.00071568 | 0
12357 | RNRTPL_1 | 1 | 0 | -0.019332 | north | -0.0027673 | -0.017142 | -0.21867 | -0.011314 | 0.0027673 | North | N | 0.0027673 | 0
12411 | FPLEFR1A | 1 | 161 | -0.017982 | north | -0.0014173 | -0.015792 | -0.21732 | -0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12412 | FPLEFR1B | 2 | 164 | -0.017982 | north | -0.0014173 | -0.015792 | -0.21732 | -0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12413 | FPLEFR1C | 3 | 164 | -0.017982 | north | -0.0014173 | -0.015792 | -0.21732 | -0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12414 | FPLEFR1S | 4 | 414 | -0.017982 | north | -0.0014173 | -0.015792 | -0.21732 | -0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12421 | FPLEFR2A | 1 | 162 | -0.017982 | north | -0.0014173 | -0.015792 | -0.21732 | -0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12422 | FPLEFR2B | 2 | 161 | -0.017982 | north | -0.0014173 | -0.015792 | -0.21732 | -0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12423 | FPLEFR2C | 3 | 163 | -0.017982 | north | -0.0014173 | -0.015792 | -0.21732 | -0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12424 | FPLEFR2S | 4 | 409 | -0.017982 | north | -0.0014173 | -0.015792 | -0.21732 | -0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12440 | PARKD_1S | 1 | 0 | -0.017938 | north | -0.0013733 | -0.015748 | -0.21727 | -0.0099199 | 0.0013733 | North | N | 0.0013733 | 0
12449 | PARKD_2S | 1 | 0 | -0.017938 | north | -0.0013733 | -0.015748 | -0.21727 | -0.0099199 | 0.0013733 | North | N | 0.0013733 | 0
13116 | TGATEWAY | 1 | 148 | -0.01659 | north | -2.5321e-05 | -0.0144 | -0.21593 | -0.0085719 | 2.5321e-05 | North | N | 2.5321e-05 | 0
13117 | TGATEWAY | 2 | 130 | -0.01659 | north | -2.5321e-05 | -0.0144 | -0.21593 | -0.0085719 | 2.5321e-05 | North | N | 2.5321e-05 | 0
13118 | TGATEWAY | 3 | 145 | -0.01659 | north | -2.5321e-05 | -0.0144 | -0.21593 | -0.0085719 | 2.5321e-05 | North | N | 2.5321e-05 | 0
13119 | TGATEWAY | 4 | 399 | -0.01659 | north | -2.5321e-05 | -0.0144 | -0.21593 | -0.0085719 | 2.5321e-05 | North | N | 2.5321e-05 | 0
13131 | CALFREST | 1 | 150.7 | -0.014971 | north | 0.0015937 | -0.012781 | -0.21431 | -0.0069529 | 0.0015937 | North | N | 0.0015937 | 0
13132 | CALFREST | 2 | 151 | -0.014971 | north | 0.0015937 | -0.012781 | -0.21431 | -0.0069529 | 0.0015937 | North | N | 0.0015937 | 0
13133 | CALFREST | 3 | 177.4 | -0.014971 | north | 0.0015937 | -0.012781 | -0.21431 | -0.0069529 | 0.0015937 | North | N | 0.0015937 | 0
13134 | CALFREST | 4 | 151.5 | -0.015031 | north | 0.0015337 | -0.012841 | -0.21437 | -0.0070129 | 0.0015337 | North | N | 0.0015337 | 0
13135 | CALFREST | 5 | 152.3 | -0.015031 | north | 0.0015337 | -0.012841 | -0.21437 | -0.0070129 | 0.0015337 | North | N | 0.0015337 | 0
13136 | CALFREST | 6 | 177.5 | -0.015031 | north | 0.0015337 | -0.012841 | -0.21437 | -0.0070129 | 0.0015337 | North | N | 0.0015337 | 0
13432 | SANDOW_5 | 5 | 581 | -0.006219 | south | 0.010346 | -0.0040287 | -0.20555 | 0.0017991 | 0.0017991 | houston | Y | 0.0040287 | 1.2954
13691 | OAKGROVE | 1 | 855 | -0.012623 | north | 0.0039417 | -0.010433 | -0.21196 | -0.0046049 | 0.0039417 | North | N | 0.0039417 | 0
13692 | OAKGROVE | 2 | 855 | -0.012623 | north | 0.0039417 | -0.010433 | -0.21196 | -0.0046049 | 0.0039417 | North | N | 0.0039417 | 0
32798 | BRYN_TAM | 1 | 32 | -0.01123 | north | 0.0053347 | -0.0090397 | -0.21057 | -0.0032119 | 0.0032119 | houston | Y | 0.0053347 | 0.067929
32883 | BRYN_DNS | 1 | 48 | -0.0112 | north | 0.0053647 | -0.0090097 | -0.21054 | -0.0031819 | 0.0031819 | houston | Y | 0.0053647 | 0.10477
32884 | BRYN_DNS | 1 | 46 | -0.0112 | north | 0.0053647 | -0.0090097 | -0.21054 | -0.0031819 | 0.0031819 | houston | Y | 0.0053647 | 0.10041
32886 | BRYN_ATK | MB | 12 | -0.011239 | north | 0.0053257 | -0.0090487 | -0.21057 | -0.0032209 | 0.0032209 | houston | Y | 0.0053257 | 0.025257
32887 | BRYN_ATK | MB | 51 | -0.011239 | north | 0.0053257 | -0.0090487 | -0.21057 | -0.0032209 | 0.0032209 | houston | Y | 0.0053257 | 0.10734
32888 | BRYN_ATK | 1 | 17 | -0.011239 | north | 0.0053257 | -0.0090487 | -0.21057 | -0.0032209 | 0.0032209 | houston | Y | 0.0053257 | 0.035781
32890 | BRYN_ATK | MB | 22 | -0.011239 | north | 0.0053257 | -0.0090487 | -0.21057 | -0.0032209 | 0.0032209 | houston | Y | 0.0053257 | 0.046305
32891 | BRYN_ATK | MB | 25 | -0.011239 | north | 0.0053257 | -0.0090487 | -0.21057 | -0.0032209 | 0.0032209 | houston | Y | 0.0053257 | 0.052619
32892 | BRYN_DNS | 1 | 105 | -0.0112 | north | 0.0053647 | -0.0090097 | -0.21054 | -0.0031819 | 0.0031819 | houston | Y | 0.0053647 | 0.22919
36998 | RDCNYNG1 | 1 | 84 | 0.1991 | west | 0.21566 | 0.20129 | -0.00023672 | 0.20712 | 0.00023672 | west | N | 0.00023672 | 0
38332 | WDWRDU2 | 1 | 80 | 0.1917 | west | 0.20826 | 0.19389 | -0.0076387 | 0.19972 | 0.0076387 | west | N | 0.0076387 | 0
38437 | TNSRBNMS | 1 | 150 | 0.1916 | west | 0.20816 | 0.19379 | -0.0077397 | 0.19961 | 0.0077397 | west | N | 0.0077397 | 0
38438 | TNSRBNMS | 1 | 150 | 0.1916 | west | 0.20816 | 0.19379 | -0.0077397 | 0.19961 | 0.0077397 | west | N | 0.0077397 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.007934 | houston | 0.0086307 | -0.0057437 | -0.20727 | 8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.007934 | houston | 0.0086307 | -0.0057437 | -0.20727 | 8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38600 | TNBP_CGN | 5 | 53 | -0.007934 | houston | 0.0086307 | -0.0057437 | -0.20727 | 8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.007934 | houston | 0.0086307 | -0.0057437 | -0.20727 | 8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.007934 | houston | 0.0086307 | -0.0057437 | -0.20727 | 8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.007934 | houston | 0.0086307 | -0.0057437 | -0.20727 | 8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38614 | TNBPAMCG | 4 | 96 | -0.007934 | houston | 0.0086307 | -0.0057437 | -0.20727 | 8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38615 | TNBPAMCG | 1 | 244 | -0.007934 | houston | 0.0086307 | -0.0057437 | -0.20727 | 8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38690 | TNBP_CGN | 3 | 40 | -0.007934 | houston | 0.0086307 | -0.0057437 | -0.20727 | 8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.007933 | houston | 0.0086317 | -0.0057427 | -0.20727 | 8.5088e-05 | 8.5088e-05 | houston | N | 8.5088e-05 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.007933 | houston | 0.0086317 | -0.0057427 | -0.20727 | 8.5088e-05 | 8.5088e-05 | houston | N | 8.5088e-05 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.007933 | houston | 0.0086317 | -0.0057427 | -0.20727 | 8.5088e-05 | 8.5088e-05 | houston | N | 8.5088e-05 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.007933 | houston | 0.0086317 | -0.0057427 | -0.20727 | 8.5088e-05 | 8.5088e-05 | houston | N | 8.5088e-05 | 0
39470 | TNDOWCGN | 1 | 32 | -0.007933 | houston | 0.0086317 | -0.0057427 | -0.20727 | 8.5088e-05 | 8.5088e-05 | houston | N | 8.5088e-05 | 0
39480 | TNDOWCGN | 1 | 30 | -0.007933 | houston | 0.0086317 | -0.0057427 | -0.20727 | 8.5088e-05 | 8.5088e-05 | houston | N | 8.5088e-05 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.007199 | houston | 0.0093657 | -0.0050087 | -0.20653 | 0.00081909 | 0.00081909 | houston | N | 0.00081909 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.007199 | houston | 0.0093657 | -0.0050087 | -0.20653 | 0.00081909 | 0.00081909 | houston | N | 0.00081909 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.007199 | houston | 0.0093657 | -0.0050087 | -0.20653 | 0.00081909 | 0.00081909 | houston | N | 0.00081909 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.007199 | houston | 0.0093657 | -0.0050087 | -0.20653 | 0.00081909 | 0.00081909 | houston | N | 0.00081909 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.012623 | north | 0.0039417 | -0.010433 | -0.21196 | -0.0046049 | 0.0039417 | North | N | 0.0039417 | 0
39970 | TNTNPONE | 1 | 153 | -0.012623 | north | 0.0039417 | -0.010433 | -0.21196 | -0.0046049 | 0.0039417 | North | N | 0.0039417 | 0
48500 | APD_GT1_ | 1 | 136 | -0.008373 | houston | 0.0081917 | -0.0061827 | -0.20771 | -0.00035491 | 0.00035491 | houston | N | 0.00035491 | 0
48510 | AK_GT1__ | 1 | 33 | -0.007689 | houston | 0.0088757 | -0.0054987 | -0.20702 | 0.00032909 | 0.00032909 | houston | N | 0.00032909 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.008372 | houston | 0.0081927 | -0.0061817 | -0.20771 | -0.00035391 | 0.00035391 | houston | N | 0.00035391 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.008372 | houston | 0.0081927 | -0.0061817 | -0.20771 | -0.00035391 | 0.00035391 | houston | N | 0.00035391 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.008372 | houston | 0.0081927 | -0.0061817 | -0.20771 | -0.00035391 | 0.00035391 | houston | N | 0.00035391 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.008372 | houston | 0.0081927 | -0.0061817 | -0.20771 | -0.00035391 | 0.00035391 | houston | N | 0.00035391 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.007066 | houston | 0.0094987 | -0.0048757 | -0.2064 | 0.00095209 | 0.00095209 | houston | N | 0.00095209 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.007066 | houston | 0.0094987 | -0.0048757 | -0.2064 | 0.00095209 | 0.00095209 | houston | N | 0.00095209 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.00767 | houston | 0.0088947 | -0.0054797 | -0.20701 | 0.00034809 | 0.00034809 | houston | N | 0.00034809 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.00767 | houston | 0.0088947 | -0.0054797 | -0.20701 | 0.00034809 | 0.00034809 | houston | N | 0.00034809 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.00767 | houston | 0.0088947 | -0.0054797 | -0.20701 | 0.00034809 | 0.00034809 | houston | N | 0.00034809 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.008207 | houston | 0.0083577 | -0.0060167 | -0.20754 | -0.00018891 | 0.00018891 | houston | N | 0.00018891 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.008207 | houston | 0.0083577 | -0.0060167 | -0.20754 | -0.00018891 | 0.00018891 | houston | N | 0.00018891 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.008207 | houston | 0.0083577 | -0.0060167 | -0.20754 | -0.00018891 | 0.00018891 | houston | N | 0.00018891 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.008207 | houston | 0.0083577 | -0.0060167 | -0.20754 | -0.00018891 | 0.00018891 | houston | N | 0.00018891 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.008313 | houston | 0.0082517 | -0.0061227 | -0.20765 | -0.00029491 | 0.00029491 | houston | N | 0.00029491 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.008313 | houston | 0.0082517 | -0.0061227 | -0.20765 | -0.00029491 | 0.00029491 | houston | N | 0.00029491 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.008175 | houston | 0.0083897 | -0.0059847 | -0.20751 | -0.00015691 | 0.00015691 | houston | N | 0.00015691 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.008175 | houston | 0.0083897 | -0.0059847 | -0.20751 | -0.00015691 | 0.00015691 | houston | N | 0.00015691 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.008175 | houston | 0.0083897 | -0.0059847 | -0.20751 | -0.00015691 | 0.00015691 | houston | N | 0.00015691 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.008175 | houston | 0.0083897 | -0.0059847 | -0.20751 | -0.00015691 | 0.00015691 | houston | N | 0.00015691 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.008175 | houston | 0.0083897 | -0.0059847 | -0.20751 | -0.00015691 | 0.00015691 | houston | N | 0.00015691 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.008502 | houston | 0.0080627 | -0.0063117 | -0.20784 | -0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.008449 | houston | 0.0081157 | -0.0062587 | -0.20778 | -0.00043091 | 0.00043091 | houston | N | 0.00043091 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.008517 | houston | 0.0080477 | -0.0063267 | -0.20785 | -0.00049891 | 0.00049891 | houston | N | 0.00049891 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.008517 | houston | 0.0080477 | -0.0063267 | -0.20785 | -0.00049891 | 0.00049891 | houston | N | 0.00049891 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.008517 | houston | 0.0080477 | -0.0063267 | -0.20785 | -0.00049891 | 0.00049891 | houston | N | 0.00049891 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.008814 | houston | 0.0077507 | -0.0066237 | -0.20815 | -0.00079591 | 0.00079591 | houston | N | 0.00079591 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.008383 | houston | 0.0081817 | -0.0061927 | -0.20772 | -0.00036491 | 0.00036491 | houston | N | 0.00036491 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.008383 | houston | 0.0081817 | -0.0061927 | -0.20772 | -0.00036491 | 0.00036491 | houston | N | 0.00036491 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.008555 | houston | 0.0080097 | -0.0063647 | -0.20789 | -0.00053691 | 0.00053691 | houston | N | 0.00053691 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.008555 | houston | 0.0080097 | -0.0063647 | -0.20789 | -0.00053691 | 0.00053691 | houston | N | 0.00053691 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.008555 | houston | 0.0080097 | -0.0063647 | -0.20789 | -0.00053691 | 0.00053691 | houston | N | 0.00053691 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.008555 | houston | 0.0080097 | -0.0063647 | -0.20789 | -0.00053691 | 0.00053691 | houston | N | 0.00053691 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.008317 | houston | 0.0082477 | -0.0061267 | -0.20765 | -0.00029891 | 0.00029891 | houston | N | 0.00029891 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.008317 | houston | 0.0082477 | -0.0061267 | -0.20765 | -0.00029891 | 0.00029891 | houston | N | 0.00029891 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.008317 | houston | 0.0082477 | -0.0061267 | -0.20765 | -0.00029891 | 0.00029891 | houston | N | 0.00029891 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.008317 | houston | 0.0082477 | -0.0061267 | -0.20765 | -0.00029891 | 0.00029891 | houston | N | 0.00029891 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.008279 | houston | 0.0082857 | -0.0060887 | -0.20761 | -0.00026091 | 0.00026091 | houston | N | 0.00026091 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.008279 | houston | 0.0082857 | -0.0060887 | -0.20761 | -0.00026091 | 0.00026091 | houston | N | 0.00026091 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.008279 | houston | 0.0082857 | -0.0060887 | -0.20761 | -0.00026091 | 0.00026091 | houston | N | 0.00026091 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.008279 | houston | 0.0082857 | -0.0060887 | -0.20761 | -0.00026091 | 0.00026091 | houston | N | 0.00026091 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.008279 | houston | 0.0082857 | -0.0060887 | -0.20761 | -0.00026091 | 0.00026091 | houston | N | 0.00026091 | 0
48651 | EP_1_2 | 1 | 5 | -0.0085 | houston | 0.0080647 | -0.0063097 | -0.20784 | -0.00048191 | 0.00048191 | houston | N | 0.00048191 | 0
48651 | EP_1_2 | 2 | 21 | -0.0085 | houston | 0.0080647 | -0.0063097 | -0.20784 | -0.00048191 | 0.00048191 | houston | N | 0.00048191 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.010836 | north | 0.0057287 | -0.0086457 | -0.21017 | -0.0028179 | 0.0028179 | houston | Y | 0.0057287 | 0.44884
48672 | FTR_GT2_ | 2 | 156 | -0.010836 | north | 0.0057287 | -0.0086457 | -0.21017 | -0.0028179 | 0.0028179 | houston | Y | 0.0057287 | 0.45408
48673 | FTR_GT3_ | 3 | 156 | -0.010836 | north | 0.0057287 | -0.0086457 | -0.21017 | -0.0028179 | 0.0028179 | houston | Y | 0.0057287 | 0.45408
48674 | FTR_CN4_ | 4 | 380 | -0.010836 | north | 0.0057287 | -0.0086457 | -0.21017 | -0.0028179 | 0.0028179 | houston | Y | 0.0057287 | 1.1061
48690 | GBY_GN5_ | 5 | 398 | -0.008572 | houston | 0.0079927 | -0.0063817 | -0.20791 | -0.00055391 | 0.00055391 | houston | N | 0.00055391 | 0
48691 | GBY_7374 | A | 46 | -0.008263 | houston | 0.0083017 | -0.0060727 | -0.2076 | -0.00024491 | 0.00024491 | houston | N | 0.00024491 | 0
48691 | GBY_7374 | B | 46 | -0.008263 | houston | 0.0083017 | -0.0060727 | -0.2076 | -0.00024491 | 0.00024491 | houston | N | 0.00024491 | 0
48692 | GBY_8182 | C | 46 | -0.008263 | houston | 0.0083017 | -0.0060727 | -0.2076 | -0.00024491 | 0.00024491 | houston | N | 0.00024491 | 0
48692 | GBY_8182 | D | 55 | -0.008263 | houston | 0.0083017 | -0.0060727 | -0.2076 | -0.00024491 | 0.00024491 | houston | N | 0.00024491 | 0
48693 | GBY_8384 | E | 55 | -0.008263 | houston | 0.0083017 | -0.0060727 | -0.2076 | -0.00024491 | 0.00024491 | houston | N | 0.00024491 | 0
48693 | GBY_8384 | F | 54 | -0.008263 | houston | 0.0083017 | -0.0060727 | -0.2076 | -0.00024491 | 0.00024491 | houston | N | 0.00024491 | 0
48721 | LEG_1___ | 1 | 827 | -0.013173 | north | 0.0033917 | -0.010983 | -0.21251 | -0.0051549 | 0.0033917 | North | N | 0.0033917 | 0
48722 | LEG_2___ | 2 | 819 | -0.013173 | north | 0.0033917 | -0.010983 | -0.21251 | -0.0051549 | 0.0033917 | North | N | 0.0033917 | 0
48730 | MNS_GT | 1 | 46.1 | -0.007625 | houston | 0.0089397 | -0.0054347 | -0.20696 | 0.00039309 | 0.00039309 | houston | N | 0.00039309 | 0
48731 | CBE_GT1 | 1 | 76 | -0.006156 | houston | 0.010409 | -0.0039657 | -0.20549 | 0.0018621 | 0.0018621 | houston | N | 0.0018621 | 0
48732 | CBE_GT2 | 1 | 76 | -0.006156 | houston | 0.010409 | -0.0039657 | -0.20549 | 0.0018621 | 0.0018621 | houston | N | 0.0018621 | 0
48733 | CBE_ST12 | 1 | 105 | -0.006156 | houston | 0.010409 | -0.0039657 | -0.20549 | 0.0018621 | 0.0018621 | houston | N | 0.0018621 | 0
48734 | CBE_GT3 | 1 | 74 | -0.006156 | houston | 0.010409 | -0.0039657 | -0.20549 | 0.0018621 | 0.0018621 | houston | N | 0.0018621 | 0
48735 | CBE_GT4 | 1 | 74 | -0.006156 | houston | 0.010409 | -0.0039657 | -0.20549 | 0.0018621 | 0.0018621 | houston | N | 0.0018621 | 0
48736 | CBE_ST34 | 1 | 102 | -0.006156 | houston | 0.010409 | -0.0039657 | -0.20549 | 0.0018621 | 0.0018621 | houston | N | 0.0018621 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.008318 | houston | 0.0082467 | -0.0061277 | -0.20765 | -0.00029991 | 0.00029991 | houston | N | 0.00029991 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.008318 | houston | 0.0082467 | -0.0061277 | -0.20765 | -0.00029991 | 0.00029991 | houston | N | 0.00029991 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.008318 | houston | 0.0082467 | -0.0061277 | -0.20765 | -0.00029991 | 0.00029991 | houston | N | 0.00029991 | 0
48761 | PR_GT1__ | 1 | 35 | -0.008297 | houston | 0.0082677 | -0.0061067 | -0.20763 | -0.00027891 | 0.00027891 | houston | N | 0.00027891 | 0
48772 | PHR_GN2_ | MB | 459 | -0.008093 | houston | 0.0084717 | -0.0059027 | -0.20743 | -7.4912e-05 | 7.4912e-05 | houston | N | 7.4912e-05 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.008502 | houston | 0.0080627 | -0.0063117 | -0.20784 | -0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.008502 | houston | 0.0080627 | -0.0063117 | -0.20784 | -0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.008502 | houston | 0.0080627 | -0.0063117 | -0.20784 | -0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.008502 | houston | 0.0080627 | -0.0063117 | -0.20784 | -0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.008502 | houston | 0.0080627 | -0.0063117 | -0.20784 | -0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.008502 | houston | 0.0080627 | -0.0063117 | -0.20784 | -0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.008502 | houston | 0.0080627 | -0.0063117 | -0.20784 | -0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.008814 | houston | 0.0077507 | -0.0066237 | -0.20815 | -0.00079591 | 0.00079591 | houston | N | 0.00079591 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.008814 | houston | 0.0077507 | -0.0066237 | -0.20815 | -0.00079591 | 0.00079591 | houston | N | 0.00079591 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.008814 | houston | 0.0077507 | -0.0066237 | -0.20815 | -0.00079591 | 0.00079591 | houston | N | 0.00079591 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.008814 | houston | 0.0077507 | -0.0066237 | -0.20815 | -0.00079591 | 0.00079591 | houston | N | 0.00079591 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.008514 | houston | 0.0080507 | -0.0063237 | -0.20785 | -0.00049591 | 0.00049591 | houston | N | 0.00049591 | 0
48820 | SHELLG1_ | 1 | 71 | -0.008338 | houston | 0.0082267 | -0.0061477 | -0.20767 | -0.00031991 | 0.00031991 | houston | N | 0.00031991 | 0
48821 | SHELLG2 | 2 | 72 | -0.008338 | houston | 0.0082267 | -0.0061477 | -0.20767 | -0.00031991 | 0.00031991 | houston | N | 0.00031991 | 0
48822 | SHELLG3_ | 1 | 39 | -0.008338 | houston | 0.0082267 | -0.0061477 | -0.20767 | -0.00031991 | 0.00031991 | houston | N | 0.00031991 | 0
48822 | SHELLG3_ | 2 | 30 | -0.008338 | houston | 0.0082267 | -0.0061477 | -0.20767 | -0.00031991 | 0.00031991 | houston | N | 0.00031991 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.008266 | houston | 0.0082987 | -0.0060757 | -0.2076 | -0.00024791 | 0.00024791 | houston | N | 0.00024791 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.008266 | houston | 0.0082987 | -0.0060757 | -0.2076 | -0.00024791 | 0.00024791 | houston | N | 0.00024791 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.008316 | houston | 0.0082487 | -0.0061257 | -0.20765 | -0.00029791 | 0.00029791 | houston | N | 0.00029791 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.008312 | houston | 0.0082527 | -0.0061217 | -0.20765 | -0.00029391 | 0.00029391 | houston | N | 0.00029391 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.008311 | houston | 0.0082537 | -0.0061207 | -0.20765 | -0.00029291 | 0.00029291 | houston | N | 0.00029291 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.008316 | houston | 0.0082487 | -0.0061257 | -0.20765 | -0.00029791 | 0.00029791 | houston | N | 0.00029791 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.008317 | houston | 0.0082477 | -0.0061267 | -0.20765 | -0.00029891 | 0.00029891 | houston | N | 0.00029891 | 0
48855 | SRB_GT21 | B2 | 12 | -0.008311 | houston | 0.0082537 | -0.0061207 | -0.20765 | -0.00029291 | 0.00029291 | houston | N | 0.00029291 | 0
48855 | SRB_GT21 | MB | 18 | -0.008311 | houston | 0.0082537 | -0.0061207 | -0.20765 | -0.00029291 | 0.00029291 | houston | N | 0.00029291 | 0
48865 | TECO_GT1 | 1 | 50 | -0.008037 | houston | 0.0085277 | -0.0058467 | -0.20737 | -1.8912e-05 | 1.8912e-05 | houston | N | 1.8912e-05 | 0
48873 | THW_ST3_ | 3 | 104 | -0.008439 | houston | 0.0081257 | -0.0062487 | -0.20777 | -0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48874 | THW_ST4_ | 4 | 104 | -0.008439 | houston | 0.0081257 | -0.0062487 | -0.20777 | -0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48875 | THW_3132 | A | 54 | -0.008439 | houston | 0.0081257 | -0.0062487 | -0.20777 | -0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48875 | THW_3132 | B | 53 | -0.008439 | houston | 0.0081257 | -0.0062487 | -0.20777 | -0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48877 | THW_3334 | C | 54 | -0.008439 | houston | 0.0081257 | -0.0062487 | -0.20777 | -0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48877 | THW_3334 | D | 57 | -0.008439 | houston | 0.0081257 | -0.0062487 | -0.20777 | -0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48879 | THW_4142 | E | 54 | -0.008439 | houston | 0.0081257 | -0.0062487 | -0.20777 | -0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48879 | THW_4142 | F | 54 | -0.008439 | houston | 0.0081257 | -0.0062487 | -0.20777 | -0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48881 | THW_4344 | G | 58 | -0.008439 | houston | 0.0081257 | -0.0062487 | -0.20777 | -0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48881 | THW_4344 | H | 58 | -0.008439 | houston | 0.0081257 | -0.0062487 | -0.20777 | -0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48883 | THW_GT1_ | B2 | 12 | -0.008487 | houston | 0.0080777 | -0.0062967 | -0.20782 | -0.00046891 | 0.00046891 | houston | N | 0.00046891 | 0
48885 | THW_5152 | A | 56 | -0.008596 | houston | 0.0079687 | -0.0064057 | -0.20793 | -0.00057791 | 0.00057791 | houston | N | 0.00057791 | 0
48885 | THW_5152 | B | 59 | -0.008596 | houston | 0.0079687 | -0.0064057 | -0.20793 | -0.00057791 | 0.00057791 | houston | N | 0.00057791 | 0
48886 | THW_5354 | C | 56 | -0.008596 | houston | 0.0079687 | -0.0064057 | -0.20793 | -0.00057791 | 0.00057791 | houston | N | 0.00057791 | 0
48886 | THW_5354 | D | 56 | -0.008596 | houston | 0.0079687 | -0.0064057 | -0.20793 | -0.00057791 | 0.00057791 | houston | N | 0.00057791 | 0
48887 | THW_5556 | E | 59 | -0.008596 | houston | 0.0079687 | -0.0064057 | -0.20793 | -0.00057791 | 0.00057791 | houston | N | 0.00057791 | 0
48887 | THW_5556 | F | 56 | -0.008596 | houston | 0.0079687 | -0.0064057 | -0.20793 | -0.00057791 | 0.00057791 | houston | N | 0.00057791 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.006258 | houston | 0.010307 | -0.0040677 | -0.20559 | 0.0017601 | 0.0017601 | houston | N | 0.0017601 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.00775 | houston | 0.0088147 | -0.0055597 | -0.20709 | 0.00026809 | 0.00026809 | houston | N | 0.00026809 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.00775 | houston | 0.0088147 | -0.0055597 | -0.20709 | 0.00026809 | 0.00026809 | houston | N | 0.00026809 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.00775 | houston | 0.0088147 | -0.0055597 | -0.20709 | 0.00026809 | 0.00026809 | houston | N | 0.00026809 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.00775 | houston | 0.0088147 | -0.0055597 | -0.20709 | 0.00026809 | 0.00026809 | houston | N | 0.00026809 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.00775 | houston | 0.0088147 | -0.0055597 | -0.20709 | 0.00026809 | 0.00026809 | houston | N | 0.00026809 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.007667 | houston | 0.0088977 | -0.0054767 | -0.207 | 0.00035109 | 0.00035109 | houston | N | 0.00035109 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.007667 | houston | 0.0088977 | -0.0054767 | -0.207 | 0.00035109 | 0.00035109 | houston | N | 0.00035109 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.007667 | houston | 0.0088977 | -0.0054767 | -0.207 | 0.00035109 | 0.00035109 | houston | N | 0.00035109 | 0
48929 | WAPGT21_ | B1 | 13 | -0.00775 | houston | 0.0088147 | -0.0055597 | -0.20709 | 0.00026809 | 0.00026809 | houston | N | 0.00026809 | 0
48940 | WARVUE_G | G1 | 12 | -0.008501 | houston | 0.0080637 | -0.0063107 | -0.20784 | -0.00048291 | 0.00048291 | houston | N | 0.00048291 | 0
49803 | EXN_15GT | 1 | 34 | -0.008462 | houston | 0.0081027 | -0.0062717 | -0.2078 | -0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.008462 | houston | 0.0081027 | -0.0062717 | -0.2078 | -0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.008462 | houston | 0.0081027 | -0.0062717 | -0.2078 | -0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49826 | EXN938GT | 5 | 45.9 | -0.008462 | houston | 0.0081027 | -0.0062717 | -0.2078 | -0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49828 | EXN941GT | 10 | 17.7 | -0.008462 | houston | 0.0081027 | -0.0062717 | -0.2078 | -0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49829 | EXN942GT | 11 | 20.4 | -0.008462 | houston | 0.0081027 | -0.0062717 | -0.2078 | -0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49830 | EXN943GT | 12 | 19.9 | -0.008462 | houston | 0.0081027 | -0.0062717 | -0.2078 | -0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49831 | EXN944GT | 13 | 35 | -0.008462 | houston | 0.0081027 | -0.0062717 | -0.2078 | -0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49832 | EXN945GT | 9 | 18 | -0.008462 | houston | 0.0081027 | -0.0062717 | -0.2078 | -0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49837 | EXN_GT | 4 | 85.4 | -0.008462 | houston | 0.0081027 | -0.0062717 | -0.2078 | -0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49838 | EXN_14GT | 14 | 148 | -0.008462 | houston | 0.0081027 | -0.0062717 | -0.2078 | -0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49851 | DOW17000 | 37 | 62 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49858 | DOW38100 | 31 | 71.4 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49859 | DOW38200 | 33 | 45 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49860 | DOW38300 | 32 | 101 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49862 | DOW39100 | 36 | 86 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49863 | DOW39200 | 35 | 88 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49865 | DOW41000 | 41 | 50 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49866 | DOW42000 | 42 | 18 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49869 | DOW49000 | 45 | 94 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49870 | DOW61000 | 61 | 70 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49871 | DOW62000 | 62 | 63 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49872 | DOW63000 | 63 | 72 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49873 | DOW64000 | 64 | 64.8 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49876 | DOW65000 | 65 | 101 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49877 | DOW66000 | 66 | 97 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49878 | DOW67000 | 67 | 103 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49882 | DOW81000 | 81 | 76 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49884 | DOW82000 | 82 | 80 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49885 | DOW83000 | 83 | 80 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49886 | DOW84000 | 84 | 171 | -0.006909 | houston | 0.0096557 | -0.0047187 | -0.20624 | 0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
58909 | PEARSALL | 1 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58909 | PEARSALL | 2 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58909 | PEARSALL | 3 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58909 | PEARSALL | 4 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58909 | PEARSALL | 5 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58909 | PEARSALL | 6 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58919 | PEARSALL | 1 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58919 | PEARSALL | 2 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58919 | PEARSALL | 3 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58919 | PEARSALL | 4 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58919 | PEARSALL | 5 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58919 | PEARSALL | 6 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58929 | PEARSALL | 1 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58929 | PEARSALL | 2 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58929 | PEARSALL | 3 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58929 | PEARSALL | 4 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58929 | PEARSALL | 5 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58929 | PEARSALL | 6 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58949 | PEARSALL | 1 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58949 | PEARSALL | 2 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58949 | PEARSALL | 3 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58949 | PEARSALL | 4 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58949 | PEARSALL | 5 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58949 | PEARSALL | 6 | 8.4 | 0.007603 | south | 0.024168 | 0.0097933 | -0.19173 | 0.015621 | 0.0097933 | south | N | 0.0097933 | 0
60000 | DSKY2 | 1 | 76.5 | 0.18684 | west | 0.20341 | 0.18903 | -0.012493 | 0.19486 | 0.012493 | west | N | 0.012493 | 0
60003 | KING_NE1 | 1 | 80 | 0.19187 | west | 0.20844 | 0.19407 | -0.0074607 | 0.19989 | 0.0074607 | west | N | 0.0074607 | 0
60005 | KING_SE1 | 1 | 40 | 0.19187 | west | 0.20844 | 0.19407 | -0.0074607 | 0.19989 | 0.0074607 | west | N | 0.0074607 | 0
60007 | KING_SW1 | 1 | 80 | 0.19262 | west | 0.20919 | 0.19481 | -0.0067127 | 0.20064 | 0.0067127 | west | N | 0.0067127 | 0
60016 | WOODWRD1 | 1 | 80 | 0.19172 | west | 0.20828 | 0.19391 | -0.0076157 | 0.19974 | 0.0076157 | west | N | 0.0076157 | 0
60017 | ORNNWP1 | 1 | 80 | 0.18779 | west | 0.20435 | 0.18998 | -0.01155 | 0.1958 | 0.01155 | west | N | 0.01155 | 0
60018 | DSKY1 | 1 | 84 | 0.1865 | west | 0.20306 | 0.18869 | -0.012836 | 0.19452 | 0.012836 | west | N | 0.012836 | 0
60019 | KING_NW1 | 1 | 80 | 0.19262 | west | 0.20919 | 0.19481 | -0.0067127 | 0.20064 | 0.0067127 | west | N | 0.0067127 | 0
60057 | CALLAHAN | 1 | 114 | -0.000337 | south | 0.016228 | 0.0018533 | -0.19967 | 0.0076811 | 0.0018533 | south | N | 0.0018533 | 0
60058 | BUFF_GAP | 1 | 120 | 0.22648 | west | 0.24305 | 0.22868 | 0.027149 | 0.2345 | 0.027149 | west | N | 0.027149 | 0
60060 | CIRELLO | 1 | 233 | 0.22648 | west | 0.24305 | 0.22868 | 0.027149 | 0.2345 | 0.027149 | west | N | 0.027149 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.22648 | west | 0.24305 | 0.22868 | 0.027149 | 0.2345 | 0.027149 | west | N | 0.027149 | 0
60066 | H_HOLLOW | 1 | 222 | -0.000337 | south | 0.016228 | 0.0018533 | -0.19967 | 0.0076811 | 0.0018533 | south | N | 0.0018533 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.000337 | south | 0.016228 | 0.0018533 | -0.19967 | 0.0076811 | 0.0018533 | south | N | 0.0018533 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.000337 | south | 0.016228 | 0.0018533 | -0.19967 | 0.0076811 | 0.0018533 | south | N | 0.0018533 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.000337 | south | 0.016228 | 0.0018533 | -0.19967 | 0.0076811 | 0.0018533 | south | N | 0.0018533 | 0
60074 | HORSH5 | 1 | 100 | -0.000337 | south | 0.016228 | 0.0018533 | -0.19967 | 0.0076811 | 0.0018533 | south | N | 0.0018533 | 0
60081 | WHRLWIND | 1 | 60 | 0.18556 | west | 0.20213 | 0.18775 | -0.013775 | 0.19358 | 0.013775 | west | N | 0.013775 | 0
60201 | RIO DRCS | F | 0 | 0.059084 | south | 0.075649 | 0.061274 | -0.14025 | 0.067102 | 0.061274 | south | N | 0.061274 | 0
60202 | FRIEND_R | F | 0 | 0.16616 | west | 0.18273 | 0.16835 | -0.033174 | 0.17418 | 0.033174 | west | N | 0.033174 | 0
60203 | PRES0A | BT | 4.8 | 0.19563 | west | 0.2122 | 0.19782 | -0.0037047 | 0.20365 | 0.0037047 | west | N | 0.0037047 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.23476 | west | 0.25132 | 0.23695 | 0.03542 | 0.24277 | 0.03542 | west | N | 0.03542 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.23476 | west | 0.25132 | 0.23695 | 0.03542 | 0.24277 | 0.03542 | west | N | 0.03542 | 0
71057 | L_SWEETW | W1 | 135 | 0.23476 | west | 0.25132 | 0.23695 | 0.03542 | 0.24277 | 0.03542 | west | N | 0.03542 | 0
71059 | L_SWEETW | W1 | 119 | 0.23476 | west | 0.25132 | 0.23695 | 0.03542 | 0.24277 | 0.03542 | west | N | 0.03542 | 0
71060 | L_SWEETW | W1 | 105 | 0.23476 | west | 0.25132 | 0.23695 | 0.03542 | 0.24277 | 0.03542 | west | N | 0.03542 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.23476 | west | 0.25132 | 0.23695 | 0.03542 | 0.24277 | 0.03542 | west | N | 0.03542 | 0
76031 | L_GASCCR | W1 | 150 | 0.19833 | west | 0.2149 | 0.20052 | -0.0010037 | 0.20635 | 0.0010037 | west | N | 0.0010037 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.19652 | west | 0.21309 | 0.19871 | -0.0028117 | 0.20454 | 0.0028117 | west | N | 0.0028117 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.19652 | west | 0.21309 | 0.19871 | -0.0028117 | 0.20454 | 0.0028117 | west | N | 0.0028117 | 0
76096 | L_CAPRSI | W1 | 186 | 0.19652 | west | 0.21309 | 0.19871 | -0.0028117 | 0.20454 | 0.0028117 | west | N | 0.0028117 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.19652 | west | 0.21309 | 0.19871 | -0.0028117 | 0.20454 | 0.0028117 | west | N | 0.0028117 | 0
80003 | MILHWYS | F | 0 | -0.001907 | south | 0.014658 | 0.00028332 | -0.20124 | 0.0061111 | 0.00028332 | south | N | 0.00028332 | 0
80010 | EPLVT1 | F | 0 | 0.035876 | south | 0.052441 | 0.038066 | -0.16346 | 0.043894 | 0.038066 | south | N | 0.038066 | 0
80012 | LAR | F | 0 | 0.003177 | south | 0.019742 | 0.0053673 | -0.19616 | 0.011195 | 0.0053673 | south | N | 0.0053673 | 0
80051 | FORPVCM0 | 8 | 28 | -0.003468 | south | 0.013097 | -0.0012777 | -0.2028 | 0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.003468 | south | 0.013097 | -0.0012777 | -0.2028 | 0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
80053 | FOR69CG0 | 10 | 74 | -0.003468 | south | 0.013097 | -0.0012777 | -0.2028 | 0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
80080 | GWINDT11 | 1 | 94 | -0.001967 | south | 0.014598 | 0.00022332 | -0.2013 | 0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80080 | GWINDT11 | 2 | 41 | -0.001967 | south | 0.014598 | 0.00022332 | -0.2013 | 0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80080 | GWINDT11 | 3 | 38 | -0.001967 | south | 0.014598 | 0.00022332 | -0.2013 | 0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80080 | GWINDT11 | 4 | 19 | -0.001967 | south | 0.014598 | 0.00022332 | -0.2013 | 0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80081 | GWINDT21 | 1 | 94 | -0.001967 | south | 0.014598 | 0.00022332 | -0.2013 | 0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80081 | GWINDT21 | 2 | 36 | -0.001967 | south | 0.014598 | 0.00022332 | -0.2013 | 0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80081 | GWINDT21 | 3 | 43 | -0.001967 | south | 0.014598 | 0.00022332 | -0.2013 | 0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80081 | GWINDT21 | 4 | 22 | -0.001967 | south | 0.014598 | 0.00022332 | -0.2013 | 0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80137 | CSDR89 | 8 | 39 | -0.003113 | south | 0.013452 | -0.00092268 | -0.20245 | 0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
80137 | CSDR89 | 9 | 15 | -0.003113 | south | 0.013452 | -0.00092268 | -0.20245 | 0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
80138 | CSDR7 | 7 | 7 | -0.003113 | south | 0.013452 | -0.00092268 | -0.20245 | 0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
80139 | CSDR56 | 5 | 15 | -0.003113 | south | 0.013452 | -0.00092268 | -0.20245 | 0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
80139 | CSDR56 | 6 | 39 | -0.003113 | south | 0.013452 | -0.00092268 | -0.20245 | 0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
80140 | CSDR11 | 11 | 39 | -0.003113 | south | 0.013452 | -0.00092268 | -0.20245 | 0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
80180 | PNSCALT1 | 1 | 148 | -0.001967 | south | 0.014598 | 0.00022332 | -0.2013 | 0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80180 | PNSCALT1 | 2 | 50 | -0.001967 | south | 0.014598 | 0.00022332 | -0.2013 | 0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80181 | PNSCALT2 | 1 | 55 | -0.001967 | south | 0.014598 | 0.00022332 | -0.2013 | 0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80181 | PNSCALT2 | 2 | 50 | -0.001967 | south | 0.014598 | 0.00022332 | -0.2013 | 0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80223 | REYSHR G | 1 | 12 | -0.002338 | south | 0.014227 | -0.00014768 | -0.20167 | 0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
80224 | VISTRONG | 1 | 15 | -0.003035 | south | 0.01353 | -0.00084468 | -0.20237 | 0.0049831 | 0.00084468 | south | N | 0.00084468 | 0
80225 | VISTRONG | 2 | 23 | -0.003035 | south | 0.01353 | -0.00084468 | -0.20237 | 0.0049831 | 0.00084468 | south | N | 0.00084468 | 0
80226 | ALCOA G | 1 | 48 | -0.003392 | south | 0.013173 | -0.0012017 | -0.20273 | 0.0046261 | 0.0012017 | south | N | 0.0012017 | 0
80227 | AIRCO G | 1 | 8 | -0.003059 | south | 0.013506 | -0.00086868 | -0.20239 | 0.0049591 | 0.00086868 | south | N | 0.00086868 | 0
80261 | NBEC81A | 1 | 180 | -0.002182 | south | 0.014383 | 8.3152e-06 | -0.20152 | 0.0058361 | 8.3152e-06 | south | N | 8.3152e-06 | 0
80262 | NBEC91A | 1 | 180 | -0.002186 | south | 0.014379 | 4.3152e-06 | -0.20152 | 0.0058321 | 4.3152e-06 | south | N | 4.3152e-06 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.002157 | south | 0.014408 | 3.3315e-05 | -0.20149 | 0.0058611 | 3.3315e-05 | south | N | 3.3315e-05 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.002157 | south | 0.014408 | 3.3315e-05 | -0.20149 | 0.0058611 | 3.3315e-05 | south | N | 3.3315e-05 | 0
80265 | LARECU40 | 4 | 100 | 0.003174 | south | 0.019739 | 0.0053643 | -0.19616 | 0.011192 | 0.0053643 | south | N | 0.0053643 | 0
80266 | LARECU50 | 5 | 100 | 0.003174 | south | 0.019739 | 0.0053643 | -0.19616 | 0.011192 | 0.0053643 | south | N | 0.0053643 | 0
80291 | PAPALOTE | 1 | 25 | -0.002274 | south | 0.014291 | -8.3685e-05 | -0.20161 | 0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80291 | PAPALOTE | 2 | 25 | -0.002274 | south | 0.014291 | -8.3685e-05 | -0.20161 | 0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80291 | PAPALOTE | 3 | 25 | -0.002274 | south | 0.014291 | -8.3685e-05 | -0.20161 | 0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80291 | PAPALOTE | 4 | 16 | -0.002274 | south | 0.014291 | -8.3685e-05 | -0.20161 | 0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80294 | PAPALOTE | 5 | 25 | -0.002274 | south | 0.014291 | -8.3685e-05 | -0.20161 | 0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80294 | PAPALOTE | 6 | 25 | -0.002274 | south | 0.014291 | -8.3685e-05 | -0.20161 | 0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80294 | PAPALOTE | 7 | 25 | -0.002274 | south | 0.014291 | -8.3685e-05 | -0.20161 | 0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80294 | PAPALOTE | 8 | 15 | -0.002274 | south | 0.014291 | -8.3685e-05 | -0.20161 | 0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
86104 | CID-138 | EQ | 0 | 0.003174 | south | 0.019739 | 0.0053643 | -0.19616 | 0.011192 | 0.0053643 | south | N | 0.0053643 | 0
86105 | CID-230 | EQ | 500 | 0.003174 | south | 0.019739 | 0.0053643 | -0.19616 | 0.011192 | 0.0053643 | south | N | 0.0053643 | 0
86106 | CUF-230 | EQ | 500 | 0.003174 | south | 0.019739 | 0.0053643 | -0.19616 | 0.011192 | 0.0053643 | south | N | 0.0053643 | 0
86107 | CUF-138 | EQ | 0 | 0.003174 | south | 0.019739 | 0.0053643 | -0.19616 | 0.011192 | 0.0053643 | south | N | 0.0053643 | 0
88198 | BEEVILLE | F | 0 | -0.001311 | south | 0.015254 | 0.00087932 | -0.20065 | 0.0067071 | 0.00087932 | south | N | 0.00087932 | 0
88253 | HAMILTON | F | 0 | 0.055041 | south | 0.071606 | 0.057231 | -0.14429 | 0.063059 | 0.057231 | south | N | 0.057231 | 0
88299 | ZAPATA | F | 0 | 0.001494 | south | 0.018059 | 0.0036843 | -0.19784 | 0.0095121 | 0.0036843 | south | N | 0.0036843 | 0
88508 | FALFURRI | F | 0 | -0.001176 | south | 0.015389 | 0.0010143 | -0.20051 | 0.0068421 | 0.0010143 | south | N | 0.0010143 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Longcreek - Cookfield 345kV [1439-1442] C: Fisher Road - Oklaunion 345kV [1425-6100] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.32518 | west | 6 | Y | N | Ywest | Nwest | 1 | 76.7427 | 236 | 0.12851 | 30.3283 | 236 | 30.3283
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.32331 | west | 6 | Y | N | Ywest | Nwest | 1 | 129.322 | 400 | 0.12663 | 50.6534 | 636 | 80.9817
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.055041 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8164 | 0 | 0.071606 | 0 | 636 | 80.9817
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.055041 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.376 | 0 | 0.071606 | 0 | 636 | 80.9817 | Weighted Shift Factors
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.055041 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.071606 | 0 | 636 | 80.9817 | North | -0.016565
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.039493 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.23696 | 0 | 0.056058 | 0 | 636 | 80.9817 | West | 0.19667
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.035876 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.052441 | 0 | 636 | 80.9817 |  | -0.21324
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.24757 | west | 4 | Y | N | Ywest | Nwest | 1 | 160.8469 | 649.7 | 0.0509 | 33.0695 | 1285.7 | 114.0512
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8034 | 37.5 | 0.038085 | 1.4282 | 1323.2 | 115.4794 | Line Rating | 1240
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.2363 | 107.5 | 0.038085 | 4.0941 | 1430.7 | 119.5735 | Conc Gen | 2393.4
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.6921 | 135 | 0.038085 | 5.1414 | 1565.7 | 124.7149 | Weighted Imp. | 151.9102
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.936 | 119 | 0.038085 | 4.5321 | 1684.7 | 129.247 | PTDF | 0.06347
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.6494 | 105 | 0.038085 | 3.9989 | 1789.7 | 133.2459
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.8979 | 80.5 | 0.038085 | 3.0658 | 1870.2 | 136.3117 | Concentration | -0.29765
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.22648 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.1782 | 120 | 0.029814 | 3.5776 | 1990.2 | 139.8893
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.22648 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.771 | 233 | 0.029814 | 6.9466 | 2223.2 | 146.8359
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.22648 | west | 6 | Y | N | Ywest | Nwest | 1 | 38.5477 | 170.2 | 0.029814 | 5.0743 | 2393.4 | 151.9102
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.22138 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.6724 | 125 | 0.024708 | 3.0885
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.22138 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.6724 | 125 | 0.024708 | 3.0885
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00796 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10905 | 0 | 0.024525 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.006121 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.1469 | 24 | 0.022686 | 0.54446
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.006121 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.1469 | 24 | 0.022686 | 0.54446
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.006121 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.14078 | 23 | 0.022686 | 0.52177
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.005652 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10174 | 0 | 0.022217 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.005652 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10174 | 0 | 0.022217 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.005652 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.08478 | 0 | 0.022217 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.0053 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.2366 | 422 | 0.021865 | 9.2269
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.004798 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13434 | 0 | 0.021363 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.004798 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13914 | 0 | 0.021363 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.059364 | 0 | 0.019863 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.059364 | 0 | 0.019863 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.003177 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.019742 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.003174 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.3174 | 100 | 0.019739 | 1.9739
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.003174 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.3174 | 100 | 0.019739 | 1.9739
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.019739 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.019739 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.019739 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.019739 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.001494 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.018059 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.21461 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.3764 | 169.5 | 0.017939 | 3.0406
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 3e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00036 | 0 | 0.016595 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 3e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00033 | 0 | 0.016595 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 3e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00036 | 0 | 0.016595 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016565 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016565 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016565 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016565 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016565 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016565 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.016565 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.016565 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.038418 | 114 | 0.016228 | 1.85
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.074814 | 222 | 0.016228 | 3.6025
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.062008 | 184 | 0.016228 | 2.9859
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.075488 | 224 | 0.016228 | 3.635
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.038755 | 115 | 0.016228 | 1.8662
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.000617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.035786 | 58 | 0.015948 | 0.92497
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.000617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.054913 | 89 | 0.015948 | 1.4193
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.027148 | 44 | 0.015948 | 0.7017
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.027148 | 44 | 0.015948 | 0.7017
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.026531 | 43 | 0.015948 | 0.68575
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.027765 | 45 | 0.015948 | 0.71765
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.000964 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.39235 | 407 | 0.015601 | 6.3495
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.001048 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.41501 | 396 | 0.015517 | 6.1446
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.001084 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.22656 | 209 | 0.015481 | 3.2355
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.001084 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.23414 | 216 | 0.015481 | 3.3438
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.049864 | 46 | 0.015481 | 0.71211
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.050948 | 47 | 0.015481 | 0.72759
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.049864 | 46 | 0.015481 | 0.71211
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.049864 | 46 | 0.015481 | 0.71211
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.001086 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.44743 | 412 | 0.015479 | 6.3772
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.001086 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.4344 | 400 | 0.015479 | 6.1915
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.001147 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.48633 | 424 | 0.015418 | 6.5371
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.001147 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.48747 | 425 | 0.015418 | 6.5525
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.001176 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.015389 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.001242 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.04347 | 0 | 0.015323 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.001242 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.042228 | 0 | 0.015323 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.001242 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.04347 | 0 | 0.015323 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.001311 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.015254 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.015162 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.015162 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.015162 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.22925 | 155 | 0.015086 | 2.3383
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25143 | 170 | 0.015086 | 2.5646
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.22925 | 155 | 0.015086 | 2.3383
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.2196 | 146.5 | 0.015066 | 2.2071
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.2217 | 147.9 | 0.015066 | 2.2282
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25933 | 173 | 0.015066 | 2.6064
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.001597 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.87196 | 546 | 0.014968 | 8.1724
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.001597 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.1978 | 750 | 0.014968 | 11.2258
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.36308 | 207 | 0.014811 | 3.0658
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.38009 | 216.7 | 0.014811 | 3.2095
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.42447 | 242 | 0.014811 | 3.5842
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25258 | 144 | 0.014811 | 2.1327
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25258 | 144 | 0.014811 | 2.1327
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.29993 | 171 | 0.014811 | 2.5326
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.001907 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.014658 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.072466 | 38 | 0.014658 | 0.55699
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.036805 | 19.3 | 0.014658 | 0.28289
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.028605 | 15 | 0.014658 | 0.21987
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.001907 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.089629 | 47 | 0.014658 | 0.68891
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.1849 | 94 | 0.014598 | 1.3722
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.080647 | 41 | 0.014598 | 0.5985
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.074746 | 38 | 0.014598 | 0.55471
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.037373 | 19 | 0.014598 | 0.27736
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.1849 | 94 | 0.014598 | 1.3722
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.070812 | 36 | 0.014598 | 0.52552
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.084581 | 43 | 0.014598 | 0.6277
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.043274 | 22 | 0.014598 | 0.32115
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.29112 | 148 | 0.014598 | 2.1605
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.09835 | 50 | 0.014598 | 0.72988
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.10819 | 55 | 0.014598 | 0.80287
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.09835 | 50 | 0.014598 | 0.72988
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.002018 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.008072 | 0 | 0.014547 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.002041 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.059189 | 0 | 0.014524 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.002052 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.012312 | 0 | 0.014513 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.002119 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.080522 | 0 | 0.014446 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.002137 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.081206 | 0 | 0.014428 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.002139 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.053475 | 0 | 0.014426 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.002139 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.053475 | 0 | 0.014426 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.31561 | 147 | 0.014418 | 2.1194
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.29629 | 138 | 0.014418 | 1.9896
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.30058 | 140 | 0.014418 | 2.0185
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.31561 | 147 | 0.014418 | 2.1194
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.39075 | 182 | 0.014418 | 2.624
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.42511 | 198 | 0.014418 | 2.8547
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.002157 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.72044 | 334 | 0.014408 | 4.8122
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.002157 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.73338 | 340 | 0.014408 | 4.8986
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.002157 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.38826 | 180 | 0.014408 | 2.5934
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.002157 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.38826 | 180 | 0.014408 | 2.5934
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.002182 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.39276 | 180 | 0.014383 | 2.5889
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.002185 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.32404 | 0 | 0.01438 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.002185 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.32469 | 0 | 0.01438 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.002185 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.33431 | 0 | 0.01438 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.002186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.7345 | 336 | 0.014379 | 4.8312
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.002186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.39348 | 180 | 0.014379 | 2.5882
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.002193 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.3794 | 629 | 0.014372 | 9.0398
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05685 | 25 | 0.014291 | 0.35727
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05685 | 25 | 0.014291 | 0.35727
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05685 | 25 | 0.014291 | 0.35727
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.036384 | 16 | 0.014291 | 0.22865
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05685 | 25 | 0.014291 | 0.35727
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05685 | 25 | 0.014291 | 0.35727
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05685 | 25 | 0.014291 | 0.35727
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.03411 | 15 | 0.014291 | 0.21436
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.002337 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0056088 | 0 | 0.014228 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.002337 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0056088 | 0 | 0.014228 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.002337 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0065436 | 0 | 0.014228 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.3694 | 0 | 0.014227 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.35771 | 0 | 0.014227 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.2338 | 0 | 0.014227 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.33901 | 0 | 0.014227 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.34369 | 0 | 0.014227 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.29693 | 0 | 0.014227 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.002338 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.028056 | 0 | 0.014227 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.33285 | 142 | 0.014221 | 2.0193
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.33988 | 145 | 0.014221 | 2.062
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.35394 | 151 | 0.014221 | 2.1473
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.67976 | 290 | 0.014221 | 4.124
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.56759 | 223.9 | 0.01403 | 3.1412
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.57037 | 225 | 0.01403 | 3.1567
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.56936 | 224.6 | 0.01403 | 3.1511
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.57468 | 226.7 | 0.01403 | 3.1805
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.002652 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.058344 | 22 | 0.013913 | 0.30608
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.002652 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.029172 | 11 | 0.013913 | 0.15304
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.002652 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.029172 | 11 | 0.013913 | 0.15304
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.00267 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.006408 | 0 | 0.013895 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.00267 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.006408 | 0 | 0.013895 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.002687 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.032244 | 0 | 0.013878 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13318 | 47.7 | 0.013773 | 0.65696
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.10414 | 37.3 | 0.013773 | 0.51372
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.12843 | 46 | 0.013773 | 0.63354
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13402 | 48 | 0.013773 | 0.66109
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.002853 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.41083 | 144 | 0.013712 | 1.9745
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.002853 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.53636 | 188 | 0.013712 | 2.5778
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.00293 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.21389 | 0 | 0.013635 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.003035 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.045525 | 0 | 0.01353 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.003035 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.069805 | 0 | 0.01353 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.003059 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.024472 | 0 | 0.013506 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.087164 | 0 | 0.013452 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.021791 | 0 | 0.013452 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12141 | 0 | 0.013452 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.046695 | 0 | 0.013452 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.021791 | 0 | 0.013452 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.046695 | 0 | 0.013452 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12141 | 0 | 0.013452 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12141 | 0 | 0.013452 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.003287 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.026296 | 0 | 0.013278 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.003287 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.026296 | 0 | 0.013278 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.003392 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.16282 | 0 | 0.013173 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16817 | 49 | 0.013133 | 0.6435
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.15787 | 46 | 0.013133 | 0.6041
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.15787 | 46 | 0.013133 | 0.6041
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1613 | 47 | 0.013133 | 0.61724
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.52853 | 154 | 0.013133 | 2.0224
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.50794 | 148 | 0.013133 | 1.9436
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16474 | 48 | 0.013133 | 0.63037
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16474 | 48 | 0.013133 | 0.63037
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27397 | 0 | 0.013097 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28091 | 0 | 0.013097 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27397 | 0 | 0.013097 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27744 | 0 | 0.013097 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27189 | 0 | 0.013097 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0867 | 0 | 0.013097 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.15953 | 0 | 0.013097 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.097104 | 0 | 0.013097 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.1512 | 0 | 0.013097 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.25663 | 0 | 0.013097 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.003479 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0785 | 310 | 0.013086 | 4.0566
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.003479 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4368 | 413 | 0.013086 | 5.4044
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.15288 | 42 | 0.012925 | 0.54284
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16016 | 44 | 0.012925 | 0.56869
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16016 | 44 | 0.012925 | 0.56869
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17108 | 47 | 0.012925 | 0.60746
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.53341 | 132 | 0.012524 | 1.6531
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.54149 | 134 | 0.012524 | 1.6782
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3052 | 323 | 0.012524 | 4.0451
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.62006 | 152.5 | 0.012499 | 1.906
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60787 | 149.5 | 0.012499 | 1.8686
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.94575 | 232.6 | 0.012499 | 2.9072
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2161 | 50 | 0.012243 | 0.61213
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2161 | 50 | 0.012243 | 0.61213
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2161 | 50 | 0.012243 | 0.61213
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2161 | 50 | 0.012243 | 0.61213
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.70278 | 158 | 0.012117 | 1.9144
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.71168 | 160 | 0.012117 | 1.9387
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.7784 | 175 | 0.012117 | 2.1204
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.004494 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.9459 | 433 | 0.012071 | 5.2266
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.004496 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.6257 | 584 | 0.012069 | 7.0481
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.004496 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.6751 | 595 | 0.012069 | 7.1809
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.20738 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.1072 | 150 | 0.01071 | 1.6064
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.20738 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9455 | 101 | 0.01071 | 1.0817
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.006038 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -8.0487 | 0 | 0.010527 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.006038 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -8.0185 | 0 | 0.010527 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.46786 | 76 | 0.010409 | 0.79106
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.46786 | 76 | 0.010409 | 0.79106
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.64638 | 105 | 0.010409 | 1.0929
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45554 | 74 | 0.010409 | 0.77024
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45554 | 74 | 0.010409 | 0.77024
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.62791 | 102 | 0.010409 | 1.0617
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.0598 | 150 | 0.010394 | 1.559
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | 45.5543 | 220 | 0.010394 | 2.2866
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | 41.413 | 200 | 0.010394 | 2.0787
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.2412 | 121.9 | 0.010394 | 1.267
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.006219 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -3.5386 | 569 | 0.010346 | 5.8867
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.006219 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -3.6132 | 581 | 0.010346 | 6.0108
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.006258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.41303 | 66 | 0.010307 | 0.68024
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.20665 | west | 8 | N | N | Nwest | Nwest | 1 | 14.4657 | 0 | 0.0099816 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.20665 | west | 8 | N | N | Nwest | Nwest | 1 | 15.1683 | 0 | 0.0099816 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.20665 | west | 8 | N | N | Nwest | Nwest | 1 | 14.5484 | 0 | 0.0099816 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42836 | 0 | 0.0096557 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4933 | 0 | 0.0096557 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3109 | 0 | 0.0096557 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69781 | 0 | 0.0096557 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59417 | 0 | 0.0096557 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.60799 | 0 | 0.0096557 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34545 | 0 | 0.0096557 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12436 | 0 | 0.0096557 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64945 | 0 | 0.0096557 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.48363 | 0 | 0.0096557 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43527 | 0 | 0.0096557 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49745 | 0 | 0.0096557 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4477 | 0 | 0.0096557 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69781 | 0 | 0.0096557 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.67017 | 0 | 0.0096557 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71163 | 0 | 0.0096557 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52508 | 0 | 0.0096557 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55272 | 0 | 0.0096557 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55272 | 0 | 0.0096557 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1814 | 0 | 0.0096557 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.007066 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50169 | 0 | 0.0094987 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.007066 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.07066 | 0 | 0.0094987 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79909 | 0 | 0.0093657 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79909 | 0 | 0.0093657 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.85668 | 0 | 0.0093657 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.78829 | 0 | 0.0093657 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.5724 | 66 | 0.0089706 | 0.59206
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | 14.1893 | 69 | 0.0089706 | 0.61897
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | 14.1893 | 69 | 0.0089706 | 0.61897
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.778 | 67 | 0.0089706 | 0.60103
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.778 | 67 | 0.0089706 | 0.60103
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.3667 | 65 | 0.0089706 | 0.58309
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.007625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35151 | 0 | 0.0089397 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.9912 | 651 | 0.0088977 | 5.7924
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.3242 | 564 | 0.0088977 | 5.0183
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.6002 | 600 | 0.0088977 | 5.3386
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2502 | 0 | 0.0088947 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2502 | 0 | 0.0088947 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8792 | 0 | 0.0088947 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.007689 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25374 | 0 | 0.0088757 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2477 | 161 | 0.0088147 | 1.4192
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2865 | 166 | 0.0088147 | 1.4632
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.922 | 248 | 0.0088147 | 2.186
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.00775 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.2315 | 546 | 0.0088147 | 4.8128
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.00775 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -4.9832 | 0 | 0.0088147 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.00775 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10075 | 13 | 0.0088147 | 0.11459
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79568 | 0 | 0.0086317 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.73698 | 0 | 0.0086317 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.81472 | 0 | 0.0086317 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.80917 | 0 | 0.0086317 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.007933 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25386 | 0 | 0.0086317 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.007933 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23799 | 0 | 0.0086317 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56173 | 0 | 0.0086307 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5292 | 0 | 0.0086307 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4205 | 0 | 0.0086307 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2155 | 0 | 0.0086307 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2179 | 0 | 0.0086307 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2083 | 0 | 0.0086307 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.76166 | 0 | 0.0086307 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9359 | 0 | 0.0086307 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31736 | 0 | 0.0086307 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.008037 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.40185 | 50 | 0.0085277 | 0.42638
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.008093 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0084717 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74392 | 0 | 0.0083897 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71613 | 0 | 0.0083897 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71122 | 0 | 0.0083897 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.44554 | 0 | 0.0083897 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.099735 | 0 | 0.0083897 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.3534 | 70 | 0.0083776 | 0.58643
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.3534 | 70 | 0.0083776 | 0.58643
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | 19.0285 | 92.8 | 0.0083776 | 0.77744
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.4039 | 80 | 0.0083776 | 0.67021
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.4039 | 80 | 0.0083776 | 0.67021
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | 23.5806 | 115 | 0.0083776 | 0.96343
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.53346 | 0 | 0.0083577 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.49242 | 0 | 0.0083577 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.53346 | 0 | 0.0083577 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.53346 | 0 | 0.0083577 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | 42.6866 | 208.2 | 0.0083556 | 1.7396
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | 29.1343 | 142.1 | 0.0083556 | 1.1873
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | 27.1456 | 132.4 | 0.0083556 | 1.1063
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | 27.8837 | 136 | 0.0083556 | 1.1364
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | 30.139 | 147 | 0.0083556 | 1.2283
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | 43.0557 | 210 | 0.0083556 | 1.7547
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.3801 | 46 | 0.0083017 | 0.38188
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.3801 | 46 | 0.0083017 | 0.38188
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.3801 | 46 | 0.0083017 | 0.38188
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.45447 | 55 | 0.0083017 | 0.45659
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.45447 | 55 | 0.0083017 | 0.45659
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.4462 | 54 | 0.0083017 | 0.44829
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.008266 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.64475 | 0 | 0.0082987 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.008266 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.66128 | 0 | 0.0082987 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3511 | 0 | 0.0082857 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3006 | 0 | 0.0082857 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3039 | 0 | 0.0082857 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2998 | 0 | 0.0082857 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2271 | 0 | 0.0082857 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.008297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2904 | 0 | 0.0082677 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.008311 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.099732 | 12 | 0.0082537 | 0.099044
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.008311 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0082537 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.008311 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.4046 | 169 | 0.0082537 | 1.3949
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.008312 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.3715 | 165 | 0.0082527 | 1.3617
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.008313 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2386 | 0 | 0.0082517 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.008313 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.54118 | 0 | 0.0082517 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.008316 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.7713 | 213 | 0.0082487 | 1.757
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.008316 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13472 | 0 | 0.0082487 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53229 | 0 | 0.0082477 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52563 | 0 | 0.0082477 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68698 | 0 | 0.0082477 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61213 | 0 | 0.0082477 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.008317 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.8963 | 228 | 0.0082477 | 1.8805
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4972 | 0 | 0.0082467 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3192 | 0 | 0.0082467 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3059 | 0 | 0.0082467 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.592 | 0 | 0.0082267 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.60034 | 0 | 0.0082267 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32518 | 0 | 0.0082267 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25014 | 0 | 0.0082267 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.35162 | 42 | 0.0081927 | 0.34409
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.35162 | 42 | 0.0081927 | 0.34409
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31814 | 38 | 0.0081927 | 0.31132
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31814 | 38 | 0.0081927 | 0.31132
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.008373 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1387 | 0 | 0.0081917 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.008383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4503 | 0 | 0.0081817 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.008383 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1317 | 0 | 0.0081817 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.87766 | 104 | 0.0081257 | 0.84507
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.87766 | 104 | 0.0081257 | 0.84507
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45571 | 54 | 0.0081257 | 0.43879
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.44727 | 53 | 0.0081257 | 0.43066
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45571 | 54 | 0.0081257 | 0.43879
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.48102 | 57 | 0.0081257 | 0.46316
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45571 | 54 | 0.0081257 | 0.43879
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45571 | 54 | 0.0081257 | 0.43879
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.48946 | 58 | 0.0081257 | 0.47129
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.48946 | 58 | 0.0081257 | 0.47129
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.008449 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -6.21 | 735 | 0.0081157 | 5.965
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28771 | 0 | 0.0081027 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.29363 | 0 | 0.0081027 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.27671 | 0 | 0.0081027 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38841 | 0 | 0.0081027 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14978 | 0 | 0.0081027 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17262 | 0 | 0.0081027 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16839 | 0 | 0.0081027 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.29617 | 0 | 0.0081027 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15232 | 0 | 0.0081027 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72265 | 0 | 0.0081027 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2524 | 0 | 0.0081027 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.008487 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10184 | 12 | 0.0080777 | 0.096932
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.0085 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0425 | 0 | 0.0080647 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.0085 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1785 | 0 | 0.0080647 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.008501 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.10201 | 12 | 0.0080637 | 0.096764
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55263 | 0 | 0.0080627 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56113 | 0 | 0.0080627 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59514 | 0 | 0.0080627 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53563 | 0 | 0.0080627 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52712 | 0 | 0.0080627 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88421 | 0 | 0.0080627 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50162 | 0 | 0.0080627 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.008502 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -6.317 | 743 | 0.0080627 | 5.9906
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.008514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3367 | 0 | 0.0080507 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4649 | 172 | 0.0080477 | 1.3842
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4649 | 172 | 0.0080477 | 1.3842
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4649 | 172 | 0.0080477 | 1.3842
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3928 | 0 | 0.0080097 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3808 | 0 | 0.0080097 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3594 | 0 | 0.0080097 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.303 | 0 | 0.0080097 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.008572 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.4117 | 398 | 0.0079927 | 3.1811
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.48138 | 56 | 0.0079687 | 0.44625
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.50716 | 59 | 0.0079687 | 0.47015
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.48138 | 56 | 0.0079687 | 0.44625
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.48138 | 56 | 0.0079687 | 0.44625
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.50716 | 59 | 0.0079687 | 0.47015
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.48138 | 56 | 0.0079687 | 0.44625
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5248 | 0 | 0.0077507 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.375 | 0 | 0.0077507 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3574 | 0 | 0.0077507 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3574 | 0 | 0.0077507 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.008814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4279 | 0 | 0.0077507 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.20435 | west | 6 | Y | N | Ywest | Nwest | 1 | 43.7716 | 214.2 | 0.0076776 | 1.6445
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.20414 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.8401 | 58 | 0.0074676 | 0.43312
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.204 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.5022 | 100.5 | 0.0073306 | 0.73673
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.20355 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.4259 | 120 | 0.0068776 | 0.82531
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.20327 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.3926 | 120 | 0.0066006 | 0.79207
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.20284 | west | 8 | N | N | Nwest | Nwest | 1 | 5.2332 | 0 | 0.0061666 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.20276 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.2109 | 149 | 0.0060866 | 0.90691
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.3814 | 66 | 0.0060776 | 0.40112
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.1787 | 65 | 0.0060776 | 0.39505
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.5842 | 67 | 0.0060776 | 0.4072
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.5842 | 67 | 0.0060776 | 0.4072
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.5842 | 67 | 0.0060776 | 0.4072
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.20275 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0060776 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.20275 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0060776 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.20272 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.095 | 35 | 0.0060436 | 0.21153
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.20272 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0815 | 30 | 0.0060436 | 0.18131
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.20257 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.762 | 63 | 0.0059006 | 0.37174
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.20257 | west | 6 | Y | N | Ywest | Nwest | 1 | 45.578 | 225 | 0.0058976 | 1.327
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.20255 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.4585 | 180 | 0.0058756 | 1.0576
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.20255 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.4585 | 180 | 0.0058756 | 1.0576
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.20152 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.4142 | 141 | 0.0048476 | 0.68351
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.20152 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.1823 | 120 | 0.0048476 | 0.58171
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.20142 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.9409 | 99 | 0.0047516 | 0.47041
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.20142 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.2868 | 61 | 0.0047516 | 0.28985
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.20142 | west | 7 | N | N | Nwest | Nwest | 1 | 5.0356 | 0 | 0.0047516 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.20142 | west | 7 | N | N | Nwest | Nwest | 1 | 9.205 | 0 | 0.0047516 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.20142 | west | 7 | N | N | Nwest | Nwest | 1 | 9.205 | 0 | 0.0047516 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.20008 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3205 | 6.6 | 0.0034056 | 0.022477
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.20008 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8626 | 34.3 | 0.0034056 | 0.11681
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.1991 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.7243 | 84 | 0.0024276 | 0.20392
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.19833 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.7498 | 150 | 0.0016606 | 0.24909
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.109 | 112.5 | -0.00014738 | -0.01658
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.3803 | 149.5 | -0.00014738 | -0.022033
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.5535 | 186 | -0.00014738 | -0.027412
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | 42.1544 | 214.5 | -0.00014738 | -0.031613
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.19563 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.93903 | 0 | -0.0010404 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.19262 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4098 | 80 | -0.0040484 | -0.32387
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.19262 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4098 | 80 | -0.0040484 | -0.32387
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.19187 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.3906 | 75 | -0.0047964 | -0.35973
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.19187 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.35 | 80 | -0.0047964 | -0.38371
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.19187 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.675 | 40 | -0.0047964 | -0.19186
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.19172 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3376 | 80 | -0.0049514 | -0.39611
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.1917 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3358 | 80 | -0.0049744 | -0.39795
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.1916 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.7394 | 150 | -0.0050754 | -0.76131
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.1916 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.7394 | 150 | -0.0050754 | -0.76131
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.1889 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.3358 | 150 | -0.0077664 | -1.165
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.18779 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0229 | 80 | -0.0088854 | -0.71083
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.18684 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.2935 | 76.5 | -0.0098284 | -0.75187
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.1865 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.666 | 84 | -0.010171 | -0.8544
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.18556 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.1337 | 60 | -0.01111 | -0.66662
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.1867 | 209 | -0.023529 | -4.9176
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.9025 | 126.5 | -0.023529 | -2.9765
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | 43.1124 | 249 | -0.023529 | -5.8588
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | 34.109 | 197 | -0.023529 | -4.6353
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.16616 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.030509 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.14784 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.176 | 150 | -0.048831 | -7.3247
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.059084 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.13759 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.02441 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.4646 | 60 | -0.17226 | -10.3357
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.19667 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.19667 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.0337 | 100 | -0.19701 | -19.7008
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.006188 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.45172 | 73 | -0.20286 | -14.8087
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.006188 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.73637 | 119 | -0.20286 | -24.1403
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.006188 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.2685 | 205 | -0.20286 | -41.5862
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.006188 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.63118 | 102 | -0.20286 | -20.6917
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.006188 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.59405 | 96 | -0.20286 | -19.4745
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.008206 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.098472 | 0 | -0.20488 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.008206 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.098472 | 0 | -0.20488 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.009179 | north | 3 | N | N | Nnorth | Nnorth | 1 | -10.6201 | 0 | -0.20585 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.009179 | north | 3 | N | N | Nnorth | Nnorth | 1 | -10.6293 | 0 | -0.20585 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.00923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.3845 | 150 | -0.2059 | -30.8852
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.00923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.7384 | 80 | -0.2059 | -16.4721
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.009568 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.14352 | 0 | -0.20624 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.009568 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.14352 | 0 | -0.20624 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.009989 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.5472 | 255 | -0.20666 | -52.6984
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.009989 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.4884 | 149 | -0.20666 | -30.7924
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.009989 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.5283 | 153 | -0.20666 | -31.619
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.2351 | 217.3 | -0.20696 | -44.9718
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.1086 | 205 | -0.20696 | -42.4263
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.8019 | 272.4 | -0.20696 | -56.3752
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.010406 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20708 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.010406 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20708 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.73129 | 70 | -0.20712 | -14.4983
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.72084 | 69 | -0.20712 | -14.2912
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.72084 | 69 | -0.20712 | -14.2912
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.7104 | 68 | -0.20712 | -14.084
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.6709 | 0 | -0.20751 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.6904 | 0 | -0.20751 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.6904 | 0 | -0.20751 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | -4.1177 | 0 | -0.20751 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.010958 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20763 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.010958 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.6239 | 787 | -0.20763 | -163.4043
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.0112 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.5376 | 48 | -0.20787 | -9.9778
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.0112 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.5152 | 46 | -0.20787 | -9.5621
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.0112 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.176 | 105 | -0.20787 | -21.8265
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.01123 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.35936 | 0 | -0.2079 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20791 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20791 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.011239 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.19106 | 17 | -0.20791 | -3.5345
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20791 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20791 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.011251 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -5.2092 | 463 | -0.20792 | -96.2681
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.011279 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.8949 | 168 | -0.20795 | -34.9357
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.011279 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.0151 | 90 | -0.20795 | -18.7155
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.7927 | 855 | -0.20929 | -178.9467
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.7927 | 855 | -0.20929 | -178.9467
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9225 | 152.3 | -0.20929 | -31.8755
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9313 | 153 | -0.20929 | -32.022
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.013173 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.8941 | 827 | -0.20984 | -173.5413
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.013173 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.7887 | 819 | -0.20984 | -171.8625
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.013587 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.6304 | 120 | -0.21026 | -25.231
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.013748 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.21042 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.2477 | 18 | -0.21043 | -3.7878
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.2477 | 18 | -0.21043 | -3.7878
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.52292 | 38 | -0.21043 | -7.9964
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.014695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -9.0374 | 615 | -0.21137 | -129.9903
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.014695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -8.626 | 587 | -0.21137 | -124.0721
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.2561 | 150.7 | -0.21164 | -31.8945
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.2606 | 151 | -0.21164 | -31.958
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.6559 | 177.4 | -0.21164 | -37.5454
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.2772 | 151.5 | -0.2117 | -32.0729
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.2892 | 152.3 | -0.2117 | -32.2423
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.668 | 177.5 | -0.2117 | -37.5772
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.4321 | 224 | -0.21199 | -47.4865
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.4628 | 226 | -0.21199 | -47.9105
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2483 | 212 | -0.21199 | -44.9426
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2329 | 211 | -0.21199 | -44.7306
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.015721 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.5215 | 224 | -0.21239 | -47.5759
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.015849 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.1064 | 196 | -0.21252 | -41.654
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.015849 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.7592 | 111 | -0.21252 | -23.5898
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.016216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5091 | 216.4 | -0.21289 | -46.0688
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.016216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5043 | 216.1 | -0.21289 | -46.005
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.016407 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.9861 | 182 | -0.21308 | -38.7803
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.016407 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -7.941 | 484 | -0.21308 | -103.1299
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.016434 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.8217 | 50 | -0.21311 | -10.6553
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.01645 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.21312 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.016465 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.9845 | 242 | -0.21314 | -51.579
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.4553 | 0 | -0.21326 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.1567 | 0 | -0.21326 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.4055 | 0 | -0.21326 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | -6.6194 | 0 | -0.21326 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.016756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.1535 | 785 | -0.21343 | -167.5405
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.016756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.321 | 795 | -0.21343 | -169.6748
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.016756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.0697 | 780 | -0.21343 | -166.4734
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.017557 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.0717 | 118 | -0.21423 | -25.2789
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.017557 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.0191 | 115 | -0.21423 | -24.6363
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.017557 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.7617 | 556 | -0.21423 | -119.111
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.017938 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.21461 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.017938 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.21461 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.8951 | 161 | -0.21465 | -34.5592
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.949 | 164 | -0.21465 | -35.2032
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.949 | 164 | -0.21465 | -35.2032
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.4445 | 414 | -0.21465 | -88.8665
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9131 | 162 | -0.21465 | -34.7738
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.8951 | 161 | -0.21465 | -34.5592
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9311 | 163 | -0.21465 | -34.9885
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.3546 | 409 | -0.21465 | -87.7932
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.018068 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -7.0104 | 388 | -0.21474 | -83.3189
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.018068 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.305 | 515 | -0.21474 | -110.5908
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.018366 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -7.9892 | 435 | -0.21504 | -93.5413
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.018377 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -7.2589 | 395 | -0.21505 | -84.9441
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.018377 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -7.994 | 435 | -0.21505 | -93.546
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.018459 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.73836 | 40 | -0.21513 | -8.6052
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.018466 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.36932 | 20 | -0.21514 | -4.3027
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.018467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.46168 | 25 | -0.21514 | -5.3785
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.018467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.75715 | 41 | -0.21514 | -8.8207
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4654 | 79 | -0.21522 | -17.0024
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.9662 | 106 | -0.21522 | -22.8134
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.7082 | 146 | -0.21522 | -31.4222
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.018549 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.4097 | 76 | -0.21522 | -16.3567
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4138 | 288 | -0.21547 | -62.0552
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7633 | 147 | -0.21547 | -31.674
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7633 | 147 | -0.21547 | -31.674
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.018884 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.5373 | 558 | -0.21556 | -120.2799
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.018884 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.9338 | 579 | -0.21556 | -124.8066
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.018884 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.2583 | 808 | -0.21556 | -174.1687
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.018969 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.4227 | 0 | -0.21564 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.018969 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.5099 | 0 | -0.21564 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.018969 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.6769 | 0 | -0.21564 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0421 | 160 | -0.21568 | -34.5095
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.966 | 156 | -0.21568 | -33.6468
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7265 | 196 | -0.21568 | -42.2741
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.966 | 156 | -0.21568 | -33.6468
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.985 | 157 | -0.21568 | -33.8624
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7646 | 198 | -0.21568 | -42.7055
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.019084 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -7.0611 | 370 | -0.21576 | -79.8295
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.6718 | 0 | -0.21576 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.6908 | 0 | -0.21576 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.897 | 0 | -0.21576 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.729 | 0 | -0.21576 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.7481 | 0 | -0.21576 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.916 | 0 | -0.21576 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.01925 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.2725 | 170 | -0.21592 | -36.7066
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.01925 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.01 | 520 | -0.21592 | -112.2791
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.019332 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.216 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.019381 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.77524 | 0 | -0.21605 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.019381 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.77524 | 0 | -0.21605 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.019856 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.21653 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.021754 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.4473 | 112.5 | -0.21843 | -24.5729
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.021865 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.21854 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.021865 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.21854 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.021865 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.21854 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.022646 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.3588 | 60 | -0.21932 | -13.159
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.022646 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4267 | 63 | -0.21932 | -13.817
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.5402 | 204 | -0.23363 | -47.6612
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.4294 | 201 | -0.23363 | -46.9603
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.9448 | 242 | -0.23363 | -56.5393
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.7522 | 20 | -0.23428 | -4.6856
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.7522 | 20 | -0.23428 | -4.6856
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.7522 | 20 | -0.23428 | -4.6856
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.63937 | 17 | -0.23428 | -3.9828
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.057392 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -21.0055 | 366 | -0.25406 | -92.9872
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.52665 | west | 6 | Y | N | Ywest | Nwest | 1 | -86.8964 | 165 | -0.72332 | -119.3472

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Longcreek - Cookfield 345kV [1439-1442] C: Fisher Road - Oklaunion 345kV [1425-6100] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.52665 | west | 6 | Y | N | Ywest | Nwest | 1 | -86.8964 | 0 | -0.72332 | 0 | 0 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.057392 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -21.0055 | 366 | -0.25406 | -92.9872 | 366 | 92.9872
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.7522 | 20 | -0.23428 | -4.6856 | 386 | 97.6728
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.7522 | 20 | -0.23428 | -4.6856 | 406 | 102.3585 | Weighted Shift Factors
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.7522 | 20 | -0.23428 | -4.6856 | 426 | 107.0441 | North | -0.016565
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.63937 | 17 | -0.23428 | -3.9828 | 443 | 111.0269 | West | 0.19667
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.5402 | 204 | -0.23363 | -47.6612 | 647 | 158.6881 |  | -0.21324
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.4294 | 201 | -0.23363 | -46.9603 | 848 | 205.6484
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.9448 | 242 | -0.23363 | -56.5393 | 1090 | 262.1877 | Line Rating | 1240
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.022646 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.3588 | 60 | -0.21932 | -13.159 | 1150 | 275.3467 | Conc Gen | 2433
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.022646 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4267 | 63 | -0.21932 | -13.817 | 1213 | 289.1637 | Weighted Imp. | 552.4884
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.021865 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.21854 | 0 | 1213 | 289.1637 | PTDF | 0.22708
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.021865 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.21854 | 0 | 1213 | 289.1637
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.021865 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.21854 | 0 | 1213 | 289.1637 | Concentration | -1.0649
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.021754 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.4473 | 0 | -0.21843 | 0 | 1213 | 289.1637
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.019856 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.21653 | 0 | 1213 | 289.1637
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.019381 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.77524 | 0 | -0.21605 | 0 | 1213 | 289.1637
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.019381 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.77524 | 0 | -0.21605 | 0 | 1213 | 289.1637
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.019332 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.216 | 0 | 1213 | 289.1637
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.01925 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.2725 | 170 | -0.21592 | -36.7066 | 1383 | 325.8703
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.01925 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.01 | 520 | -0.21592 | -112.2791 | 1903 | 438.1494
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.019084 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -7.0611 | 370 | -0.21576 | -79.8295 | 2273 | 517.9789
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.6718 | 0 | -0.21576 | 0 | 2273 | 517.9789
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.6908 | 0 | -0.21576 | 0 | 2273 | 517.9789
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.897 | 0 | -0.21576 | 0 | 2273 | 517.9789
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.729 | 0 | -0.21576 | 0 | 2273 | 517.9789
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.7481 | 0 | -0.21576 | 0 | 2273 | 517.9789
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.916 | 0 | -0.21576 | 0 | 2273 | 517.9789
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.0421 | 160 | -0.21568 | -34.5095 | 2433 | 552.4884
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.966 | 156 | -0.21568 | -33.6468
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7265 | 196 | -0.21568 | -42.2741
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.966 | 156 | -0.21568 | -33.6468
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.985 | 157 | -0.21568 | -33.8624
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7646 | 198 | -0.21568 | -42.7055
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.018969 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.4227 | 0 | -0.21564 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.018969 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.5099 | 0 | -0.21564 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.018969 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.6769 | 0 | -0.21564 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.018884 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.5373 | 0 | -0.21556 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.018884 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.9338 | 0 | -0.21556 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.018884 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.2583 | 0 | -0.21556 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4138 | 288 | -0.21547 | -62.0552
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7633 | 147 | -0.21547 | -31.674
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7633 | 147 | -0.21547 | -31.674
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4654 | 79 | -0.21522 | -17.0024
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.9662 | 106 | -0.21522 | -22.8134
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.7082 | 146 | -0.21522 | -31.4222
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.018549 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.4097 | 76 | -0.21522 | -16.3567
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.018467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.46168 | 25 | -0.21514 | -5.3785
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.018467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.75715 | 41 | -0.21514 | -8.8207
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.018466 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.36932 | 20 | -0.21514 | -4.3027
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.018459 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.73836 | 40 | -0.21513 | -8.6052
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.018377 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -7.2589 | 395 | -0.21505 | -84.9441
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.018377 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -7.994 | 435 | -0.21505 | -93.546
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.018366 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -7.9892 | 435 | -0.21504 | -93.5413
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.018068 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -7.0104 | 388 | -0.21474 | -83.3189
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.018068 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.305 | 515 | -0.21474 | -110.5908
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.8951 | 161 | -0.21465 | -34.5592
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.949 | 164 | -0.21465 | -35.2032
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.949 | 164 | -0.21465 | -35.2032
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.4445 | 414 | -0.21465 | -88.8665
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9131 | 162 | -0.21465 | -34.7738
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.8951 | 161 | -0.21465 | -34.5592
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9311 | 163 | -0.21465 | -34.9885
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.3546 | 409 | -0.21465 | -87.7932
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.017938 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.21461 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.017938 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.21461 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.017557 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.0717 | 118 | -0.21423 | -25.2789
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.017557 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.0191 | 115 | -0.21423 | -24.6363
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.017557 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.7617 | 556 | -0.21423 | -119.111
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.016756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.1535 | 0 | -0.21343 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.016756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.321 | 0 | -0.21343 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.016756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.0697 | 0 | -0.21343 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.4553 | 0 | -0.21326 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.1567 | 0 | -0.21326 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.4055 | 0 | -0.21326 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | -6.6194 | 0 | -0.21326 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.016465 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.9845 | 242 | -0.21314 | -51.579
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.01645 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.21312 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.016434 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.8217 | 0 | -0.21311 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.016407 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.9861 | 182 | -0.21308 | -38.7803
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.016407 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -7.941 | 484 | -0.21308 | -103.1299
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.016216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5091 | 216.4 | -0.21289 | -46.0688
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.016216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5043 | 216.1 | -0.21289 | -46.005
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.015849 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.1064 | 196 | -0.21252 | -41.654
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.015849 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.7592 | 111 | -0.21252 | -23.5898
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.015721 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.5215 | 224 | -0.21239 | -47.5759
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.4321 | 224 | -0.21199 | -47.4865
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.4628 | 226 | -0.21199 | -47.9105
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2483 | 212 | -0.21199 | -44.9426
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2329 | 211 | -0.21199 | -44.7306
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.2772 | 151.5 | -0.2117 | -32.0729
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.2892 | 152.3 | -0.2117 | -32.2423
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.668 | 177.5 | -0.2117 | -37.5772
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.2561 | 150.7 | -0.21164 | -31.8945
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.2606 | 151 | -0.21164 | -31.958
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.6559 | 177.4 | -0.21164 | -37.5454
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.014695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -9.0374 | 0 | -0.21137 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.014695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -8.626 | 0 | -0.21137 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.2477 | 18 | -0.21043 | -3.7878
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.2477 | 18 | -0.21043 | -3.7878
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.52292 | 38 | -0.21043 | -7.9964
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.013748 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.21042 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.013587 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.6304 | 0 | -0.21026 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.013173 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.8941 | 0 | -0.20984 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.013173 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.7887 | 0 | -0.20984 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.7927 | 0 | -0.20929 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.7927 | 0 | -0.20929 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9225 | 0 | -0.20929 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9313 | 0 | -0.20929 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.011279 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.8949 | 168 | -0.20795 | -34.9357
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.011279 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.0151 | 90 | -0.20795 | -18.7155
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.011251 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -5.2092 | 0 | -0.20792 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20791 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20791 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.011239 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.19106 | 17 | -0.20791 | -3.5345
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20791 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20791 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.01123 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.35936 | 0 | -0.2079 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.0112 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.5376 | 48 | -0.20787 | -9.9778
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.0112 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.5152 | 46 | -0.20787 | -9.5621
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.0112 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.176 | 105 | -0.20787 | -21.8265
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.010958 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20763 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.010958 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.6239 | 787 | -0.20763 | -163.4043
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.6709 | 0 | -0.20751 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.6904 | 0 | -0.20751 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.6904 | 0 | -0.20751 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | -4.1177 | 0 | -0.20751 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.73129 | 70 | -0.20712 | -14.4983
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.72084 | 69 | -0.20712 | -14.2912
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.72084 | 69 | -0.20712 | -14.2912
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.7104 | 68 | -0.20712 | -14.084
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.010406 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20708 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.010406 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.20708 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.2351 | 217.3 | -0.20696 | -44.9718
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.1086 | 205 | -0.20696 | -42.4263
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.8019 | 272.4 | -0.20696 | -56.3752
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.009989 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.5472 | 255 | -0.20666 | -52.6984
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.009989 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.4884 | 149 | -0.20666 | -30.7924
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.009989 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.5283 | 153 | -0.20666 | -31.619
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.009568 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.14352 | 0 | -0.20624 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.009568 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.14352 | 0 | -0.20624 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.00923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.3845 | 150 | -0.2059 | -30.8852
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.00923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.7384 | 80 | -0.2059 | -16.4721
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.009179 | north | 3 | N | N | Nnorth | Nnorth | 1 | -10.6201 | 0 | -0.20585 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.009179 | north | 3 | N | N | Nnorth | Nnorth | 1 | -10.6293 | 0 | -0.20585 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.008206 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.098472 | 0 | -0.20488 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.008206 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.098472 | 0 | -0.20488 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.006188 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.45172 | 73 | -0.20286 | -14.8087
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.006188 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.73637 | 119 | -0.20286 | -24.1403
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.006188 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.2685 | 205 | -0.20286 | -41.5862
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.006188 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.63118 | 102 | -0.20286 | -20.6917
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.006188 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.59405 | 96 | -0.20286 | -19.4745
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.0337 | 0 | -0.19701 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.19667 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.19667 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.02441 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.4646 | 0 | -0.17226 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.059084 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.13759 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.14784 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.176 | 0 | -0.048831 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.16616 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.030509 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.1867 | 0 | -0.023529 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.9025 | 0 | -0.023529 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | 43.1124 | 0 | -0.023529 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | 34.109 | 0 | -0.023529 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.18556 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.1337 | 0 | -0.01111 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.1865 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.666 | 0 | -0.010171 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.18684 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.2935 | 0 | -0.0098284 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.18779 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0229 | 0 | -0.0088854 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.1889 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.3358 | 0 | -0.0077664 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.1916 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.7394 | 0 | -0.0050754 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.1916 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.7394 | 0 | -0.0050754 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.1917 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3358 | 0 | -0.0049744 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.19172 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.3376 | 0 | -0.0049514 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.19187 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.3906 | 0 | -0.0047964 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.19187 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.35 | 0 | -0.0047964 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.19187 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.675 | 0 | -0.0047964 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.19262 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4098 | 0 | -0.0040484 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.19262 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.4098 | 0 | -0.0040484 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.19563 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.93903 | 0 | -0.0010404 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.109 | 0 | -0.00014738 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.3803 | 0 | -0.00014738 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.5535 | 0 | -0.00014738 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | 42.1544 | 0 | -0.00014738 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.19833 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.7498 | 0 | 0.0016606 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.1991 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.7243 | 0 | 0.0024276 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.20008 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3205 | 0 | 0.0034056 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.20008 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8626 | 0 | 0.0034056 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.20142 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.9409 | 0 | 0.0047516 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.20142 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.2868 | 0 | 0.0047516 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.20142 | west | 7 | N | N | Nwest | Nwest | 1 | 5.0356 | 0 | 0.0047516 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.20142 | west | 7 | N | N | Nwest | Nwest | 1 | 9.205 | 0 | 0.0047516 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.20142 | west | 7 | N | N | Nwest | Nwest | 1 | 9.205 | 0 | 0.0047516 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.20152 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.4142 | 0 | 0.0048476 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.20152 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.1823 | 0 | 0.0048476 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.20255 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.4585 | 0 | 0.0058756 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.20255 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.4585 | 0 | 0.0058756 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.20257 | west | 6 | Y | N | Ywest | Nwest | 1 | 45.578 | 0 | 0.0058976 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.20257 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.762 | 0 | 0.0059006 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.20272 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.095 | 0 | 0.0060436 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.20272 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0815 | 0 | 0.0060436 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.3814 | 66 | 0.0060776 | 0.40112
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.1787 | 65 | 0.0060776 | 0.39505
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.5842 | 67 | 0.0060776 | 0.4072
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.5842 | 67 | 0.0060776 | 0.4072
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.5842 | 67 | 0.0060776 | 0.4072
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.20275 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0060776 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.20275 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0060776 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.20276 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.2109 | 0 | 0.0060866 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.20284 | west | 8 | N | N | Nwest | Nwest | 1 | 5.2332 | 0 | 0.0061666 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.20327 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.3926 | 0 | 0.0066006 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.20355 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.4259 | 0 | 0.0068776 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.204 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.5022 | 0 | 0.0073306 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.20414 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.8401 | 0 | 0.0074676 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.20435 | west | 6 | Y | N | Ywest | Nwest | 1 | 43.7716 | 0 | 0.0076776 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5248 | 0 | 0.0077507 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.375 | 0 | 0.0077507 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3574 | 0 | 0.0077507 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3574 | 0 | 0.0077507 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.008814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4279 | 0 | 0.0077507 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.48138 | 56 | 0.0079687 | 0.44625
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.50716 | 59 | 0.0079687 | 0.47015
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.48138 | 56 | 0.0079687 | 0.44625
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.48138 | 56 | 0.0079687 | 0.44625
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.50716 | 59 | 0.0079687 | 0.47015
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.48138 | 56 | 0.0079687 | 0.44625
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.008572 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.4117 | 398 | 0.0079927 | 3.1811
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3928 | 0 | 0.0080097 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3808 | 0 | 0.0080097 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3594 | 0 | 0.0080097 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.303 | 0 | 0.0080097 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4649 | 172 | 0.0080477 | 1.3842
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4649 | 172 | 0.0080477 | 1.3842
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4649 | 172 | 0.0080477 | 1.3842
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.008514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3367 | 0 | 0.0080507 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.008502 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -6.317 | 743 | 0.0080627 | 5.9906
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55263 | 0 | 0.0080627 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56113 | 0 | 0.0080627 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59514 | 0 | 0.0080627 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53563 | 0 | 0.0080627 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52712 | 0 | 0.0080627 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88421 | 0 | 0.0080627 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50162 | 0 | 0.0080627 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.008501 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.10201 | 0 | 0.0080637 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.0085 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0425 | 0 | 0.0080647 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.0085 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1785 | 0 | 0.0080647 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.008487 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10184 | 12 | 0.0080777 | 0.096932
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28771 | 0 | 0.0081027 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.29363 | 0 | 0.0081027 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.27671 | 0 | 0.0081027 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38841 | 0 | 0.0081027 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14978 | 0 | 0.0081027 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17262 | 0 | 0.0081027 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16839 | 0 | 0.0081027 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.29617 | 0 | 0.0081027 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15232 | 0 | 0.0081027 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72265 | 0 | 0.0081027 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2524 | 0 | 0.0081027 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.008449 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -6.21 | 735 | 0.0081157 | 5.965
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.87766 | 104 | 0.0081257 | 0.84507
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.87766 | 104 | 0.0081257 | 0.84507
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45571 | 54 | 0.0081257 | 0.43879
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.44727 | 53 | 0.0081257 | 0.43066
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45571 | 54 | 0.0081257 | 0.43879
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.48102 | 57 | 0.0081257 | 0.46316
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45571 | 54 | 0.0081257 | 0.43879
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45571 | 54 | 0.0081257 | 0.43879
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.48946 | 58 | 0.0081257 | 0.47129
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.48946 | 58 | 0.0081257 | 0.47129
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.008383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4503 | 0 | 0.0081817 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.008383 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1317 | 0 | 0.0081817 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.008373 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1387 | 0 | 0.0081917 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.35162 | 42 | 0.0081927 | 0.34409
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.35162 | 42 | 0.0081927 | 0.34409
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31814 | 38 | 0.0081927 | 0.31132
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.31814 | 38 | 0.0081927 | 0.31132
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.592 | 0 | 0.0082267 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.60034 | 0 | 0.0082267 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32518 | 0 | 0.0082267 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25014 | 0 | 0.0082267 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4972 | 0 | 0.0082467 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3192 | 0 | 0.0082467 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3059 | 0 | 0.0082467 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.008317 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.8963 | 228 | 0.0082477 | 1.8805
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53229 | 0 | 0.0082477 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52563 | 0 | 0.0082477 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68698 | 0 | 0.0082477 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61213 | 0 | 0.0082477 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.008316 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13472 | 0 | 0.0082487 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.008316 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.7713 | 213 | 0.0082487 | 1.757
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.008313 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2386 | 0 | 0.0082517 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.008313 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.54118 | 0 | 0.0082517 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.008312 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.3715 | 165 | 0.0082527 | 1.3617
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.008311 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.4046 | 169 | 0.0082537 | 1.3949
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.008311 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.099732 | 12 | 0.0082537 | 0.099044
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.008311 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0082537 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.008297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2904 | 0 | 0.0082677 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3511 | 0 | 0.0082857 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3006 | 0 | 0.0082857 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3039 | 0 | 0.0082857 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2998 | 0 | 0.0082857 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.2271 | 0 | 0.0082857 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.008266 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.64475 | 0 | 0.0082987 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.008266 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.66128 | 0 | 0.0082987 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.3801 | 46 | 0.0083017 | 0.38188
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.3801 | 46 | 0.0083017 | 0.38188
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.3801 | 46 | 0.0083017 | 0.38188
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.45447 | 55 | 0.0083017 | 0.45659
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.45447 | 55 | 0.0083017 | 0.45659
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.4462 | 54 | 0.0083017 | 0.44829
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | 42.6866 | 208.2 | 0.0083556 | 1.7396
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | 29.1343 | 142.1 | 0.0083556 | 1.1873
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | 27.1456 | 132.4 | 0.0083556 | 1.1063
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | 27.8837 | 136 | 0.0083556 | 1.1364
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | 30.139 | 147 | 0.0083556 | 1.2283
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | 43.0557 | 210 | 0.0083556 | 1.7547
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.53346 | 0 | 0.0083577 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.49242 | 0 | 0.0083577 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.53346 | 0 | 0.0083577 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.53346 | 0 | 0.0083577 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.3534 | 70 | 0.0083776 | 0.58643
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.3534 | 70 | 0.0083776 | 0.58643
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | 19.0285 | 92.8 | 0.0083776 | 0.77744
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.4039 | 80 | 0.0083776 | 0.67021
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.4039 | 80 | 0.0083776 | 0.67021
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | 23.5806 | 115 | 0.0083776 | 0.96343
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74392 | 0 | 0.0083897 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71613 | 0 | 0.0083897 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71122 | 0 | 0.0083897 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.44554 | 0 | 0.0083897 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.099735 | 0 | 0.0083897 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.008093 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0084717 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.008037 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.40185 | 50 | 0.0085277 | 0.42638
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56173 | 0 | 0.0086307 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5292 | 0 | 0.0086307 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4205 | 0 | 0.0086307 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2155 | 0 | 0.0086307 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2179 | 0 | 0.0086307 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2083 | 0 | 0.0086307 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.76166 | 0 | 0.0086307 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9359 | 0 | 0.0086307 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31736 | 0 | 0.0086307 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.007933 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25386 | 0 | 0.0086317 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.007933 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23799 | 0 | 0.0086317 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79568 | 0 | 0.0086317 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.73698 | 0 | 0.0086317 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.81472 | 0 | 0.0086317 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.80917 | 0 | 0.0086317 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2477 | 161 | 0.0088147 | 1.4192
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2865 | 166 | 0.0088147 | 1.4632
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.922 | 248 | 0.0088147 | 2.186
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.00775 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.2315 | 546 | 0.0088147 | 4.8128
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.00775 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -4.9832 | 0 | 0.0088147 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.00775 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10075 | 13 | 0.0088147 | 0.11459
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.007689 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25374 | 0 | 0.0088757 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2502 | 0 | 0.0088947 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2502 | 0 | 0.0088947 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8792 | 0 | 0.0088947 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.9912 | 0 | 0.0088977 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.3242 | 0 | 0.0088977 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.6002 | 0 | 0.0088977 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.007625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35151 | 0 | 0.0089397 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.5724 | 66 | 0.0089706 | 0.59206
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | 14.1893 | 69 | 0.0089706 | 0.61897
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | 14.1893 | 69 | 0.0089706 | 0.61897
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.778 | 67 | 0.0089706 | 0.60103
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.778 | 67 | 0.0089706 | 0.60103
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | 13.3667 | 65 | 0.0089706 | 0.58309
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79909 | 0 | 0.0093657 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79909 | 0 | 0.0093657 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.85668 | 0 | 0.0093657 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.78829 | 0 | 0.0093657 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.007066 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50169 | 0 | 0.0094987 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.007066 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.07066 | 0 | 0.0094987 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42836 | 0 | 0.0096557 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4933 | 0 | 0.0096557 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3109 | 0 | 0.0096557 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69781 | 0 | 0.0096557 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59417 | 0 | 0.0096557 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.60799 | 0 | 0.0096557 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34545 | 0 | 0.0096557 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12436 | 0 | 0.0096557 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64945 | 0 | 0.0096557 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.48363 | 0 | 0.0096557 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43527 | 0 | 0.0096557 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49745 | 0 | 0.0096557 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4477 | 0 | 0.0096557 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69781 | 0 | 0.0096557 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.67017 | 0 | 0.0096557 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71163 | 0 | 0.0096557 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52508 | 0 | 0.0096557 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55272 | 0 | 0.0096557 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55272 | 0 | 0.0096557 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1814 | 0 | 0.0096557 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.20665 | west | 8 | N | N | Nwest | Nwest | 1 | 14.4657 | 0 | 0.0099816 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.20665 | west | 8 | N | N | Nwest | Nwest | 1 | 15.1683 | 0 | 0.0099816 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.20665 | west | 8 | N | N | Nwest | Nwest | 1 | 14.5484 | 0 | 0.0099816 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.006258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.41303 | 66 | 0.010307 | 0.68024
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.006219 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -3.5386 | 0 | 0.010346 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.006219 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -3.6132 | 0 | 0.010346 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.0598 | 0 | 0.010394 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | 45.5543 | 0 | 0.010394 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | 41.413 | 0 | 0.010394 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.2412 | 0 | 0.010394 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.46786 | 76 | 0.010409 | 0.79106
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.46786 | 76 | 0.010409 | 0.79106
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.64638 | 105 | 0.010409 | 1.0929
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45554 | 74 | 0.010409 | 0.77024
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.45554 | 74 | 0.010409 | 0.77024
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.62791 | 102 | 0.010409 | 1.0617
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.006038 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -8.0487 | 0 | 0.010527 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.006038 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -8.0185 | 0 | 0.010527 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.20738 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.1072 | 0 | 0.01071 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.20738 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9455 | 0 | 0.01071 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.004496 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.6257 | 0 | 0.012069 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.004496 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.6751 | 0 | 0.012069 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.004494 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.9459 | 0 | 0.012071 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.70278 | 158 | 0.012117 | 1.9144
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.71168 | 160 | 0.012117 | 1.9387
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.7784 | 175 | 0.012117 | 2.1204
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2161 | 50 | 0.012243 | 0.61213
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2161 | 50 | 0.012243 | 0.61213
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2161 | 50 | 0.012243 | 0.61213
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2161 | 50 | 0.012243 | 0.61213
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.62006 | 152.5 | 0.012499 | 1.906
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60787 | 149.5 | 0.012499 | 1.8686
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.94575 | 232.6 | 0.012499 | 2.9072
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.53341 | 132 | 0.012524 | 1.6531
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.54149 | 134 | 0.012524 | 1.6782
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3052 | 323 | 0.012524 | 4.0451
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.15288 | 42 | 0.012925 | 0.54284
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16016 | 44 | 0.012925 | 0.56869
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16016 | 44 | 0.012925 | 0.56869
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17108 | 47 | 0.012925 | 0.60746
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.003479 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0785 | 310 | 0.013086 | 4.0566
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.003479 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4368 | 413 | 0.013086 | 5.4044
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27397 | 0 | 0.013097 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28091 | 0 | 0.013097 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27397 | 0 | 0.013097 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27744 | 0 | 0.013097 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27189 | 0 | 0.013097 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0867 | 0 | 0.013097 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.15953 | 0 | 0.013097 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.097104 | 0 | 0.013097 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.1512 | 0 | 0.013097 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.25663 | 0 | 0.013097 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16817 | 49 | 0.013133 | 0.6435
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.15787 | 46 | 0.013133 | 0.6041
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.15787 | 46 | 0.013133 | 0.6041
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1613 | 47 | 0.013133 | 0.61724
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.52853 | 154 | 0.013133 | 2.0224
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.50794 | 148 | 0.013133 | 1.9436
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16474 | 48 | 0.013133 | 0.63037
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16474 | 48 | 0.013133 | 0.63037
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.003392 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.16282 | 0 | 0.013173 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.003287 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.026296 | 0 | 0.013278 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.003287 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.026296 | 0 | 0.013278 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.087164 | 0 | 0.013452 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.021791 | 0 | 0.013452 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12141 | 0 | 0.013452 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.046695 | 0 | 0.013452 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.021791 | 0 | 0.013452 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.046695 | 0 | 0.013452 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12141 | 0 | 0.013452 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12141 | 0 | 0.013452 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.003059 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.024472 | 0 | 0.013506 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.003035 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.045525 | 0 | 0.01353 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.003035 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.069805 | 0 | 0.01353 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.00293 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.21389 | 0 | 0.013635 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.002853 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.41083 | 144 | 0.013712 | 1.9745
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.002853 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.53636 | 188 | 0.013712 | 2.5778
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13318 | 47.7 | 0.013773 | 0.65696
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.10414 | 37.3 | 0.013773 | 0.51372
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.12843 | 46 | 0.013773 | 0.63354
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13402 | 48 | 0.013773 | 0.66109
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.002687 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.032244 | 0 | 0.013878 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.00267 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.006408 | 0 | 0.013895 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.00267 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.006408 | 0 | 0.013895 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.002652 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.058344 | 22 | 0.013913 | 0.30608
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.002652 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.029172 | 11 | 0.013913 | 0.15304
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.002652 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.029172 | 11 | 0.013913 | 0.15304
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.56759 | 223.9 | 0.01403 | 3.1412
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.57037 | 225 | 0.01403 | 3.1567
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.56936 | 224.6 | 0.01403 | 3.1511
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.57468 | 226.7 | 0.01403 | 3.1805
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.33285 | 142 | 0.014221 | 2.0193
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.33988 | 145 | 0.014221 | 2.062
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.35394 | 151 | 0.014221 | 2.1473
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.67976 | 290 | 0.014221 | 4.124
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.3694 | 0 | 0.014227 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.35771 | 0 | 0.014227 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.2338 | 0 | 0.014227 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.33901 | 0 | 0.014227 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.34369 | 0 | 0.014227 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.29693 | 0 | 0.014227 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.002338 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.028056 | 0 | 0.014227 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.002337 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0056088 | 0 | 0.014228 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.002337 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0056088 | 0 | 0.014228 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.002337 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0065436 | 0 | 0.014228 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05685 | 0 | 0.014291 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05685 | 0 | 0.014291 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05685 | 0 | 0.014291 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.036384 | 0 | 0.014291 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05685 | 0 | 0.014291 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05685 | 0 | 0.014291 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.05685 | 0 | 0.014291 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.03411 | 0 | 0.014291 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.002193 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.3794 | 0 | 0.014372 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.002186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.7345 | 336 | 0.014379 | 4.8312
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.002186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.39348 | 180 | 0.014379 | 2.5882
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.002185 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.32404 | 0 | 0.01438 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.002185 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.32469 | 0 | 0.01438 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.002185 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.33431 | 0 | 0.01438 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.002182 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.39276 | 180 | 0.014383 | 2.5889
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.002157 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.72044 | 334 | 0.014408 | 4.8122
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.002157 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.73338 | 340 | 0.014408 | 4.8986
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.002157 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.38826 | 180 | 0.014408 | 2.5934
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.002157 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.38826 | 180 | 0.014408 | 2.5934
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.31561 | 147 | 0.014418 | 2.1194
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.29629 | 138 | 0.014418 | 1.9896
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.30058 | 140 | 0.014418 | 2.0185
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.31561 | 147 | 0.014418 | 2.1194
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.39075 | 182 | 0.014418 | 2.624
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.42511 | 198 | 0.014418 | 2.8547
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.002139 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.053475 | 0 | 0.014426 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.002139 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.053475 | 0 | 0.014426 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.002137 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.081206 | 0 | 0.014428 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.002119 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.080522 | 0 | 0.014446 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.002052 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.012312 | 0 | 0.014513 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.002041 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.059189 | 0 | 0.014524 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.002018 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.008072 | 0 | 0.014547 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.1849 | 0 | 0.014598 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.080647 | 0 | 0.014598 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.074746 | 0 | 0.014598 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.037373 | 0 | 0.014598 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.1849 | 0 | 0.014598 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.070812 | 0 | 0.014598 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.084581 | 0 | 0.014598 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.043274 | 0 | 0.014598 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.29112 | 0 | 0.014598 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.09835 | 0 | 0.014598 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.10819 | 0 | 0.014598 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.09835 | 0 | 0.014598 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.072466 | 38 | 0.014658 | 0.55699
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.036805 | 19.3 | 0.014658 | 0.28289
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.028605 | 15 | 0.014658 | 0.21987
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.001907 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.089629 | 47 | 0.014658 | 0.68891
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.001907 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.014658 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25258 | 144 | 0.014811 | 2.1327
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25258 | 144 | 0.014811 | 2.1327
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.29993 | 171 | 0.014811 | 2.5326
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.36308 | 207 | 0.014811 | 3.0658
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.38009 | 216.7 | 0.014811 | 3.2095
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.42447 | 242 | 0.014811 | 3.5842
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.001597 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.87196 | 0 | 0.014968 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.001597 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.1978 | 0 | 0.014968 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.2196 | 146.5 | 0.015066 | 2.2071
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.2217 | 147.9 | 0.015066 | 2.2282
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25933 | 173 | 0.015066 | 2.6064
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.22925 | 155 | 0.015086 | 2.3383
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.25143 | 170 | 0.015086 | 2.5646
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.22925 | 155 | 0.015086 | 2.3383
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.015162 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.015162 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.015162 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.001311 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.015254 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.001242 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.04347 | 0 | 0.015323 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.001242 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.042228 | 0 | 0.015323 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.001242 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.04347 | 0 | 0.015323 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.001176 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.015389 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.001147 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.48633 | 0 | 0.015418 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.001147 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.48747 | 0 | 0.015418 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.001086 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.44743 | 412 | 0.015479 | 6.3772
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.001086 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.4344 | 400 | 0.015479 | 6.1915
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.001084 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.22656 | 209 | 0.015481 | 3.2355
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.001084 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.23414 | 216 | 0.015481 | 3.3438
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.049864 | 46 | 0.015481 | 0.71211
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.050948 | 47 | 0.015481 | 0.72759
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.049864 | 46 | 0.015481 | 0.71211
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.049864 | 46 | 0.015481 | 0.71211
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.001048 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.41501 | 0 | 0.015517 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.000964 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.39235 | 407 | 0.015601 | 6.3495
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.000617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.035786 | 58 | 0.015948 | 0.92497
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.000617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.054913 | 89 | 0.015948 | 1.4193
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.027148 | 44 | 0.015948 | 0.7017
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.027148 | 44 | 0.015948 | 0.7017
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.026531 | 43 | 0.015948 | 0.68575
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.027765 | 45 | 0.015948 | 0.71765
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.038418 | 0 | 0.016228 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.074814 | 0 | 0.016228 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.062008 | 0 | 0.016228 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.075488 | 0 | 0.016228 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.038755 | 0 | 0.016228 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016565 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016565 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016565 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016565 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016565 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016565 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.016565 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.016565 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 3e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00036 | 0 | 0.016595 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 3e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00033 | 0 | 0.016595 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 3e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00036 | 0 | 0.016595 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.21461 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.3764 | 0 | 0.017939 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.001494 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.018059 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.003174 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.3174 | 100 | 0.019739 | 1.9739
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.003174 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.3174 | 100 | 0.019739 | 1.9739
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.019739 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.019739 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.019739 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.019739 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.003177 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.019742 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.059364 | 0 | 0.019863 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.059364 | 0 | 0.019863 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.004798 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13434 | 0 | 0.021363 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.004798 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13914 | 0 | 0.021363 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.0053 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 2.2366 | 422 | 0.021865 | 9.2269
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.005652 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10174 | 0 | 0.022217 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.005652 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10174 | 0 | 0.022217 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.005652 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.08478 | 0 | 0.022217 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.006121 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.1469 | 24 | 0.022686 | 0.54446
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.006121 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.1469 | 24 | 0.022686 | 0.54446
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.006121 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.14078 | 23 | 0.022686 | 0.52177
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.063865 | 8.4 | 0.024168 | 0.20301
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00796 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10905 | 0 | 0.024525 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.22138 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.6724 | 0 | 0.024708 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.22138 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.6724 | 0 | 0.024708 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.22648 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.1782 | 0 | 0.029814 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.22648 | west | 6 | Y | N | Ywest | Nwest | 1 | 52.771 | 0 | 0.029814 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.22648 | west | 6 | Y | N | Ywest | Nwest | 1 | 38.5477 | 0 | 0.029814 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8034 | 0 | 0.038085 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.2363 | 0 | 0.038085 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | 31.6921 | 0 | 0.038085 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.936 | 0 | 0.038085 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.6494 | 0 | 0.038085 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.8979 | 0 | 0.038085 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.24757 | west | 4 | Y | N | Ywest | Nwest | 1 | 160.8469 | 0 | 0.0509 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.035876 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.052441 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.039493 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.23696 | 0 | 0.056058 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.055041 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8164 | 0 | 0.071606 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.055041 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.376 | 0 | 0.071606 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.055041 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.071606 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.32331 | west | 6 | Y | N | Ywest | Nwest | 1 | 129.322 | 0 | 0.12663 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.32518 | west | 6 | Y | N | Ywest | Nwest | 1 | 76.7427 | 0 | 0.12851 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
Average line rating
| 20 | 1340
| 25 | 1340
| 30 | 1340
| 35 | 1340
| 40 | 1340
| 45 | 1340
| 50 | 1340
| 55 | 1340
| 60 | 1334
| 65 | 1307
| 70 | 1280
| 75 | 1251
| 80 | 1223
| 85 | 1194
| 90 | 1163
| 95 | 1132
| 100 | 1098
| 105 | 1065
| 110 | 1031
| 115 | 994
| avg | 1239.6