## test results
CRE test for: |  | 1427 FISHERRD - 1448 WCHTFLLS | [5 empty] | FAIL
Line Rating: |  | 260
Direcction |  | North | → | West |  | N-W
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 1427 FISHERRD - 1448 WCHTFLLS
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.0033863
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.00033797
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.051963
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.00083119
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 1427 FISHERRD - 1448 WCHTFLLS
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.0037361
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.00040266
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.036774
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.0008509
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 1427 FISHERRD - 1448 WCHTFLLS
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.003789
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.04016
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.0025354
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.036436
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.0011692
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.052814
PTDF tests
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.04016 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.04016 | -0.003789
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.2171
[6 empty] | Concentration |  | -5.4059 | FAIL
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.06273
[6 empty] | Concentration |  | -1.562 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 37.011
| Percent of line rating => | [6 empty] | 14.24% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -20.288
[7 empty] | B1(N-S) | -0.036744 | 0.040127 | 0.076871 | -0.036744
[7 empty] | B2 (N-W) | 0 | 0.81477 | 0.81477 | 0
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.032464 | 0.018975 | 0.051439 | -0.032464
[7 empty] | B4 (S-W) | 0.03656 | 0.77577 | 0.73921 | 0.03656
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.0036957 | -0.020024 | -0.02372 | 0.0036957
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.27855 | -0.79294 | -1.0715 | 0.27855
[7 empty] | test | 0 | 0.81477 | 0.81477 | 0
[7 empty] | B1 | -4.51%
Deployment Error Percent | [6 empty] | B2 | 0%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -3.984%
[7 empty] | B4 | 4.487%
[7 empty] | B5 | 0.4536%
[7 empty] | B6 | 34.19%
[7 empty] | Max Abs Error | 34.19% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-W
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:1427 FISHERRD - 1448 WCHTFLLS C:1422 BOWMAN_5 - 1425 FISHRDSS | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:1427 FISHERRD - 1448 WCHTFLLS C:1422 BOWMAN_5 - 1425 FISHRDSS
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.001384 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -0.35292
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.001384 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -0.20622
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.001727 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.025905
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.001727 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.025905
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.001384 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -0.21175
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.001369 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -0.20535
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.001369 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -0.10952
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.007205 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -0.52597
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.007205 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -0.8574
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.007205 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -1.477
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.007205 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -0.73491
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.007205 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -0.69168
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.023305 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.27966
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.023305 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.27966
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.00194 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -0.32592
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.00194 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -0.1746
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.011303 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.20345
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.011303 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.20345
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.011303 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -0.42951
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.022113 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -6.3685
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.022113 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -3.2506
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.022113 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -3.2506
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.025921 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -2.9161
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.00327 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -0.1308
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.003304 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -0.26102
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.003304 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -0.35022
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.003304 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -0.48238
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.003304 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -0.2511
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.006106 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -0.36636
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.006106 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -0.38468
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.00328 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -0.0656
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.00328 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -0.082
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.00328 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -0.13448
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.00148 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -0.68524
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 2.5974
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 2.558
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.6367
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.6367
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.6367
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039354 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 4.4864
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.039354 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 20.2673
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 2.6892
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.8114
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.8114
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 2.7299
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 2.7299
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 2.6484
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.039624 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 2.7737
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.039624 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 2.9084
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.039624 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 2.7895
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.03963 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 5.9445
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.03963 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 8.7186
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.04286 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 4.2431
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.04286 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 2.6145
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.042784 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 6.0325
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.04286 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 1.0715
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.04286 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.9587
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.04286 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.9587
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.042784 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 5.1341
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.040649 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 1.0487
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.040051 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 4.0251
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.040893 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 4.9072
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.040098 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 2.3257
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.040189 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 8.6085
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.045271 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 6.7907
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.040244 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.26561
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.040244 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 1.3804
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.045271 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 4.5724
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.041046 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 4.9255
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.00224 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 0.81984
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.019748 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -4.779
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.034332 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 13.7328
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.034234 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 8.0792
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.026556 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 4.3817
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.004897 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -0.99899
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.004897 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -0.9843
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.004897 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -1.1851
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.047669 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.95338
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.047669 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.95338
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.047669 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.95338
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.047669 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -0.81037
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.015829 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -1.8995
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.001229 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 0.07374
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.003667 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -0.27503
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.003667 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -0.29189
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.003667 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -0.32416
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -0.58176
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -0.56722
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -0.71266
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -0.56722
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -0.57085
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -0.71993
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.004172 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -0.70924
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.004172 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -2.1694
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003687 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -1.3642
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.003486 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -1.9452
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.003486 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -2.0184
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.003486 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -2.8167
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.004829 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -0.54085
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.004829 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -0.4829
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.004829 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -1.8254
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.000497 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -0.108
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.000497 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -0.10189
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.000497 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -0.13538
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.001209 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -0.93093
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.001896 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -0.13272
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.001896 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.13082
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.001896 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.13082
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.001896 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -0.12893
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.000231 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -0.26727
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.000231 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -0.2675
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.002027 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -0.45405
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.002027 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -0.4581
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.002273 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -0.49188
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.002273 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -0.4912
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.002027 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -0.42972
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.002027 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -0.4277
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.002753 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -1.0874
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.002821 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -1.2271
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.002753 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -1.1976
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.004004 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -0.55255
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.002824 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -0.33323
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.002824 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -0.32476
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.002824 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -1.5701
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.003107 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -1.2055
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.003107 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -1.6001
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.002742 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -2.1525
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.002742 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -2.1799
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.002742 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -2.1388
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.002646 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -0.48157
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.002646 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -1.2807
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.002497 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -0.55933
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.002646 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -0.1323
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.002651 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -0.11134
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.002152 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -1.3235
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.002152 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -1.2632
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.001403 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -0.75341
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.001403 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -1.1042
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.001326 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -0.09945
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.001326 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -0.29437
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.000471 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -0.268
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.00056 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 0.11704
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.00056 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 0.12096
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.000584 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 0.23769
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.00056 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.02576
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.00056 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 0.02632
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.00056 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.02576
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.00056 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.02576
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.000547 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 0.23193
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.000547 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 0.23247
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000653 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 0.037874
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000653 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 0.058117
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000653 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.028732
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000653 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.028732
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000653 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 0.028079
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000653 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 0.029385
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.000559 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 0.23031
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.000559 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 0.2236
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.000457 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 0.24952
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.000457 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 0.34275
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.000496 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 0.030256
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.000496 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 0.04712
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.000496 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 0.074896
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.000481 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.074555
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.000481 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 0.08177
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.000481 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.074555
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.000244 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.005368
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.000244 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.002684
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.000244 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.002684
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.000216 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 0.010303
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.000216 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.0080568
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.000216 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 0.009936
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.000216 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 0.010368
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000778 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.009336
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000778 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.008558
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.001991 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.047784
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.001991 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.047784
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.001991 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.045793
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.000565 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 0.22374
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.000434 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -0.57852
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.000434 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -0.57635
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.000393 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.014934
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.000393 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.0075849
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.000393 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.005895
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.000393 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 0.018471
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.037626 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 2.822
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.050233 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 7.535
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.046069 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 7.8087
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.030657 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 4.5986
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.042268 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 2.6629
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.25388 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 164.9426
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.004494 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.17976
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.004494 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.17976
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.001859 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 0.7845
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -3.2e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -0.004224
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -3.2e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -0.004288
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -3.2e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -0.010336
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.000114 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -0.018012
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.000114 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -0.01824
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.000114 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -0.01995
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.000124 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -0.072416
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.000124 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -0.07378
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.000123 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -0.053259
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.00027 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 0.060453
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.00027 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 0.06075
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.00027 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 0.060642
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.00027 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 0.061209
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.00012 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.00096
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.00012 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.00096
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.001926 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.034668
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.001926 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.034668
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.001926 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.02889
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.002398 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.032853
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.001453 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.026154
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.001453 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.026154
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000533 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.018655
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000533 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.018122
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.000533 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.018655
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.001756 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.049168
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.001756 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.050924
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.039435 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 1.3802
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.039435 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 1.183
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.00445
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.00445
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.00445
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.00445
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.000368 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.002208
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.000309 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0007416
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.000309 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0007416
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.000309 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.0008652
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.000373 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.001492
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.000242 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0005808
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.000242 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0005808
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.051009
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 0.047886
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 0.04858
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.051009
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 0.063154
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 0.068706
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -3.7e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -0.0056425
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -3.7e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -0.0055315
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -3.7e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -0.0086062
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.000308 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 0.043736
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.000308 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 0.04466
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.000308 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 0.046508
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.000308 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 0.08932
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.011717 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.38666
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.011717 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.29292
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000778 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.009336
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.000188 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 0.013724
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.006399
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 0.006561
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.004256
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.001064
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.006399
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 0.00648
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 0.0063504
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.002025
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.003726
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.000336 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 0.21134
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.000204 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 0.029376
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.000204 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 0.038352
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.000238 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.002856
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.008626 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.051756
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.000337 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 0.11323
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.000343 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 0.11456
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.000343 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 0.11662
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.00035 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.0133
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.000346 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.00865
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.000346 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.00865
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.000347 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.013186
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.000366 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.010614
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.000337 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 0.049977
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.000337 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 0.050078
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.000337 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 0.051561
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 0.048506
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 0.046971
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 0.0307
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 0.044515
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 0.045129
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 0.038989
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.000474 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 0.069441
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.000474 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 0.070105
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.000474 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 0.082002
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 0.087561
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 0.091664
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 0.10237
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.060912
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.060912
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 0.072333
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 8.1e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 0.02511
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 8.1e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 0.033453
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 4.8e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.002016
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 4.8e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.002112
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 4.8e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.002112
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 4.8e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.002256
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.00441
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.00414
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.00414
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.00423
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 9e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 0.01386
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 9e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 0.01332
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.00432
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.00432
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.7651
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.7651
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 3.6657
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 3.1601
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 3.1601
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 4.5426
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 8.2239
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 5.6129
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 5.2298
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 5.372
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 5.8065
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 8.295
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.034797 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 7.2726
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.034797 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 4.4018
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.034797 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 8.6645
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.034797 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 6.855
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.03963 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 7.926
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.03963 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 4.8309
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.039632 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 5.9052
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.041689 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 7.504
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.041689 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 7.504
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.041608 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 9.3618
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.039028 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 4.8785
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.039028 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 4.8785
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -0.51618
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -0.51987
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -1.1393
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -0.52724
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -0.53093
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -1.143
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.002453 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -0.48079
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.002453 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -0.27228
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.003555 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -0.50071
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -0.51004
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -0.51004
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -1.2875
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -0.50382
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -0.50071
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -0.50693
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -1.272
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.003035 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.003035 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.002692 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -0.39842
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.002692 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -0.34996
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.002692 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -0.39034
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.002692 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -1.0741
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.00222 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -0.33455
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.00222 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -0.33522
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.00222 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -0.39383
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.002244 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -0.33997
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.002244 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -0.34176
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.002244 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -0.39831
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.000471 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -0.27365
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.001756 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -1.5014
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.001756 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -1.5014
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.001477 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.047264
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.001472 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -0.070656
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.001472 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -0.067712
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.001479 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.017748
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.001479 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -0.075429
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.001479 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.025143
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.001479 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.032538
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.001479 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.036975
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.001472 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -0.15456
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.044229 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 3.7152
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.037597 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 3.0078
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.03758 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 5.637
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.03758 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 5.637
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.057631
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.054294
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.043142
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -0.1247
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -0.12495
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -0.12397
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.078144
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -0.19862
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.03256
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -0.081644
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.075621
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -0.083598
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -0.083028
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.026048
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.02442
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.000667 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.074037
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.000667 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.074037
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.000667 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -0.079373
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.000667 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -0.073037
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.001756 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -0.26744
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.001756 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -0.26867
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.000902 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -0.12267
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.000765 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.025245
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.000902 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.037884
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.000902 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.037884
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.000902 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.034276
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.000902 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.034276
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.00064 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.04544
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.00064 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.0064
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.000761 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.12404
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.000761 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.12404
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.000761 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -0.18644
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.000869 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.056485
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.000869 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.05214
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.000869 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.056485
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.000869 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.056485
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.00089 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -0.13261
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.00089 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.057939
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.078533
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.075599
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.075081
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.047033
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.010529
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.000928 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -0.6895
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.000918 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -0.67473
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.000931 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.16013
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.000931 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.16013
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.000931 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.16013
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000991 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -0.17144
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.000904 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -0.15639
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.000904 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -0.12204
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.000939 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -0.15287
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.000939 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -0.15155
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.000939 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -0.14921
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.000939 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -0.25278
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.057024
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.056311
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.073597
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.065578
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -0.14411
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -0.13872
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -0.13907
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -0.13863
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -0.23753
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.00464
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.019488
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.001396 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -0.21526
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.001396 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.21778
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.001396 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.21778
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.001396 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -0.53048
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.000942 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -0.37492
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.04048
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.04048
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.04048
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.0484
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.0484
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.04752
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.001867 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -1.544
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.001867 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -1.5291
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.000752 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.034667
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.034808
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.034808
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -0.04809
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.033892
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.033892
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -0.046716
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.000891 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -0.16038
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.000891 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -0.14131
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.000891 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -0.13989
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.000887 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.031045
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.000846 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -0.38831
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.06032
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.061248
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.06496
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.058464
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.057536
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -0.096512
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.054752
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000991 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -0.1546
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000991 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.15261
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000991 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.15261
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000991 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -0.16054
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.000931 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -0.14617
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.000895 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.063545
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.000895 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.06444
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.000895 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.034905
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.000895 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.02685
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.000881 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.068718
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.000881 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.07048
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.014434
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.00089 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -0.14685
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.00089 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -0.15041
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.000891 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -0.18978
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.000891 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -0.20315
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.00089 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.01068
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.00089 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.01602
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.000835 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.04175
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.095264
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.095264
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.049464
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.048548
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.049464
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.052212
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.049464
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.049464
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.053128
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.053128
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.000925 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.0111
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.053032
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.055873
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.053032
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.053032
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.055873
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.053032
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.000478 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -0.031548
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000777 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -0.1251
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000777 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -0.12898
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000777 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -0.1927
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000777 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -0.42424
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000777 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -0.49961
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.000761 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -0.49541
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.000761 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -0.4292
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.000761 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -0.4566
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000777 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.010101
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.000928 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.011136
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.03128
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.031924
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.030084
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.042228
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.016284
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.018768
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.018308
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.0322
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.01656
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.078568
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -0.13616
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.037758
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -0.043483
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.027405
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.061509
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -0.052374
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -0.053592
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.03045
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.010962
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -0.057246
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -0.04263
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.038367
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -0.043848
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.039463
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.061509
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -0.059073
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -0.062727
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -0.046284
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.04872
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.04872
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -0.10414
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.019202
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.036842 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 2.8184
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.037626 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 3.0101
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.037626 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 1.505
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.037749 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 3.0199
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.0376 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 3.008
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.036962 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 2.957
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.036753 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 3.0873
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.037749 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 3.0199
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 0.081396
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.048933 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 5.872
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.048933 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 11.4014
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.048933 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 8.3284
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 0.15851
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 0.13138
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 0.15994
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 0.08211
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 0.0714
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.074307 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 4.4584
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.012817 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.033436 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.038222 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.18347
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 1.814
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 5.2002
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 6.5305
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 5.7565
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 5.0793
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 3.8941
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.039029 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 5.8544
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.038905 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 4.3768
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.038905 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 5.8163
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.038905 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 7.2363
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.038905 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 8.3451
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.000393 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.007907 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.001405 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.002268
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.0035316
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 0.005994
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.035814
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.015621
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.014478
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.007239
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.035814
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.013716
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 0.016383
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.008382
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.005928
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.00228
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.001064
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.00228
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.005928
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.005928
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 0.056388
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.01905
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 0.020955
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.01905
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.000307 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.003684
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.000167 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.002505
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.000167 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.003841
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 9.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.004608
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.000163 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.001304
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.000338 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 0.06084
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.000337 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 0.06066
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.000343 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.06174
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.000343 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.06174
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001404 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.1404
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001404 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.1404
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.007975
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.007975
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.007975
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.005104
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.007975
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.007975
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.007975
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.004785
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001404 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001404 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 0.702
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001404 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 0.702
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.001404 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.000512 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.011717 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.00107 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.000538 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L:1427 FISHERRD - 1448 WCHTFLLS C:1422 BOWMAN_5 - 1425 FISHRDSS | [7 empty] | 37.011
Number of Bus | Name of Bus | ID | Max MW | L:1427 FISHERRD - 1448 WCHTFLLS C:1422 BOWMAN_5 - 1425 FISHRDSS | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.001384 | north | 0.0020023 | -0.001722 | -0.053347 | -0.00055281 | 0.00055281 | houston | Y | 0.0020023 | 0.36963
239 | BOSQUESW | 1 | 149 | -0.001384 | north | 0.0020023 | -0.001722 | -0.053347 | -0.00055281 | 0.00055281 | houston | Y | 0.0020023 | 0.21598
244 | WHITNYDM | 1 | 15 | -0.001727 | north | 0.0016593 | -0.002065 | -0.05369 | -0.00089581 | 0.00089581 | houston | Y | 0.0016593 | 0.011453
245 | WHITNYDM | 2 | 15 | -0.001727 | north | 0.0016593 | -0.002065 | -0.05369 | -0.00089581 | 0.00089581 | houston | Y | 0.0016593 | 0.011453
247 | BOSQUESW | 2 | 153 | -0.001384 | north | 0.0020023 | -0.001722 | -0.053347 | -0.00055281 | 0.00055281 | houston | Y | 0.0020023 | 0.22178
251 | BOSQUESW | 2 | 150 | -0.001369 | north | 0.0020173 | -0.001707 | -0.053332 | -0.00053781 | 0.00053781 | houston | Y | 0.0020173 | 0.22193
253 | BOSQUESW | 2 | 80 | -0.001369 | north | 0.0020173 | -0.001707 | -0.053332 | -0.00053781 | 0.00053781 | houston | Y | 0.0020173 | 0.11836
332 | RWMILLER | 1 | 73 | -0.007205 | north | -0.0038187 | -0.007543 | -0.059168 | -0.0063738 | 0.0038187 | North | N | 0.0038187 | 0
333 | RWMILLER | 2 | 119 | -0.007205 | north | -0.0038187 | -0.007543 | -0.059168 | -0.0063738 | 0.0038187 | North | N | 0.0038187 | 0
334 | RWMILLER | 3 | 205 | -0.007205 | north | -0.0038187 | -0.007543 | -0.059168 | -0.0063738 | 0.0038187 | North | N | 0.0038187 | 0
335 | RWMILLER | 4 | 102 | -0.007205 | north | -0.0038187 | -0.007543 | -0.059168 | -0.0063738 | 0.0038187 | North | N | 0.0038187 | 0
336 | RWMILLER | 5 | 96 | -0.007205 | north | -0.0038187 | -0.007543 | -0.059168 | -0.0063738 | 0.0038187 | North | N | 0.0038187 | 0
344 | MRSSHPRD | 1 | 12 | -0.023305 | north | -0.019919 | -0.023643 | -0.075268 | -0.022474 | 0.019919 | North | N | 0.019919 | 0
345 | MRSSHPRD | 2 | 12 | -0.023305 | north | -0.019919 | -0.023643 | -0.075268 | -0.022474 | 0.019919 | North | N | 0.019919 | 0
366 | JNSNCNTY | 1 | 168 | -0.00194 | north | 0.0014463 | -0.002278 | -0.053903 | -0.0011088 | 0.0011088 | houston | Y | 0.0014463 | 0.056704
367 | JNSNCNTY | 2 | 90 | -0.00194 | north | 0.0014463 | -0.002278 | -0.053903 | -0.0011088 | 0.0011088 | houston | Y | 0.0014463 | 0.030377
503 | NTHTEXAS | 1 | 18 | -0.011303 | north | -0.0079167 | -0.011641 | -0.063266 | -0.010472 | 0.0079167 | North | N | 0.0079167 | 0
504 | NTHTEXAS | 2 | 18 | -0.011303 | north | -0.0079167 | -0.011641 | -0.063266 | -0.010472 | 0.0079167 | North | N | 0.0079167 | 0
505 | NTHTEXAS | 3 | 38 | -0.011303 | north | -0.0079167 | -0.011641 | -0.063266 | -0.010472 | 0.0079167 | North | N | 0.0079167 | 0
580 | JCKCNTY8 | 1 | 288 | -0.022113 | north | -0.018727 | -0.022451 | -0.074076 | -0.021282 | 0.018727 | North | N | 0.018727 | 0
581 | JCKCNTY8 | 2 | 147 | -0.022113 | north | -0.018727 | -0.022451 | -0.074076 | -0.021282 | 0.018727 | North | N | 0.018727 | 0
582 | JCKCNTY8 | 3 | 147 | -0.022113 | north | -0.018727 | -0.022451 | -0.074076 | -0.021282 | 0.018727 | North | N | 0.018727 | 0
728 | WOLFRIDG | 1 | 112.5 | -0.025921 | north | -0.022535 | -0.026259 | -0.077884 | -0.02509 | 0.022535 | North | N | 0.022535 | 0
837 | NEWMAN_G | 1 | 40 | -0.00327 | north | 0.00011634 | -0.003608 | -0.055233 | -0.0024388 | 0.00011634 | North | N | 0.00011634 | 0
842 | OLINGER_ | 1 | 79 | -0.003304 | north | 8.2338e-05 | -0.003642 | -0.055267 | -0.0024728 | 8.2338e-05 | North | N | 8.2338e-05 | 0
843 | OLINGER_ | 1 | 106 | -0.003304 | north | 8.2338e-05 | -0.003642 | -0.055267 | -0.0024728 | 8.2338e-05 | North | N | 8.2338e-05 | 0
844 | OLINGER_ | 1 | 146 | -0.003304 | north | 8.2338e-05 | -0.003642 | -0.055267 | -0.0024728 | 8.2338e-05 | North | N | 8.2338e-05 | 0
845 | OLINGER_ | 1 | 76 | -0.003304 | north | 8.2338e-05 | -0.003642 | -0.055267 | -0.0024728 | 8.2338e-05 | North | N | 8.2338e-05 | 0
923 | SPENCER_ | 1 | 60 | -0.006106 | north | -0.0027197 | -0.006444 | -0.058069 | -0.0052748 | 0.0027197 | North | N | 0.0027197 | 0
924 | SPENCER_ | 1 | 63 | -0.006106 | north | -0.0027197 | -0.006444 | -0.058069 | -0.0052748 | 0.0027197 | North | N | 0.0027197 | 0
948 | STEAM1 | 1 | 20 | -0.00328 | north | 0.00010634 | -0.003618 | -0.055243 | -0.0024488 | 0.00010634 | North | N | 0.00010634 | 0
949 | STEAM2 | 1 | 25 | -0.00328 | north | 0.00010634 | -0.003618 | -0.055243 | -0.0024488 | 0.00010634 | North | N | 0.00010634 | 0
950 | STEAM3 | 1 | 41 | -0.00328 | north | 0.00010634 | -0.003618 | -0.055243 | -0.0024488 | 0.00010634 | North | N | 0.00010634 | 0
990 | GIBN_CRE | 1 | 463 | -0.00148 | north | 0.0019063 | -0.001818 | -0.053443 | -0.00064881 | 0.00064881 | houston | Y | 0.0019063 | 0.58223
1002 | PBCTAGE_ | A | 66 | 0.039354 | west | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1003 | PBCTBGE_ | B | 65 | 0.039354 | west | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1004 | PBCTCGE_ | C | 67 | 0.039354 | west | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1005 | PBCTDGE_ | D | 67 | 0.039354 | west | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1006 | PBCTEGE_ | E | 67 | 0.039354 | west | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1007 | PB5GEN_6 | MB | 114 | 0.039354 | west | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1008 | PB6GEN_7 | MB | 515 | 0.039354 | west | 0.04274 | 0.039016 | -0.012609 | 0.040185 | 0.012609 | west | N | 0.012609 | 0
1039 | MRGNAG_1 | A | 66 | 0.040745 | west | 0.044131 | 0.040407 | -0.011218 | 0.041576 | 0.011218 | west | N | 0.011218 | 0
1040 | MRGNBG_2 | B | 69 | 0.040745 | west | 0.044131 | 0.040407 | -0.011218 | 0.041576 | 0.011218 | west | N | 0.011218 | 0
1041 | MRGNCG_3 | C | 69 | 0.040745 | west | 0.044131 | 0.040407 | -0.011218 | 0.041576 | 0.011218 | west | N | 0.011218 | 0
1042 | MRGNDG_4 | D | 67 | 0.040745 | west | 0.044131 | 0.040407 | -0.011218 | 0.041576 | 0.011218 | west | N | 0.011218 | 0
1043 | MRGNEG_5 | E | 67 | 0.040745 | west | 0.044131 | 0.040407 | -0.011218 | 0.041576 | 0.011218 | west | N | 0.011218 | 0
1044 | MRGNFG_6 | F | 65 | 0.040745 | west | 0.044131 | 0.040407 | -0.011218 | 0.041576 | 0.011218 | west | N | 0.011218 | 0
1045 | CALENG1G | 1 | 70 | 0.039624 | west | 0.04301 | 0.039286 | -0.012339 | 0.040455 | 0.012339 | west | N | 0.012339 | 0
1046 | CALENG2G | 2 | 73.4 | 0.039624 | west | 0.04301 | 0.039286 | -0.012339 | 0.040455 | 0.012339 | west | N | 0.012339 | 0
1047 | CALENG3G | 3 | 70.4 | 0.039624 | west | 0.04301 | 0.039286 | -0.012339 | 0.040455 | 0.012339 | west | N | 0.012339 | 0
1058 | LONGSHOR | 1 | 150 | 0.03963 | west | 0.043016 | 0.039292 | -0.012333 | 0.040461 | 0.012333 | west | N | 0.012333 | 0
1058 | LONGSHOR | 2 | 220 | 0.03963 | west | 0.043016 | 0.039292 | -0.012333 | 0.040461 | 0.012333 | west | N | 0.012333 | 0
1061 | CIELOGEN | 1 | 99 | 0.04286 | west | 0.046246 | 0.042522 | -0.0091031 | 0.043691 | 0.0091031 | west | N | 0.0091031 | 0
1062 | CIELOGEN | 1 | 61 | 0.04286 | west | 0.046246 | 0.042522 | -0.0091031 | 0.043691 | 0.0091031 | west | N | 0.0091031 | 0
1068 | SCURRYCW | 1 | 141 | 0.042784 | west | 0.04617 | 0.042446 | -0.0091791 | 0.043615 | 0.0091791 | west | N | 0.0091791 | 0
1069 | KINDERMG | 1 | 25 | 0.04286 | west | 0.046246 | 0.042522 | -0.0091031 | 0.043691 | 0.0091031 | west | N | 0.0091031 | 0
1070 | KINDERMG | 1 | 45.7 | 0.04286 | west | 0.046246 | 0.042522 | -0.0091031 | 0.043691 | 0.0091031 | west | N | 0.0091031 | 0
1071 | KINDERMG | 1 | 45.7 | 0.04286 | west | 0.046246 | 0.042522 | -0.0091031 | 0.043691 | 0.0091031 | west | N | 0.0091031 | 0
1073 | SCURRYCW | 2 | 120 | 0.042784 | west | 0.04617 | 0.042446 | -0.0091791 | 0.043615 | 0.0091791 | west | N | 0.0091791 | 0
1320 | BSP 1 | 1 | 25.8 | 0.040649 | west | 0.044035 | 0.040311 | -0.011314 | 0.04148 | 0.011314 | west | N | 0.011314 | 0
1326 | STANTONW | 1 | 100.5 | 0.040051 | west | 0.043437 | 0.039713 | -0.011912 | 0.040882 | 0.011912 | west | N | 0.011912 | 0
1327 | WILDHRSE | 1 | 120 | 0.040893 | west | 0.044279 | 0.040555 | -0.01107 | 0.041724 | 0.01107 | west | N | 0.01107 | 0
1328 | OCOTILLO | 1 | 58 | 0.040098 | west | 0.043484 | 0.03976 | -0.011865 | 0.040929 | 0.011865 | west | N | 0.011865 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.040189 | west | 0.043575 | 0.039851 | -0.011774 | 0.04102 | 0.011774 | west | N | 0.011774 | 0
1343 | TRENTIPP | 1 | 150 | 0.045271 | west | 0.048657 | 0.044933 | -0.0066921 | 0.046102 | 0.0066921 | west | N | 0.0066921 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.040244 | west | 0.04363 | 0.039906 | -0.011719 | 0.041075 | 0.011719 | west | N | 0.011719 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.040244 | west | 0.04363 | 0.039906 | -0.011719 | 0.041075 | 0.011719 | west | N | 0.011719 | 0
1354 | AEPWIND_ | 1 | 101 | 0.045271 | west | 0.048657 | 0.044933 | -0.0066921 | 0.046102 | 0.0066921 | west | N | 0.0066921 | 0
1360 | GUNSIGHT | 1 | 120 | 0.041046 | west | 0.044432 | 0.040708 | -0.010917 | 0.041877 | 0.010917 | west | N | 0.010917 | 0
1432 | GRHAMSES | 2 | 366 | 0.00224 | north | 0.0056263 | 0.001902 | -0.049723 | 0.0030712 | 0.001902 | south | Y | 0.0056263 | 1.3631
1433 | GRHAMSES | 1 | 242 | -0.019748 | north | -0.016362 | -0.020086 | -0.071711 | -0.018917 | 0.016362 | North | N | 0.016362 | 0
1437 | MESQUITW | 1 | 400 | 0.034332 | west | 0.037718 | 0.033994 | -0.017631 | 0.035163 | 0.017631 | west | N | 0.017631 | 0
1438 | MESQUITW | 1 | 236 | 0.034234 | west | 0.03762 | 0.033896 | -0.017729 | 0.035065 | 0.017729 | west | N | 0.017729 | 0
1442 | COKFIELD | 1 | 165 | 0.026556 | west | 0.029942 | 0.026218 | -0.025407 | 0.027387 | 0.025407 | west | N | 0.025407 | 0
1453 | WCPWRCO_ | 1 | 204 | -0.004897 | north | -0.0015107 | -0.005235 | -0.05686 | -0.0040658 | 0.0015107 | North | N | 0.0015107 | 0
1454 | WCPWRCO_ | 2 | 201 | -0.004897 | north | -0.0015107 | -0.005235 | -0.05686 | -0.0040658 | 0.0015107 | North | N | 0.0015107 | 0
1455 | WCPWRCO_ | 3 | 242 | -0.004897 | north | -0.0015107 | -0.005235 | -0.05686 | -0.0040658 | 0.0015107 | North | N | 0.0015107 | 0
1479 | WFCOGEN_ | 1 | 20 | -0.047669 | west | -0.044283 | -0.048007 | -0.099632 | -0.046838 | 0.044283 | North | Y | 0.099632 | 1.107
1479 | WFCOGEN_ | 2 | 20 | -0.047669 | west | -0.044283 | -0.048007 | -0.099632 | -0.046838 | 0.044283 | North | Y | 0.099632 | 1.107
1482 | WFCOGEN_ | 1 | 20 | -0.047669 | west | -0.044283 | -0.048007 | -0.099632 | -0.046838 | 0.044283 | North | Y | 0.099632 | 1.107
1482 | WFCOGEN_ | 2 | 17 | -0.047669 | west | -0.044283 | -0.048007 | -0.099632 | -0.046838 | 0.044283 | North | Y | 0.099632 | 0.94094
1600 | BARTNWND | 1 | 120 | -0.015829 | north | -0.012443 | -0.016167 | -0.067792 | -0.014998 | 0.012443 | North | N | 0.012443 | 0
1643 | SLSTR1PP | 1 | 60 | 0.001229 | north | 0.0046153 | 0.00089103 | -0.050734 | 0.0020602 | 0.00089103 | south | Y | 0.0046153 | 0.22346
1675 | PEC_1G | 1 | 75 | -0.003667 | north | -0.00028066 | -0.004005 | -0.05563 | -0.0028358 | 0.00028066 | North | N | 0.00028066 | 0
1676 | PEC_2G | 2 | 79.6 | -0.003667 | north | -0.00028066 | -0.004005 | -0.05563 | -0.0028358 | 0.00028066 | North | N | 0.00028066 | 0
1677 | PEC_3G | 3 | 88.4 | -0.003667 | north | -0.00028066 | -0.004005 | -0.05563 | -0.0028358 | 0.00028066 | North | N | 0.00028066 | 0
1678 | LAMARPWR | 1 | 160 | -0.003636 | north | -0.00024966 | -0.003974 | -0.055599 | -0.0028048 | 0.00024966 | North | N | 0.00024966 | 0
1679 | LAMARPWR | 2 | 156 | -0.003636 | north | -0.00024966 | -0.003974 | -0.055599 | -0.0028048 | 0.00024966 | North | N | 0.00024966 | 0
1680 | LAMARPWR | 3 | 196 | -0.003636 | north | -0.00024966 | -0.003974 | -0.055599 | -0.0028048 | 0.00024966 | North | N | 0.00024966 | 0
1681 | LAMARPWR | 4 | 156 | -0.003636 | north | -0.00024966 | -0.003974 | -0.055599 | -0.0028048 | 0.00024966 | North | N | 0.00024966 | 0
1682 | LAMARPWR | 5 | 157 | -0.003636 | north | -0.00024966 | -0.003974 | -0.055599 | -0.0028048 | 0.00024966 | North | N | 0.00024966 | 0
1683 | LAMARPWR | 6 | 198 | -0.003636 | north | -0.00024966 | -0.003974 | -0.055599 | -0.0028048 | 0.00024966 | North | N | 0.00024966 | 0
1687 | VALLEY_1 | 1 | 170 | -0.004172 | north | -0.00078566 | -0.00451 | -0.056135 | -0.0033408 | 0.00078566 | North | N | 0.00078566 | 0
1688 | VALLEY_2 | 2 | 520 | -0.004172 | north | -0.00078566 | -0.00451 | -0.056135 | -0.0033408 | 0.00078566 | North | N | 0.00078566 | 0
1689 | VALLEY_3 | 3 | 370 | -0.003687 | north | -0.00030066 | -0.004025 | -0.05565 | -0.0028558 | 0.00030066 | North | N | 0.00030066 | 0
1701 | MOSES_1G | 1 | 558 | -0.003486 | north | -9.9662e-05 | -0.003824 | -0.055449 | -0.0026548 | 9.9662e-05 | North | N | 9.9662e-05 | 0
1702 | MOSES_2G | 2 | 579 | -0.003486 | north | -9.9662e-05 | -0.003824 | -0.055449 | -0.0026548 | 9.9662e-05 | North | N | 9.9662e-05 | 0
1703 | MOSES_3G | 3 | 808 | -0.003486 | north | -9.9662e-05 | -0.003824 | -0.055449 | -0.0026548 | 9.9662e-05 | North | N | 9.9662e-05 | 0
1861 | EAGLEMNT | MB | 112 | -0.004829 | north | -0.0014427 | -0.005167 | -0.056792 | -0.0039978 | 0.0014427 | North | N | 0.0014427 | 0
1862 | EAGLEMNT | MB | 100 | -0.004829 | north | -0.0014427 | -0.005167 | -0.056792 | -0.0039978 | 0.0014427 | North | N | 0.0014427 | 0
1863 | EAGLEMNT | MB | 378 | -0.004829 | north | -0.0014427 | -0.005167 | -0.056792 | -0.0039978 | 0.0014427 | North | N | 0.0014427 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.000497 | north | 0.0028893 | -0.00083497 | -0.05246 | 0.00033419 | 0.00033419 | houston | Y | 0.0028893 | 0.55523
1878 | WLFHOLW_ | 2 | 205 | -0.000497 | north | 0.0028893 | -0.00083497 | -0.05246 | 0.00033419 | 0.00033419 | houston | Y | 0.0028893 | 0.52381
1879 | WLFHOLW_ | 3 | 272.4 | -0.000497 | north | 0.0028893 | -0.00083497 | -0.05246 | 0.00033419 | 0.00033419 | houston | Y | 0.0028893 | 0.69602
1889 | DECRDOVA | MB | 770 | -0.001209 | north | 0.0021773 | -0.001547 | -0.053172 | -0.00037781 | 0.00037781 | houston | Y | 0.0021773 | 1.3856
1892 | DECRDOVA | A | 70 | -0.001896 | north | 0.0014903 | -0.002234 | -0.053859 | -0.0010648 | 0.0010648 | houston | Y | 0.0014903 | 0.029787
1893 | DECRDOVA | B | 69 | -0.001896 | north | 0.0014903 | -0.002234 | -0.053859 | -0.0010648 | 0.0010648 | houston | Y | 0.0014903 | 0.029361
1894 | DECRDOVA | C | 69 | -0.001896 | north | 0.0014903 | -0.002234 | -0.053859 | -0.0010648 | 0.0010648 | houston | Y | 0.0014903 | 0.029361
1895 | DECRDOVA | D | 68 | -0.001896 | north | 0.0014903 | -0.002234 | -0.053859 | -0.0010648 | 0.0010648 | houston | Y | 0.0014903 | 0.028936
1898 | COMCHEPK | 1 | 1157 | -0.000231 | north | 0.0031553 | -0.00056897 | -0.052194 | 0.00060019 | 0.00056897 | south | Y | 0.0031553 | 2.9924
1899 | COMCHEPK | 2 | 1158 | -0.000231 | north | 0.0031553 | -0.00056897 | -0.052194 | 0.00060019 | 0.00056897 | south | Y | 0.0031553 | 2.995
1937 | MDLTHELP | 5 | 224 | -0.002027 | north | 0.0013593 | -0.002365 | -0.05399 | -0.0011958 | 0.0011958 | houston | Y | 0.0013593 | 0.03663
1938 | MDLTHELP | 6 | 226 | -0.002027 | north | 0.0013593 | -0.002365 | -0.05399 | -0.0011958 | 0.0011958 | houston | Y | 0.0013593 | 0.036957
1941 | MDLTHELP | 1 | 216.4 | -0.002273 | north | 0.0011133 | -0.002611 | -0.054236 | -0.0014418 | 0.0011133 | North | N | 0.0011133 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.002273 | north | 0.0011133 | -0.002611 | -0.054236 | -0.0014418 | 0.0011133 | North | N | 0.0011133 | 0
1943 | MDLTHELP | 3 | 212 | -0.002027 | north | 0.0013593 | -0.002365 | -0.05399 | -0.0011958 | 0.0011958 | houston | Y | 0.0013593 | 0.034667
1944 | MDLTHELP | 4 | 211 | -0.002027 | north | 0.0013593 | -0.002365 | -0.05399 | -0.0011958 | 0.0011958 | houston | Y | 0.0013593 | 0.034504
1947 | HANDLEY_ | 3 | 395 | -0.002753 | north | 0.00063334 | -0.003091 | -0.054716 | -0.0019218 | 0.00063334 | North | N | 0.00063334 | 0
1948 | HANDLEY_ | 4 | 435 | -0.002821 | north | 0.00056534 | -0.003159 | -0.054784 | -0.0019898 | 0.00056534 | North | N | 0.00056534 | 0
1949 | HANDLEY_ | 5 | 435 | -0.002753 | north | 0.00063334 | -0.003091 | -0.054716 | -0.0019218 | 0.00063334 | North | N | 0.00063334 | 0
2371 | COLLIN_1 | MB | 138 | -0.004004 | north | -0.00061766 | -0.004342 | -0.055967 | -0.0031728 | 0.00061766 | North | N | 0.00061766 | 0
2413 | MTCK6_G | 6 | 118 | -0.002824 | north | 0.00056234 | -0.003162 | -0.054787 | -0.0019928 | 0.00056234 | North | N | 0.00056234 | 0
2414 | MTCK7_G | 7 | 115 | -0.002824 | north | 0.00056234 | -0.003162 | -0.054787 | -0.0019928 | 0.00056234 | North | N | 0.00056234 | 0
2417 | MTCK8_G | 8 | 556 | -0.002824 | north | 0.00056234 | -0.003162 | -0.054787 | -0.0019928 | 0.00056234 | North | N | 0.00056234 | 0
2451 | LKHB1_G | 1 | 388 | -0.003107 | north | 0.00027934 | -0.003445 | -0.05507 | -0.0022758 | 0.00027934 | North | N | 0.00027934 | 0
2452 | LKHB2_G | 2 | 515 | -0.003107 | north | 0.00027934 | -0.003445 | -0.05507 | -0.0022758 | 0.00027934 | North | N | 0.00027934 | 0
3097 | MARTLAKE | 1 | 785 | -0.002742 | north | 0.00064434 | -0.00308 | -0.054705 | -0.0019108 | 0.00064434 | North | N | 0.00064434 | 0
3098 | MARTLAKE | 2 | 795 | -0.002742 | north | 0.00064434 | -0.00308 | -0.054705 | -0.0019108 | 0.00064434 | North | N | 0.00064434 | 0
3099 | MARTLAKE | 3 | 780 | -0.002742 | north | 0.00064434 | -0.00308 | -0.054705 | -0.0019108 | 0.00064434 | North | N | 0.00064434 | 0
3107 | STRYKER_ | 1 | 182 | -0.002646 | north | 0.00074034 | -0.002984 | -0.054609 | -0.0018148 | 0.00074034 | North | N | 0.00074034 | 0
3108 | STRYKER_ | 2 | 484 | -0.002646 | north | 0.00074034 | -0.002984 | -0.054609 | -0.0018148 | 0.00074034 | North | N | 0.00074034 | 0
3126 | TRINIDAD | 1 | 224 | -0.002497 | north | 0.00088934 | -0.002835 | -0.05446 | -0.0016658 | 0.00088934 | North | N | 0.00088934 | 0
3309 | ASPN_G | 1 | 50 | -0.002646 | north | 0.00074034 | -0.002984 | -0.054609 | -0.0018148 | 0.00074034 | North | N | 0.00074034 | 0
3348 | CHAMPION | MB | 42 | -0.002651 | north | 0.00073534 | -0.002989 | -0.054614 | -0.0018198 | 0.00073534 | North | N | 0.00073534 | 0
3381 | BBRN_1G | 1 | 615 | -0.002152 | north | 0.0012343 | -0.00249 | -0.054115 | -0.0013208 | 0.0012343 | North | N | 0.0012343 | 0
3382 | BBRN_2G | 2 | 587 | -0.002152 | north | 0.0012343 | -0.00249 | -0.054115 | -0.0013208 | 0.0012343 | North | N | 0.0012343 | 0
3403 | THOUSE_1 | MB | 537 | -0.001403 | north | 0.0019833 | -0.001741 | -0.053366 | -0.00057181 | 0.00057181 | houston | Y | 0.0019833 | 0.75799
3404 | THOUSE_2 | 2 | 787 | -0.001403 | north | 0.0019833 | -0.001741 | -0.053366 | -0.00057181 | 0.00057181 | houston | Y | 0.0019833 | 1.1109
3416 | LAKE_CRK | MB | 75 | -0.001326 | north | 0.0020603 | -0.001664 | -0.053289 | -0.00049481 | 0.00049481 | houston | Y | 0.0020603 | 0.11741
3417 | LAKE_CRK | MB | 222 | -0.001326 | north | 0.0020603 | -0.001664 | -0.053289 | -0.00049481 | 0.00049481 | houston | Y | 0.0020603 | 0.34755
3432 | SANDOW_4 | 4 | 569 | -0.000471 | south | 0.0029153 | -0.00080897 | -0.052434 | 0.00036019 | 0.00036019 | houston | Y | 0.00080897 | 0.25536
5026 | BRAUNIG_ | 1 | 209 | 0.00056 | south | 0.0039463 | 0.00022203 | -0.051403 | 0.0013912 | 0.00022203 | south | N | 0.00022203 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.00056 | south | 0.0039463 | 0.00022203 | -0.051403 | 0.0013912 | 0.00022203 | south | N | 0.00022203 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.000584 | south | 0.0039703 | 0.00024603 | -0.051379 | 0.0014152 | 0.00024603 | south | N | 0.00024603 | 0
5031 | BRA_VHBC | 1 | 46 | 0.00056 | south | 0.0039463 | 0.00022203 | -0.051403 | 0.0013912 | 0.00022203 | south | N | 0.00022203 | 0
5032 | BRA_VHBC | 2 | 47 | 0.00056 | south | 0.0039463 | 0.00022203 | -0.051403 | 0.0013912 | 0.00022203 | south | N | 0.00022203 | 0
5033 | BRA_VHBC | 3 | 46 | 0.00056 | south | 0.0039463 | 0.00022203 | -0.051403 | 0.0013912 | 0.00022203 | south | N | 0.00022203 | 0
5034 | BRA_VHBC | 4 | 46 | 0.00056 | south | 0.0039463 | 0.00022203 | -0.051403 | 0.0013912 | 0.00022203 | south | N | 0.00022203 | 0
5111 | CALAVER_ | 1 | 424 | 0.000547 | south | 0.0039333 | 0.00020903 | -0.051416 | 0.0013782 | 0.00020903 | south | N | 0.00020903 | 0
5112 | CALAVER_ | 2 | 425 | 0.000547 | south | 0.0039333 | 0.00020903 | -0.051416 | 0.0013782 | 0.00020903 | south | N | 0.00020903 | 0
5264 | LEON_LCP | 3 | 58 | 0.000653 | south | 0.0040393 | 0.00031503 | -0.05131 | 0.0014842 | 0.00031503 | south | N | 0.00031503 | 0
5265 | LEON_LCP | 4 | 89 | 0.000653 | south | 0.0040393 | 0.00031503 | -0.05131 | 0.0014842 | 0.00031503 | south | N | 0.00031503 | 0
5266 | LEON_LCP | 1 | 44 | 0.000653 | south | 0.0040393 | 0.00031503 | -0.05131 | 0.0014842 | 0.00031503 | south | N | 0.00031503 | 0
5267 | LEON_LCP | 2 | 44 | 0.000653 | south | 0.0040393 | 0.00031503 | -0.05131 | 0.0014842 | 0.00031503 | south | N | 0.00031503 | 0
5268 | LEON_LCP | 3 | 43 | 0.000653 | south | 0.0040393 | 0.00031503 | -0.05131 | 0.0014842 | 0.00031503 | south | N | 0.00031503 | 0
5269 | LEON_LCP | 4 | 45 | 0.000653 | south | 0.0040393 | 0.00031503 | -0.05131 | 0.0014842 | 0.00031503 | south | N | 0.00031503 | 0
5396 | CALAVER_ | 1 | 412 | 0.000559 | south | 0.0039453 | 0.00022103 | -0.051404 | 0.0013902 | 0.00022103 | south | N | 0.00022103 | 0
5397 | CALAVER_ | 2 | 400 | 0.000559 | south | 0.0039453 | 0.00022103 | -0.051404 | 0.0013902 | 0.00022103 | south | N | 0.00022103 | 0
5401 | CALAVER_ | 1 | 546 | 0.000457 | south | 0.0038433 | 0.00011903 | -0.051506 | 0.0012882 | 0.00011903 | south | N | 0.00011903 | 0
5402 | CALAVER_ | 2 | 750 | 0.000457 | south | 0.0038433 | 0.00011903 | -0.051506 | 0.0012882 | 0.00011903 | south | N | 0.00011903 | 0
5436 | TUTTL_WB | MB | 61 | 0.000496 | south | 0.0038823 | 0.00015803 | -0.051467 | 0.0013272 | 0.00015803 | south | N | 0.00015803 | 0
5438 | TUTTL_WB | MB | 95 | 0.000496 | south | 0.0038823 | 0.00015803 | -0.051467 | 0.0013272 | 0.00015803 | south | N | 0.00015803 | 0
5439 | TUTTL_WB | MB | 151 | 0.000496 | south | 0.0038823 | 0.00015803 | -0.051467 | 0.0013272 | 0.00015803 | south | N | 0.00015803 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.000481 | south | 0.0038673 | 0.00014303 | -0.051482 | 0.0013122 | 0.00014303 | south | N | 0.00014303 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.000481 | south | 0.0038673 | 0.00014303 | -0.051482 | 0.0013122 | 0.00014303 | south | N | 0.00014303 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.000481 | south | 0.0038673 | 0.00014303 | -0.051482 | 0.0013122 | 0.00014303 | south | N | 0.00014303 | 0
5503 | RAYBURNG | 1 | 22 | 0.000244 | south | 0.0036303 | -9.3967e-05 | -0.051719 | 0.0010752 | 9.3967e-05 | south | N | 9.3967e-05 | 0
5505 | RAYBURNG | 1 | 11 | 0.000244 | south | 0.0036303 | -9.3967e-05 | -0.051719 | 0.0010752 | 9.3967e-05 | south | N | 9.3967e-05 | 0
5506 | RAYBURNG | 1 | 11 | 0.000244 | south | 0.0036303 | -9.3967e-05 | -0.051719 | 0.0010752 | 9.3967e-05 | south | N | 9.3967e-05 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.000216 | south | 0.0036023 | -0.00012197 | -0.051747 | 0.0010472 | 0.00012197 | south | N | 0.00012197 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.000216 | south | 0.0036023 | -0.00012197 | -0.051747 | 0.0010472 | 0.00012197 | south | N | 0.00012197 | 0
5511 | RAYBURNC | 1 | 46 | 0.000216 | south | 0.0036023 | -0.00012197 | -0.051747 | 0.0010472 | 0.00012197 | south | N | 0.00012197 | 0
5512 | RAYBURNC | 1 | 48 | 0.000216 | south | 0.0036023 | -0.00012197 | -0.051747 | 0.0010472 | 0.00012197 | south | N | 0.00012197 | 0
5728 | FALCONHY | 2 | 12 | 0.000778 | south | 0.0041643 | 0.00044003 | -0.051185 | 0.0016092 | 0.00044003 | south | N | 0.00044003 | 0
5729 | FALCONHY | 3 | 11 | 0.000778 | south | 0.0041643 | 0.00044003 | -0.051185 | 0.0016092 | 0.00044003 | south | N | 0.00044003 | 0
5890 | PEARSALL | 1 | 24 | 0.001991 | south | 0.0053773 | 0.001653 | -0.049972 | 0.0028222 | 0.001653 | south | N | 0.001653 | 0
5891 | PEARSALL | 1 | 24 | 0.001991 | south | 0.0053773 | 0.001653 | -0.049972 | 0.0028222 | 0.001653 | south | N | 0.001653 | 0
5892 | PEARSALL | 1 | 23 | 0.001991 | south | 0.0053773 | 0.001653 | -0.049972 | 0.0028222 | 0.001653 | south | N | 0.001653 | 0
5903 | SANMIGUE | 1 | 396 | 0.000565 | south | 0.0039513 | 0.00022703 | -0.051398 | 0.0013962 | 0.00022703 | south | N | 0.00022703 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.000434 | houston | 0.0029523 | -0.00077197 | -0.052397 | 0.00039719 | 0.00039719 | houston | N | 0.00039719 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.000434 | houston | 0.0029523 | -0.00077197 | -0.052397 | 0.00039719 | 0.00039719 | houston | N | 0.00039719 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | 0.0033863 | -0.00033797 | -0.051963 | 0.00083119 | 0.00033797 | south | Y | 0.0033863 | 1.829
5932 | SI_RAY9 | 9 | 38 | 0.000393 | south | 0.0037793 | 5.5033e-05 | -0.05157 | 0.0012242 | 5.5033e-05 | south | N | 5.5033e-05 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.000393 | south | 0.0037793 | 5.5033e-05 | -0.05157 | 0.0012242 | 5.5033e-05 | south | N | 5.5033e-05 | 0
5934 | SI_RAY5 | 5 | 15 | 0.000393 | south | 0.0037793 | 5.5033e-05 | -0.05157 | 0.0012242 | 5.5033e-05 | south | N | 5.5033e-05 | 0
5935 | SI_RAY10 | 10 | 47 | 0.000393 | south | 0.0037793 | 5.5033e-05 | -0.05157 | 0.0012242 | 5.5033e-05 | south | N | 5.5033e-05 | 0
6016 | SWMESA | 1 | 75 | 0.037626 | west | 0.041012 | 0.037288 | -0.014337 | 0.038457 | 0.014337 | west | N | 0.014337 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | 0.0033863 | -0.00033797 | -0.051963 | 0.00083119 | 0.00033797 | south | Y | 0.051963 | 11.3575
6144 | MCADOO1A | 1 | 150 | 0.050233 | west | 0.053619 | 0.049895 | -0.0017301 | 0.051064 | 0.0017301 | west | N | 0.0017301 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.046069 | west | 0.049455 | 0.045731 | -0.0058941 | 0.0469 | 0.0058941 | west | N | 0.0058941 | 0
6476 | LANGFORD | 1 | 150 | 0.030657 | west | 0.034043 | 0.030319 | -0.021306 | 0.031488 | 0.021306 | west | N | 0.021306 | 0
6637 | SNYDERW1 | 1 | 63 | 0.042268 | west | 0.045654 | 0.04193 | -0.0096951 | 0.043099 | 0.0096951 | west | N | 0.0096951 | 0
6752 | OKLA0A | 1 | 649.7 | 0.25388 | west | 0.25726 | 0.25354 | 0.20191 | 0.25471 | 0.20191 | west | N | 0.20191 | 0
6948 | DENISNDM | 1 | 40 | -0.004494 | north | -0.0011077 | -0.004832 | -0.056457 | -0.0036628 | 0.0011077 | North | N | 0.0011077 | 0
6948 | DENISNDM | 2 | 40 | -0.004494 | north | -0.0011077 | -0.004832 | -0.056457 | -0.0036628 | 0.0011077 | North | N | 0.0011077 | 0
7000 | L_FERGUS | 1 | 422 | 0.001859 | south | 0.0052453 | 0.001521 | -0.050104 | 0.0026902 | 0.001521 | south | N | 0.001521 | 0
7004 | L_SIMGID | 1 | 132 | -3.2e-05 | south | 0.0033543 | -0.00036997 | -0.051995 | 0.00079919 | 0.00036997 | south | N | 0.00036997 | 0
7005 | L_SIMGID | 2 | 134 | -3.2e-05 | south | 0.0033543 | -0.00036997 | -0.051995 | 0.00079919 | 0.00036997 | south | N | 0.00036997 | 0
7006 | L_SIMGID | 3 | 323 | -3.2e-05 | south | 0.0033543 | -0.00036997 | -0.051995 | 0.00079919 | 0.00036997 | south | N | 0.00036997 | 0
7007 | L_LOSTPI | 1 | 158 | -0.000114 | south | 0.0032723 | -0.00045197 | -0.052077 | 0.00071719 | 0.00045197 | south | N | 0.00045197 | 0
7008 | L_LOSTPI | 2 | 160 | -0.000114 | south | 0.0032723 | -0.00045197 | -0.052077 | 0.00071719 | 0.00045197 | south | N | 0.00045197 | 0
7009 | L_LOSTPI | 3 | 175 | -0.000114 | south | 0.0032723 | -0.00045197 | -0.052077 | 0.00071719 | 0.00045197 | south | N | 0.00045197 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.000124 | south | 0.0032623 | -0.00046197 | -0.052087 | 0.00070719 | 0.00046197 | south | N | 0.00046197 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.000124 | south | 0.0032623 | -0.00046197 | -0.052087 | 0.00070719 | 0.00046197 | south | N | 0.00046197 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.000123 | south | 0.0032633 | -0.00046097 | -0.052086 | 0.00070819 | 0.00046097 | south | N | 0.00046097 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.00027 | south | 0.0036563 | -6.7967e-05 | -0.051693 | 0.0011012 | 6.7967e-05 | south | N | 6.7967e-05 | 0
7015 | L_HAYSEN | 2 | 225 | 0.00027 | south | 0.0036563 | -6.7967e-05 | -0.051693 | 0.0011012 | 6.7967e-05 | south | N | 6.7967e-05 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.00027 | south | 0.0036563 | -6.7967e-05 | -0.051693 | 0.0011012 | 6.7967e-05 | south | N | 6.7967e-05 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.00027 | south | 0.0036563 | -6.7967e-05 | -0.051693 | 0.0011012 | 6.7967e-05 | south | N | 6.7967e-05 | 0
7020 | L_AUSTPL | 1 | 8 | 0.00012 | south | 0.0035063 | -0.00021797 | -0.051843 | 0.00095119 | 0.00021797 | south | N | 0.00021797 | 0
7020 | L_AUSTPL | 2 | 8 | 0.00012 | south | 0.0035063 | -0.00021797 | -0.051843 | 0.00095119 | 0.00021797 | south | N | 0.00021797 | 0
7022 | L_BUCHAN | 1 | 18 | 0.001926 | south | 0.0053123 | 0.001588 | -0.050037 | 0.0027572 | 0.001588 | south | N | 0.001588 | 0
7023 | L_BUCHAN | 2 | 18 | 0.001926 | south | 0.0053123 | 0.001588 | -0.050037 | 0.0027572 | 0.001588 | south | N | 0.001588 | 0
7024 | L_BUCHAN | 3 | 15 | 0.001926 | south | 0.0053123 | 0.001588 | -0.050037 | 0.0027572 | 0.001588 | south | N | 0.001588 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.002398 | south | 0.0057843 | 0.00206 | -0.049565 | 0.0032292 | 0.00206 | south | N | 0.00206 | 0
7028 | L_MARBFA | 1 | 18 | 0.001453 | south | 0.0048393 | 0.001115 | -0.05051 | 0.0022842 | 0.001115 | south | N | 0.001115 | 0
7029 | L_MARBFA | 2 | 18 | 0.001453 | south | 0.0048393 | 0.001115 | -0.05051 | 0.0022842 | 0.001115 | south | N | 0.001115 | 0
7031 | L_MARSFO | 1 | 35 | 0.000533 | south | 0.0039193 | 0.00019503 | -0.05143 | 0.0013642 | 0.00019503 | south | N | 0.00019503 | 0
7032 | L_MARSFO | 2 | 34 | 0.000533 | south | 0.0039193 | 0.00019503 | -0.05143 | 0.0013642 | 0.00019503 | south | N | 0.00019503 | 0
7033 | L_MARSFO | 3 | 35 | 0.000533 | south | 0.0039193 | 0.00019503 | -0.05143 | 0.0013642 | 0.00019503 | south | N | 0.00019503 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.001756 | south | 0.0051423 | 0.001418 | -0.050207 | 0.0025872 | 0.001418 | south | N | 0.001418 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.001756 | south | 0.0051423 | 0.001418 | -0.050207 | 0.0025872 | 0.001418 | south | N | 0.001418 | 0
7038 | L_DELAWA | 1 | 35 | 0.039435 | west | 0.042821 | 0.039097 | -0.012528 | 0.040266 | 0.012528 | west | N | 0.012528 | 0
7038 | L_DELAWA | 2 | 30 | 0.039435 | west | 0.042821 | 0.039097 | -0.012528 | 0.040266 | 0.012528 | west | N | 0.012528 | 0
7303 | L_WPPGS1 | 1 | 50 | -8.9e-05 | south | 0.0032973 | -0.00042697 | -0.052052 | 0.00074219 | 0.00042697 | south | N | 0.00042697 | 0
7303 | L_WPPGS1 | 2 | 50 | -8.9e-05 | south | 0.0032973 | -0.00042697 | -0.052052 | 0.00074219 | 0.00042697 | south | N | 0.00042697 | 0
7305 | L_WPPGS3 | 3 | 50 | -8.9e-05 | south | 0.0032973 | -0.00042697 | -0.052052 | 0.00074219 | 0.00042697 | south | N | 0.00042697 | 0
7305 | L_WPPGS3 | 4 | 50 | -8.9e-05 | south | 0.0032973 | -0.00042697 | -0.052052 | 0.00074219 | 0.00042697 | south | N | 0.00042697 | 0
7487 | L_CANYHY | 1 | 6 | 0.000368 | south | 0.0037543 | 3.0033e-05 | -0.051595 | 0.0011992 | 3.0033e-05 | south | N | 3.0033e-05 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.000309 | south | 0.0036953 | -2.8967e-05 | -0.051654 | 0.0011402 | 2.8967e-05 | south | N | 2.8967e-05 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.000309 | south | 0.0036953 | -2.8967e-05 | -0.051654 | 0.0011402 | 2.8967e-05 | south | N | 2.8967e-05 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.000309 | south | 0.0036953 | -2.8967e-05 | -0.051654 | 0.0011402 | 2.8967e-05 | south | N | 2.8967e-05 | 0
7609 | L_SCHUMA | 1 | 4 | 0.000373 | south | 0.0037593 | 3.5033e-05 | -0.05159 | 0.0012042 | 3.5033e-05 | south | N | 3.5033e-05 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.000242 | south | 0.0036283 | -9.5967e-05 | -0.051721 | 0.0010732 | 9.5967e-05 | south | N | 9.5967e-05 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.000242 | south | 0.0036283 | -9.5967e-05 | -0.051721 | 0.0010732 | 9.5967e-05 | south | N | 9.5967e-05 | 0
7800 | L_GUADGE | 1 | 147 | 0.000347 | south | 0.0037333 | 9.0332e-06 | -0.051616 | 0.0011782 | 9.0332e-06 | south | N | 9.0332e-06 | 0
7801 | L_GUADGE | 2 | 138 | 0.000347 | south | 0.0037333 | 9.0332e-06 | -0.051616 | 0.0011782 | 9.0332e-06 | south | N | 9.0332e-06 | 0
7802 | L_GUADGE | 3 | 140 | 0.000347 | south | 0.0037333 | 9.0332e-06 | -0.051616 | 0.0011782 | 9.0332e-06 | south | N | 9.0332e-06 | 0
7803 | L_GUADGE | 4 | 147 | 0.000347 | south | 0.0037333 | 9.0332e-06 | -0.051616 | 0.0011782 | 9.0332e-06 | south | N | 9.0332e-06 | 0
7804 | L_GUADGE | 5 | 182 | 0.000347 | south | 0.0037333 | 9.0332e-06 | -0.051616 | 0.0011782 | 9.0332e-06 | south | N | 9.0332e-06 | 0
7805 | L_GUADGE | 6 | 198 | 0.000347 | south | 0.0037333 | 9.0332e-06 | -0.051616 | 0.0011782 | 9.0332e-06 | south | N | 9.0332e-06 | 0
7807 | L_BASTEN | 1 | 152.5 | -3.7e-05 | south | 0.0033493 | -0.00037497 | -0.052 | 0.00079419 | 0.00037497 | south | N | 0.00037497 | 0
7808 | L_BASTEN | 1 | 149.5 | -3.7e-05 | south | 0.0033493 | -0.00037497 | -0.052 | 0.00079419 | 0.00037497 | south | N | 0.00037497 | 0
7809 | L_BASTEN | 1 | 232.6 | -3.7e-05 | south | 0.0033493 | -0.00037497 | -0.052 | 0.00079419 | 0.00037497 | south | N | 0.00037497 | 0
7810 | L_RIONOG | 1 | 142 | 0.000308 | south | 0.0036943 | -2.9967e-05 | -0.051655 | 0.0011392 | 2.9967e-05 | south | N | 2.9967e-05 | 0
7811 | L_RIONOG | 2 | 145 | 0.000308 | south | 0.0036943 | -2.9967e-05 | -0.051655 | 0.0011392 | 2.9967e-05 | south | N | 2.9967e-05 | 0
7812 | L_RIONOG | 3 | 151 | 0.000308 | south | 0.0036943 | -2.9967e-05 | -0.051655 | 0.0011392 | 2.9967e-05 | south | N | 2.9967e-05 | 0
7813 | L_RIONOG | 4 | 290 | 0.000308 | south | 0.0036943 | -2.9967e-05 | -0.051655 | 0.0011392 | 2.9967e-05 | south | N | 2.9967e-05 | 0
8032 | AMISTADH | 1 | 33 | 0.011717 | south | 0.015103 | 0.011379 | -0.040246 | 0.012548 | 0.011379 | south | N | 0.011379 | 0
8033 | AMISTADH | 2 | 25 | 0.011717 | south | 0.015103 | 0.011379 | -0.040246 | 0.012548 | 0.011379 | south | N | 0.011379 | 0
8048 | FALCONHY | 1 | 12 | 0.000778 | south | 0.0041643 | 0.00044003 | -0.051185 | 0.0016092 | 0.00044003 | south | N | 0.00044003 | 0
8066 | DUP1V#1 | 1 | 73 | 0.000188 | south | 0.0035743 | -0.00014997 | -0.051775 | 0.0010192 | 0.00014997 | south | N | 0.00014997 | 0
8134 | FOR69CG0 | 1 | 79 | 8.1e-05 | south | 0.0034673 | -0.00025697 | -0.051882 | 0.00091219 | 0.00025697 | south | N | 0.00025697 | 0
8138 | FOR69CG0 | 2 | 81 | 8.1e-05 | south | 0.0034673 | -0.00025697 | -0.051882 | 0.00091219 | 0.00025697 | south | N | 0.00025697 | 0
8139 | JOS #1 | MB | 255 | 0 | south | 0.0033863 | -0.00033797 | -0.051963 | 0.00083119 | 0.00033797 | south | N | 0.00033797 | 0
8147 | UCAR #2 | 10 | 28 | 0.000152 | south | 0.0035383 | -0.00018597 | -0.051811 | 0.00098319 | 0.00018597 | south | N | 0.00018597 | 0
8148 | UCAR #1 | 2 | 7 | 0.000152 | south | 0.0035383 | -0.00018597 | -0.051811 | 0.00098319 | 0.00018597 | south | N | 0.00018597 | 0
8153 | FOR69CG0 | 3 | 79 | 8.1e-05 | south | 0.0034673 | -0.00025697 | -0.051882 | 0.00091219 | 0.00025697 | south | N | 0.00025697 | 0
8154 | FOR69CG0 | 4 | 80 | 8.1e-05 | south | 0.0034673 | -0.00025697 | -0.051882 | 0.00091219 | 0.00025697 | south | N | 0.00025697 | 0
8155 | FOR69CG0 | 5 | 78.4 | 8.1e-05 | south | 0.0034673 | -0.00025697 | -0.051882 | 0.00091219 | 0.00025697 | south | N | 0.00025697 | 0
8156 | FOR69CG0 | 6 | 25 | 8.1e-05 | south | 0.0034673 | -0.00025697 | -0.051882 | 0.00091219 | 0.00025697 | south | N | 0.00025697 | 0
8157 | FOR69CG0 | 7 | 46 | 8.1e-05 | south | 0.0034673 | -0.00025697 | -0.051882 | 0.00091219 | 0.00025697 | south | N | 0.00025697 | 0
8161 | COLETOU1 | 1 | 629 | 0.000336 | south | 0.0037223 | -1.9668e-06 | -0.051627 | 0.0011672 | 1.9668e-06 | south | N | 1.9668e-06 | 0
8173 | VICEC51A | 5 | 144 | 0.000204 | south | 0.0035903 | -0.00013397 | -0.051759 | 0.0010352 | 0.00013397 | south | N | 0.00013397 | 0
8174 | VICEC61A | 6 | 188 | 0.000204 | south | 0.0035903 | -0.00013397 | -0.051759 | 0.0010352 | 0.00013397 | south | N | 0.00013397 | 0
8189 | CUERO 2 | 1 | 12 | 0.000238 | south | 0.0036243 | -9.9967e-05 | -0.051725 | 0.0010692 | 9.9967e-05 | south | N | 9.9967e-05 | 0
8262 | ELPS | 1 | 6 | 0.008626 | south | 0.012012 | 0.008288 | -0.043337 | 0.0094572 | 0.008288 | south | N | 0.008288 | 0
8285 | LAR #1 | MB | 32 | 0 | south | 0.0033863 | -0.00033797 | -0.051963 | 0.00083119 | 0.00033797 | south | N | 0.00033797 | 0
8287 | LAR #2 | MB | 32 | 0 | south | 0.0033863 | -0.00033797 | -0.051963 | 0.00083119 | 0.00033797 | south | N | 0.00033797 | 0
8288 | LAR #3 | MB | 105 | 0 | south | 0.0033863 | -0.00033797 | -0.051963 | 0.00083119 | 0.00033797 | south | N | 0.00033797 | 0
8388 | BATES0A | MB | 70 | 0 | south | 0.0033863 | -0.00033797 | -0.051963 | 0.00083119 | 0.00033797 | south | N | 0.00033797 | 0
8393 | BATES0B | MB | 110 | 0 | south | 0.0033863 | -0.00033797 | -0.051963 | 0.00083119 | 0.00033797 | south | N | 0.00033797 | 0
8442 | NBEC71A | 1 | 336 | 0.000337 | south | 0.0037233 | -9.6682e-07 | -0.051626 | 0.0011682 | 9.6682e-07 | south | N | 9.6682e-07 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | 0.0033863 | -0.00033797 | -0.051963 | 0.00083119 | 0.00033797 | south | N | 0.00033797 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | 0.0033863 | -0.00033797 | -0.051963 | 0.00083119 | 0.00033797 | south | N | 0.00033797 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.000343 | south | 0.0037293 | 5.0332e-06 | -0.05162 | 0.0011742 | 5.0332e-06 | south | N | 5.0332e-06 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.000343 | south | 0.0037293 | 5.0332e-06 | -0.05162 | 0.0011742 | 5.0332e-06 | south | N | 5.0332e-06 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.00035 | south | 0.0037363 | 1.2033e-05 | -0.051613 | 0.0011812 | 1.2033e-05 | south | N | 1.2033e-05 | 0
8506 | VAL #1 | 1 | 25 | 0.000346 | south | 0.0037323 | 8.0332e-06 | -0.051617 | 0.0011772 | 8.0332e-06 | south | N | 8.0332e-06 | 0
8507 | VAL #2 | 2 | 25 | 0.000346 | south | 0.0037323 | 8.0332e-06 | -0.051617 | 0.0011772 | 8.0332e-06 | south | N | 8.0332e-06 | 0
8511 | OXY_CC0A | 1 | 38 | 0.000347 | south | 0.0037333 | 9.0332e-06 | -0.051616 | 0.0011782 | 9.0332e-06 | south | N | 9.0332e-06 | 0
8517 | CELANEBI | 1 | 29 | 0.000366 | south | 0.0037523 | 2.8033e-05 | -0.051597 | 0.0011972 | 2.8033e-05 | south | N | 2.8033e-05 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.000337 | south | 0.0037233 | -9.6682e-07 | -0.051626 | 0.0011682 | 9.6682e-07 | south | N | 9.6682e-07 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.000337 | south | 0.0037233 | -9.6682e-07 | -0.051626 | 0.0011682 | 9.6682e-07 | south | N | 9.6682e-07 | 0
8562 | CNOPST1 | 3 | 153 | 0.000337 | south | 0.0037233 | -9.6682e-07 | -0.051626 | 0.0011682 | 9.6682e-07 | south | N | 9.6682e-07 | 0
8926 | LGE_GT10 | 1 | 158 | 0.000307 | south | 0.0036933 | -3.0967e-05 | -0.051656 | 0.0011382 | 3.0967e-05 | south | N | 3.0967e-05 | 0
8927 | LGE_GT20 | 2 | 153 | 0.000307 | south | 0.0036933 | -3.0967e-05 | -0.051656 | 0.0011382 | 3.0967e-05 | south | N | 3.0967e-05 | 0
8928 | LGE_STG0 | 3 | 100 | 0.000307 | south | 0.0036933 | -3.0967e-05 | -0.051656 | 0.0011382 | 3.0967e-05 | south | N | 3.0967e-05 | 0
8930 | ICPGN10A | 1 | 145 | 0.000307 | south | 0.0036933 | -3.0967e-05 | -0.051656 | 0.0011382 | 3.0967e-05 | south | N | 3.0967e-05 | 0
8931 | ICPGN20A | 2 | 147 | 0.000307 | south | 0.0036933 | -3.0967e-05 | -0.051656 | 0.0011382 | 3.0967e-05 | south | N | 3.0967e-05 | 0
8932 | ICPGN30A | 3 | 127 | 0.000307 | south | 0.0036933 | -3.0967e-05 | -0.051656 | 0.0011382 | 3.0967e-05 | south | N | 3.0967e-05 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.000474 | south | 0.0038603 | 0.00013603 | -0.051489 | 0.0013052 | 0.00013603 | south | N | 0.00013603 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.000474 | south | 0.0038603 | 0.00013603 | -0.051489 | 0.0013052 | 0.00013603 | south | N | 0.00013603 | 0
8935 | FGNTS201 | 3 | 173 | 0.000474 | south | 0.0038603 | 0.00013603 | -0.051489 | 0.0013052 | 0.00013603 | south | N | 0.00013603 | 0
8936 | MVGN#1 | 1 | 207 | 0.000423 | south | 0.0038093 | 8.5033e-05 | -0.05154 | 0.0012542 | 8.5033e-05 | south | N | 8.5033e-05 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.000423 | south | 0.0038093 | 8.5033e-05 | -0.05154 | 0.0012542 | 8.5033e-05 | south | N | 8.5033e-05 | 0
8938 | MVGN#3 | 3 | 242 | 0.000423 | south | 0.0038093 | 8.5033e-05 | -0.05154 | 0.0012542 | 8.5033e-05 | south | N | 8.5033e-05 | 0
8981 | HECN1 | 1 | 144 | 0.000423 | south | 0.0038093 | 8.5033e-05 | -0.05154 | 0.0012542 | 8.5033e-05 | south | N | 8.5033e-05 | 0
8982 | HECN2 | 2 | 144 | 0.000423 | south | 0.0038093 | 8.5033e-05 | -0.05154 | 0.0012542 | 8.5033e-05 | south | N | 8.5033e-05 | 0
8983 | HECN3 | 3 | 171 | 0.000423 | south | 0.0038093 | 8.5033e-05 | -0.05154 | 0.0012542 | 8.5033e-05 | south | N | 8.5033e-05 | 0
9000 | DECKR_G1 | 1 | 310 | 8.1e-05 | south | 0.0034673 | -0.00025697 | -0.051882 | 0.00091219 | 0.00025697 | south | N | 0.00025697 | 0
9001 | DECKR_G2 | 2 | 413 | 8.1e-05 | south | 0.0034673 | -0.00025697 | -0.051882 | 0.00091219 | 0.00025697 | south | N | 0.00025697 | 0
9002 | DECKR_G3 | 3 | 42 | 4.8e-05 | south | 0.0034343 | -0.00028997 | -0.051915 | 0.00087919 | 0.00028997 | south | N | 0.00028997 | 0
9003 | DECKR_G4 | 4 | 44 | 4.8e-05 | south | 0.0034343 | -0.00028997 | -0.051915 | 0.00087919 | 0.00028997 | south | N | 0.00028997 | 0
9004 | DECKR_G5 | 5 | 44 | 4.8e-05 | south | 0.0034343 | -0.00028997 | -0.051915 | 0.00087919 | 0.00028997 | south | N | 0.00028997 | 0
9005 | DECKR_G6 | 6 | 47 | 4.8e-05 | south | 0.0034343 | -0.00028997 | -0.051915 | 0.00087919 | 0.00028997 | south | N | 0.00028997 | 0
9016 | SANDH_G1 | 1 | 49 | 9e-05 | south | 0.0034763 | -0.00024797 | -0.051873 | 0.00092119 | 0.00024797 | south | N | 0.00024797 | 0
9017 | SANDH_G2 | 2 | 46 | 9e-05 | south | 0.0034763 | -0.00024797 | -0.051873 | 0.00092119 | 0.00024797 | south | N | 0.00024797 | 0
9018 | SANDH_G3 | 3 | 46 | 9e-05 | south | 0.0034763 | -0.00024797 | -0.051873 | 0.00092119 | 0.00024797 | south | N | 0.00024797 | 0
9019 | SANDH_G4 | 4 | 47 | 9e-05 | south | 0.0034763 | -0.00024797 | -0.051873 | 0.00092119 | 0.00024797 | south | N | 0.00024797 | 0
9020 | SANDHG5A | 5A | 154 | 9e-05 | south | 0.0034763 | -0.00024797 | -0.051873 | 0.00092119 | 0.00024797 | south | N | 0.00024797 | 0
9021 | SANDHG5C | 5C | 148 | 9e-05 | south | 0.0034763 | -0.00024797 | -0.051873 | 0.00092119 | 0.00024797 | south | N | 0.00024797 | 0
9022 | SANDH_G6 | 6 | 48 | 9e-05 | south | 0.0034763 | -0.00024797 | -0.051873 | 0.00092119 | 0.00024797 | south | N | 0.00024797 | 0
9023 | SANDH_G7 | 7 | 48 | 9e-05 | south | 0.0034763 | -0.00024797 | -0.051873 | 0.00092119 | 0.00024797 | south | N | 0.00024797 | 0
11001 | NAV1CT | 1 | 70 | 0.039501 | west | 0.042887 | 0.039163 | -0.012462 | 0.040332 | 0.012462 | west | N | 0.012462 | 0
11009 | NAV2CT | 1 | 70 | 0.039501 | west | 0.042887 | 0.039163 | -0.012462 | 0.040332 | 0.012462 | west | N | 0.012462 | 0
11011 | NAV3ST | 1 | 92.8 | 0.039501 | west | 0.042887 | 0.039163 | -0.012462 | 0.040332 | 0.012462 | west | N | 0.012462 | 0
11012 | NAV4CT | 1 | 80 | 0.039501 | west | 0.042887 | 0.039163 | -0.012462 | 0.040332 | 0.012462 | west | N | 0.012462 | 0
11013 | NAV5CT | 1 | 80 | 0.039501 | west | 0.042887 | 0.039163 | -0.012462 | 0.040332 | 0.012462 | west | N | 0.012462 | 0
11014 | NAV6ST | 1 | 115 | 0.039501 | west | 0.042887 | 0.039163 | -0.012462 | 0.040332 | 0.012462 | west | N | 0.012462 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.0395 | west | 0.042886 | 0.039162 | -0.012463 | 0.040331 | 0.012463 | west | N | 0.012463 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.0395 | west | 0.042886 | 0.039162 | -0.012463 | 0.040331 | 0.012463 | west | N | 0.012463 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.0395 | west | 0.042886 | 0.039162 | -0.012463 | 0.040331 | 0.012463 | west | N | 0.012463 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.0395 | west | 0.042886 | 0.039162 | -0.012463 | 0.040331 | 0.012463 | west | N | 0.012463 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.0395 | west | 0.042886 | 0.039162 | -0.012463 | 0.040331 | 0.012463 | west | N | 0.012463 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.0395 | west | 0.042886 | 0.039162 | -0.012463 | 0.040331 | 0.012463 | west | N | 0.012463 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.034797 | west | 0.038183 | 0.034459 | -0.017166 | 0.035628 | 0.017166 | west | N | 0.017166 | 0
11057 | CHAMPION | 1 | 126.5 | 0.034797 | west | 0.038183 | 0.034459 | -0.017166 | 0.035628 | 0.017166 | west | N | 0.017166 | 0
11058 | PYRON_1G | 1 | 249 | 0.034797 | west | 0.038183 | 0.034459 | -0.017166 | 0.035628 | 0.017166 | west | N | 0.017166 | 0
11059 | INADALE_ | 1 | 197 | 0.034797 | west | 0.038183 | 0.034459 | -0.017166 | 0.035628 | 0.017166 | west | N | 0.017166 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.03963 | west | 0.043016 | 0.039292 | -0.012333 | 0.040461 | 0.012333 | west | N | 0.012333 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.03963 | west | 0.043016 | 0.039292 | -0.012333 | 0.040461 | 0.012333 | west | N | 0.012333 | 0
11147 | NOTREES_ | 1 | 149 | 0.039632 | west | 0.043018 | 0.039294 | -0.012331 | 0.040463 | 0.012331 | west | N | 0.012331 | 0
11309 | BULLCREK | 1 | 180 | 0.041689 | west | 0.045075 | 0.041351 | -0.010274 | 0.04252 | 0.010274 | west | N | 0.010274 | 0
11310 | BULLCREK | 1 | 180 | 0.041689 | west | 0.045075 | 0.041351 | -0.010274 | 0.04252 | 0.010274 | west | N | 0.010274 | 0
11320 | COYOTE_1 | 1 | 225 | 0.041608 | west | 0.044994 | 0.04127 | -0.010355 | 0.042439 | 0.010355 | west | N | 0.010355 | 0
11415 | LORAINE_ | 1 | 125 | 0.039028 | west | 0.042414 | 0.03869 | -0.012935 | 0.039859 | 0.012935 | west | N | 0.012935 | 0
11416 | LORAINE_ | 1 | 125 | 0.039028 | west | 0.042414 | 0.03869 | -0.012935 | 0.039859 | 0.012935 | west | N | 0.012935 | 0
11691 | KMICHICT | 1 | 140 | -0.003687 | north | -0.00030066 | -0.004025 | -0.05565 | -0.0028558 | 0.00030066 | North | N | 0.00030066 | 0
11692 | KMICHICT | 2 | 141 | -0.003687 | north | -0.00030066 | -0.004025 | -0.05565 | -0.0028558 | 0.00030066 | North | N | 0.00030066 | 0
11693 | KMICHIST | 3 | 309 | -0.003687 | north | -0.00030066 | -0.004025 | -0.05565 | -0.0028558 | 0.00030066 | North | N | 0.00030066 | 0
11694 | KMICHICT | 4 | 143 | -0.003687 | north | -0.00030066 | -0.004025 | -0.05565 | -0.0028558 | 0.00030066 | North | N | 0.00030066 | 0
11695 | KMICHICT | 5 | 144 | -0.003687 | north | -0.00030066 | -0.004025 | -0.05565 | -0.0028558 | 0.00030066 | North | N | 0.00030066 | 0
11696 | KMICHIST | 6 | 310 | -0.003687 | north | -0.00030066 | -0.004025 | -0.05565 | -0.0028558 | 0.00030066 | North | N | 0.00030066 | 0
12322 | ENNSTRAC | 1 | 196 | -0.002453 | north | 0.00093334 | -0.002791 | -0.054416 | -0.0016218 | 0.00093334 | North | N | 0.00093334 | 0
12323 | ENNSTRAC | 2 | 111 | -0.002453 | north | 0.00093334 | -0.002791 | -0.054416 | -0.0016218 | 0.00093334 | North | N | 0.00093334 | 0
12357 | RNRTPL_1 | 1 | 0 | -0.003555 | north | -0.00016866 | -0.003893 | -0.055518 | -0.0027238 | 0.00016866 | North | N | 0.00016866 | 0
12411 | FPLEFR1A | 1 | 161 | -0.00311 | north | 0.00027634 | -0.003448 | -0.055073 | -0.0022788 | 0.00027634 | North | N | 0.00027634 | 0
12412 | FPLEFR1B | 2 | 164 | -0.00311 | north | 0.00027634 | -0.003448 | -0.055073 | -0.0022788 | 0.00027634 | North | N | 0.00027634 | 0
12413 | FPLEFR1C | 3 | 164 | -0.00311 | north | 0.00027634 | -0.003448 | -0.055073 | -0.0022788 | 0.00027634 | North | N | 0.00027634 | 0
12414 | FPLEFR1S | 4 | 414 | -0.00311 | north | 0.00027634 | -0.003448 | -0.055073 | -0.0022788 | 0.00027634 | North | N | 0.00027634 | 0
12421 | FPLEFR2A | 1 | 162 | -0.00311 | north | 0.00027634 | -0.003448 | -0.055073 | -0.0022788 | 0.00027634 | North | N | 0.00027634 | 0
12422 | FPLEFR2B | 2 | 161 | -0.00311 | north | 0.00027634 | -0.003448 | -0.055073 | -0.0022788 | 0.00027634 | North | N | 0.00027634 | 0
12423 | FPLEFR2C | 3 | 163 | -0.00311 | north | 0.00027634 | -0.003448 | -0.055073 | -0.0022788 | 0.00027634 | North | N | 0.00027634 | 0
12424 | FPLEFR2S | 4 | 409 | -0.00311 | north | 0.00027634 | -0.003448 | -0.055073 | -0.0022788 | 0.00027634 | North | N | 0.00027634 | 0
12440 | PARKD_1S | 1 | 0 | -0.003035 | north | 0.00035134 | -0.003373 | -0.054998 | -0.0022038 | 0.00035134 | North | N | 0.00035134 | 0
12449 | PARKD_2S | 1 | 0 | -0.003035 | north | 0.00035134 | -0.003373 | -0.054998 | -0.0022038 | 0.00035134 | North | N | 0.00035134 | 0
13116 | TGATEWAY | 1 | 148 | -0.002692 | north | 0.00069434 | -0.00303 | -0.054655 | -0.0018608 | 0.00069434 | North | N | 0.00069434 | 0
13117 | TGATEWAY | 2 | 130 | -0.002692 | north | 0.00069434 | -0.00303 | -0.054655 | -0.0018608 | 0.00069434 | North | N | 0.00069434 | 0
13118 | TGATEWAY | 3 | 145 | -0.002692 | north | 0.00069434 | -0.00303 | -0.054655 | -0.0018608 | 0.00069434 | North | N | 0.00069434 | 0
13119 | TGATEWAY | 4 | 399 | -0.002692 | north | 0.00069434 | -0.00303 | -0.054655 | -0.0018608 | 0.00069434 | North | N | 0.00069434 | 0
13131 | CALFREST | 1 | 150.7 | -0.00222 | north | 0.0011663 | -0.002558 | -0.054183 | -0.0013888 | 0.0011663 | North | N | 0.0011663 | 0
13132 | CALFREST | 2 | 151 | -0.00222 | north | 0.0011663 | -0.002558 | -0.054183 | -0.0013888 | 0.0011663 | North | N | 0.0011663 | 0
13133 | CALFREST | 3 | 177.4 | -0.00222 | north | 0.0011663 | -0.002558 | -0.054183 | -0.0013888 | 0.0011663 | North | N | 0.0011663 | 0
13134 | CALFREST | 4 | 151.5 | -0.002244 | north | 0.0011423 | -0.002582 | -0.054207 | -0.0014128 | 0.0011423 | North | N | 0.0011423 | 0
13135 | CALFREST | 5 | 152.3 | -0.002244 | north | 0.0011423 | -0.002582 | -0.054207 | -0.0014128 | 0.0011423 | North | N | 0.0011423 | 0
13136 | CALFREST | 6 | 177.5 | -0.002244 | north | 0.0011423 | -0.002582 | -0.054207 | -0.0014128 | 0.0011423 | North | N | 0.0011423 | 0
13432 | SANDOW_5 | 5 | 581 | -0.000471 | south | 0.0029153 | -0.00080897 | -0.052434 | 0.00036019 | 0.00036019 | houston | Y | 0.00080897 | 0.26074
13691 | OAKGROVE | 1 | 855 | -0.001756 | north | 0.0016303 | -0.002094 | -0.053719 | -0.00092481 | 0.00092481 | houston | Y | 0.0016303 | 0.60322
13692 | OAKGROVE | 2 | 855 | -0.001756 | north | 0.0016303 | -0.002094 | -0.053719 | -0.00092481 | 0.00092481 | houston | Y | 0.0016303 | 0.60322
32798 | BRYN_TAM | 1 | 32 | -0.001477 | north | 0.0019093 | -0.001815 | -0.05344 | -0.00064581 | 0.00064581 | houston | Y | 0.0019093 | 0.040433
32883 | BRYN_DNS | 1 | 48 | -0.001472 | north | 0.0019143 | -0.00181 | -0.053435 | -0.00064081 | 0.00064081 | houston | Y | 0.0019143 | 0.061129
32884 | BRYN_DNS | 1 | 46 | -0.001472 | north | 0.0019143 | -0.00181 | -0.053435 | -0.00064081 | 0.00064081 | houston | Y | 0.0019143 | 0.058582
32886 | BRYN_ATK | MB | 12 | -0.001479 | north | 0.0019073 | -0.001817 | -0.053442 | -0.00064781 | 0.00064781 | houston | Y | 0.0019073 | 0.015114
32887 | BRYN_ATK | MB | 51 | -0.001479 | north | 0.0019073 | -0.001817 | -0.053442 | -0.00064781 | 0.00064781 | houston | Y | 0.0019073 | 0.064236
32888 | BRYN_ATK | 1 | 17 | -0.001479 | north | 0.0019073 | -0.001817 | -0.053442 | -0.00064781 | 0.00064781 | houston | Y | 0.0019073 | 0.021412
32890 | BRYN_ATK | MB | 22 | -0.001479 | north | 0.0019073 | -0.001817 | -0.053442 | -0.00064781 | 0.00064781 | houston | Y | 0.0019073 | 0.02771
32891 | BRYN_ATK | MB | 25 | -0.001479 | north | 0.0019073 | -0.001817 | -0.053442 | -0.00064781 | 0.00064781 | houston | Y | 0.0019073 | 0.031488
32892 | BRYN_DNS | 1 | 105 | -0.001472 | north | 0.0019143 | -0.00181 | -0.053435 | -0.00064081 | 0.00064081 | houston | Y | 0.0019143 | 0.13372
36998 | RDCNYNG1 | 1 | 84 | 0.044229 | west | 0.047615 | 0.043891 | -0.0077341 | 0.04506 | 0.0077341 | west | N | 0.0077341 | 0
38332 | WDWRDU2 | 1 | 80 | 0.037597 | west | 0.040983 | 0.037259 | -0.014366 | 0.038428 | 0.014366 | west | N | 0.014366 | 0
38437 | TNSRBNMS | 1 | 150 | 0.03758 | west | 0.040966 | 0.037242 | -0.014383 | 0.038411 | 0.014383 | west | N | 0.014383 | 0
38438 | TNSRBNMS | 1 | 150 | 0.03758 | west | 0.040966 | 0.037242 | -0.014383 | 0.038411 | 0.014383 | west | N | 0.014383 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
38600 | TNBP_CGN | 5 | 53 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
38614 | TNBPAMCG | 4 | 96 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
38615 | TNBPAMCG | 1 | 244 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
38690 | TNBP_CGN | 3 | 40 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
39470 | TNDOWCGN | 1 | 32 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
39480 | TNDOWCGN | 1 | 30 | -0.000814 | houston | 0.0025723 | -0.001152 | -0.052777 | 1.7188e-05 | 1.7188e-05 | houston | N | 1.7188e-05 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.000667 | houston | 0.0027193 | -0.001005 | -0.05263 | 0.00016419 | 0.00016419 | houston | N | 0.00016419 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.000667 | houston | 0.0027193 | -0.001005 | -0.05263 | 0.00016419 | 0.00016419 | houston | N | 0.00016419 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.000667 | houston | 0.0027193 | -0.001005 | -0.05263 | 0.00016419 | 0.00016419 | houston | N | 0.00016419 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.000667 | houston | 0.0027193 | -0.001005 | -0.05263 | 0.00016419 | 0.00016419 | houston | N | 0.00016419 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.001756 | north | 0.0016303 | -0.002094 | -0.053719 | -0.00092481 | 0.00092481 | houston | Y | 0.0016303 | 0.10745
39970 | TNTNPONE | 1 | 153 | -0.001756 | north | 0.0016303 | -0.002094 | -0.053719 | -0.00092481 | 0.00092481 | houston | Y | 0.0016303 | 0.10795
48500 | APD_GT1_ | 1 | 136 | -0.000902 | houston | 0.0024843 | -0.00124 | -0.052865 | -7.0812e-05 | 7.0812e-05 | houston | N | 7.0812e-05 | 0
48510 | AK_GT1__ | 1 | 33 | -0.000765 | houston | 0.0026213 | -0.001103 | -0.052728 | 6.6188e-05 | 6.6188e-05 | houston | N | 6.6188e-05 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.000902 | houston | 0.0024843 | -0.00124 | -0.052865 | -7.0812e-05 | 7.0812e-05 | houston | N | 7.0812e-05 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.000902 | houston | 0.0024843 | -0.00124 | -0.052865 | -7.0812e-05 | 7.0812e-05 | houston | N | 7.0812e-05 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.000902 | houston | 0.0024843 | -0.00124 | -0.052865 | -7.0812e-05 | 7.0812e-05 | houston | N | 7.0812e-05 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.000902 | houston | 0.0024843 | -0.00124 | -0.052865 | -7.0812e-05 | 7.0812e-05 | houston | N | 7.0812e-05 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.00064 | houston | 0.0027463 | -0.00097797 | -0.052603 | 0.00019119 | 0.00019119 | houston | N | 0.00019119 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.00064 | houston | 0.0027463 | -0.00097797 | -0.052603 | 0.00019119 | 0.00019119 | houston | N | 0.00019119 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.000761 | houston | 0.0026253 | -0.001099 | -0.052724 | 7.0188e-05 | 7.0188e-05 | houston | N | 7.0188e-05 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.000761 | houston | 0.0026253 | -0.001099 | -0.052724 | 7.0188e-05 | 7.0188e-05 | houston | N | 7.0188e-05 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.000761 | houston | 0.0026253 | -0.001099 | -0.052724 | 7.0188e-05 | 7.0188e-05 | houston | N | 7.0188e-05 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.000869 | houston | 0.0025173 | -0.001207 | -0.052832 | -3.7812e-05 | 3.7812e-05 | houston | N | 3.7812e-05 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.000869 | houston | 0.0025173 | -0.001207 | -0.052832 | -3.7812e-05 | 3.7812e-05 | houston | N | 3.7812e-05 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.000869 | houston | 0.0025173 | -0.001207 | -0.052832 | -3.7812e-05 | 3.7812e-05 | houston | N | 3.7812e-05 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.000869 | houston | 0.0025173 | -0.001207 | -0.052832 | -3.7812e-05 | 3.7812e-05 | houston | N | 3.7812e-05 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.00089 | houston | 0.0024963 | -0.001228 | -0.052853 | -5.8812e-05 | 5.8812e-05 | houston | N | 5.8812e-05 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.00089 | houston | 0.0024963 | -0.001228 | -0.052853 | -5.8812e-05 | 5.8812e-05 | houston | N | 5.8812e-05 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.000863 | houston | 0.0025233 | -0.001201 | -0.052826 | -3.1812e-05 | 3.1812e-05 | houston | N | 3.1812e-05 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.000863 | houston | 0.0025233 | -0.001201 | -0.052826 | -3.1812e-05 | 3.1812e-05 | houston | N | 3.1812e-05 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.000863 | houston | 0.0025233 | -0.001201 | -0.052826 | -3.1812e-05 | 3.1812e-05 | houston | N | 3.1812e-05 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.000863 | houston | 0.0025233 | -0.001201 | -0.052826 | -3.1812e-05 | 3.1812e-05 | houston | N | 3.1812e-05 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.000863 | houston | 0.0025233 | -0.001201 | -0.052826 | -3.1812e-05 | 3.1812e-05 | houston | N | 3.1812e-05 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.000928 | houston | 0.0024583 | -0.001266 | -0.052891 | -9.6812e-05 | 9.6812e-05 | houston | N | 9.6812e-05 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.000918 | houston | 0.0024683 | -0.001256 | -0.052881 | -8.6812e-05 | 8.6812e-05 | houston | N | 8.6812e-05 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.000931 | houston | 0.0024553 | -0.001269 | -0.052894 | -9.9812e-05 | 9.9812e-05 | houston | N | 9.9812e-05 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.000931 | houston | 0.0024553 | -0.001269 | -0.052894 | -9.9812e-05 | 9.9812e-05 | houston | N | 9.9812e-05 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.000931 | houston | 0.0024553 | -0.001269 | -0.052894 | -9.9812e-05 | 9.9812e-05 | houston | N | 9.9812e-05 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.000991 | houston | 0.0023953 | -0.001329 | -0.052954 | -0.00015981 | 0.00015981 | houston | N | 0.00015981 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.000904 | houston | 0.0024823 | -0.001242 | -0.052867 | -7.2812e-05 | 7.2812e-05 | houston | N | 7.2812e-05 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.000904 | houston | 0.0024823 | -0.001242 | -0.052867 | -7.2812e-05 | 7.2812e-05 | houston | N | 7.2812e-05 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.000939 | houston | 0.0024473 | -0.001277 | -0.052902 | -0.00010781 | 0.00010781 | houston | N | 0.00010781 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.000939 | houston | 0.0024473 | -0.001277 | -0.052902 | -0.00010781 | 0.00010781 | houston | N | 0.00010781 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.000939 | houston | 0.0024473 | -0.001277 | -0.052902 | -0.00010781 | 0.00010781 | houston | N | 0.00010781 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.000939 | houston | 0.0024473 | -0.001277 | -0.052902 | -0.00010781 | 0.00010781 | houston | N | 0.00010781 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.000891 | houston | 0.0024953 | -0.001229 | -0.052854 | -5.9812e-05 | 5.9812e-05 | houston | N | 5.9812e-05 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.000891 | houston | 0.0024953 | -0.001229 | -0.052854 | -5.9812e-05 | 5.9812e-05 | houston | N | 5.9812e-05 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.000891 | houston | 0.0024953 | -0.001229 | -0.052854 | -5.9812e-05 | 5.9812e-05 | houston | N | 5.9812e-05 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.000891 | houston | 0.0024953 | -0.001229 | -0.052854 | -5.9812e-05 | 5.9812e-05 | houston | N | 5.9812e-05 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.000883 | houston | 0.0025033 | -0.001221 | -0.052846 | -5.1812e-05 | 5.1812e-05 | houston | N | 5.1812e-05 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.000883 | houston | 0.0025033 | -0.001221 | -0.052846 | -5.1812e-05 | 5.1812e-05 | houston | N | 5.1812e-05 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.000883 | houston | 0.0025033 | -0.001221 | -0.052846 | -5.1812e-05 | 5.1812e-05 | houston | N | 5.1812e-05 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.000883 | houston | 0.0025033 | -0.001221 | -0.052846 | -5.1812e-05 | 5.1812e-05 | houston | N | 5.1812e-05 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.000883 | houston | 0.0025033 | -0.001221 | -0.052846 | -5.1812e-05 | 5.1812e-05 | houston | N | 5.1812e-05 | 0
48651 | EP_1_2 | 1 | 5 | -0.000928 | houston | 0.0024583 | -0.001266 | -0.052891 | -9.6812e-05 | 9.6812e-05 | houston | N | 9.6812e-05 | 0
48651 | EP_1_2 | 2 | 21 | -0.000928 | houston | 0.0024583 | -0.001266 | -0.052891 | -9.6812e-05 | 9.6812e-05 | houston | N | 9.6812e-05 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.001396 | north | 0.0019903 | -0.001734 | -0.053359 | -0.00056481 | 0.00056481 | houston | Y | 0.0019903 | 0.21982
48672 | FTR_GT2_ | 2 | 156 | -0.001396 | north | 0.0019903 | -0.001734 | -0.053359 | -0.00056481 | 0.00056481 | houston | Y | 0.0019903 | 0.22238
48673 | FTR_GT3_ | 3 | 156 | -0.001396 | north | 0.0019903 | -0.001734 | -0.053359 | -0.00056481 | 0.00056481 | houston | Y | 0.0019903 | 0.22238
48674 | FTR_CN4_ | 4 | 380 | -0.001396 | north | 0.0019903 | -0.001734 | -0.053359 | -0.00056481 | 0.00056481 | houston | Y | 0.0019903 | 0.5417
48690 | GBY_GN5_ | 5 | 398 | -0.000942 | houston | 0.0024443 | -0.00128 | -0.052905 | -0.00011081 | 0.00011081 | houston | N | 0.00011081 | 0
48691 | GBY_7374 | A | 46 | -0.00088 | houston | 0.0025063 | -0.001218 | -0.052843 | -4.8812e-05 | 4.8812e-05 | houston | N | 4.8812e-05 | 0
48691 | GBY_7374 | B | 46 | -0.00088 | houston | 0.0025063 | -0.001218 | -0.052843 | -4.8812e-05 | 4.8812e-05 | houston | N | 4.8812e-05 | 0
48692 | GBY_8182 | C | 46 | -0.00088 | houston | 0.0025063 | -0.001218 | -0.052843 | -4.8812e-05 | 4.8812e-05 | houston | N | 4.8812e-05 | 0
48692 | GBY_8182 | D | 55 | -0.00088 | houston | 0.0025063 | -0.001218 | -0.052843 | -4.8812e-05 | 4.8812e-05 | houston | N | 4.8812e-05 | 0
48693 | GBY_8384 | E | 55 | -0.00088 | houston | 0.0025063 | -0.001218 | -0.052843 | -4.8812e-05 | 4.8812e-05 | houston | N | 4.8812e-05 | 0
48693 | GBY_8384 | F | 54 | -0.00088 | houston | 0.0025063 | -0.001218 | -0.052843 | -4.8812e-05 | 4.8812e-05 | houston | N | 4.8812e-05 | 0
48721 | LEG_1___ | 1 | 827 | -0.001867 | north | 0.0015193 | -0.002205 | -0.05383 | -0.0010358 | 0.0010358 | houston | Y | 0.0015193 | 0.39988
48722 | LEG_2___ | 2 | 819 | -0.001867 | north | 0.0015193 | -0.002205 | -0.05383 | -0.0010358 | 0.0010358 | houston | Y | 0.0015193 | 0.39601
48730 | MNS_GT | 1 | 46.1 | -0.000752 | houston | 0.0026343 | -0.00109 | -0.052715 | 7.9188e-05 | 7.9188e-05 | houston | N | 7.9188e-05 | 0
48731 | CBE_GT1 | 1 | 76 | -0.000458 | houston | 0.0029283 | -0.00079597 | -0.052421 | 0.00037319 | 0.00037319 | houston | N | 0.00037319 | 0
48732 | CBE_GT2 | 1 | 76 | -0.000458 | houston | 0.0029283 | -0.00079597 | -0.052421 | 0.00037319 | 0.00037319 | houston | N | 0.00037319 | 0
48733 | CBE_ST12 | 1 | 105 | -0.000458 | houston | 0.0029283 | -0.00079597 | -0.052421 | 0.00037319 | 0.00037319 | houston | N | 0.00037319 | 0
48734 | CBE_GT3 | 1 | 74 | -0.000458 | houston | 0.0029283 | -0.00079597 | -0.052421 | 0.00037319 | 0.00037319 | houston | N | 0.00037319 | 0
48735 | CBE_GT4 | 1 | 74 | -0.000458 | houston | 0.0029283 | -0.00079597 | -0.052421 | 0.00037319 | 0.00037319 | houston | N | 0.00037319 | 0
48736 | CBE_ST34 | 1 | 102 | -0.000458 | houston | 0.0029283 | -0.00079597 | -0.052421 | 0.00037319 | 0.00037319 | houston | N | 0.00037319 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.000891 | houston | 0.0024953 | -0.001229 | -0.052854 | -5.9812e-05 | 5.9812e-05 | houston | N | 5.9812e-05 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.000891 | houston | 0.0024953 | -0.001229 | -0.052854 | -5.9812e-05 | 5.9812e-05 | houston | N | 5.9812e-05 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.000891 | houston | 0.0024953 | -0.001229 | -0.052854 | -5.9812e-05 | 5.9812e-05 | houston | N | 5.9812e-05 | 0
48761 | PR_GT1__ | 1 | 35 | -0.000887 | houston | 0.0024993 | -0.001225 | -0.05285 | -5.5812e-05 | 5.5812e-05 | houston | N | 5.5812e-05 | 0
48772 | PHR_GN2_ | MB | 459 | -0.000846 | houston | 0.0025403 | -0.001184 | -0.052809 | -1.4812e-05 | 1.4812e-05 | houston | N | 1.4812e-05 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.000928 | houston | 0.0024583 | -0.001266 | -0.052891 | -9.6812e-05 | 9.6812e-05 | houston | N | 9.6812e-05 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.000928 | houston | 0.0024583 | -0.001266 | -0.052891 | -9.6812e-05 | 9.6812e-05 | houston | N | 9.6812e-05 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.000928 | houston | 0.0024583 | -0.001266 | -0.052891 | -9.6812e-05 | 9.6812e-05 | houston | N | 9.6812e-05 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.000928 | houston | 0.0024583 | -0.001266 | -0.052891 | -9.6812e-05 | 9.6812e-05 | houston | N | 9.6812e-05 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.000928 | houston | 0.0024583 | -0.001266 | -0.052891 | -9.6812e-05 | 9.6812e-05 | houston | N | 9.6812e-05 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.000928 | houston | 0.0024583 | -0.001266 | -0.052891 | -9.6812e-05 | 9.6812e-05 | houston | N | 9.6812e-05 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.000928 | houston | 0.0024583 | -0.001266 | -0.052891 | -9.6812e-05 | 9.6812e-05 | houston | N | 9.6812e-05 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.000991 | houston | 0.0023953 | -0.001329 | -0.052954 | -0.00015981 | 0.00015981 | houston | N | 0.00015981 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.000991 | houston | 0.0023953 | -0.001329 | -0.052954 | -0.00015981 | 0.00015981 | houston | N | 0.00015981 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.000991 | houston | 0.0023953 | -0.001329 | -0.052954 | -0.00015981 | 0.00015981 | houston | N | 0.00015981 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.000991 | houston | 0.0023953 | -0.001329 | -0.052954 | -0.00015981 | 0.00015981 | houston | N | 0.00015981 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.000931 | houston | 0.0024553 | -0.001269 | -0.052894 | -9.9812e-05 | 9.9812e-05 | houston | N | 9.9812e-05 | 0
48820 | SHELLG1_ | 1 | 71 | -0.000895 | houston | 0.0024913 | -0.001233 | -0.052858 | -6.3812e-05 | 6.3812e-05 | houston | N | 6.3812e-05 | 0
48821 | SHELLG2 | 2 | 72 | -0.000895 | houston | 0.0024913 | -0.001233 | -0.052858 | -6.3812e-05 | 6.3812e-05 | houston | N | 6.3812e-05 | 0
48822 | SHELLG3_ | 1 | 39 | -0.000895 | houston | 0.0024913 | -0.001233 | -0.052858 | -6.3812e-05 | 6.3812e-05 | houston | N | 6.3812e-05 | 0
48822 | SHELLG3_ | 2 | 30 | -0.000895 | houston | 0.0024913 | -0.001233 | -0.052858 | -6.3812e-05 | 6.3812e-05 | houston | N | 6.3812e-05 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.000881 | houston | 0.0025053 | -0.001219 | -0.052844 | -4.9812e-05 | 4.9812e-05 | houston | N | 4.9812e-05 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.000881 | houston | 0.0025053 | -0.001219 | -0.052844 | -4.9812e-05 | 4.9812e-05 | houston | N | 4.9812e-05 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.000891 | houston | 0.0024953 | -0.001229 | -0.052854 | -5.9812e-05 | 5.9812e-05 | houston | N | 5.9812e-05 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.00089 | houston | 0.0024963 | -0.001228 | -0.052853 | -5.8812e-05 | 5.8812e-05 | houston | N | 5.8812e-05 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.00089 | houston | 0.0024963 | -0.001228 | -0.052853 | -5.8812e-05 | 5.8812e-05 | houston | N | 5.8812e-05 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.000891 | houston | 0.0024953 | -0.001229 | -0.052854 | -5.9812e-05 | 5.9812e-05 | houston | N | 5.9812e-05 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.000891 | houston | 0.0024953 | -0.001229 | -0.052854 | -5.9812e-05 | 5.9812e-05 | houston | N | 5.9812e-05 | 0
48855 | SRB_GT21 | B2 | 12 | -0.00089 | houston | 0.0024963 | -0.001228 | -0.052853 | -5.8812e-05 | 5.8812e-05 | houston | N | 5.8812e-05 | 0
48855 | SRB_GT21 | MB | 18 | -0.00089 | houston | 0.0024963 | -0.001228 | -0.052853 | -5.8812e-05 | 5.8812e-05 | houston | N | 5.8812e-05 | 0
48865 | TECO_GT1 | 1 | 50 | -0.000835 | houston | 0.0025513 | -0.001173 | -0.052798 | -3.8122e-06 | 3.8122e-06 | houston | N | 3.8122e-06 | 0
48873 | THW_ST3_ | 3 | 104 | -0.000916 | houston | 0.0024703 | -0.001254 | -0.052879 | -8.4812e-05 | 8.4812e-05 | houston | N | 8.4812e-05 | 0
48874 | THW_ST4_ | 4 | 104 | -0.000916 | houston | 0.0024703 | -0.001254 | -0.052879 | -8.4812e-05 | 8.4812e-05 | houston | N | 8.4812e-05 | 0
48875 | THW_3132 | A | 54 | -0.000916 | houston | 0.0024703 | -0.001254 | -0.052879 | -8.4812e-05 | 8.4812e-05 | houston | N | 8.4812e-05 | 0
48875 | THW_3132 | B | 53 | -0.000916 | houston | 0.0024703 | -0.001254 | -0.052879 | -8.4812e-05 | 8.4812e-05 | houston | N | 8.4812e-05 | 0
48877 | THW_3334 | C | 54 | -0.000916 | houston | 0.0024703 | -0.001254 | -0.052879 | -8.4812e-05 | 8.4812e-05 | houston | N | 8.4812e-05 | 0
48877 | THW_3334 | D | 57 | -0.000916 | houston | 0.0024703 | -0.001254 | -0.052879 | -8.4812e-05 | 8.4812e-05 | houston | N | 8.4812e-05 | 0
48879 | THW_4142 | E | 54 | -0.000916 | houston | 0.0024703 | -0.001254 | -0.052879 | -8.4812e-05 | 8.4812e-05 | houston | N | 8.4812e-05 | 0
48879 | THW_4142 | F | 54 | -0.000916 | houston | 0.0024703 | -0.001254 | -0.052879 | -8.4812e-05 | 8.4812e-05 | houston | N | 8.4812e-05 | 0
48881 | THW_4344 | G | 58 | -0.000916 | houston | 0.0024703 | -0.001254 | -0.052879 | -8.4812e-05 | 8.4812e-05 | houston | N | 8.4812e-05 | 0
48881 | THW_4344 | H | 58 | -0.000916 | houston | 0.0024703 | -0.001254 | -0.052879 | -8.4812e-05 | 8.4812e-05 | houston | N | 8.4812e-05 | 0
48883 | THW_GT1_ | B2 | 12 | -0.000925 | houston | 0.0024613 | -0.001263 | -0.052888 | -9.3812e-05 | 9.3812e-05 | houston | N | 9.3812e-05 | 0
48885 | THW_5152 | A | 56 | -0.000947 | houston | 0.0024393 | -0.001285 | -0.05291 | -0.00011581 | 0.00011581 | houston | N | 0.00011581 | 0
48885 | THW_5152 | B | 59 | -0.000947 | houston | 0.0024393 | -0.001285 | -0.05291 | -0.00011581 | 0.00011581 | houston | N | 0.00011581 | 0
48886 | THW_5354 | C | 56 | -0.000947 | houston | 0.0024393 | -0.001285 | -0.05291 | -0.00011581 | 0.00011581 | houston | N | 0.00011581 | 0
48886 | THW_5354 | D | 56 | -0.000947 | houston | 0.0024393 | -0.001285 | -0.05291 | -0.00011581 | 0.00011581 | houston | N | 0.00011581 | 0
48887 | THW_5556 | E | 59 | -0.000947 | houston | 0.0024393 | -0.001285 | -0.05291 | -0.00011581 | 0.00011581 | houston | N | 0.00011581 | 0
48887 | THW_5556 | F | 56 | -0.000947 | houston | 0.0024393 | -0.001285 | -0.05291 | -0.00011581 | 0.00011581 | houston | N | 0.00011581 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.000478 | houston | 0.0029083 | -0.00081597 | -0.052441 | 0.00035319 | 0.00035319 | houston | N | 0.00035319 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.000777 | houston | 0.0026093 | -0.001115 | -0.05274 | 5.4188e-05 | 5.4188e-05 | houston | N | 5.4188e-05 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.000777 | houston | 0.0026093 | -0.001115 | -0.05274 | 5.4188e-05 | 5.4188e-05 | houston | N | 5.4188e-05 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.000777 | houston | 0.0026093 | -0.001115 | -0.05274 | 5.4188e-05 | 5.4188e-05 | houston | N | 5.4188e-05 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.000777 | houston | 0.0026093 | -0.001115 | -0.05274 | 5.4188e-05 | 5.4188e-05 | houston | N | 5.4188e-05 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.000777 | houston | 0.0026093 | -0.001115 | -0.05274 | 5.4188e-05 | 5.4188e-05 | houston | N | 5.4188e-05 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.000761 | houston | 0.0026253 | -0.001099 | -0.052724 | 7.0188e-05 | 7.0188e-05 | houston | N | 7.0188e-05 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.000761 | houston | 0.0026253 | -0.001099 | -0.052724 | 7.0188e-05 | 7.0188e-05 | houston | N | 7.0188e-05 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.000761 | houston | 0.0026253 | -0.001099 | -0.052724 | 7.0188e-05 | 7.0188e-05 | houston | N | 7.0188e-05 | 0
48929 | WAPGT21_ | B1 | 13 | -0.000777 | houston | 0.0026093 | -0.001115 | -0.05274 | 5.4188e-05 | 5.4188e-05 | houston | N | 5.4188e-05 | 0
48940 | WARVUE_G | G1 | 12 | -0.000928 | houston | 0.0024583 | -0.001266 | -0.052891 | -9.6812e-05 | 9.6812e-05 | houston | N | 9.6812e-05 | 0
49803 | EXN_15GT | 1 | 34 | -0.00092 | houston | 0.0024663 | -0.001258 | -0.052883 | -8.8812e-05 | 8.8812e-05 | houston | N | 8.8812e-05 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.00092 | houston | 0.0024663 | -0.001258 | -0.052883 | -8.8812e-05 | 8.8812e-05 | houston | N | 8.8812e-05 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.00092 | houston | 0.0024663 | -0.001258 | -0.052883 | -8.8812e-05 | 8.8812e-05 | houston | N | 8.8812e-05 | 0
49826 | EXN938GT | 5 | 45.9 | -0.00092 | houston | 0.0024663 | -0.001258 | -0.052883 | -8.8812e-05 | 8.8812e-05 | houston | N | 8.8812e-05 | 0
49828 | EXN941GT | 10 | 17.7 | -0.00092 | houston | 0.0024663 | -0.001258 | -0.052883 | -8.8812e-05 | 8.8812e-05 | houston | N | 8.8812e-05 | 0
49829 | EXN942GT | 11 | 20.4 | -0.00092 | houston | 0.0024663 | -0.001258 | -0.052883 | -8.8812e-05 | 8.8812e-05 | houston | N | 8.8812e-05 | 0
49830 | EXN943GT | 12 | 19.9 | -0.00092 | houston | 0.0024663 | -0.001258 | -0.052883 | -8.8812e-05 | 8.8812e-05 | houston | N | 8.8812e-05 | 0
49831 | EXN944GT | 13 | 35 | -0.00092 | houston | 0.0024663 | -0.001258 | -0.052883 | -8.8812e-05 | 8.8812e-05 | houston | N | 8.8812e-05 | 0
49832 | EXN945GT | 9 | 18 | -0.00092 | houston | 0.0024663 | -0.001258 | -0.052883 | -8.8812e-05 | 8.8812e-05 | houston | N | 8.8812e-05 | 0
49837 | EXN_GT | 4 | 85.4 | -0.00092 | houston | 0.0024663 | -0.001258 | -0.052883 | -8.8812e-05 | 8.8812e-05 | houston | N | 8.8812e-05 | 0
49838 | EXN_14GT | 14 | 148 | -0.00092 | houston | 0.0024663 | -0.001258 | -0.052883 | -8.8812e-05 | 8.8812e-05 | houston | N | 8.8812e-05 | 0
49851 | DOW17000 | 37 | 62 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49858 | DOW38100 | 31 | 71.4 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49859 | DOW38200 | 33 | 45 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49860 | DOW38300 | 32 | 101 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49862 | DOW39100 | 36 | 86 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49863 | DOW39200 | 35 | 88 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49865 | DOW41000 | 41 | 50 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49866 | DOW42000 | 42 | 18 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49869 | DOW49000 | 45 | 94 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49870 | DOW61000 | 61 | 70 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49871 | DOW62000 | 62 | 63 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49872 | DOW63000 | 63 | 72 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49873 | DOW64000 | 64 | 64.8 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49876 | DOW65000 | 65 | 101 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49877 | DOW66000 | 66 | 97 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49878 | DOW67000 | 67 | 103 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49882 | DOW81000 | 81 | 76 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49884 | DOW82000 | 82 | 80 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49885 | DOW83000 | 83 | 80 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
49886 | DOW84000 | 84 | 171 | -0.000609 | houston | 0.0027773 | -0.00094697 | -0.052572 | 0.00022219 | 0.00022219 | houston | N | 0.00022219 | 0
58909 | PEARSALL | 1 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58909 | PEARSALL | 2 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58909 | PEARSALL | 3 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58909 | PEARSALL | 4 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58909 | PEARSALL | 5 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58909 | PEARSALL | 6 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58919 | PEARSALL | 1 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58919 | PEARSALL | 2 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58919 | PEARSALL | 3 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58919 | PEARSALL | 4 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58919 | PEARSALL | 5 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58919 | PEARSALL | 6 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58929 | PEARSALL | 1 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58929 | PEARSALL | 2 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58929 | PEARSALL | 3 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58929 | PEARSALL | 4 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58929 | PEARSALL | 5 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58929 | PEARSALL | 6 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58949 | PEARSALL | 1 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58949 | PEARSALL | 2 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58949 | PEARSALL | 3 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58949 | PEARSALL | 4 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58949 | PEARSALL | 5 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
58949 | PEARSALL | 6 | 8.4 | 0.002286 | south | 0.0056723 | 0.001948 | -0.049677 | 0.0031172 | 0.001948 | south | N | 0.001948 | 0
60000 | DSKY2 | 1 | 76.5 | 0.036842 | west | 0.040228 | 0.036504 | -0.015121 | 0.037673 | 0.015121 | west | N | 0.015121 | 0
60003 | KING_NE1 | 1 | 80 | 0.037626 | west | 0.041012 | 0.037288 | -0.014337 | 0.038457 | 0.014337 | west | N | 0.014337 | 0
60005 | KING_SE1 | 1 | 40 | 0.037626 | west | 0.041012 | 0.037288 | -0.014337 | 0.038457 | 0.014337 | west | N | 0.014337 | 0
60007 | KING_SW1 | 1 | 80 | 0.037749 | west | 0.041135 | 0.037411 | -0.014214 | 0.03858 | 0.014214 | west | N | 0.014214 | 0
60016 | WOODWRD1 | 1 | 80 | 0.0376 | west | 0.040986 | 0.037262 | -0.014363 | 0.038431 | 0.014363 | west | N | 0.014363 | 0
60017 | ORNNWP1 | 1 | 80 | 0.036962 | west | 0.040348 | 0.036624 | -0.015001 | 0.037793 | 0.015001 | west | N | 0.015001 | 0
60018 | DSKY1 | 1 | 84 | 0.036753 | west | 0.040139 | 0.036415 | -0.01521 | 0.037584 | 0.01521 | west | N | 0.01521 | 0
60019 | KING_NW1 | 1 | 80 | 0.037749 | west | 0.041135 | 0.037411 | -0.014214 | 0.03858 | 0.014214 | west | N | 0.014214 | 0
60057 | CALLAHAN | 1 | 114 | 0.000714 | south | 0.0041003 | 0.00037603 | -0.051249 | 0.0015452 | 0.00037603 | south | N | 0.00037603 | 0
60058 | BUFF_GAP | 1 | 120 | 0.048933 | west | 0.052319 | 0.048595 | -0.0030301 | 0.049764 | 0.0030301 | west | N | 0.0030301 | 0
60060 | CIRELLO | 1 | 233 | 0.048933 | west | 0.052319 | 0.048595 | -0.0030301 | 0.049764 | 0.0030301 | west | N | 0.0030301 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.048933 | west | 0.052319 | 0.048595 | -0.0030301 | 0.049764 | 0.0030301 | west | N | 0.0030301 | 0
60066 | H_HOLLOW | 1 | 222 | 0.000714 | south | 0.0041003 | 0.00037603 | -0.051249 | 0.0015452 | 0.00037603 | south | N | 0.00037603 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.000714 | south | 0.0041003 | 0.00037603 | -0.051249 | 0.0015452 | 0.00037603 | south | N | 0.00037603 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.000714 | south | 0.0041003 | 0.00037603 | -0.051249 | 0.0015452 | 0.00037603 | south | N | 0.00037603 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.000714 | south | 0.0041003 | 0.00037603 | -0.051249 | 0.0015452 | 0.00037603 | south | N | 0.00037603 | 0
60074 | HORSH5 | 1 | 100 | 0.000714 | south | 0.0041003 | 0.00037603 | -0.051249 | 0.0015452 | 0.00037603 | south | N | 0.00037603 | 0
60081 | WHRLWIND | 1 | 60 | 0.074307 | west | 0.077693 | 0.073969 | 0.022344 | 0.075138 | 0.022344 | west | N | 0.022344 | 0
60201 | RIO DRCS | F | 0 | 0.012817 | south | 0.016203 | 0.012479 | -0.039146 | 0.013648 | 0.012479 | south | N | 0.012479 | 0
60202 | FRIEND_R | F | 0 | 0.033436 | west | 0.036822 | 0.033098 | -0.018527 | 0.034267 | 0.018527 | west | N | 0.018527 | 0
60203 | PRES0A | BT | 4.8 | 0.038222 | west | 0.041608 | 0.037884 | -0.013741 | 0.039053 | 0.013741 | west | N | 0.013741 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.048374 | west | 0.05176 | 0.048036 | -0.0035891 | 0.049205 | 0.0035891 | west | N | 0.0035891 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.048374 | west | 0.05176 | 0.048036 | -0.0035891 | 0.049205 | 0.0035891 | west | N | 0.0035891 | 0
71057 | L_SWEETW | W1 | 135 | 0.048374 | west | 0.05176 | 0.048036 | -0.0035891 | 0.049205 | 0.0035891 | west | N | 0.0035891 | 0
71059 | L_SWEETW | W1 | 119 | 0.048374 | west | 0.05176 | 0.048036 | -0.0035891 | 0.049205 | 0.0035891 | west | N | 0.0035891 | 0
71060 | L_SWEETW | W1 | 105 | 0.048374 | west | 0.05176 | 0.048036 | -0.0035891 | 0.049205 | 0.0035891 | west | N | 0.0035891 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.048374 | west | 0.05176 | 0.048036 | -0.0035891 | 0.049205 | 0.0035891 | west | N | 0.0035891 | 0
76031 | L_GASCCR | W1 | 150 | 0.039029 | west | 0.042415 | 0.038691 | -0.012934 | 0.03986 | 0.012934 | west | N | 0.012934 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.038905 | west | 0.042291 | 0.038567 | -0.013058 | 0.039736 | 0.013058 | west | N | 0.013058 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.038905 | west | 0.042291 | 0.038567 | -0.013058 | 0.039736 | 0.013058 | west | N | 0.013058 | 0
76096 | L_CAPRSI | W1 | 186 | 0.038905 | west | 0.042291 | 0.038567 | -0.013058 | 0.039736 | 0.013058 | west | N | 0.013058 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.038905 | west | 0.042291 | 0.038567 | -0.013058 | 0.039736 | 0.013058 | west | N | 0.013058 | 0
80003 | MILHWYS | F | 0 | 0.000393 | south | 0.0037793 | 5.5033e-05 | -0.05157 | 0.0012242 | 5.5033e-05 | south | N | 5.5033e-05 | 0
80010 | EPLVT1 | F | 0 | 0.007907 | south | 0.011293 | 0.007569 | -0.044056 | 0.0087382 | 0.007569 | south | N | 0.007569 | 0
80012 | LAR | F | 0 | 0.001405 | south | 0.0047913 | 0.001067 | -0.050558 | 0.0022362 | 0.001067 | south | N | 0.001067 | 0
80051 | FORPVCM0 | 8 | 28 | 8.1e-05 | south | 0.0034673 | -0.00025697 | -0.051882 | 0.00091219 | 0.00025697 | south | N | 0.00025697 | 0
80052 | FOR69CG0 | 9 | 43.6 | 8.1e-05 | south | 0.0034673 | -0.00025697 | -0.051882 | 0.00091219 | 0.00025697 | south | N | 0.00025697 | 0
80053 | FOR69CG0 | 10 | 74 | 8.1e-05 | south | 0.0034673 | -0.00025697 | -0.051882 | 0.00091219 | 0.00025697 | south | N | 0.00025697 | 0
80080 | GWINDT11 | 1 | 94 | 0.000381 | south | 0.0037673 | 4.3033e-05 | -0.051582 | 0.0012122 | 4.3033e-05 | south | N | 4.3033e-05 | 0
80080 | GWINDT11 | 2 | 41 | 0.000381 | south | 0.0037673 | 4.3033e-05 | -0.051582 | 0.0012122 | 4.3033e-05 | south | N | 4.3033e-05 | 0
80080 | GWINDT11 | 3 | 38 | 0.000381 | south | 0.0037673 | 4.3033e-05 | -0.051582 | 0.0012122 | 4.3033e-05 | south | N | 4.3033e-05 | 0
80080 | GWINDT11 | 4 | 19 | 0.000381 | south | 0.0037673 | 4.3033e-05 | -0.051582 | 0.0012122 | 4.3033e-05 | south | N | 4.3033e-05 | 0
80081 | GWINDT21 | 1 | 94 | 0.000381 | south | 0.0037673 | 4.3033e-05 | -0.051582 | 0.0012122 | 4.3033e-05 | south | N | 4.3033e-05 | 0
80081 | GWINDT21 | 2 | 36 | 0.000381 | south | 0.0037673 | 4.3033e-05 | -0.051582 | 0.0012122 | 4.3033e-05 | south | N | 4.3033e-05 | 0
80081 | GWINDT21 | 3 | 43 | 0.000381 | south | 0.0037673 | 4.3033e-05 | -0.051582 | 0.0012122 | 4.3033e-05 | south | N | 4.3033e-05 | 0
80081 | GWINDT21 | 4 | 22 | 0.000381 | south | 0.0037673 | 4.3033e-05 | -0.051582 | 0.0012122 | 4.3033e-05 | south | N | 4.3033e-05 | 0
80137 | CSDR89 | 8 | 39 | 0.000152 | south | 0.0035383 | -0.00018597 | -0.051811 | 0.00098319 | 0.00018597 | south | N | 0.00018597 | 0
80137 | CSDR89 | 9 | 15 | 0.000152 | south | 0.0035383 | -0.00018597 | -0.051811 | 0.00098319 | 0.00018597 | south | N | 0.00018597 | 0
80138 | CSDR7 | 7 | 7 | 0.000152 | south | 0.0035383 | -0.00018597 | -0.051811 | 0.00098319 | 0.00018597 | south | N | 0.00018597 | 0
80139 | CSDR56 | 5 | 15 | 0.000152 | south | 0.0035383 | -0.00018597 | -0.051811 | 0.00098319 | 0.00018597 | south | N | 0.00018597 | 0
80139 | CSDR56 | 6 | 39 | 0.000152 | south | 0.0035383 | -0.00018597 | -0.051811 | 0.00098319 | 0.00018597 | south | N | 0.00018597 | 0
80140 | CSDR11 | 11 | 39 | 0.000152 | south | 0.0035383 | -0.00018597 | -0.051811 | 0.00098319 | 0.00018597 | south | N | 0.00018597 | 0
80180 | PNSCALT1 | 1 | 148 | 0.000381 | south | 0.0037673 | 4.3033e-05 | -0.051582 | 0.0012122 | 4.3033e-05 | south | N | 4.3033e-05 | 0
80180 | PNSCALT1 | 2 | 50 | 0.000381 | south | 0.0037673 | 4.3033e-05 | -0.051582 | 0.0012122 | 4.3033e-05 | south | N | 4.3033e-05 | 0
80181 | PNSCALT2 | 1 | 55 | 0.000381 | south | 0.0037673 | 4.3033e-05 | -0.051582 | 0.0012122 | 4.3033e-05 | south | N | 4.3033e-05 | 0
80181 | PNSCALT2 | 2 | 50 | 0.000381 | south | 0.0037673 | 4.3033e-05 | -0.051582 | 0.0012122 | 4.3033e-05 | south | N | 4.3033e-05 | 0
80223 | REYSHR G | 1 | 12 | 0.000307 | south | 0.0036933 | -3.0967e-05 | -0.051656 | 0.0011382 | 3.0967e-05 | south | N | 3.0967e-05 | 0
80224 | VISTRONG | 1 | 15 | 0.000167 | south | 0.0035533 | -0.00017097 | -0.051796 | 0.00099819 | 0.00017097 | south | N | 0.00017097 | 0
80225 | VISTRONG | 2 | 23 | 0.000167 | south | 0.0035533 | -0.00017097 | -0.051796 | 0.00099819 | 0.00017097 | south | N | 0.00017097 | 0
80226 | ALCOA G | 1 | 48 | 9.6e-05 | south | 0.0034823 | -0.00024197 | -0.051867 | 0.00092719 | 0.00024197 | south | N | 0.00024197 | 0
80227 | AIRCO G | 1 | 8 | 0.000163 | south | 0.0035493 | -0.00017497 | -0.0518 | 0.00099419 | 0.00017497 | south | N | 0.00017497 | 0
80261 | NBEC81A | 1 | 180 | 0.000338 | south | 0.0037243 | 3.3182e-08 | -0.051625 | 0.0011692 | 3.3182e-08 | south | N | 3.3182e-08 | 0
80262 | NBEC91A | 1 | 180 | 0.000337 | south | 0.0037233 | -9.6682e-07 | -0.051626 | 0.0011682 | 9.6682e-07 | south | N | 9.6682e-07 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.000343 | south | 0.0037293 | 5.0332e-06 | -0.05162 | 0.0011742 | 5.0332e-06 | south | N | 5.0332e-06 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.000343 | south | 0.0037293 | 5.0332e-06 | -0.05162 | 0.0011742 | 5.0332e-06 | south | N | 5.0332e-06 | 0
80265 | LARECU40 | 4 | 100 | 0.001404 | south | 0.0047903 | 0.001066 | -0.050559 | 0.0022352 | 0.001066 | south | N | 0.001066 | 0
80266 | LARECU50 | 5 | 100 | 0.001404 | south | 0.0047903 | 0.001066 | -0.050559 | 0.0022352 | 0.001066 | south | N | 0.001066 | 0
80291 | PAPALOTE | 1 | 25 | 0.000319 | south | 0.0037053 | -1.8967e-05 | -0.051644 | 0.0011502 | 1.8967e-05 | south | N | 1.8967e-05 | 0
80291 | PAPALOTE | 2 | 25 | 0.000319 | south | 0.0037053 | -1.8967e-05 | -0.051644 | 0.0011502 | 1.8967e-05 | south | N | 1.8967e-05 | 0
80291 | PAPALOTE | 3 | 25 | 0.000319 | south | 0.0037053 | -1.8967e-05 | -0.051644 | 0.0011502 | 1.8967e-05 | south | N | 1.8967e-05 | 0
80291 | PAPALOTE | 4 | 16 | 0.000319 | south | 0.0037053 | -1.8967e-05 | -0.051644 | 0.0011502 | 1.8967e-05 | south | N | 1.8967e-05 | 0
80294 | PAPALOTE | 5 | 25 | 0.000319 | south | 0.0037053 | -1.8967e-05 | -0.051644 | 0.0011502 | 1.8967e-05 | south | N | 1.8967e-05 | 0
80294 | PAPALOTE | 6 | 25 | 0.000319 | south | 0.0037053 | -1.8967e-05 | -0.051644 | 0.0011502 | 1.8967e-05 | south | N | 1.8967e-05 | 0
80294 | PAPALOTE | 7 | 25 | 0.000319 | south | 0.0037053 | -1.8967e-05 | -0.051644 | 0.0011502 | 1.8967e-05 | south | N | 1.8967e-05 | 0
80294 | PAPALOTE | 8 | 15 | 0.000319 | south | 0.0037053 | -1.8967e-05 | -0.051644 | 0.0011502 | 1.8967e-05 | south | N | 1.8967e-05 | 0
86104 | CID-138 | EQ | 0 | 0.001404 | south | 0.0047903 | 0.001066 | -0.050559 | 0.0022352 | 0.001066 | south | N | 0.001066 | 0
86105 | CID-230 | EQ | 500 | 0.001404 | south | 0.0047903 | 0.001066 | -0.050559 | 0.0022352 | 0.001066 | south | N | 0.001066 | 0
86106 | CUF-230 | EQ | 500 | 0.001404 | south | 0.0047903 | 0.001066 | -0.050559 | 0.0022352 | 0.001066 | south | N | 0.001066 | 0
86107 | CUF-138 | EQ | 0 | 0.001404 | south | 0.0047903 | 0.001066 | -0.050559 | 0.0022352 | 0.001066 | south | N | 0.001066 | 0
88198 | BEEVILLE | F | 0 | 0.000512 | south | 0.0038983 | 0.00017403 | -0.051451 | 0.0013432 | 0.00017403 | south | N | 0.00017403 | 0
88253 | HAMILTON | F | 0 | 0.011717 | south | 0.015103 | 0.011379 | -0.040246 | 0.012548 | 0.011379 | south | N | 0.011379 | 0
88299 | ZAPATA | F | 0 | 0.00107 | south | 0.0044563 | 0.00073203 | -0.050893 | 0.0019012 | 0.00073203 | south | N | 0.00073203 | 0
88508 | FALFURRI | F | 0 | 0.000538 | south | 0.0039243 | 0.00020003 | -0.051425 | 0.0013692 | 0.00020003 | south | N | 0.00020003 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:1427 FISHERRD - 1448 WCHTFLLS C:1422 BOWMAN_5 - 1425 FISHRDSS | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.25388 | west | 4 | Y | N | Ywest | Nwest | 1 | 164.9426 | 649.7 | 0.2171 | 141.0507 | 649.7 | 141.0507
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.074307 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4584 | 60 | 0.037533 | 2.252
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.011717 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.38666 | 0 | 0.015103 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.011717 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.29292 | 0 | 0.015103 | 0 |  |  | Weighted Shift Factors
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.011717 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.015103 | 0 |  |  | North | -0.0033863
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.050233 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.535 | 150 | 0.013459 | 2.0189 |  |  | West | 0.036774
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.048933 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.872 | 120 | 0.012159 | 1.4591 |  |  |  | -0.04016
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.048933 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.4014 | 233 | 0.012159 | 2.8331
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.048933 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3284 | 170.2 | 0.012159 | 2.0695 |  |  | Line Rating | 260
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.008626 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.051756 | 0 | 0.012012 | 0 |  |  | Conc Gen | 649.7
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.814 | 37.5 | 0.0116 | 0.43501 |  |  | Weighted Imp. | 141.0507
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.2002 | 107.5 | 0.0116 | 1.247 |  |  | PTDF | 0.2171
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5305 | 135 | 0.0116 | 1.566
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.7565 | 119 | 0.0116 | 1.3804 |  |  | Concentration | -5.4059
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.0793 | 105 | 0.0116 | 1.218
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8941 | 80.5 | 0.0116 | 0.93382
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.007907 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011293 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.046069 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8087 | 169.5 | 0.0092953 | 1.5756
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.045271 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7907 | 150 | 0.0084973 | 1.2746
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.045271 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5724 | 101 | 0.0084973 | 0.85823
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.044229 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7152 | 84 | 0.0074553 | 0.62625
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.04286 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2431 | 99 | 0.0060863 | 0.60254
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.04286 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6145 | 61 | 0.0060863 | 0.37126
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.04286 | west | 7 | N | N | Nwest | Nwest | 1 | 1.0715 | 0 | 0.0060863 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.04286 | west | 7 | N | N | Nwest | Nwest | 1 | 1.9587 | 0 | 0.0060863 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.04286 | west | 7 | N | N | Nwest | Nwest | 1 | 1.9587 | 0 | 0.0060863 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.042784 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0325 | 141 | 0.0060103 | 0.84745
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.042784 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1341 | 120 | 0.0060103 | 0.72124
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.002398 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.032853 | 0 | 0.0057843 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.042268 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6629 | 63 | 0.0054943 | 0.34614
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.001991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.047784 | 24 | 0.0053773 | 0.12906
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.001991 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.047784 | 24 | 0.0053773 | 0.12906
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.001991 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.045793 | 23 | 0.0053773 | 0.12368
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.001926 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.034668 | 0 | 0.0053123 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.001926 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.034668 | 0 | 0.0053123 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.001926 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.02889 | 0 | 0.0053123 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001859 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.7845 | 422 | 0.0052453 | 2.2135
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.001756 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.049168 | 0 | 0.0051423 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.001756 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.050924 | 0 | 0.0051423 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.041689 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.504 | 180 | 0.0049153 | 0.88476
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.041689 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.504 | 180 | 0.0049153 | 0.88476
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.001453 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.026154 | 0 | 0.0048393 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.001453 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.026154 | 0 | 0.0048393 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.041608 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3618 | 225 | 0.0048343 | 1.0877
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.001405 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0047913 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.001404 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1404 | 100 | 0.0047903 | 0.47903
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.001404 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1404 | 100 | 0.0047903 | 0.47903
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.001404 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0047903 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.001404 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0047903 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.001404 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0047903 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.001404 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0047903 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.00107 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0044563 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.041046 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9255 | 120 | 0.0042723 | 0.51268
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.000778 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.009336 | 0 | 0.0041643 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.000778 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.008558 | 0 | 0.0041643 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000778 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.009336 | 0 | 0.0041643 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.040893 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9072 | 120 | 0.0041193 | 0.49432
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.081396 | 114 | 0.0041003 | 0.46744
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15851 | 222 | 0.0041003 | 0.91028
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13138 | 184 | 0.0041003 | 0.75446
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15994 | 224 | 0.0041003 | 0.91848
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08211 | 115 | 0.0041003 | 0.47154
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.000653 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.037874 | 58 | 0.0040393 | 0.23428
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.000653 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.058117 | 89 | 0.0040393 | 0.3595
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.000653 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.028732 | 44 | 0.0040393 | 0.17773
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.000653 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.028732 | 44 | 0.0040393 | 0.17773
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.000653 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.028079 | 43 | 0.0040393 | 0.17369
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.000653 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.029385 | 45 | 0.0040393 | 0.18177
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6892 | 66 | 0.0039713 | 0.26211
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.8114 | 69 | 0.0039713 | 0.27402
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.8114 | 69 | 0.0039713 | 0.27402
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.7299 | 67 | 0.0039713 | 0.26608
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.7299 | 67 | 0.0039713 | 0.26608
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6484 | 65 | 0.0039713 | 0.25814
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.000584 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.23769 | 407 | 0.0039703 | 1.6159
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.000565 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.22374 | 396 | 0.0039513 | 1.5647
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.00056 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.11704 | 209 | 0.0039463 | 0.82478
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.00056 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.12096 | 216 | 0.0039463 | 0.85241
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.00056 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.02576 | 46 | 0.0039463 | 0.18153
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.00056 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.02632 | 47 | 0.0039463 | 0.18548
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.00056 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.02576 | 46 | 0.0039463 | 0.18153
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.00056 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.02576 | 46 | 0.0039463 | 0.18153
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.000559 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.23031 | 412 | 0.0039453 | 1.6255
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.000559 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.2236 | 400 | 0.0039453 | 1.5781
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.000547 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.23193 | 424 | 0.0039333 | 1.6677
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.000547 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.23247 | 425 | 0.0039333 | 1.6717
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.000538 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0039243 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.000533 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018655 | 0 | 0.0039193 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.000533 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018122 | 0 | 0.0039193 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.000533 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018655 | 0 | 0.0039193 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.000512 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0038983 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.000496 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0038823 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.000496 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0038823 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.000496 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0038823 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.040649 | west | 8 | N | N | Nwest | Nwest | 1 | 1.0487 | 0 | 0.0038753 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.000481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.074555 | 155 | 0.0038673 | 0.59944
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.000481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.08177 | 170 | 0.0038673 | 0.65745
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.000481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.074555 | 155 | 0.0038673 | 0.59944
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.000474 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.069441 | 146.5 | 0.0038603 | 0.56554
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.000474 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.070105 | 147.9 | 0.0038603 | 0.57094
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.000474 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.082002 | 173 | 0.0038603 | 0.66784
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.000457 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.24952 | 546 | 0.0038433 | 2.0985
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.000457 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.34275 | 750 | 0.0038433 | 2.8825
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.060912 | 144 | 0.0038093 | 0.54854
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.060912 | 144 | 0.0038093 | 0.54854
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.072333 | 171 | 0.0038093 | 0.6514
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.087561 | 207 | 0.0038093 | 0.78853
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.091664 | 216.7 | 0.0038093 | 0.82548
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10237 | 242 | 0.0038093 | 0.92186
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.000393 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0037793 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.000393 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.014934 | 38 | 0.0037793 | 0.14361
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.000393 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.0075849 | 19.3 | 0.0037793 | 0.072941
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.000393 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.005895 | 15 | 0.0037793 | 0.05669
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.000393 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.018471 | 47 | 0.0037793 | 0.17763
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.035814 | 94 | 0.0037673 | 0.35413
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.015621 | 41 | 0.0037673 | 0.15446
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.014478 | 38 | 0.0037673 | 0.14316
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007239 | 19 | 0.0037673 | 0.071579
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.035814 | 94 | 0.0037673 | 0.35413
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.013716 | 36 | 0.0037673 | 0.13562
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.016383 | 43 | 0.0037673 | 0.162
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.008382 | 22 | 0.0037673 | 0.082881
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.056388 | 148 | 0.0037673 | 0.55757
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01905 | 50 | 0.0037673 | 0.18837
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.020955 | 55 | 0.0037673 | 0.2072
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01905 | 50 | 0.0037673 | 0.18837
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.000373 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001492 | 0 | 0.0037593 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.000368 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002208 | 0 | 0.0037543 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.000366 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.010614 | 0 | 0.0037523 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.00035 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0133 | 0 | 0.0037363 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.000347 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.013186 | 0 | 0.0037333 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.051009 | 147 | 0.0037333 | 0.5488
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.047886 | 138 | 0.0037333 | 0.5152
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.04858 | 140 | 0.0037333 | 0.52267
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.051009 | 147 | 0.0037333 | 0.5488
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.063154 | 182 | 0.0037333 | 0.67947
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.068706 | 198 | 0.0037333 | 0.7392
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.000346 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00865 | 0 | 0.0037323 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.000346 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00865 | 0 | 0.0037323 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.000343 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.11456 | 334 | 0.0037293 | 1.2456
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.000343 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.11662 | 340 | 0.0037293 | 1.268
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.000343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.06174 | 180 | 0.0037293 | 0.67128
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.000343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.06174 | 180 | 0.0037293 | 0.67128
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.000338 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.06084 | 180 | 0.0037243 | 0.67038
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.000337 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.11323 | 336 | 0.0037233 | 1.251
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.000337 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.06066 | 180 | 0.0037233 | 0.6702
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.000337 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.049977 | 0 | 0.0037233 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.000337 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.050078 | 0 | 0.0037233 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.000337 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.051561 | 0 | 0.0037233 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.000336 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.21134 | 629 | 0.0037223 | 2.3414
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007975 | 25 | 0.0037053 | 0.092633
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007975 | 25 | 0.0037053 | 0.092633
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007975 | 25 | 0.0037053 | 0.092633
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.005104 | 16 | 0.0037053 | 0.059285
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007975 | 25 | 0.0037053 | 0.092633
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007975 | 25 | 0.0037053 | 0.092633
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007975 | 25 | 0.0037053 | 0.092633
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.004785 | 15 | 0.0037053 | 0.05558
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.000309 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0007416 | 0 | 0.0036953 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.000309 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0007416 | 0 | 0.0036953 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.000309 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0008652 | 0 | 0.0036953 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.000308 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.043736 | 142 | 0.0036943 | 0.5246
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.000308 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.04466 | 145 | 0.0036943 | 0.53568
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.000308 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.046508 | 151 | 0.0036943 | 0.55785
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.000308 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.08932 | 290 | 0.0036943 | 1.0714
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.048506 | 0 | 0.0036933 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.046971 | 0 | 0.0036933 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.0307 | 0 | 0.0036933 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.044515 | 0 | 0.0036933 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.045129 | 0 | 0.0036933 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.038989 | 0 | 0.0036933 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.000307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.003684 | 0 | 0.0036933 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.00027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.060453 | 223.9 | 0.0036563 | 0.81865
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.00027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.06075 | 225 | 0.0036563 | 0.82268
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.00027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.060642 | 224.6 | 0.0036563 | 0.82121
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.00027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.061209 | 226.7 | 0.0036563 | 0.82889
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.000244 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.005368 | 22 | 0.0036303 | 0.079867
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.000244 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.002684 | 11 | 0.0036303 | 0.039934
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.000244 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.002684 | 11 | 0.0036303 | 0.039934
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.000242 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0005808 | 0 | 0.0036283 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.000242 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0005808 | 0 | 0.0036283 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000238 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002856 | 0 | 0.0036243 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.000216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.010303 | 47.7 | 0.0036023 | 0.17183
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.000216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0080568 | 37.3 | 0.0036023 | 0.13437
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.000216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.009936 | 46 | 0.0036023 | 0.16571
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.000216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.010368 | 48 | 0.0036023 | 0.17291
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.000204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.029376 | 144 | 0.0035903 | 0.51701
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.000204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.038352 | 188 | 0.0035903 | 0.67498
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.000188 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.013724 | 0 | 0.0035743 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.000167 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.002505 | 0 | 0.0035533 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.000167 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.003841 | 0 | 0.0035533 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.000163 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.001304 | 0 | 0.0035493 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.004256 | 0 | 0.0035383 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.001064 | 0 | 0.0035383 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.005928 | 0 | 0.0035383 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00228 | 0 | 0.0035383 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.001064 | 0 | 0.0035383 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00228 | 0 | 0.0035383 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.005928 | 0 | 0.0035383 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.005928 | 0 | 0.0035383 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.00012 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00096 | 0 | 0.0035063 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.00012 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00096 | 0 | 0.0035063 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 9.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.004608 | 0 | 0.0034823 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00441 | 49 | 0.0034763 | 0.17034
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00414 | 46 | 0.0034763 | 0.15991
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00414 | 46 | 0.0034763 | 0.15991
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00423 | 47 | 0.0034763 | 0.16339
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 9e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.01386 | 154 | 0.0034763 | 0.53536
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 9e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.01332 | 148 | 0.0034763 | 0.5145
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00432 | 48 | 0.0034763 | 0.16686
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00432 | 48 | 0.0034763 | 0.16686
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.040244 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.26561 | 6.6 | 0.0034703 | 0.022904
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.040244 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3804 | 34.3 | 0.0034703 | 0.11903
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.006399 | 0 | 0.0034673 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.006561 | 0 | 0.0034673 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.006399 | 0 | 0.0034673 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00648 | 0 | 0.0034673 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0063504 | 0 | 0.0034673 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.002025 | 0 | 0.0034673 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.003726 | 0 | 0.0034673 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.002268 | 0 | 0.0034673 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0035316 | 0 | 0.0034673 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.005994 | 0 | 0.0034673 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 8.1e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.02511 | 310 | 0.0034673 | 1.0749
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 8.1e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.033453 | 413 | 0.0034673 | 1.432
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 4.8e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.002016 | 42 | 0.0034343 | 0.14424
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 4.8e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.002112 | 44 | 0.0034343 | 0.15111
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 4.8e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.002112 | 44 | 0.0034343 | 0.15111
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 4.8e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.002256 | 47 | 0.0034343 | 0.16141
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.040189 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6085 | 214.2 | 0.0034153 | 0.73156
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0033863 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0033863 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0033863 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0033863 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0033863 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0033863 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0033863 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0033863 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -3.2e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.004224 | 132 | 0.0033543 | 0.44277
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -3.2e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.004288 | 134 | 0.0033543 | 0.44948
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -3.2e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.010336 | 323 | 0.0033543 | 1.0835
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -3.7e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0056425 | 152.5 | 0.0033493 | 0.51077
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -3.7e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0055315 | 149.5 | 0.0033493 | 0.50073
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -3.7e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0086062 | 232.6 | 0.0033493 | 0.77906
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.040098 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3257 | 58 | 0.0033243 | 0.19281
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00445 | 50 | 0.0032973 | 0.16487
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00445 | 50 | 0.0032973 | 0.16487
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00445 | 50 | 0.0032973 | 0.16487
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00445 | 50 | 0.0032973 | 0.16487
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.040051 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0251 | 100.5 | 0.0032773 | 0.32937
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.000114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.018012 | 158 | 0.0032723 | 0.51703
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.000114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01824 | 160 | 0.0032723 | 0.52357
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.000114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01995 | 175 | 0.0032723 | 0.57266
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.000123 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.053259 | 433 | 0.0032633 | 1.413
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.000124 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.072416 | 584 | 0.0032623 | 1.9052
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.000124 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.07378 | 595 | 0.0032623 | 1.9411
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.000434 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.57852 | 0 | 0.0029523 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.000434 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.57635 | 0 | 0.0029523 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.034808 | 76 | 0.0029283 | 0.22255
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.034808 | 76 | 0.0029283 | 0.22255
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.04809 | 105 | 0.0029283 | 0.30748
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.033892 | 74 | 0.0029283 | 0.2167
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.033892 | 74 | 0.0029283 | 0.2167
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.046716 | 102 | 0.0029283 | 0.29869
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.000471 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.268 | 569 | 0.0029153 | 1.6588
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.000471 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.27365 | 581 | 0.0029153 | 1.6938
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.000478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.031548 | 66 | 0.0029083 | 0.19195
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.039632 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9052 | 149 | 0.0028583 | 0.42589
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.03963 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9445 | 150 | 0.0028563 | 0.42845
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.03963 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7186 | 220 | 0.0028563 | 0.62839
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.03963 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.926 | 200 | 0.0028563 | 0.57126
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.03963 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8309 | 121.9 | 0.0028563 | 0.34818
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.039624 | west | 8 | N | N | Nwest | Nwest | 1 | 2.7737 | 0 | 0.0028503 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.039624 | west | 8 | N | N | Nwest | Nwest | 1 | 2.9084 | 0 | 0.0028503 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.039624 | west | 8 | N | N | Nwest | Nwest | 1 | 2.7895 | 0 | 0.0028503 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.037758 | 0 | 0.0027773 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.043483 | 0 | 0.0027773 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.027405 | 0 | 0.0027773 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.061509 | 0 | 0.0027773 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.052374 | 0 | 0.0027773 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.053592 | 0 | 0.0027773 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03045 | 0 | 0.0027773 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.010962 | 0 | 0.0027773 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057246 | 0 | 0.0027773 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04263 | 0 | 0.0027773 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.038367 | 0 | 0.0027773 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.043848 | 0 | 0.0027773 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.039463 | 0 | 0.0027773 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.061509 | 0 | 0.0027773 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.059073 | 0 | 0.0027773 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.062727 | 0 | 0.0027773 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.046284 | 0 | 0.0027773 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04872 | 0 | 0.0027773 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04872 | 0 | 0.0027773 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10414 | 0 | 0.0027773 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.00064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04544 | 0 | 0.0027463 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.00064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0064 | 0 | 0.0027463 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7651 | 70 | 0.0027273 | 0.19091
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7651 | 70 | 0.0027273 | 0.19091
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.6657 | 92.8 | 0.0027273 | 0.25309
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.1601 | 80 | 0.0027273 | 0.21818
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.1601 | 80 | 0.0027273 | 0.21818
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.5426 | 115 | 0.0027273 | 0.31364
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.2239 | 208.2 | 0.0027263 | 0.56762
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.6129 | 142.1 | 0.0027263 | 0.38741
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.2298 | 132.4 | 0.0027263 | 0.36096
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.372 | 136 | 0.0027263 | 0.37078
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.8065 | 147 | 0.0027263 | 0.40077
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.295 | 210 | 0.0027263 | 0.57252
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.000667 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.074037 | 0 | 0.0027193 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.000667 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.074037 | 0 | 0.0027193 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.000667 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.079373 | 0 | 0.0027193 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.000667 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.073037 | 0 | 0.0027193 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.039435 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3802 | 35 | 0.0026613 | 0.093146
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.039435 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.183 | 30 | 0.0026613 | 0.079839
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.000752 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.034667 | 0 | 0.0026343 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.000761 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12404 | 0 | 0.0026253 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.000761 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12404 | 0 | 0.0026253 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.000761 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.18644 | 0 | 0.0026253 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.000761 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.49541 | 651 | 0.0026253 | 1.7091
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.000761 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.4292 | 564 | 0.0026253 | 1.4807
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.000761 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.4566 | 600 | 0.0026253 | 1.5752
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.000765 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.025245 | 0 | 0.0026213 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.000777 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.1251 | 161 | 0.0026093 | 0.4201
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.000777 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.12898 | 166 | 0.0026093 | 0.43315
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.000777 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.1927 | 248 | 0.0026093 | 0.64712
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.000777 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.42424 | 546 | 0.0026093 | 1.4247
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.000777 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -0.49961 | 0 | 0.0026093 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.000777 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.010101 | 13 | 0.0026093 | 0.033921
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.5974 | 66 | 0.0025803 | 0.1703
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.558 | 65 | 0.0025803 | 0.16772
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6367 | 67 | 0.0025803 | 0.17288
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6367 | 67 | 0.0025803 | 0.17288
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6367 | 67 | 0.0025803 | 0.17288
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.039354 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0025803 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.039354 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0025803 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057631 | 0 | 0.0025723 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.054294 | 0 | 0.0025723 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.043142 | 0 | 0.0025723 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1247 | 0 | 0.0025723 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12495 | 0 | 0.0025723 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12397 | 0 | 0.0025723 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.078144 | 0 | 0.0025723 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19862 | 0 | 0.0025723 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03256 | 0 | 0.0025723 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.026048 | 0 | 0.0025723 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02442 | 0 | 0.0025723 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.081644 | 0 | 0.0025723 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.075621 | 0 | 0.0025723 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.083598 | 0 | 0.0025723 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.083028 | 0 | 0.0025723 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.000835 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.04175 | 50 | 0.0025513 | 0.12757
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.000846 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0025403 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.078533 | 0 | 0.0025233 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.075599 | 0 | 0.0025233 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.075081 | 0 | 0.0025233 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.047033 | 0 | 0.0025233 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.010529 | 0 | 0.0025233 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.000869 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.056485 | 0 | 0.0025173 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.000869 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.05214 | 0 | 0.0025173 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.000869 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.056485 | 0 | 0.0025173 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.000869 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.056485 | 0 | 0.0025173 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.04048 | 46 | 0.0025063 | 0.11529
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.04048 | 46 | 0.0025063 | 0.11529
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.04048 | 46 | 0.0025063 | 0.11529
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.0484 | 55 | 0.0025063 | 0.13785
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.0484 | 55 | 0.0025063 | 0.13785
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.04752 | 54 | 0.0025063 | 0.13534
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.000881 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.068718 | 0 | 0.0025053 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.000881 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.07048 | 0 | 0.0025053 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14411 | 0 | 0.0025033 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.13872 | 0 | 0.0025033 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.13907 | 0 | 0.0025033 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.13863 | 0 | 0.0025033 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.23753 | 0 | 0.0025033 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.000887 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.031045 | 0 | 0.0024993 | 0
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.00089 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13261 | 0 | 0.0024963 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.00089 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057939 | 0 | 0.0024963 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.00089 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.14685 | 165 | 0.0024963 | 0.4119
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.00089 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.15041 | 169 | 0.0024963 | 0.42188
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.00089 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.01068 | 12 | 0.0024963 | 0.029956
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.00089 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0024963 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.000891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.16038 | 0 | 0.0024953 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.000891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14131 | 0 | 0.0024953 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.000891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.13989 | 0 | 0.0024953 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.000891 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.20315 | 228 | 0.0024953 | 0.56894
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057024 | 0 | 0.0024953 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.056311 | 0 | 0.0024953 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.073597 | 0 | 0.0024953 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.065578 | 0 | 0.0024953 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.014434 | 0 | 0.0024953 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.000891 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.18978 | 213 | 0.0024953 | 0.53151
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.000895 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.063545 | 0 | 0.0024913 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.000895 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.06444 | 0 | 0.0024913 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.000895 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.034905 | 0 | 0.0024913 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.000895 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02685 | 0 | 0.0024913 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.000902 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.037884 | 42 | 0.0024843 | 0.10434
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.000902 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.037884 | 42 | 0.0024843 | 0.10434
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.000902 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.034276 | 38 | 0.0024843 | 0.094405
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.000902 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.034276 | 38 | 0.0024843 | 0.094405
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.000902 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12267 | 0 | 0.0024843 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.000904 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15639 | 0 | 0.0024823 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.000904 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12204 | 0 | 0.0024823 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.095264 | 104 | 0.0024703 | 0.25692
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.095264 | 104 | 0.0024703 | 0.25692
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.049464 | 54 | 0.0024703 | 0.1334
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.048548 | 53 | 0.0024703 | 0.13093
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.049464 | 54 | 0.0024703 | 0.1334
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.052212 | 57 | 0.0024703 | 0.14081
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.049464 | 54 | 0.0024703 | 0.1334
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.049464 | 54 | 0.0024703 | 0.1334
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.053128 | 58 | 0.0024703 | 0.14328
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.053128 | 58 | 0.0024703 | 0.14328
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.000918 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.67473 | 735 | 0.0024683 | 1.8142
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03128 | 0 | 0.0024663 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.031924 | 0 | 0.0024663 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.030084 | 0 | 0.0024663 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.042228 | 0 | 0.0024663 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.016284 | 0 | 0.0024663 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.018768 | 0 | 0.0024663 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.018308 | 0 | 0.0024663 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0322 | 0 | 0.0024663 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01656 | 0 | 0.0024663 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.078568 | 0 | 0.0024663 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13616 | 0 | 0.0024663 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.000925 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.0111 | 12 | 0.0024613 | 0.029536
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.000928 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.6895 | 743 | 0.0024583 | 1.8265
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.000928 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.011136 | 12 | 0.0024583 | 0.0295
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.06032 | 0 | 0.0024583 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.061248 | 0 | 0.0024583 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.06496 | 0 | 0.0024583 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.058464 | 0 | 0.0024583 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057536 | 0 | 0.0024583 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.096512 | 0 | 0.0024583 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.054752 | 0 | 0.0024583 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.00464 | 0 | 0.0024583 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.019488 | 0 | 0.0024583 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.000931 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16013 | 172 | 0.0024553 | 0.42232
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.000931 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16013 | 172 | 0.0024553 | 0.42232
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.000931 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16013 | 172 | 0.0024553 | 0.42232
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.000931 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14617 | 0 | 0.0024553 | 0
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.000939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15287 | 0 | 0.0024473 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.000939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15155 | 0 | 0.0024473 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.000939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14921 | 0 | 0.0024473 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.000939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25278 | 0 | 0.0024473 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.000942 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.37492 | 398 | 0.0024443 | 0.97285
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.053032 | 56 | 0.0024393 | 0.1366
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.055873 | 59 | 0.0024393 | 0.14392
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.053032 | 56 | 0.0024393 | 0.1366
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.053032 | 56 | 0.0024393 | 0.1366
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.055873 | 59 | 0.0024393 | 0.14392
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.053032 | 56 | 0.0024393 | 0.1366
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.000991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.17144 | 0 | 0.0023953 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.000991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1546 | 0 | 0.0023953 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.000991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.15261 | 0 | 0.0023953 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.000991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.15261 | 0 | 0.0023953 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.000991 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16054 | 0 | 0.0023953 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.039029 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8544 | 150 | 0.0022553 | 0.3383
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.039028 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8785 | 125 | 0.0022543 | 0.28179
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.039028 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8785 | 125 | 0.0022543 | 0.28179
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.038905 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3768 | 112.5 | 0.0021313 | 0.23977
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.038905 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8163 | 149.5 | 0.0021313 | 0.31863
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.038905 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2363 | 186 | 0.0021313 | 0.39642
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.038905 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3451 | 214.5 | 0.0021313 | 0.45717
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.038222 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.18347 | 0 | 0.0014483 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037749 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0199 | 80 | 0.00097531 | 0.078025
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037749 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0199 | 80 | 0.00097531 | 0.078025
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.037626 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.822 | 75 | 0.00085231 | 0.063923
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037626 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0101 | 80 | 0.00085231 | 0.068185
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.037626 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.505 | 40 | 0.00085231 | 0.034092
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.0376 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.008 | 80 | 0.00082631 | 0.066105
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.037597 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0078 | 80 | 0.00082331 | 0.065865
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.03758 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.637 | 150 | 0.00080631 | 0.12095
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.03758 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.637 | 150 | 0.00080631 | 0.12095
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.036962 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.957 | 80 | 0.00018831 | 0.015065
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.036842 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.8184 | 76.5 | 6.8309e-05 | 0.0052256
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.036753 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0873 | 84 | -2.0691e-05 | -0.001738
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.034797 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2726 | 209 | -0.0019767 | -0.41313
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.034797 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4018 | 126.5 | -0.0019767 | -0.25005
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.034797 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6645 | 249 | -0.0019767 | -0.4922
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.034797 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.855 | 197 | -0.0019767 | -0.38941
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.034332 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.7328 | 400 | -0.0024417 | -0.97668
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.034234 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0792 | 236 | -0.0025397 | -0.59937
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.033436 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.0033377 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.030657 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5986 | 150 | -0.0061167 | -0.9175
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.026556 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3817 | 165 | -0.010218 | -1.6859
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.012817 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.023957 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.00224 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.81984 | 366 | -0.034534 | -12.6393
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.001229 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.07374 | 60 | -0.035545 | -2.1327
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0714 | 100 | -0.03606 | -3.606
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.036774 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.036774 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.000231 | north | 3 | N | N | Nnorth | Nnorth | 1 | -0.26727 | 0 | -0.037005 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.000231 | north | 3 | N | N | Nnorth | Nnorth | 1 | -0.2675 | 0 | -0.037005 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.000497 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.108 | 217.3 | -0.037271 | -8.0989
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.000497 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.10189 | 205 | -0.037271 | -7.6405
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.000497 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13538 | 272.4 | -0.037271 | -10.1525
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.001209 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.037983 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.001326 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0381 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.001326 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0381 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.001369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.20535 | 150 | -0.038143 | -5.7214
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.001369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.10952 | 80 | -0.038143 | -3.0514
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.001384 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.35292 | 255 | -0.038158 | -9.7302
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.001384 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.20622 | 149 | -0.038158 | -5.6855
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.001384 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.21175 | 153 | -0.038158 | -5.8381
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.001396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.21526 | 0 | -0.03817 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.001396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.21778 | 0 | -0.03817 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.001396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.21778 | 0 | -0.03817 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.001396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.53048 | 0 | -0.03817 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.001403 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038177 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.001403 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.1042 | 787 | -0.038177 | -30.0451
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.001472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.070656 | 48 | -0.038246 | -1.8358
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.001472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.067712 | 46 | -0.038246 | -1.7593
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.001472 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.15456 | 105 | -0.038246 | -4.0158
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.001477 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.047264 | 0 | -0.038251 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.001479 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.001479 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.001479 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.025143 | 17 | -0.038253 | -0.6503
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.001479 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.001479 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.00148 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.68524 | 463 | -0.038254 | -17.7115
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.001727 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.025905 | 0 | -0.038501 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.001727 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.025905 | 0 | -0.038501 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.001756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.5014 | 855 | -0.03853 | -32.9429
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.001756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.5014 | 855 | -0.03853 | -32.9429
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.001756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.26744 | 152.3 | -0.03853 | -5.8681
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.001756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.26867 | 153 | -0.03853 | -5.895
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.001867 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.544 | 827 | -0.038641 | -31.9559
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.001867 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.5291 | 819 | -0.038641 | -31.6467
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.001896 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.13272 | 70 | -0.03867 | -2.7069
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.001896 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.13082 | 69 | -0.03867 | -2.6682
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.001896 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.13082 | 69 | -0.03867 | -2.6682
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.001896 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.12893 | 68 | -0.03867 | -2.6295
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.00194 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.32592 | 168 | -0.038714 | -6.5039
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.00194 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.1746 | 90 | -0.038714 | -3.4842
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.002027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.45405 | 224 | -0.038801 | -8.6914
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.002027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.4581 | 226 | -0.038801 | -8.769
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.002027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.42972 | 212 | -0.038801 | -8.2257
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.002027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.4277 | 211 | -0.038801 | -8.1869
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.002152 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.3235 | 615 | -0.038926 | -23.9393
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.002152 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.2632 | 587 | -0.038926 | -22.8494
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.00222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.33455 | 150.7 | -0.038994 | -5.8763
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.00222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.33522 | 151 | -0.038994 | -5.888
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.00222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.39383 | 177.4 | -0.038994 | -6.9175
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.002244 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.33997 | 151.5 | -0.039018 | -5.9112
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.002244 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.34176 | 152.3 | -0.039018 | -5.9424
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.002244 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.39831 | 177.5 | -0.039018 | -6.9256
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.002273 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.49188 | 216.4 | -0.039047 | -8.4497
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.002273 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.4912 | 216.1 | -0.039047 | -8.438
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.002453 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.48079 | 196 | -0.039227 | -7.6884
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.002453 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.27228 | 111 | -0.039227 | -4.3542
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.002497 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.55933 | 224 | -0.039271 | -8.7966
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.002646 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.1323 | 50 | -0.03942 | -1.971
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.002646 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.48157 | 182 | -0.03942 | -7.1744
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.002646 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.2807 | 484 | -0.03942 | -19.0791
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.002651 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.039425 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.002692 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.39842 | 0 | -0.039466 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.002692 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.34996 | 0 | -0.039466 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.002692 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.39034 | 0 | -0.039466 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.002692 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.0741 | 0 | -0.039466 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.002742 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.1525 | 785 | -0.039516 | -31.0198
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.002742 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.1799 | 795 | -0.039516 | -31.415
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.002742 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.1388 | 780 | -0.039516 | -30.8222
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.002753 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.0874 | 395 | -0.039527 | -15.613
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.002753 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.1976 | 435 | -0.039527 | -17.1941
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.002821 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.2271 | 435 | -0.039595 | -17.2237
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.002824 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.33323 | 118 | -0.039598 | -4.6725
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.002824 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.32476 | 115 | -0.039598 | -4.5537
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.002824 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.5701 | 556 | -0.039598 | -22.0163
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.003035 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.039809 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.003035 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.039809 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.003107 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.2055 | 388 | -0.039881 | -15.4737
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.003107 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.6001 | 515 | -0.039881 | -20.5386
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.50071 | 161 | -0.039884 | -6.4213
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.51004 | 164 | -0.039884 | -6.5409
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.51004 | 164 | -0.039884 | -6.5409
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.2875 | 414 | -0.039884 | -16.5118
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.50382 | 162 | -0.039884 | -6.4612
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.50071 | 161 | -0.039884 | -6.4213
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.50693 | 163 | -0.039884 | -6.501
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.272 | 409 | -0.039884 | -16.3124
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.00327 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.1308 | 40 | -0.040044 | -1.6017
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.00328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.0656 | 20 | -0.040054 | -0.80107
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.00328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.082 | 25 | -0.040054 | -1.0013
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.00328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.13448 | 41 | -0.040054 | -1.6422
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.003304 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.26102 | 79 | -0.040078 | -3.1661
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.003304 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.35022 | 106 | -0.040078 | -4.2482
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.003304 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.48238 | 146 | -0.040078 | -5.8513
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.003304 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.2511 | 76 | -0.040078 | -3.0459
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.003486 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9452 | 558 | -0.04026 | -22.4649
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.003486 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.0184 | 579 | -0.04026 | -23.3104
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.003486 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.8167 | 808 | -0.04026 | -32.5298
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.003555 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.040329 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.58176 | 160 | -0.04041 | -6.4656
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.56722 | 156 | -0.04041 | -6.3039
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.71266 | 196 | -0.04041 | -7.9203
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.56722 | 156 | -0.04041 | -6.3039
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.57085 | 157 | -0.04041 | -6.3443
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.71993 | 198 | -0.04041 | -8.0011
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.003667 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.27503 | 0 | -0.040441 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.003667 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.29189 | 0 | -0.040441 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.003667 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.32416 | 0 | -0.040441 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.003687 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.3642 | 370 | -0.040461 | -14.9705
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.51618 | 0 | -0.040461 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.51987 | 0 | -0.040461 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.1393 | 0 | -0.040461 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.52724 | 0 | -0.040461 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.53093 | 0 | -0.040461 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.143 | 0 | -0.040461 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.004004 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.040778 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.004172 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.70924 | 170 | -0.040946 | -6.9608
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.004172 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.1694 | 520 | -0.040946 | -21.2918
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.004494 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.17976 | 0 | -0.041268 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.004494 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.17976 | 0 | -0.041268 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.004829 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.041603 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.004829 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.041603 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.004829 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.041603 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.004897 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.99899 | 204 | -0.041671 | -8.5008
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.004897 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.9843 | 201 | -0.041671 | -8.3758
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.004897 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.1851 | 242 | -0.041671 | -10.0843
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.006106 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.36636 | 60 | -0.04288 | -2.5728
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.006106 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.38468 | 63 | -0.04288 | -2.7014
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.007205 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.52597 | 73 | -0.043979 | -3.2104
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.007205 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.8574 | 119 | -0.043979 | -5.2335
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.007205 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.477 | 205 | -0.043979 | -9.0156
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.007205 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.73491 | 102 | -0.043979 | -4.4858
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.007205 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.69168 | 96 | -0.043979 | -4.222
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.011303 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.20345 | 18 | -0.048077 | -0.86538
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.011303 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.20345 | 18 | -0.048077 | -0.86538
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.011303 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.42951 | 38 | -0.048077 | -1.8269
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.015829 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.8995 | 120 | -0.052603 | -6.3123
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.019748 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.779 | 242 | -0.056522 | -13.6782
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.022113 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3685 | 288 | -0.058887 | -16.9594
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.022113 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2506 | 147 | -0.058887 | -8.6563
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.022113 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2506 | 147 | -0.058887 | -8.6563
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.023305 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27966 | 0 | -0.060079 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.023305 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27966 | 0 | -0.060079 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.025921 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.9161 | 112.5 | -0.062695 | -7.0532
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.047669 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.95338 | 20 | -0.084443 | -1.6889
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.047669 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.95338 | 20 | -0.084443 | -1.6889
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.047669 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.95338 | 20 | -0.084443 | -1.6889
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.047669 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.81037 | 17 | -0.084443 | -1.4355

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:1427 FISHERRD - 1448 WCHTFLLS C:1422 BOWMAN_5 - 1425 FISHRDSS | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.047669 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.95338 | 20 | -0.084443 | -1.6889 | 20 | 1.6889
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.047669 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.95338 | 20 | -0.084443 | -1.6889 | 40 | 3.3777
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.047669 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.95338 | 20 | -0.084443 | -1.6889 | 60 | 5.0666
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.047669 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.81037 | 17 | -0.084443 | -1.4355 | 77 | 6.5021 | Weighted Shift Factors
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.025921 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.9161 | 0 | -0.062695 | 0 | 77 | 6.5021 | North | -0.0033863
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.023305 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27966 | 0 | -0.060079 | 0 | 77 | 6.5021 | West | 0.036774
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.023305 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.27966 | 0 | -0.060079 | 0 | 77 | 6.5021 |  | -0.04016
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.022113 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3685 | 288 | -0.058887 | -16.9594 | 365 | 23.4615
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.022113 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2506 | 147 | -0.058887 | -8.6563 | 512 | 32.1178 | Line Rating | 260
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.022113 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2506 | 147 | -0.058887 | -8.6563 |  |  | Conc Gen | 512
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.019748 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.779 | 242 | -0.056522 | -13.6782 |  |  | Weighted Imp. | 32.1178
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.015829 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.8995 | 0 | -0.052603 | 0 |  |  | PTDF | 0.06273
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.011303 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.20345 | 18 | -0.048077 | -0.86538
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.011303 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.20345 | 18 | -0.048077 | -0.86538 |  |  | Concentration | -1.562
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.011303 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.42951 | 38 | -0.048077 | -1.8269
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.007205 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.52597 | 73 | -0.043979 | -3.2104
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.007205 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.8574 | 119 | -0.043979 | -5.2335
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.007205 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.477 | 205 | -0.043979 | -9.0156
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.007205 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.73491 | 102 | -0.043979 | -4.4858
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.007205 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.69168 | 96 | -0.043979 | -4.222
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.006106 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.36636 | 60 | -0.04288 | -2.5728
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.006106 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.38468 | 63 | -0.04288 | -2.7014
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.004897 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.99899 | 204 | -0.041671 | -8.5008
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.004897 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.9843 | 201 | -0.041671 | -8.3758
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.004897 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.1851 | 242 | -0.041671 | -10.0843
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.004829 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.041603 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.004829 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.041603 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.004829 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.041603 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.004494 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.17976 | 0 | -0.041268 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.004494 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.17976 | 0 | -0.041268 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.004172 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.70924 | 170 | -0.040946 | -6.9608
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.004172 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.1694 | 520 | -0.040946 | -21.2918
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.004004 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.040778 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.003687 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.3642 | 370 | -0.040461 | -14.9705
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.51618 | 0 | -0.040461 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.51987 | 0 | -0.040461 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.1393 | 0 | -0.040461 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.52724 | 0 | -0.040461 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.53093 | 0 | -0.040461 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.003687 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.143 | 0 | -0.040461 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.003667 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.27503 | 0 | -0.040441 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.003667 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.29189 | 0 | -0.040441 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.003667 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.32416 | 0 | -0.040441 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.58176 | 160 | -0.04041 | -6.4656
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.56722 | 156 | -0.04041 | -6.3039
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.71266 | 196 | -0.04041 | -7.9203
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.56722 | 156 | -0.04041 | -6.3039
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.57085 | 157 | -0.04041 | -6.3443
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.003636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.71993 | 198 | -0.04041 | -8.0011
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.003555 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.040329 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.003486 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.9452 | 0 | -0.04026 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.003486 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.0184 | 0 | -0.04026 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.003486 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.8167 | 0 | -0.04026 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.003304 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.26102 | 79 | -0.040078 | -3.1661
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.003304 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.35022 | 106 | -0.040078 | -4.2482
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.003304 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.48238 | 146 | -0.040078 | -5.8513
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.003304 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.2511 | 76 | -0.040078 | -3.0459
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.00328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.0656 | 20 | -0.040054 | -0.80107
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.00328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.082 | 25 | -0.040054 | -1.0013
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.00328 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.13448 | 41 | -0.040054 | -1.6422
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.00327 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.1308 | 40 | -0.040044 | -1.6017
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.50071 | 161 | -0.039884 | -6.4213
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.51004 | 164 | -0.039884 | -6.5409
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.51004 | 164 | -0.039884 | -6.5409
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.2875 | 414 | -0.039884 | -16.5118
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.50382 | 162 | -0.039884 | -6.4612
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.50071 | 161 | -0.039884 | -6.4213
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.50693 | 163 | -0.039884 | -6.501
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.00311 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.272 | 409 | -0.039884 | -16.3124
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.003107 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.2055 | 388 | -0.039881 | -15.4737
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.003107 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.6001 | 515 | -0.039881 | -20.5386
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.003035 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.039809 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.003035 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.039809 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.002824 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.33323 | 118 | -0.039598 | -4.6725
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.002824 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.32476 | 115 | -0.039598 | -4.5537
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.002824 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.5701 | 556 | -0.039598 | -22.0163
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.002821 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.2271 | 435 | -0.039595 | -17.2237
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.002753 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.0874 | 395 | -0.039527 | -15.613
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.002753 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.1976 | 435 | -0.039527 | -17.1941
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.002742 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.1525 | 0 | -0.039516 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.002742 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.1799 | 0 | -0.039516 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.002742 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.1388 | 0 | -0.039516 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.002692 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.39842 | 0 | -0.039466 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.002692 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.34996 | 0 | -0.039466 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.002692 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.39034 | 0 | -0.039466 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.002692 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.0741 | 0 | -0.039466 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.002651 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.039425 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.002646 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.48157 | 182 | -0.03942 | -7.1744
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.002646 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.2807 | 484 | -0.03942 | -19.0791
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.002646 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.1323 | 0 | -0.03942 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.002497 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.55933 | 224 | -0.039271 | -8.7966
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.002453 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.48079 | 196 | -0.039227 | -7.6884
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.002453 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.27228 | 111 | -0.039227 | -4.3542
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.002273 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.49188 | 216.4 | -0.039047 | -8.4497
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.002273 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.4912 | 216.1 | -0.039047 | -8.438
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.002244 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.33997 | 151.5 | -0.039018 | -5.9112
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.002244 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.34176 | 152.3 | -0.039018 | -5.9424
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.002244 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.39831 | 177.5 | -0.039018 | -6.9256
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.00222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.33455 | 150.7 | -0.038994 | -5.8763
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.00222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.33522 | 151 | -0.038994 | -5.888
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.00222 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.39383 | 177.4 | -0.038994 | -6.9175
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.002152 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.3235 | 0 | -0.038926 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.002152 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.2632 | 0 | -0.038926 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.002027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.45405 | 224 | -0.038801 | -8.6914
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.002027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.4581 | 226 | -0.038801 | -8.769
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.002027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.42972 | 212 | -0.038801 | -8.2257
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.002027 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.4277 | 211 | -0.038801 | -8.1869
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.00194 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.32592 | 168 | -0.038714 | -6.5039
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.00194 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.1746 | 90 | -0.038714 | -3.4842
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.001896 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.13272 | 70 | -0.03867 | -2.7069
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.001896 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.13082 | 69 | -0.03867 | -2.6682
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.001896 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.13082 | 69 | -0.03867 | -2.6682
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.001896 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.12893 | 68 | -0.03867 | -2.6295
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.001867 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.544 | 0 | -0.038641 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.001867 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.5291 | 0 | -0.038641 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.001756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.5014 | 0 | -0.03853 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.001756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.5014 | 0 | -0.03853 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.001756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.26744 | 0 | -0.03853 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.001756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.26867 | 0 | -0.03853 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.001727 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.025905 | 0 | -0.038501 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.001727 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.025905 | 0 | -0.038501 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.00148 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.68524 | 0 | -0.038254 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.001479 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.001479 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.001479 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.025143 | 17 | -0.038253 | -0.6503
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.001479 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.001479 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038253 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.001477 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.047264 | 0 | -0.038251 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.001472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.070656 | 48 | -0.038246 | -1.8358
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.001472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.067712 | 46 | -0.038246 | -1.7593
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.001472 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.15456 | 105 | -0.038246 | -4.0158
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.001403 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.038177 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.001403 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.1042 | 787 | -0.038177 | -30.0451
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.001396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.21526 | 0 | -0.03817 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.001396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.21778 | 0 | -0.03817 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.001396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.21778 | 0 | -0.03817 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.001396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.53048 | 0 | -0.03817 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.001384 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.35292 | 255 | -0.038158 | -9.7302
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.001384 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.20622 | 149 | -0.038158 | -5.6855
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.001384 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.21175 | 153 | -0.038158 | -5.8381
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.001369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.20535 | 150 | -0.038143 | -5.7214
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.001369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.10952 | 80 | -0.038143 | -3.0514
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.001326 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0381 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.001326 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0381 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.001209 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.037983 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.000497 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.108 | 217.3 | -0.037271 | -8.0989
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.000497 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.10189 | 205 | -0.037271 | -7.6405
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.000497 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13538 | 272.4 | -0.037271 | -10.1525
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.000231 | north | 3 | N | N | Nnorth | Nnorth | 1 | -0.26727 | 0 | -0.037005 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.000231 | north | 3 | N | N | Nnorth | Nnorth | 1 | -0.2675 | 0 | -0.037005 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.036774 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.036774 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0714 | 0 | -0.03606 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.001229 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.07374 | 0 | -0.035545 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.00224 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.81984 | 366 | -0.034534 | -12.6393
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.012817 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.023957 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.026556 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3817 | 0 | -0.010218 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.030657 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5986 | 0 | -0.0061167 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.033436 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.0033377 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.034234 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0792 | 0 | -0.0025397 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.034332 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.7328 | 0 | -0.0024417 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.034797 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2726 | 0 | -0.0019767 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.034797 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4018 | 0 | -0.0019767 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.034797 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6645 | 0 | -0.0019767 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.034797 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.855 | 0 | -0.0019767 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.036753 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0873 | 0 | -2.0691e-05 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.036842 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.8184 | 0 | 6.8309e-05 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.036962 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.957 | 0 | 0.00018831 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.03758 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.637 | 0 | 0.00080631 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.03758 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.637 | 0 | 0.00080631 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.037597 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0078 | 0 | 0.00082331 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.0376 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.008 | 0 | 0.00082631 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.037626 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.822 | 0 | 0.00085231 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037626 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0101 | 0 | 0.00085231 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.037626 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.505 | 0 | 0.00085231 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037749 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0199 | 0 | 0.00097531 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.037749 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0199 | 0 | 0.00097531 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.038222 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.18347 | 0 | 0.0014483 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.038905 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3768 | 0 | 0.0021313 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.038905 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8163 | 0 | 0.0021313 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.038905 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2363 | 0 | 0.0021313 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.038905 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3451 | 0 | 0.0021313 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.039028 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8785 | 0 | 0.0022543 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.039028 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8785 | 0 | 0.0022543 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.039029 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8544 | 0 | 0.0022553 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.000991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.17144 | 0 | 0.0023953 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.000991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1546 | 0 | 0.0023953 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.000991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.15261 | 0 | 0.0023953 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.000991 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.15261 | 0 | 0.0023953 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.000991 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16054 | 0 | 0.0023953 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.053032 | 56 | 0.0024393 | 0.1366
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.055873 | 59 | 0.0024393 | 0.14392
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.053032 | 56 | 0.0024393 | 0.1366
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.053032 | 56 | 0.0024393 | 0.1366
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.055873 | 59 | 0.0024393 | 0.14392
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.000947 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.053032 | 56 | 0.0024393 | 0.1366
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.000942 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.37492 | 398 | 0.0024443 | 0.97285
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.000939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15287 | 0 | 0.0024473 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.000939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15155 | 0 | 0.0024473 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.000939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14921 | 0 | 0.0024473 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.000939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25278 | 0 | 0.0024473 | 0
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.000931 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14617 | 0 | 0.0024553 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.000931 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16013 | 172 | 0.0024553 | 0.42232
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.000931 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16013 | 172 | 0.0024553 | 0.42232
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.000931 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16013 | 172 | 0.0024553 | 0.42232
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.00464 | 0 | 0.0024583 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.019488 | 0 | 0.0024583 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.06032 | 0 | 0.0024583 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.061248 | 0 | 0.0024583 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.06496 | 0 | 0.0024583 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.058464 | 0 | 0.0024583 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057536 | 0 | 0.0024583 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.096512 | 0 | 0.0024583 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.000928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.054752 | 0 | 0.0024583 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.000928 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.011136 | 0 | 0.0024583 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.000928 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.6895 | 743 | 0.0024583 | 1.8265
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.000925 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.0111 | 12 | 0.0024613 | 0.029536
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03128 | 0 | 0.0024663 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.031924 | 0 | 0.0024663 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.030084 | 0 | 0.0024663 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.042228 | 0 | 0.0024663 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.016284 | 0 | 0.0024663 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.018768 | 0 | 0.0024663 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.018308 | 0 | 0.0024663 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0322 | 0 | 0.0024663 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01656 | 0 | 0.0024663 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.078568 | 0 | 0.0024663 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.00092 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13616 | 0 | 0.0024663 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.000918 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.67473 | 735 | 0.0024683 | 1.8142
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.095264 | 104 | 0.0024703 | 0.25692
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.095264 | 104 | 0.0024703 | 0.25692
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.049464 | 54 | 0.0024703 | 0.1334
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.048548 | 53 | 0.0024703 | 0.13093
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.049464 | 54 | 0.0024703 | 0.1334
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.052212 | 57 | 0.0024703 | 0.14081
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.049464 | 54 | 0.0024703 | 0.1334
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.049464 | 54 | 0.0024703 | 0.1334
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.053128 | 58 | 0.0024703 | 0.14328
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.000916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.053128 | 58 | 0.0024703 | 0.14328
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.000904 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15639 | 0 | 0.0024823 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.000904 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12204 | 0 | 0.0024823 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.000902 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12267 | 0 | 0.0024843 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.000902 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.037884 | 42 | 0.0024843 | 0.10434
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.000902 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.037884 | 42 | 0.0024843 | 0.10434
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.000902 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.034276 | 38 | 0.0024843 | 0.094405
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.000902 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.034276 | 38 | 0.0024843 | 0.094405
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.000895 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.063545 | 0 | 0.0024913 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.000895 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.06444 | 0 | 0.0024913 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.000895 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.034905 | 0 | 0.0024913 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.000895 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02685 | 0 | 0.0024913 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.000891 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.18978 | 213 | 0.0024953 | 0.53151
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.014434 | 0 | 0.0024953 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057024 | 0 | 0.0024953 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.056311 | 0 | 0.0024953 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.073597 | 0 | 0.0024953 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.000891 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.065578 | 0 | 0.0024953 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.000891 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.20315 | 228 | 0.0024953 | 0.56894
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.000891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.16038 | 0 | 0.0024953 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.000891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14131 | 0 | 0.0024953 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.000891 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.13989 | 0 | 0.0024953 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.00089 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.01068 | 12 | 0.0024963 | 0.029956
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.00089 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0024963 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.00089 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.15041 | 169 | 0.0024963 | 0.42188
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.00089 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.14685 | 165 | 0.0024963 | 0.4119
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.00089 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13261 | 0 | 0.0024963 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.00089 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057939 | 0 | 0.0024963 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.000887 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.031045 | 0 | 0.0024993 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.14411 | 0 | 0.0025033 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.13872 | 0 | 0.0025033 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.13907 | 0 | 0.0025033 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.13863 | 0 | 0.0025033 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.000883 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.23753 | 0 | 0.0025033 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.000881 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.068718 | 0 | 0.0025053 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.000881 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.07048 | 0 | 0.0025053 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.04048 | 46 | 0.0025063 | 0.11529
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.04048 | 46 | 0.0025063 | 0.11529
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.04048 | 46 | 0.0025063 | 0.11529
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.0484 | 55 | 0.0025063 | 0.13785
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.0484 | 55 | 0.0025063 | 0.13785
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.00088 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.04752 | 54 | 0.0025063 | 0.13534
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.000869 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.056485 | 0 | 0.0025173 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.000869 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.05214 | 0 | 0.0025173 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.000869 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.056485 | 0 | 0.0025173 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.000869 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.056485 | 0 | 0.0025173 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.078533 | 0 | 0.0025233 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.075599 | 0 | 0.0025233 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.075081 | 0 | 0.0025233 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.047033 | 0 | 0.0025233 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.000863 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.010529 | 0 | 0.0025233 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.000846 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0025403 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.000835 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.04175 | 50 | 0.0025513 | 0.12757
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.081644 | 0 | 0.0025723 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.075621 | 0 | 0.0025723 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.083598 | 0 | 0.0025723 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.083028 | 0 | 0.0025723 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.026048 | 0 | 0.0025723 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02442 | 0 | 0.0025723 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057631 | 0 | 0.0025723 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.054294 | 0 | 0.0025723 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.043142 | 0 | 0.0025723 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.1247 | 0 | 0.0025723 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12495 | 0 | 0.0025723 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12397 | 0 | 0.0025723 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.078144 | 0 | 0.0025723 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.000814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19862 | 0 | 0.0025723 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.000814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03256 | 0 | 0.0025723 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.5974 | 66 | 0.0025803 | 0.1703
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.558 | 65 | 0.0025803 | 0.16772
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6367 | 67 | 0.0025803 | 0.17288
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6367 | 67 | 0.0025803 | 0.17288
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.039354 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6367 | 67 | 0.0025803 | 0.17288
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.039354 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0025803 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.039354 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0025803 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.000777 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.1251 | 161 | 0.0026093 | 0.4201
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.000777 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.12898 | 166 | 0.0026093 | 0.43315
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.000777 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.1927 | 248 | 0.0026093 | 0.64712
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.000777 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.42424 | 546 | 0.0026093 | 1.4247
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.000777 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -0.49961 | 0 | 0.0026093 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.000777 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.010101 | 13 | 0.0026093 | 0.033921
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.000765 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.025245 | 0 | 0.0026213 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.000761 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.49541 | 0 | 0.0026253 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.000761 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.4292 | 0 | 0.0026253 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.000761 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.4566 | 0 | 0.0026253 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.000761 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12404 | 0 | 0.0026253 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.000761 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.12404 | 0 | 0.0026253 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.000761 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.18644 | 0 | 0.0026253 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.000752 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.034667 | 0 | 0.0026343 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.039435 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3802 | 0 | 0.0026613 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.039435 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.183 | 0 | 0.0026613 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.000667 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.074037 | 0 | 0.0027193 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.000667 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.074037 | 0 | 0.0027193 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.000667 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.079373 | 0 | 0.0027193 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.000667 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.073037 | 0 | 0.0027193 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.2239 | 208.2 | 0.0027263 | 0.56762
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.6129 | 142.1 | 0.0027263 | 0.38741
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.2298 | 132.4 | 0.0027263 | 0.36096
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.372 | 136 | 0.0027263 | 0.37078
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.8065 | 147 | 0.0027263 | 0.40077
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.0395 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.295 | 210 | 0.0027263 | 0.57252
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7651 | 70 | 0.0027273 | 0.19091
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7651 | 70 | 0.0027273 | 0.19091
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.6657 | 92.8 | 0.0027273 | 0.25309
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.1601 | 80 | 0.0027273 | 0.21818
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.1601 | 80 | 0.0027273 | 0.21818
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.039501 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.5426 | 115 | 0.0027273 | 0.31364
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.00064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04544 | 0 | 0.0027463 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.00064 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0064 | 0 | 0.0027463 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.037758 | 0 | 0.0027773 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.043483 | 0 | 0.0027773 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.027405 | 0 | 0.0027773 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.061509 | 0 | 0.0027773 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.052374 | 0 | 0.0027773 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.053592 | 0 | 0.0027773 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03045 | 0 | 0.0027773 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.010962 | 0 | 0.0027773 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057246 | 0 | 0.0027773 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04263 | 0 | 0.0027773 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.038367 | 0 | 0.0027773 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.043848 | 0 | 0.0027773 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.039463 | 0 | 0.0027773 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.061509 | 0 | 0.0027773 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.059073 | 0 | 0.0027773 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.062727 | 0 | 0.0027773 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.046284 | 0 | 0.0027773 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04872 | 0 | 0.0027773 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04872 | 0 | 0.0027773 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.000609 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10414 | 0 | 0.0027773 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.039624 | west | 8 | N | N | Nwest | Nwest | 1 | 2.7737 | 0 | 0.0028503 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.039624 | west | 8 | N | N | Nwest | Nwest | 1 | 2.9084 | 0 | 0.0028503 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.039624 | west | 8 | N | N | Nwest | Nwest | 1 | 2.7895 | 0 | 0.0028503 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.03963 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9445 | 0 | 0.0028563 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.03963 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.7186 | 0 | 0.0028563 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.03963 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.926 | 0 | 0.0028563 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.03963 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8309 | 0 | 0.0028563 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.039632 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9052 | 0 | 0.0028583 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.000478 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.031548 | 66 | 0.0029083 | 0.19195
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.000471 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.268 | 0 | 0.0029153 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.000471 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.27365 | 0 | 0.0029153 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.034808 | 76 | 0.0029283 | 0.22255
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.034808 | 76 | 0.0029283 | 0.22255
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.04809 | 105 | 0.0029283 | 0.30748
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.033892 | 74 | 0.0029283 | 0.2167
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.033892 | 74 | 0.0029283 | 0.2167
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.000458 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.046716 | 102 | 0.0029283 | 0.29869
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.000434 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.57852 | 0 | 0.0029523 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.000434 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.57635 | 0 | 0.0029523 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.000124 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.072416 | 0 | 0.0032623 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.000124 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.07378 | 0 | 0.0032623 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.000123 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.053259 | 0 | 0.0032633 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.000114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.018012 | 158 | 0.0032723 | 0.51703
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.000114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01824 | 160 | 0.0032723 | 0.52357
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.000114 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.01995 | 175 | 0.0032723 | 0.57266
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.040051 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0251 | 0 | 0.0032773 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00445 | 50 | 0.0032973 | 0.16487
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00445 | 50 | 0.0032973 | 0.16487
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00445 | 50 | 0.0032973 | 0.16487
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -8.9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.00445 | 50 | 0.0032973 | 0.16487
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.040098 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3257 | 0 | 0.0033243 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -3.7e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0056425 | 152.5 | 0.0033493 | 0.51077
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -3.7e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0055315 | 149.5 | 0.0033493 | 0.50073
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -3.7e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0086062 | 232.6 | 0.0033493 | 0.77906
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -3.2e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.004224 | 132 | 0.0033543 | 0.44277
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -3.2e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.004288 | 134 | 0.0033543 | 0.44948
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -3.2e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.010336 | 323 | 0.0033543 | 1.0835
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0033863 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0033863 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0033863 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0033863 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0033863 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0033863 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0033863 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0033863 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.040189 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6085 | 0 | 0.0034153 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 4.8e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.002016 | 42 | 0.0034343 | 0.14424
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 4.8e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.002112 | 44 | 0.0034343 | 0.15111
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 4.8e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.002112 | 44 | 0.0034343 | 0.15111
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 4.8e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.002256 | 47 | 0.0034343 | 0.16141
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 8.1e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.02511 | 310 | 0.0034673 | 1.0749
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 8.1e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.033453 | 413 | 0.0034673 | 1.432
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.006399 | 0 | 0.0034673 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.006561 | 0 | 0.0034673 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.006399 | 0 | 0.0034673 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00648 | 0 | 0.0034673 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0063504 | 0 | 0.0034673 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.002025 | 0 | 0.0034673 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.003726 | 0 | 0.0034673 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.002268 | 0 | 0.0034673 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0035316 | 0 | 0.0034673 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 8.1e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.005994 | 0 | 0.0034673 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.040244 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.26561 | 0 | 0.0034703 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.040244 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3804 | 0 | 0.0034703 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00441 | 49 | 0.0034763 | 0.17034
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00414 | 46 | 0.0034763 | 0.15991
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00414 | 46 | 0.0034763 | 0.15991
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00423 | 47 | 0.0034763 | 0.16339
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 9e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.01386 | 154 | 0.0034763 | 0.53536
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 9e-05 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.01332 | 148 | 0.0034763 | 0.5145
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00432 | 48 | 0.0034763 | 0.16686
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 9e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.00432 | 48 | 0.0034763 | 0.16686
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 9.6e-05 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.004608 | 0 | 0.0034823 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.00012 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00096 | 0 | 0.0035063 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.00012 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00096 | 0 | 0.0035063 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.004256 | 0 | 0.0035383 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.001064 | 0 | 0.0035383 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.005928 | 0 | 0.0035383 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00228 | 0 | 0.0035383 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.001064 | 0 | 0.0035383 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00228 | 0 | 0.0035383 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.005928 | 0 | 0.0035383 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.000152 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.005928 | 0 | 0.0035383 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.000163 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.001304 | 0 | 0.0035493 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.000167 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.002505 | 0 | 0.0035533 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.000167 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.003841 | 0 | 0.0035533 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.000188 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.013724 | 0 | 0.0035743 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.000204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.029376 | 144 | 0.0035903 | 0.51701
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.000204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.038352 | 188 | 0.0035903 | 0.67498
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.000216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.010303 | 47.7 | 0.0036023 | 0.17183
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.000216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.0080568 | 37.3 | 0.0036023 | 0.13437
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.000216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.009936 | 46 | 0.0036023 | 0.16571
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.000216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.010368 | 48 | 0.0036023 | 0.17291
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000238 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002856 | 0 | 0.0036243 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.000242 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0005808 | 0 | 0.0036283 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.000242 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0005808 | 0 | 0.0036283 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.000244 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.005368 | 22 | 0.0036303 | 0.079867
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.000244 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.002684 | 11 | 0.0036303 | 0.039934
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.000244 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.002684 | 11 | 0.0036303 | 0.039934
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.00027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.060453 | 223.9 | 0.0036563 | 0.81865
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.00027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.06075 | 225 | 0.0036563 | 0.82268
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.00027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.060642 | 224.6 | 0.0036563 | 0.82121
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.00027 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.061209 | 226.7 | 0.0036563 | 0.82889
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.048506 | 0 | 0.0036933 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.046971 | 0 | 0.0036933 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.0307 | 0 | 0.0036933 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.044515 | 0 | 0.0036933 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.045129 | 0 | 0.0036933 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.000307 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.038989 | 0 | 0.0036933 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.000307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.003684 | 0 | 0.0036933 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.000308 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.043736 | 142 | 0.0036943 | 0.5246
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.000308 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.04466 | 145 | 0.0036943 | 0.53568
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.000308 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.046508 | 151 | 0.0036943 | 0.55785
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.000308 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.08932 | 290 | 0.0036943 | 1.0714
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.000309 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0007416 | 0 | 0.0036953 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.000309 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0007416 | 0 | 0.0036953 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.000309 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0008652 | 0 | 0.0036953 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007975 | 0 | 0.0037053 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007975 | 0 | 0.0037053 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007975 | 0 | 0.0037053 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.005104 | 0 | 0.0037053 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007975 | 0 | 0.0037053 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007975 | 0 | 0.0037053 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007975 | 0 | 0.0037053 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.000319 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.004785 | 0 | 0.0037053 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.000336 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.21134 | 0 | 0.0037223 | 0
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.000337 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.049977 | 0 | 0.0037233 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.000337 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.050078 | 0 | 0.0037233 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.000337 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.051561 | 0 | 0.0037233 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.000337 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.11323 | 336 | 0.0037233 | 1.251
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.000337 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.06066 | 180 | 0.0037233 | 0.6702
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.000338 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.06084 | 180 | 0.0037243 | 0.67038
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.000343 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.11456 | 334 | 0.0037293 | 1.2456
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.000343 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.11662 | 340 | 0.0037293 | 1.268
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.000343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.06174 | 180 | 0.0037293 | 0.67128
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.000343 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.06174 | 180 | 0.0037293 | 0.67128
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.000346 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00865 | 0 | 0.0037323 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.000346 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.00865 | 0 | 0.0037323 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.051009 | 147 | 0.0037333 | 0.5488
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.047886 | 138 | 0.0037333 | 0.5152
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.04858 | 140 | 0.0037333 | 0.52267
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.051009 | 147 | 0.0037333 | 0.5488
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.063154 | 182 | 0.0037333 | 0.67947
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.000347 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.068706 | 198 | 0.0037333 | 0.7392
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.000347 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.013186 | 0 | 0.0037333 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.00035 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0133 | 0 | 0.0037363 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.000366 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.010614 | 0 | 0.0037523 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.000368 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.002208 | 0 | 0.0037543 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.000373 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001492 | 0 | 0.0037593 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.035814 | 0 | 0.0037673 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.015621 | 0 | 0.0037673 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.014478 | 0 | 0.0037673 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.007239 | 0 | 0.0037673 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.035814 | 0 | 0.0037673 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.013716 | 0 | 0.0037673 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.016383 | 0 | 0.0037673 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.008382 | 0 | 0.0037673 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.056388 | 0 | 0.0037673 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01905 | 0 | 0.0037673 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.020955 | 0 | 0.0037673 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.000381 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.01905 | 0 | 0.0037673 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.000393 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.014934 | 38 | 0.0037793 | 0.14361
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.000393 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.0075849 | 19.3 | 0.0037793 | 0.072941
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.000393 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.005895 | 15 | 0.0037793 | 0.05669
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.000393 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.018471 | 47 | 0.0037793 | 0.17763
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.000393 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0037793 | 0
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.087561 | 207 | 0.0038093 | 0.78853
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.091664 | 216.7 | 0.0038093 | 0.82548
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10237 | 242 | 0.0038093 | 0.92186
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.060912 | 144 | 0.0038093 | 0.54854
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.060912 | 144 | 0.0038093 | 0.54854
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.000423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.072333 | 171 | 0.0038093 | 0.6514
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.000457 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.24952 | 0 | 0.0038433 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.000457 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.34275 | 0 | 0.0038433 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.000474 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.069441 | 146.5 | 0.0038603 | 0.56554
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.000474 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.070105 | 147.9 | 0.0038603 | 0.57094
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.000474 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.082002 | 173 | 0.0038603 | 0.66784
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.000481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.074555 | 155 | 0.0038673 | 0.59944
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.000481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.08177 | 170 | 0.0038673 | 0.65745
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.000481 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.074555 | 155 | 0.0038673 | 0.59944
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.040649 | west | 8 | N | N | Nwest | Nwest | 1 | 1.0487 | 0 | 0.0038753 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.000496 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0038823 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.000496 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0038823 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.000496 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0038823 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.000512 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0038983 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.000533 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018655 | 0 | 0.0039193 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.000533 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018122 | 0 | 0.0039193 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.000533 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018655 | 0 | 0.0039193 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.000538 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0039243 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.000547 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.23193 | 0 | 0.0039333 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.000547 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.23247 | 0 | 0.0039333 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.000559 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.23031 | 412 | 0.0039453 | 1.6255
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.000559 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.2236 | 400 | 0.0039453 | 1.5781
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.00056 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.11704 | 209 | 0.0039463 | 0.82478
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.00056 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.12096 | 216 | 0.0039463 | 0.85241
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.00056 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.02576 | 46 | 0.0039463 | 0.18153
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.00056 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.02632 | 47 | 0.0039463 | 0.18548
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.00056 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.02576 | 46 | 0.0039463 | 0.18153
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.00056 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.02576 | 46 | 0.0039463 | 0.18153
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.000565 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.22374 | 0 | 0.0039513 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.000584 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.23769 | 407 | 0.0039703 | 1.6159
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6892 | 66 | 0.0039713 | 0.26211
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.8114 | 69 | 0.0039713 | 0.27402
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.8114 | 69 | 0.0039713 | 0.27402
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.7299 | 67 | 0.0039713 | 0.26608
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.7299 | 67 | 0.0039713 | 0.26608
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.040745 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.6484 | 65 | 0.0039713 | 0.25814
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.000653 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.037874 | 58 | 0.0040393 | 0.23428
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.000653 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.058117 | 89 | 0.0040393 | 0.3595
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.000653 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.028732 | 44 | 0.0040393 | 0.17773
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.000653 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.028732 | 44 | 0.0040393 | 0.17773
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.000653 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.028079 | 43 | 0.0040393 | 0.17369
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.000653 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.029385 | 45 | 0.0040393 | 0.18177
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.081396 | 0 | 0.0041003 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15851 | 0 | 0.0041003 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13138 | 0 | 0.0041003 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15994 | 0 | 0.0041003 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000714 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08211 | 0 | 0.0041003 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.040893 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9072 | 0 | 0.0041193 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.000778 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.009336 | 0 | 0.0041643 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.000778 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.008558 | 0 | 0.0041643 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000778 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.009336 | 0 | 0.0041643 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.041046 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9255 | 0 | 0.0042723 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.00107 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0044563 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.001404 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1404 | 100 | 0.0047903 | 0.47903
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.001404 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1404 | 100 | 0.0047903 | 0.47903
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.001404 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0047903 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.001404 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0047903 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.001404 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0047903 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.001404 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0047903 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.001405 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0047913 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.041608 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3618 | 0 | 0.0048343 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.001453 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.026154 | 0 | 0.0048393 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.001453 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.026154 | 0 | 0.0048393 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.041689 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.504 | 0 | 0.0049153 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.041689 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.504 | 0 | 0.0049153 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.001756 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.049168 | 0 | 0.0051423 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.001756 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.050924 | 0 | 0.0051423 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001859 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.7845 | 422 | 0.0052453 | 2.2135
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.001926 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.034668 | 0 | 0.0053123 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.001926 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.034668 | 0 | 0.0053123 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.001926 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.02889 | 0 | 0.0053123 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.001991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.047784 | 24 | 0.0053773 | 0.12906
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.001991 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.047784 | 24 | 0.0053773 | 0.12906
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.001991 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.045793 | 23 | 0.0053773 | 0.12368
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.042268 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6629 | 0 | 0.0054943 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.002286 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.019202 | 8.4 | 0.0056723 | 0.047648
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.002398 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.032853 | 0 | 0.0057843 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.042784 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0325 | 0 | 0.0060103 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.042784 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.1341 | 0 | 0.0060103 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.04286 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2431 | 0 | 0.0060863 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.04286 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.6145 | 0 | 0.0060863 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.04286 | west | 7 | N | N | Nwest | Nwest | 1 | 1.0715 | 0 | 0.0060863 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.04286 | west | 7 | N | N | Nwest | Nwest | 1 | 1.9587 | 0 | 0.0060863 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.04286 | west | 7 | N | N | Nwest | Nwest | 1 | 1.9587 | 0 | 0.0060863 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.044229 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7152 | 0 | 0.0074553 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.045271 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7907 | 0 | 0.0084973 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.045271 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5724 | 0 | 0.0084973 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.046069 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8087 | 0 | 0.0092953 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.007907 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.011293 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.814 | 0 | 0.0116 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.2002 | 0 | 0.0116 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5305 | 0 | 0.0116 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.7565 | 0 | 0.0116 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.0793 | 0 | 0.0116 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.048374 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8941 | 0 | 0.0116 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.008626 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.051756 | 0 | 0.012012 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.048933 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.872 | 0 | 0.012159 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.048933 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.4014 | 0 | 0.012159 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.048933 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3284 | 0 | 0.012159 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.050233 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.535 | 0 | 0.013459 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.011717 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.38666 | 0 | 0.015103 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.011717 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.29292 | 0 | 0.015103 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.011717 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.015103 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.074307 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4584 | 0 | 0.037533 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.25388 | west | 4 | Y | N | Ywest | Nwest | 1 | 164.9426 | 0 | 0.2171 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
20
25
30
35
40
45
50
55
60
65
70
75
80
85
90
95
100
105
110
| 115 | 0
| Max | 260
| Min | 260
| Avg | 260