## test results
CRE test for: |  | 3666 HUTTOSS1 - 3670 RNDRCKNE_ctg1 | [5 empty] | FAIL
Line Rating: |  | 247.6
Direcction |  | South | → | North |  | S-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3666 HUTTOSS1 - 3670 RNDRCKNE_ctg1
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.039437
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.051858
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.035371
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.012795
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3666 HUTTOSS1 - 3670 RNDRCKNE_ctg1
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.042506
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.061278
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.035552
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.011894
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3666 HUTTOSS1 - 3670 RNDRCKNE_ctg1
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.10072
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.0038848
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.051331
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.08741
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.039063
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.047265
PTDF tests
South | → | North | 0.039819 | 0.42071 | -0.42071 | -0.21445 | -0.039819 | -0.094364 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.094364 | 0.10072
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.14041
[6 empty] | Concentration |  | -1.488 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.049089
[6 empty] | Concentration |  | -0.52021 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 178.1753
| Percent of line rating => | [6 empty] | 71.96% | FAIL
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -4.4584
[7 empty] | B1(N-S) | 0.0471 | -0.40193 | -0.44903 | 0.0471
[7 empty] | B2 (N-W) | 0.00070595 | -0.016614 | -0.01732 | 0.00070595
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.0097017 | -0.21915 | -0.22885 | 0.0097017
[7 empty] | B4 (S-W) | -0.00012366 | 0.38958 | 0.38971 | -0.00012366
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.012889 | 0.18705 | 0.17416 | 0.012889
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.0089291 | -0.20179 | -0.21072 | 0.0089291
[7 empty] | test | 0 | 0.42071 | 0.42071 | 0
[7 empty] | B1 | 11.2%
Deployment Error Percent | [6 empty] | B2 | 0.1678%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 2.306%
[7 empty] | B4 | -0.02939%
[7 empty] | B5 | 3.064%
[7 empty] | B6 | 2.122%
[7 empty] | Max Abs Error | 11.2% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | S-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3666 HUTTOSS1 - 3670 RNDRCKNE_ctg1 C:3429 SANDOW__ - 7040 L_AUSTRO C:7040 L_AUSTRO - 13429 SAND_TXU_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3666 HUTTOSS1 - 3670 RNDRCKNE_ctg1 C:3429 SANDOW__ - 7040 L_AUSTRO C:7040 L_AUSTRO - 13429 SAND_TXU_
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.058959 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 15.0345
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.058959 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 8.7849
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.054469 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.81703
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.054469 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.81703
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.058959 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 9.0207
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.057078 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 8.5617
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.057078 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 4.5662
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.041923 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 3.0604
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.041923 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 4.9888
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.041923 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 8.5942
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.041923 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 4.2761
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.041923 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 4.0246
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.040683 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.4882
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.040683 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.4882
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.04384 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 7.3651
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.04384 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 3.9456
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.041615 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.74907
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.041615 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.74907
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.041615 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 1.5814
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.041277 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 11.8878
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.041277 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 6.0677
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.041277 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 6.0677
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.040948 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 4.6067
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.040652 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 1.6261
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.040632 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 3.2099
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.040632 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 4.307
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.040632 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 5.9323
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.040632 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 3.088
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.041007 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 2.4604
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.041007 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 2.5834
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.04059 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.8118
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.04059 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 1.0148
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.04059 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 1.6642
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.016747 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 7.7539
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 2.2907
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 2.256
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.3254
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.3254
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.3254
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.034707 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 3.9566
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.034707 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 17.8741
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 2.3813
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.4895
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.4895
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 2.4174
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 2.4174
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 2.3452
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.035872 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 2.511
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.035872 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 2.633
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.035872 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 2.5254
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.035982 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 5.3973
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.035982 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 7.916
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.036164 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 3.5802
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.036164 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 2.206
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.036153 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 5.0976
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.036164 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 0.9041
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.036164 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.6527
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.036164 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.6527
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.036153 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 4.3384
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.035551 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 0.91722
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.035426 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 3.5603
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.035768 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 4.2922
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.035417 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 2.0542
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.03551 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 7.6062
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.036395 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 5.4592
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.035056 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.23137
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.035056 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 1.2024
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.036395 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 3.6759
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.035785 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 4.2942
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.039567 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 14.4815
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.039643 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 9.5936
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.037834 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 15.1336
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.037836 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 8.9293
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.038251 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 6.3114
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.040514 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 8.2649
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.040514 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 8.1433
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.040514 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 9.8044
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.039658 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.79316
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.039658 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.79316
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.039658 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.79316
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.039658 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.67419
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.040667 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 4.88
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.041323 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 2.4794
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.040623 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 3.0467
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.040623 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 3.2336
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.040623 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 3.5911
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 6.5029
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 6.3403
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 7.966
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 6.3403
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 6.381
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 8.0473
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.040698 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 6.9187
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.040698 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 21.163
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.040665 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 15.046
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.040608 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 22.6593
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.040608 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 23.512
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.040608 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 32.8113
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.041459 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 4.6434
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.041459 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 4.1459
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.041459 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 15.6715
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.041761 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 9.0747
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.041761 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 8.561
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.041761 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 11.3757
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.041902 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 32.2645
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.042559 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 2.9791
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.042559 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 2.9366
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.042559 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 2.9366
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.042559 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 2.894
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.041655 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 48.1948
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.041655 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 48.2365
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.043579 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 9.7617
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.043579 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 9.8489
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.043463 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 9.4054
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.043463 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 9.3924
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.043579 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 9.2387
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.043579 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 9.1952
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.042106 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 16.6319
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.042051 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 18.2922
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.042106 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 18.3161
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.040876 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 5.6409
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.041208 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 4.8625
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.041208 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 4.7389
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.041208 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 22.9116
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.040607 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 15.7555
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.040607 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 20.9126
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.039212 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 30.7814
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.039212 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 31.1735
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.039212 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 30.5854
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.03887 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 7.0743
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.03887 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 18.8131
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.041014 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 9.1871
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.038883 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 1.9442
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.038901 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 1.6338
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.036605 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 22.5121
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.036605 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 21.4871
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.061253 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 32.8929
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.061253 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 48.2061
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.061576 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 4.6182
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.061576 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 13.6699
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.088554 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 50.3872
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.058138 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -12.1508
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.058138 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -12.5578
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.058081 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -23.639
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.058138 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -2.6743
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.058138 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -2.7325
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.058138 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -2.6743
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.058138 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -2.6743
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.05821 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -24.681
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.05821 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -24.7392
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.057768 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -3.3505
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.057768 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -5.1414
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.057768 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -2.5418
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.057768 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -2.5418
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.057768 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -2.484
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.057768 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -2.5996
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.0582 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -23.9784
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.0582 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -23.28
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.057585 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -31.4414
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.057585 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -43.1887
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.058375 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -3.5609
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.058375 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -5.5456
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.058375 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -8.8146
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.057907 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -8.9756
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.057907 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -9.8442
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.057907 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -8.9756
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.046129 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -1.0148
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.046129 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.50742
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.046129 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.50742
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.04656 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -2.2209
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.04656 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -1.7367
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.04656 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -2.1418
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.04656 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -2.2349
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.048967 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.5876
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.048967 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.53864
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.051454 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.2349
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.051454 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.2349
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.051454 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -1.1834
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.054365 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -21.5285
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.029337 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -39.1062
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.029337 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -38.9595
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.048106 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -1.828
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.048106 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.92845
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.048106 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.72159
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.048106 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -2.261
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.030908 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 2.3181
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.036711 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 5.5066
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.034717 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 5.8845
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.014596 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 2.1894
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.036122 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 2.2757
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.038593 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 25.0739
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.040728 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 1.6291
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.040728 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 1.6291
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.065216 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -27.5212
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.060432 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -7.977
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.060432 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -8.0979
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.060432 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -19.5195
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.069182 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -10.9308
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.069182 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -11.0691
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.069182 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -12.1068
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.062594 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -36.5549
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.062594 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -37.2434
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.06256 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -27.0885
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.063869 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -14.3003
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.063869 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -14.3705
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.063869 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -14.345
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.063869 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -14.4791
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.10175 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.81401
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.10175 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.81401
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.055408 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.99734
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.055408 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.99734
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.055408 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.83112
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.056119 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.76883
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.073263 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.3187
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.073263 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.3187
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.09151 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -3.2029
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.09151 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -3.1113
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.09151 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -3.2029
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.065872 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -1.8444
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.065872 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -1.9103
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.034742 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 1.216
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.034742 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 1.0423
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.058762 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -2.9381
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.058762 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -2.9381
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.058762 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -2.9381
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.058762 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -2.9381
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.069438 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.41663
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.062708 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.1505
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.062708 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.1505
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.062708 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.17558
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.06179 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.24716
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.061252 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.147
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.061252 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.147
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -8.7505
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -8.2147
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -8.3338
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -8.7505
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -10.8339
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -11.7863
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.072694 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -11.0858
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.072694 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -10.8678
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.072694 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -16.9086
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.06169 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -8.76
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.06169 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -8.9451
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.06169 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -9.3152
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.06169 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -17.8901
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.028987 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -0.95657
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.028987 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -0.72467
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.048967 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.5876
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.046635 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -3.4044
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -3.4349
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -3.5219
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -1.2646
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.31616
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -3.4349
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -3.4784
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -3.4088
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -1.087
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -2.0001
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.049622 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -31.2122
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.047171 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -6.7926
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.047171 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -8.8681
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.056951 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.68341
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.035961 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.21577
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.047561 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -15.9805
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.047675 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -15.9235
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.047675 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -16.2095
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.047744 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -1.8143
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.047691 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.1923
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.047691 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.1923
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.047741 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -1.8142
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.047987 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -1.3916
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.047567 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -7.0542
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.047567 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -7.0685
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.047567 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -7.2778
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -7.4331
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -7.1979
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -4.7045
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -6.8215
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -6.9156
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -5.9747
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.048312 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -7.0777
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.048312 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -7.1453
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.048312 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -8.358
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.048207 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -9.9788
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.048207 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -10.4465
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.048207 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -11.6661
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.048205 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -6.9415
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.048205 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -6.9415
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.048205 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -8.2431
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.10095 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -31.2936
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.10095 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -41.6911
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.098803 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -4.1497
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.098803 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -4.3473
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.098803 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -4.3473
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.098803 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -4.6437
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -4.7001
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -4.4123
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -4.4123
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -4.5082
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.09592 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -14.7717
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.09592 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -14.1962
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -4.6042
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -4.6042
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.4772
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.4772
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 3.2841
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 2.8311
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 2.8311
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 4.0697
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 7.3667
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 5.0279
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 4.6847
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 4.8121
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 5.2013
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 7.4304
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.036586 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 7.6465
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.036586 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 4.6281
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.036586 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 9.1099
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.036586 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 7.2074
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.035982 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 7.1964
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.035982 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 4.3862
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.034859 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 5.194
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.035892 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 6.4606
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.035892 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 6.4606
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.035856 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 8.0676
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.036339 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 4.5424
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.036339 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 4.5424
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 5.6931
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 5.7338
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 12.5655
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 5.8151
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 5.8558
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 12.6061
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.042065 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 8.2447
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.042065 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 4.6692
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.040888 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 6.4923
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 6.6133
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 6.6133
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 16.6945
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 6.5327
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 6.4923
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 6.573
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 16.4929
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.040722 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.040722 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.039047 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 5.779
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.039047 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 5.0761
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.039047 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 5.6618
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.039047 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 15.5798
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.037024 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 5.5795
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.037024 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 5.5906
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.037024 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 6.5681
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.037107 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 5.6217
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.037107 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 5.6514
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.037107 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 6.5865
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.088554 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 51.4499
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.027019 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 23.1012
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.027019 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 23.1012
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.022449 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.71837
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.024394 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 1.1709
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.024394 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 1.1221
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.022617 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.2714
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.022617 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 1.1535
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.022617 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.38449
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.022617 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.49757
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.022617 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.56542
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.024394 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 2.5614
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.036265 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 3.0463
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.030839 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 2.4671
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.030804 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 4.6206
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.030804 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 4.6206
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.013496 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.95552
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.013496 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.90018
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.013496 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.71529
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -2.0676
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -2.0716
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -2.0554
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -1.2956
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -3.293
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.013496 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.53984
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.013506 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -1.3547
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.013506 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -1.2547
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.013506 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -1.3871
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.013506 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -1.3776
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.013506 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.43219
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.013506 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.40518
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.019754 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -2.1927
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.019754 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -2.1927
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.019754 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -2.3507
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.019754 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -2.1631
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.027019 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 4.115
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.027019 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 4.1339
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.009656 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -1.3132
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.015582 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.51421
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.009638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.4048
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.009638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.4048
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.009638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.36624
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.009638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.36624
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.020811 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -1.4776
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.020811 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.20811
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.015971 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -2.6033
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.015971 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -2.6033
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.015971 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -3.9129
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.011092 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.72098
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.011092 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.66552
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.011092 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.72098
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.011092 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.72098
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.010157 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -1.5134
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.010157 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.66122
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -1.0349
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.99619
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.98936
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.61977
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.13874
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.00847 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -6.2932
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.008944 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -6.5738
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.008327 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.4322
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.008327 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.4322
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.008327 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.4322
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.005692 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -0.98472
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.009562 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -1.6542
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.009562 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -1.2909
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.007992 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -1.3011
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.007992 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -1.2899
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.007992 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -1.2699
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.007992 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -2.1514
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.010126 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.64806
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.010126 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.63996
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.010126 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.83641
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.010126 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.74527
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -1.7022
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -1.6386
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -1.6427
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -1.6375
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -2.8057
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.008493 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.042465
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.008493 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.17835
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.012805 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 1.9745
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.012805 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.9976
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.012805 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.9976
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.012805 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 4.8659
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.007871 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -3.1327
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.49059
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.49059
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.49059
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.58657
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.58657
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.57591
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.031053 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 25.6808
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.031053 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 25.4324
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.016127 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.74345
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -2.1886
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -2.1886
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -3.0237
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -2.131
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -2.131
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -2.9373
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.010117 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -1.8211
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.010117 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -1.6046
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.010117 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -1.5884
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.010306 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.36071
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.012092 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -5.5502
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.55178
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.56027
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.59423
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.53481
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.52632
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -0.88286
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.50085
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.005692 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -0.88795
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.005692 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.87657
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.005692 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.87657
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.005692 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -0.9221
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.00838 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -1.3157
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.009941 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.70581
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.009941 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.71575
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.009941 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.3877
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.009941 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.29823
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.010569 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.82438
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.010569 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.84552
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.010129 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.16409
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.010165 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -1.6772
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.010175 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -1.7196
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.010132 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -2.1581
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.010122 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -2.3078
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.010182 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.12218
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.010182 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.18328
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.01269 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.6345
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.94713
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.94713
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.49178
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.48267
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.49178
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.5191
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.49178
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.49178
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.52821
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.52821
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.008672 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.10406
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.42935
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.45235
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.42935
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.42935
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.45235
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.42935
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.027247 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -1.7983
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.015364 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -2.4736
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.015364 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -2.5504
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.015364 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -3.8103
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.015364 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -8.3887
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.015364 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -9.8791
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.016002 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -10.4173
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.016002 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -9.0251
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.016002 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -9.6012
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.015364 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.19973
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.008482 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.10178
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.30015
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.30633
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.28868
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.40521
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.15626
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.18009
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.17568
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.30898
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.1589
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.75391
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -1.3065
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -1.3721
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -1.5801
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.99585
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -2.2351
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -1.9032
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -1.9474
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -1.1065
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.39834
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -2.0802
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -1.5491
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -1.3942
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -1.5934
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -1.434
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -2.2351
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -2.1466
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -2.2794
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -1.6819
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -1.7704
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -1.7704
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -3.7842
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.42761
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.029181 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 2.2323
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.030908 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 2.4726
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.030908 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 1.2363
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.031186 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 2.4949
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.030848 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 2.4678
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.029416 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 2.3533
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.028948 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 2.4316
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.031186 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 2.4949
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -6.9746
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.035838 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 4.3006
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.035838 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 8.3503
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.035838 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 6.0996
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -13.5822
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -11.2573
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -13.7045
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -7.0358
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -6.1181
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.037239 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 2.2343
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.033041 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.021481 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.032216 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.15464
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 1.3704
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 3.9285
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 4.9334
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 4.3487
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 3.8371
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 2.9418
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.035396 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 5.3094
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.035251 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 3.9657
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.035251 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 5.27
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.035251 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 6.5567
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.035251 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 7.5613
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.048106 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.037583 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.05096 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -1.2174
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -1.8957
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -3.2175
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -4.5187
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -1.9709
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -1.8267
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.91335
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -4.5187
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -1.7306
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -2.0671
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -1.0576
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -1.7614
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.67748
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.31616
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.67748
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -1.7614
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -1.7614
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -7.1145
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -2.4036
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -2.6439
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -2.4036
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.047045 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.56454
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.045704 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.68556
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.045704 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -1.0512
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.043876 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -2.106
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.045368 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.36294
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.047576 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -8.5637
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.047561 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -8.561
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.047675 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -8.5815
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.047675 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -8.5815
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.050965 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -5.0965
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.050965 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -5.0965
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.1812
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.1812
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.1812
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.756
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.1812
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.1812
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.1812
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.70875
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.050965 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.050965 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -25.4825
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.050965 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -25.4825
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.050965 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.050385 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.028987 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.049593 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.048936 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L:3666 HUTTOSS1 - 3670 RNDRCKNE_ctg1 C:3429 SANDOW__ - 7040 L_AUSTRO C:7040 L_AUSTRO - 13429 SAND_TXU_ | [7 empty] | 178.1753
Number of Bus | Name of Bus | ID | Max MW | L:3666 HUTTOSS1 - 3670 RNDRCKNE_ctg1 C:3429 SANDOW__ - 7040 L_AUSTRO C:7040 L_AUSTRO - 13429 SAND_TXU_ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.058959 | north | 0.019522 | 0.11082 | 0.023588 | 0.071754 | 0.019522 | North | N | 0.019522 | 0
239 | BOSQUESW | 1 | 149 | 0.058959 | north | 0.019522 | 0.11082 | 0.023588 | 0.071754 | 0.019522 | North | N | 0.019522 | 0
244 | WHITNYDM | 1 | 15 | 0.054469 | north | 0.015032 | 0.10633 | 0.019098 | 0.067264 | 0.015032 | North | N | 0.015032 | 0
245 | WHITNYDM | 2 | 15 | 0.054469 | north | 0.015032 | 0.10633 | 0.019098 | 0.067264 | 0.015032 | North | N | 0.015032 | 0
247 | BOSQUESW | 2 | 153 | 0.058959 | north | 0.019522 | 0.11082 | 0.023588 | 0.071754 | 0.019522 | North | N | 0.019522 | 0
251 | BOSQUESW | 2 | 150 | 0.057078 | north | 0.017641 | 0.10894 | 0.021707 | 0.069873 | 0.017641 | North | N | 0.017641 | 0
253 | BOSQUESW | 2 | 80 | 0.057078 | north | 0.017641 | 0.10894 | 0.021707 | 0.069873 | 0.017641 | North | N | 0.017641 | 0
332 | RWMILLER | 1 | 73 | 0.041923 | north | 0.0024859 | 0.093781 | 0.0065525 | 0.054718 | 0.0024859 | North | N | 0.0024859 | 0
333 | RWMILLER | 2 | 119 | 0.041923 | north | 0.0024859 | 0.093781 | 0.0065525 | 0.054718 | 0.0024859 | North | N | 0.0024859 | 0
334 | RWMILLER | 3 | 205 | 0.041923 | north | 0.0024859 | 0.093781 | 0.0065525 | 0.054718 | 0.0024859 | North | N | 0.0024859 | 0
335 | RWMILLER | 4 | 102 | 0.041923 | north | 0.0024859 | 0.093781 | 0.0065525 | 0.054718 | 0.0024859 | North | N | 0.0024859 | 0
336 | RWMILLER | 5 | 96 | 0.041923 | north | 0.0024859 | 0.093781 | 0.0065525 | 0.054718 | 0.0024859 | North | N | 0.0024859 | 0
344 | MRSSHPRD | 1 | 12 | 0.040683 | north | 0.0012459 | 0.092541 | 0.0053125 | 0.053478 | 0.0012459 | North | N | 0.0012459 | 0
345 | MRSSHPRD | 2 | 12 | 0.040683 | north | 0.0012459 | 0.092541 | 0.0053125 | 0.053478 | 0.0012459 | North | N | 0.0012459 | 0
366 | JNSNCNTY | 1 | 168 | 0.04384 | north | 0.0044029 | 0.095698 | 0.0084695 | 0.056635 | 0.0044029 | North | N | 0.0044029 | 0
367 | JNSNCNTY | 2 | 90 | 0.04384 | north | 0.0044029 | 0.095698 | 0.0084695 | 0.056635 | 0.0044029 | North | N | 0.0044029 | 0
503 | NTHTEXAS | 1 | 18 | 0.041615 | north | 0.0021779 | 0.093473 | 0.0062445 | 0.05441 | 0.0021779 | North | N | 0.0021779 | 0
504 | NTHTEXAS | 2 | 18 | 0.041615 | north | 0.0021779 | 0.093473 | 0.0062445 | 0.05441 | 0.0021779 | North | N | 0.0021779 | 0
505 | NTHTEXAS | 3 | 38 | 0.041615 | north | 0.0021779 | 0.093473 | 0.0062445 | 0.05441 | 0.0021779 | North | N | 0.0021779 | 0
580 | JCKCNTY8 | 1 | 288 | 0.041277 | north | 0.0018399 | 0.093135 | 0.0059065 | 0.054072 | 0.0018399 | North | N | 0.0018399 | 0
581 | JCKCNTY8 | 2 | 147 | 0.041277 | north | 0.0018399 | 0.093135 | 0.0059065 | 0.054072 | 0.0018399 | North | N | 0.0018399 | 0
582 | JCKCNTY8 | 3 | 147 | 0.041277 | north | 0.0018399 | 0.093135 | 0.0059065 | 0.054072 | 0.0018399 | North | N | 0.0018399 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.040948 | north | 0.0015109 | 0.092806 | 0.0055775 | 0.053743 | 0.0015109 | North | N | 0.0015109 | 0
837 | NEWMAN_G | 1 | 40 | 0.040652 | north | 0.0012149 | 0.09251 | 0.0052815 | 0.053447 | 0.0012149 | North | N | 0.0012149 | 0
842 | OLINGER_ | 1 | 79 | 0.040632 | north | 0.0011949 | 0.09249 | 0.0052615 | 0.053427 | 0.0011949 | North | N | 0.0011949 | 0
843 | OLINGER_ | 1 | 106 | 0.040632 | north | 0.0011949 | 0.09249 | 0.0052615 | 0.053427 | 0.0011949 | North | N | 0.0011949 | 0
844 | OLINGER_ | 1 | 146 | 0.040632 | north | 0.0011949 | 0.09249 | 0.0052615 | 0.053427 | 0.0011949 | North | N | 0.0011949 | 0
845 | OLINGER_ | 1 | 76 | 0.040632 | north | 0.0011949 | 0.09249 | 0.0052615 | 0.053427 | 0.0011949 | North | N | 0.0011949 | 0
923 | SPENCER_ | 1 | 60 | 0.041007 | north | 0.0015699 | 0.092865 | 0.0056365 | 0.053802 | 0.0015699 | North | N | 0.0015699 | 0
924 | SPENCER_ | 1 | 63 | 0.041007 | north | 0.0015699 | 0.092865 | 0.0056365 | 0.053802 | 0.0015699 | North | N | 0.0015699 | 0
948 | STEAM1 | 1 | 20 | 0.04059 | north | 0.0011529 | 0.092448 | 0.0052195 | 0.053385 | 0.0011529 | North | N | 0.0011529 | 0
949 | STEAM2 | 1 | 25 | 0.04059 | north | 0.0011529 | 0.092448 | 0.0052195 | 0.053385 | 0.0011529 | North | N | 0.0011529 | 0
950 | STEAM3 | 1 | 41 | 0.04059 | north | 0.0011529 | 0.092448 | 0.0052195 | 0.053385 | 0.0011529 | North | N | 0.0011529 | 0
990 | GIBN_CRE | 1 | 463 | 0.016747 | north | -0.02269 | 0.068605 | -0.018624 | 0.029542 | 0.018624 | west | Y | 0.02269 | 1.8828
1002 | PBCTAGE_ | A | 66 | 0.034707 | west | -0.0047301 | 0.086565 | -0.00066352 | 0.047502 | 0.00066352 | west | N | 0.00066352 | 0
1003 | PBCTBGE_ | B | 65 | 0.034707 | west | -0.0047301 | 0.086565 | -0.00066352 | 0.047502 | 0.00066352 | west | N | 0.00066352 | 0
1004 | PBCTCGE_ | C | 67 | 0.034707 | west | -0.0047301 | 0.086565 | -0.00066352 | 0.047502 | 0.00066352 | west | N | 0.00066352 | 0
1005 | PBCTDGE_ | D | 67 | 0.034707 | west | -0.0047301 | 0.086565 | -0.00066352 | 0.047502 | 0.00066352 | west | N | 0.00066352 | 0
1006 | PBCTEGE_ | E | 67 | 0.034707 | west | -0.0047301 | 0.086565 | -0.00066352 | 0.047502 | 0.00066352 | west | N | 0.00066352 | 0
1007 | PB5GEN_6 | MB | 114 | 0.034707 | west | -0.0047301 | 0.086565 | -0.00066352 | 0.047502 | 0.00066352 | west | N | 0.00066352 | 0
1008 | PB6GEN_7 | MB | 515 | 0.034707 | west | -0.0047301 | 0.086565 | -0.00066352 | 0.047502 | 0.00066352 | west | N | 0.00066352 | 0
1039 | MRGNAG_1 | A | 66 | 0.03608 | west | -0.0033571 | 0.087938 | 0.00070948 | 0.048875 | 0.00070948 | west | N | 0.00070948 | 0
1040 | MRGNBG_2 | B | 69 | 0.03608 | west | -0.0033571 | 0.087938 | 0.00070948 | 0.048875 | 0.00070948 | west | N | 0.00070948 | 0
1041 | MRGNCG_3 | C | 69 | 0.03608 | west | -0.0033571 | 0.087938 | 0.00070948 | 0.048875 | 0.00070948 | west | N | 0.00070948 | 0
1042 | MRGNDG_4 | D | 67 | 0.03608 | west | -0.0033571 | 0.087938 | 0.00070948 | 0.048875 | 0.00070948 | west | N | 0.00070948 | 0
1043 | MRGNEG_5 | E | 67 | 0.03608 | west | -0.0033571 | 0.087938 | 0.00070948 | 0.048875 | 0.00070948 | west | N | 0.00070948 | 0
1044 | MRGNFG_6 | F | 65 | 0.03608 | west | -0.0033571 | 0.087938 | 0.00070948 | 0.048875 | 0.00070948 | west | N | 0.00070948 | 0
1045 | CALENG1G | 1 | 70 | 0.035872 | west | -0.0035651 | 0.08773 | 0.00050148 | 0.048667 | 0.00050148 | west | N | 0.00050148 | 0
1046 | CALENG2G | 2 | 73.4 | 0.035872 | west | -0.0035651 | 0.08773 | 0.00050148 | 0.048667 | 0.00050148 | west | N | 0.00050148 | 0
1047 | CALENG3G | 3 | 70.4 | 0.035872 | west | -0.0035651 | 0.08773 | 0.00050148 | 0.048667 | 0.00050148 | west | N | 0.00050148 | 0
1058 | LONGSHOR | 1 | 150 | 0.035982 | west | -0.0034551 | 0.08784 | 0.00061148 | 0.048777 | 0.00061148 | west | N | 0.00061148 | 0
1058 | LONGSHOR | 2 | 220 | 0.035982 | west | -0.0034551 | 0.08784 | 0.00061148 | 0.048777 | 0.00061148 | west | N | 0.00061148 | 0
1061 | CIELOGEN | 1 | 99 | 0.036164 | west | -0.0032731 | 0.088022 | 0.00079348 | 0.048959 | 0.00079348 | west | N | 0.00079348 | 0
1062 | CIELOGEN | 1 | 61 | 0.036164 | west | -0.0032731 | 0.088022 | 0.00079348 | 0.048959 | 0.00079348 | west | N | 0.00079348 | 0
1068 | SCURRYCW | 1 | 141 | 0.036153 | west | -0.0032841 | 0.088011 | 0.00078248 | 0.048948 | 0.00078248 | west | N | 0.00078248 | 0
1069 | KINDERMG | 1 | 25 | 0.036164 | west | -0.0032731 | 0.088022 | 0.00079348 | 0.048959 | 0.00079348 | west | N | 0.00079348 | 0
1070 | KINDERMG | 1 | 45.7 | 0.036164 | west | -0.0032731 | 0.088022 | 0.00079348 | 0.048959 | 0.00079348 | west | N | 0.00079348 | 0
1071 | KINDERMG | 1 | 45.7 | 0.036164 | west | -0.0032731 | 0.088022 | 0.00079348 | 0.048959 | 0.00079348 | west | N | 0.00079348 | 0
1073 | SCURRYCW | 2 | 120 | 0.036153 | west | -0.0032841 | 0.088011 | 0.00078248 | 0.048948 | 0.00078248 | west | N | 0.00078248 | 0
1320 | BSP 1 | 1 | 25.8 | 0.035551 | west | -0.0038861 | 0.087409 | 0.00018048 | 0.048346 | 0.00018048 | west | N | 0.00018048 | 0
1326 | STANTONW | 1 | 100.5 | 0.035426 | west | -0.0040111 | 0.087284 | 5.5477e-05 | 0.048221 | 5.5477e-05 | west | N | 5.5477e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.035768 | west | -0.0036691 | 0.087626 | 0.00039748 | 0.048563 | 0.00039748 | west | N | 0.00039748 | 0
1328 | OCOTILLO | 1 | 58 | 0.035417 | west | -0.0040201 | 0.087275 | 4.6477e-05 | 0.048212 | 4.6477e-05 | west | N | 4.6477e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.03551 | west | -0.0039271 | 0.087368 | 0.00013948 | 0.048305 | 0.00013948 | west | N | 0.00013948 | 0
1343 | TRENTIPP | 1 | 150 | 0.036395 | west | -0.0030421 | 0.088253 | 0.0010245 | 0.04919 | 0.0010245 | west | N | 0.0010245 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.035056 | west | -0.0043811 | 0.086914 | -0.00031452 | 0.047851 | 0.00031452 | west | N | 0.00031452 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.035056 | west | -0.0043811 | 0.086914 | -0.00031452 | 0.047851 | 0.00031452 | west | N | 0.00031452 | 0
1354 | AEPWIND_ | 1 | 101 | 0.036395 | west | -0.0030421 | 0.088253 | 0.0010245 | 0.04919 | 0.0010245 | west | N | 0.0010245 | 0
1360 | GUNSIGHT | 1 | 120 | 0.035785 | west | -0.0036521 | 0.087643 | 0.00041448 | 0.04858 | 0.00041448 | west | N | 0.00041448 | 0
1432 | GRHAMSES | 2 | 366 | 0.039567 | north | 0.00012989 | 0.091425 | 0.0041965 | 0.052362 | 0.00012989 | North | N | 0.00012989 | 0
1433 | GRHAMSES | 1 | 242 | 0.039643 | north | 0.00020589 | 0.091501 | 0.0042725 | 0.052438 | 0.00020589 | North | N | 0.00020589 | 0
1437 | MESQUITW | 1 | 400 | 0.037834 | west | -0.0016031 | 0.089692 | 0.0024635 | 0.050629 | 0.0016031 | North | Y | 0.0024635 | 0.34415
1438 | MESQUITW | 1 | 236 | 0.037836 | west | -0.0016011 | 0.089694 | 0.0024655 | 0.050631 | 0.0016011 | North | Y | 0.0024655 | 0.20399
1442 | COKFIELD | 1 | 165 | 0.038251 | west | -0.0011861 | 0.090109 | 0.0028805 | 0.051046 | 0.0011861 | North | Y | 0.0028805 | 0.27957
1453 | WCPWRCO_ | 1 | 204 | 0.040514 | north | 0.0010769 | 0.092372 | 0.0051435 | 0.053309 | 0.0010769 | North | N | 0.0010769 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.040514 | north | 0.0010769 | 0.092372 | 0.0051435 | 0.053309 | 0.0010769 | North | N | 0.0010769 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.040514 | north | 0.0010769 | 0.092372 | 0.0051435 | 0.053309 | 0.0010769 | North | N | 0.0010769 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.039658 | west | 0.00022089 | 0.091516 | 0.0042875 | 0.052453 | 0.00022089 | North | Y | 0.0042875 | 0.081332
1479 | WFCOGEN_ | 2 | 20 | 0.039658 | west | 0.00022089 | 0.091516 | 0.0042875 | 0.052453 | 0.00022089 | North | Y | 0.0042875 | 0.081332
1482 | WFCOGEN_ | 1 | 20 | 0.039658 | west | 0.00022089 | 0.091516 | 0.0042875 | 0.052453 | 0.00022089 | North | Y | 0.0042875 | 0.081332
1482 | WFCOGEN_ | 2 | 17 | 0.039658 | west | 0.00022089 | 0.091516 | 0.0042875 | 0.052453 | 0.00022089 | North | Y | 0.0042875 | 0.069132
1600 | BARTNWND | 1 | 120 | 0.040667 | north | 0.0012299 | 0.092525 | 0.0052965 | 0.053462 | 0.0012299 | North | N | 0.0012299 | 0
1643 | SLSTR1PP | 1 | 60 | 0.041323 | north | 0.0018859 | 0.093181 | 0.0059525 | 0.054118 | 0.0018859 | North | N | 0.0018859 | 0
1675 | PEC_1G | 1 | 75 | 0.040623 | north | 0.0011859 | 0.092481 | 0.0052525 | 0.053418 | 0.0011859 | North | N | 0.0011859 | 0
1676 | PEC_2G | 2 | 79.6 | 0.040623 | north | 0.0011859 | 0.092481 | 0.0052525 | 0.053418 | 0.0011859 | North | N | 0.0011859 | 0
1677 | PEC_3G | 3 | 88.4 | 0.040623 | north | 0.0011859 | 0.092481 | 0.0052525 | 0.053418 | 0.0011859 | North | N | 0.0011859 | 0
1678 | LAMARPWR | 1 | 160 | 0.040643 | north | 0.0012059 | 0.092501 | 0.0052725 | 0.053438 | 0.0012059 | North | N | 0.0012059 | 0
1679 | LAMARPWR | 2 | 156 | 0.040643 | north | 0.0012059 | 0.092501 | 0.0052725 | 0.053438 | 0.0012059 | North | N | 0.0012059 | 0
1680 | LAMARPWR | 3 | 196 | 0.040643 | north | 0.0012059 | 0.092501 | 0.0052725 | 0.053438 | 0.0012059 | North | N | 0.0012059 | 0
1681 | LAMARPWR | 4 | 156 | 0.040643 | north | 0.0012059 | 0.092501 | 0.0052725 | 0.053438 | 0.0012059 | North | N | 0.0012059 | 0
1682 | LAMARPWR | 5 | 157 | 0.040643 | north | 0.0012059 | 0.092501 | 0.0052725 | 0.053438 | 0.0012059 | North | N | 0.0012059 | 0
1683 | LAMARPWR | 6 | 198 | 0.040643 | north | 0.0012059 | 0.092501 | 0.0052725 | 0.053438 | 0.0012059 | North | N | 0.0012059 | 0
1687 | VALLEY_1 | 1 | 170 | 0.040698 | north | 0.0012609 | 0.092556 | 0.0053275 | 0.053493 | 0.0012609 | North | N | 0.0012609 | 0
1688 | VALLEY_2 | 2 | 520 | 0.040698 | north | 0.0012609 | 0.092556 | 0.0053275 | 0.053493 | 0.0012609 | North | N | 0.0012609 | 0
1689 | VALLEY_3 | 3 | 370 | 0.040665 | north | 0.0012279 | 0.092523 | 0.0052945 | 0.05346 | 0.0012279 | North | N | 0.0012279 | 0
1701 | MOSES_1G | 1 | 558 | 0.040608 | north | 0.0011709 | 0.092466 | 0.0052375 | 0.053403 | 0.0011709 | North | N | 0.0011709 | 0
1702 | MOSES_2G | 2 | 579 | 0.040608 | north | 0.0011709 | 0.092466 | 0.0052375 | 0.053403 | 0.0011709 | North | N | 0.0011709 | 0
1703 | MOSES_3G | 3 | 808 | 0.040608 | north | 0.0011709 | 0.092466 | 0.0052375 | 0.053403 | 0.0011709 | North | N | 0.0011709 | 0
1861 | EAGLEMNT | MB | 112 | 0.041459 | north | 0.0020219 | 0.093317 | 0.0060885 | 0.054254 | 0.0020219 | North | N | 0.0020219 | 0
1862 | EAGLEMNT | MB | 100 | 0.041459 | north | 0.0020219 | 0.093317 | 0.0060885 | 0.054254 | 0.0020219 | North | N | 0.0020219 | 0
1863 | EAGLEMNT | MB | 378 | 0.041459 | north | 0.0020219 | 0.093317 | 0.0060885 | 0.054254 | 0.0020219 | North | N | 0.0020219 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.041761 | north | 0.0023239 | 0.093619 | 0.0063905 | 0.054556 | 0.0023239 | North | N | 0.0023239 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.041761 | north | 0.0023239 | 0.093619 | 0.0063905 | 0.054556 | 0.0023239 | North | N | 0.0023239 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.041761 | north | 0.0023239 | 0.093619 | 0.0063905 | 0.054556 | 0.0023239 | North | N | 0.0023239 | 0
1889 | DECRDOVA | MB | 770 | 0.041902 | north | 0.0024649 | 0.09376 | 0.0065315 | 0.054697 | 0.0024649 | North | N | 0.0024649 | 0
1892 | DECRDOVA | A | 70 | 0.042559 | north | 0.0031219 | 0.094417 | 0.0071885 | 0.055354 | 0.0031219 | North | N | 0.0031219 | 0
1893 | DECRDOVA | B | 69 | 0.042559 | north | 0.0031219 | 0.094417 | 0.0071885 | 0.055354 | 0.0031219 | North | N | 0.0031219 | 0
1894 | DECRDOVA | C | 69 | 0.042559 | north | 0.0031219 | 0.094417 | 0.0071885 | 0.055354 | 0.0031219 | North | N | 0.0031219 | 0
1895 | DECRDOVA | D | 68 | 0.042559 | north | 0.0031219 | 0.094417 | 0.0071885 | 0.055354 | 0.0031219 | North | N | 0.0031219 | 0
1898 | COMCHEPK | 1 | 1157 | 0.041655 | north | 0.0022179 | 0.093513 | 0.0062845 | 0.05445 | 0.0022179 | North | N | 0.0022179 | 0
1899 | COMCHEPK | 2 | 1158 | 0.041655 | north | 0.0022179 | 0.093513 | 0.0062845 | 0.05445 | 0.0022179 | North | N | 0.0022179 | 0
1937 | MDLTHELP | 5 | 224 | 0.043579 | north | 0.0041419 | 0.095437 | 0.0082085 | 0.056374 | 0.0041419 | North | N | 0.0041419 | 0
1938 | MDLTHELP | 6 | 226 | 0.043579 | north | 0.0041419 | 0.095437 | 0.0082085 | 0.056374 | 0.0041419 | North | N | 0.0041419 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.043463 | north | 0.0040259 | 0.095321 | 0.0080925 | 0.056258 | 0.0040259 | North | N | 0.0040259 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.043463 | north | 0.0040259 | 0.095321 | 0.0080925 | 0.056258 | 0.0040259 | North | N | 0.0040259 | 0
1943 | MDLTHELP | 3 | 212 | 0.043579 | north | 0.0041419 | 0.095437 | 0.0082085 | 0.056374 | 0.0041419 | North | N | 0.0041419 | 0
1944 | MDLTHELP | 4 | 211 | 0.043579 | north | 0.0041419 | 0.095437 | 0.0082085 | 0.056374 | 0.0041419 | North | N | 0.0041419 | 0
1947 | HANDLEY_ | 3 | 395 | 0.042106 | north | 0.0026689 | 0.093964 | 0.0067355 | 0.054901 | 0.0026689 | North | N | 0.0026689 | 0
1948 | HANDLEY_ | 4 | 435 | 0.042051 | north | 0.0026139 | 0.093909 | 0.0066805 | 0.054846 | 0.0026139 | North | N | 0.0026139 | 0
1949 | HANDLEY_ | 5 | 435 | 0.042106 | north | 0.0026689 | 0.093964 | 0.0067355 | 0.054901 | 0.0026689 | North | N | 0.0026689 | 0
2371 | COLLIN_1 | MB | 138 | 0.040876 | north | 0.0014389 | 0.092734 | 0.0055055 | 0.053671 | 0.0014389 | North | N | 0.0014389 | 0
2413 | MTCK6_G | 6 | 118 | 0.041208 | north | 0.0017709 | 0.093066 | 0.0058375 | 0.054003 | 0.0017709 | North | N | 0.0017709 | 0
2414 | MTCK7_G | 7 | 115 | 0.041208 | north | 0.0017709 | 0.093066 | 0.0058375 | 0.054003 | 0.0017709 | North | N | 0.0017709 | 0
2417 | MTCK8_G | 8 | 556 | 0.041208 | north | 0.0017709 | 0.093066 | 0.0058375 | 0.054003 | 0.0017709 | North | N | 0.0017709 | 0
2451 | LKHB1_G | 1 | 388 | 0.040607 | north | 0.0011699 | 0.092465 | 0.0052365 | 0.053402 | 0.0011699 | North | N | 0.0011699 | 0
2452 | LKHB2_G | 2 | 515 | 0.040607 | north | 0.0011699 | 0.092465 | 0.0052365 | 0.053402 | 0.0011699 | North | N | 0.0011699 | 0
3097 | MARTLAKE | 1 | 785 | 0.039212 | north | -0.00022511 | 0.09107 | 0.0038415 | 0.052007 | 0.00022511 | North | N | 0.00022511 | 0
3098 | MARTLAKE | 2 | 795 | 0.039212 | north | -0.00022511 | 0.09107 | 0.0038415 | 0.052007 | 0.00022511 | North | N | 0.00022511 | 0
3099 | MARTLAKE | 3 | 780 | 0.039212 | north | -0.00022511 | 0.09107 | 0.0038415 | 0.052007 | 0.00022511 | North | N | 0.00022511 | 0
3107 | STRYKER_ | 1 | 182 | 0.03887 | north | -0.00056711 | 0.090728 | 0.0034995 | 0.051665 | 0.00056711 | North | N | 0.00056711 | 0
3108 | STRYKER_ | 2 | 484 | 0.03887 | north | -0.00056711 | 0.090728 | 0.0034995 | 0.051665 | 0.00056711 | North | N | 0.00056711 | 0
3126 | TRINIDAD | 1 | 224 | 0.041014 | north | 0.0015769 | 0.092872 | 0.0056435 | 0.053809 | 0.0015769 | North | N | 0.0015769 | 0
3309 | ASPN_G | 1 | 50 | 0.038883 | north | -0.00055411 | 0.090741 | 0.0035125 | 0.051678 | 0.00055411 | North | N | 0.00055411 | 0
3348 | CHAMPION | MB | 42 | 0.038901 | north | -0.00053611 | 0.090759 | 0.0035305 | 0.051696 | 0.00053611 | North | N | 0.00053611 | 0
3381 | BBRN_1G | 1 | 615 | 0.036605 | north | -0.0028321 | 0.088463 | 0.0012345 | 0.0494 | 0.0012345 | west | Y | 0.0028321 | 0.98254
3382 | BBRN_2G | 2 | 587 | 0.036605 | north | -0.0028321 | 0.088463 | 0.0012345 | 0.0494 | 0.0012345 | west | Y | 0.0028321 | 0.93781
3403 | THOUSE_1 | MB | 537 | 0.061253 | north | 0.021816 | 0.11311 | 0.025882 | 0.074048 | 0.021816 | North | N | 0.021816 | 0
3404 | THOUSE_2 | 2 | 787 | 0.061253 | north | 0.021816 | 0.11311 | 0.025882 | 0.074048 | 0.021816 | North | N | 0.021816 | 0
3416 | LAKE_CRK | MB | 75 | 0.061576 | north | 0.022139 | 0.11343 | 0.026205 | 0.074371 | 0.022139 | North | N | 0.022139 | 0
3417 | LAKE_CRK | MB | 222 | 0.061576 | north | 0.022139 | 0.11343 | 0.026205 | 0.074371 | 0.022139 | North | N | 0.022139 | 0
3432 | SANDOW_4 | 4 | 569 | 0.088554 | south | 0.049117 | 0.14041 | 0.053183 | 0.10135 | 0.049117 | North | Y | 0.14041 | 51.9468
5026 | BRAUNIG_ | 1 | 209 | -0.058138 | south | -0.097575 | -0.0062801 | -0.093509 | -0.045343 | 0.0062801 | south | N | 0.0062801 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.058138 | south | -0.097575 | -0.0062801 | -0.093509 | -0.045343 | 0.0062801 | south | N | 0.0062801 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.058081 | south | -0.097518 | -0.0062231 | -0.093452 | -0.045286 | 0.0062231 | south | N | 0.0062231 | 0
5031 | BRA_VHBC | 1 | 46 | -0.058138 | south | -0.097575 | -0.0062801 | -0.093509 | -0.045343 | 0.0062801 | south | N | 0.0062801 | 0
5032 | BRA_VHBC | 2 | 47 | -0.058138 | south | -0.097575 | -0.0062801 | -0.093509 | -0.045343 | 0.0062801 | south | N | 0.0062801 | 0
5033 | BRA_VHBC | 3 | 46 | -0.058138 | south | -0.097575 | -0.0062801 | -0.093509 | -0.045343 | 0.0062801 | south | N | 0.0062801 | 0
5034 | BRA_VHBC | 4 | 46 | -0.058138 | south | -0.097575 | -0.0062801 | -0.093509 | -0.045343 | 0.0062801 | south | N | 0.0062801 | 0
5111 | CALAVER_ | 1 | 424 | -0.05821 | south | -0.097647 | -0.0063521 | -0.093581 | -0.045415 | 0.0063521 | south | N | 0.0063521 | 0
5112 | CALAVER_ | 2 | 425 | -0.05821 | south | -0.097647 | -0.0063521 | -0.093581 | -0.045415 | 0.0063521 | south | N | 0.0063521 | 0
5264 | LEON_LCP | 3 | 58 | -0.057768 | south | -0.097205 | -0.0059101 | -0.093139 | -0.044973 | 0.0059101 | south | N | 0.0059101 | 0
5265 | LEON_LCP | 4 | 89 | -0.057768 | south | -0.097205 | -0.0059101 | -0.093139 | -0.044973 | 0.0059101 | south | N | 0.0059101 | 0
5266 | LEON_LCP | 1 | 44 | -0.057768 | south | -0.097205 | -0.0059101 | -0.093139 | -0.044973 | 0.0059101 | south | N | 0.0059101 | 0
5267 | LEON_LCP | 2 | 44 | -0.057768 | south | -0.097205 | -0.0059101 | -0.093139 | -0.044973 | 0.0059101 | south | N | 0.0059101 | 0
5268 | LEON_LCP | 3 | 43 | -0.057768 | south | -0.097205 | -0.0059101 | -0.093139 | -0.044973 | 0.0059101 | south | N | 0.0059101 | 0
5269 | LEON_LCP | 4 | 45 | -0.057768 | south | -0.097205 | -0.0059101 | -0.093139 | -0.044973 | 0.0059101 | south | N | 0.0059101 | 0
5396 | CALAVER_ | 1 | 412 | -0.0582 | south | -0.097637 | -0.0063421 | -0.093571 | -0.045405 | 0.0063421 | south | N | 0.0063421 | 0
5397 | CALAVER_ | 2 | 400 | -0.0582 | south | -0.097637 | -0.0063421 | -0.093571 | -0.045405 | 0.0063421 | south | N | 0.0063421 | 0
5401 | CALAVER_ | 1 | 546 | -0.057585 | south | -0.097022 | -0.0057271 | -0.092956 | -0.04479 | 0.0057271 | south | N | 0.0057271 | 0
5402 | CALAVER_ | 2 | 750 | -0.057585 | south | -0.097022 | -0.0057271 | -0.092956 | -0.04479 | 0.0057271 | south | N | 0.0057271 | 0
5436 | TUTTL_WB | MB | 61 | -0.058375 | south | -0.097812 | -0.0065171 | -0.093746 | -0.04558 | 0.0065171 | south | N | 0.0065171 | 0
5438 | TUTTL_WB | MB | 95 | -0.058375 | south | -0.097812 | -0.0065171 | -0.093746 | -0.04558 | 0.0065171 | south | N | 0.0065171 | 0
5439 | TUTTL_WB | MB | 151 | -0.058375 | south | -0.097812 | -0.0065171 | -0.093746 | -0.04558 | 0.0065171 | south | N | 0.0065171 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.057907 | south | -0.097344 | -0.0060491 | -0.093278 | -0.045112 | 0.0060491 | south | N | 0.0060491 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.057907 | south | -0.097344 | -0.0060491 | -0.093278 | -0.045112 | 0.0060491 | south | N | 0.0060491 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.057907 | south | -0.097344 | -0.0060491 | -0.093278 | -0.045112 | 0.0060491 | south | N | 0.0060491 | 0
5503 | RAYBURNG | 1 | 22 | -0.046129 | south | -0.085566 | 0.0057289 | -0.0815 | -0.033334 | 0.0057289 | south | N | 0.0057289 | 0
5505 | RAYBURNG | 1 | 11 | -0.046129 | south | -0.085566 | 0.0057289 | -0.0815 | -0.033334 | 0.0057289 | south | N | 0.0057289 | 0
5506 | RAYBURNG | 1 | 11 | -0.046129 | south | -0.085566 | 0.0057289 | -0.0815 | -0.033334 | 0.0057289 | south | N | 0.0057289 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.04656 | south | -0.085997 | 0.0052979 | -0.081931 | -0.033765 | 0.0052979 | south | N | 0.0052979 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.04656 | south | -0.085997 | 0.0052979 | -0.081931 | -0.033765 | 0.0052979 | south | N | 0.0052979 | 0
5511 | RAYBURNC | 1 | 46 | -0.04656 | south | -0.085997 | 0.0052979 | -0.081931 | -0.033765 | 0.0052979 | south | N | 0.0052979 | 0
5512 | RAYBURNC | 1 | 48 | -0.04656 | south | -0.085997 | 0.0052979 | -0.081931 | -0.033765 | 0.0052979 | south | N | 0.0052979 | 0
5728 | FALCONHY | 2 | 12 | -0.048967 | south | -0.088404 | 0.0028909 | -0.084338 | -0.036172 | 0.0028909 | south | N | 0.0028909 | 0
5729 | FALCONHY | 3 | 11 | -0.048967 | south | -0.088404 | 0.0028909 | -0.084338 | -0.036172 | 0.0028909 | south | N | 0.0028909 | 0
5890 | PEARSALL | 1 | 24 | -0.051454 | south | -0.090891 | 0.00040386 | -0.086825 | -0.038659 | 0.00040386 | south | N | 0.00040386 | 0
5891 | PEARSALL | 1 | 24 | -0.051454 | south | -0.090891 | 0.00040386 | -0.086825 | -0.038659 | 0.00040386 | south | N | 0.00040386 | 0
5892 | PEARSALL | 1 | 23 | -0.051454 | south | -0.090891 | 0.00040386 | -0.086825 | -0.038659 | 0.00040386 | south | N | 0.00040386 | 0
5903 | SANMIGUE | 1 | 396 | -0.054365 | south | -0.093802 | -0.0025071 | -0.089736 | -0.04157 | 0.0025071 | south | N | 0.0025071 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.029337 | houston | -0.068774 | 0.022521 | -0.064708 | -0.016542 | 0.016542 | houston | N | 0.016542 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.029337 | houston | -0.068774 | 0.022521 | -0.064708 | -0.016542 | 0.016542 | houston | N | 0.016542 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | -0.039437 | 0.051858 | -0.035371 | 0.012795 | 0.012795 | houston | Y | 0.039437 | 15.9852
5932 | SI_RAY9 | 9 | 38 | -0.048106 | south | -0.087543 | 0.0037519 | -0.083477 | -0.035311 | 0.0037519 | south | N | 0.0037519 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.048106 | south | -0.087543 | 0.0037519 | -0.083477 | -0.035311 | 0.0037519 | south | N | 0.0037519 | 0
5934 | SI_RAY5 | 5 | 15 | -0.048106 | south | -0.087543 | 0.0037519 | -0.083477 | -0.035311 | 0.0037519 | south | N | 0.0037519 | 0
5935 | SI_RAY10 | 10 | 47 | -0.048106 | south | -0.087543 | 0.0037519 | -0.083477 | -0.035311 | 0.0037519 | south | N | 0.0037519 | 0
6016 | SWMESA | 1 | 75 | 0.030908 | west | -0.0085291 | 0.082766 | -0.0044625 | 0.043703 | 0.0044625 | west | N | 0.0044625 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | -0.039437 | 0.051858 | -0.035371 | 0.012795 | 0.012795 | houston | Y | 0.035371 | 4.9666
6144 | MCADOO1A | 1 | 150 | 0.036711 | west | -0.0027261 | 0.088569 | 0.0013405 | 0.049506 | 0.0013405 | west | N | 0.0013405 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.034717 | west | -0.0047201 | 0.086575 | -0.00065352 | 0.047512 | 0.00065352 | west | N | 0.00065352 | 0
6476 | LANGFORD | 1 | 150 | 0.014596 | west | -0.024841 | 0.066454 | -0.020775 | 0.027391 | 0.020775 | west | N | 0.020775 | 0
6637 | SNYDERW1 | 1 | 63 | 0.036122 | west | -0.0033151 | 0.08798 | 0.00075148 | 0.048917 | 0.00075148 | west | N | 0.00075148 | 0
6752 | OKLA0A | 1 | 649.7 | 0.038593 | west | -0.00084411 | 0.090451 | 0.0032225 | 0.051388 | 0.00084411 | North | Y | 0.0032225 | 1.5452
6948 | DENISNDM | 1 | 40 | 0.040728 | north | 0.0012909 | 0.092586 | 0.0053575 | 0.053523 | 0.0012909 | North | N | 0.0012909 | 0
6948 | DENISNDM | 2 | 40 | 0.040728 | north | 0.0012909 | 0.092586 | 0.0053575 | 0.053523 | 0.0012909 | North | N | 0.0012909 | 0
7000 | L_FERGUS | 1 | 422 | -0.065216 | south | -0.10465 | -0.013358 | -0.10059 | -0.052421 | 0.013358 | south | N | 0.013358 | 0
7004 | L_SIMGID | 1 | 132 | -0.060432 | south | -0.099869 | -0.0085741 | -0.095803 | -0.047637 | 0.0085741 | south | N | 0.0085741 | 0
7005 | L_SIMGID | 2 | 134 | -0.060432 | south | -0.099869 | -0.0085741 | -0.095803 | -0.047637 | 0.0085741 | south | N | 0.0085741 | 0
7006 | L_SIMGID | 3 | 323 | -0.060432 | south | -0.099869 | -0.0085741 | -0.095803 | -0.047637 | 0.0085741 | south | N | 0.0085741 | 0
7007 | L_LOSTPI | 1 | 158 | -0.069182 | south | -0.10862 | -0.017324 | -0.10455 | -0.056387 | 0.017324 | south | N | 0.017324 | 0
7008 | L_LOSTPI | 2 | 160 | -0.069182 | south | -0.10862 | -0.017324 | -0.10455 | -0.056387 | 0.017324 | south | N | 0.017324 | 0
7009 | L_LOSTPI | 3 | 175 | -0.069182 | south | -0.10862 | -0.017324 | -0.10455 | -0.056387 | 0.017324 | south | N | 0.017324 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.062594 | south | -0.10203 | -0.010736 | -0.097965 | -0.049799 | 0.010736 | south | N | 0.010736 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.062594 | south | -0.10203 | -0.010736 | -0.097965 | -0.049799 | 0.010736 | south | N | 0.010736 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.06256 | south | -0.102 | -0.010702 | -0.097931 | -0.049765 | 0.010702 | south | N | 0.010702 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.063869 | south | -0.10331 | -0.012011 | -0.09924 | -0.051074 | 0.012011 | south | N | 0.012011 | 0
7015 | L_HAYSEN | 2 | 225 | -0.063869 | south | -0.10331 | -0.012011 | -0.09924 | -0.051074 | 0.012011 | south | N | 0.012011 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.063869 | south | -0.10331 | -0.012011 | -0.09924 | -0.051074 | 0.012011 | south | N | 0.012011 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.063869 | south | -0.10331 | -0.012011 | -0.09924 | -0.051074 | 0.012011 | south | N | 0.012011 | 0
7020 | L_AUSTPL | 1 | 8 | -0.10175 | south | -0.14119 | -0.049893 | -0.13712 | -0.088956 | 0.049893 | south | N | 0.049893 | 0
7020 | L_AUSTPL | 2 | 8 | -0.10175 | south | -0.14119 | -0.049893 | -0.13712 | -0.088956 | 0.049893 | south | N | 0.049893 | 0
7022 | L_BUCHAN | 1 | 18 | -0.055408 | south | -0.094845 | -0.0035501 | -0.090779 | -0.042613 | 0.0035501 | south | N | 0.0035501 | 0
7023 | L_BUCHAN | 2 | 18 | -0.055408 | south | -0.094845 | -0.0035501 | -0.090779 | -0.042613 | 0.0035501 | south | N | 0.0035501 | 0
7024 | L_BUCHAN | 3 | 15 | -0.055408 | south | -0.094845 | -0.0035501 | -0.090779 | -0.042613 | 0.0035501 | south | N | 0.0035501 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.056119 | south | -0.095556 | -0.0042611 | -0.09149 | -0.043324 | 0.0042611 | south | N | 0.0042611 | 0
7028 | L_MARBFA | 1 | 18 | -0.073263 | south | -0.1127 | -0.021405 | -0.10863 | -0.060468 | 0.021405 | south | N | 0.021405 | 0
7029 | L_MARBFA | 2 | 18 | -0.073263 | south | -0.1127 | -0.021405 | -0.10863 | -0.060468 | 0.021405 | south | N | 0.021405 | 0
7031 | L_MARSFO | 1 | 35 | -0.09151 | south | -0.13095 | -0.039652 | -0.12688 | -0.078715 | 0.039652 | south | N | 0.039652 | 0
7032 | L_MARSFO | 2 | 34 | -0.09151 | south | -0.13095 | -0.039652 | -0.12688 | -0.078715 | 0.039652 | south | N | 0.039652 | 0
7033 | L_MARSFO | 3 | 35 | -0.09151 | south | -0.13095 | -0.039652 | -0.12688 | -0.078715 | 0.039652 | south | N | 0.039652 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.065872 | south | -0.10531 | -0.014014 | -0.10124 | -0.053077 | 0.014014 | south | N | 0.014014 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.065872 | south | -0.10531 | -0.014014 | -0.10124 | -0.053077 | 0.014014 | south | N | 0.014014 | 0
7038 | L_DELAWA | 1 | 35 | 0.034742 | west | -0.0046951 | 0.0866 | -0.00062852 | 0.047537 | 0.00062852 | west | N | 0.00062852 | 0
7038 | L_DELAWA | 2 | 30 | 0.034742 | west | -0.0046951 | 0.0866 | -0.00062852 | 0.047537 | 0.00062852 | west | N | 0.00062852 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.058762 | south | -0.098199 | -0.0069041 | -0.094133 | -0.045967 | 0.0069041 | south | N | 0.0069041 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.058762 | south | -0.098199 | -0.0069041 | -0.094133 | -0.045967 | 0.0069041 | south | N | 0.0069041 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.058762 | south | -0.098199 | -0.0069041 | -0.094133 | -0.045967 | 0.0069041 | south | N | 0.0069041 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.058762 | south | -0.098199 | -0.0069041 | -0.094133 | -0.045967 | 0.0069041 | south | N | 0.0069041 | 0
7487 | L_CANYHY | 1 | 6 | -0.069438 | south | -0.10888 | -0.01758 | -0.10481 | -0.056643 | 0.01758 | south | N | 0.01758 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.062708 | south | -0.10215 | -0.01085 | -0.098079 | -0.049913 | 0.01085 | south | N | 0.01085 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.062708 | south | -0.10215 | -0.01085 | -0.098079 | -0.049913 | 0.01085 | south | N | 0.01085 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.062708 | south | -0.10215 | -0.01085 | -0.098079 | -0.049913 | 0.01085 | south | N | 0.01085 | 0
7609 | L_SCHUMA | 1 | 4 | -0.06179 | south | -0.10123 | -0.0099321 | -0.097161 | -0.048995 | 0.0099321 | south | N | 0.0099321 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.061252 | south | -0.10069 | -0.0093941 | -0.096623 | -0.048457 | 0.0093941 | south | N | 0.0093941 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.061252 | south | -0.10069 | -0.0093941 | -0.096623 | -0.048457 | 0.0093941 | south | N | 0.0093941 | 0
7800 | L_GUADGE | 1 | 147 | -0.059527 | south | -0.098964 | -0.0076691 | -0.094898 | -0.046732 | 0.0076691 | south | N | 0.0076691 | 0
7801 | L_GUADGE | 2 | 138 | -0.059527 | south | -0.098964 | -0.0076691 | -0.094898 | -0.046732 | 0.0076691 | south | N | 0.0076691 | 0
7802 | L_GUADGE | 3 | 140 | -0.059527 | south | -0.098964 | -0.0076691 | -0.094898 | -0.046732 | 0.0076691 | south | N | 0.0076691 | 0
7803 | L_GUADGE | 4 | 147 | -0.059527 | south | -0.098964 | -0.0076691 | -0.094898 | -0.046732 | 0.0076691 | south | N | 0.0076691 | 0
7804 | L_GUADGE | 5 | 182 | -0.059527 | south | -0.098964 | -0.0076691 | -0.094898 | -0.046732 | 0.0076691 | south | N | 0.0076691 | 0
7805 | L_GUADGE | 6 | 198 | -0.059527 | south | -0.098964 | -0.0076691 | -0.094898 | -0.046732 | 0.0076691 | south | N | 0.0076691 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.072694 | south | -0.11213 | -0.020836 | -0.10806 | -0.059899 | 0.020836 | south | N | 0.020836 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.072694 | south | -0.11213 | -0.020836 | -0.10806 | -0.059899 | 0.020836 | south | N | 0.020836 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.072694 | south | -0.11213 | -0.020836 | -0.10806 | -0.059899 | 0.020836 | south | N | 0.020836 | 0
7810 | L_RIONOG | 1 | 142 | -0.06169 | south | -0.10113 | -0.0098321 | -0.097061 | -0.048895 | 0.0098321 | south | N | 0.0098321 | 0
7811 | L_RIONOG | 2 | 145 | -0.06169 | south | -0.10113 | -0.0098321 | -0.097061 | -0.048895 | 0.0098321 | south | N | 0.0098321 | 0
7812 | L_RIONOG | 3 | 151 | -0.06169 | south | -0.10113 | -0.0098321 | -0.097061 | -0.048895 | 0.0098321 | south | N | 0.0098321 | 0
7813 | L_RIONOG | 4 | 290 | -0.06169 | south | -0.10113 | -0.0098321 | -0.097061 | -0.048895 | 0.0098321 | south | N | 0.0098321 | 0
8032 | AMISTADH | 1 | 33 | -0.028987 | south | -0.068424 | 0.022871 | -0.064358 | -0.016192 | 0.016192 | houston | Y | 0.022871 | 0.22041
8033 | AMISTADH | 2 | 25 | -0.028987 | south | -0.068424 | 0.022871 | -0.064358 | -0.016192 | 0.016192 | houston | Y | 0.022871 | 0.16697
8048 | FALCONHY | 1 | 12 | -0.048967 | south | -0.088404 | 0.0028909 | -0.084338 | -0.036172 | 0.0028909 | south | N | 0.0028909 | 0
8066 | DUP1V#1 | 1 | 73 | -0.046635 | south | -0.086072 | 0.0052229 | -0.082006 | -0.03384 | 0.0052229 | south | N | 0.0052229 | 0
8134 | FOR69CG0 | 1 | 79 | -0.04348 | south | -0.082917 | 0.0083779 | -0.078851 | -0.030685 | 0.0083779 | south | N | 0.0083779 | 0
8138 | FOR69CG0 | 2 | 81 | -0.04348 | south | -0.082917 | 0.0083779 | -0.078851 | -0.030685 | 0.0083779 | south | N | 0.0083779 | 0
8139 | JOS #1 | MB | 255 | 0 | south | -0.039437 | 0.051858 | -0.035371 | 0.012795 | 0.012795 | houston | Y | 0.051858 | 9.961
8147 | UCAR #2 | 10 | 28 | -0.045165 | south | -0.084602 | 0.0066929 | -0.080536 | -0.03237 | 0.0066929 | south | N | 0.0066929 | 0
8148 | UCAR #1 | 2 | 7 | -0.045165 | south | -0.084602 | 0.0066929 | -0.080536 | -0.03237 | 0.0066929 | south | N | 0.0066929 | 0
8153 | FOR69CG0 | 3 | 79 | -0.04348 | south | -0.082917 | 0.0083779 | -0.078851 | -0.030685 | 0.0083779 | south | N | 0.0083779 | 0
8154 | FOR69CG0 | 4 | 80 | -0.04348 | south | -0.082917 | 0.0083779 | -0.078851 | -0.030685 | 0.0083779 | south | N | 0.0083779 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.04348 | south | -0.082917 | 0.0083779 | -0.078851 | -0.030685 | 0.0083779 | south | N | 0.0083779 | 0
8156 | FOR69CG0 | 6 | 25 | -0.04348 | south | -0.082917 | 0.0083779 | -0.078851 | -0.030685 | 0.0083779 | south | N | 0.0083779 | 0
8157 | FOR69CG0 | 7 | 46 | -0.04348 | south | -0.082917 | 0.0083779 | -0.078851 | -0.030685 | 0.0083779 | south | N | 0.0083779 | 0
8161 | COLETOU1 | 1 | 629 | -0.049622 | south | -0.089059 | 0.0022359 | -0.084993 | -0.036827 | 0.0022359 | south | N | 0.0022359 | 0
8173 | VICEC51A | 5 | 144 | -0.047171 | south | -0.086608 | 0.0046869 | -0.082542 | -0.034376 | 0.0046869 | south | N | 0.0046869 | 0
8174 | VICEC61A | 6 | 188 | -0.047171 | south | -0.086608 | 0.0046869 | -0.082542 | -0.034376 | 0.0046869 | south | N | 0.0046869 | 0
8189 | CUERO 2 | 1 | 12 | -0.056951 | south | -0.096388 | -0.0050931 | -0.092322 | -0.044156 | 0.0050931 | south | N | 0.0050931 | 0
8262 | ELPS | 1 | 6 | -0.035961 | south | -0.075398 | 0.015897 | -0.071332 | -0.023166 | 0.015897 | south | N | 0.015897 | 0
8285 | LAR #1 | MB | 32 | 0 | south | -0.039437 | 0.051858 | -0.035371 | 0.012795 | 0.012795 | houston | Y | 0.051858 | 1.25
8287 | LAR #2 | MB | 32 | 0 | south | -0.039437 | 0.051858 | -0.035371 | 0.012795 | 0.012795 | houston | Y | 0.051858 | 1.25
8288 | LAR #3 | MB | 105 | 0 | south | -0.039437 | 0.051858 | -0.035371 | 0.012795 | 0.012795 | houston | Y | 0.051858 | 4.1016
8388 | BATES0A | MB | 70 | 0 | south | -0.039437 | 0.051858 | -0.035371 | 0.012795 | 0.012795 | houston | Y | 0.051858 | 2.7344
8393 | BATES0B | MB | 110 | 0 | south | -0.039437 | 0.051858 | -0.035371 | 0.012795 | 0.012795 | houston | Y | 0.051858 | 4.2969
8442 | NBEC71A | 1 | 336 | -0.047561 | south | -0.086998 | 0.0042969 | -0.082932 | -0.034766 | 0.0042969 | south | N | 0.0042969 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | -0.039437 | 0.051858 | -0.035371 | 0.012795 | 0.012795 | houston | Y | 0.051858 | 0.78125
8457 | COSW#2 | 2 | 14 | 0 | south | -0.039437 | 0.051858 | -0.035371 | 0.012795 | 0.012795 | houston | Y | 0.051858 | 0.54688
8459 | B_DAVIS1 | 1 | 334 | -0.047675 | south | -0.087112 | 0.0041829 | -0.083046 | -0.03488 | 0.0041829 | south | N | 0.0041829 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.047675 | south | -0.087112 | 0.0041829 | -0.083046 | -0.03488 | 0.0041829 | south | N | 0.0041829 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.047744 | south | -0.087181 | 0.0041139 | -0.083115 | -0.034949 | 0.0041139 | south | N | 0.0041139 | 0
8506 | VAL #1 | 1 | 25 | -0.047691 | south | -0.087128 | 0.0041669 | -0.083062 | -0.034896 | 0.0041669 | south | N | 0.0041669 | 0
8507 | VAL #2 | 2 | 25 | -0.047691 | south | -0.087128 | 0.0041669 | -0.083062 | -0.034896 | 0.0041669 | south | N | 0.0041669 | 0
8511 | OXY_CC0A | 1 | 38 | -0.047741 | south | -0.087178 | 0.0041169 | -0.083112 | -0.034946 | 0.0041169 | south | N | 0.0041169 | 0
8517 | CELANEBI | 1 | 29 | -0.047987 | south | -0.087424 | 0.0038709 | -0.083358 | -0.035192 | 0.0038709 | south | N | 0.0038709 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.047567 | south | -0.087004 | 0.0042909 | -0.082938 | -0.034772 | 0.0042909 | south | N | 0.0042909 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.047567 | south | -0.087004 | 0.0042909 | -0.082938 | -0.034772 | 0.0042909 | south | N | 0.0042909 | 0
8562 | CNOPST1 | 3 | 153 | -0.047567 | south | -0.087004 | 0.0042909 | -0.082938 | -0.034772 | 0.0042909 | south | N | 0.0042909 | 0
8926 | LGE_GT10 | 1 | 158 | -0.047045 | south | -0.086482 | 0.0048129 | -0.082416 | -0.03425 | 0.0048129 | south | N | 0.0048129 | 0
8927 | LGE_GT20 | 2 | 153 | -0.047045 | south | -0.086482 | 0.0048129 | -0.082416 | -0.03425 | 0.0048129 | south | N | 0.0048129 | 0
8928 | LGE_STG0 | 3 | 100 | -0.047045 | south | -0.086482 | 0.0048129 | -0.082416 | -0.03425 | 0.0048129 | south | N | 0.0048129 | 0
8930 | ICPGN10A | 1 | 145 | -0.047045 | south | -0.086482 | 0.0048129 | -0.082416 | -0.03425 | 0.0048129 | south | N | 0.0048129 | 0
8931 | ICPGN20A | 2 | 147 | -0.047045 | south | -0.086482 | 0.0048129 | -0.082416 | -0.03425 | 0.0048129 | south | N | 0.0048129 | 0
8932 | ICPGN30A | 3 | 127 | -0.047045 | south | -0.086482 | 0.0048129 | -0.082416 | -0.03425 | 0.0048129 | south | N | 0.0048129 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.048312 | south | -0.087749 | 0.0035459 | -0.083683 | -0.035517 | 0.0035459 | south | N | 0.0035459 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.048312 | south | -0.087749 | 0.0035459 | -0.083683 | -0.035517 | 0.0035459 | south | N | 0.0035459 | 0
8935 | FGNTS201 | 3 | 173 | -0.048312 | south | -0.087749 | 0.0035459 | -0.083683 | -0.035517 | 0.0035459 | south | N | 0.0035459 | 0
8936 | MVGN#1 | 1 | 207 | -0.048207 | south | -0.087644 | 0.0036509 | -0.083578 | -0.035412 | 0.0036509 | south | N | 0.0036509 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.048207 | south | -0.087644 | 0.0036509 | -0.083578 | -0.035412 | 0.0036509 | south | N | 0.0036509 | 0
8938 | MVGN#3 | 3 | 242 | -0.048207 | south | -0.087644 | 0.0036509 | -0.083578 | -0.035412 | 0.0036509 | south | N | 0.0036509 | 0
8981 | HECN1 | 1 | 144 | -0.048205 | south | -0.087642 | 0.0036529 | -0.083576 | -0.03541 | 0.0036529 | south | N | 0.0036529 | 0
8982 | HECN2 | 2 | 144 | -0.048205 | south | -0.087642 | 0.0036529 | -0.083576 | -0.03541 | 0.0036529 | south | N | 0.0036529 | 0
8983 | HECN3 | 3 | 171 | -0.048205 | south | -0.087642 | 0.0036529 | -0.083576 | -0.03541 | 0.0036529 | south | N | 0.0036529 | 0
9000 | DECKR_G1 | 1 | 310 | -0.10095 | south | -0.14038 | -0.049089 | -0.13632 | -0.088152 | 0.049089 | south | N | 0.049089 | 0
9001 | DECKR_G2 | 2 | 413 | -0.10095 | south | -0.14038 | -0.049089 | -0.13632 | -0.088152 | 0.049089 | south | N | 0.049089 | 0
9002 | DECKR_G3 | 3 | 42 | -0.098803 | south | -0.13824 | -0.046945 | -0.13417 | -0.086008 | 0.046945 | south | N | 0.046945 | 0
9003 | DECKR_G4 | 4 | 44 | -0.098803 | south | -0.13824 | -0.046945 | -0.13417 | -0.086008 | 0.046945 | south | N | 0.046945 | 0
9004 | DECKR_G5 | 5 | 44 | -0.098803 | south | -0.13824 | -0.046945 | -0.13417 | -0.086008 | 0.046945 | south | N | 0.046945 | 0
9005 | DECKR_G6 | 6 | 47 | -0.098803 | south | -0.13824 | -0.046945 | -0.13417 | -0.086008 | 0.046945 | south | N | 0.046945 | 0
9016 | SANDH_G1 | 1 | 49 | -0.09592 | south | -0.13536 | -0.044062 | -0.13129 | -0.083125 | 0.044062 | south | N | 0.044062 | 0
9017 | SANDH_G2 | 2 | 46 | -0.09592 | south | -0.13536 | -0.044062 | -0.13129 | -0.083125 | 0.044062 | south | N | 0.044062 | 0
9018 | SANDH_G3 | 3 | 46 | -0.09592 | south | -0.13536 | -0.044062 | -0.13129 | -0.083125 | 0.044062 | south | N | 0.044062 | 0
9019 | SANDH_G4 | 4 | 47 | -0.09592 | south | -0.13536 | -0.044062 | -0.13129 | -0.083125 | 0.044062 | south | N | 0.044062 | 0
9020 | SANDHG5A | 5A | 154 | -0.09592 | south | -0.13536 | -0.044062 | -0.13129 | -0.083125 | 0.044062 | south | N | 0.044062 | 0
9021 | SANDHG5C | 5C | 148 | -0.09592 | south | -0.13536 | -0.044062 | -0.13129 | -0.083125 | 0.044062 | south | N | 0.044062 | 0
9022 | SANDH_G6 | 6 | 48 | -0.09592 | south | -0.13536 | -0.044062 | -0.13129 | -0.083125 | 0.044062 | south | N | 0.044062 | 0
9023 | SANDH_G7 | 7 | 48 | -0.09592 | south | -0.13536 | -0.044062 | -0.13129 | -0.083125 | 0.044062 | south | N | 0.044062 | 0
11001 | NAV1CT | 1 | 70 | 0.035389 | west | -0.0040481 | 0.087247 | 1.8477e-05 | 0.048184 | 1.8477e-05 | west | N | 1.8477e-05 | 0
11009 | NAV2CT | 1 | 70 | 0.035389 | west | -0.0040481 | 0.087247 | 1.8477e-05 | 0.048184 | 1.8477e-05 | west | N | 1.8477e-05 | 0
11011 | NAV3ST | 1 | 92.8 | 0.035389 | west | -0.0040481 | 0.087247 | 1.8477e-05 | 0.048184 | 1.8477e-05 | west | N | 1.8477e-05 | 0
11012 | NAV4CT | 1 | 80 | 0.035389 | west | -0.0040481 | 0.087247 | 1.8477e-05 | 0.048184 | 1.8477e-05 | west | N | 1.8477e-05 | 0
11013 | NAV5CT | 1 | 80 | 0.035389 | west | -0.0040481 | 0.087247 | 1.8477e-05 | 0.048184 | 1.8477e-05 | west | N | 1.8477e-05 | 0
11014 | NAV6ST | 1 | 115 | 0.035389 | west | -0.0040481 | 0.087247 | 1.8477e-05 | 0.048184 | 1.8477e-05 | west | N | 1.8477e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.035383 | west | -0.0040541 | 0.087241 | 1.2477e-05 | 0.048178 | 1.2477e-05 | west | N | 1.2477e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.035383 | west | -0.0040541 | 0.087241 | 1.2477e-05 | 0.048178 | 1.2477e-05 | west | N | 1.2477e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.035383 | west | -0.0040541 | 0.087241 | 1.2477e-05 | 0.048178 | 1.2477e-05 | west | N | 1.2477e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.035383 | west | -0.0040541 | 0.087241 | 1.2477e-05 | 0.048178 | 1.2477e-05 | west | N | 1.2477e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.035383 | west | -0.0040541 | 0.087241 | 1.2477e-05 | 0.048178 | 1.2477e-05 | west | N | 1.2477e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.035383 | west | -0.0040541 | 0.087241 | 1.2477e-05 | 0.048178 | 1.2477e-05 | west | N | 1.2477e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.036586 | west | -0.0028511 | 0.088444 | 0.0012155 | 0.049381 | 0.0012155 | west | N | 0.0012155 | 0
11057 | CHAMPION | 1 | 126.5 | 0.036586 | west | -0.0028511 | 0.088444 | 0.0012155 | 0.049381 | 0.0012155 | west | N | 0.0012155 | 0
11058 | PYRON_1G | 1 | 249 | 0.036586 | west | -0.0028511 | 0.088444 | 0.0012155 | 0.049381 | 0.0012155 | west | N | 0.0012155 | 0
11059 | INADALE_ | 1 | 197 | 0.036586 | west | -0.0028511 | 0.088444 | 0.0012155 | 0.049381 | 0.0012155 | west | N | 0.0012155 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.035982 | west | -0.0034551 | 0.08784 | 0.00061148 | 0.048777 | 0.00061148 | west | N | 0.00061148 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.035982 | west | -0.0034551 | 0.08784 | 0.00061148 | 0.048777 | 0.00061148 | west | N | 0.00061148 | 0
11147 | NOTREES_ | 1 | 149 | 0.034859 | west | -0.0045781 | 0.086717 | -0.00051152 | 0.047654 | 0.00051152 | west | N | 0.00051152 | 0
11309 | BULLCREK | 1 | 180 | 0.035892 | west | -0.0035451 | 0.08775 | 0.00052148 | 0.048687 | 0.00052148 | west | N | 0.00052148 | 0
11310 | BULLCREK | 1 | 180 | 0.035892 | west | -0.0035451 | 0.08775 | 0.00052148 | 0.048687 | 0.00052148 | west | N | 0.00052148 | 0
11320 | COYOTE_1 | 1 | 225 | 0.035856 | west | -0.0035811 | 0.087714 | 0.00048548 | 0.048651 | 0.00048548 | west | N | 0.00048548 | 0
11415 | LORAINE_ | 1 | 125 | 0.036339 | west | -0.0030981 | 0.088197 | 0.00096848 | 0.049134 | 0.00096848 | west | N | 0.00096848 | 0
11416 | LORAINE_ | 1 | 125 | 0.036339 | west | -0.0030981 | 0.088197 | 0.00096848 | 0.049134 | 0.00096848 | west | N | 0.00096848 | 0
11691 | KMICHICT | 1 | 140 | 0.040665 | north | 0.0012279 | 0.092523 | 0.0052945 | 0.05346 | 0.0012279 | North | N | 0.0012279 | 0
11692 | KMICHICT | 2 | 141 | 0.040665 | north | 0.0012279 | 0.092523 | 0.0052945 | 0.05346 | 0.0012279 | North | N | 0.0012279 | 0
11693 | KMICHIST | 3 | 309 | 0.040665 | north | 0.0012279 | 0.092523 | 0.0052945 | 0.05346 | 0.0012279 | North | N | 0.0012279 | 0
11694 | KMICHICT | 4 | 143 | 0.040665 | north | 0.0012279 | 0.092523 | 0.0052945 | 0.05346 | 0.0012279 | North | N | 0.0012279 | 0
11695 | KMICHICT | 5 | 144 | 0.040665 | north | 0.0012279 | 0.092523 | 0.0052945 | 0.05346 | 0.0012279 | North | N | 0.0012279 | 0
11696 | KMICHIST | 6 | 310 | 0.040665 | north | 0.0012279 | 0.092523 | 0.0052945 | 0.05346 | 0.0012279 | North | N | 0.0012279 | 0
12322 | ENNSTRAC | 1 | 196 | 0.042065 | north | 0.0026279 | 0.093923 | 0.0066945 | 0.05486 | 0.0026279 | North | N | 0.0026279 | 0
12323 | ENNSTRAC | 2 | 111 | 0.042065 | north | 0.0026279 | 0.093923 | 0.0066945 | 0.05486 | 0.0026279 | North | N | 0.0026279 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.040888 | north | 0.0014509 | 0.092746 | 0.0055175 | 0.053683 | 0.0014509 | North | N | 0.0014509 | 0
12411 | FPLEFR1A | 1 | 161 | 0.040325 | north | 0.00088789 | 0.092183 | 0.0049545 | 0.05312 | 0.00088789 | North | N | 0.00088789 | 0
12412 | FPLEFR1B | 2 | 164 | 0.040325 | north | 0.00088789 | 0.092183 | 0.0049545 | 0.05312 | 0.00088789 | North | N | 0.00088789 | 0
12413 | FPLEFR1C | 3 | 164 | 0.040325 | north | 0.00088789 | 0.092183 | 0.0049545 | 0.05312 | 0.00088789 | North | N | 0.00088789 | 0
12414 | FPLEFR1S | 4 | 414 | 0.040325 | north | 0.00088789 | 0.092183 | 0.0049545 | 0.05312 | 0.00088789 | North | N | 0.00088789 | 0
12421 | FPLEFR2A | 1 | 162 | 0.040325 | north | 0.00088789 | 0.092183 | 0.0049545 | 0.05312 | 0.00088789 | North | N | 0.00088789 | 0
12422 | FPLEFR2B | 2 | 161 | 0.040325 | north | 0.00088789 | 0.092183 | 0.0049545 | 0.05312 | 0.00088789 | North | N | 0.00088789 | 0
12423 | FPLEFR2C | 3 | 163 | 0.040325 | north | 0.00088789 | 0.092183 | 0.0049545 | 0.05312 | 0.00088789 | North | N | 0.00088789 | 0
12424 | FPLEFR2S | 4 | 409 | 0.040325 | north | 0.00088789 | 0.092183 | 0.0049545 | 0.05312 | 0.00088789 | North | N | 0.00088789 | 0
12440 | PARKD_1S | 1 | 0 | 0.040722 | north | 0.0012849 | 0.09258 | 0.0053515 | 0.053517 | 0.0012849 | North | N | 0.0012849 | 0
12449 | PARKD_2S | 1 | 0 | 0.040722 | north | 0.0012849 | 0.09258 | 0.0053515 | 0.053517 | 0.0012849 | North | N | 0.0012849 | 0
13116 | TGATEWAY | 1 | 148 | 0.039047 | north | -0.00039011 | 0.090905 | 0.0036765 | 0.051842 | 0.00039011 | North | N | 0.00039011 | 0
13117 | TGATEWAY | 2 | 130 | 0.039047 | north | -0.00039011 | 0.090905 | 0.0036765 | 0.051842 | 0.00039011 | North | N | 0.00039011 | 0
13118 | TGATEWAY | 3 | 145 | 0.039047 | north | -0.00039011 | 0.090905 | 0.0036765 | 0.051842 | 0.00039011 | North | N | 0.00039011 | 0
13119 | TGATEWAY | 4 | 399 | 0.039047 | north | -0.00039011 | 0.090905 | 0.0036765 | 0.051842 | 0.00039011 | North | N | 0.00039011 | 0
13131 | CALFREST | 1 | 150.7 | 0.037024 | north | -0.0024131 | 0.088882 | 0.0016535 | 0.049819 | 0.0016535 | west | Y | 0.0024131 | 0.11448
13132 | CALFREST | 2 | 151 | 0.037024 | north | -0.0024131 | 0.088882 | 0.0016535 | 0.049819 | 0.0016535 | west | Y | 0.0024131 | 0.1147
13133 | CALFREST | 3 | 177.4 | 0.037024 | north | -0.0024131 | 0.088882 | 0.0016535 | 0.049819 | 0.0016535 | west | Y | 0.0024131 | 0.13476
13134 | CALFREST | 4 | 151.5 | 0.037107 | north | -0.0023301 | 0.088965 | 0.0017365 | 0.049902 | 0.0017365 | west | Y | 0.0023301 | 0.089935
13135 | CALFREST | 5 | 152.3 | 0.037107 | north | -0.0023301 | 0.088965 | 0.0017365 | 0.049902 | 0.0017365 | west | Y | 0.0023301 | 0.09041
13136 | CALFREST | 6 | 177.5 | 0.037107 | north | -0.0023301 | 0.088965 | 0.0017365 | 0.049902 | 0.0017365 | west | Y | 0.0023301 | 0.10537
13432 | SANDOW_5 | 5 | 581 | 0.088554 | south | 0.049117 | 0.14041 | 0.053183 | 0.10135 | 0.049117 | North | Y | 0.14041 | 53.0424
13691 | OAKGROVE | 1 | 855 | 0.027019 | north | -0.012418 | 0.078877 | -0.0083515 | 0.039814 | 0.0083515 | west | Y | 0.012418 | 3.4769
13692 | OAKGROVE | 2 | 855 | 0.027019 | north | -0.012418 | 0.078877 | -0.0083515 | 0.039814 | 0.0083515 | west | Y | 0.012418 | 3.4769
32798 | BRYN_TAM | 1 | 32 | 0.022449 | north | -0.016988 | 0.074307 | -0.012922 | 0.035244 | 0.012922 | west | Y | 0.016988 | 0.13013
32883 | BRYN_DNS | 1 | 48 | 0.024394 | north | -0.015043 | 0.076252 | -0.010977 | 0.037189 | 0.010977 | west | Y | 0.015043 | 0.1952
32884 | BRYN_DNS | 1 | 46 | 0.024394 | north | -0.015043 | 0.076252 | -0.010977 | 0.037189 | 0.010977 | west | Y | 0.015043 | 0.18706
32886 | BRYN_ATK | MB | 12 | 0.022617 | north | -0.01682 | 0.074475 | -0.012754 | 0.035412 | 0.012754 | west | Y | 0.01682 | 0.048799
32887 | BRYN_ATK | MB | 51 | 0.022617 | north | -0.01682 | 0.074475 | -0.012754 | 0.035412 | 0.012754 | west | Y | 0.01682 | 0.2074
32888 | BRYN_ATK | 1 | 17 | 0.022617 | north | -0.01682 | 0.074475 | -0.012754 | 0.035412 | 0.012754 | west | Y | 0.01682 | 0.069132
32890 | BRYN_ATK | MB | 22 | 0.022617 | north | -0.01682 | 0.074475 | -0.012754 | 0.035412 | 0.012754 | west | Y | 0.01682 | 0.089465
32891 | BRYN_ATK | MB | 25 | 0.022617 | north | -0.01682 | 0.074475 | -0.012754 | 0.035412 | 0.012754 | west | Y | 0.01682 | 0.10166
32892 | BRYN_DNS | 1 | 105 | 0.024394 | north | -0.015043 | 0.076252 | -0.010977 | 0.037189 | 0.010977 | west | Y | 0.015043 | 0.42699
36998 | RDCNYNG1 | 1 | 84 | 0.036265 | west | -0.0031721 | 0.088123 | 0.00089448 | 0.04906 | 0.00089448 | west | N | 0.00089448 | 0
38332 | WDWRDU2 | 1 | 80 | 0.030839 | west | -0.0085981 | 0.082697 | -0.0045315 | 0.043634 | 0.0045315 | west | N | 0.0045315 | 0
38437 | TNSRBNMS | 1 | 150 | 0.030804 | west | -0.0086331 | 0.082662 | -0.0045665 | 0.043599 | 0.0045665 | west | N | 0.0045665 | 0
38438 | TNSRBNMS | 1 | 150 | 0.030804 | west | -0.0086331 | 0.082662 | -0.0045665 | 0.043599 | 0.0045665 | west | N | 0.0045665 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.013496 | houston | -0.052933 | 0.038362 | -0.048867 | -0.00070088 | 0.00070088 | houston | N | 0.00070088 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.013496 | houston | -0.052933 | 0.038362 | -0.048867 | -0.00070088 | 0.00070088 | houston | N | 0.00070088 | 0
38600 | TNBP_CGN | 5 | 53 | -0.013496 | houston | -0.052933 | 0.038362 | -0.048867 | -0.00070088 | 0.00070088 | houston | N | 0.00070088 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.013496 | houston | -0.052933 | 0.038362 | -0.048867 | -0.00070088 | 0.00070088 | houston | N | 0.00070088 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.013496 | houston | -0.052933 | 0.038362 | -0.048867 | -0.00070088 | 0.00070088 | houston | N | 0.00070088 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.013496 | houston | -0.052933 | 0.038362 | -0.048867 | -0.00070088 | 0.00070088 | houston | N | 0.00070088 | 0
38614 | TNBPAMCG | 4 | 96 | -0.013496 | houston | -0.052933 | 0.038362 | -0.048867 | -0.00070088 | 0.00070088 | houston | N | 0.00070088 | 0
38615 | TNBPAMCG | 1 | 244 | -0.013496 | houston | -0.052933 | 0.038362 | -0.048867 | -0.00070088 | 0.00070088 | houston | N | 0.00070088 | 0
38690 | TNBP_CGN | 3 | 40 | -0.013496 | houston | -0.052933 | 0.038362 | -0.048867 | -0.00070088 | 0.00070088 | houston | N | 0.00070088 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.013506 | houston | -0.052943 | 0.038352 | -0.048877 | -0.00071088 | 0.00071088 | houston | N | 0.00071088 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.013506 | houston | -0.052943 | 0.038352 | -0.048877 | -0.00071088 | 0.00071088 | houston | N | 0.00071088 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.013506 | houston | -0.052943 | 0.038352 | -0.048877 | -0.00071088 | 0.00071088 | houston | N | 0.00071088 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.013506 | houston | -0.052943 | 0.038352 | -0.048877 | -0.00071088 | 0.00071088 | houston | N | 0.00071088 | 0
39470 | TNDOWCGN | 1 | 32 | -0.013506 | houston | -0.052943 | 0.038352 | -0.048877 | -0.00071088 | 0.00071088 | houston | N | 0.00071088 | 0
39480 | TNDOWCGN | 1 | 30 | -0.013506 | houston | -0.052943 | 0.038352 | -0.048877 | -0.00071088 | 0.00071088 | houston | N | 0.00071088 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.019754 | houston | -0.059191 | 0.032104 | -0.055125 | -0.0069589 | 0.0069589 | houston | N | 0.0069589 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.019754 | houston | -0.059191 | 0.032104 | -0.055125 | -0.0069589 | 0.0069589 | houston | N | 0.0069589 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.019754 | houston | -0.059191 | 0.032104 | -0.055125 | -0.0069589 | 0.0069589 | houston | N | 0.0069589 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.019754 | houston | -0.059191 | 0.032104 | -0.055125 | -0.0069589 | 0.0069589 | houston | N | 0.0069589 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.027019 | north | -0.012418 | 0.078877 | -0.0083515 | 0.039814 | 0.0083515 | west | Y | 0.012418 | 0.61934
39970 | TNTNPONE | 1 | 153 | 0.027019 | north | -0.012418 | 0.078877 | -0.0083515 | 0.039814 | 0.0083515 | west | Y | 0.012418 | 0.62219
48500 | APD_GT1_ | 1 | 136 | -0.009656 | houston | -0.049093 | 0.042202 | -0.045027 | 0.0031391 | 0.0031391 | houston | N | 0.0031391 | 0
48510 | AK_GT1__ | 1 | 33 | -0.015582 | houston | -0.055019 | 0.036276 | -0.050953 | -0.0027869 | 0.0027869 | houston | N | 0.0027869 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.009638 | houston | -0.049075 | 0.04222 | -0.045009 | 0.0031571 | 0.0031571 | houston | N | 0.0031571 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.009638 | houston | -0.049075 | 0.04222 | -0.045009 | 0.0031571 | 0.0031571 | houston | N | 0.0031571 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.009638 | houston | -0.049075 | 0.04222 | -0.045009 | 0.0031571 | 0.0031571 | houston | N | 0.0031571 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.009638 | houston | -0.049075 | 0.04222 | -0.045009 | 0.0031571 | 0.0031571 | houston | N | 0.0031571 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.020811 | houston | -0.060248 | 0.031047 | -0.056182 | -0.0080159 | 0.0080159 | houston | N | 0.0080159 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.020811 | houston | -0.060248 | 0.031047 | -0.056182 | -0.0080159 | 0.0080159 | houston | N | 0.0080159 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.015971 | houston | -0.055408 | 0.035887 | -0.051342 | -0.0031759 | 0.0031759 | houston | N | 0.0031759 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.015971 | houston | -0.055408 | 0.035887 | -0.051342 | -0.0031759 | 0.0031759 | houston | N | 0.0031759 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.015971 | houston | -0.055408 | 0.035887 | -0.051342 | -0.0031759 | 0.0031759 | houston | N | 0.0031759 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.011092 | houston | -0.050529 | 0.040766 | -0.046463 | 0.0017031 | 0.0017031 | houston | N | 0.0017031 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.011092 | houston | -0.050529 | 0.040766 | -0.046463 | 0.0017031 | 0.0017031 | houston | N | 0.0017031 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.011092 | houston | -0.050529 | 0.040766 | -0.046463 | 0.0017031 | 0.0017031 | houston | N | 0.0017031 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.011092 | houston | -0.050529 | 0.040766 | -0.046463 | 0.0017031 | 0.0017031 | houston | N | 0.0017031 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.010157 | houston | -0.049594 | 0.041701 | -0.045528 | 0.0026381 | 0.0026381 | houston | N | 0.0026381 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.010157 | houston | -0.049594 | 0.041701 | -0.045528 | 0.0026381 | 0.0026381 | houston | N | 0.0026381 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.011372 | houston | -0.050809 | 0.040486 | -0.046743 | 0.0014231 | 0.0014231 | houston | N | 0.0014231 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.011372 | houston | -0.050809 | 0.040486 | -0.046743 | 0.0014231 | 0.0014231 | houston | N | 0.0014231 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.011372 | houston | -0.050809 | 0.040486 | -0.046743 | 0.0014231 | 0.0014231 | houston | N | 0.0014231 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.011372 | houston | -0.050809 | 0.040486 | -0.046743 | 0.0014231 | 0.0014231 | houston | N | 0.0014231 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.011372 | houston | -0.050809 | 0.040486 | -0.046743 | 0.0014231 | 0.0014231 | houston | N | 0.0014231 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.00847 | houston | -0.047907 | 0.043388 | -0.043841 | 0.0043251 | 0.0043251 | houston | N | 0.0043251 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.008944 | houston | -0.048381 | 0.042914 | -0.044315 | 0.0038511 | 0.0038511 | houston | N | 0.0038511 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.008327 | houston | -0.047764 | 0.043531 | -0.043698 | 0.0044681 | 0.0044681 | houston | N | 0.0044681 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.008327 | houston | -0.047764 | 0.043531 | -0.043698 | 0.0044681 | 0.0044681 | houston | N | 0.0044681 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.008327 | houston | -0.047764 | 0.043531 | -0.043698 | 0.0044681 | 0.0044681 | houston | N | 0.0044681 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.005692 | houston | -0.045129 | 0.046166 | -0.041063 | 0.0071031 | 0.0071031 | houston | N | 0.0071031 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.009562 | houston | -0.048999 | 0.042296 | -0.044933 | 0.0032331 | 0.0032331 | houston | N | 0.0032331 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.009562 | houston | -0.048999 | 0.042296 | -0.044933 | 0.0032331 | 0.0032331 | houston | N | 0.0032331 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.007992 | houston | -0.047429 | 0.043866 | -0.043363 | 0.0048031 | 0.0048031 | houston | N | 0.0048031 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.007992 | houston | -0.047429 | 0.043866 | -0.043363 | 0.0048031 | 0.0048031 | houston | N | 0.0048031 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.007992 | houston | -0.047429 | 0.043866 | -0.043363 | 0.0048031 | 0.0048031 | houston | N | 0.0048031 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.007992 | houston | -0.047429 | 0.043866 | -0.043363 | 0.0048031 | 0.0048031 | houston | N | 0.0048031 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.010126 | houston | -0.049563 | 0.041732 | -0.045497 | 0.0026691 | 0.0026691 | houston | N | 0.0026691 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.010126 | houston | -0.049563 | 0.041732 | -0.045497 | 0.0026691 | 0.0026691 | houston | N | 0.0026691 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.010126 | houston | -0.049563 | 0.041732 | -0.045497 | 0.0026691 | 0.0026691 | houston | N | 0.0026691 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.010126 | houston | -0.049563 | 0.041732 | -0.045497 | 0.0026691 | 0.0026691 | houston | N | 0.0026691 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.01043 | houston | -0.049867 | 0.041428 | -0.045801 | 0.0023651 | 0.0023651 | houston | N | 0.0023651 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.01043 | houston | -0.049867 | 0.041428 | -0.045801 | 0.0023651 | 0.0023651 | houston | N | 0.0023651 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.01043 | houston | -0.049867 | 0.041428 | -0.045801 | 0.0023651 | 0.0023651 | houston | N | 0.0023651 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.01043 | houston | -0.049867 | 0.041428 | -0.045801 | 0.0023651 | 0.0023651 | houston | N | 0.0023651 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.01043 | houston | -0.049867 | 0.041428 | -0.045801 | 0.0023651 | 0.0023651 | houston | N | 0.0023651 | 0
48651 | EP_1_2 | 1 | 5 | -0.008493 | houston | -0.04793 | 0.043365 | -0.043864 | 0.0043021 | 0.0043021 | houston | N | 0.0043021 | 0
48651 | EP_1_2 | 2 | 21 | -0.008493 | houston | -0.04793 | 0.043365 | -0.043864 | 0.0043021 | 0.0043021 | houston | N | 0.0043021 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.012805 | north | -0.026632 | 0.064663 | -0.022566 | 0.0256 | 0.022566 | west | Y | 0.026632 | 0.62707
48672 | FTR_GT2_ | 2 | 156 | 0.012805 | north | -0.026632 | 0.064663 | -0.022566 | 0.0256 | 0.022566 | west | Y | 0.026632 | 0.63439
48673 | FTR_GT3_ | 3 | 156 | 0.012805 | north | -0.026632 | 0.064663 | -0.022566 | 0.0256 | 0.022566 | west | Y | 0.026632 | 0.63439
48674 | FTR_CN4_ | 4 | 380 | 0.012805 | north | -0.026632 | 0.064663 | -0.022566 | 0.0256 | 0.022566 | west | Y | 0.026632 | 1.5453
48690 | GBY_GN5_ | 5 | 398 | -0.007871 | houston | -0.047308 | 0.043987 | -0.043242 | 0.0049241 | 0.0049241 | houston | N | 0.0049241 | 0
48691 | GBY_7374 | A | 46 | -0.010665 | houston | -0.050102 | 0.041193 | -0.046036 | 0.0021301 | 0.0021301 | houston | N | 0.0021301 | 0
48691 | GBY_7374 | B | 46 | -0.010665 | houston | -0.050102 | 0.041193 | -0.046036 | 0.0021301 | 0.0021301 | houston | N | 0.0021301 | 0
48692 | GBY_8182 | C | 46 | -0.010665 | houston | -0.050102 | 0.041193 | -0.046036 | 0.0021301 | 0.0021301 | houston | N | 0.0021301 | 0
48692 | GBY_8182 | D | 55 | -0.010665 | houston | -0.050102 | 0.041193 | -0.046036 | 0.0021301 | 0.0021301 | houston | N | 0.0021301 | 0
48693 | GBY_8384 | E | 55 | -0.010665 | houston | -0.050102 | 0.041193 | -0.046036 | 0.0021301 | 0.0021301 | houston | N | 0.0021301 | 0
48693 | GBY_8384 | F | 54 | -0.010665 | houston | -0.050102 | 0.041193 | -0.046036 | 0.0021301 | 0.0021301 | houston | N | 0.0021301 | 0
48721 | LEG_1___ | 1 | 827 | 0.031053 | north | -0.0083841 | 0.082911 | -0.0043175 | 0.043848 | 0.0043175 | west | Y | 0.0083841 | 3.3631
48722 | LEG_2___ | 2 | 819 | 0.031053 | north | -0.0083841 | 0.082911 | -0.0043175 | 0.043848 | 0.0043175 | west | Y | 0.0083841 | 3.3305
48730 | MNS_GT | 1 | 46.1 | -0.016127 | houston | -0.055564 | 0.035731 | -0.051498 | -0.0033319 | 0.0033319 | houston | N | 0.0033319 | 0
48731 | CBE_GT1 | 1 | 76 | -0.028797 | houston | -0.068234 | 0.023061 | -0.064168 | -0.016002 | 0.016002 | houston | N | 0.016002 | 0
48732 | CBE_GT2 | 1 | 76 | -0.028797 | houston | -0.068234 | 0.023061 | -0.064168 | -0.016002 | 0.016002 | houston | N | 0.016002 | 0
48733 | CBE_ST12 | 1 | 105 | -0.028797 | houston | -0.068234 | 0.023061 | -0.064168 | -0.016002 | 0.016002 | houston | N | 0.016002 | 0
48734 | CBE_GT3 | 1 | 74 | -0.028797 | houston | -0.068234 | 0.023061 | -0.064168 | -0.016002 | 0.016002 | houston | N | 0.016002 | 0
48735 | CBE_GT4 | 1 | 74 | -0.028797 | houston | -0.068234 | 0.023061 | -0.064168 | -0.016002 | 0.016002 | houston | N | 0.016002 | 0
48736 | CBE_ST34 | 1 | 102 | -0.028797 | houston | -0.068234 | 0.023061 | -0.064168 | -0.016002 | 0.016002 | houston | N | 0.016002 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.010117 | houston | -0.049554 | 0.041741 | -0.045488 | 0.0026781 | 0.0026781 | houston | N | 0.0026781 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.010117 | houston | -0.049554 | 0.041741 | -0.045488 | 0.0026781 | 0.0026781 | houston | N | 0.0026781 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.010117 | houston | -0.049554 | 0.041741 | -0.045488 | 0.0026781 | 0.0026781 | houston | N | 0.0026781 | 0
48761 | PR_GT1__ | 1 | 35 | -0.010306 | houston | -0.049743 | 0.041552 | -0.045677 | 0.0024891 | 0.0024891 | houston | N | 0.0024891 | 0
48772 | PHR_GN2_ | MB | 459 | -0.012092 | houston | -0.051529 | 0.039766 | -0.047463 | 0.00070312 | 0.00070312 | houston | N | 0.00070312 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.008489 | houston | -0.047926 | 0.043369 | -0.04386 | 0.0043061 | 0.0043061 | houston | N | 0.0043061 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.008489 | houston | -0.047926 | 0.043369 | -0.04386 | 0.0043061 | 0.0043061 | houston | N | 0.0043061 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.008489 | houston | -0.047926 | 0.043369 | -0.04386 | 0.0043061 | 0.0043061 | houston | N | 0.0043061 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.008489 | houston | -0.047926 | 0.043369 | -0.04386 | 0.0043061 | 0.0043061 | houston | N | 0.0043061 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.008489 | houston | -0.047926 | 0.043369 | -0.04386 | 0.0043061 | 0.0043061 | houston | N | 0.0043061 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.008489 | houston | -0.047926 | 0.043369 | -0.04386 | 0.0043061 | 0.0043061 | houston | N | 0.0043061 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.008489 | houston | -0.047926 | 0.043369 | -0.04386 | 0.0043061 | 0.0043061 | houston | N | 0.0043061 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.005692 | houston | -0.045129 | 0.046166 | -0.041063 | 0.0071031 | 0.0071031 | houston | N | 0.0071031 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.005692 | houston | -0.045129 | 0.046166 | -0.041063 | 0.0071031 | 0.0071031 | houston | N | 0.0071031 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.005692 | houston | -0.045129 | 0.046166 | -0.041063 | 0.0071031 | 0.0071031 | houston | N | 0.0071031 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.005692 | houston | -0.045129 | 0.046166 | -0.041063 | 0.0071031 | 0.0071031 | houston | N | 0.0071031 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.00838 | houston | -0.047817 | 0.043478 | -0.043751 | 0.0044151 | 0.0044151 | houston | N | 0.0044151 | 0
48820 | SHELLG1_ | 1 | 71 | -0.009941 | houston | -0.049378 | 0.041917 | -0.045312 | 0.0028541 | 0.0028541 | houston | N | 0.0028541 | 0
48821 | SHELLG2 | 2 | 72 | -0.009941 | houston | -0.049378 | 0.041917 | -0.045312 | 0.0028541 | 0.0028541 | houston | N | 0.0028541 | 0
48822 | SHELLG3_ | 1 | 39 | -0.009941 | houston | -0.049378 | 0.041917 | -0.045312 | 0.0028541 | 0.0028541 | houston | N | 0.0028541 | 0
48822 | SHELLG3_ | 2 | 30 | -0.009941 | houston | -0.049378 | 0.041917 | -0.045312 | 0.0028541 | 0.0028541 | houston | N | 0.0028541 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.010569 | houston | -0.050006 | 0.041289 | -0.04594 | 0.0022261 | 0.0022261 | houston | N | 0.0022261 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.010569 | houston | -0.050006 | 0.041289 | -0.04594 | 0.0022261 | 0.0022261 | houston | N | 0.0022261 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.010129 | houston | -0.049566 | 0.041729 | -0.0455 | 0.0026661 | 0.0026661 | houston | N | 0.0026661 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.010165 | houston | -0.049602 | 0.041693 | -0.045536 | 0.0026301 | 0.0026301 | houston | N | 0.0026301 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.010175 | houston | -0.049612 | 0.041683 | -0.045546 | 0.0026201 | 0.0026201 | houston | N | 0.0026201 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.010132 | houston | -0.049569 | 0.041726 | -0.045503 | 0.0026631 | 0.0026631 | houston | N | 0.0026631 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.010122 | houston | -0.049559 | 0.041736 | -0.045493 | 0.0026731 | 0.0026731 | houston | N | 0.0026731 | 0
48855 | SRB_GT21 | B2 | 12 | -0.010182 | houston | -0.049619 | 0.041676 | -0.045553 | 0.0026131 | 0.0026131 | houston | N | 0.0026131 | 0
48855 | SRB_GT21 | MB | 18 | -0.010182 | houston | -0.049619 | 0.041676 | -0.045553 | 0.0026131 | 0.0026131 | houston | N | 0.0026131 | 0
48865 | TECO_GT1 | 1 | 50 | -0.01269 | houston | -0.052127 | 0.039168 | -0.048061 | 0.00010512 | 0.00010512 | houston | N | 0.00010512 | 0
48873 | THW_ST3_ | 3 | 104 | -0.009107 | houston | -0.048544 | 0.042751 | -0.044478 | 0.0036881 | 0.0036881 | houston | N | 0.0036881 | 0
48874 | THW_ST4_ | 4 | 104 | -0.009107 | houston | -0.048544 | 0.042751 | -0.044478 | 0.0036881 | 0.0036881 | houston | N | 0.0036881 | 0
48875 | THW_3132 | A | 54 | -0.009107 | houston | -0.048544 | 0.042751 | -0.044478 | 0.0036881 | 0.0036881 | houston | N | 0.0036881 | 0
48875 | THW_3132 | B | 53 | -0.009107 | houston | -0.048544 | 0.042751 | -0.044478 | 0.0036881 | 0.0036881 | houston | N | 0.0036881 | 0
48877 | THW_3334 | C | 54 | -0.009107 | houston | -0.048544 | 0.042751 | -0.044478 | 0.0036881 | 0.0036881 | houston | N | 0.0036881 | 0
48877 | THW_3334 | D | 57 | -0.009107 | houston | -0.048544 | 0.042751 | -0.044478 | 0.0036881 | 0.0036881 | houston | N | 0.0036881 | 0
48879 | THW_4142 | E | 54 | -0.009107 | houston | -0.048544 | 0.042751 | -0.044478 | 0.0036881 | 0.0036881 | houston | N | 0.0036881 | 0
48879 | THW_4142 | F | 54 | -0.009107 | houston | -0.048544 | 0.042751 | -0.044478 | 0.0036881 | 0.0036881 | houston | N | 0.0036881 | 0
48881 | THW_4344 | G | 58 | -0.009107 | houston | -0.048544 | 0.042751 | -0.044478 | 0.0036881 | 0.0036881 | houston | N | 0.0036881 | 0
48881 | THW_4344 | H | 58 | -0.009107 | houston | -0.048544 | 0.042751 | -0.044478 | 0.0036881 | 0.0036881 | houston | N | 0.0036881 | 0
48883 | THW_GT1_ | B2 | 12 | -0.008672 | houston | -0.048109 | 0.043186 | -0.044043 | 0.0041231 | 0.0041231 | houston | N | 0.0041231 | 0
48885 | THW_5152 | A | 56 | -0.007667 | houston | -0.047104 | 0.044191 | -0.043038 | 0.0051281 | 0.0051281 | houston | N | 0.0051281 | 0
48885 | THW_5152 | B | 59 | -0.007667 | houston | -0.047104 | 0.044191 | -0.043038 | 0.0051281 | 0.0051281 | houston | N | 0.0051281 | 0
48886 | THW_5354 | C | 56 | -0.007667 | houston | -0.047104 | 0.044191 | -0.043038 | 0.0051281 | 0.0051281 | houston | N | 0.0051281 | 0
48886 | THW_5354 | D | 56 | -0.007667 | houston | -0.047104 | 0.044191 | -0.043038 | 0.0051281 | 0.0051281 | houston | N | 0.0051281 | 0
48887 | THW_5556 | E | 59 | -0.007667 | houston | -0.047104 | 0.044191 | -0.043038 | 0.0051281 | 0.0051281 | houston | N | 0.0051281 | 0
48887 | THW_5556 | F | 56 | -0.007667 | houston | -0.047104 | 0.044191 | -0.043038 | 0.0051281 | 0.0051281 | houston | N | 0.0051281 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.027247 | houston | -0.066684 | 0.024611 | -0.062618 | -0.014452 | 0.014452 | houston | N | 0.014452 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.015364 | houston | -0.054801 | 0.036494 | -0.050735 | -0.0025689 | 0.0025689 | houston | N | 0.0025689 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.015364 | houston | -0.054801 | 0.036494 | -0.050735 | -0.0025689 | 0.0025689 | houston | N | 0.0025689 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.015364 | houston | -0.054801 | 0.036494 | -0.050735 | -0.0025689 | 0.0025689 | houston | N | 0.0025689 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.015364 | houston | -0.054801 | 0.036494 | -0.050735 | -0.0025689 | 0.0025689 | houston | N | 0.0025689 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.015364 | houston | -0.054801 | 0.036494 | -0.050735 | -0.0025689 | 0.0025689 | houston | N | 0.0025689 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.016002 | houston | -0.055439 | 0.035856 | -0.051373 | -0.0032069 | 0.0032069 | houston | N | 0.0032069 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.016002 | houston | -0.055439 | 0.035856 | -0.051373 | -0.0032069 | 0.0032069 | houston | N | 0.0032069 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.016002 | houston | -0.055439 | 0.035856 | -0.051373 | -0.0032069 | 0.0032069 | houston | N | 0.0032069 | 0
48929 | WAPGT21_ | B1 | 13 | -0.015364 | houston | -0.054801 | 0.036494 | -0.050735 | -0.0025689 | 0.0025689 | houston | N | 0.0025689 | 0
48940 | WARVUE_G | G1 | 12 | -0.008482 | houston | -0.047919 | 0.043376 | -0.043853 | 0.0043131 | 0.0043131 | houston | N | 0.0043131 | 0
49803 | EXN_15GT | 1 | 34 | -0.008828 | houston | -0.048265 | 0.04303 | -0.044199 | 0.0039671 | 0.0039671 | houston | N | 0.0039671 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.008828 | houston | -0.048265 | 0.04303 | -0.044199 | 0.0039671 | 0.0039671 | houston | N | 0.0039671 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.008828 | houston | -0.048265 | 0.04303 | -0.044199 | 0.0039671 | 0.0039671 | houston | N | 0.0039671 | 0
49826 | EXN938GT | 5 | 45.9 | -0.008828 | houston | -0.048265 | 0.04303 | -0.044199 | 0.0039671 | 0.0039671 | houston | N | 0.0039671 | 0
49828 | EXN941GT | 10 | 17.7 | -0.008828 | houston | -0.048265 | 0.04303 | -0.044199 | 0.0039671 | 0.0039671 | houston | N | 0.0039671 | 0
49829 | EXN942GT | 11 | 20.4 | -0.008828 | houston | -0.048265 | 0.04303 | -0.044199 | 0.0039671 | 0.0039671 | houston | N | 0.0039671 | 0
49830 | EXN943GT | 12 | 19.9 | -0.008828 | houston | -0.048265 | 0.04303 | -0.044199 | 0.0039671 | 0.0039671 | houston | N | 0.0039671 | 0
49831 | EXN944GT | 13 | 35 | -0.008828 | houston | -0.048265 | 0.04303 | -0.044199 | 0.0039671 | 0.0039671 | houston | N | 0.0039671 | 0
49832 | EXN945GT | 9 | 18 | -0.008828 | houston | -0.048265 | 0.04303 | -0.044199 | 0.0039671 | 0.0039671 | houston | N | 0.0039671 | 0
49837 | EXN_GT | 4 | 85.4 | -0.008828 | houston | -0.048265 | 0.04303 | -0.044199 | 0.0039671 | 0.0039671 | houston | N | 0.0039671 | 0
49838 | EXN_14GT | 14 | 148 | -0.008828 | houston | -0.048265 | 0.04303 | -0.044199 | 0.0039671 | 0.0039671 | houston | N | 0.0039671 | 0
49851 | DOW17000 | 37 | 62 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49858 | DOW38100 | 31 | 71.4 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49859 | DOW38200 | 33 | 45 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49860 | DOW38300 | 32 | 101 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49862 | DOW39100 | 36 | 86 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49863 | DOW39200 | 35 | 88 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49865 | DOW41000 | 41 | 50 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49866 | DOW42000 | 42 | 18 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49869 | DOW49000 | 45 | 94 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49870 | DOW61000 | 61 | 70 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49871 | DOW62000 | 62 | 63 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49872 | DOW63000 | 63 | 72 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49873 | DOW64000 | 64 | 64.8 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49876 | DOW65000 | 65 | 101 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49877 | DOW66000 | 66 | 97 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49878 | DOW67000 | 67 | 103 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49882 | DOW81000 | 81 | 76 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49884 | DOW82000 | 82 | 80 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49885 | DOW83000 | 83 | 80 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
49886 | DOW84000 | 84 | 171 | -0.02213 | houston | -0.061567 | 0.029728 | -0.057501 | -0.0093349 | 0.0093349 | houston | N | 0.0093349 | 0
58909 | PEARSALL | 1 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58909 | PEARSALL | 2 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58909 | PEARSALL | 3 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58909 | PEARSALL | 4 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58909 | PEARSALL | 5 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58909 | PEARSALL | 6 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58919 | PEARSALL | 1 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58919 | PEARSALL | 2 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58919 | PEARSALL | 3 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58919 | PEARSALL | 4 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58919 | PEARSALL | 5 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58919 | PEARSALL | 6 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58929 | PEARSALL | 1 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58929 | PEARSALL | 2 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58929 | PEARSALL | 3 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58929 | PEARSALL | 4 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58929 | PEARSALL | 5 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58929 | PEARSALL | 6 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58949 | PEARSALL | 1 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58949 | PEARSALL | 2 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58949 | PEARSALL | 3 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58949 | PEARSALL | 4 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58949 | PEARSALL | 5 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
58949 | PEARSALL | 6 | 8.4 | -0.050906 | south | -0.090343 | 0.00095186 | -0.086277 | -0.038111 | 0.00095186 | south | N | 0.00095186 | 0
60000 | DSKY2 | 1 | 76.5 | 0.029181 | west | -0.010256 | 0.081039 | -0.0061895 | 0.041976 | 0.0061895 | west | N | 0.0061895 | 0
60003 | KING_NE1 | 1 | 80 | 0.030908 | west | -0.0085291 | 0.082766 | -0.0044625 | 0.043703 | 0.0044625 | west | N | 0.0044625 | 0
60005 | KING_SE1 | 1 | 40 | 0.030908 | west | -0.0085291 | 0.082766 | -0.0044625 | 0.043703 | 0.0044625 | west | N | 0.0044625 | 0
60007 | KING_SW1 | 1 | 80 | 0.031186 | west | -0.0082511 | 0.083044 | -0.0041845 | 0.043981 | 0.0041845 | west | N | 0.0041845 | 0
60016 | WOODWRD1 | 1 | 80 | 0.030848 | west | -0.0085891 | 0.082706 | -0.0045225 | 0.043643 | 0.0045225 | west | N | 0.0045225 | 0
60017 | ORNNWP1 | 1 | 80 | 0.029416 | west | -0.010021 | 0.081274 | -0.0059545 | 0.042211 | 0.0059545 | west | N | 0.0059545 | 0
60018 | DSKY1 | 1 | 84 | 0.028948 | west | -0.010489 | 0.080806 | -0.0064225 | 0.041743 | 0.0064225 | west | N | 0.0064225 | 0
60019 | KING_NW1 | 1 | 80 | 0.031186 | west | -0.0082511 | 0.083044 | -0.0041845 | 0.043981 | 0.0041845 | west | N | 0.0041845 | 0
60057 | CALLAHAN | 1 | 114 | -0.061181 | south | -0.10062 | -0.0093231 | -0.096552 | -0.048386 | 0.0093231 | south | N | 0.0093231 | 0
60058 | BUFF_GAP | 1 | 120 | 0.035838 | west | -0.0035991 | 0.087696 | 0.00046748 | 0.048633 | 0.00046748 | west | N | 0.00046748 | 0
60060 | CIRELLO | 1 | 233 | 0.035838 | west | -0.0035991 | 0.087696 | 0.00046748 | 0.048633 | 0.00046748 | west | N | 0.00046748 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.035838 | west | -0.0035991 | 0.087696 | 0.00046748 | 0.048633 | 0.00046748 | west | N | 0.00046748 | 0
60066 | H_HOLLOW | 1 | 222 | -0.061181 | south | -0.10062 | -0.0093231 | -0.096552 | -0.048386 | 0.0093231 | south | N | 0.0093231 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.061181 | south | -0.10062 | -0.0093231 | -0.096552 | -0.048386 | 0.0093231 | south | N | 0.0093231 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.061181 | south | -0.10062 | -0.0093231 | -0.096552 | -0.048386 | 0.0093231 | south | N | 0.0093231 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.061181 | south | -0.10062 | -0.0093231 | -0.096552 | -0.048386 | 0.0093231 | south | N | 0.0093231 | 0
60074 | HORSH5 | 1 | 100 | -0.061181 | south | -0.10062 | -0.0093231 | -0.096552 | -0.048386 | 0.0093231 | south | N | 0.0093231 | 0
60081 | WHRLWIND | 1 | 60 | 0.037239 | west | -0.0021981 | 0.089097 | 0.0018685 | 0.050034 | 0.0018685 | west | N | 0.0018685 | 0
60201 | RIO DRCS | F | 0 | -0.033041 | south | -0.072478 | 0.018817 | -0.068412 | -0.020246 | 0.018817 | south | N | 0.018817 | 0
60202 | FRIEND_R | F | 0 | 0.021481 | west | -0.017956 | 0.073339 | -0.01389 | 0.034276 | 0.01389 | west | N | 0.01389 | 0
60203 | PRES0A | BT | 4.8 | 0.032216 | west | -0.0072211 | 0.084074 | -0.0031545 | 0.045011 | 0.0031545 | west | N | 0.0031545 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.036544 | west | -0.0028931 | 0.088402 | 0.0011735 | 0.049339 | 0.0011735 | west | N | 0.0011735 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.036544 | west | -0.0028931 | 0.088402 | 0.0011735 | 0.049339 | 0.0011735 | west | N | 0.0011735 | 0
71057 | L_SWEETW | W1 | 135 | 0.036544 | west | -0.0028931 | 0.088402 | 0.0011735 | 0.049339 | 0.0011735 | west | N | 0.0011735 | 0
71059 | L_SWEETW | W1 | 119 | 0.036544 | west | -0.0028931 | 0.088402 | 0.0011735 | 0.049339 | 0.0011735 | west | N | 0.0011735 | 0
71060 | L_SWEETW | W1 | 105 | 0.036544 | west | -0.0028931 | 0.088402 | 0.0011735 | 0.049339 | 0.0011735 | west | N | 0.0011735 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.036544 | west | -0.0028931 | 0.088402 | 0.0011735 | 0.049339 | 0.0011735 | west | N | 0.0011735 | 0
76031 | L_GASCCR | W1 | 150 | 0.035396 | west | -0.0040411 | 0.087254 | 2.5477e-05 | 0.048191 | 2.5477e-05 | west | N | 2.5477e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.035251 | west | -0.0041861 | 0.087109 | -0.00011952 | 0.048046 | 0.00011952 | west | N | 0.00011952 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.035251 | west | -0.0041861 | 0.087109 | -0.00011952 | 0.048046 | 0.00011952 | west | N | 0.00011952 | 0
76096 | L_CAPRSI | W1 | 186 | 0.035251 | west | -0.0041861 | 0.087109 | -0.00011952 | 0.048046 | 0.00011952 | west | N | 0.00011952 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.035251 | west | -0.0041861 | 0.087109 | -0.00011952 | 0.048046 | 0.00011952 | west | N | 0.00011952 | 0
80003 | MILHWYS | F | 0 | -0.048106 | south | -0.087543 | 0.0037519 | -0.083477 | -0.035311 | 0.0037519 | south | N | 0.0037519 | 0
80010 | EPLVT1 | F | 0 | -0.037583 | south | -0.07702 | 0.014275 | -0.072954 | -0.024788 | 0.014275 | south | N | 0.014275 | 0
80012 | LAR | F | 0 | -0.05096 | south | -0.090397 | 0.00089786 | -0.086331 | -0.038165 | 0.00089786 | south | N | 0.00089786 | 0
80051 | FORPVCM0 | 8 | 28 | -0.04348 | south | -0.082917 | 0.0083779 | -0.078851 | -0.030685 | 0.0083779 | south | N | 0.0083779 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.04348 | south | -0.082917 | 0.0083779 | -0.078851 | -0.030685 | 0.0083779 | south | N | 0.0083779 | 0
80053 | FOR69CG0 | 10 | 74 | -0.04348 | south | -0.082917 | 0.0083779 | -0.078851 | -0.030685 | 0.0083779 | south | N | 0.0083779 | 0
80080 | GWINDT11 | 1 | 94 | -0.048071 | south | -0.087508 | 0.0037869 | -0.083442 | -0.035276 | 0.0037869 | south | N | 0.0037869 | 0
80080 | GWINDT11 | 2 | 41 | -0.048071 | south | -0.087508 | 0.0037869 | -0.083442 | -0.035276 | 0.0037869 | south | N | 0.0037869 | 0
80080 | GWINDT11 | 3 | 38 | -0.048071 | south | -0.087508 | 0.0037869 | -0.083442 | -0.035276 | 0.0037869 | south | N | 0.0037869 | 0
80080 | GWINDT11 | 4 | 19 | -0.048071 | south | -0.087508 | 0.0037869 | -0.083442 | -0.035276 | 0.0037869 | south | N | 0.0037869 | 0
80081 | GWINDT21 | 1 | 94 | -0.048071 | south | -0.087508 | 0.0037869 | -0.083442 | -0.035276 | 0.0037869 | south | N | 0.0037869 | 0
80081 | GWINDT21 | 2 | 36 | -0.048071 | south | -0.087508 | 0.0037869 | -0.083442 | -0.035276 | 0.0037869 | south | N | 0.0037869 | 0
80081 | GWINDT21 | 3 | 43 | -0.048071 | south | -0.087508 | 0.0037869 | -0.083442 | -0.035276 | 0.0037869 | south | N | 0.0037869 | 0
80081 | GWINDT21 | 4 | 22 | -0.048071 | south | -0.087508 | 0.0037869 | -0.083442 | -0.035276 | 0.0037869 | south | N | 0.0037869 | 0
80137 | CSDR89 | 8 | 39 | -0.045165 | south | -0.084602 | 0.0066929 | -0.080536 | -0.03237 | 0.0066929 | south | N | 0.0066929 | 0
80137 | CSDR89 | 9 | 15 | -0.045165 | south | -0.084602 | 0.0066929 | -0.080536 | -0.03237 | 0.0066929 | south | N | 0.0066929 | 0
80138 | CSDR7 | 7 | 7 | -0.045165 | south | -0.084602 | 0.0066929 | -0.080536 | -0.03237 | 0.0066929 | south | N | 0.0066929 | 0
80139 | CSDR56 | 5 | 15 | -0.045165 | south | -0.084602 | 0.0066929 | -0.080536 | -0.03237 | 0.0066929 | south | N | 0.0066929 | 0
80139 | CSDR56 | 6 | 39 | -0.045165 | south | -0.084602 | 0.0066929 | -0.080536 | -0.03237 | 0.0066929 | south | N | 0.0066929 | 0
80140 | CSDR11 | 11 | 39 | -0.045165 | south | -0.084602 | 0.0066929 | -0.080536 | -0.03237 | 0.0066929 | south | N | 0.0066929 | 0
80180 | PNSCALT1 | 1 | 148 | -0.048071 | south | -0.087508 | 0.0037869 | -0.083442 | -0.035276 | 0.0037869 | south | N | 0.0037869 | 0
80180 | PNSCALT1 | 2 | 50 | -0.048071 | south | -0.087508 | 0.0037869 | -0.083442 | -0.035276 | 0.0037869 | south | N | 0.0037869 | 0
80181 | PNSCALT2 | 1 | 55 | -0.048071 | south | -0.087508 | 0.0037869 | -0.083442 | -0.035276 | 0.0037869 | south | N | 0.0037869 | 0
80181 | PNSCALT2 | 2 | 50 | -0.048071 | south | -0.087508 | 0.0037869 | -0.083442 | -0.035276 | 0.0037869 | south | N | 0.0037869 | 0
80223 | REYSHR G | 1 | 12 | -0.047045 | south | -0.086482 | 0.0048129 | -0.082416 | -0.03425 | 0.0048129 | south | N | 0.0048129 | 0
80224 | VISTRONG | 1 | 15 | -0.045704 | south | -0.085141 | 0.0061539 | -0.081075 | -0.032909 | 0.0061539 | south | N | 0.0061539 | 0
80225 | VISTRONG | 2 | 23 | -0.045704 | south | -0.085141 | 0.0061539 | -0.081075 | -0.032909 | 0.0061539 | south | N | 0.0061539 | 0
80226 | ALCOA G | 1 | 48 | -0.043876 | south | -0.083313 | 0.0079819 | -0.079247 | -0.031081 | 0.0079819 | south | N | 0.0079819 | 0
80227 | AIRCO G | 1 | 8 | -0.045368 | south | -0.084805 | 0.0064899 | -0.080739 | -0.032573 | 0.0064899 | south | N | 0.0064899 | 0
80261 | NBEC81A | 1 | 180 | -0.047576 | south | -0.087013 | 0.0042819 | -0.082947 | -0.034781 | 0.0042819 | south | N | 0.0042819 | 0
80262 | NBEC91A | 1 | 180 | -0.047561 | south | -0.086998 | 0.0042969 | -0.082932 | -0.034766 | 0.0042969 | south | N | 0.0042969 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.047675 | south | -0.087112 | 0.0041829 | -0.083046 | -0.03488 | 0.0041829 | south | N | 0.0041829 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.047675 | south | -0.087112 | 0.0041829 | -0.083046 | -0.03488 | 0.0041829 | south | N | 0.0041829 | 0
80265 | LARECU40 | 4 | 100 | -0.050965 | south | -0.090402 | 0.00089286 | -0.086336 | -0.03817 | 0.00089286 | south | N | 0.00089286 | 0
80266 | LARECU50 | 5 | 100 | -0.050965 | south | -0.090402 | 0.00089286 | -0.086336 | -0.03817 | 0.00089286 | south | N | 0.00089286 | 0
80291 | PAPALOTE | 1 | 25 | -0.04725 | south | -0.086687 | 0.0046079 | -0.082621 | -0.034455 | 0.0046079 | south | N | 0.0046079 | 0
80291 | PAPALOTE | 2 | 25 | -0.04725 | south | -0.086687 | 0.0046079 | -0.082621 | -0.034455 | 0.0046079 | south | N | 0.0046079 | 0
80291 | PAPALOTE | 3 | 25 | -0.04725 | south | -0.086687 | 0.0046079 | -0.082621 | -0.034455 | 0.0046079 | south | N | 0.0046079 | 0
80291 | PAPALOTE | 4 | 16 | -0.04725 | south | -0.086687 | 0.0046079 | -0.082621 | -0.034455 | 0.0046079 | south | N | 0.0046079 | 0
80294 | PAPALOTE | 5 | 25 | -0.04725 | south | -0.086687 | 0.0046079 | -0.082621 | -0.034455 | 0.0046079 | south | N | 0.0046079 | 0
80294 | PAPALOTE | 6 | 25 | -0.04725 | south | -0.086687 | 0.0046079 | -0.082621 | -0.034455 | 0.0046079 | south | N | 0.0046079 | 0
80294 | PAPALOTE | 7 | 25 | -0.04725 | south | -0.086687 | 0.0046079 | -0.082621 | -0.034455 | 0.0046079 | south | N | 0.0046079 | 0
80294 | PAPALOTE | 8 | 15 | -0.04725 | south | -0.086687 | 0.0046079 | -0.082621 | -0.034455 | 0.0046079 | south | N | 0.0046079 | 0
86104 | CID-138 | EQ | 0 | -0.050965 | south | -0.090402 | 0.00089286 | -0.086336 | -0.03817 | 0.00089286 | south | N | 0.00089286 | 0
86105 | CID-230 | EQ | 500 | -0.050965 | south | -0.090402 | 0.00089286 | -0.086336 | -0.03817 | 0.00089286 | south | N | 0.00089286 | 0
86106 | CUF-230 | EQ | 500 | -0.050965 | south | -0.090402 | 0.00089286 | -0.086336 | -0.03817 | 0.00089286 | south | N | 0.00089286 | 0
86107 | CUF-138 | EQ | 0 | -0.050965 | south | -0.090402 | 0.00089286 | -0.086336 | -0.03817 | 0.00089286 | south | N | 0.00089286 | 0
88198 | BEEVILLE | F | 0 | -0.050385 | south | -0.089822 | 0.0014729 | -0.085756 | -0.03759 | 0.0014729 | south | N | 0.0014729 | 0
88253 | HAMILTON | F | 0 | -0.028987 | south | -0.068424 | 0.022871 | -0.064358 | -0.016192 | 0.016192 | houston | Y | 0.022871 | 0
88299 | ZAPATA | F | 0 | -0.049593 | south | -0.08903 | 0.0022649 | -0.084964 | -0.036798 | 0.0022649 | south | N | 0.0022649 | 0
88508 | FALFURRI | F | 0 | -0.048936 | south | -0.088373 | 0.0029219 | -0.084307 | -0.036141 | 0.0029219 | south | N | 0.0029219 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3666 HUTTOSS1 - 3670 RNDRCKNE_ctg1 C:3429 SANDOW__ - 7040 L_AUSTRO C:7040 L_AUSTRO - 13429 SAND_TXU_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.088554 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 50.3872 | 569 | 0.14041 | 79.8943 | 569 | 79.8943
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.088554 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 51.4499 | 581 | 0.14041 | 81.5793
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051858 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051858 | 0 |  |  | Weighted Shift Factors
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051858 | 0 |  |  | South | -0.051858
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051858 | 0 |  |  | North | 0.042506
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051858 | 0 |  |  |  | -0.094364
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051858 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051858 | 0 |  |  | Line Rating | 247.6
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051858 | 0 |  |  | Conc Gen | 569
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.005692 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.98472 | 0 | 0.046166 | 0 |  |  | Weighted Imp. | 79.8943
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.005692 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.88795 | 0 | 0.046166 | 0 |  |  | PTDF | 0.14041
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.005692 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.87657 | 0 | 0.046166 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.005692 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.87657 | 0 | 0.046166 | 0 |  |  | Concentration | -1.488
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.005692 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9221 | 0 | 0.046166 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.42935 | 56 | 0.044191 | 2.4747
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.45235 | 59 | 0.044191 | 2.6073
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.42935 | 56 | 0.044191 | 2.4747
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.42935 | 56 | 0.044191 | 2.4747
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.45235 | 59 | 0.044191 | 2.6073
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.42935 | 56 | 0.044191 | 2.4747
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.007871 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.1327 | 398 | 0.043987 | 17.5068
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.007992 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3011 | 0 | 0.043866 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.007992 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2899 | 0 | 0.043866 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.007992 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2699 | 0 | 0.043866 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.007992 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1514 | 0 | 0.043866 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.008327 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4322 | 172 | 0.043531 | 7.4873
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.008327 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4322 | 172 | 0.043531 | 7.4873
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.008327 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4322 | 172 | 0.043531 | 7.4873
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.00838 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3157 | 0 | 0.043478 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.00847 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -6.2932 | 743 | 0.043388 | 32.2372
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.008482 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.10178 | 12 | 0.043376 | 0.52051
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55178 | 0 | 0.043369 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56027 | 0 | 0.043369 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59423 | 0 | 0.043369 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53481 | 0 | 0.043369 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52632 | 0 | 0.043369 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88286 | 0 | 0.043369 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50085 | 0 | 0.043369 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.008493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.042465 | 0 | 0.043365 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.008493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17835 | 0 | 0.043365 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.008672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10406 | 12 | 0.043186 | 0.51823
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30015 | 0 | 0.04303 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30633 | 0 | 0.04303 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28868 | 0 | 0.04303 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40521 | 0 | 0.04303 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15626 | 0 | 0.04303 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18009 | 0 | 0.04303 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17568 | 0 | 0.04303 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30898 | 0 | 0.04303 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1589 | 0 | 0.04303 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.75391 | 0 | 0.04303 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3065 | 0 | 0.04303 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.008944 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -6.5738 | 735 | 0.042914 | 31.5417
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.94713 | 104 | 0.042751 | 4.4461
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.94713 | 104 | 0.042751 | 4.4461
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49178 | 54 | 0.042751 | 2.3085
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.48267 | 53 | 0.042751 | 2.2658
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49178 | 54 | 0.042751 | 2.3085
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.5191 | 57 | 0.042751 | 2.4368
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49178 | 54 | 0.042751 | 2.3085
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49178 | 54 | 0.042751 | 2.3085
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.52821 | 58 | 0.042751 | 2.4795
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.52821 | 58 | 0.042751 | 2.4795
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.009562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6542 | 0 | 0.042296 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.009562 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2909 | 0 | 0.042296 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.009638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.4048 | 42 | 0.04222 | 1.7732
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.009638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.4048 | 42 | 0.04222 | 1.7732
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.009638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.36624 | 38 | 0.04222 | 1.6044
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.009638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.36624 | 38 | 0.04222 | 1.6044
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.009656 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3132 | 0 | 0.042202 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.009941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70581 | 0 | 0.041917 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.009941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71575 | 0 | 0.041917 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.009941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3877 | 0 | 0.041917 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.009941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.29823 | 0 | 0.041917 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.010117 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8211 | 0 | 0.041741 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.010117 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6046 | 0 | 0.041741 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.010117 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5884 | 0 | 0.041741 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.010122 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.3078 | 228 | 0.041736 | 9.5158
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.010126 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64806 | 0 | 0.041732 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.010126 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63996 | 0 | 0.041732 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.010126 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.83641 | 0 | 0.041732 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.010126 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74527 | 0 | 0.041732 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.010129 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16409 | 0 | 0.041729 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.010132 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.1581 | 213 | 0.041726 | 8.8876
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.010157 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5134 | 0 | 0.041701 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.010157 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66122 | 0 | 0.041701 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.010165 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.6772 | 165 | 0.041693 | 6.8793
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.010175 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.7196 | 169 | 0.041683 | 7.0444
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.010182 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12218 | 12 | 0.041676 | 0.50011
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.010182 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.041676 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.010306 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.36071 | 0 | 0.041552 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7022 | 0 | 0.041428 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6386 | 0 | 0.041428 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6427 | 0 | 0.041428 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6375 | 0 | 0.041428 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8057 | 0 | 0.041428 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.010569 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.82438 | 0 | 0.041289 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.010569 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.84552 | 0 | 0.041289 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.49059 | 46 | 0.041193 | 1.8949
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.49059 | 46 | 0.041193 | 1.8949
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.49059 | 46 | 0.041193 | 1.8949
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.58657 | 55 | 0.041193 | 2.2656
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.58657 | 55 | 0.041193 | 2.2656
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.57591 | 54 | 0.041193 | 2.2244
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.011092 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.72098 | 0 | 0.040766 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.011092 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.66552 | 0 | 0.040766 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.011092 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.72098 | 0 | 0.040766 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.011092 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.72098 | 0 | 0.040766 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0349 | 0 | 0.040486 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.99619 | 0 | 0.040486 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.98936 | 0 | 0.040486 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61977 | 0 | 0.040486 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13874 | 0 | 0.040486 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.012092 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039766 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.01269 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.6345 | 50 | 0.039168 | 1.9584
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.013496 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.95552 | 0 | 0.038362 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.013496 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90018 | 0 | 0.038362 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.013496 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71529 | 0 | 0.038362 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0676 | 0 | 0.038362 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0716 | 0 | 0.038362 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0554 | 0 | 0.038362 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2956 | 0 | 0.038362 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.293 | 0 | 0.038362 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.013496 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53984 | 0 | 0.038362 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.013506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43219 | 0 | 0.038352 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.013506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40518 | 0 | 0.038352 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.013506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3547 | 0 | 0.038352 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.013506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2547 | 0 | 0.038352 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.013506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3871 | 0 | 0.038352 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.013506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3776 | 0 | 0.038352 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.015364 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.4736 | 161 | 0.036494 | 5.8755
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.015364 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.5504 | 166 | 0.036494 | 6.058
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.015364 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.8103 | 248 | 0.036494 | 9.0505
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.015364 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -8.3887 | 546 | 0.036494 | 19.9256
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.015364 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -9.8791 | 0 | 0.036494 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.015364 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.19973 | 13 | 0.036494 | 0.47442
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.015582 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51421 | 0 | 0.036276 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.015971 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6033 | 0 | 0.035887 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.015971 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6033 | 0 | 0.035887 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.015971 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.9129 | 0 | 0.035887 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.016002 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -10.4173 | 651 | 0.035856 | 23.3422
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.016002 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -9.0251 | 564 | 0.035856 | 20.2227
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.016002 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -9.6012 | 600 | 0.035856 | 21.5135
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.016127 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74345 | 0 | 0.035731 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.019754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1927 | 0 | 0.032104 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.019754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1927 | 0 | 0.032104 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.019754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3507 | 0 | 0.032104 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.019754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1631 | 0 | 0.032104 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.020811 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4776 | 0 | 0.031047 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.020811 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20811 | 0 | 0.031047 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3721 | 0 | 0.029728 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5801 | 0 | 0.029728 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.99585 | 0 | 0.029728 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2351 | 0 | 0.029728 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9032 | 0 | 0.029728 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9474 | 0 | 0.029728 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1065 | 0 | 0.029728 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.39834 | 0 | 0.029728 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0802 | 0 | 0.029728 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5491 | 0 | 0.029728 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3942 | 0 | 0.029728 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5934 | 0 | 0.029728 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.434 | 0 | 0.029728 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2351 | 0 | 0.029728 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1466 | 0 | 0.029728 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2794 | 0 | 0.029728 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6819 | 0 | 0.029728 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7704 | 0 | 0.029728 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7704 | 0 | 0.029728 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7842 | 0 | 0.029728 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.027247 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7983 | 66 | 0.024611 | 1.6243
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.1886 | 76 | 0.023061 | 1.7526
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.1886 | 76 | 0.023061 | 1.7526
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.0237 | 105 | 0.023061 | 2.4214
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.131 | 74 | 0.023061 | 1.7065
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.131 | 74 | 0.023061 | 1.7065
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.9373 | 102 | 0.023061 | 2.3522
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.028987 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.95657 | 0 | 0.022871 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.028987 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.72467 | 0 | 0.022871 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.028987 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022871 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.029337 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -39.1062 | 0 | 0.022521 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.029337 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -38.9595 | 0 | 0.022521 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.061576 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.01907 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.061576 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.01907 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.061253 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.018747 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.061253 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 48.2061 | 787 | 0.018747 | 14.7536
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.058959 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.0345 | 255 | 0.016453 | 4.1954
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.058959 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.7849 | 149 | 0.016453 | 2.4514
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.058959 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.0207 | 153 | 0.016453 | 2.5172
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.035961 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21577 | 0 | 0.015897 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.057078 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.5617 | 150 | 0.014572 | 2.1857
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.057078 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.5662 | 80 | 0.014572 | 1.1657
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.037583 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.014275 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.054469 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.81703 | 0 | 0.011963 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.054469 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.81703 | 0 | 0.011963 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4349 | 0 | 0.0083779 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5219 | 0 | 0.0083779 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4349 | 0 | 0.0083779 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4784 | 0 | 0.0083779 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4088 | 0 | 0.0083779 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.087 | 0 | 0.0083779 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0001 | 0 | 0.0083779 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2174 | 0 | 0.0083779 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8957 | 0 | 0.0083779 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2175 | 0 | 0.0083779 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.043876 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.106 | 0 | 0.0079819 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2646 | 0 | 0.0066929 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.31616 | 0 | 0.0066929 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7614 | 0 | 0.0066929 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.67748 | 0 | 0.0066929 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.31616 | 0 | 0.0066929 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.67748 | 0 | 0.0066929 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7614 | 0 | 0.0066929 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7614 | 0 | 0.0066929 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.045368 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.36294 | 0 | 0.0064899 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.045704 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.68556 | 0 | 0.0061539 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.045704 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0512 | 0 | 0.0061539 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.046129 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0148 | 22 | 0.0057289 | 0.12603
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.046129 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.50742 | 11 | 0.0057289 | 0.063017
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.046129 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.50742 | 11 | 0.0057289 | 0.063017
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.04656 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2209 | 47.7 | 0.0052979 | 0.25271
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.04656 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.7367 | 37.3 | 0.0052979 | 0.19761
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.04656 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.1418 | 46 | 0.0052979 | 0.2437
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.04656 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2349 | 48 | 0.0052979 | 0.2543
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.046635 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4044 | 0 | 0.0052229 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.4331 | 0 | 0.0048129 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.1979 | 0 | 0.0048129 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.7045 | 0 | 0.0048129 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.8215 | 0 | 0.0048129 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.9156 | 0 | 0.0048129 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.9747 | 0 | 0.0048129 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.047045 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.56454 | 0 | 0.0048129 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.047171 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.7926 | 144 | 0.0046869 | 0.67491
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.047171 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.8681 | 188 | 0.0046869 | 0.88113
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1812 | 25 | 0.0046079 | 0.1152
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1812 | 25 | 0.0046079 | 0.1152
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1812 | 25 | 0.0046079 | 0.1152
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.756 | 16 | 0.0046079 | 0.073726
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1812 | 25 | 0.0046079 | 0.1152
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1812 | 25 | 0.0046079 | 0.1152
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1812 | 25 | 0.0046079 | 0.1152
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.70875 | 15 | 0.0046079 | 0.069118
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.047561 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.9805 | 336 | 0.0042969 | 1.4437
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.047561 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.561 | 180 | 0.0042969 | 0.77343
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.047567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.0542 | 0 | 0.0042909 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.047567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.0685 | 0 | 0.0042909 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.047567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.2778 | 0 | 0.0042909 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.047576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.5637 | 180 | 0.0042819 | 0.77073
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.047675 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.9235 | 334 | 0.0041829 | 1.3971
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.047675 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.2095 | 340 | 0.0041829 | 1.4222
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.047675 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.5815 | 180 | 0.0041829 | 0.75291
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.047675 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.5815 | 180 | 0.0041829 | 0.75291
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.047691 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1923 | 0 | 0.0041669 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.047691 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1923 | 0 | 0.0041669 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.047741 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8142 | 0 | 0.0041169 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.047744 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8143 | 0 | 0.0041139 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.047987 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3916 | 0 | 0.0038709 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.5187 | 94 | 0.0037869 | 0.35596
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9709 | 41 | 0.0037869 | 0.15526
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8267 | 38 | 0.0037869 | 0.1439
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.91335 | 19 | 0.0037869 | 0.07195
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.5187 | 94 | 0.0037869 | 0.35596
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7306 | 36 | 0.0037869 | 0.13633
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0671 | 43 | 0.0037869 | 0.16283
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0576 | 22 | 0.0037869 | 0.083311
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.1145 | 148 | 0.0037869 | 0.56045
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4036 | 50 | 0.0037869 | 0.18934
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6439 | 55 | 0.0037869 | 0.20828
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4036 | 50 | 0.0037869 | 0.18934
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.048106 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0037519 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.048106 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.828 | 38 | 0.0037519 | 0.14257
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.048106 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.92845 | 19.3 | 0.0037519 | 0.072411
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.048106 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.72159 | 15 | 0.0037519 | 0.056278
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.048106 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.261 | 47 | 0.0037519 | 0.17634
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.048205 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9415 | 144 | 0.0036529 | 0.52601
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.048205 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9415 | 144 | 0.0036529 | 0.52601
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.048205 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.2431 | 171 | 0.0036529 | 0.62464
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.048207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.9788 | 207 | 0.0036509 | 0.75573
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.048207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.4465 | 216.7 | 0.0036509 | 0.79114
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.048207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.6661 | 242 | 0.0036509 | 0.88351
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.048312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.0777 | 146.5 | 0.0035459 | 0.51947
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.048312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1453 | 147.9 | 0.0035459 | 0.52443
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.048312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.358 | 173 | 0.0035459 | 0.61343
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.048936 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0029219 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.048967 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.5876 | 0 | 0.0028909 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.048967 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.53864 | 0 | 0.0028909 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.048967 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.5876 | 0 | 0.0028909 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.049593 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0022649 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.049622 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -31.2122 | 629 | 0.0022359 | 1.4064
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.050385 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0014729 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.04384 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.3651 | 168 | 0.0013336 | 0.22404
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.04384 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9456 | 90 | 0.0013336 | 0.12002
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.043579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.7617 | 224 | 0.0010726 | 0.24026
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.043579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.8489 | 226 | 0.0010726 | 0.2424
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.043579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2387 | 212 | 0.0010726 | 0.22739
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.043579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.1952 | 211 | 0.0010726 | 0.22632
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.043463 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.4054 | 216.4 | 0.00095659 | 0.20701
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.043463 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3924 | 216.1 | 0.00095659 | 0.20672
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.05096 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.00089786 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.050965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0965 | 100 | 0.00089286 | 0.089286
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.050965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0965 | 100 | 0.00089286 | 0.089286
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.050965 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.00089286 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.050965 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.00089286 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.050965 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.00089286 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.050965 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.00089286 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.051454 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2349 | 24 | 0.00040386 | 0.0096926
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.051454 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.2349 | 24 | 0.00040386 | 0.0096926
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.051454 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.1834 | 23 | 0.00040386 | 0.0092887
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.042559 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.9791 | 70 | 5.2586e-05 | 0.003681
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.042559 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.9366 | 69 | 5.2586e-05 | 0.0036284
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.042559 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.9366 | 69 | 5.2586e-05 | 0.0036284
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.042559 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.894 | 68 | 5.2586e-05 | 0.0035759
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.042106 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.6319 | 395 | -0.00040041 | -0.15816
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.042106 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 18.3161 | 435 | -0.00040041 | -0.17418
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.042065 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.2447 | 196 | -0.00044141 | -0.086517
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.042065 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6692 | 111 | -0.00044141 | -0.048997
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.042051 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 18.2922 | 435 | -0.00045541 | -0.19811
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.041923 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 3.0604 | 73 | -0.00058341 | -0.042589
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.041923 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.9888 | 119 | -0.00058341 | -0.069426
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.041923 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.5942 | 205 | -0.00058341 | -0.1196
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.041923 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.2761 | 102 | -0.00058341 | -0.059508
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.041923 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.0246 | 96 | -0.00058341 | -0.056008
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.041902 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00060441 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.041761 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.0747 | 217.3 | -0.00074541 | -0.16198
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.041761 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.561 | 205 | -0.00074541 | -0.15281
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.041761 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.3757 | 272.4 | -0.00074541 | -0.20305
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.041655 | north | 3 | N | N | Nnorth | Nnorth | 1 | 48.1948 | 0 | -0.00085141 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.041655 | north | 3 | N | N | Nnorth | Nnorth | 1 | 48.2365 | 0 | -0.00085141 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.041615 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.74907 | 18 | -0.00089141 | -0.016045
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.041615 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.74907 | 18 | -0.00089141 | -0.016045
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.041615 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.5814 | 38 | -0.00089141 | -0.033874
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.041459 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0010474 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.041459 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0010474 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.041459 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0010474 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.041323 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.4794 | 60 | -0.0011834 | -0.071005
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.041277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8878 | 288 | -0.0012294 | -0.35407
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.041277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0677 | 147 | -0.0012294 | -0.18072
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.041277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0677 | 147 | -0.0012294 | -0.18072
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.041208 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.8625 | 118 | -0.0012984 | -0.15321
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.041208 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.7389 | 115 | -0.0012984 | -0.14932
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.041208 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 22.9116 | 556 | -0.0012984 | -0.72192
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.041014 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.1871 | 224 | -0.0014924 | -0.3343
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.041007 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.4604 | 60 | -0.0014994 | -0.089965
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.041007 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.5834 | 63 | -0.0014994 | -0.094463
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.040948 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.6067 | 112.5 | -0.0015584 | -0.17532
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.040888 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0016184 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.040876 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016304 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.040728 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6291 | 0 | -0.0017784 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.040728 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6291 | 0 | -0.0017784 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.040722 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0017844 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.040722 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0017844 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.040698 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.9187 | 170 | -0.0018084 | -0.30743
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.040698 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 21.163 | 520 | -0.0018084 | -0.94038
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.040683 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.4882 | 0 | -0.0018234 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.040683 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.4882 | 0 | -0.0018234 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.040667 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.88 | 120 | -0.0018394 | -0.22073
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.040665 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 15.046 | 370 | -0.0018414 | -0.68132
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.6931 | 0 | -0.0018414 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.7338 | 0 | -0.0018414 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | 1 | 12.5655 | 0 | -0.0018414 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.8151 | 0 | -0.0018414 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.8558 | 0 | -0.0018414 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | 1 | 12.6061 | 0 | -0.0018414 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.040652 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.6261 | 40 | -0.0018544 | -0.074177
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5029 | 160 | -0.0018634 | -0.29815
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.3403 | 156 | -0.0018634 | -0.29069
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.966 | 196 | -0.0018634 | -0.36523
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.3403 | 156 | -0.0018634 | -0.29069
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.381 | 157 | -0.0018634 | -0.29256
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.0473 | 198 | -0.0018634 | -0.36896
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.040632 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.2099 | 79 | -0.0018744 | -0.14808
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.040632 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.307 | 106 | -0.0018744 | -0.19869
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.040632 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.9323 | 146 | -0.0018744 | -0.27366
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.040632 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 3.088 | 76 | -0.0018744 | -0.14246
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.040623 | north | 8 | N | N | Nnorth | Nnorth | 1 | 3.0467 | 0 | -0.0018834 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.040623 | north | 8 | N | N | Nnorth | Nnorth | 1 | 3.2336 | 0 | -0.0018834 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.040623 | north | 8 | N | N | Nnorth | Nnorth | 1 | 3.5911 | 0 | -0.0018834 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.040608 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.6593 | 558 | -0.0018984 | -1.0593
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.040608 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 23.512 | 579 | -0.0018984 | -1.0992
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.040608 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 32.8113 | 808 | -0.0018984 | -1.5339
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.040607 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 15.7555 | 388 | -0.0018994 | -0.73697
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.040607 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 20.9126 | 515 | -0.0018994 | -0.9782
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.04059 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.8118 | 20 | -0.0019164 | -0.038328
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.04059 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.0148 | 25 | -0.0019164 | -0.04791
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.04059 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.6642 | 41 | -0.0019164 | -0.078573
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.040514 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.2649 | 204 | -0.0019924 | -0.40645
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.040514 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.1433 | 201 | -0.0019924 | -0.40048
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.040514 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.8044 | 242 | -0.0019924 | -0.48216
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.4923 | 161 | -0.0021814 | -0.35121
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.6133 | 164 | -0.0021814 | -0.35775
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.6133 | 164 | -0.0021814 | -0.35775
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6945 | 414 | -0.0021814 | -0.90311
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5327 | 162 | -0.0021814 | -0.35339
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.4923 | 161 | -0.0021814 | -0.35121
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.573 | 163 | -0.0021814 | -0.35557
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.4929 | 409 | -0.0021814 | -0.8922
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.054365 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.5285 | 396 | -0.0025071 | -0.99283
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.039658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.79316 | 20 | -0.0028484 | -0.056968
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.039658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.79316 | 20 | -0.0028484 | -0.056968
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.039658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.79316 | 20 | -0.0028484 | -0.056968
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.039658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.67419 | 17 | -0.0028484 | -0.048423
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.039643 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.5936 | 242 | -0.0028634 | -0.69295
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.039567 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.4815 | 366 | -0.0029394 | -1.0758
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.039212 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 30.7814 | 785 | -0.0032944 | -2.5861
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.039212 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 31.1735 | 795 | -0.0032944 | -2.6191
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.039212 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 30.5854 | 780 | -0.0032944 | -2.5696
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.039047 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.779 | 0 | -0.0034594 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.039047 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.0761 | 0 | -0.0034594 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.039047 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.6618 | 0 | -0.0034594 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.039047 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.5798 | 0 | -0.0034594 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.055408 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.99734 | 0 | -0.0035501 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.055408 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.99734 | 0 | -0.0035501 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.055408 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.83112 | 0 | -0.0035501 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.038901 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0036054 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.038883 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.9442 | 50 | -0.0036234 | -0.18117
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.03887 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.0743 | 182 | -0.0036364 | -0.66183
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.03887 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 18.8131 | 484 | -0.0036364 | -1.76
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.038593 | west | 4 | Y | N | Ywest | Nwest | 1 | 25.0739 | 649.7 | -0.0039134 | -2.5425
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.038251 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3114 | 165 | -0.0042554 | -0.70214
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.056119 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.76883 | 0 | -0.0042611 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.037836 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9293 | 236 | -0.0046704 | -1.1022
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.037834 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1336 | 400 | -0.0046724 | -1.869
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.056951 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.68341 | 0 | -0.0050931 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.037239 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2343 | 60 | -0.0052674 | -0.31604
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.037107 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.6217 | 151.5 | -0.0053994 | -0.81801
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.037107 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.6514 | 152.3 | -0.0053994 | -0.82233
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.037107 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5865 | 177.5 | -0.0053994 | -0.9584
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.037024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.5795 | 150.7 | -0.0054824 | -0.8262
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.037024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.5906 | 151 | -0.0054824 | -0.82784
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.037024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5681 | 177.4 | -0.0054824 | -0.97258
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.057585 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -31.4414 | 546 | -0.0057271 | -3.127
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.057585 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -43.1887 | 750 | -0.0057271 | -4.2954
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.036711 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5066 | 150 | -0.0057954 | -0.86931
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.036605 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.5121 | 615 | -0.0059014 | -3.6294
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.036605 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 21.4871 | 587 | -0.0059014 | -3.4641
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.057768 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.3505 | 58 | -0.0059101 | -0.34279
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.057768 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.1414 | 89 | -0.0059101 | -0.526
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.057768 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.5418 | 44 | -0.0059101 | -0.26005
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.057768 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.5418 | 44 | -0.0059101 | -0.26005
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.057768 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.484 | 43 | -0.0059101 | -0.25414
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.057768 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.5996 | 45 | -0.0059101 | -0.26596
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.036586 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6465 | 209 | -0.0059204 | -1.2374
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.036586 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6281 | 126.5 | -0.0059204 | -0.74893
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.036586 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1099 | 249 | -0.0059204 | -1.4742
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.036586 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2074 | 197 | -0.0059204 | -1.1663
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3704 | 37.5 | -0.0059624 | -0.22359
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9285 | 107.5 | -0.0059624 | -0.64096
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9334 | 135 | -0.0059624 | -0.80493
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3487 | 119 | -0.0059624 | -0.70953
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8371 | 105 | -0.0059624 | -0.62605
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.9418 | 80.5 | -0.0059624 | -0.47997
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.057907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.9756 | 155 | -0.0060491 | -0.93762
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.057907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.8442 | 170 | -0.0060491 | -1.0284
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.057907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.9756 | 155 | -0.0060491 | -0.93762
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.036395 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4592 | 150 | -0.0061114 | -0.91671
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.036395 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6759 | 101 | -0.0061114 | -0.61725
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.036339 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5424 | 125 | -0.0061674 | -0.77093
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.036339 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5424 | 125 | -0.0061674 | -0.77093
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.058081 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -23.639 | 407 | -0.0062231 | -2.5328
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.036265 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0463 | 84 | -0.0062414 | -0.52428
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.058138 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.1508 | 209 | -0.0062801 | -1.3125
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.058138 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.5578 | 216 | -0.0062801 | -1.3565
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.058138 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.6743 | 46 | -0.0062801 | -0.28889
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.058138 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.7325 | 47 | -0.0062801 | -0.29517
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.058138 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.6743 | 46 | -0.0062801 | -0.28889
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.058138 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.6743 | 46 | -0.0062801 | -0.28889
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.0582 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -23.9784 | 412 | -0.0063421 | -2.613
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.0582 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -23.28 | 400 | -0.0063421 | -2.5369
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.036164 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5802 | 99 | -0.0063424 | -0.6279
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.036164 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.206 | 61 | -0.0063424 | -0.38689
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.036164 | west | 7 | N | N | Nwest | Nwest | 1 | 0.9041 | 0 | -0.0063424 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.036164 | west | 7 | N | N | Nwest | Nwest | 1 | 1.6527 | 0 | -0.0063424 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.036164 | west | 7 | N | N | Nwest | Nwest | 1 | 1.6527 | 0 | -0.0063424 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.05821 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -24.681 | 424 | -0.0063521 | -2.6933
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.05821 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -24.7392 | 425 | -0.0063521 | -2.6997
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.036153 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.0976 | 141 | -0.0063534 | -0.89583
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.036153 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3384 | 120 | -0.0063534 | -0.76241
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.036122 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2757 | 63 | -0.0063844 | -0.40222
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3813 | 66 | -0.0064264 | -0.42414
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.4895 | 69 | -0.0064264 | -0.44342
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.4895 | 69 | -0.0064264 | -0.44342
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.4174 | 67 | -0.0064264 | -0.43057
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.4174 | 67 | -0.0064264 | -0.43057
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3452 | 65 | -0.0064264 | -0.41772
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.058375 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0065171 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.058375 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0065171 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.058375 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0065171 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.035982 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3973 | 150 | -0.0065244 | -0.97866
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.035982 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.916 | 220 | -0.0065244 | -1.4354
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.035982 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1964 | 200 | -0.0065244 | -1.3049
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.035982 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3862 | 121.9 | -0.0065244 | -0.79533
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.035892 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4606 | 180 | -0.0066144 | -1.1906
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.035892 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4606 | 180 | -0.0066144 | -1.1906
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.035872 | west | 8 | N | N | Nwest | Nwest | 1 | 2.511 | 0 | -0.0066344 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.035872 | west | 8 | N | N | Nwest | Nwest | 1 | 2.633 | 0 | -0.0066344 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.035872 | west | 8 | N | N | Nwest | Nwest | 1 | 2.5254 | 0 | -0.0066344 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.035856 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0676 | 225 | -0.0066504 | -1.4963
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.035838 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3006 | 120 | -0.0066684 | -0.80021
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.035838 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3503 | 233 | -0.0066684 | -1.5537
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.035838 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0996 | 170.2 | -0.0066684 | -1.135
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.035785 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2942 | 120 | -0.0067214 | -0.80657
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.035768 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2922 | 120 | -0.0067384 | -0.80861
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.058762 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.9381 | 50 | -0.0069041 | -0.34521
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.058762 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.9381 | 50 | -0.0069041 | -0.34521
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.058762 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.9381 | 50 | -0.0069041 | -0.34521
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.058762 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.9381 | 50 | -0.0069041 | -0.34521
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.035551 | west | 8 | N | N | Nwest | Nwest | 1 | 0.91722 | 0 | -0.0069554 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.03551 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6062 | 214.2 | -0.0069964 | -1.4986
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.035426 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5603 | 100.5 | -0.0070804 | -0.71158
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.035417 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0542 | 58 | -0.0070894 | -0.41119
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.035396 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3094 | 150 | -0.0071104 | -1.0666
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4772 | 70 | -0.0071174 | -0.49822
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4772 | 70 | -0.0071174 | -0.49822
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.2841 | 92.8 | -0.0071174 | -0.6605
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8311 | 80 | -0.0071174 | -0.56939
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8311 | 80 | -0.0071174 | -0.56939
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.0697 | 115 | -0.0071174 | -0.8185
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.3667 | 208.2 | -0.0071234 | -1.4831
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.0279 | 142.1 | -0.0071234 | -1.0122
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.6847 | 132.4 | -0.0071234 | -0.94314
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.8121 | 136 | -0.0071234 | -0.96878
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.2013 | 147 | -0.0071234 | -1.0471
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.4304 | 210 | -0.0071234 | -1.4959
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.035251 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9657 | 112.5 | -0.0072554 | -0.81623
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.035251 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.27 | 149.5 | -0.0072554 | -1.0847
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.035251 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5567 | 186 | -0.0072554 | -1.3495
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.035251 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5613 | 214.5 | -0.0072554 | -1.5563
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.035056 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.23137 | 6.6 | -0.0074504 | -0.049173
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.035056 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2024 | 34.3 | -0.0074504 | -0.25555
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.034859 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.194 | 149 | -0.0076474 | -1.1395
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.7505 | 147 | -0.0076691 | -1.1274
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.2147 | 138 | -0.0076691 | -1.0583
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.3338 | 140 | -0.0076691 | -1.0737
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.7505 | 147 | -0.0076691 | -1.1274
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.8339 | 182 | -0.0076691 | -1.3958
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7863 | 198 | -0.0076691 | -1.5185
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.034742 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.216 | 35 | -0.0077644 | -0.27175
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.034742 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0423 | 30 | -0.0077644 | -0.23293
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.034717 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8845 | 169.5 | -0.0077894 | -1.3203
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2907 | 66 | -0.0077994 | -0.51476
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.256 | 65 | -0.0077994 | -0.50696
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3254 | 67 | -0.0077994 | -0.52256
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3254 | 67 | -0.0077994 | -0.52256
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3254 | 67 | -0.0077994 | -0.52256
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.034707 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0077994 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.034707 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0077994 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.060432 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.977 | 132 | -0.0085741 | -1.1318
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.060432 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.0979 | 134 | -0.0085741 | -1.1489
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.060432 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -19.5195 | 323 | -0.0085741 | -2.7694
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9746 | 114 | -0.0093231 | -1.0628
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -13.5822 | 222 | -0.0093231 | -2.0697
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -11.2573 | 184 | -0.0093231 | -1.7155
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -13.7045 | 224 | -0.0093231 | -2.0884
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.0358 | 115 | -0.0093231 | -1.0722
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.061252 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.147 | 0 | -0.0093941 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.061252 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.147 | 0 | -0.0093941 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.06169 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.76 | 142 | -0.0098321 | -1.3962
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.06169 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.9451 | 145 | -0.0098321 | -1.4257
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.06169 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.3152 | 151 | -0.0098321 | -1.4847
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.06169 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.8901 | 290 | -0.0098321 | -2.8513
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.06179 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.24716 | 0 | -0.0099321 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.032216 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.15464 | 0 | -0.01029 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.06256 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -27.0885 | 433 | -0.010702 | -4.634
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.062594 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -36.5549 | 584 | -0.010736 | -6.2699
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.062594 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -37.2434 | 595 | -0.010736 | -6.388
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.062708 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1505 | 0 | -0.01085 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.062708 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1505 | 0 | -0.01085 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.062708 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17558 | 0 | -0.01085 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.031186 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4949 | 80 | -0.01132 | -0.90563
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.031186 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4949 | 80 | -0.01132 | -0.90563
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.031053 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 25.6808 | 827 | -0.011453 | -9.472
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.031053 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 25.4324 | 819 | -0.011453 | -9.3803
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.030908 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3181 | 75 | -0.011598 | -0.86988
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.030908 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4726 | 80 | -0.011598 | -0.92787
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.030908 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2363 | 40 | -0.011598 | -0.46394
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.030848 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4678 | 80 | -0.011658 | -0.93267
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.030839 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4671 | 80 | -0.011667 | -0.93339
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.030804 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6206 | 150 | -0.011702 | -1.7554
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.030804 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6206 | 150 | -0.011702 | -1.7554
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.063869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.3003 | 223.9 | -0.012011 | -2.6893
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.063869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.3705 | 225 | -0.012011 | -2.7025
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.063869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.345 | 224.6 | -0.012011 | -2.6977
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.063869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.4791 | 226.7 | -0.012011 | -2.7229
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.029416 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3533 | 80 | -0.01309 | -1.0472
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.029181 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2323 | 76.5 | -0.013325 | -1.0194
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.065216 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -27.5212 | 422 | -0.013358 | -5.6371
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.028948 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4316 | 84 | -0.013558 | -1.1389
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.065872 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8444 | 0 | -0.014014 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.065872 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9103 | 0 | -0.014014 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.027019 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 23.1012 | 855 | -0.015487 | -13.2417
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.027019 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 23.1012 | 855 | -0.015487 | -13.2417
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.027019 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.115 | 152.3 | -0.015487 | -2.3587
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.027019 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.1339 | 153 | -0.015487 | -2.3696
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.069182 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.9308 | 158 | -0.017324 | -2.7372
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.069182 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.0691 | 160 | -0.017324 | -2.7719
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.069182 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.1068 | 175 | -0.017324 | -3.0317
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.069438 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.41663 | 0 | -0.01758 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.024394 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.1709 | 48 | -0.018112 | -0.8694
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.024394 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.1221 | 46 | -0.018112 | -0.83317
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.024394 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.5614 | 105 | -0.018112 | -1.9018
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.022617 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.019889 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.022617 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.019889 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.022617 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.38449 | 17 | -0.019889 | -0.33812
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.022617 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.019889 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.022617 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.019889 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.022449 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.71837 | 0 | -0.020057 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.072694 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.0858 | 152.5 | -0.020836 | -3.1775
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.072694 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.8678 | 149.5 | -0.020836 | -3.115
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.072694 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.9086 | 232.6 | -0.020836 | -4.8465
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.021481 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.021025 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.073263 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3187 | 0 | -0.021405 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.073263 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3187 | 0 | -0.021405 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.016747 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.7539 | 463 | -0.025759 | -11.9266
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.014596 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1894 | 150 | -0.02791 | -4.1866
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.012805 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.9745 | 0 | -0.029701 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.012805 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.9976 | 0 | -0.029701 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.012805 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.9976 | 0 | -0.029701 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.012805 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.8659 | 0 | -0.029701 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.09151 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.2029 | 0 | -0.039652 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.09151 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.1113 | 0 | -0.039652 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.09151 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.2029 | 0 | -0.039652 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.042506 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.042506 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.7001 | 49 | -0.044062 | -2.159
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.4123 | 46 | -0.044062 | -2.0269
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.4123 | 46 | -0.044062 | -2.0269
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.5082 | 47 | -0.044062 | -2.0709
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.09592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.7717 | 154 | -0.044062 | -6.7856
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.09592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.1962 | 148 | -0.044062 | -6.5212
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6042 | 48 | -0.044062 | -2.115
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6042 | 48 | -0.044062 | -2.115
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.098803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.1497 | 42 | -0.046945 | -1.9717
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.098803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.3473 | 44 | -0.046945 | -2.0656
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.098803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.3473 | 44 | -0.046945 | -2.0656
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.098803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6437 | 47 | -0.046945 | -2.2064
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.10095 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -31.2936 | 310 | -0.049089 | -15.2176
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.10095 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -41.6911 | 413 | -0.049089 | -20.2738
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.10175 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.81401 | 0 | -0.049893 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.10175 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.81401 | 0 | -0.049893 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.033041 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.075547 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -6.1181 | 100 | -0.10369 | -10.3687

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3666 HUTTOSS1 - 3670 RNDRCKNE_ctg1 C:3429 SANDOW__ - 7040 L_AUSTRO C:7040 L_AUSTRO - 13429 SAND_TXU_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -6.1181 | 0 | -0.10369 | 0 | 0 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.033041 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.075547 | 0 | 0 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.10175 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.81401 | 0 | -0.049893 | 0 | 0 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.10175 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.81401 | 0 | -0.049893 | 0 | 0 | 0 | Weighted Shift Factors
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.10095 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -31.2936 | 310 | -0.049089 | -15.2176 | 310 | 15.2176 | South | -0.051858
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.10095 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -41.6911 | 413 | -0.049089 | -20.2738 |  |  | North | 0.042506
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.098803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.1497 | 42 | -0.046945 | -1.9717 |  |  |  | -0.094364
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.098803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.3473 | 44 | -0.046945 | -2.0656
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.098803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.3473 | 44 | -0.046945 | -2.0656 |  |  | Line Rating | 247.6
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.098803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6437 | 47 | -0.046945 | -2.2064 |  |  | Conc Gen | 310
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.7001 | 49 | -0.044062 | -2.159 |  |  | Weighted Imp. | 15.2176
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.4123 | 46 | -0.044062 | -2.0269 |  |  | PTDF | 0.049089
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.4123 | 46 | -0.044062 | -2.0269
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.5082 | 47 | -0.044062 | -2.0709 |  |  | Concentration | -0.52021
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.09592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.7717 | 154 | -0.044062 | -6.7856
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.09592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.1962 | 148 | -0.044062 | -6.5212
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6042 | 48 | -0.044062 | -2.115
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.09592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6042 | 48 | -0.044062 | -2.115
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.042506 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.042506 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.09151 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.2029 | 0 | -0.039652 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.09151 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.1113 | 0 | -0.039652 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.09151 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.2029 | 0 | -0.039652 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.012805 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.9745 | 0 | -0.029701 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.012805 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.9976 | 0 | -0.029701 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.012805 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.9976 | 0 | -0.029701 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.012805 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.8659 | 0 | -0.029701 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.014596 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1894 | 0 | -0.02791 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.016747 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.7539 | 0 | -0.025759 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.073263 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3187 | 0 | -0.021405 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.073263 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3187 | 0 | -0.021405 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.021481 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.021025 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.072694 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.0858 | 152.5 | -0.020836 | -3.1775
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.072694 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.8678 | 149.5 | -0.020836 | -3.115
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.072694 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.9086 | 232.6 | -0.020836 | -4.8465
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.022449 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.71837 | 0 | -0.020057 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.022617 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.019889 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.022617 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.019889 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.022617 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.38449 | 17 | -0.019889 | -0.33812
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.022617 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.019889 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.022617 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.019889 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.024394 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.1709 | 48 | -0.018112 | -0.8694
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.024394 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.1221 | 46 | -0.018112 | -0.83317
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.024394 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.5614 | 105 | -0.018112 | -1.9018
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.069438 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.41663 | 0 | -0.01758 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.069182 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.9308 | 158 | -0.017324 | -2.7372
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.069182 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.0691 | 160 | -0.017324 | -2.7719
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.069182 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.1068 | 175 | -0.017324 | -3.0317
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.027019 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 23.1012 | 0 | -0.015487 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.027019 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 23.1012 | 0 | -0.015487 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.027019 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.115 | 0 | -0.015487 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.027019 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.1339 | 0 | -0.015487 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.065872 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8444 | 0 | -0.014014 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.065872 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9103 | 0 | -0.014014 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.028948 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4316 | 0 | -0.013558 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.065216 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -27.5212 | 422 | -0.013358 | -5.6371
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.029181 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2323 | 0 | -0.013325 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.029416 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3533 | 0 | -0.01309 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.063869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.3003 | 223.9 | -0.012011 | -2.6893
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.063869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.3705 | 225 | -0.012011 | -2.7025
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.063869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.345 | 224.6 | -0.012011 | -2.6977
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.063869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.4791 | 226.7 | -0.012011 | -2.7229
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.030804 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6206 | 0 | -0.011702 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.030804 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6206 | 0 | -0.011702 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.030839 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4671 | 0 | -0.011667 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.030848 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4678 | 0 | -0.011658 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.030908 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3181 | 0 | -0.011598 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.030908 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4726 | 0 | -0.011598 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.030908 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2363 | 0 | -0.011598 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.031053 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 25.6808 | 0 | -0.011453 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.031053 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 25.4324 | 0 | -0.011453 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.031186 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4949 | 0 | -0.01132 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.031186 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4949 | 0 | -0.01132 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.062708 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1505 | 0 | -0.01085 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.062708 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1505 | 0 | -0.01085 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.062708 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17558 | 0 | -0.01085 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.062594 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -36.5549 | 0 | -0.010736 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.062594 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -37.2434 | 0 | -0.010736 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.06256 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -27.0885 | 0 | -0.010702 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.032216 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.15464 | 0 | -0.01029 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.06179 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.24716 | 0 | -0.0099321 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.06169 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.76 | 142 | -0.0098321 | -1.3962
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.06169 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.9451 | 145 | -0.0098321 | -1.4257
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.06169 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.3152 | 151 | -0.0098321 | -1.4847
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.06169 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.8901 | 290 | -0.0098321 | -2.8513
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.061252 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.147 | 0 | -0.0093941 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.061252 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.147 | 0 | -0.0093941 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9746 | 0 | -0.0093231 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -13.5822 | 0 | -0.0093231 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -11.2573 | 0 | -0.0093231 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -13.7045 | 0 | -0.0093231 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.061181 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.0358 | 0 | -0.0093231 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.060432 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.977 | 132 | -0.0085741 | -1.1318
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.060432 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.0979 | 134 | -0.0085741 | -1.1489
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.060432 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -19.5195 | 323 | -0.0085741 | -2.7694
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2907 | 66 | -0.0077994 | -0.51476
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.256 | 65 | -0.0077994 | -0.50696
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3254 | 67 | -0.0077994 | -0.52256
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3254 | 67 | -0.0077994 | -0.52256
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.034707 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3254 | 67 | -0.0077994 | -0.52256
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.034707 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0077994 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.034707 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0077994 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.034717 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8845 | 0 | -0.0077894 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.034742 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.216 | 0 | -0.0077644 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.034742 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0423 | 0 | -0.0077644 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.7505 | 147 | -0.0076691 | -1.1274
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.2147 | 138 | -0.0076691 | -1.0583
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.3338 | 140 | -0.0076691 | -1.0737
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.7505 | 147 | -0.0076691 | -1.1274
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.8339 | 182 | -0.0076691 | -1.3958
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.059527 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.7863 | 198 | -0.0076691 | -1.5185
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.034859 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.194 | 0 | -0.0076474 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.035056 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.23137 | 0 | -0.0074504 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.035056 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2024 | 0 | -0.0074504 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.035251 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9657 | 0 | -0.0072554 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.035251 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.27 | 0 | -0.0072554 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.035251 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5567 | 0 | -0.0072554 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.035251 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5613 | 0 | -0.0072554 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.3667 | 208.2 | -0.0071234 | -1.4831
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.0279 | 142.1 | -0.0071234 | -1.0122
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.6847 | 132.4 | -0.0071234 | -0.94314
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.8121 | 136 | -0.0071234 | -0.96878
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 1 | 5.2013 | 147 | -0.0071234 | -1.0471
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.035383 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.4304 | 210 | -0.0071234 | -1.4959
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4772 | 70 | -0.0071174 | -0.49822
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4772 | 70 | -0.0071174 | -0.49822
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.2841 | 92.8 | -0.0071174 | -0.6605
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8311 | 80 | -0.0071174 | -0.56939
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8311 | 80 | -0.0071174 | -0.56939
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.035389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.0697 | 115 | -0.0071174 | -0.8185
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.035396 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3094 | 0 | -0.0071104 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.035417 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0542 | 0 | -0.0070894 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.035426 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5603 | 0 | -0.0070804 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.03551 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6062 | 0 | -0.0069964 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.035551 | west | 8 | N | N | Nwest | Nwest | 1 | 0.91722 | 0 | -0.0069554 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.058762 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.9381 | 50 | -0.0069041 | -0.34521
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.058762 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.9381 | 50 | -0.0069041 | -0.34521
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.058762 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.9381 | 50 | -0.0069041 | -0.34521
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.058762 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.9381 | 50 | -0.0069041 | -0.34521
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.035768 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2922 | 0 | -0.0067384 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.035785 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2942 | 0 | -0.0067214 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.035838 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3006 | 0 | -0.0066684 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.035838 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.3503 | 0 | -0.0066684 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.035838 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0996 | 0 | -0.0066684 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.035856 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0676 | 0 | -0.0066504 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.035872 | west | 8 | N | N | Nwest | Nwest | 1 | 2.511 | 0 | -0.0066344 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.035872 | west | 8 | N | N | Nwest | Nwest | 1 | 2.633 | 0 | -0.0066344 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.035872 | west | 8 | N | N | Nwest | Nwest | 1 | 2.5254 | 0 | -0.0066344 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.035892 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4606 | 0 | -0.0066144 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.035892 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4606 | 0 | -0.0066144 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.035982 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3973 | 0 | -0.0065244 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.035982 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.916 | 0 | -0.0065244 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.035982 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1964 | 0 | -0.0065244 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.035982 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3862 | 0 | -0.0065244 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.058375 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0065171 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.058375 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0065171 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.058375 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0065171 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3813 | 66 | -0.0064264 | -0.42414
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.4895 | 69 | -0.0064264 | -0.44342
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.4895 | 69 | -0.0064264 | -0.44342
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.4174 | 67 | -0.0064264 | -0.43057
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.4174 | 67 | -0.0064264 | -0.43057
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.03608 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.3452 | 65 | -0.0064264 | -0.41772
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.036122 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2757 | 0 | -0.0063844 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.036153 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.0976 | 0 | -0.0063534 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.036153 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3384 | 0 | -0.0063534 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.05821 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -24.681 | 0 | -0.0063521 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.05821 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -24.7392 | 0 | -0.0063521 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.036164 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5802 | 0 | -0.0063424 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.036164 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.206 | 0 | -0.0063424 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.036164 | west | 7 | N | N | Nwest | Nwest | 1 | 0.9041 | 0 | -0.0063424 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.036164 | west | 7 | N | N | Nwest | Nwest | 1 | 1.6527 | 0 | -0.0063424 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.036164 | west | 7 | N | N | Nwest | Nwest | 1 | 1.6527 | 0 | -0.0063424 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.0582 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -23.9784 | 412 | -0.0063421 | -2.613
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.0582 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -23.28 | 400 | -0.0063421 | -2.5369
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.058138 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.1508 | 209 | -0.0062801 | -1.3125
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.058138 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.5578 | 216 | -0.0062801 | -1.3565
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.058138 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.6743 | 46 | -0.0062801 | -0.28889
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.058138 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.7325 | 47 | -0.0062801 | -0.29517
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.058138 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.6743 | 46 | -0.0062801 | -0.28889
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.058138 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.6743 | 46 | -0.0062801 | -0.28889
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.036265 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0463 | 0 | -0.0062414 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.058081 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -23.639 | 407 | -0.0062231 | -2.5328
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.036339 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5424 | 0 | -0.0061674 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.036339 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5424 | 0 | -0.0061674 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.036395 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4592 | 0 | -0.0061114 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.036395 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6759 | 0 | -0.0061114 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.057907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.9756 | 155 | -0.0060491 | -0.93762
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.057907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.8442 | 170 | -0.0060491 | -1.0284
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.057907 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.9756 | 155 | -0.0060491 | -0.93762
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.3704 | 0 | -0.0059624 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9285 | 0 | -0.0059624 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.9334 | 0 | -0.0059624 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3487 | 0 | -0.0059624 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.8371 | 0 | -0.0059624 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.036544 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.9418 | 0 | -0.0059624 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.036586 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6465 | 0 | -0.0059204 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.036586 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6281 | 0 | -0.0059204 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.036586 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1099 | 0 | -0.0059204 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.036586 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2074 | 0 | -0.0059204 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.057768 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.3505 | 58 | -0.0059101 | -0.34279
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.057768 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.1414 | 89 | -0.0059101 | -0.526
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.057768 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.5418 | 44 | -0.0059101 | -0.26005
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.057768 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.5418 | 44 | -0.0059101 | -0.26005
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.057768 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.484 | 43 | -0.0059101 | -0.25414
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.057768 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.5996 | 45 | -0.0059101 | -0.26596
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.036605 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.5121 | 0 | -0.0059014 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.036605 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 21.4871 | 0 | -0.0059014 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.036711 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5066 | 0 | -0.0057954 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.057585 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -31.4414 | 0 | -0.0057271 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.057585 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -43.1887 | 0 | -0.0057271 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.037024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.5795 | 150.7 | -0.0054824 | -0.8262
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.037024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.5906 | 151 | -0.0054824 | -0.82784
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.037024 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5681 | 177.4 | -0.0054824 | -0.97258
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.037107 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.6217 | 151.5 | -0.0053994 | -0.81801
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.037107 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.6514 | 152.3 | -0.0053994 | -0.82233
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.037107 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5865 | 177.5 | -0.0053994 | -0.9584
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.037239 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2343 | 0 | -0.0052674 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.056951 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.68341 | 0 | -0.0050931 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.037834 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1336 | 0 | -0.0046724 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.037836 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.9293 | 0 | -0.0046704 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.056119 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.76883 | 0 | -0.0042611 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.038251 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3114 | 0 | -0.0042554 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.038593 | west | 4 | Y | N | Ywest | Nwest | 1 | 25.0739 | 0 | -0.0039134 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.03887 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.0743 | 182 | -0.0036364 | -0.66183
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.03887 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 18.8131 | 484 | -0.0036364 | -1.76
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.038883 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.9442 | 0 | -0.0036234 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.038901 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0036054 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.055408 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.99734 | 0 | -0.0035501 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.055408 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.99734 | 0 | -0.0035501 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.055408 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.83112 | 0 | -0.0035501 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.039047 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.779 | 0 | -0.0034594 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.039047 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.0761 | 0 | -0.0034594 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.039047 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.6618 | 0 | -0.0034594 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.039047 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.5798 | 0 | -0.0034594 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.039212 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 30.7814 | 0 | -0.0032944 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.039212 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 31.1735 | 0 | -0.0032944 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.039212 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 30.5854 | 0 | -0.0032944 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.039567 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.4815 | 366 | -0.0029394 | -1.0758
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.039643 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.5936 | 242 | -0.0028634 | -0.69295
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.039658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.79316 | 20 | -0.0028484 | -0.056968
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.039658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.79316 | 20 | -0.0028484 | -0.056968
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.039658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.79316 | 20 | -0.0028484 | -0.056968
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.039658 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.67419 | 17 | -0.0028484 | -0.048423
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.054365 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.5285 | 0 | -0.0025071 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.4923 | 161 | -0.0021814 | -0.35121
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.6133 | 164 | -0.0021814 | -0.35775
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.6133 | 164 | -0.0021814 | -0.35775
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6945 | 414 | -0.0021814 | -0.90311
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5327 | 162 | -0.0021814 | -0.35339
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.4923 | 161 | -0.0021814 | -0.35121
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.573 | 163 | -0.0021814 | -0.35557
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.040325 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.4929 | 409 | -0.0021814 | -0.8922
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.040514 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.2649 | 204 | -0.0019924 | -0.40645
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.040514 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.1433 | 201 | -0.0019924 | -0.40048
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.040514 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.8044 | 242 | -0.0019924 | -0.48216
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.04059 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.8118 | 20 | -0.0019164 | -0.038328
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.04059 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.0148 | 25 | -0.0019164 | -0.04791
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.04059 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.6642 | 41 | -0.0019164 | -0.078573
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.040607 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 15.7555 | 388 | -0.0018994 | -0.73697
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.040607 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 20.9126 | 515 | -0.0018994 | -0.9782
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.040608 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 22.6593 | 0 | -0.0018984 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.040608 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 23.512 | 0 | -0.0018984 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.040608 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 32.8113 | 0 | -0.0018984 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.040623 | north | 8 | N | N | Nnorth | Nnorth | 1 | 3.0467 | 0 | -0.0018834 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.040623 | north | 8 | N | N | Nnorth | Nnorth | 1 | 3.2336 | 0 | -0.0018834 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.040623 | north | 8 | N | N | Nnorth | Nnorth | 1 | 3.5911 | 0 | -0.0018834 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.040632 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.2099 | 79 | -0.0018744 | -0.14808
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.040632 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.307 | 106 | -0.0018744 | -0.19869
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.040632 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.9323 | 146 | -0.0018744 | -0.27366
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.040632 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 3.088 | 76 | -0.0018744 | -0.14246
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5029 | 160 | -0.0018634 | -0.29815
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.3403 | 156 | -0.0018634 | -0.29069
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.966 | 196 | -0.0018634 | -0.36523
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.3403 | 156 | -0.0018634 | -0.29069
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.381 | 157 | -0.0018634 | -0.29256
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.040643 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.0473 | 198 | -0.0018634 | -0.36896
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.040652 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.6261 | 40 | -0.0018544 | -0.074177
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.040665 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 15.046 | 370 | -0.0018414 | -0.68132
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.6931 | 0 | -0.0018414 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.7338 | 0 | -0.0018414 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | 1 | 12.5655 | 0 | -0.0018414 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.8151 | 0 | -0.0018414 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.8558 | 0 | -0.0018414 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.040665 | north | 1 | N | N | Nnorth | Nnorth | 1 | 12.6061 | 0 | -0.0018414 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.040667 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.88 | 0 | -0.0018394 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.040683 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.4882 | 0 | -0.0018234 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.040683 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.4882 | 0 | -0.0018234 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.040698 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.9187 | 170 | -0.0018084 | -0.30743
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.040698 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 21.163 | 520 | -0.0018084 | -0.94038
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.040722 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0017844 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.040722 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0017844 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.040728 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6291 | 0 | -0.0017784 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.040728 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.6291 | 0 | -0.0017784 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.040876 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016304 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.040888 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0016184 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.040948 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.6067 | 0 | -0.0015584 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.041007 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.4604 | 60 | -0.0014994 | -0.089965
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.041007 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.5834 | 63 | -0.0014994 | -0.094463
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.041014 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.1871 | 224 | -0.0014924 | -0.3343
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.041208 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.8625 | 118 | -0.0012984 | -0.15321
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.041208 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.7389 | 115 | -0.0012984 | -0.14932
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.041208 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 22.9116 | 556 | -0.0012984 | -0.72192
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.041277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8878 | 288 | -0.0012294 | -0.35407
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.041277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0677 | 147 | -0.0012294 | -0.18072
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.041277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0677 | 147 | -0.0012294 | -0.18072
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.041323 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.4794 | 0 | -0.0011834 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.041459 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0010474 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.041459 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0010474 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.041459 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0010474 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.041615 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.74907 | 18 | -0.00089141 | -0.016045
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.041615 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.74907 | 18 | -0.00089141 | -0.016045
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.041615 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.5814 | 38 | -0.00089141 | -0.033874
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.041655 | north | 3 | N | N | Nnorth | Nnorth | 1 | 48.1948 | 0 | -0.00085141 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.041655 | north | 3 | N | N | Nnorth | Nnorth | 1 | 48.2365 | 0 | -0.00085141 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.041761 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.0747 | 217.3 | -0.00074541 | -0.16198
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.041761 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.561 | 205 | -0.00074541 | -0.15281
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.041761 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.3757 | 272.4 | -0.00074541 | -0.20305
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.041902 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00060441 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.041923 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 3.0604 | 73 | -0.00058341 | -0.042589
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.041923 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.9888 | 119 | -0.00058341 | -0.069426
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.041923 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.5942 | 205 | -0.00058341 | -0.1196
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.041923 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.2761 | 102 | -0.00058341 | -0.059508
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.041923 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.0246 | 96 | -0.00058341 | -0.056008
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.042051 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 18.2922 | 435 | -0.00045541 | -0.19811
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.042065 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.2447 | 196 | -0.00044141 | -0.086517
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.042065 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6692 | 111 | -0.00044141 | -0.048997
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.042106 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.6319 | 395 | -0.00040041 | -0.15816
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.042106 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 18.3161 | 435 | -0.00040041 | -0.17418
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.042559 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.9791 | 70 | 5.2586e-05 | 0.003681
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.042559 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.9366 | 69 | 5.2586e-05 | 0.0036284
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.042559 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.9366 | 69 | 5.2586e-05 | 0.0036284
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.042559 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.894 | 68 | 5.2586e-05 | 0.0035759
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.051454 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2349 | 24 | 0.00040386 | 0.0096926
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.051454 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.2349 | 24 | 0.00040386 | 0.0096926
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.051454 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.1834 | 23 | 0.00040386 | 0.0092887
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.050965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0965 | 100 | 0.00089286 | 0.089286
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.050965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -5.0965 | 100 | 0.00089286 | 0.089286
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.050965 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.00089286 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.050965 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.00089286 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.050965 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.00089286 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.050965 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.00089286 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.05096 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.00089786 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.050906 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.42761 | 8.4 | 0.00095186 | 0.0079956
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.043463 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.4054 | 216.4 | 0.00095659 | 0.20701
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.043463 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3924 | 216.1 | 0.00095659 | 0.20672
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.043579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.7617 | 224 | 0.0010726 | 0.24026
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.043579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.8489 | 226 | 0.0010726 | 0.2424
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.043579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2387 | 212 | 0.0010726 | 0.22739
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.043579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.1952 | 211 | 0.0010726 | 0.22632
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.04384 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.3651 | 168 | 0.0013336 | 0.22404
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.04384 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9456 | 90 | 0.0013336 | 0.12002
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.050385 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0014729 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.049622 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -31.2122 | 0 | 0.0022359 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.049593 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0022649 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.048967 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.5876 | 0 | 0.0028909 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.048967 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.53864 | 0 | 0.0028909 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.048967 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.5876 | 0 | 0.0028909 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.048936 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0029219 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.048312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.0777 | 146.5 | 0.0035459 | 0.51947
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.048312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1453 | 147.9 | 0.0035459 | 0.52443
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.048312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.358 | 173 | 0.0035459 | 0.61343
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.048207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.9788 | 207 | 0.0036509 | 0.75573
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.048207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.4465 | 216.7 | 0.0036509 | 0.79114
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.048207 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.6661 | 242 | 0.0036509 | 0.88351
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.048205 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9415 | 144 | 0.0036529 | 0.52601
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.048205 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.9415 | 144 | 0.0036529 | 0.52601
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.048205 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.2431 | 171 | 0.0036529 | 0.62464
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.048106 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.828 | 38 | 0.0037519 | 0.14257
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.048106 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.92845 | 19.3 | 0.0037519 | 0.072411
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.048106 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.72159 | 15 | 0.0037519 | 0.056278
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.048106 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.261 | 47 | 0.0037519 | 0.17634
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.048106 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.0037519 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.5187 | 0 | 0.0037869 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9709 | 0 | 0.0037869 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8267 | 0 | 0.0037869 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.91335 | 0 | 0.0037869 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.5187 | 0 | 0.0037869 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7306 | 0 | 0.0037869 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0671 | 0 | 0.0037869 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0576 | 0 | 0.0037869 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.1145 | 0 | 0.0037869 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4036 | 0 | 0.0037869 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6439 | 0 | 0.0037869 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.048071 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4036 | 0 | 0.0037869 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.047987 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3916 | 0 | 0.0038709 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.047744 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8143 | 0 | 0.0041139 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.047741 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8142 | 0 | 0.0041169 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.047691 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1923 | 0 | 0.0041669 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.047691 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.1923 | 0 | 0.0041669 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.047675 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.9235 | 334 | 0.0041829 | 1.3971
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.047675 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -16.2095 | 340 | 0.0041829 | 1.4222
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.047675 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.5815 | 180 | 0.0041829 | 0.75291
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.047675 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.5815 | 180 | 0.0041829 | 0.75291
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.047576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.5637 | 180 | 0.0042819 | 0.77073
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.047567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.0542 | 0 | 0.0042909 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.047567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.0685 | 0 | 0.0042909 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.047567 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.2778 | 0 | 0.0042909 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.047561 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.9805 | 336 | 0.0042969 | 1.4437
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.047561 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.561 | 180 | 0.0042969 | 0.77343
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1812 | 0 | 0.0046079 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1812 | 0 | 0.0046079 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1812 | 0 | 0.0046079 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.756 | 0 | 0.0046079 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1812 | 0 | 0.0046079 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1812 | 0 | 0.0046079 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1812 | 0 | 0.0046079 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.04725 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.70875 | 0 | 0.0046079 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.047171 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.7926 | 144 | 0.0046869 | 0.67491
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.047171 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.8681 | 188 | 0.0046869 | 0.88113
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.4331 | 0 | 0.0048129 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.1979 | 0 | 0.0048129 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -1 | -4.7045 | 0 | 0.0048129 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.8215 | 0 | 0.0048129 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.9156 | 0 | 0.0048129 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.047045 | south | 8 | N | N | Nsouth | Nsouth | -1 | -5.9747 | 0 | 0.0048129 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.047045 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.56454 | 0 | 0.0048129 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.046635 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4044 | 0 | 0.0052229 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.04656 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2209 | 47.7 | 0.0052979 | 0.25271
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.04656 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.7367 | 37.3 | 0.0052979 | 0.19761
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.04656 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.1418 | 46 | 0.0052979 | 0.2437
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.04656 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.2349 | 48 | 0.0052979 | 0.2543
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.046129 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.0148 | 22 | 0.0057289 | 0.12603
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.046129 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.50742 | 11 | 0.0057289 | 0.063017
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.046129 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.50742 | 11 | 0.0057289 | 0.063017
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.045704 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.68556 | 0 | 0.0061539 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.045704 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0512 | 0 | 0.0061539 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.045368 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.36294 | 0 | 0.0064899 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2646 | 0 | 0.0066929 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.31616 | 0 | 0.0066929 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7614 | 0 | 0.0066929 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.67748 | 0 | 0.0066929 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.31616 | 0 | 0.0066929 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.67748 | 0 | 0.0066929 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7614 | 0 | 0.0066929 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.045165 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7614 | 0 | 0.0066929 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.043876 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.106 | 0 | 0.0079819 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4349 | 0 | 0.0083779 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5219 | 0 | 0.0083779 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4349 | 0 | 0.0083779 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4784 | 0 | 0.0083779 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4088 | 0 | 0.0083779 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.087 | 0 | 0.0083779 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0001 | 0 | 0.0083779 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2174 | 0 | 0.0083779 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8957 | 0 | 0.0083779 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.04348 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2175 | 0 | 0.0083779 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.054469 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.81703 | 0 | 0.011963 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.054469 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.81703 | 0 | 0.011963 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.037583 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.014275 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.057078 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.5617 | 150 | 0.014572 | 2.1857
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.057078 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.5662 | 80 | 0.014572 | 1.1657
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.035961 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21577 | 0 | 0.015897 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.058959 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.0345 | 255 | 0.016453 | 4.1954
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.058959 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.7849 | 149 | 0.016453 | 2.4514
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.058959 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.0207 | 153 | 0.016453 | 2.5172
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.061253 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.018747 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.061253 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 48.2061 | 787 | 0.018747 | 14.7536
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.061576 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.01907 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.061576 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.01907 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.029337 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -39.1062 | 0 | 0.022521 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.029337 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -38.9595 | 0 | 0.022521 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.028987 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.95657 | 0 | 0.022871 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.028987 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.72467 | 0 | 0.022871 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.028987 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022871 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.1886 | 76 | 0.023061 | 1.7526
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.1886 | 76 | 0.023061 | 1.7526
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.0237 | 105 | 0.023061 | 2.4214
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.131 | 74 | 0.023061 | 1.7065
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.131 | 74 | 0.023061 | 1.7065
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.028797 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.9373 | 102 | 0.023061 | 2.3522
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.027247 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7983 | 66 | 0.024611 | 1.6243
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3721 | 0 | 0.029728 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5801 | 0 | 0.029728 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.99585 | 0 | 0.029728 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2351 | 0 | 0.029728 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9032 | 0 | 0.029728 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9474 | 0 | 0.029728 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1065 | 0 | 0.029728 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.39834 | 0 | 0.029728 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0802 | 0 | 0.029728 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5491 | 0 | 0.029728 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3942 | 0 | 0.029728 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5934 | 0 | 0.029728 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.434 | 0 | 0.029728 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2351 | 0 | 0.029728 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1466 | 0 | 0.029728 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2794 | 0 | 0.029728 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6819 | 0 | 0.029728 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7704 | 0 | 0.029728 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7704 | 0 | 0.029728 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.02213 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7842 | 0 | 0.029728 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.020811 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4776 | 0 | 0.031047 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.020811 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20811 | 0 | 0.031047 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.019754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1927 | 0 | 0.032104 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.019754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1927 | 0 | 0.032104 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.019754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.3507 | 0 | 0.032104 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.019754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1631 | 0 | 0.032104 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.016127 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74345 | 0 | 0.035731 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.016002 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -10.4173 | 0 | 0.035856 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.016002 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -9.0251 | 0 | 0.035856 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.016002 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -9.6012 | 0 | 0.035856 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.015971 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6033 | 0 | 0.035887 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.015971 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6033 | 0 | 0.035887 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.015971 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.9129 | 0 | 0.035887 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.015582 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51421 | 0 | 0.036276 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.015364 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.4736 | 161 | 0.036494 | 5.8755
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.015364 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.5504 | 166 | 0.036494 | 6.058
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.015364 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.8103 | 248 | 0.036494 | 9.0505
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.015364 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -8.3887 | 546 | 0.036494 | 19.9256
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.015364 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -9.8791 | 0 | 0.036494 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.015364 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.19973 | 13 | 0.036494 | 0.47442
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.013506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3547 | 0 | 0.038352 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.013506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2547 | 0 | 0.038352 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.013506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3871 | 0 | 0.038352 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.013506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3776 | 0 | 0.038352 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.013506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43219 | 0 | 0.038352 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.013506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40518 | 0 | 0.038352 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.013496 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.95552 | 0 | 0.038362 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.013496 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90018 | 0 | 0.038362 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.013496 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71529 | 0 | 0.038362 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0676 | 0 | 0.038362 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0716 | 0 | 0.038362 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.0554 | 0 | 0.038362 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2956 | 0 | 0.038362 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.013496 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.293 | 0 | 0.038362 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.013496 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53984 | 0 | 0.038362 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.01269 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.6345 | 50 | 0.039168 | 1.9584
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.012092 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.039766 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0349 | 0 | 0.040486 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.99619 | 0 | 0.040486 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.98936 | 0 | 0.040486 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61977 | 0 | 0.040486 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.011372 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13874 | 0 | 0.040486 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.011092 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.72098 | 0 | 0.040766 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.011092 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.66552 | 0 | 0.040766 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.011092 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.72098 | 0 | 0.040766 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.011092 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.72098 | 0 | 0.040766 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.49059 | 46 | 0.041193 | 1.8949
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.49059 | 46 | 0.041193 | 1.8949
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.49059 | 46 | 0.041193 | 1.8949
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.58657 | 55 | 0.041193 | 2.2656
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.58657 | 55 | 0.041193 | 2.2656
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.010665 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.57591 | 54 | 0.041193 | 2.2244
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.010569 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.82438 | 0 | 0.041289 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.010569 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.84552 | 0 | 0.041289 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7022 | 0 | 0.041428 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6386 | 0 | 0.041428 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6427 | 0 | 0.041428 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6375 | 0 | 0.041428 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.01043 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8057 | 0 | 0.041428 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.010306 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.36071 | 0 | 0.041552 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.010182 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12218 | 12 | 0.041676 | 0.50011
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.010182 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.041676 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.010175 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.7196 | 169 | 0.041683 | 7.0444
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.010165 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.6772 | 165 | 0.041693 | 6.8793
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.010157 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5134 | 0 | 0.041701 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.010157 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66122 | 0 | 0.041701 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.010132 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.1581 | 213 | 0.041726 | 8.8876
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.010129 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16409 | 0 | 0.041729 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.010126 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64806 | 0 | 0.041732 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.010126 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63996 | 0 | 0.041732 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.010126 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.83641 | 0 | 0.041732 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.010126 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74527 | 0 | 0.041732 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.010122 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.3078 | 228 | 0.041736 | 9.5158
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.010117 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8211 | 0 | 0.041741 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.010117 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6046 | 0 | 0.041741 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.010117 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5884 | 0 | 0.041741 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.009941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70581 | 0 | 0.041917 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.009941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71575 | 0 | 0.041917 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.009941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3877 | 0 | 0.041917 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.009941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.29823 | 0 | 0.041917 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.009656 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3132 | 0 | 0.042202 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.009638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.4048 | 42 | 0.04222 | 1.7732
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.009638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.4048 | 42 | 0.04222 | 1.7732
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.009638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.36624 | 38 | 0.04222 | 1.6044
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.009638 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.36624 | 38 | 0.04222 | 1.6044
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.009562 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6542 | 0 | 0.042296 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.009562 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2909 | 0 | 0.042296 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.94713 | 104 | 0.042751 | 4.4461
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.94713 | 104 | 0.042751 | 4.4461
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49178 | 54 | 0.042751 | 2.3085
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.48267 | 53 | 0.042751 | 2.2658
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49178 | 54 | 0.042751 | 2.3085
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.5191 | 57 | 0.042751 | 2.4368
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49178 | 54 | 0.042751 | 2.3085
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49178 | 54 | 0.042751 | 2.3085
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.52821 | 58 | 0.042751 | 2.4795
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.009107 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.52821 | 58 | 0.042751 | 2.4795
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.008944 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -6.5738 | 735 | 0.042914 | 31.5417
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30015 | 0 | 0.04303 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30633 | 0 | 0.04303 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28868 | 0 | 0.04303 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.40521 | 0 | 0.04303 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.15626 | 0 | 0.04303 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18009 | 0 | 0.04303 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17568 | 0 | 0.04303 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30898 | 0 | 0.04303 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1589 | 0 | 0.04303 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.75391 | 0 | 0.04303 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.008828 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3065 | 0 | 0.04303 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.008672 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10406 | 12 | 0.043186 | 0.51823
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.008493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.042465 | 0 | 0.043365 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.008493 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17835 | 0 | 0.043365 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55178 | 0 | 0.043369 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56027 | 0 | 0.043369 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59423 | 0 | 0.043369 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53481 | 0 | 0.043369 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52632 | 0 | 0.043369 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88286 | 0 | 0.043369 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.008489 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50085 | 0 | 0.043369 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.008482 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.10178 | 0 | 0.043376 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.00847 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -6.2932 | 743 | 0.043388 | 32.2372
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.00838 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.3157 | 0 | 0.043478 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.008327 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4322 | 172 | 0.043531 | 7.4873
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.008327 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4322 | 172 | 0.043531 | 7.4873
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.008327 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4322 | 172 | 0.043531 | 7.4873
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.007992 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3011 | 0 | 0.043866 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.007992 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2899 | 0 | 0.043866 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.007992 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2699 | 0 | 0.043866 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.007992 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1514 | 0 | 0.043866 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.007871 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.1327 | 398 | 0.043987 | 17.5068
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.42935 | 56 | 0.044191 | 2.4747
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.45235 | 59 | 0.044191 | 2.6073
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.42935 | 56 | 0.044191 | 2.4747
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.42935 | 56 | 0.044191 | 2.4747
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.45235 | 59 | 0.044191 | 2.6073
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.007667 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.42935 | 56 | 0.044191 | 2.4747
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.005692 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.98472 | 0 | 0.046166 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.005692 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.88795 | 0 | 0.046166 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.005692 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.87657 | 0 | 0.046166 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.005692 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.87657 | 0 | 0.046166 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.005692 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9221 | 0 | 0.046166 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051858 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051858 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051858 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051858 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051858 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.051858 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051858 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.051858 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.088554 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 50.3872 | 0 | 0.14041 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.088554 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 51.4499 | 0 | 0.14041 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 268
| 25 | 268
| 30 | 268
| 35 | 268
| 40 | 268
| 45 | 268
| 50 | 268
| 55 | 268
| 60 | 266
| 65 | 261
| 70 | 256
| 75 | 250
| 80 | 244
| 85 | 238
| 90 | 232
| 95 | 226
| 100 | 219
| 105 | 212
| 110 | 206
| 115 | 198
| Max | 268
| Min | 198
| Avg | 247.6