## test results
CRE test for: |  | 3668 RNDROCK1 - 3670 RNDRCKNE_ctg1 | [5 empty] | FAIL
Line Rating: |  | 247.95
Direcction |  | South | → | North |  | S-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3668 RNDROCK1 - 3670 RNDRCKNE_ctg1
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.038245
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.05305
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.034178
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.013987
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3668 RNDROCK1 - 3670 RNDRCKNE_ctg1
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.041314
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.06247
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.03436
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.013086
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3668 RNDROCK1 - 3670 RNDRCKNE_ctg1
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.10072
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.003885
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.051331
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.08741
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.039063
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.047265
PTDF tests
South | → | North | 0.039819 | 0.42071 | -0.42071 | -0.21445 | -0.039819 | 0.094364 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.094364 | -0.10072
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.062406
[6 empty] | Concentration |  | 0.66133 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.044191
[6 empty] | Concentration |  | 0.4683 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 176.22
| Percent of line rating => | [6 empty] | 71.07% | FAIL
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 4.4584
[7 empty] | B1(N-S) | 0.0471 | -0.40193 | -0.44903 | 0.0471
[7 empty] | B2 (N-W) | 0.00070701 | -0.016614 | -0.017321 | 0.00070701
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.0097015 | -0.21915 | -0.22885 | 0.0097015
[7 empty] | B4 (S-W) | -0.00012243 | 0.38958 | 0.38971 | -0.00012243
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.012889 | 0.18705 | 0.17416 | 0.012889
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.0089289 | -0.20179 | -0.21072 | 0.0089289
[7 empty] | test | 0 | 0.42071 | 0.42071 | 0
[7 empty] | B1 | 11.2%
Deployment Error Percent | [6 empty] | B2 | 0.1681%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 2.306%
[7 empty] | B4 | -0.0291%
[7 empty] | B5 | 3.064%
[7 empty] | B6 | 2.122%
[7 empty] | Max Abs Error | 11.2% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | S-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3668 RNDROCK1 - 3670 RNDRCKNE_ctg1 C:SANDOW__5-L_AUSTRO5_1Y C:L_AUSTRO5_1Y-SAND_TXU_59 [3429 - 7040 ckt1] and [7040 - 13429 ckt2] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3668 RNDROCK1 - 3670 RNDRCKNE_ctg1 C:SANDOW__5-L_AUSTRO5_1Y C:L_AUSTRO5_1Y-SAND_TXU_59 [3429 - 7040 ckt1] and [7040 - 13429 ckt2]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.057767 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -14.7306
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.057767 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -8.6073
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.053277 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.79915
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.053277 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.79915
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.057767 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -8.8384
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.055886 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -8.3829
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.055886 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -4.4709
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.040731 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -2.9734
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.040731 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -4.847
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.040731 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -8.3499
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.040731 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -4.1546
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.040731 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -3.9102
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.03949 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.47388
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.03949 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.47388
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.042648 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -7.1649
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.042648 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -3.8383
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.040423 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.72761
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.040423 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.72761
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.040423 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -1.5361
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.040084 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -11.5442
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.040084 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -5.8923
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.040084 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -5.8923
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.039756 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -4.4726
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.039459 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -1.5784
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.03944 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -3.1158
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.03944 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -4.1806
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.03944 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -5.7582
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.03944 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -2.9974
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.039815 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -2.3889
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.039815 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -2.5083
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.039397 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -0.78794
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.039398 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -0.98495
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.039398 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -1.6153
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.015554 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -7.2015
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -2.212
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -2.1785
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -2.2455
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -2.2455
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -2.2455
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.033515 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -3.8207
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.033515 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -17.2602
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -2.3026
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -2.4073
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -2.4073
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -2.3375
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -2.3375
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -2.2677
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.03468 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -2.4276
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.03468 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -2.5455
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.03468 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -2.4415
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.034789 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -5.2184
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.034789 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -7.6536
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.034972 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -3.4622
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.034972 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -2.1333
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.034961 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -4.9295
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.034972 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -0.8743
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.034972 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -1.5982
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.034972 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -1.5982
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.034961 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -4.1953
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.034359 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -0.88646
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.034234 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -3.4405
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.034576 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -4.1491
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.034225 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -1.985
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.034317 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -7.3507
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.035202 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -5.2803
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.033864 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -0.2235
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.033864 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -1.1615
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.035202 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -3.5554
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.034592 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -4.151
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | -0.038374 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | -14.0449
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.038451 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -9.3051
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.036642 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -14.6568
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.036644 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -8.648
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.037059 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -6.1147
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.039322 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -8.0217
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.039322 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -7.9037
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.039322 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -9.5159
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.038466 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.76932
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.038466 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.76932
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.038466 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.76932
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.038466 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -0.65392
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.039474 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -4.7369
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.040131 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -2.4079
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.03943 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -2.9573
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.03943 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -3.1386
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.03943 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -3.4856
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -6.3122
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -6.1544
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -7.7324
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -6.1544
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -6.1938
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -7.8113
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.039506 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -6.716
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.039506 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -20.5431
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.039473 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -14.605
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.039415 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -21.9936
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.039415 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -22.8213
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.039415 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -31.8473
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.040267 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -4.5099
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.040267 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -4.0267
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.040267 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -15.2209
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.040569 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -8.8156
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.040569 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -8.3166
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.040569 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -11.051
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.040709 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -31.3459
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.041367 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -2.8957
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.041367 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -2.8543
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.041367 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -2.8543
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.041367 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -2.813
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.040463 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -46.8157
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.040463 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -46.8562
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.042387 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -9.4947
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.042387 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -9.5795
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.042271 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -9.1474
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.042271 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -9.1348
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.042387 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -8.986
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.042387 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -8.9437
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.040914 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -16.161
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.040858 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -17.7732
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.040914 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -17.7976
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.039684 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -5.4764
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.040016 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -4.7219
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.040016 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -4.6018
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.040016 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -22.2489
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.039415 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -15.293
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.039415 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -20.2987
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.03802 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -29.8457
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.03802 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -30.2259
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.03802 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -29.6556
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.037678 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -6.8574
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.037678 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -18.2362
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.039822 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -8.9201
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.037691 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -1.8845
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.037709 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -1.5838
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.035413 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -21.779
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.035413 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -20.7874
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.06006 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -32.2522
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.06006 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -47.2672
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.060383 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -4.5287
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.060383 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -13.405
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.087362 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -49.709
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.05933 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 12.4
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.05933 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 12.8153
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.059273 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 24.1241
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.05933 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 2.7292
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.05933 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 2.7885
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.05933 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 2.7292
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.05933 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 2.7292
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.059403 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 25.1869
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.059403 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 25.2463
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.058961 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 3.4197
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.058961 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 5.2475
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.058961 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 2.5943
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.058961 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 2.5943
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.058961 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 2.5353
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.058961 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 2.6532
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.059392 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 24.4695
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.059392 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 23.7568
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.058777 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 32.0922
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.058777 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 44.0827
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.059567 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 3.6336
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.059567 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 5.6589
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.059567 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 8.9946
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.059099 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 9.1603
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.059099 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 10.0468
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.059099 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 9.1603
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.047321 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 1.0411
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.047321 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.52053
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.047321 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.52053
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.047752 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 2.2778
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.047752 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 1.7811
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.047752 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 2.1966
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.047752 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 2.2921
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.050159 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.60191
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.050159 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.55175
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.052646 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 1.2635
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.052646 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 1.2635
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.052646 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 1.2109
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.055557 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 22.0006
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.030529 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 40.6952
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.030529 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 40.5425
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.049298 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 1.8733
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.049298 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.95145
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.049298 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.73947
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.049298 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 2.317
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.029716 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -2.2287
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.035519 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -5.3278
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.033525 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -5.6825
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.013404 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -2.0106
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.03493 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -2.2006
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.037401 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -24.2994
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.039535 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -1.5814
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.039535 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -1.5814
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.066408 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 28.0242
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.061624 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 8.1344
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.061624 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 8.2576
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.061624 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 19.9046
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.070374 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 11.1191
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.070374 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 11.2598
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.070374 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 12.3155
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.063786 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 37.251
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.063786 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 37.9527
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.063753 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 27.605
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.065061 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 14.5672
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.065061 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 14.6387
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.065061 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 14.6127
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.065061 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 14.7493
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.10294 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.82354
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.10294 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.82354
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.056601 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 1.0188
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.056601 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 1.0188
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.056601 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.84901
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.057312 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.78517
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.074455 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 1.3402
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.074455 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 1.3402
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.092702 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 3.2446
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.092702 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 3.1519
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.092702 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 3.2446
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.067064 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 1.8778
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.067064 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 1.9449
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.033549 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -1.1742
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.033549 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -1.0065
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.059954 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 2.9977
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.059954 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 2.9977
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.059954 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 2.9977
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.059954 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 2.9977
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.07063 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.42378
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.0639 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.15336
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.0639 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.15336
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.0639 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.17892
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.062982 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.25193
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.062444 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.14987
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.062444 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.14987
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 8.9257
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 8.3792
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 8.5007
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 8.9257
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 11.0509
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 12.0224
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.073887 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 11.2678
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.073887 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 11.0461
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.073887 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 17.1861
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.062882 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 8.9292
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.062882 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 9.1179
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.062882 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 9.4952
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.062882 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 18.2358
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.030179 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.99591
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.030179 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.75448
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.050159 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.60191
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.047827 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 3.4914
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 3.5291
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 3.6184
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 1.298
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.3245
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 3.5291
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 3.5738
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 3.5023
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 1.1168
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 2.0549
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.050815 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 31.9626
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.048364 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 6.9644
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.048364 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 9.0924
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.058143 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.69772
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.037154 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.22292
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.048753 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 16.381
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.048867 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 16.3216
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.048867 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 16.6148
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.048936 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 1.8596
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.048884 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 1.2221
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.048884 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 1.2221
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.048934 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 1.8595
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.049179 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 1.4262
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.048759 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 7.231
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.048759 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 7.2456
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.048759 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 7.4601
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 7.6214
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 7.3803
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 4.8237
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 6.9944
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 7.0908
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 6.1261
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.049504 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 7.2523
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.049504 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 7.3216
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.049504 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 8.5642
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.049399 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 10.2256
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.049399 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 10.7048
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.049399 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 11.9546
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.049398 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 7.1133
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.049398 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 7.1133
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.049398 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 8.4471
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.10214 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 31.6631
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.10214 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 42.1834
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.099995 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 4.1998
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.099995 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 4.3998
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.099995 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 4.3998
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.099995 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 4.6998
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 4.7585
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 4.4672
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 4.4672
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 4.5643
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.097112 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 14.9552
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.097112 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 14.3726
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 4.6614
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 4.6614
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -2.3938
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -2.3938
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -3.1735
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -2.7358
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -2.7358
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -3.9327
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -7.1184
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -4.8584
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -4.5268
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -4.6498
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -5.0259
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -7.1799
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.035394 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -7.3973
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.035394 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -4.4773
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.035394 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -8.8131
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.035394 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -6.9726
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.034789 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -6.9578
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.034789 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -4.2408
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.033667 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -5.0164
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.0347 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -6.246
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.0347 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -6.246
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.034664 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -7.7994
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.035147 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -4.3934
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.035147 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -4.3934
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -5.5262
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -5.5657
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -12.1972
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -5.6446
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -5.6841
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -12.2366
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.040873 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -8.0111
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.040873 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -4.5369
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.039696 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -6.3004
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -6.4178
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -6.4178
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -16.2011
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -6.3395
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -6.3004
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -6.3787
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -16.0054
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.03953 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.03953 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.037855 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -5.6025
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.037855 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -4.9211
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.037855 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -5.489
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.037855 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -15.1041
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.035832 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -5.3999
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.035832 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -5.4106
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.035832 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -6.3566
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.035915 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -5.4411
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.035915 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -5.4699
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.035915 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -6.3749
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.087362 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -50.7573
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.025827 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -22.0821
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.025827 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -22.0821
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.021257 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.68022
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.023201 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -1.1136
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.023201 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -1.0672
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.021425 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.2571
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.021425 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -1.0927
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.021425 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.36423
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.021425 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.47135
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.021425 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.53563
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.023201 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -2.4361
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.035073 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -2.9461
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.029647 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -2.3718
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.029612 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -4.4418
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.029612 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -4.4418
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.014688 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 1.0399
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.014688 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 0.97969
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.014688 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 0.77846
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 2.2502
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 2.2546
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 2.237
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 1.41
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 3.5839
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.014688 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 0.58752
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.014698 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 1.4742
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.014698 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 1.3654
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.014698 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 1.5095
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.014698 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 1.4992
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.014698 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 0.47034
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.014698 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 0.44094
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.020946 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 2.325
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.020946 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 2.325
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.020946 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 2.4926
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.020946 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 2.2936
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.025827 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -3.9335
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.025827 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -3.9515
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.010849 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 1.4755
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.016774 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.55354
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.01083 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.45486
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.01083 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.45486
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.01083 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.41154
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.01083 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.41154
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.022003 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 1.5622
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.022003 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.22003
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.017164 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 2.7977
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.017164 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 2.7977
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.017164 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 4.2052
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.012284 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.79846
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.012284 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 0.73704
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.012284 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.79846
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.012284 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.79846
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 1.691
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 0.73882
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 1.1434
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 1.1007
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 1.0932
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 0.68479
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.15329
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.009662 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 7.1789
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.010136 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 7.45
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.00952 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.6374
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.00952 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.6374
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.00952 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.6374
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.006885 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 1.1911
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.010755 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 1.8606
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.010755 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 1.4519
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 1.4952
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 1.4823
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 1.4593
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 2.4723
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.011318 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 0.72435
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.011318 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 0.7153
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.011318 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 0.93487
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.011318 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 0.833
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 1.8967
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 1.8258
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 1.8305
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 1.8247
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 3.1263
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.009686 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.04843
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.009686 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 0.20341
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.011613 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -1.7907
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.011613 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -1.8116
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.011613 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -1.8116
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.011613 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -4.4129
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.009063 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 3.6071
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.54542
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.54542
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.54542
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.65214
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.65214
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 0.64028
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.029861 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -24.695
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.029861 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -24.4562
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.017319 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.79841
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 2.2792
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 2.2792
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 3.149
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 2.2193
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 2.2193
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 3.059
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.011309 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 2.0356
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.011309 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 1.7936
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.011309 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 1.7755
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.011498 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 0.40243
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.013284 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 6.0974
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 0.62926
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 0.63895
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 0.67767
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 0.6099
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 0.60022
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 1.0068
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 0.57118
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.006885 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 1.0741
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.006885 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.0603
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.006885 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.0603
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.006885 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 1.1154
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.009572 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 1.5028
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 0.79044
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 0.80158
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 0.43419
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 0.33399
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.011761 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 0.91736
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.011761 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 0.94088
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 0.1834
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.011357 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 1.8739
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.011367 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 1.921
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.011324 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 2.412
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.011314 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 2.5796
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.011374 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.13649
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.011374 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 0.20473
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.013882 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 0.6941
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 1.0711
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 1.0711
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.55615
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.54585
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.55615
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.58704
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.55615
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.55615
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.59734
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.59734
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.009865 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.11838
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.4961
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.52268
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.4961
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.4961
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.52268
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.4961
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.028439 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 1.877
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.016556 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 2.6655
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.016556 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 2.7483
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.016556 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 4.1059
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.016556 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 9.0396
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.016556 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 10.6455
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.017194 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 11.1933
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.017194 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 9.6974
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.017194 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 10.3164
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.016556 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.21523
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.009674 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.11609
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 0.34068
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 0.34769
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 0.32765
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 0.45992
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 0.17735
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 0.20441
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 0.1994
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 0.3507
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 0.18036
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 0.85571
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 1.483
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 1.446
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 1.6652
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 1.0495
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 2.3555
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 2.0057
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 2.0523
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 1.1661
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.4198
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 2.1923
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 1.6325
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 1.4693
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 1.6792
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 1.5113
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 2.3555
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 2.2622
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 2.4022
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 1.7725
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 1.8658
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 1.8658
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 3.9881
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.43762
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.027989 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -2.1412
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.029716 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -2.3773
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.029716 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -1.1886
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.029994 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -2.3995
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.029655 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -2.3724
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.028224 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -2.2579
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.027756 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -2.3315
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.029994 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -2.3995
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 7.1105
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.034646 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -4.1575
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.034646 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -8.0725
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.034646 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -5.8967
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 13.8468
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 11.4766
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 13.9716
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 7.1729
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 6.2373
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.036047 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -2.1628
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.034233 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.020289 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.031024 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -0.14892
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -1.3257
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -3.8003
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -4.7725
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -4.2069
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -3.712
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -2.8458
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.034204 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -5.1306
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.034059 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -3.8316
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.034059 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -5.0918
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.034059 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -6.335
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.034059 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -7.3057
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.049298 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.038776 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.052152 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 1.2508
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 1.9477
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 3.3057
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 4.6307
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 2.0198
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 1.872
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.936
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 4.6307
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 1.7735
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 2.1183
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 1.0838
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 1.8079
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.69535
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.3245
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.69535
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 1.8079
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 1.8079
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 7.2909
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 2.4632
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 2.7095
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 2.4632
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.048237 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.57884
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.046896 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.70344
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.046896 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 1.0786
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.045069 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 2.1633
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.04656 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.37248
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.048768 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 8.7782
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.048753 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 8.7755
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.048867 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 8.7961
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.048867 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 8.7961
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.052157 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 5.2157
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.052157 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 5.2157
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 1.211
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 1.211
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 1.211
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.77507
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 1.211
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 1.211
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 1.211
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.72663
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.052157 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.052157 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 26.0785
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.052157 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 26.0785
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.052157 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.051577 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.030179 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.050786 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.050128 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L:3668 RNDROCK1 - 3670 RNDRCKNE_ctg1 C:SANDOW__5-L_AUSTRO5_1Y C:L_AUSTRO5_1Y-SAND_TXU_59 [3429 - 7040 ckt1] and [7040 - 13429 ckt2] | [7 empty] | 176.22
Number of Bus | Name of Bus | ID | Max MW | L:3668 RNDROCK1 - 3670 RNDRCKNE_ctg1 C:SANDOW__5-L_AUSTRO5_1Y C:L_AUSTRO5_1Y-SAND_TXU_59 [3429 - 7040 ckt1] and [7040 - 13429 ckt2] | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.057767 | north | -0.019522 | -0.11082 | -0.023589 | -0.071754 | 0.019522 | North | N | 0.019522 | 0
239 | BOSQUESW | 1 | 149 | -0.057767 | north | -0.019522 | -0.11082 | -0.023589 | -0.071754 | 0.019522 | North | N | 0.019522 | 0
244 | WHITNYDM | 1 | 15 | -0.053277 | north | -0.015032 | -0.10633 | -0.019099 | -0.067264 | 0.015032 | North | N | 0.015032 | 0
245 | WHITNYDM | 2 | 15 | -0.053277 | north | -0.015032 | -0.10633 | -0.019099 | -0.067264 | 0.015032 | North | N | 0.015032 | 0
247 | BOSQUESW | 2 | 153 | -0.057767 | north | -0.019522 | -0.11082 | -0.023589 | -0.071754 | 0.019522 | North | N | 0.019522 | 0
251 | BOSQUESW | 2 | 150 | -0.055886 | north | -0.017641 | -0.10894 | -0.021708 | -0.069873 | 0.017641 | North | N | 0.017641 | 0
253 | BOSQUESW | 2 | 80 | -0.055886 | north | -0.017641 | -0.10894 | -0.021708 | -0.069873 | 0.017641 | North | N | 0.017641 | 0
332 | RWMILLER | 1 | 73 | -0.040731 | north | -0.0024861 | -0.093781 | -0.0065527 | -0.054718 | 0.0024861 | North | N | 0.0024861 | 0
333 | RWMILLER | 2 | 119 | -0.040731 | north | -0.0024861 | -0.093781 | -0.0065527 | -0.054718 | 0.0024861 | North | N | 0.0024861 | 0
334 | RWMILLER | 3 | 205 | -0.040731 | north | -0.0024861 | -0.093781 | -0.0065527 | -0.054718 | 0.0024861 | North | N | 0.0024861 | 0
335 | RWMILLER | 4 | 102 | -0.040731 | north | -0.0024861 | -0.093781 | -0.0065527 | -0.054718 | 0.0024861 | North | N | 0.0024861 | 0
336 | RWMILLER | 5 | 96 | -0.040731 | north | -0.0024861 | -0.093781 | -0.0065527 | -0.054718 | 0.0024861 | North | N | 0.0024861 | 0
344 | MRSSHPRD | 1 | 12 | -0.03949 | north | -0.0012451 | -0.09254 | -0.0053117 | -0.053477 | 0.0012451 | North | N | 0.0012451 | 0
345 | MRSSHPRD | 2 | 12 | -0.03949 | north | -0.0012451 | -0.09254 | -0.0053117 | -0.053477 | 0.0012451 | North | N | 0.0012451 | 0
366 | JNSNCNTY | 1 | 168 | -0.042648 | north | -0.0044031 | -0.095698 | -0.0084697 | -0.056635 | 0.0044031 | North | N | 0.0044031 | 0
367 | JNSNCNTY | 2 | 90 | -0.042648 | north | -0.0044031 | -0.095698 | -0.0084697 | -0.056635 | 0.0044031 | North | N | 0.0044031 | 0
503 | NTHTEXAS | 1 | 18 | -0.040423 | north | -0.0021781 | -0.093473 | -0.0062447 | -0.05441 | 0.0021781 | North | N | 0.0021781 | 0
504 | NTHTEXAS | 2 | 18 | -0.040423 | north | -0.0021781 | -0.093473 | -0.0062447 | -0.05441 | 0.0021781 | North | N | 0.0021781 | 0
505 | NTHTEXAS | 3 | 38 | -0.040423 | north | -0.0021781 | -0.093473 | -0.0062447 | -0.05441 | 0.0021781 | North | N | 0.0021781 | 0
580 | JCKCNTY8 | 1 | 288 | -0.040084 | north | -0.0018391 | -0.093134 | -0.0059057 | -0.054071 | 0.0018391 | North | N | 0.0018391 | 0
581 | JCKCNTY8 | 2 | 147 | -0.040084 | north | -0.0018391 | -0.093134 | -0.0059057 | -0.054071 | 0.0018391 | North | N | 0.0018391 | 0
582 | JCKCNTY8 | 3 | 147 | -0.040084 | north | -0.0018391 | -0.093134 | -0.0059057 | -0.054071 | 0.0018391 | North | N | 0.0018391 | 0
728 | WOLFRIDG | 1 | 112.5 | -0.039756 | north | -0.0015111 | -0.092806 | -0.0055777 | -0.053743 | 0.0015111 | North | N | 0.0015111 | 0
837 | NEWMAN_G | 1 | 40 | -0.039459 | north | -0.0012141 | -0.092509 | -0.0052807 | -0.053446 | 0.0012141 | North | N | 0.0012141 | 0
842 | OLINGER_ | 1 | 79 | -0.03944 | north | -0.0011951 | -0.09249 | -0.0052617 | -0.053427 | 0.0011951 | North | N | 0.0011951 | 0
843 | OLINGER_ | 1 | 106 | -0.03944 | north | -0.0011951 | -0.09249 | -0.0052617 | -0.053427 | 0.0011951 | North | N | 0.0011951 | 0
844 | OLINGER_ | 1 | 146 | -0.03944 | north | -0.0011951 | -0.09249 | -0.0052617 | -0.053427 | 0.0011951 | North | N | 0.0011951 | 0
845 | OLINGER_ | 1 | 76 | -0.03944 | north | -0.0011951 | -0.09249 | -0.0052617 | -0.053427 | 0.0011951 | North | N | 0.0011951 | 0
923 | SPENCER_ | 1 | 60 | -0.039815 | north | -0.0015701 | -0.092865 | -0.0056367 | -0.053802 | 0.0015701 | North | N | 0.0015701 | 0
924 | SPENCER_ | 1 | 63 | -0.039815 | north | -0.0015701 | -0.092865 | -0.0056367 | -0.053802 | 0.0015701 | North | N | 0.0015701 | 0
948 | STEAM1 | 1 | 20 | -0.039397 | north | -0.0011521 | -0.092447 | -0.0052187 | -0.053384 | 0.0011521 | North | N | 0.0011521 | 0
949 | STEAM2 | 1 | 25 | -0.039398 | north | -0.0011531 | -0.092448 | -0.0052197 | -0.053385 | 0.0011531 | North | N | 0.0011531 | 0
950 | STEAM3 | 1 | 41 | -0.039398 | north | -0.0011531 | -0.092448 | -0.0052197 | -0.053385 | 0.0011531 | North | N | 0.0011531 | 0
990 | GIBN_CRE | 1 | 463 | -0.015554 | north | 0.022691 | -0.068604 | 0.018624 | -0.029541 | 0.018624 | west | Y | 0.022691 | 1.8828
1002 | PBCTAGE_ | A | 66 | -0.033515 | west | 0.0047299 | -0.086565 | 0.00066331 | -0.047502 | 0.00066331 | west | N | 0.00066331 | 0
1003 | PBCTBGE_ | B | 65 | -0.033515 | west | 0.0047299 | -0.086565 | 0.00066331 | -0.047502 | 0.00066331 | west | N | 0.00066331 | 0
1004 | PBCTCGE_ | C | 67 | -0.033515 | west | 0.0047299 | -0.086565 | 0.00066331 | -0.047502 | 0.00066331 | west | N | 0.00066331 | 0
1005 | PBCTDGE_ | D | 67 | -0.033515 | west | 0.0047299 | -0.086565 | 0.00066331 | -0.047502 | 0.00066331 | west | N | 0.00066331 | 0
1006 | PBCTEGE_ | E | 67 | -0.033515 | west | 0.0047299 | -0.086565 | 0.00066331 | -0.047502 | 0.00066331 | west | N | 0.00066331 | 0
1007 | PB5GEN_6 | MB | 114 | -0.033515 | west | 0.0047299 | -0.086565 | 0.00066331 | -0.047502 | 0.00066331 | west | N | 0.00066331 | 0
1008 | PB6GEN_7 | MB | 515 | -0.033515 | west | 0.0047299 | -0.086565 | 0.00066331 | -0.047502 | 0.00066331 | west | N | 0.00066331 | 0
1039 | MRGNAG_1 | A | 66 | -0.034888 | west | 0.0033569 | -0.087938 | -0.00070969 | -0.048875 | 0.00070969 | west | N | 0.00070969 | 0
1040 | MRGNBG_2 | B | 69 | -0.034888 | west | 0.0033569 | -0.087938 | -0.00070969 | -0.048875 | 0.00070969 | west | N | 0.00070969 | 0
1041 | MRGNCG_3 | C | 69 | -0.034888 | west | 0.0033569 | -0.087938 | -0.00070969 | -0.048875 | 0.00070969 | west | N | 0.00070969 | 0
1042 | MRGNDG_4 | D | 67 | -0.034888 | west | 0.0033569 | -0.087938 | -0.00070969 | -0.048875 | 0.00070969 | west | N | 0.00070969 | 0
1043 | MRGNEG_5 | E | 67 | -0.034888 | west | 0.0033569 | -0.087938 | -0.00070969 | -0.048875 | 0.00070969 | west | N | 0.00070969 | 0
1044 | MRGNFG_6 | F | 65 | -0.034888 | west | 0.0033569 | -0.087938 | -0.00070969 | -0.048875 | 0.00070969 | west | N | 0.00070969 | 0
1045 | CALENG1G | 1 | 70 | -0.03468 | west | 0.0035649 | -0.08773 | -0.00050169 | -0.048667 | 0.00050169 | west | N | 0.00050169 | 0
1046 | CALENG2G | 2 | 73.4 | -0.03468 | west | 0.0035649 | -0.08773 | -0.00050169 | -0.048667 | 0.00050169 | west | N | 0.00050169 | 0
1047 | CALENG3G | 3 | 70.4 | -0.03468 | west | 0.0035649 | -0.08773 | -0.00050169 | -0.048667 | 0.00050169 | west | N | 0.00050169 | 0
1058 | LONGSHOR | 1 | 150 | -0.034789 | west | 0.0034559 | -0.087839 | -0.00061069 | -0.048776 | 0.00061069 | west | N | 0.00061069 | 0
1058 | LONGSHOR | 2 | 220 | -0.034789 | west | 0.0034559 | -0.087839 | -0.00061069 | -0.048776 | 0.00061069 | west | N | 0.00061069 | 0
1061 | CIELOGEN | 1 | 99 | -0.034972 | west | 0.0032729 | -0.088022 | -0.00079369 | -0.048959 | 0.00079369 | west | N | 0.00079369 | 0
1062 | CIELOGEN | 1 | 61 | -0.034972 | west | 0.0032729 | -0.088022 | -0.00079369 | -0.048959 | 0.00079369 | west | N | 0.00079369 | 0
1068 | SCURRYCW | 1 | 141 | -0.034961 | west | 0.0032839 | -0.088011 | -0.00078269 | -0.048948 | 0.00078269 | west | N | 0.00078269 | 0
1069 | KINDERMG | 1 | 25 | -0.034972 | west | 0.0032729 | -0.088022 | -0.00079369 | -0.048959 | 0.00079369 | west | N | 0.00079369 | 0
1070 | KINDERMG | 1 | 45.7 | -0.034972 | west | 0.0032729 | -0.088022 | -0.00079369 | -0.048959 | 0.00079369 | west | N | 0.00079369 | 0
1071 | KINDERMG | 1 | 45.7 | -0.034972 | west | 0.0032729 | -0.088022 | -0.00079369 | -0.048959 | 0.00079369 | west | N | 0.00079369 | 0
1073 | SCURRYCW | 2 | 120 | -0.034961 | west | 0.0032839 | -0.088011 | -0.00078269 | -0.048948 | 0.00078269 | west | N | 0.00078269 | 0
1320 | BSP 1 | 1 | 25.8 | -0.034359 | west | 0.0038859 | -0.087409 | -0.00018069 | -0.048346 | 0.00018069 | west | N | 0.00018069 | 0
1326 | STANTONW | 1 | 100.5 | -0.034234 | west | 0.0040109 | -0.087284 | -5.569e-05 | -0.048221 | 5.569e-05 | west | N | 5.569e-05 | 0
1327 | WILDHRSE | 1 | 120 | -0.034576 | west | 0.0036689 | -0.087626 | -0.00039769 | -0.048563 | 0.00039769 | west | N | 0.00039769 | 0
1328 | OCOTILLO | 1 | 58 | -0.034225 | west | 0.0040199 | -0.087275 | -4.669e-05 | -0.048212 | 4.669e-05 | west | N | 4.669e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.034317 | west | 0.0039279 | -0.087367 | -0.00013869 | -0.048304 | 0.00013869 | west | N | 0.00013869 | 0
1343 | TRENTIPP | 1 | 150 | -0.035202 | west | 0.0030429 | -0.088252 | -0.0010237 | -0.049189 | 0.0010237 | west | N | 0.0010237 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.033864 | west | 0.0043809 | -0.086914 | 0.00031431 | -0.047851 | 0.00031431 | west | N | 0.00031431 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.033864 | west | 0.0043809 | -0.086914 | 0.00031431 | -0.047851 | 0.00031431 | west | N | 0.00031431 | 0
1354 | AEPWIND_ | 1 | 101 | -0.035202 | west | 0.0030429 | -0.088252 | -0.0010237 | -0.049189 | 0.0010237 | west | N | 0.0010237 | 0
1360 | GUNSIGHT | 1 | 120 | -0.034592 | west | 0.0036529 | -0.087642 | -0.00041369 | -0.048579 | 0.00041369 | west | N | 0.00041369 | 0
1432 | GRHAMSES | 2 | 366 | -0.038374 | north | -0.00012908 | -0.091424 | -0.0041957 | -0.052361 | 0.00012908 | North | N | 0.00012908 | 0
1433 | GRHAMSES | 1 | 242 | -0.038451 | north | -0.00020608 | -0.091501 | -0.0042727 | -0.052438 | 0.00020608 | North | N | 0.00020608 | 0
1437 | MESQUITW | 1 | 400 | -0.036642 | west | 0.0016029 | -0.089692 | -0.0024637 | -0.050629 | 0.0016029 | North | Y | 0.0024637 | 0.34431
1438 | MESQUITW | 1 | 236 | -0.036644 | west | 0.0016009 | -0.089694 | -0.0024657 | -0.050631 | 0.0016009 | North | Y | 0.0024657 | 0.20409
1442 | COKFIELD | 1 | 165 | -0.037059 | west | 0.0011859 | -0.090109 | -0.0028807 | -0.051046 | 0.0011859 | North | Y | 0.0028807 | 0.27964
1453 | WCPWRCO_ | 1 | 204 | -0.039322 | north | -0.0010771 | -0.092372 | -0.0051437 | -0.053309 | 0.0010771 | North | N | 0.0010771 | 0
1454 | WCPWRCO_ | 2 | 201 | -0.039322 | north | -0.0010771 | -0.092372 | -0.0051437 | -0.053309 | 0.0010771 | North | N | 0.0010771 | 0
1455 | WCPWRCO_ | 3 | 242 | -0.039322 | north | -0.0010771 | -0.092372 | -0.0051437 | -0.053309 | 0.0010771 | North | N | 0.0010771 | 0
1479 | WFCOGEN_ | 1 | 20 | -0.038466 | west | -0.00022108 | -0.091516 | -0.0042877 | -0.052453 | 0.00022108 | North | Y | 0.0042877 | 0.081332
1479 | WFCOGEN_ | 2 | 20 | -0.038466 | west | -0.00022108 | -0.091516 | -0.0042877 | -0.052453 | 0.00022108 | North | Y | 0.0042877 | 0.081332
1482 | WFCOGEN_ | 1 | 20 | -0.038466 | west | -0.00022108 | -0.091516 | -0.0042877 | -0.052453 | 0.00022108 | North | Y | 0.0042877 | 0.081332
1482 | WFCOGEN_ | 2 | 17 | -0.038466 | west | -0.00022108 | -0.091516 | -0.0042877 | -0.052453 | 0.00022108 | North | Y | 0.0042877 | 0.069132
1600 | BARTNWND | 1 | 120 | -0.039474 | north | -0.0012291 | -0.092524 | -0.0052957 | -0.053461 | 0.0012291 | North | N | 0.0012291 | 0
1643 | SLSTR1PP | 1 | 60 | -0.040131 | north | -0.0018861 | -0.093181 | -0.0059527 | -0.054118 | 0.0018861 | North | N | 0.0018861 | 0
1675 | PEC_1G | 1 | 75 | -0.03943 | north | -0.0011851 | -0.09248 | -0.0052517 | -0.053417 | 0.0011851 | North | N | 0.0011851 | 0
1676 | PEC_2G | 2 | 79.6 | -0.03943 | north | -0.0011851 | -0.09248 | -0.0052517 | -0.053417 | 0.0011851 | North | N | 0.0011851 | 0
1677 | PEC_3G | 3 | 88.4 | -0.03943 | north | -0.0011851 | -0.09248 | -0.0052517 | -0.053417 | 0.0011851 | North | N | 0.0011851 | 0
1678 | LAMARPWR | 1 | 160 | -0.039451 | north | -0.0012061 | -0.092501 | -0.0052727 | -0.053438 | 0.0012061 | North | N | 0.0012061 | 0
1679 | LAMARPWR | 2 | 156 | -0.039451 | north | -0.0012061 | -0.092501 | -0.0052727 | -0.053438 | 0.0012061 | North | N | 0.0012061 | 0
1680 | LAMARPWR | 3 | 196 | -0.039451 | north | -0.0012061 | -0.092501 | -0.0052727 | -0.053438 | 0.0012061 | North | N | 0.0012061 | 0
1681 | LAMARPWR | 4 | 156 | -0.039451 | north | -0.0012061 | -0.092501 | -0.0052727 | -0.053438 | 0.0012061 | North | N | 0.0012061 | 0
1682 | LAMARPWR | 5 | 157 | -0.039451 | north | -0.0012061 | -0.092501 | -0.0052727 | -0.053438 | 0.0012061 | North | N | 0.0012061 | 0
1683 | LAMARPWR | 6 | 198 | -0.039451 | north | -0.0012061 | -0.092501 | -0.0052727 | -0.053438 | 0.0012061 | North | N | 0.0012061 | 0
1687 | VALLEY_1 | 1 | 170 | -0.039506 | north | -0.0012611 | -0.092556 | -0.0053277 | -0.053493 | 0.0012611 | North | N | 0.0012611 | 0
1688 | VALLEY_2 | 2 | 520 | -0.039506 | north | -0.0012611 | -0.092556 | -0.0053277 | -0.053493 | 0.0012611 | North | N | 0.0012611 | 0
1689 | VALLEY_3 | 3 | 370 | -0.039473 | north | -0.0012281 | -0.092523 | -0.0052947 | -0.05346 | 0.0012281 | North | N | 0.0012281 | 0
1701 | MOSES_1G | 1 | 558 | -0.039415 | north | -0.0011701 | -0.092465 | -0.0052367 | -0.053402 | 0.0011701 | North | N | 0.0011701 | 0
1702 | MOSES_2G | 2 | 579 | -0.039415 | north | -0.0011701 | -0.092465 | -0.0052367 | -0.053402 | 0.0011701 | North | N | 0.0011701 | 0
1703 | MOSES_3G | 3 | 808 | -0.039415 | north | -0.0011701 | -0.092465 | -0.0052367 | -0.053402 | 0.0011701 | North | N | 0.0011701 | 0
1861 | EAGLEMNT | MB | 112 | -0.040267 | north | -0.0020221 | -0.093317 | -0.0060887 | -0.054254 | 0.0020221 | North | N | 0.0020221 | 0
1862 | EAGLEMNT | MB | 100 | -0.040267 | north | -0.0020221 | -0.093317 | -0.0060887 | -0.054254 | 0.0020221 | North | N | 0.0020221 | 0
1863 | EAGLEMNT | MB | 378 | -0.040267 | north | -0.0020221 | -0.093317 | -0.0060887 | -0.054254 | 0.0020221 | North | N | 0.0020221 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.040569 | north | -0.0023241 | -0.093619 | -0.0063907 | -0.054556 | 0.0023241 | North | N | 0.0023241 | 0
1878 | WLFHOLW_ | 2 | 205 | -0.040569 | north | -0.0023241 | -0.093619 | -0.0063907 | -0.054556 | 0.0023241 | North | N | 0.0023241 | 0
1879 | WLFHOLW_ | 3 | 272.4 | -0.040569 | north | -0.0023241 | -0.093619 | -0.0063907 | -0.054556 | 0.0023241 | North | N | 0.0023241 | 0
1889 | DECRDOVA | MB | 770 | -0.040709 | north | -0.0024641 | -0.093759 | -0.0065307 | -0.054696 | 0.0024641 | North | N | 0.0024641 | 0
1892 | DECRDOVA | A | 70 | -0.041367 | north | -0.0031221 | -0.094417 | -0.0071887 | -0.055354 | 0.0031221 | North | N | 0.0031221 | 0
1893 | DECRDOVA | B | 69 | -0.041367 | north | -0.0031221 | -0.094417 | -0.0071887 | -0.055354 | 0.0031221 | North | N | 0.0031221 | 0
1894 | DECRDOVA | C | 69 | -0.041367 | north | -0.0031221 | -0.094417 | -0.0071887 | -0.055354 | 0.0031221 | North | N | 0.0031221 | 0
1895 | DECRDOVA | D | 68 | -0.041367 | north | -0.0031221 | -0.094417 | -0.0071887 | -0.055354 | 0.0031221 | North | N | 0.0031221 | 0
1898 | COMCHEPK | 1 | 1157 | -0.040463 | north | -0.0022181 | -0.093513 | -0.0062847 | -0.05445 | 0.0022181 | North | N | 0.0022181 | 0
1899 | COMCHEPK | 2 | 1158 | -0.040463 | north | -0.0022181 | -0.093513 | -0.0062847 | -0.05445 | 0.0022181 | North | N | 0.0022181 | 0
1937 | MDLTHELP | 5 | 224 | -0.042387 | north | -0.0041421 | -0.095437 | -0.0082087 | -0.056374 | 0.0041421 | North | N | 0.0041421 | 0
1938 | MDLTHELP | 6 | 226 | -0.042387 | north | -0.0041421 | -0.095437 | -0.0082087 | -0.056374 | 0.0041421 | North | N | 0.0041421 | 0
1941 | MDLTHELP | 1 | 216.4 | -0.042271 | north | -0.0040261 | -0.095321 | -0.0080927 | -0.056258 | 0.0040261 | North | N | 0.0040261 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.042271 | north | -0.0040261 | -0.095321 | -0.0080927 | -0.056258 | 0.0040261 | North | N | 0.0040261 | 0
1943 | MDLTHELP | 3 | 212 | -0.042387 | north | -0.0041421 | -0.095437 | -0.0082087 | -0.056374 | 0.0041421 | North | N | 0.0041421 | 0
1944 | MDLTHELP | 4 | 211 | -0.042387 | north | -0.0041421 | -0.095437 | -0.0082087 | -0.056374 | 0.0041421 | North | N | 0.0041421 | 0
1947 | HANDLEY_ | 3 | 395 | -0.040914 | north | -0.0026691 | -0.093964 | -0.0067357 | -0.054901 | 0.0026691 | North | N | 0.0026691 | 0
1948 | HANDLEY_ | 4 | 435 | -0.040858 | north | -0.0026131 | -0.093908 | -0.0066797 | -0.054845 | 0.0026131 | North | N | 0.0026131 | 0
1949 | HANDLEY_ | 5 | 435 | -0.040914 | north | -0.0026691 | -0.093964 | -0.0067357 | -0.054901 | 0.0026691 | North | N | 0.0026691 | 0
2371 | COLLIN_1 | MB | 138 | -0.039684 | north | -0.0014391 | -0.092734 | -0.0055057 | -0.053671 | 0.0014391 | North | N | 0.0014391 | 0
2413 | MTCK6_G | 6 | 118 | -0.040016 | north | -0.0017711 | -0.093066 | -0.0058377 | -0.054003 | 0.0017711 | North | N | 0.0017711 | 0
2414 | MTCK7_G | 7 | 115 | -0.040016 | north | -0.0017711 | -0.093066 | -0.0058377 | -0.054003 | 0.0017711 | North | N | 0.0017711 | 0
2417 | MTCK8_G | 8 | 556 | -0.040016 | north | -0.0017711 | -0.093066 | -0.0058377 | -0.054003 | 0.0017711 | North | N | 0.0017711 | 0
2451 | LKHB1_G | 1 | 388 | -0.039415 | north | -0.0011701 | -0.092465 | -0.0052367 | -0.053402 | 0.0011701 | North | N | 0.0011701 | 0
2452 | LKHB2_G | 2 | 515 | -0.039415 | north | -0.0011701 | -0.092465 | -0.0052367 | -0.053402 | 0.0011701 | North | N | 0.0011701 | 0
3097 | MARTLAKE | 1 | 785 | -0.03802 | north | 0.00022492 | -0.09107 | -0.0038417 | -0.052007 | 0.00022492 | North | N | 0.00022492 | 0
3098 | MARTLAKE | 2 | 795 | -0.03802 | north | 0.00022492 | -0.09107 | -0.0038417 | -0.052007 | 0.00022492 | North | N | 0.00022492 | 0
3099 | MARTLAKE | 3 | 780 | -0.03802 | north | 0.00022492 | -0.09107 | -0.0038417 | -0.052007 | 0.00022492 | North | N | 0.00022492 | 0
3107 | STRYKER_ | 1 | 182 | -0.037678 | north | 0.00056692 | -0.090728 | -0.0034997 | -0.051665 | 0.00056692 | North | N | 0.00056692 | 0
3108 | STRYKER_ | 2 | 484 | -0.037678 | north | 0.00056692 | -0.090728 | -0.0034997 | -0.051665 | 0.00056692 | North | N | 0.00056692 | 0
3126 | TRINIDAD | 1 | 224 | -0.039822 | north | -0.0015771 | -0.092872 | -0.0056437 | -0.053809 | 0.0015771 | North | N | 0.0015771 | 0
3309 | ASPN_G | 1 | 50 | -0.037691 | north | 0.00055392 | -0.090741 | -0.0035127 | -0.051678 | 0.00055392 | North | N | 0.00055392 | 0
3348 | CHAMPION | MB | 42 | -0.037709 | north | 0.00053592 | -0.090759 | -0.0035307 | -0.051696 | 0.00053592 | North | N | 0.00053592 | 0
3381 | BBRN_1G | 1 | 615 | -0.035413 | north | 0.0028319 | -0.088463 | -0.0012347 | -0.0494 | 0.0012347 | west | Y | 0.0028319 | 0.9823
3382 | BBRN_2G | 2 | 587 | -0.035413 | north | 0.0028319 | -0.088463 | -0.0012347 | -0.0494 | 0.0012347 | west | Y | 0.0028319 | 0.93758
3403 | THOUSE_1 | MB | 537 | -0.06006 | north | -0.021815 | -0.11311 | -0.025882 | -0.074047 | 0.021815 | North | N | 0.021815 | 0
3404 | THOUSE_2 | 2 | 787 | -0.06006 | north | -0.021815 | -0.11311 | -0.025882 | -0.074047 | 0.021815 | North | N | 0.021815 | 0
3416 | LAKE_CRK | MB | 75 | -0.060383 | north | -0.022138 | -0.11343 | -0.026205 | -0.07437 | 0.022138 | North | N | 0.022138 | 0
3417 | LAKE_CRK | MB | 222 | -0.060383 | north | -0.022138 | -0.11343 | -0.026205 | -0.07437 | 0.022138 | North | N | 0.022138 | 0
3432 | SANDOW_4 | 4 | 569 | -0.087362 | south | -0.049117 | -0.14041 | -0.053184 | -0.10135 | 0.049117 | North | Y | 0.14041 | 51.9468
5026 | BRAUNIG_ | 1 | 209 | 0.05933 | south | 0.097575 | 0.00628 | 0.093508 | 0.045343 | 0.00628 | south | N | 0.00628 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.05933 | south | 0.097575 | 0.00628 | 0.093508 | 0.045343 | 0.00628 | south | N | 0.00628 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.059273 | south | 0.097518 | 0.006223 | 0.093451 | 0.045286 | 0.006223 | south | N | 0.006223 | 0
5031 | BRA_VHBC | 1 | 46 | 0.05933 | south | 0.097575 | 0.00628 | 0.093508 | 0.045343 | 0.00628 | south | N | 0.00628 | 0
5032 | BRA_VHBC | 2 | 47 | 0.05933 | south | 0.097575 | 0.00628 | 0.093508 | 0.045343 | 0.00628 | south | N | 0.00628 | 0
5033 | BRA_VHBC | 3 | 46 | 0.05933 | south | 0.097575 | 0.00628 | 0.093508 | 0.045343 | 0.00628 | south | N | 0.00628 | 0
5034 | BRA_VHBC | 4 | 46 | 0.05933 | south | 0.097575 | 0.00628 | 0.093508 | 0.045343 | 0.00628 | south | N | 0.00628 | 0
5111 | CALAVER_ | 1 | 424 | 0.059403 | south | 0.097648 | 0.006353 | 0.093581 | 0.045416 | 0.006353 | south | N | 0.006353 | 0
5112 | CALAVER_ | 2 | 425 | 0.059403 | south | 0.097648 | 0.006353 | 0.093581 | 0.045416 | 0.006353 | south | N | 0.006353 | 0
5264 | LEON_LCP | 3 | 58 | 0.058961 | south | 0.097206 | 0.005911 | 0.093139 | 0.044974 | 0.005911 | south | N | 0.005911 | 0
5265 | LEON_LCP | 4 | 89 | 0.058961 | south | 0.097206 | 0.005911 | 0.093139 | 0.044974 | 0.005911 | south | N | 0.005911 | 0
5266 | LEON_LCP | 1 | 44 | 0.058961 | south | 0.097206 | 0.005911 | 0.093139 | 0.044974 | 0.005911 | south | N | 0.005911 | 0
5267 | LEON_LCP | 2 | 44 | 0.058961 | south | 0.097206 | 0.005911 | 0.093139 | 0.044974 | 0.005911 | south | N | 0.005911 | 0
5268 | LEON_LCP | 3 | 43 | 0.058961 | south | 0.097206 | 0.005911 | 0.093139 | 0.044974 | 0.005911 | south | N | 0.005911 | 0
5269 | LEON_LCP | 4 | 45 | 0.058961 | south | 0.097206 | 0.005911 | 0.093139 | 0.044974 | 0.005911 | south | N | 0.005911 | 0
5396 | CALAVER_ | 1 | 412 | 0.059392 | south | 0.097637 | 0.006342 | 0.09357 | 0.045405 | 0.006342 | south | N | 0.006342 | 0
5397 | CALAVER_ | 2 | 400 | 0.059392 | south | 0.097637 | 0.006342 | 0.09357 | 0.045405 | 0.006342 | south | N | 0.006342 | 0
5401 | CALAVER_ | 1 | 546 | 0.058777 | south | 0.097022 | 0.005727 | 0.092955 | 0.04479 | 0.005727 | south | N | 0.005727 | 0
5402 | CALAVER_ | 2 | 750 | 0.058777 | south | 0.097022 | 0.005727 | 0.092955 | 0.04479 | 0.005727 | south | N | 0.005727 | 0
5436 | TUTTL_WB | MB | 61 | 0.059567 | south | 0.097812 | 0.006517 | 0.093745 | 0.04558 | 0.006517 | south | N | 0.006517 | 0
5438 | TUTTL_WB | MB | 95 | 0.059567 | south | 0.097812 | 0.006517 | 0.093745 | 0.04558 | 0.006517 | south | N | 0.006517 | 0
5439 | TUTTL_WB | MB | 151 | 0.059567 | south | 0.097812 | 0.006517 | 0.093745 | 0.04558 | 0.006517 | south | N | 0.006517 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.059099 | south | 0.097344 | 0.006049 | 0.093277 | 0.045112 | 0.006049 | south | N | 0.006049 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.059099 | south | 0.097344 | 0.006049 | 0.093277 | 0.045112 | 0.006049 | south | N | 0.006049 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.059099 | south | 0.097344 | 0.006049 | 0.093277 | 0.045112 | 0.006049 | south | N | 0.006049 | 0
5503 | RAYBURNG | 1 | 22 | 0.047321 | south | 0.085566 | -0.005729 | 0.081499 | 0.033334 | 0.005729 | south | N | 0.005729 | 0
5505 | RAYBURNG | 1 | 11 | 0.047321 | south | 0.085566 | -0.005729 | 0.081499 | 0.033334 | 0.005729 | south | N | 0.005729 | 0
5506 | RAYBURNG | 1 | 11 | 0.047321 | south | 0.085566 | -0.005729 | 0.081499 | 0.033334 | 0.005729 | south | N | 0.005729 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.047752 | south | 0.085997 | -0.005298 | 0.08193 | 0.033765 | 0.005298 | south | N | 0.005298 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.047752 | south | 0.085997 | -0.005298 | 0.08193 | 0.033765 | 0.005298 | south | N | 0.005298 | 0
5511 | RAYBURNC | 1 | 46 | 0.047752 | south | 0.085997 | -0.005298 | 0.08193 | 0.033765 | 0.005298 | south | N | 0.005298 | 0
5512 | RAYBURNC | 1 | 48 | 0.047752 | south | 0.085997 | -0.005298 | 0.08193 | 0.033765 | 0.005298 | south | N | 0.005298 | 0
5728 | FALCONHY | 2 | 12 | 0.050159 | south | 0.088404 | -0.002891 | 0.084337 | 0.036172 | 0.002891 | south | N | 0.002891 | 0
5729 | FALCONHY | 3 | 11 | 0.050159 | south | 0.088404 | -0.002891 | 0.084337 | 0.036172 | 0.002891 | south | N | 0.002891 | 0
5890 | PEARSALL | 1 | 24 | 0.052646 | south | 0.090891 | -0.00040402 | 0.086824 | 0.038659 | 0.00040402 | south | N | 0.00040402 | 0
5891 | PEARSALL | 1 | 24 | 0.052646 | south | 0.090891 | -0.00040402 | 0.086824 | 0.038659 | 0.00040402 | south | N | 0.00040402 | 0
5892 | PEARSALL | 1 | 23 | 0.052646 | south | 0.090891 | -0.00040402 | 0.086824 | 0.038659 | 0.00040402 | south | N | 0.00040402 | 0
5903 | SANMIGUE | 1 | 396 | 0.055557 | south | 0.093802 | 0.002507 | 0.089735 | 0.04157 | 0.002507 | south | N | 0.002507 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.030529 | houston | 0.068774 | -0.022521 | 0.064707 | 0.016542 | 0.016542 | houston | N | 0.016542 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.030529 | houston | 0.068774 | -0.022521 | 0.064707 | 0.016542 | 0.016542 | houston | N | 0.016542 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | 0.038245 | -0.05305 | 0.034178 | -0.013987 | 0.013987 | houston | Y | 0.038245 | 14.5546
5932 | SI_RAY9 | 9 | 38 | 0.049298 | south | 0.087543 | -0.003752 | 0.083476 | 0.035311 | 0.003752 | south | N | 0.003752 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.049298 | south | 0.087543 | -0.003752 | 0.083476 | 0.035311 | 0.003752 | south | N | 0.003752 | 0
5934 | SI_RAY5 | 5 | 15 | 0.049298 | south | 0.087543 | -0.003752 | 0.083476 | 0.035311 | 0.003752 | south | N | 0.003752 | 0
5935 | SI_RAY10 | 10 | 47 | 0.049298 | south | 0.087543 | -0.003752 | 0.083476 | 0.035311 | 0.003752 | south | N | 0.003752 | 0
6016 | SWMESA | 1 | 75 | -0.029716 | west | 0.0085289 | -0.082766 | 0.0044623 | -0.043703 | 0.0044623 | west | N | 0.0044623 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | 0.038245 | -0.05305 | 0.034178 | -0.013987 | 0.013987 | houston | Y | 0.034178 | 4.442
6144 | MCADOO1A | 1 | 150 | -0.035519 | west | 0.0027259 | -0.088569 | -0.0013407 | -0.049506 | 0.0013407 | west | N | 0.0013407 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.033525 | west | 0.0047199 | -0.086575 | 0.00065331 | -0.047512 | 0.00065331 | west | N | 0.00065331 | 0
6476 | LANGFORD | 1 | 150 | -0.013404 | west | 0.024841 | -0.066454 | 0.020774 | -0.027391 | 0.020774 | west | N | 0.020774 | 0
6637 | SNYDERW1 | 1 | 63 | -0.03493 | west | 0.0033149 | -0.08798 | -0.00075169 | -0.048917 | 0.00075169 | west | N | 0.00075169 | 0
6752 | OKLA0A | 1 | 649.7 | -0.037401 | west | 0.00084392 | -0.090451 | -0.0032227 | -0.051388 | 0.00084392 | North | Y | 0.0032227 | 1.5455
6948 | DENISNDM | 1 | 40 | -0.039535 | north | -0.0012901 | -0.092585 | -0.0053567 | -0.053522 | 0.0012901 | North | N | 0.0012901 | 0
6948 | DENISNDM | 2 | 40 | -0.039535 | north | -0.0012901 | -0.092585 | -0.0053567 | -0.053522 | 0.0012901 | North | N | 0.0012901 | 0
7000 | L_FERGUS | 1 | 422 | 0.066408 | south | 0.10465 | 0.013358 | 0.10059 | 0.052421 | 0.013358 | south | N | 0.013358 | 0
7004 | L_SIMGID | 1 | 132 | 0.061624 | south | 0.099869 | 0.008574 | 0.095802 | 0.047637 | 0.008574 | south | N | 0.008574 | 0
7005 | L_SIMGID | 2 | 134 | 0.061624 | south | 0.099869 | 0.008574 | 0.095802 | 0.047637 | 0.008574 | south | N | 0.008574 | 0
7006 | L_SIMGID | 3 | 323 | 0.061624 | south | 0.099869 | 0.008574 | 0.095802 | 0.047637 | 0.008574 | south | N | 0.008574 | 0
7007 | L_LOSTPI | 1 | 158 | 0.070374 | south | 0.10862 | 0.017324 | 0.10455 | 0.056387 | 0.017324 | south | N | 0.017324 | 0
7008 | L_LOSTPI | 2 | 160 | 0.070374 | south | 0.10862 | 0.017324 | 0.10455 | 0.056387 | 0.017324 | south | N | 0.017324 | 0
7009 | L_LOSTPI | 3 | 175 | 0.070374 | south | 0.10862 | 0.017324 | 0.10455 | 0.056387 | 0.017324 | south | N | 0.017324 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.063786 | south | 0.10203 | 0.010736 | 0.097964 | 0.049799 | 0.010736 | south | N | 0.010736 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.063786 | south | 0.10203 | 0.010736 | 0.097964 | 0.049799 | 0.010736 | south | N | 0.010736 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.063753 | south | 0.102 | 0.010703 | 0.097931 | 0.049766 | 0.010703 | south | N | 0.010703 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.065061 | south | 0.10331 | 0.012011 | 0.099239 | 0.051074 | 0.012011 | south | N | 0.012011 | 0
7015 | L_HAYSEN | 2 | 225 | 0.065061 | south | 0.10331 | 0.012011 | 0.099239 | 0.051074 | 0.012011 | south | N | 0.012011 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.065061 | south | 0.10331 | 0.012011 | 0.099239 | 0.051074 | 0.012011 | south | N | 0.012011 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.065061 | south | 0.10331 | 0.012011 | 0.099239 | 0.051074 | 0.012011 | south | N | 0.012011 | 0
7020 | L_AUSTPL | 1 | 8 | 0.10294 | south | 0.14119 | 0.049893 | 0.13712 | 0.088956 | 0.049893 | south | N | 0.049893 | 0
7020 | L_AUSTPL | 2 | 8 | 0.10294 | south | 0.14119 | 0.049893 | 0.13712 | 0.088956 | 0.049893 | south | N | 0.049893 | 0
7022 | L_BUCHAN | 1 | 18 | 0.056601 | south | 0.094846 | 0.003551 | 0.090779 | 0.042614 | 0.003551 | south | N | 0.003551 | 0
7023 | L_BUCHAN | 2 | 18 | 0.056601 | south | 0.094846 | 0.003551 | 0.090779 | 0.042614 | 0.003551 | south | N | 0.003551 | 0
7024 | L_BUCHAN | 3 | 15 | 0.056601 | south | 0.094846 | 0.003551 | 0.090779 | 0.042614 | 0.003551 | south | N | 0.003551 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.057312 | south | 0.095557 | 0.004262 | 0.09149 | 0.043325 | 0.004262 | south | N | 0.004262 | 0
7028 | L_MARBFA | 1 | 18 | 0.074455 | south | 0.1127 | 0.021405 | 0.10863 | 0.060468 | 0.021405 | south | N | 0.021405 | 0
7029 | L_MARBFA | 2 | 18 | 0.074455 | south | 0.1127 | 0.021405 | 0.10863 | 0.060468 | 0.021405 | south | N | 0.021405 | 0
7031 | L_MARSFO | 1 | 35 | 0.092702 | south | 0.13095 | 0.039652 | 0.12688 | 0.078715 | 0.039652 | south | N | 0.039652 | 0
7032 | L_MARSFO | 2 | 34 | 0.092702 | south | 0.13095 | 0.039652 | 0.12688 | 0.078715 | 0.039652 | south | N | 0.039652 | 0
7033 | L_MARSFO | 3 | 35 | 0.092702 | south | 0.13095 | 0.039652 | 0.12688 | 0.078715 | 0.039652 | south | N | 0.039652 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.067064 | south | 0.10531 | 0.014014 | 0.10124 | 0.053077 | 0.014014 | south | N | 0.014014 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.067064 | south | 0.10531 | 0.014014 | 0.10124 | 0.053077 | 0.014014 | south | N | 0.014014 | 0
7038 | L_DELAWA | 1 | 35 | -0.033549 | west | 0.0046959 | -0.086599 | 0.00062931 | -0.047536 | 0.00062931 | west | N | 0.00062931 | 0
7038 | L_DELAWA | 2 | 30 | -0.033549 | west | 0.0046959 | -0.086599 | 0.00062931 | -0.047536 | 0.00062931 | west | N | 0.00062931 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.059954 | south | 0.098199 | 0.006904 | 0.094132 | 0.045967 | 0.006904 | south | N | 0.006904 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.059954 | south | 0.098199 | 0.006904 | 0.094132 | 0.045967 | 0.006904 | south | N | 0.006904 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.059954 | south | 0.098199 | 0.006904 | 0.094132 | 0.045967 | 0.006904 | south | N | 0.006904 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.059954 | south | 0.098199 | 0.006904 | 0.094132 | 0.045967 | 0.006904 | south | N | 0.006904 | 0
7487 | L_CANYHY | 1 | 6 | 0.07063 | south | 0.10887 | 0.01758 | 0.10481 | 0.056643 | 0.01758 | south | N | 0.01758 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.0639 | south | 0.10214 | 0.01085 | 0.098078 | 0.049913 | 0.01085 | south | N | 0.01085 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.0639 | south | 0.10214 | 0.01085 | 0.098078 | 0.049913 | 0.01085 | south | N | 0.01085 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.0639 | south | 0.10214 | 0.01085 | 0.098078 | 0.049913 | 0.01085 | south | N | 0.01085 | 0
7609 | L_SCHUMA | 1 | 4 | 0.062982 | south | 0.10123 | 0.009932 | 0.09716 | 0.048995 | 0.009932 | south | N | 0.009932 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.062444 | south | 0.10069 | 0.009394 | 0.096622 | 0.048457 | 0.009394 | south | N | 0.009394 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.062444 | south | 0.10069 | 0.009394 | 0.096622 | 0.048457 | 0.009394 | south | N | 0.009394 | 0
7800 | L_GUADGE | 1 | 147 | 0.060719 | south | 0.098964 | 0.007669 | 0.094897 | 0.046732 | 0.007669 | south | N | 0.007669 | 0
7801 | L_GUADGE | 2 | 138 | 0.060719 | south | 0.098964 | 0.007669 | 0.094897 | 0.046732 | 0.007669 | south | N | 0.007669 | 0
7802 | L_GUADGE | 3 | 140 | 0.060719 | south | 0.098964 | 0.007669 | 0.094897 | 0.046732 | 0.007669 | south | N | 0.007669 | 0
7803 | L_GUADGE | 4 | 147 | 0.060719 | south | 0.098964 | 0.007669 | 0.094897 | 0.046732 | 0.007669 | south | N | 0.007669 | 0
7804 | L_GUADGE | 5 | 182 | 0.060719 | south | 0.098964 | 0.007669 | 0.094897 | 0.046732 | 0.007669 | south | N | 0.007669 | 0
7805 | L_GUADGE | 6 | 198 | 0.060719 | south | 0.098964 | 0.007669 | 0.094897 | 0.046732 | 0.007669 | south | N | 0.007669 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.073887 | south | 0.11213 | 0.020837 | 0.10807 | 0.0599 | 0.020837 | south | N | 0.020837 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.073887 | south | 0.11213 | 0.020837 | 0.10807 | 0.0599 | 0.020837 | south | N | 0.020837 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.073887 | south | 0.11213 | 0.020837 | 0.10807 | 0.0599 | 0.020837 | south | N | 0.020837 | 0
7810 | L_RIONOG | 1 | 142 | 0.062882 | south | 0.10113 | 0.009832 | 0.09706 | 0.048895 | 0.009832 | south | N | 0.009832 | 0
7811 | L_RIONOG | 2 | 145 | 0.062882 | south | 0.10113 | 0.009832 | 0.09706 | 0.048895 | 0.009832 | south | N | 0.009832 | 0
7812 | L_RIONOG | 3 | 151 | 0.062882 | south | 0.10113 | 0.009832 | 0.09706 | 0.048895 | 0.009832 | south | N | 0.009832 | 0
7813 | L_RIONOG | 4 | 290 | 0.062882 | south | 0.10113 | 0.009832 | 0.09706 | 0.048895 | 0.009832 | south | N | 0.009832 | 0
8032 | AMISTADH | 1 | 33 | 0.030179 | south | 0.068424 | -0.022871 | 0.064357 | 0.016192 | 0.016192 | houston | Y | 0.022871 | 0.22042
8033 | AMISTADH | 2 | 25 | 0.030179 | south | 0.068424 | -0.022871 | 0.064357 | 0.016192 | 0.016192 | houston | Y | 0.022871 | 0.16698
8048 | FALCONHY | 1 | 12 | 0.050159 | south | 0.088404 | -0.002891 | 0.084337 | 0.036172 | 0.002891 | south | N | 0.002891 | 0
8066 | DUP1V#1 | 1 | 73 | 0.047827 | south | 0.086072 | -0.005223 | 0.082005 | 0.03384 | 0.005223 | south | N | 0.005223 | 0
8134 | FOR69CG0 | 1 | 79 | 0.044672 | south | 0.082917 | -0.008378 | 0.07885 | 0.030685 | 0.008378 | south | N | 0.008378 | 0
8138 | FOR69CG0 | 2 | 81 | 0.044672 | south | 0.082917 | -0.008378 | 0.07885 | 0.030685 | 0.008378 | south | N | 0.008378 | 0
8139 | JOS #1 | MB | 255 | 0 | south | 0.038245 | -0.05305 | 0.034178 | -0.013987 | 0.013987 | houston | Y | 0.05305 | 9.961
8147 | UCAR #2 | 10 | 28 | 0.046357 | south | 0.084602 | -0.006693 | 0.080535 | 0.03237 | 0.006693 | south | N | 0.006693 | 0
8148 | UCAR #1 | 2 | 7 | 0.046357 | south | 0.084602 | -0.006693 | 0.080535 | 0.03237 | 0.006693 | south | N | 0.006693 | 0
8153 | FOR69CG0 | 3 | 79 | 0.044672 | south | 0.082917 | -0.008378 | 0.07885 | 0.030685 | 0.008378 | south | N | 0.008378 | 0
8154 | FOR69CG0 | 4 | 80 | 0.044672 | south | 0.082917 | -0.008378 | 0.07885 | 0.030685 | 0.008378 | south | N | 0.008378 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.044672 | south | 0.082917 | -0.008378 | 0.07885 | 0.030685 | 0.008378 | south | N | 0.008378 | 0
8156 | FOR69CG0 | 6 | 25 | 0.044672 | south | 0.082917 | -0.008378 | 0.07885 | 0.030685 | 0.008378 | south | N | 0.008378 | 0
8157 | FOR69CG0 | 7 | 46 | 0.044672 | south | 0.082917 | -0.008378 | 0.07885 | 0.030685 | 0.008378 | south | N | 0.008378 | 0
8161 | COLETOU1 | 1 | 629 | 0.050815 | south | 0.08906 | -0.002235 | 0.084993 | 0.036828 | 0.002235 | south | N | 0.002235 | 0
8173 | VICEC51A | 5 | 144 | 0.048364 | south | 0.086609 | -0.004686 | 0.082542 | 0.034377 | 0.004686 | south | N | 0.004686 | 0
8174 | VICEC61A | 6 | 188 | 0.048364 | south | 0.086609 | -0.004686 | 0.082542 | 0.034377 | 0.004686 | south | N | 0.004686 | 0
8189 | CUERO 2 | 1 | 12 | 0.058143 | south | 0.096388 | 0.005093 | 0.092321 | 0.044156 | 0.005093 | south | N | 0.005093 | 0
8262 | ELPS | 1 | 6 | 0.037154 | south | 0.075399 | -0.015896 | 0.071332 | 0.023167 | 0.015896 | south | N | 0.015896 | 0
8285 | LAR #1 | MB | 32 | 0 | south | 0.038245 | -0.05305 | 0.034178 | -0.013987 | 0.013987 | houston | Y | 0.05305 | 1.25
8287 | LAR #2 | MB | 32 | 0 | south | 0.038245 | -0.05305 | 0.034178 | -0.013987 | 0.013987 | houston | Y | 0.05305 | 1.25
8288 | LAR #3 | MB | 105 | 0 | south | 0.038245 | -0.05305 | 0.034178 | -0.013987 | 0.013987 | houston | Y | 0.05305 | 4.1016
8388 | BATES0A | MB | 70 | 0 | south | 0.038245 | -0.05305 | 0.034178 | -0.013987 | 0.013987 | houston | Y | 0.05305 | 2.7344
8393 | BATES0B | MB | 110 | 0 | south | 0.038245 | -0.05305 | 0.034178 | -0.013987 | 0.013987 | houston | Y | 0.05305 | 4.2969
8442 | NBEC71A | 1 | 336 | 0.048753 | south | 0.086998 | -0.004297 | 0.082931 | 0.034766 | 0.004297 | south | N | 0.004297 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | 0.038245 | -0.05305 | 0.034178 | -0.013987 | 0.013987 | houston | Y | 0.05305 | 0.78126
8457 | COSW#2 | 2 | 14 | 0 | south | 0.038245 | -0.05305 | 0.034178 | -0.013987 | 0.013987 | houston | Y | 0.05305 | 0.54688
8459 | B_DAVIS1 | 1 | 334 | 0.048867 | south | 0.087112 | -0.004183 | 0.083045 | 0.03488 | 0.004183 | south | N | 0.004183 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.048867 | south | 0.087112 | -0.004183 | 0.083045 | 0.03488 | 0.004183 | south | N | 0.004183 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.048936 | south | 0.087181 | -0.004114 | 0.083114 | 0.034949 | 0.004114 | south | N | 0.004114 | 0
8506 | VAL #1 | 1 | 25 | 0.048884 | south | 0.087129 | -0.004166 | 0.083062 | 0.034897 | 0.004166 | south | N | 0.004166 | 0
8507 | VAL #2 | 2 | 25 | 0.048884 | south | 0.087129 | -0.004166 | 0.083062 | 0.034897 | 0.004166 | south | N | 0.004166 | 0
8511 | OXY_CC0A | 1 | 38 | 0.048934 | south | 0.087179 | -0.004116 | 0.083112 | 0.034947 | 0.004116 | south | N | 0.004116 | 0
8517 | CELANEBI | 1 | 29 | 0.049179 | south | 0.087424 | -0.003871 | 0.083357 | 0.035192 | 0.003871 | south | N | 0.003871 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.048759 | south | 0.087004 | -0.004291 | 0.082937 | 0.034772 | 0.004291 | south | N | 0.004291 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.048759 | south | 0.087004 | -0.004291 | 0.082937 | 0.034772 | 0.004291 | south | N | 0.004291 | 0
8562 | CNOPST1 | 3 | 153 | 0.048759 | south | 0.087004 | -0.004291 | 0.082937 | 0.034772 | 0.004291 | south | N | 0.004291 | 0
8926 | LGE_GT10 | 1 | 158 | 0.048237 | south | 0.086482 | -0.004813 | 0.082415 | 0.03425 | 0.004813 | south | N | 0.004813 | 0
8927 | LGE_GT20 | 2 | 153 | 0.048237 | south | 0.086482 | -0.004813 | 0.082415 | 0.03425 | 0.004813 | south | N | 0.004813 | 0
8928 | LGE_STG0 | 3 | 100 | 0.048237 | south | 0.086482 | -0.004813 | 0.082415 | 0.03425 | 0.004813 | south | N | 0.004813 | 0
8930 | ICPGN10A | 1 | 145 | 0.048237 | south | 0.086482 | -0.004813 | 0.082415 | 0.03425 | 0.004813 | south | N | 0.004813 | 0
8931 | ICPGN20A | 2 | 147 | 0.048237 | south | 0.086482 | -0.004813 | 0.082415 | 0.03425 | 0.004813 | south | N | 0.004813 | 0
8932 | ICPGN30A | 3 | 127 | 0.048237 | south | 0.086482 | -0.004813 | 0.082415 | 0.03425 | 0.004813 | south | N | 0.004813 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.049504 | south | 0.087749 | -0.003546 | 0.083682 | 0.035517 | 0.003546 | south | N | 0.003546 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.049504 | south | 0.087749 | -0.003546 | 0.083682 | 0.035517 | 0.003546 | south | N | 0.003546 | 0
8935 | FGNTS201 | 3 | 173 | 0.049504 | south | 0.087749 | -0.003546 | 0.083682 | 0.035517 | 0.003546 | south | N | 0.003546 | 0
8936 | MVGN#1 | 1 | 207 | 0.049399 | south | 0.087644 | -0.003651 | 0.083577 | 0.035412 | 0.003651 | south | N | 0.003651 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.049399 | south | 0.087644 | -0.003651 | 0.083577 | 0.035412 | 0.003651 | south | N | 0.003651 | 0
8938 | MVGN#3 | 3 | 242 | 0.049399 | south | 0.087644 | -0.003651 | 0.083577 | 0.035412 | 0.003651 | south | N | 0.003651 | 0
8981 | HECN1 | 1 | 144 | 0.049398 | south | 0.087643 | -0.003652 | 0.083576 | 0.035411 | 0.003652 | south | N | 0.003652 | 0
8982 | HECN2 | 2 | 144 | 0.049398 | south | 0.087643 | -0.003652 | 0.083576 | 0.035411 | 0.003652 | south | N | 0.003652 | 0
8983 | HECN3 | 3 | 171 | 0.049398 | south | 0.087643 | -0.003652 | 0.083576 | 0.035411 | 0.003652 | south | N | 0.003652 | 0
9000 | DECKR_G1 | 1 | 310 | 0.10214 | south | 0.14038 | 0.049089 | 0.13632 | 0.088152 | 0.049089 | south | N | 0.049089 | 0
9001 | DECKR_G2 | 2 | 413 | 0.10214 | south | 0.14038 | 0.049089 | 0.13632 | 0.088152 | 0.049089 | south | N | 0.049089 | 0
9002 | DECKR_G3 | 3 | 42 | 0.099995 | south | 0.13824 | 0.046945 | 0.13417 | 0.086008 | 0.046945 | south | N | 0.046945 | 0
9003 | DECKR_G4 | 4 | 44 | 0.099995 | south | 0.13824 | 0.046945 | 0.13417 | 0.086008 | 0.046945 | south | N | 0.046945 | 0
9004 | DECKR_G5 | 5 | 44 | 0.099995 | south | 0.13824 | 0.046945 | 0.13417 | 0.086008 | 0.046945 | south | N | 0.046945 | 0
9005 | DECKR_G6 | 6 | 47 | 0.099995 | south | 0.13824 | 0.046945 | 0.13417 | 0.086008 | 0.046945 | south | N | 0.046945 | 0
9016 | SANDH_G1 | 1 | 49 | 0.097112 | south | 0.13536 | 0.044062 | 0.13129 | 0.083125 | 0.044062 | south | N | 0.044062 | 0
9017 | SANDH_G2 | 2 | 46 | 0.097112 | south | 0.13536 | 0.044062 | 0.13129 | 0.083125 | 0.044062 | south | N | 0.044062 | 0
9018 | SANDH_G3 | 3 | 46 | 0.097112 | south | 0.13536 | 0.044062 | 0.13129 | 0.083125 | 0.044062 | south | N | 0.044062 | 0
9019 | SANDH_G4 | 4 | 47 | 0.097112 | south | 0.13536 | 0.044062 | 0.13129 | 0.083125 | 0.044062 | south | N | 0.044062 | 0
9020 | SANDHG5A | 5A | 154 | 0.097112 | south | 0.13536 | 0.044062 | 0.13129 | 0.083125 | 0.044062 | south | N | 0.044062 | 0
9021 | SANDHG5C | 5C | 148 | 0.097112 | south | 0.13536 | 0.044062 | 0.13129 | 0.083125 | 0.044062 | south | N | 0.044062 | 0
9022 | SANDH_G6 | 6 | 48 | 0.097112 | south | 0.13536 | 0.044062 | 0.13129 | 0.083125 | 0.044062 | south | N | 0.044062 | 0
9023 | SANDH_G7 | 7 | 48 | 0.097112 | south | 0.13536 | 0.044062 | 0.13129 | 0.083125 | 0.044062 | south | N | 0.044062 | 0
11001 | NAV1CT | 1 | 70 | -0.034197 | west | 0.0040479 | -0.087247 | -1.869e-05 | -0.048184 | 1.869e-05 | west | N | 1.869e-05 | 0
11009 | NAV2CT | 1 | 70 | -0.034197 | west | 0.0040479 | -0.087247 | -1.869e-05 | -0.048184 | 1.869e-05 | west | N | 1.869e-05 | 0
11011 | NAV3ST | 1 | 92.8 | -0.034197 | west | 0.0040479 | -0.087247 | -1.869e-05 | -0.048184 | 1.869e-05 | west | N | 1.869e-05 | 0
11012 | NAV4CT | 1 | 80 | -0.034197 | west | 0.0040479 | -0.087247 | -1.869e-05 | -0.048184 | 1.869e-05 | west | N | 1.869e-05 | 0
11013 | NAV5CT | 1 | 80 | -0.034197 | west | 0.0040479 | -0.087247 | -1.869e-05 | -0.048184 | 1.869e-05 | west | N | 1.869e-05 | 0
11014 | NAV6ST | 1 | 115 | -0.034197 | west | 0.0040479 | -0.087247 | -1.869e-05 | -0.048184 | 1.869e-05 | west | N | 1.869e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.03419 | west | 0.0040549 | -0.08724 | -1.169e-05 | -0.048177 | 1.169e-05 | west | N | 1.169e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.03419 | west | 0.0040549 | -0.08724 | -1.169e-05 | -0.048177 | 1.169e-05 | west | N | 1.169e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.03419 | west | 0.0040549 | -0.08724 | -1.169e-05 | -0.048177 | 1.169e-05 | west | N | 1.169e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.03419 | west | 0.0040549 | -0.08724 | -1.169e-05 | -0.048177 | 1.169e-05 | west | N | 1.169e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.03419 | west | 0.0040549 | -0.08724 | -1.169e-05 | -0.048177 | 1.169e-05 | west | N | 1.169e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.03419 | west | 0.0040549 | -0.08724 | -1.169e-05 | -0.048177 | 1.169e-05 | west | N | 1.169e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.035394 | west | 0.0028509 | -0.088444 | -0.0012157 | -0.049381 | 0.0012157 | west | N | 0.0012157 | 0
11057 | CHAMPION | 1 | 126.5 | -0.035394 | west | 0.0028509 | -0.088444 | -0.0012157 | -0.049381 | 0.0012157 | west | N | 0.0012157 | 0
11058 | PYRON_1G | 1 | 249 | -0.035394 | west | 0.0028509 | -0.088444 | -0.0012157 | -0.049381 | 0.0012157 | west | N | 0.0012157 | 0
11059 | INADALE_ | 1 | 197 | -0.035394 | west | 0.0028509 | -0.088444 | -0.0012157 | -0.049381 | 0.0012157 | west | N | 0.0012157 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.034789 | west | 0.0034559 | -0.087839 | -0.00061069 | -0.048776 | 0.00061069 | west | N | 0.00061069 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.034789 | west | 0.0034559 | -0.087839 | -0.00061069 | -0.048776 | 0.00061069 | west | N | 0.00061069 | 0
11147 | NOTREES_ | 1 | 149 | -0.033667 | west | 0.0045779 | -0.086717 | 0.00051131 | -0.047654 | 0.00051131 | west | N | 0.00051131 | 0
11309 | BULLCREK | 1 | 180 | -0.0347 | west | 0.0035449 | -0.08775 | -0.00052169 | -0.048687 | 0.00052169 | west | N | 0.00052169 | 0
11310 | BULLCREK | 1 | 180 | -0.0347 | west | 0.0035449 | -0.08775 | -0.00052169 | -0.048687 | 0.00052169 | west | N | 0.00052169 | 0
11320 | COYOTE_1 | 1 | 225 | -0.034664 | west | 0.0035809 | -0.087714 | -0.00048569 | -0.048651 | 0.00048569 | west | N | 0.00048569 | 0
11415 | LORAINE_ | 1 | 125 | -0.035147 | west | 0.0030979 | -0.088197 | -0.00096869 | -0.049134 | 0.00096869 | west | N | 0.00096869 | 0
11416 | LORAINE_ | 1 | 125 | -0.035147 | west | 0.0030979 | -0.088197 | -0.00096869 | -0.049134 | 0.00096869 | west | N | 0.00096869 | 0
11691 | KMICHICT | 1 | 140 | -0.039473 | north | -0.0012281 | -0.092523 | -0.0052947 | -0.05346 | 0.0012281 | North | N | 0.0012281 | 0
11692 | KMICHICT | 2 | 141 | -0.039473 | north | -0.0012281 | -0.092523 | -0.0052947 | -0.05346 | 0.0012281 | North | N | 0.0012281 | 0
11693 | KMICHIST | 3 | 309 | -0.039473 | north | -0.0012281 | -0.092523 | -0.0052947 | -0.05346 | 0.0012281 | North | N | 0.0012281 | 0
11694 | KMICHICT | 4 | 143 | -0.039473 | north | -0.0012281 | -0.092523 | -0.0052947 | -0.05346 | 0.0012281 | North | N | 0.0012281 | 0
11695 | KMICHICT | 5 | 144 | -0.039473 | north | -0.0012281 | -0.092523 | -0.0052947 | -0.05346 | 0.0012281 | North | N | 0.0012281 | 0
11696 | KMICHIST | 6 | 310 | -0.039473 | north | -0.0012281 | -0.092523 | -0.0052947 | -0.05346 | 0.0012281 | North | N | 0.0012281 | 0
12322 | ENNSTRAC | 1 | 196 | -0.040873 | north | -0.0026281 | -0.093923 | -0.0066947 | -0.05486 | 0.0026281 | North | N | 0.0026281 | 0
12323 | ENNSTRAC | 2 | 111 | -0.040873 | north | -0.0026281 | -0.093923 | -0.0066947 | -0.05486 | 0.0026281 | North | N | 0.0026281 | 0
12357 | RNRTPL_1 | 1 | 0 | -0.039696 | north | -0.0014511 | -0.092746 | -0.0055177 | -0.053683 | 0.0014511 | North | N | 0.0014511 | 0
12411 | FPLEFR1A | 1 | 161 | -0.039133 | north | -0.00088808 | -0.092183 | -0.0049547 | -0.05312 | 0.00088808 | North | N | 0.00088808 | 0
12412 | FPLEFR1B | 2 | 164 | -0.039133 | north | -0.00088808 | -0.092183 | -0.0049547 | -0.05312 | 0.00088808 | North | N | 0.00088808 | 0
12413 | FPLEFR1C | 3 | 164 | -0.039133 | north | -0.00088808 | -0.092183 | -0.0049547 | -0.05312 | 0.00088808 | North | N | 0.00088808 | 0
12414 | FPLEFR1S | 4 | 414 | -0.039133 | north | -0.00088808 | -0.092183 | -0.0049547 | -0.05312 | 0.00088808 | North | N | 0.00088808 | 0
12421 | FPLEFR2A | 1 | 162 | -0.039133 | north | -0.00088808 | -0.092183 | -0.0049547 | -0.05312 | 0.00088808 | North | N | 0.00088808 | 0
12422 | FPLEFR2B | 2 | 161 | -0.039133 | north | -0.00088808 | -0.092183 | -0.0049547 | -0.05312 | 0.00088808 | North | N | 0.00088808 | 0
12423 | FPLEFR2C | 3 | 163 | -0.039133 | north | -0.00088808 | -0.092183 | -0.0049547 | -0.05312 | 0.00088808 | North | N | 0.00088808 | 0
12424 | FPLEFR2S | 4 | 409 | -0.039133 | north | -0.00088808 | -0.092183 | -0.0049547 | -0.05312 | 0.00088808 | North | N | 0.00088808 | 0
12440 | PARKD_1S | 1 | 0 | -0.03953 | north | -0.0012851 | -0.09258 | -0.0053517 | -0.053517 | 0.0012851 | North | N | 0.0012851 | 0
12449 | PARKD_2S | 1 | 0 | -0.03953 | north | -0.0012851 | -0.09258 | -0.0053517 | -0.053517 | 0.0012851 | North | N | 0.0012851 | 0
13116 | TGATEWAY | 1 | 148 | -0.037855 | north | 0.00038992 | -0.090905 | -0.0036767 | -0.051842 | 0.00038992 | North | N | 0.00038992 | 0
13117 | TGATEWAY | 2 | 130 | -0.037855 | north | 0.00038992 | -0.090905 | -0.0036767 | -0.051842 | 0.00038992 | North | N | 0.00038992 | 0
13118 | TGATEWAY | 3 | 145 | -0.037855 | north | 0.00038992 | -0.090905 | -0.0036767 | -0.051842 | 0.00038992 | North | N | 0.00038992 | 0
13119 | TGATEWAY | 4 | 399 | -0.037855 | north | 0.00038992 | -0.090905 | -0.0036767 | -0.051842 | 0.00038992 | North | N | 0.00038992 | 0
13131 | CALFREST | 1 | 150.7 | -0.035832 | north | 0.0024129 | -0.088882 | -0.0016537 | -0.049819 | 0.0016537 | west | Y | 0.0024129 | 0.11442
13132 | CALFREST | 2 | 151 | -0.035832 | north | 0.0024129 | -0.088882 | -0.0016537 | -0.049819 | 0.0016537 | west | Y | 0.0024129 | 0.11464
13133 | CALFREST | 3 | 177.4 | -0.035832 | north | 0.0024129 | -0.088882 | -0.0016537 | -0.049819 | 0.0016537 | west | Y | 0.0024129 | 0.13469
13134 | CALFREST | 4 | 151.5 | -0.035915 | north | 0.0023299 | -0.088965 | -0.0017367 | -0.049902 | 0.0017367 | west | Y | 0.0023299 | 0.089875
13135 | CALFREST | 5 | 152.3 | -0.035915 | north | 0.0023299 | -0.088965 | -0.0017367 | -0.049902 | 0.0017367 | west | Y | 0.0023299 | 0.090349
13136 | CALFREST | 6 | 177.5 | -0.035915 | north | 0.0023299 | -0.088965 | -0.0017367 | -0.049902 | 0.0017367 | west | Y | 0.0023299 | 0.1053
13432 | SANDOW_5 | 5 | 581 | -0.087362 | south | -0.049117 | -0.14041 | -0.053184 | -0.10135 | 0.049117 | North | Y | 0.14041 | 53.0424
13691 | OAKGROVE | 1 | 855 | -0.025827 | north | 0.012418 | -0.078877 | 0.0083513 | -0.039814 | 0.0083513 | west | Y | 0.012418 | 3.477
13692 | OAKGROVE | 2 | 855 | -0.025827 | north | 0.012418 | -0.078877 | 0.0083513 | -0.039814 | 0.0083513 | west | Y | 0.012418 | 3.477
32798 | BRYN_TAM | 1 | 32 | -0.021257 | north | 0.016988 | -0.074307 | 0.012921 | -0.035244 | 0.012921 | west | Y | 0.016988 | 0.13013
32883 | BRYN_DNS | 1 | 48 | -0.023201 | north | 0.015044 | -0.076251 | 0.010977 | -0.037188 | 0.010977 | west | Y | 0.015044 | 0.1952
32884 | BRYN_DNS | 1 | 46 | -0.023201 | north | 0.015044 | -0.076251 | 0.010977 | -0.037188 | 0.010977 | west | Y | 0.015044 | 0.18706
32886 | BRYN_ATK | MB | 12 | -0.021425 | north | 0.01682 | -0.074475 | 0.012753 | -0.035412 | 0.012753 | west | Y | 0.01682 | 0.048799
32887 | BRYN_ATK | MB | 51 | -0.021425 | north | 0.01682 | -0.074475 | 0.012753 | -0.035412 | 0.012753 | west | Y | 0.01682 | 0.2074
32888 | BRYN_ATK | 1 | 17 | -0.021425 | north | 0.01682 | -0.074475 | 0.012753 | -0.035412 | 0.012753 | west | Y | 0.01682 | 0.069132
32890 | BRYN_ATK | MB | 22 | -0.021425 | north | 0.01682 | -0.074475 | 0.012753 | -0.035412 | 0.012753 | west | Y | 0.01682 | 0.089465
32891 | BRYN_ATK | MB | 25 | -0.021425 | north | 0.01682 | -0.074475 | 0.012753 | -0.035412 | 0.012753 | west | Y | 0.01682 | 0.10167
32892 | BRYN_DNS | 1 | 105 | -0.023201 | north | 0.015044 | -0.076251 | 0.010977 | -0.037188 | 0.010977 | west | Y | 0.015044 | 0.42699
36998 | RDCNYNG1 | 1 | 84 | -0.035073 | west | 0.0031719 | -0.088123 | -0.00089469 | -0.04906 | 0.00089469 | west | N | 0.00089469 | 0
38332 | WDWRDU2 | 1 | 80 | -0.029647 | west | 0.0085979 | -0.082697 | 0.0045313 | -0.043634 | 0.0045313 | west | N | 0.0045313 | 0
38437 | TNSRBNMS | 1 | 150 | -0.029612 | west | 0.0086329 | -0.082662 | 0.0045663 | -0.043599 | 0.0045663 | west | N | 0.0045663 | 0
38438 | TNSRBNMS | 1 | 150 | -0.029612 | west | 0.0086329 | -0.082662 | 0.0045663 | -0.043599 | 0.0045663 | west | N | 0.0045663 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.014688 | houston | 0.052933 | -0.038362 | 0.048866 | 0.00070075 | 0.00070075 | houston | N | 0.00070075 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.014688 | houston | 0.052933 | -0.038362 | 0.048866 | 0.00070075 | 0.00070075 | houston | N | 0.00070075 | 0
38600 | TNBP_CGN | 5 | 53 | 0.014688 | houston | 0.052933 | -0.038362 | 0.048866 | 0.00070075 | 0.00070075 | houston | N | 0.00070075 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.014688 | houston | 0.052933 | -0.038362 | 0.048866 | 0.00070075 | 0.00070075 | houston | N | 0.00070075 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.014688 | houston | 0.052933 | -0.038362 | 0.048866 | 0.00070075 | 0.00070075 | houston | N | 0.00070075 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.014688 | houston | 0.052933 | -0.038362 | 0.048866 | 0.00070075 | 0.00070075 | houston | N | 0.00070075 | 0
38614 | TNBPAMCG | 4 | 96 | 0.014688 | houston | 0.052933 | -0.038362 | 0.048866 | 0.00070075 | 0.00070075 | houston | N | 0.00070075 | 0
38615 | TNBPAMCG | 1 | 244 | 0.014688 | houston | 0.052933 | -0.038362 | 0.048866 | 0.00070075 | 0.00070075 | houston | N | 0.00070075 | 0
38690 | TNBP_CGN | 3 | 40 | 0.014688 | houston | 0.052933 | -0.038362 | 0.048866 | 0.00070075 | 0.00070075 | houston | N | 0.00070075 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.014698 | houston | 0.052943 | -0.038352 | 0.048876 | 0.00071075 | 0.00071075 | houston | N | 0.00071075 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.014698 | houston | 0.052943 | -0.038352 | 0.048876 | 0.00071075 | 0.00071075 | houston | N | 0.00071075 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.014698 | houston | 0.052943 | -0.038352 | 0.048876 | 0.00071075 | 0.00071075 | houston | N | 0.00071075 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.014698 | houston | 0.052943 | -0.038352 | 0.048876 | 0.00071075 | 0.00071075 | houston | N | 0.00071075 | 0
39470 | TNDOWCGN | 1 | 32 | 0.014698 | houston | 0.052943 | -0.038352 | 0.048876 | 0.00071075 | 0.00071075 | houston | N | 0.00071075 | 0
39480 | TNDOWCGN | 1 | 30 | 0.014698 | houston | 0.052943 | -0.038352 | 0.048876 | 0.00071075 | 0.00071075 | houston | N | 0.00071075 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.020946 | houston | 0.059191 | -0.032104 | 0.055124 | 0.0069588 | 0.0069588 | houston | N | 0.0069588 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.020946 | houston | 0.059191 | -0.032104 | 0.055124 | 0.0069588 | 0.0069588 | houston | N | 0.0069588 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.020946 | houston | 0.059191 | -0.032104 | 0.055124 | 0.0069588 | 0.0069588 | houston | N | 0.0069588 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.020946 | houston | 0.059191 | -0.032104 | 0.055124 | 0.0069588 | 0.0069588 | houston | N | 0.0069588 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.025827 | north | 0.012418 | -0.078877 | 0.0083513 | -0.039814 | 0.0083513 | west | Y | 0.012418 | 0.61935
39970 | TNTNPONE | 1 | 153 | -0.025827 | north | 0.012418 | -0.078877 | 0.0083513 | -0.039814 | 0.0083513 | west | Y | 0.012418 | 0.62219
48500 | APD_GT1_ | 1 | 136 | 0.010849 | houston | 0.049094 | -0.042201 | 0.045027 | -0.0031382 | 0.0031382 | houston | N | 0.0031382 | 0
48510 | AK_GT1__ | 1 | 33 | 0.016774 | houston | 0.055019 | -0.036276 | 0.050952 | 0.0027868 | 0.0027868 | houston | N | 0.0027868 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.01083 | houston | 0.049075 | -0.04222 | 0.045008 | -0.0031572 | 0.0031572 | houston | N | 0.0031572 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.01083 | houston | 0.049075 | -0.04222 | 0.045008 | -0.0031572 | 0.0031572 | houston | N | 0.0031572 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.01083 | houston | 0.049075 | -0.04222 | 0.045008 | -0.0031572 | 0.0031572 | houston | N | 0.0031572 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.01083 | houston | 0.049075 | -0.04222 | 0.045008 | -0.0031572 | 0.0031572 | houston | N | 0.0031572 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.022003 | houston | 0.060248 | -0.031047 | 0.056181 | 0.0080158 | 0.0080158 | houston | N | 0.0080158 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.022003 | houston | 0.060248 | -0.031047 | 0.056181 | 0.0080158 | 0.0080158 | houston | N | 0.0080158 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.017164 | houston | 0.055409 | -0.035886 | 0.051342 | 0.0031768 | 0.0031768 | houston | N | 0.0031768 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.017164 | houston | 0.055409 | -0.035886 | 0.051342 | 0.0031768 | 0.0031768 | houston | N | 0.0031768 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.017164 | houston | 0.055409 | -0.035886 | 0.051342 | 0.0031768 | 0.0031768 | houston | N | 0.0031768 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.012284 | houston | 0.050529 | -0.040766 | 0.046462 | -0.0017032 | 0.0017032 | houston | N | 0.0017032 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.012284 | houston | 0.050529 | -0.040766 | 0.046462 | -0.0017032 | 0.0017032 | houston | N | 0.0017032 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.012284 | houston | 0.050529 | -0.040766 | 0.046462 | -0.0017032 | 0.0017032 | houston | N | 0.0017032 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.012284 | houston | 0.050529 | -0.040766 | 0.046462 | -0.0017032 | 0.0017032 | houston | N | 0.0017032 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.011349 | houston | 0.049594 | -0.041701 | 0.045527 | -0.0026382 | 0.0026382 | houston | N | 0.0026382 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.011349 | houston | 0.049594 | -0.041701 | 0.045527 | -0.0026382 | 0.0026382 | houston | N | 0.0026382 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.012565 | houston | 0.05081 | -0.040485 | 0.046743 | -0.0014222 | 0.0014222 | houston | N | 0.0014222 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.012565 | houston | 0.05081 | -0.040485 | 0.046743 | -0.0014222 | 0.0014222 | houston | N | 0.0014222 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.012565 | houston | 0.05081 | -0.040485 | 0.046743 | -0.0014222 | 0.0014222 | houston | N | 0.0014222 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.012565 | houston | 0.05081 | -0.040485 | 0.046743 | -0.0014222 | 0.0014222 | houston | N | 0.0014222 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.012565 | houston | 0.05081 | -0.040485 | 0.046743 | -0.0014222 | 0.0014222 | houston | N | 0.0014222 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.009662 | houston | 0.047907 | -0.043388 | 0.04384 | -0.0043252 | 0.0043252 | houston | N | 0.0043252 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.010136 | houston | 0.048381 | -0.042914 | 0.044314 | -0.0038512 | 0.0038512 | houston | N | 0.0038512 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.00952 | houston | 0.047765 | -0.04353 | 0.043698 | -0.0044672 | 0.0044672 | houston | N | 0.0044672 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.00952 | houston | 0.047765 | -0.04353 | 0.043698 | -0.0044672 | 0.0044672 | houston | N | 0.0044672 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.00952 | houston | 0.047765 | -0.04353 | 0.043698 | -0.0044672 | 0.0044672 | houston | N | 0.0044672 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.006885 | houston | 0.04513 | -0.046165 | 0.041063 | -0.0071022 | 0.0071022 | houston | N | 0.0071022 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.010755 | houston | 0.049 | -0.042295 | 0.044933 | -0.0032322 | 0.0032322 | houston | N | 0.0032322 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.010755 | houston | 0.049 | -0.042295 | 0.044933 | -0.0032322 | 0.0032322 | houston | N | 0.0032322 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.009184 | houston | 0.047429 | -0.043866 | 0.043362 | -0.0048032 | 0.0048032 | houston | N | 0.0048032 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.009184 | houston | 0.047429 | -0.043866 | 0.043362 | -0.0048032 | 0.0048032 | houston | N | 0.0048032 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.009184 | houston | 0.047429 | -0.043866 | 0.043362 | -0.0048032 | 0.0048032 | houston | N | 0.0048032 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.009184 | houston | 0.047429 | -0.043866 | 0.043362 | -0.0048032 | 0.0048032 | houston | N | 0.0048032 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.011318 | houston | 0.049563 | -0.041732 | 0.045496 | -0.0026692 | 0.0026692 | houston | N | 0.0026692 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.011318 | houston | 0.049563 | -0.041732 | 0.045496 | -0.0026692 | 0.0026692 | houston | N | 0.0026692 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.011318 | houston | 0.049563 | -0.041732 | 0.045496 | -0.0026692 | 0.0026692 | houston | N | 0.0026692 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.011318 | houston | 0.049563 | -0.041732 | 0.045496 | -0.0026692 | 0.0026692 | houston | N | 0.0026692 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.011622 | houston | 0.049867 | -0.041428 | 0.0458 | -0.0023652 | 0.0023652 | houston | N | 0.0023652 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.011622 | houston | 0.049867 | -0.041428 | 0.0458 | -0.0023652 | 0.0023652 | houston | N | 0.0023652 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.011622 | houston | 0.049867 | -0.041428 | 0.0458 | -0.0023652 | 0.0023652 | houston | N | 0.0023652 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.011622 | houston | 0.049867 | -0.041428 | 0.0458 | -0.0023652 | 0.0023652 | houston | N | 0.0023652 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.011622 | houston | 0.049867 | -0.041428 | 0.0458 | -0.0023652 | 0.0023652 | houston | N | 0.0023652 | 0
48651 | EP_1_2 | 1 | 5 | 0.009686 | houston | 0.047931 | -0.043364 | 0.043864 | -0.0043012 | 0.0043012 | houston | N | 0.0043012 | 0
48651 | EP_1_2 | 2 | 21 | 0.009686 | houston | 0.047931 | -0.043364 | 0.043864 | -0.0043012 | 0.0043012 | houston | N | 0.0043012 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.011613 | north | 0.026632 | -0.064663 | 0.022565 | -0.0256 | 0.022565 | west | Y | 0.026632 | 0.62707
48672 | FTR_GT2_ | 2 | 156 | -0.011613 | north | 0.026632 | -0.064663 | 0.022565 | -0.0256 | 0.022565 | west | Y | 0.026632 | 0.63439
48673 | FTR_GT3_ | 3 | 156 | -0.011613 | north | 0.026632 | -0.064663 | 0.022565 | -0.0256 | 0.022565 | west | Y | 0.026632 | 0.63439
48674 | FTR_CN4_ | 4 | 380 | -0.011613 | north | 0.026632 | -0.064663 | 0.022565 | -0.0256 | 0.022565 | west | Y | 0.026632 | 1.5453
48690 | GBY_GN5_ | 5 | 398 | 0.009063 | houston | 0.047308 | -0.043987 | 0.043241 | -0.0049242 | 0.0049242 | houston | N | 0.0049242 | 0
48691 | GBY_7374 | A | 46 | 0.011857 | houston | 0.050102 | -0.041193 | 0.046035 | -0.0021302 | 0.0021302 | houston | N | 0.0021302 | 0
48691 | GBY_7374 | B | 46 | 0.011857 | houston | 0.050102 | -0.041193 | 0.046035 | -0.0021302 | 0.0021302 | houston | N | 0.0021302 | 0
48692 | GBY_8182 | C | 46 | 0.011857 | houston | 0.050102 | -0.041193 | 0.046035 | -0.0021302 | 0.0021302 | houston | N | 0.0021302 | 0
48692 | GBY_8182 | D | 55 | 0.011857 | houston | 0.050102 | -0.041193 | 0.046035 | -0.0021302 | 0.0021302 | houston | N | 0.0021302 | 0
48693 | GBY_8384 | E | 55 | 0.011857 | houston | 0.050102 | -0.041193 | 0.046035 | -0.0021302 | 0.0021302 | houston | N | 0.0021302 | 0
48693 | GBY_8384 | F | 54 | 0.011857 | houston | 0.050102 | -0.041193 | 0.046035 | -0.0021302 | 0.0021302 | houston | N | 0.0021302 | 0
48721 | LEG_1___ | 1 | 827 | -0.029861 | north | 0.0083839 | -0.082911 | 0.0043173 | -0.043848 | 0.0043173 | west | Y | 0.0083839 | 3.3631
48722 | LEG_2___ | 2 | 819 | -0.029861 | north | 0.0083839 | -0.082911 | 0.0043173 | -0.043848 | 0.0043173 | west | Y | 0.0083839 | 3.3306
48730 | MNS_GT | 1 | 46.1 | 0.017319 | houston | 0.055564 | -0.035731 | 0.051497 | 0.0033318 | 0.0033318 | houston | N | 0.0033318 | 0
48731 | CBE_GT1 | 1 | 76 | 0.02999 | houston | 0.068235 | -0.02306 | 0.064168 | 0.016003 | 0.016003 | houston | N | 0.016003 | 0
48732 | CBE_GT2 | 1 | 76 | 0.02999 | houston | 0.068235 | -0.02306 | 0.064168 | 0.016003 | 0.016003 | houston | N | 0.016003 | 0
48733 | CBE_ST12 | 1 | 105 | 0.02999 | houston | 0.068235 | -0.02306 | 0.064168 | 0.016003 | 0.016003 | houston | N | 0.016003 | 0
48734 | CBE_GT3 | 1 | 74 | 0.02999 | houston | 0.068235 | -0.02306 | 0.064168 | 0.016003 | 0.016003 | houston | N | 0.016003 | 0
48735 | CBE_GT4 | 1 | 74 | 0.02999 | houston | 0.068235 | -0.02306 | 0.064168 | 0.016003 | 0.016003 | houston | N | 0.016003 | 0
48736 | CBE_ST34 | 1 | 102 | 0.02999 | houston | 0.068235 | -0.02306 | 0.064168 | 0.016003 | 0.016003 | houston | N | 0.016003 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.011309 | houston | 0.049554 | -0.041741 | 0.045487 | -0.0026782 | 0.0026782 | houston | N | 0.0026782 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.011309 | houston | 0.049554 | -0.041741 | 0.045487 | -0.0026782 | 0.0026782 | houston | N | 0.0026782 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.011309 | houston | 0.049554 | -0.041741 | 0.045487 | -0.0026782 | 0.0026782 | houston | N | 0.0026782 | 0
48761 | PR_GT1__ | 1 | 35 | 0.011498 | houston | 0.049743 | -0.041552 | 0.045676 | -0.0024892 | 0.0024892 | houston | N | 0.0024892 | 0
48772 | PHR_GN2_ | MB | 459 | 0.013284 | houston | 0.051529 | -0.039766 | 0.047462 | -0.00070325 | 0.00070325 | houston | N | 0.00070325 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.009681 | houston | 0.047926 | -0.043369 | 0.043859 | -0.0043062 | 0.0043062 | houston | N | 0.0043062 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.009681 | houston | 0.047926 | -0.043369 | 0.043859 | -0.0043062 | 0.0043062 | houston | N | 0.0043062 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.009681 | houston | 0.047926 | -0.043369 | 0.043859 | -0.0043062 | 0.0043062 | houston | N | 0.0043062 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.009681 | houston | 0.047926 | -0.043369 | 0.043859 | -0.0043062 | 0.0043062 | houston | N | 0.0043062 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.009681 | houston | 0.047926 | -0.043369 | 0.043859 | -0.0043062 | 0.0043062 | houston | N | 0.0043062 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.009681 | houston | 0.047926 | -0.043369 | 0.043859 | -0.0043062 | 0.0043062 | houston | N | 0.0043062 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.009681 | houston | 0.047926 | -0.043369 | 0.043859 | -0.0043062 | 0.0043062 | houston | N | 0.0043062 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.006885 | houston | 0.04513 | -0.046165 | 0.041063 | -0.0071022 | 0.0071022 | houston | N | 0.0071022 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.006885 | houston | 0.04513 | -0.046165 | 0.041063 | -0.0071022 | 0.0071022 | houston | N | 0.0071022 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.006885 | houston | 0.04513 | -0.046165 | 0.041063 | -0.0071022 | 0.0071022 | houston | N | 0.0071022 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.006885 | houston | 0.04513 | -0.046165 | 0.041063 | -0.0071022 | 0.0071022 | houston | N | 0.0071022 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.009572 | houston | 0.047817 | -0.043478 | 0.04375 | -0.0044152 | 0.0044152 | houston | N | 0.0044152 | 0
48820 | SHELLG1_ | 1 | 71 | 0.011133 | houston | 0.049378 | -0.041917 | 0.045311 | -0.0028542 | 0.0028542 | houston | N | 0.0028542 | 0
48821 | SHELLG2 | 2 | 72 | 0.011133 | houston | 0.049378 | -0.041917 | 0.045311 | -0.0028542 | 0.0028542 | houston | N | 0.0028542 | 0
48822 | SHELLG3_ | 1 | 39 | 0.011133 | houston | 0.049378 | -0.041917 | 0.045311 | -0.0028542 | 0.0028542 | houston | N | 0.0028542 | 0
48822 | SHELLG3_ | 2 | 30 | 0.011133 | houston | 0.049378 | -0.041917 | 0.045311 | -0.0028542 | 0.0028542 | houston | N | 0.0028542 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.011761 | houston | 0.050006 | -0.041289 | 0.045939 | -0.0022262 | 0.0022262 | houston | N | 0.0022262 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.011761 | houston | 0.050006 | -0.041289 | 0.045939 | -0.0022262 | 0.0022262 | houston | N | 0.0022262 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.011321 | houston | 0.049566 | -0.041729 | 0.045499 | -0.0026662 | 0.0026662 | houston | N | 0.0026662 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.011357 | houston | 0.049602 | -0.041693 | 0.045535 | -0.0026302 | 0.0026302 | houston | N | 0.0026302 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.011367 | houston | 0.049612 | -0.041683 | 0.045545 | -0.0026202 | 0.0026202 | houston | N | 0.0026202 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.011324 | houston | 0.049569 | -0.041726 | 0.045502 | -0.0026632 | 0.0026632 | houston | N | 0.0026632 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.011314 | houston | 0.049559 | -0.041736 | 0.045492 | -0.0026732 | 0.0026732 | houston | N | 0.0026732 | 0
48855 | SRB_GT21 | B2 | 12 | 0.011374 | houston | 0.049619 | -0.041676 | 0.045552 | -0.0026132 | 0.0026132 | houston | N | 0.0026132 | 0
48855 | SRB_GT21 | MB | 18 | 0.011374 | houston | 0.049619 | -0.041676 | 0.045552 | -0.0026132 | 0.0026132 | houston | N | 0.0026132 | 0
48865 | TECO_GT1 | 1 | 50 | 0.013882 | houston | 0.052127 | -0.039168 | 0.04806 | -0.00010525 | 0.00010525 | houston | N | 0.00010525 | 0
48873 | THW_ST3_ | 3 | 104 | 0.010299 | houston | 0.048544 | -0.042751 | 0.044477 | -0.0036882 | 0.0036882 | houston | N | 0.0036882 | 0
48874 | THW_ST4_ | 4 | 104 | 0.010299 | houston | 0.048544 | -0.042751 | 0.044477 | -0.0036882 | 0.0036882 | houston | N | 0.0036882 | 0
48875 | THW_3132 | A | 54 | 0.010299 | houston | 0.048544 | -0.042751 | 0.044477 | -0.0036882 | 0.0036882 | houston | N | 0.0036882 | 0
48875 | THW_3132 | B | 53 | 0.010299 | houston | 0.048544 | -0.042751 | 0.044477 | -0.0036882 | 0.0036882 | houston | N | 0.0036882 | 0
48877 | THW_3334 | C | 54 | 0.010299 | houston | 0.048544 | -0.042751 | 0.044477 | -0.0036882 | 0.0036882 | houston | N | 0.0036882 | 0
48877 | THW_3334 | D | 57 | 0.010299 | houston | 0.048544 | -0.042751 | 0.044477 | -0.0036882 | 0.0036882 | houston | N | 0.0036882 | 0
48879 | THW_4142 | E | 54 | 0.010299 | houston | 0.048544 | -0.042751 | 0.044477 | -0.0036882 | 0.0036882 | houston | N | 0.0036882 | 0
48879 | THW_4142 | F | 54 | 0.010299 | houston | 0.048544 | -0.042751 | 0.044477 | -0.0036882 | 0.0036882 | houston | N | 0.0036882 | 0
48881 | THW_4344 | G | 58 | 0.010299 | houston | 0.048544 | -0.042751 | 0.044477 | -0.0036882 | 0.0036882 | houston | N | 0.0036882 | 0
48881 | THW_4344 | H | 58 | 0.010299 | houston | 0.048544 | -0.042751 | 0.044477 | -0.0036882 | 0.0036882 | houston | N | 0.0036882 | 0
48883 | THW_GT1_ | B2 | 12 | 0.009865 | houston | 0.04811 | -0.043185 | 0.044043 | -0.0041222 | 0.0041222 | houston | N | 0.0041222 | 0
48885 | THW_5152 | A | 56 | 0.008859 | houston | 0.047104 | -0.044191 | 0.043037 | -0.0051282 | 0.0051282 | houston | N | 0.0051282 | 0
48885 | THW_5152 | B | 59 | 0.008859 | houston | 0.047104 | -0.044191 | 0.043037 | -0.0051282 | 0.0051282 | houston | N | 0.0051282 | 0
48886 | THW_5354 | C | 56 | 0.008859 | houston | 0.047104 | -0.044191 | 0.043037 | -0.0051282 | 0.0051282 | houston | N | 0.0051282 | 0
48886 | THW_5354 | D | 56 | 0.008859 | houston | 0.047104 | -0.044191 | 0.043037 | -0.0051282 | 0.0051282 | houston | N | 0.0051282 | 0
48887 | THW_5556 | E | 59 | 0.008859 | houston | 0.047104 | -0.044191 | 0.043037 | -0.0051282 | 0.0051282 | houston | N | 0.0051282 | 0
48887 | THW_5556 | F | 56 | 0.008859 | houston | 0.047104 | -0.044191 | 0.043037 | -0.0051282 | 0.0051282 | houston | N | 0.0051282 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.028439 | houston | 0.066684 | -0.024611 | 0.062617 | 0.014452 | 0.014452 | houston | N | 0.014452 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.016556 | houston | 0.054801 | -0.036494 | 0.050734 | 0.0025688 | 0.0025688 | houston | N | 0.0025688 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.016556 | houston | 0.054801 | -0.036494 | 0.050734 | 0.0025688 | 0.0025688 | houston | N | 0.0025688 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.016556 | houston | 0.054801 | -0.036494 | 0.050734 | 0.0025688 | 0.0025688 | houston | N | 0.0025688 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.016556 | houston | 0.054801 | -0.036494 | 0.050734 | 0.0025688 | 0.0025688 | houston | N | 0.0025688 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.016556 | houston | 0.054801 | -0.036494 | 0.050734 | 0.0025688 | 0.0025688 | houston | N | 0.0025688 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.017194 | houston | 0.055439 | -0.035856 | 0.051372 | 0.0032068 | 0.0032068 | houston | N | 0.0032068 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.017194 | houston | 0.055439 | -0.035856 | 0.051372 | 0.0032068 | 0.0032068 | houston | N | 0.0032068 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.017194 | houston | 0.055439 | -0.035856 | 0.051372 | 0.0032068 | 0.0032068 | houston | N | 0.0032068 | 0
48929 | WAPGT21_ | B1 | 13 | 0.016556 | houston | 0.054801 | -0.036494 | 0.050734 | 0.0025688 | 0.0025688 | houston | N | 0.0025688 | 0
48940 | WARVUE_G | G1 | 12 | 0.009674 | houston | 0.047919 | -0.043376 | 0.043852 | -0.0043132 | 0.0043132 | houston | N | 0.0043132 | 0
49803 | EXN_15GT | 1 | 34 | 0.01002 | houston | 0.048265 | -0.04303 | 0.044198 | -0.0039672 | 0.0039672 | houston | N | 0.0039672 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.01002 | houston | 0.048265 | -0.04303 | 0.044198 | -0.0039672 | 0.0039672 | houston | N | 0.0039672 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.01002 | houston | 0.048265 | -0.04303 | 0.044198 | -0.0039672 | 0.0039672 | houston | N | 0.0039672 | 0
49826 | EXN938GT | 5 | 45.9 | 0.01002 | houston | 0.048265 | -0.04303 | 0.044198 | -0.0039672 | 0.0039672 | houston | N | 0.0039672 | 0
49828 | EXN941GT | 10 | 17.7 | 0.01002 | houston | 0.048265 | -0.04303 | 0.044198 | -0.0039672 | 0.0039672 | houston | N | 0.0039672 | 0
49829 | EXN942GT | 11 | 20.4 | 0.01002 | houston | 0.048265 | -0.04303 | 0.044198 | -0.0039672 | 0.0039672 | houston | N | 0.0039672 | 0
49830 | EXN943GT | 12 | 19.9 | 0.01002 | houston | 0.048265 | -0.04303 | 0.044198 | -0.0039672 | 0.0039672 | houston | N | 0.0039672 | 0
49831 | EXN944GT | 13 | 35 | 0.01002 | houston | 0.048265 | -0.04303 | 0.044198 | -0.0039672 | 0.0039672 | houston | N | 0.0039672 | 0
49832 | EXN945GT | 9 | 18 | 0.01002 | houston | 0.048265 | -0.04303 | 0.044198 | -0.0039672 | 0.0039672 | houston | N | 0.0039672 | 0
49837 | EXN_GT | 4 | 85.4 | 0.01002 | houston | 0.048265 | -0.04303 | 0.044198 | -0.0039672 | 0.0039672 | houston | N | 0.0039672 | 0
49838 | EXN_14GT | 14 | 148 | 0.01002 | houston | 0.048265 | -0.04303 | 0.044198 | -0.0039672 | 0.0039672 | houston | N | 0.0039672 | 0
49851 | DOW17000 | 37 | 62 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49858 | DOW38100 | 31 | 71.4 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49859 | DOW38200 | 33 | 45 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49860 | DOW38300 | 32 | 101 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49862 | DOW39100 | 36 | 86 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49863 | DOW39200 | 35 | 88 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49865 | DOW41000 | 41 | 50 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49866 | DOW42000 | 42 | 18 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49869 | DOW49000 | 45 | 94 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49870 | DOW61000 | 61 | 70 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49871 | DOW62000 | 62 | 63 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49872 | DOW63000 | 63 | 72 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49873 | DOW64000 | 64 | 64.8 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49876 | DOW65000 | 65 | 101 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49877 | DOW66000 | 66 | 97 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49878 | DOW67000 | 67 | 103 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49882 | DOW81000 | 81 | 76 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49884 | DOW82000 | 82 | 80 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49885 | DOW83000 | 83 | 80 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
49886 | DOW84000 | 84 | 171 | 0.023322 | houston | 0.061567 | -0.029728 | 0.0575 | 0.0093348 | 0.0093348 | houston | N | 0.0093348 | 0
58909 | PEARSALL | 1 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58909 | PEARSALL | 2 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58909 | PEARSALL | 3 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58909 | PEARSALL | 4 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58909 | PEARSALL | 5 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58909 | PEARSALL | 6 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58919 | PEARSALL | 1 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58919 | PEARSALL | 2 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58919 | PEARSALL | 3 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58919 | PEARSALL | 4 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58919 | PEARSALL | 5 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58919 | PEARSALL | 6 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58929 | PEARSALL | 1 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58929 | PEARSALL | 2 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58929 | PEARSALL | 3 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58929 | PEARSALL | 4 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58929 | PEARSALL | 5 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58929 | PEARSALL | 6 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58949 | PEARSALL | 1 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58949 | PEARSALL | 2 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58949 | PEARSALL | 3 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58949 | PEARSALL | 4 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58949 | PEARSALL | 5 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
58949 | PEARSALL | 6 | 8.4 | 0.052098 | south | 0.090343 | -0.00095202 | 0.086276 | 0.038111 | 0.00095202 | south | N | 0.00095202 | 0
60000 | DSKY2 | 1 | 76.5 | -0.027989 | west | 0.010256 | -0.081039 | 0.0061893 | -0.041976 | 0.0061893 | west | N | 0.0061893 | 0
60003 | KING_NE1 | 1 | 80 | -0.029716 | west | 0.0085289 | -0.082766 | 0.0044623 | -0.043703 | 0.0044623 | west | N | 0.0044623 | 0
60005 | KING_SE1 | 1 | 40 | -0.029716 | west | 0.0085289 | -0.082766 | 0.0044623 | -0.043703 | 0.0044623 | west | N | 0.0044623 | 0
60007 | KING_SW1 | 1 | 80 | -0.029994 | west | 0.0082509 | -0.083044 | 0.0041843 | -0.043981 | 0.0041843 | west | N | 0.0041843 | 0
60016 | WOODWRD1 | 1 | 80 | -0.029655 | west | 0.0085899 | -0.082705 | 0.0045233 | -0.043642 | 0.0045233 | west | N | 0.0045233 | 0
60017 | ORNNWP1 | 1 | 80 | -0.028224 | west | 0.010021 | -0.081274 | 0.0059543 | -0.042211 | 0.0059543 | west | N | 0.0059543 | 0
60018 | DSKY1 | 1 | 84 | -0.027756 | west | 0.010489 | -0.080806 | 0.0064223 | -0.041743 | 0.0064223 | west | N | 0.0064223 | 0
60019 | KING_NW1 | 1 | 80 | -0.029994 | west | 0.0082509 | -0.083044 | 0.0041843 | -0.043981 | 0.0041843 | west | N | 0.0041843 | 0
60057 | CALLAHAN | 1 | 114 | 0.062373 | south | 0.10062 | 0.009323 | 0.096551 | 0.048386 | 0.009323 | south | N | 0.009323 | 0
60058 | BUFF_GAP | 1 | 120 | -0.034646 | west | 0.0035989 | -0.087696 | -0.00046769 | -0.048633 | 0.00046769 | west | N | 0.00046769 | 0
60060 | CIRELLO | 1 | 233 | -0.034646 | west | 0.0035989 | -0.087696 | -0.00046769 | -0.048633 | 0.00046769 | west | N | 0.00046769 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.034646 | west | 0.0035989 | -0.087696 | -0.00046769 | -0.048633 | 0.00046769 | west | N | 0.00046769 | 0
60066 | H_HOLLOW | 1 | 222 | 0.062373 | south | 0.10062 | 0.009323 | 0.096551 | 0.048386 | 0.009323 | south | N | 0.009323 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.062373 | south | 0.10062 | 0.009323 | 0.096551 | 0.048386 | 0.009323 | south | N | 0.009323 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.062373 | south | 0.10062 | 0.009323 | 0.096551 | 0.048386 | 0.009323 | south | N | 0.009323 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.062373 | south | 0.10062 | 0.009323 | 0.096551 | 0.048386 | 0.009323 | south | N | 0.009323 | 0
60074 | HORSH5 | 1 | 100 | 0.062373 | south | 0.10062 | 0.009323 | 0.096551 | 0.048386 | 0.009323 | south | N | 0.009323 | 0
60081 | WHRLWIND | 1 | 60 | -0.036047 | west | 0.0021979 | -0.089097 | -0.0018687 | -0.050034 | 0.0018687 | west | N | 0.0018687 | 0
60201 | RIO DRCS | F | 0 | 0.034233 | south | 0.072478 | -0.018817 | 0.068411 | 0.020246 | 0.018817 | south | N | 0.018817 | 0
60202 | FRIEND_R | F | 0 | -0.020289 | west | 0.017956 | -0.073339 | 0.013889 | -0.034276 | 0.013889 | west | N | 0.013889 | 0
60203 | PRES0A | BT | 4.8 | -0.031024 | west | 0.0072209 | -0.084074 | 0.0031543 | -0.045011 | 0.0031543 | west | N | 0.0031543 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.035352 | west | 0.0028929 | -0.088402 | -0.0011737 | -0.049339 | 0.0011737 | west | N | 0.0011737 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.035352 | west | 0.0028929 | -0.088402 | -0.0011737 | -0.049339 | 0.0011737 | west | N | 0.0011737 | 0
71057 | L_SWEETW | W1 | 135 | -0.035352 | west | 0.0028929 | -0.088402 | -0.0011737 | -0.049339 | 0.0011737 | west | N | 0.0011737 | 0
71059 | L_SWEETW | W1 | 119 | -0.035352 | west | 0.0028929 | -0.088402 | -0.0011737 | -0.049339 | 0.0011737 | west | N | 0.0011737 | 0
71060 | L_SWEETW | W1 | 105 | -0.035352 | west | 0.0028929 | -0.088402 | -0.0011737 | -0.049339 | 0.0011737 | west | N | 0.0011737 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.035352 | west | 0.0028929 | -0.088402 | -0.0011737 | -0.049339 | 0.0011737 | west | N | 0.0011737 | 0
76031 | L_GASCCR | W1 | 150 | -0.034204 | west | 0.0040409 | -0.087254 | -2.569e-05 | -0.048191 | 2.569e-05 | west | N | 2.569e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.034059 | west | 0.0041859 | -0.087109 | 0.00011931 | -0.048046 | 0.00011931 | west | N | 0.00011931 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.034059 | west | 0.0041859 | -0.087109 | 0.00011931 | -0.048046 | 0.00011931 | west | N | 0.00011931 | 0
76096 | L_CAPRSI | W1 | 186 | -0.034059 | west | 0.0041859 | -0.087109 | 0.00011931 | -0.048046 | 0.00011931 | west | N | 0.00011931 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.034059 | west | 0.0041859 | -0.087109 | 0.00011931 | -0.048046 | 0.00011931 | west | N | 0.00011931 | 0
80003 | MILHWYS | F | 0 | 0.049298 | south | 0.087543 | -0.003752 | 0.083476 | 0.035311 | 0.003752 | south | N | 0.003752 | 0
80010 | EPLVT1 | F | 0 | 0.038776 | south | 0.077021 | -0.014274 | 0.072954 | 0.024789 | 0.014274 | south | N | 0.014274 | 0
80012 | LAR | F | 0 | 0.052152 | south | 0.090397 | -0.00089802 | 0.08633 | 0.038165 | 0.00089802 | south | N | 0.00089802 | 0
80051 | FORPVCM0 | 8 | 28 | 0.044672 | south | 0.082917 | -0.008378 | 0.07885 | 0.030685 | 0.008378 | south | N | 0.008378 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.044672 | south | 0.082917 | -0.008378 | 0.07885 | 0.030685 | 0.008378 | south | N | 0.008378 | 0
80053 | FOR69CG0 | 10 | 74 | 0.044672 | south | 0.082917 | -0.008378 | 0.07885 | 0.030685 | 0.008378 | south | N | 0.008378 | 0
80080 | GWINDT11 | 1 | 94 | 0.049263 | south | 0.087508 | -0.003787 | 0.083441 | 0.035276 | 0.003787 | south | N | 0.003787 | 0
80080 | GWINDT11 | 2 | 41 | 0.049263 | south | 0.087508 | -0.003787 | 0.083441 | 0.035276 | 0.003787 | south | N | 0.003787 | 0
80080 | GWINDT11 | 3 | 38 | 0.049263 | south | 0.087508 | -0.003787 | 0.083441 | 0.035276 | 0.003787 | south | N | 0.003787 | 0
80080 | GWINDT11 | 4 | 19 | 0.049263 | south | 0.087508 | -0.003787 | 0.083441 | 0.035276 | 0.003787 | south | N | 0.003787 | 0
80081 | GWINDT21 | 1 | 94 | 0.049263 | south | 0.087508 | -0.003787 | 0.083441 | 0.035276 | 0.003787 | south | N | 0.003787 | 0
80081 | GWINDT21 | 2 | 36 | 0.049263 | south | 0.087508 | -0.003787 | 0.083441 | 0.035276 | 0.003787 | south | N | 0.003787 | 0
80081 | GWINDT21 | 3 | 43 | 0.049263 | south | 0.087508 | -0.003787 | 0.083441 | 0.035276 | 0.003787 | south | N | 0.003787 | 0
80081 | GWINDT21 | 4 | 22 | 0.049263 | south | 0.087508 | -0.003787 | 0.083441 | 0.035276 | 0.003787 | south | N | 0.003787 | 0
80137 | CSDR89 | 8 | 39 | 0.046357 | south | 0.084602 | -0.006693 | 0.080535 | 0.03237 | 0.006693 | south | N | 0.006693 | 0
80137 | CSDR89 | 9 | 15 | 0.046357 | south | 0.084602 | -0.006693 | 0.080535 | 0.03237 | 0.006693 | south | N | 0.006693 | 0
80138 | CSDR7 | 7 | 7 | 0.046357 | south | 0.084602 | -0.006693 | 0.080535 | 0.03237 | 0.006693 | south | N | 0.006693 | 0
80139 | CSDR56 | 5 | 15 | 0.046357 | south | 0.084602 | -0.006693 | 0.080535 | 0.03237 | 0.006693 | south | N | 0.006693 | 0
80139 | CSDR56 | 6 | 39 | 0.046357 | south | 0.084602 | -0.006693 | 0.080535 | 0.03237 | 0.006693 | south | N | 0.006693 | 0
80140 | CSDR11 | 11 | 39 | 0.046357 | south | 0.084602 | -0.006693 | 0.080535 | 0.03237 | 0.006693 | south | N | 0.006693 | 0
80180 | PNSCALT1 | 1 | 148 | 0.049263 | south | 0.087508 | -0.003787 | 0.083441 | 0.035276 | 0.003787 | south | N | 0.003787 | 0
80180 | PNSCALT1 | 2 | 50 | 0.049263 | south | 0.087508 | -0.003787 | 0.083441 | 0.035276 | 0.003787 | south | N | 0.003787 | 0
80181 | PNSCALT2 | 1 | 55 | 0.049263 | south | 0.087508 | -0.003787 | 0.083441 | 0.035276 | 0.003787 | south | N | 0.003787 | 0
80181 | PNSCALT2 | 2 | 50 | 0.049263 | south | 0.087508 | -0.003787 | 0.083441 | 0.035276 | 0.003787 | south | N | 0.003787 | 0
80223 | REYSHR G | 1 | 12 | 0.048237 | south | 0.086482 | -0.004813 | 0.082415 | 0.03425 | 0.004813 | south | N | 0.004813 | 0
80224 | VISTRONG | 1 | 15 | 0.046896 | south | 0.085141 | -0.006154 | 0.081074 | 0.032909 | 0.006154 | south | N | 0.006154 | 0
80225 | VISTRONG | 2 | 23 | 0.046896 | south | 0.085141 | -0.006154 | 0.081074 | 0.032909 | 0.006154 | south | N | 0.006154 | 0
80226 | ALCOA G | 1 | 48 | 0.045069 | south | 0.083314 | -0.007981 | 0.079247 | 0.031082 | 0.007981 | south | N | 0.007981 | 0
80227 | AIRCO G | 1 | 8 | 0.04656 | south | 0.084805 | -0.00649 | 0.080738 | 0.032573 | 0.00649 | south | N | 0.00649 | 0
80261 | NBEC81A | 1 | 180 | 0.048768 | south | 0.087013 | -0.004282 | 0.082946 | 0.034781 | 0.004282 | south | N | 0.004282 | 0
80262 | NBEC91A | 1 | 180 | 0.048753 | south | 0.086998 | -0.004297 | 0.082931 | 0.034766 | 0.004297 | south | N | 0.004297 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.048867 | south | 0.087112 | -0.004183 | 0.083045 | 0.03488 | 0.004183 | south | N | 0.004183 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.048867 | south | 0.087112 | -0.004183 | 0.083045 | 0.03488 | 0.004183 | south | N | 0.004183 | 0
80265 | LARECU40 | 4 | 100 | 0.052157 | south | 0.090402 | -0.00089302 | 0.086335 | 0.03817 | 0.00089302 | south | N | 0.00089302 | 0
80266 | LARECU50 | 5 | 100 | 0.052157 | south | 0.090402 | -0.00089302 | 0.086335 | 0.03817 | 0.00089302 | south | N | 0.00089302 | 0
80291 | PAPALOTE | 1 | 25 | 0.048442 | south | 0.086687 | -0.004608 | 0.08262 | 0.034455 | 0.004608 | south | N | 0.004608 | 0
80291 | PAPALOTE | 2 | 25 | 0.048442 | south | 0.086687 | -0.004608 | 0.08262 | 0.034455 | 0.004608 | south | N | 0.004608 | 0
80291 | PAPALOTE | 3 | 25 | 0.048442 | south | 0.086687 | -0.004608 | 0.08262 | 0.034455 | 0.004608 | south | N | 0.004608 | 0
80291 | PAPALOTE | 4 | 16 | 0.048442 | south | 0.086687 | -0.004608 | 0.08262 | 0.034455 | 0.004608 | south | N | 0.004608 | 0
80294 | PAPALOTE | 5 | 25 | 0.048442 | south | 0.086687 | -0.004608 | 0.08262 | 0.034455 | 0.004608 | south | N | 0.004608 | 0
80294 | PAPALOTE | 6 | 25 | 0.048442 | south | 0.086687 | -0.004608 | 0.08262 | 0.034455 | 0.004608 | south | N | 0.004608 | 0
80294 | PAPALOTE | 7 | 25 | 0.048442 | south | 0.086687 | -0.004608 | 0.08262 | 0.034455 | 0.004608 | south | N | 0.004608 | 0
80294 | PAPALOTE | 8 | 15 | 0.048442 | south | 0.086687 | -0.004608 | 0.08262 | 0.034455 | 0.004608 | south | N | 0.004608 | 0
86104 | CID-138 | EQ | 0 | 0.052157 | south | 0.090402 | -0.00089302 | 0.086335 | 0.03817 | 0.00089302 | south | N | 0.00089302 | 0
86105 | CID-230 | EQ | 500 | 0.052157 | south | 0.090402 | -0.00089302 | 0.086335 | 0.03817 | 0.00089302 | south | N | 0.00089302 | 0
86106 | CUF-230 | EQ | 500 | 0.052157 | south | 0.090402 | -0.00089302 | 0.086335 | 0.03817 | 0.00089302 | south | N | 0.00089302 | 0
86107 | CUF-138 | EQ | 0 | 0.052157 | south | 0.090402 | -0.00089302 | 0.086335 | 0.03817 | 0.00089302 | south | N | 0.00089302 | 0
88198 | BEEVILLE | F | 0 | 0.051577 | south | 0.089822 | -0.001473 | 0.085755 | 0.03759 | 0.001473 | south | N | 0.001473 | 0
88253 | HAMILTON | F | 0 | 0.030179 | south | 0.068424 | -0.022871 | 0.064357 | 0.016192 | 0.016192 | houston | Y | 0.022871 | 0
88299 | ZAPATA | F | 0 | 0.050786 | south | 0.089031 | -0.002264 | 0.084964 | 0.036799 | 0.002264 | south | N | 0.002264 | 0
88508 | FALFURRI | F | 0 | 0.050128 | south | 0.088373 | -0.002922 | 0.084306 | 0.036141 | 0.002922 | south | N | 0.002922 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3668 RNDROCK1 - 3670 RNDRCKNE_ctg1 C:SANDOW__5-L_AUSTRO5_1Y C:L_AUSTRO5_1Y-SAND_TXU_59 [3429 - 7040 ckt1] and [7040 - 13429 ckt2] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 6.2373 | 100 | 0.10369 | 10.3687 | 100 | 10.3687
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.034233 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.075547 | 0 | 100 | 10.3687
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.10294 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.82354 | 0 | 0.049893 | 0 | 100 | 10.3687
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.10294 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.82354 | 0 | 0.049893 | 0 | 100 | 10.3687 | Weighted Shift Factors
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.10214 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 31.6631 | 310 | 0.049089 | 15.2176 | 410 | 25.5863 | South | 0.05305
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.10214 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 42.1834 | 413 | 0.049089 | 20.2737 |  |  | North | -0.041314
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.099995 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.1998 | 42 | 0.046945 | 1.9717 |  |  |  | 0.094364
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.099995 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.3998 | 44 | 0.046945 | 2.0656
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.099995 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.3998 | 44 | 0.046945 | 2.0656 |  |  | Line Rating | 247.95
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.099995 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.6998 | 47 | 0.046945 | 2.2064 |  |  | Conc Gen | 410
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.7585 | 49 | 0.044062 | 2.159 |  |  | Weighted Imp. | 25.5863
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.4672 | 46 | 0.044062 | 2.0269 |  |  | PTDF | 0.062406
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.4672 | 46 | 0.044062 | 2.0269
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.5643 | 47 | 0.044062 | 2.0709 |  |  | Concentration | 0.66133
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.097112 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.9552 | 154 | 0.044062 | 6.7855
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.097112 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.3726 | 148 | 0.044062 | 6.5212
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.6614 | 48 | 0.044062 | 2.115
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.6614 | 48 | 0.044062 | 2.115
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.041314 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.041314 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.092702 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.2446 | 0 | 0.039652 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.092702 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.1519 | 0 | 0.039652 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.092702 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.2446 | 0 | 0.039652 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.011613 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.7907 | 0 | 0.029701 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.011613 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.8116 | 0 | 0.029701 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.011613 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.8116 | 0 | 0.029701 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.011613 | north | 1 | N | N | Nnorth | Nnorth | 1 | -4.4129 | 0 | 0.029701 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.013404 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0106 | 150 | 0.02791 | 4.1865
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.015554 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -7.2015 | 463 | 0.02576 | 11.927
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.074455 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3402 | 0 | 0.021405 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.074455 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3402 | 0 | 0.021405 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.020289 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.021025 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.073887 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.2678 | 152.5 | 0.020837 | 3.1776
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.073887 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.0461 | 149.5 | 0.020837 | 3.1151
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.073887 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 17.1861 | 232.6 | 0.020837 | 4.8467
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.021257 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.68022 | 0 | 0.020057 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.021425 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.019889 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.021425 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.019889 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.021425 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.36423 | 17 | 0.019889 | 0.33812
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.021425 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.019889 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.021425 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.019889 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.023201 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.1136 | 48 | 0.018113 | 0.86944
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.023201 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.0672 | 46 | 0.018113 | 0.83321
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.023201 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.4361 | 105 | 0.018113 | 1.9019
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.07063 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.42378 | 0 | 0.01758 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.070374 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.1191 | 158 | 0.017324 | 2.7372
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.070374 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.2598 | 160 | 0.017324 | 2.7718
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.070374 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 12.3155 | 175 | 0.017324 | 3.0317
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.025827 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -22.0821 | 855 | 0.015487 | 13.2416
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.025827 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -22.0821 | 855 | 0.015487 | 13.2416
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.025827 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.9335 | 152.3 | 0.015487 | 2.3587
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.025827 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.9515 | 153 | 0.015487 | 2.3696
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.067064 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8778 | 0 | 0.014014 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.067064 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.9449 | 0 | 0.014014 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.027756 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3315 | 84 | 0.013558 | 1.1389
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.066408 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 28.0242 | 422 | 0.013358 | 5.6371
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.027989 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.1412 | 76.5 | 0.013325 | 1.0194
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.028224 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2579 | 80 | 0.01309 | 1.0472
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.065061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.5672 | 223.9 | 0.012011 | 2.6893
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.065061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.6387 | 225 | 0.012011 | 2.7025
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.065061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.6127 | 224.6 | 0.012011 | 2.6977
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.065061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.7493 | 226.7 | 0.012011 | 2.7229
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.029612 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4418 | 150 | 0.011702 | 1.7553
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.029612 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4418 | 150 | 0.011702 | 1.7553
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.029647 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3718 | 80 | 0.011667 | 0.93338
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.029655 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3724 | 80 | 0.011659 | 0.93274
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.029716 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2287 | 75 | 0.011598 | 0.86987
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.029716 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3773 | 80 | 0.011598 | 0.92786
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.029716 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.1886 | 40 | 0.011598 | 0.46393
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.029861 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -24.695 | 827 | 0.011453 | 9.4719
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.029861 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -24.4562 | 819 | 0.011453 | 9.3802
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.029994 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3995 | 80 | 0.01132 | 0.90562
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.029994 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3995 | 80 | 0.01132 | 0.90562
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.0639 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.15336 | 0 | 0.01085 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.0639 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.15336 | 0 | 0.01085 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.0639 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.17892 | 0 | 0.01085 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.063786 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 37.251 | 584 | 0.010736 | 6.2698
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.063786 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 37.9527 | 595 | 0.010736 | 6.3879
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.063753 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 27.605 | 433 | 0.010703 | 4.6344
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.031024 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.14892 | 0 | 0.01029 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.062982 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.25193 | 0 | 0.009932 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.062882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.9292 | 142 | 0.009832 | 1.3961
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.062882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.1179 | 145 | 0.009832 | 1.4256
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.062882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.4952 | 151 | 0.009832 | 1.4846
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.062882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.2358 | 290 | 0.009832 | 2.8513
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.062444 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14987 | 0 | 0.009394 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.062444 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14987 | 0 | 0.009394 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.1105 | 114 | 0.009323 | 1.0628
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 13.8468 | 222 | 0.009323 | 2.0697
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 11.4766 | 184 | 0.009323 | 1.7154
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 13.9716 | 224 | 0.009323 | 2.0883
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.1729 | 115 | 0.009323 | 1.0721
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.061624 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.1344 | 132 | 0.008574 | 1.1318
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.061624 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.2576 | 134 | 0.008574 | 1.1489
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.061624 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 19.9046 | 323 | 0.008574 | 2.7694
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.212 | 66 | 0.0077993 | 0.51475
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.1785 | 65 | 0.0077993 | 0.50695
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.2455 | 67 | 0.0077993 | 0.52255
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.2455 | 67 | 0.0077993 | 0.52255
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.2455 | 67 | 0.0077993 | 0.52255
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.033515 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0077993 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.033515 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0077993 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.033525 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.6825 | 169.5 | 0.0077893 | 1.3203
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.033549 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.1742 | 35 | 0.0077653 | 0.27178
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.033549 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.0065 | 30 | 0.0077653 | 0.23296
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.9257 | 147 | 0.007669 | 1.1273
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.3792 | 138 | 0.007669 | 1.0583
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.5007 | 140 | 0.007669 | 1.0737
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.9257 | 147 | 0.007669 | 1.1273
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.0509 | 182 | 0.007669 | 1.3958
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 12.0224 | 198 | 0.007669 | 1.5185
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.033667 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.0164 | 149 | 0.0076473 | 1.1394
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.033864 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.2235 | 6.6 | 0.0074503 | 0.049172
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.033864 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.1615 | 34.3 | 0.0074503 | 0.25554
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.034059 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8316 | 112.5 | 0.0072553 | 0.81622
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.034059 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.0918 | 149.5 | 0.0072553 | 1.0847
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.034059 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.335 | 186 | 0.0072553 | 1.3495
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.034059 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.3057 | 214.5 | 0.0072553 | 1.5563
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.1184 | 208.2 | 0.0071243 | 1.4833
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.8584 | 142.1 | 0.0071243 | 1.0124
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.5268 | 132.4 | 0.0071243 | 0.94325
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.6498 | 136 | 0.0071243 | 0.9689
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.0259 | 147 | 0.0071243 | 1.0473
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.1799 | 210 | 0.0071243 | 1.4961
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.3938 | 70 | 0.0071173 | 0.49821
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.3938 | 70 | 0.0071173 | 0.49821
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.1735 | 92.8 | 0.0071173 | 0.66048
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.7358 | 80 | 0.0071173 | 0.56938
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.7358 | 80 | 0.0071173 | 0.56938
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.9327 | 115 | 0.0071173 | 0.81849
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.034204 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.1306 | 150 | 0.0071103 | 1.0665
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.034225 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.985 | 58 | 0.0070893 | 0.41118
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.034234 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4405 | 100.5 | 0.0070803 | 0.71157
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.034317 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.3507 | 214.2 | 0.0069973 | 1.4988
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.034359 | west | 8 | N | N | Nwest | Nwest | 1 | -0.88646 | 0 | 0.0069553 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.059954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.9977 | 50 | 0.006904 | 0.3452
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.059954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.9977 | 50 | 0.006904 | 0.3452
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.059954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.9977 | 50 | 0.006904 | 0.3452
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.059954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.9977 | 50 | 0.006904 | 0.3452
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.034576 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1491 | 120 | 0.0067383 | 0.80859
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.034592 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.151 | 120 | 0.0067223 | 0.80667
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.034646 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1575 | 120 | 0.0066683 | 0.80019
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.034646 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.0725 | 233 | 0.0066683 | 1.5537
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.034646 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.8967 | 170.2 | 0.0066683 | 1.1349
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.034664 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.7994 | 225 | 0.0066503 | 1.4963
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.03468 | west | 8 | N | N | Nwest | Nwest | 1 | -2.4276 | 0 | 0.0066343 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.03468 | west | 8 | N | N | Nwest | Nwest | 1 | -2.5455 | 0 | 0.0066343 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.03468 | west | 8 | N | N | Nwest | Nwest | 1 | -2.4415 | 0 | 0.0066343 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.0347 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.246 | 180 | 0.0066143 | 1.1906
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.0347 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.246 | 180 | 0.0066143 | 1.1906
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.034789 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2184 | 150 | 0.0065253 | 0.97879
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.034789 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.6536 | 220 | 0.0065253 | 1.4356
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.034789 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9578 | 200 | 0.0065253 | 1.3051
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.034789 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2408 | 121.9 | 0.0065253 | 0.79543
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.059567 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.006517 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.059567 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.006517 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.059567 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.006517 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.3026 | 66 | 0.0064263 | 0.42413
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4073 | 69 | 0.0064263 | 0.44341
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4073 | 69 | 0.0064263 | 0.44341
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.3375 | 67 | 0.0064263 | 0.43056
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.3375 | 67 | 0.0064263 | 0.43056
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.2677 | 65 | 0.0064263 | 0.41771
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.03493 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2006 | 63 | 0.0063843 | 0.40221
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.034961 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.9295 | 141 | 0.0063533 | 0.89581
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.034961 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1953 | 120 | 0.0063533 | 0.76239
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.059403 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 25.1869 | 424 | 0.006353 | 2.6937
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.059403 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 25.2463 | 425 | 0.006353 | 2.7
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.034972 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4622 | 99 | 0.0063423 | 0.62788
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.034972 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.1333 | 61 | 0.0063423 | 0.38688
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.034972 | west | 7 | N | N | Nwest | Nwest | 1 | -0.8743 | 0 | 0.0063423 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.034972 | west | 7 | N | N | Nwest | Nwest | 1 | -1.5982 | 0 | 0.0063423 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.034972 | west | 7 | N | N | Nwest | Nwest | 1 | -1.5982 | 0 | 0.0063423 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.059392 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 24.4695 | 412 | 0.006342 | 2.6129
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.059392 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 23.7568 | 400 | 0.006342 | 2.5368
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.05933 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 12.4 | 209 | 0.00628 | 1.3125
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.05933 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 12.8153 | 216 | 0.00628 | 1.3565
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.05933 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.7292 | 46 | 0.00628 | 0.28888
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.05933 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.7885 | 47 | 0.00628 | 0.29516
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.05933 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.7292 | 46 | 0.00628 | 0.28888
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.05933 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.7292 | 46 | 0.00628 | 0.28888
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.035073 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9461 | 84 | 0.0062413 | 0.52427
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.059273 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 24.1241 | 407 | 0.006223 | 2.5328
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.035147 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.3934 | 125 | 0.0061673 | 0.77091
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.035147 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.3934 | 125 | 0.0061673 | 0.77091
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.035202 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2803 | 150 | 0.0061123 | 0.91684
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.035202 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.5554 | 101 | 0.0061123 | 0.61734
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.059099 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.1603 | 155 | 0.006049 | 0.93759
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.059099 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 10.0468 | 170 | 0.006049 | 1.0283
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.059099 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.1603 | 155 | 0.006049 | 0.93759
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3257 | 37.5 | 0.0059623 | 0.22358
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8003 | 107.5 | 0.0059623 | 0.64094
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7725 | 135 | 0.0059623 | 0.80491
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2069 | 119 | 0.0059623 | 0.70951
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.712 | 105 | 0.0059623 | 0.62604
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8458 | 80.5 | 0.0059623 | 0.47996
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.035394 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.3973 | 209 | 0.0059203 | 1.2373
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.035394 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4773 | 126.5 | 0.0059203 | 0.74891
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.035394 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8131 | 249 | 0.0059203 | 1.4741
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.035394 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9726 | 197 | 0.0059203 | 1.1663
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.058961 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.4197 | 58 | 0.005911 | 0.34284
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.058961 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.2475 | 89 | 0.005911 | 0.52608
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.058961 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.5943 | 44 | 0.005911 | 0.26008
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.058961 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.5943 | 44 | 0.005911 | 0.26008
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.058961 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.5353 | 43 | 0.005911 | 0.25417
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.058961 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.6532 | 45 | 0.005911 | 0.26599
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.035413 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -21.779 | 615 | 0.0059013 | 3.6293
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.035413 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -20.7874 | 587 | 0.0059013 | 3.464
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.035519 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.3278 | 150 | 0.0057953 | 0.86929
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.058777 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 32.0922 | 546 | 0.005727 | 3.1269
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.058777 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 44.0827 | 750 | 0.005727 | 4.2952
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.035832 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.3999 | 150.7 | 0.0054823 | 0.82618
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.035832 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4106 | 151 | 0.0054823 | 0.82782
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.035832 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3566 | 177.4 | 0.0054823 | 0.97255
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.035915 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4411 | 151.5 | 0.0053993 | 0.81799
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.035915 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4699 | 152.3 | 0.0053993 | 0.82231
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.035915 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3749 | 177.5 | 0.0053993 | 0.95837
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.036047 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.1628 | 60 | 0.0052673 | 0.31604
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.058143 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.69772 | 0 | 0.005093 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.036642 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.6568 | 400 | 0.0046723 | 1.8689
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.036644 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.648 | 236 | 0.0046703 | 1.1022
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.057312 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.78517 | 0 | 0.004262 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.037059 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.1147 | 165 | 0.0042553 | 0.70212
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.037401 | west | 4 | Y | N | Ywest | Nwest | 1 | -24.2994 | 649.7 | 0.0039133 | 2.5424
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.037678 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -6.8574 | 182 | 0.0036363 | 0.6618
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.037678 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -18.2362 | 484 | 0.0036363 | 1.76
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.037691 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.8845 | 50 | 0.0036233 | 0.18116
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.037709 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.0036053 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.056601 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.0188 | 0 | 0.003551 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.056601 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.0188 | 0 | 0.003551 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.056601 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.84901 | 0 | 0.003551 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.037855 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.6025 | 0 | 0.0034593 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.037855 | north | 1 | N | N | Nnorth | Nnorth | 1 | -4.9211 | 0 | 0.0034593 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.037855 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.489 | 0 | 0.0034593 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.037855 | north | 1 | N | N | Nnorth | Nnorth | 1 | -15.1041 | 0 | 0.0034593 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.03802 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -29.8457 | 785 | 0.0032943 | 2.586
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.03802 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -30.2259 | 795 | 0.0032943 | 2.6189
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.03802 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -29.6556 | 780 | 0.0032943 | 2.5695
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.038374 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -14.0449 | 366 | 0.0029403 | 1.0761
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.038451 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.3051 | 242 | 0.0028633 | 0.69291
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.038466 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.76932 | 20 | 0.0028483 | 0.056965
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.038466 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.76932 | 20 | 0.0028483 | 0.056965
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.038466 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.76932 | 20 | 0.0028483 | 0.056965
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.038466 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.65392 | 17 | 0.0028483 | 0.048421
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.055557 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 22.0006 | 396 | 0.002507 | 0.99276
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3004 | 161 | 0.0021813 | 0.35118
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.4178 | 164 | 0.0021813 | 0.35773
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.4178 | 164 | 0.0021813 | 0.35773
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -16.2011 | 414 | 0.0021813 | 0.90304
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3395 | 162 | 0.0021813 | 0.35337
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3004 | 161 | 0.0021813 | 0.35118
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3787 | 163 | 0.0021813 | 0.35555
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -16.0054 | 409 | 0.0021813 | 0.89214
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.039322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.0217 | 204 | 0.0019923 | 0.40642
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.039322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.9037 | 201 | 0.0019923 | 0.40045
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.039322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.5159 | 242 | 0.0019923 | 0.48213
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.039397 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.78794 | 20 | 0.0019173 | 0.038345
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.039398 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.98495 | 25 | 0.0019163 | 0.047907
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.039398 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.6153 | 41 | 0.0019163 | 0.078567
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.039415 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -15.293 | 388 | 0.0018993 | 0.73692
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.039415 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -20.2987 | 515 | 0.0018993 | 0.97812
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.039415 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -21.9936 | 558 | 0.0018993 | 1.0598
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.039415 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -22.8213 | 579 | 0.0018993 | 1.0997
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.039415 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -31.8473 | 808 | 0.0018993 | 1.5346
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.03943 | north | 8 | N | N | Nnorth | Nnorth | 1 | -2.9573 | 0 | 0.0018843 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.03943 | north | 8 | N | N | Nnorth | Nnorth | 1 | -3.1386 | 0 | 0.0018843 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.03943 | north | 8 | N | N | Nnorth | Nnorth | 1 | -3.4856 | 0 | 0.0018843 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.03944 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.1158 | 79 | 0.0018743 | 0.14807
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.03944 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -4.1806 | 106 | 0.0018743 | 0.19867
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.03944 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -5.7582 | 146 | 0.0018743 | 0.27364
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.03944 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.9974 | 76 | 0.0018743 | 0.14244
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3122 | 160 | 0.0018633 | 0.29812
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.1544 | 156 | 0.0018633 | 0.29067
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.7324 | 196 | 0.0018633 | 0.3652
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.1544 | 156 | 0.0018633 | 0.29067
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.1938 | 157 | 0.0018633 | 0.29253
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.8113 | 198 | 0.0018633 | 0.36893
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.039459 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.5784 | 40 | 0.0018553 | 0.074211
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.039473 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -14.605 | 370 | 0.0018413 | 0.68127
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.5262 | 0 | 0.0018413 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.5657 | 0 | 0.0018413 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | 1 | -12.1972 | 0 | 0.0018413 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.6446 | 0 | 0.0018413 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.6841 | 0 | 0.0018413 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | 1 | -12.2366 | 0 | 0.0018413 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.039474 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -4.7369 | 120 | 0.0018403 | 0.22083
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.03949 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.47388 | 0 | 0.0018243 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.03949 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.47388 | 0 | 0.0018243 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.039506 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -6.716 | 170 | 0.0018083 | 0.30741
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.039506 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -20.5431 | 520 | 0.0018083 | 0.9403
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.03953 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0017843 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.03953 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0017843 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.039535 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.5814 | 0 | 0.0017793 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.039535 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.5814 | 0 | 0.0017793 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.039684 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0016303 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.039696 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0016183 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.039756 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -4.4726 | 112.5 | 0.0015583 | 0.1753
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.039815 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.3889 | 60 | 0.0014993 | 0.089956
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.039815 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.5083 | 63 | 0.0014993 | 0.094454
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.039822 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.9201 | 224 | 0.0014923 | 0.33427
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.040016 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.7219 | 118 | 0.0012983 | 0.1532
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.040016 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -4.6018 | 115 | 0.0012983 | 0.1493
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.040016 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -22.2489 | 556 | 0.0012983 | 0.72184
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.040084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.5442 | 288 | 0.0012303 | 0.35432
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.040084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.8923 | 147 | 0.0012303 | 0.18085
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.040084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.8923 | 147 | 0.0012303 | 0.18085
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.040131 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.4079 | 60 | 0.0011833 | 0.070996
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.040267 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0010473 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.040267 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0010473 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.040267 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0010473 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.040423 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.72761 | 18 | 0.00089127 | 0.016043
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.040423 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.72761 | 18 | 0.00089127 | 0.016043
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.040423 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.5361 | 38 | 0.00089127 | 0.033868
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.040463 | north | 3 | N | N | Nnorth | Nnorth | 1 | -46.8157 | 0 | 0.00085127 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.040463 | north | 3 | N | N | Nnorth | Nnorth | 1 | -46.8562 | 0 | 0.00085127 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.040569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.8156 | 217.3 | 0.00074527 | 0.16195
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.040569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.3166 | 205 | 0.00074527 | 0.15278
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.040569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.051 | 272.4 | 0.00074527 | 0.20301
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.040709 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00060527 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.040731 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.9734 | 73 | 0.00058327 | 0.042578
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.040731 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.847 | 119 | 0.00058327 | 0.069409
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.040731 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.3499 | 205 | 0.00058327 | 0.11957
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.040731 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -4.1546 | 102 | 0.00058327 | 0.059493
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.040731 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -3.9102 | 96 | 0.00058327 | 0.055994
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.040858 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -17.7732 | 435 | 0.00045627 | 0.19848
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.040873 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.0111 | 196 | 0.00044127 | 0.086488
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.040873 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.5369 | 111 | 0.00044127 | 0.048981
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.040914 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -16.161 | 395 | 0.00040027 | 0.15811
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.040914 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -17.7976 | 435 | 0.00040027 | 0.17412
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.041367 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.8957 | 70 | -5.2734e-05 | -0.0036914
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.041367 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.8543 | 69 | -5.2734e-05 | -0.0036386
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.041367 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.8543 | 69 | -5.2734e-05 | -0.0036386
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.041367 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.813 | 68 | -5.2734e-05 | -0.0035859
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.052646 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2635 | 24 | -0.00040402 | -0.0096966
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.052646 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 1.2635 | 24 | -0.00040402 | -0.0096966
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.052646 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 1.2109 | 23 | -0.00040402 | -0.0092926
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.052157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.2157 | 100 | -0.00089302 | -0.089302
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.052157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.2157 | 100 | -0.00089302 | -0.089302
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.052157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.00089302 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.052157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.00089302 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.052157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.00089302 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.052157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.00089302 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.052152 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.00089802 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.042271 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.1474 | 216.4 | -0.00095673 | -0.20704
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.042271 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.1348 | 216.1 | -0.00095673 | -0.20675
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.042387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.4947 | 224 | -0.0010727 | -0.24029
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.042387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.5795 | 226 | -0.0010727 | -0.24244
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.042387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.986 | 212 | -0.0010727 | -0.22742
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.042387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.9437 | 211 | -0.0010727 | -0.22635
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.042648 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.1649 | 168 | -0.0013337 | -0.22407
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.042648 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8383 | 90 | -0.0013337 | -0.12004
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.051577 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.001473 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.050815 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 31.9626 | 629 | -0.002235 | -1.4058
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.050786 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.002264 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.050159 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.60191 | 0 | -0.002891 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.050159 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.55175 | 0 | -0.002891 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.050159 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.60191 | 0 | -0.002891 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.050128 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.002922 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.049504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.2523 | 146.5 | -0.003546 | -0.51949
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.049504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.3216 | 147.9 | -0.003546 | -0.52446
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.049504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.5642 | 173 | -0.003546 | -0.61346
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.049399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 10.2256 | 207 | -0.003651 | -0.75576
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.049399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 10.7048 | 216.7 | -0.003651 | -0.79118
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.049399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.9546 | 242 | -0.003651 | -0.88355
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.049398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.1133 | 144 | -0.003652 | -0.52589
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.049398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.1133 | 144 | -0.003652 | -0.52589
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.049398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.4471 | 171 | -0.003652 | -0.6245
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.049298 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.003752 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.049298 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8733 | 38 | -0.003752 | -0.14258
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.049298 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.95145 | 19.3 | -0.003752 | -0.072414
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.049298 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.73947 | 15 | -0.003752 | -0.05628
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.049298 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.317 | 47 | -0.003752 | -0.17635
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.6307 | 94 | -0.003787 | -0.35598
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0198 | 41 | -0.003787 | -0.15527
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.872 | 38 | -0.003787 | -0.14391
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.936 | 19 | -0.003787 | -0.071953
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.6307 | 94 | -0.003787 | -0.35598
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7735 | 36 | -0.003787 | -0.13633
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.1183 | 43 | -0.003787 | -0.16284
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.0838 | 22 | -0.003787 | -0.083315
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.2909 | 148 | -0.003787 | -0.56048
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.4632 | 50 | -0.003787 | -0.18935
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.7095 | 55 | -0.003787 | -0.20829
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.4632 | 50 | -0.003787 | -0.18935
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.049179 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.4262 | 0 | -0.003871 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.048936 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8596 | 0 | -0.004114 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.048934 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8595 | 0 | -0.004116 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.048884 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2221 | 0 | -0.004166 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.048884 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2221 | 0 | -0.004166 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.048867 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 16.3216 | 334 | -0.004183 | -1.3971
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.048867 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 16.6148 | 340 | -0.004183 | -1.4222
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.048867 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.7961 | 180 | -0.004183 | -0.75294
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.048867 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.7961 | 180 | -0.004183 | -0.75294
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.048768 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.7782 | 180 | -0.004282 | -0.77076
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.048759 | south | 8 | N | N | Nsouth | Nsouth | -1 | 7.231 | 0 | -0.004291 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.048759 | south | 8 | N | N | Nsouth | Nsouth | -1 | 7.2456 | 0 | -0.004291 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.048759 | south | 8 | N | N | Nsouth | Nsouth | -1 | 7.4601 | 0 | -0.004291 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.048753 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 16.381 | 336 | -0.004297 | -1.4438
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.048753 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.7755 | 180 | -0.004297 | -0.77346
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.211 | 25 | -0.004608 | -0.1152
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.211 | 25 | -0.004608 | -0.1152
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.211 | 25 | -0.004608 | -0.1152
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.77507 | 16 | -0.004608 | -0.073728
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.211 | 25 | -0.004608 | -0.1152
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.211 | 25 | -0.004608 | -0.1152
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.211 | 25 | -0.004608 | -0.1152
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.72663 | 15 | -0.004608 | -0.06912
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.048364 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.9644 | 144 | -0.004686 | -0.67479
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.048364 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.0924 | 188 | -0.004686 | -0.88097
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -1 | 7.6214 | 0 | -0.004813 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -1 | 7.3803 | 0 | -0.004813 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.8237 | 0 | -0.004813 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -1 | 6.9944 | 0 | -0.004813 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -1 | 7.0908 | 0 | -0.004813 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -1 | 6.1261 | 0 | -0.004813 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.048237 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.57884 | 0 | -0.004813 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.047827 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.4914 | 0 | -0.005223 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.047752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2778 | 47.7 | -0.005298 | -0.25272
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.047752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.7811 | 37.3 | -0.005298 | -0.19762
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.047752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1966 | 46 | -0.005298 | -0.24371
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.047752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2921 | 48 | -0.005298 | -0.25431
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.047321 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0411 | 22 | -0.005729 | -0.12604
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.047321 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.52053 | 11 | -0.005729 | -0.063019
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.047321 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.52053 | 11 | -0.005729 | -0.063019
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.046896 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.70344 | 0 | -0.006154 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.046896 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0786 | 0 | -0.006154 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.04656 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.37248 | 0 | -0.00649 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.298 | 0 | -0.006693 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3245 | 0 | -0.006693 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8079 | 0 | -0.006693 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.69535 | 0 | -0.006693 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3245 | 0 | -0.006693 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.69535 | 0 | -0.006693 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8079 | 0 | -0.006693 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8079 | 0 | -0.006693 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.045069 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.1633 | 0 | -0.007981 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.5291 | 0 | -0.008378 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.6184 | 0 | -0.008378 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.5291 | 0 | -0.008378 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.5738 | 0 | -0.008378 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.5023 | 0 | -0.008378 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1168 | 0 | -0.008378 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.0549 | 0 | -0.008378 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2508 | 0 | -0.008378 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9477 | 0 | -0.008378 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.3057 | 0 | -0.008378 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.053277 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.79915 | 0 | -0.011963 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.053277 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.79915 | 0 | -0.011963 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.038776 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.014274 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.055886 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.3829 | 150 | -0.014572 | -2.1858
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.055886 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.4709 | 80 | -0.014572 | -1.1657
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.037154 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22292 | 0 | -0.015896 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.057767 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -14.7306 | 255 | -0.016453 | -4.1954
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.057767 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.6073 | 149 | -0.016453 | -2.4515
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.057767 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.8384 | 153 | -0.016453 | -2.5173
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.06006 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.018746 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.06006 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -47.2672 | 787 | -0.018746 | -14.7529
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.060383 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.019069 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.060383 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.019069 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.030529 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 40.6952 | 0 | -0.022521 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.030529 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 40.5425 | 0 | -0.022521 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.030179 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.99591 | 0 | -0.022871 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.030179 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.75448 | 0 | -0.022871 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.030179 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.022871 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.2792 | 76 | -0.02306 | -1.7526
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.2792 | 76 | -0.02306 | -1.7526
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.149 | 105 | -0.02306 | -2.4213
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.2193 | 74 | -0.02306 | -1.7064
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.2193 | 74 | -0.02306 | -1.7064
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.059 | 102 | -0.02306 | -2.3521
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.028439 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.877 | 66 | -0.024611 | -1.6243
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.446 | 0 | -0.029728 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6652 | 0 | -0.029728 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0495 | 0 | -0.029728 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.3555 | 0 | -0.029728 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.0057 | 0 | -0.029728 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.0523 | 0 | -0.029728 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1661 | 0 | -0.029728 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4198 | 0 | -0.029728 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.1923 | 0 | -0.029728 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6325 | 0 | -0.029728 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4693 | 0 | -0.029728 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6792 | 0 | -0.029728 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5113 | 0 | -0.029728 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.3555 | 0 | -0.029728 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.2622 | 0 | -0.029728 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4022 | 0 | -0.029728 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.7725 | 0 | -0.029728 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8658 | 0 | -0.029728 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8658 | 0 | -0.029728 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.9881 | 0 | -0.029728 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.022003 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5622 | 0 | -0.031047 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.022003 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22003 | 0 | -0.031047 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.020946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.325 | 0 | -0.032104 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.020946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.325 | 0 | -0.032104 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.020946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.4926 | 0 | -0.032104 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.020946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.2936 | 0 | -0.032104 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.017319 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79841 | 0 | -0.035731 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.017194 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 11.1933 | 651 | -0.035856 | -23.3423
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.017194 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 9.6974 | 564 | -0.035856 | -20.2228
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.017194 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 10.3164 | 600 | -0.035856 | -21.5136
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.017164 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.7977 | 0 | -0.035886 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.017164 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.7977 | 0 | -0.035886 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.017164 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.2052 | 0 | -0.035886 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.016774 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55354 | 0 | -0.036276 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.016556 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.6655 | 161 | -0.036494 | -5.8755
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.016556 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.7483 | 166 | -0.036494 | -6.058
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.016556 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.1059 | 248 | -0.036494 | -9.0505
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.016556 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 9.0396 | 546 | -0.036494 | -19.9257
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.016556 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 10.6455 | 0 | -0.036494 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.016556 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21523 | 13 | -0.036494 | -0.47442
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.014698 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.47034 | 0 | -0.038352 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.014698 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.44094 | 0 | -0.038352 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.014698 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4742 | 0 | -0.038352 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.014698 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3654 | 0 | -0.038352 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.014698 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5095 | 0 | -0.038352 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.014698 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4992 | 0 | -0.038352 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.014688 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0399 | 0 | -0.038362 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.014688 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.97969 | 0 | -0.038362 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.014688 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77846 | 0 | -0.038362 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.2502 | 0 | -0.038362 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.2546 | 0 | -0.038362 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.237 | 0 | -0.038362 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.41 | 0 | -0.038362 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.5839 | 0 | -0.038362 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.014688 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58752 | 0 | -0.038362 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.013882 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.6941 | 50 | -0.039168 | -1.9584
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.013284 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.039766 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1434 | 0 | -0.040485 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1007 | 0 | -0.040485 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0932 | 0 | -0.040485 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68479 | 0 | -0.040485 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15329 | 0 | -0.040485 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.012284 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.79846 | 0 | -0.040766 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.012284 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.73704 | 0 | -0.040766 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.012284 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.79846 | 0 | -0.040766 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.012284 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.79846 | 0 | -0.040766 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.54542 | 46 | -0.041193 | -1.8949
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.54542 | 46 | -0.041193 | -1.8949
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.54542 | 46 | -0.041193 | -1.8949
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65214 | 55 | -0.041193 | -2.2656
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65214 | 55 | -0.041193 | -2.2656
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.64028 | 54 | -0.041193 | -2.2244
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.011761 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91736 | 0 | -0.041289 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.011761 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.94088 | 0 | -0.041289 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8967 | 0 | -0.041428 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8258 | 0 | -0.041428 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8305 | 0 | -0.041428 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8247 | 0 | -0.041428 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.1263 | 0 | -0.041428 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.011498 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.40243 | 0 | -0.041552 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.011374 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13649 | 12 | -0.041676 | -0.50011
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.011374 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.041676 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.011367 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.921 | 169 | -0.041683 | -7.0444
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.011357 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.8739 | 165 | -0.041693 | -6.8793
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.691 | 0 | -0.041701 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.73882 | 0 | -0.041701 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.011324 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.412 | 213 | -0.041726 | -8.8876
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1834 | 0 | -0.041729 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.011318 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72435 | 0 | -0.041732 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.011318 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7153 | 0 | -0.041732 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.011318 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.93487 | 0 | -0.041732 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.011318 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.833 | 0 | -0.041732 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.011314 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.5796 | 228 | -0.041736 | -9.5158
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.011309 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.0356 | 0 | -0.041741 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.011309 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7936 | 0 | -0.041741 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.011309 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7755 | 0 | -0.041741 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79044 | 0 | -0.041917 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80158 | 0 | -0.041917 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.43419 | 0 | -0.041917 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33399 | 0 | -0.041917 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.010849 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4755 | 0 | -0.042201 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.01083 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.45486 | 42 | -0.04222 | -1.7732
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.01083 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.45486 | 42 | -0.04222 | -1.7732
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.01083 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.41154 | 38 | -0.04222 | -1.6044
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.01083 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.41154 | 38 | -0.04222 | -1.6044
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.010755 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8606 | 0 | -0.042295 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.010755 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4519 | 0 | -0.042295 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.0711 | 104 | -0.042751 | -4.4461
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.0711 | 104 | -0.042751 | -4.4461
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.55615 | 54 | -0.042751 | -2.3086
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.54585 | 53 | -0.042751 | -2.2658
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.55615 | 54 | -0.042751 | -2.3086
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.58704 | 57 | -0.042751 | -2.4368
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.55615 | 54 | -0.042751 | -2.3086
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.55615 | 54 | -0.042751 | -2.3086
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.59734 | 58 | -0.042751 | -2.4796
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.59734 | 58 | -0.042751 | -2.4796
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.010136 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 7.45 | 735 | -0.042914 | -31.5418
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34068 | 0 | -0.04303 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34769 | 0 | -0.04303 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32765 | 0 | -0.04303 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.45992 | 0 | -0.04303 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17735 | 0 | -0.04303 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20441 | 0 | -0.04303 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1994 | 0 | -0.04303 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3507 | 0 | -0.04303 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18036 | 0 | -0.04303 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.85571 | 0 | -0.04303 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.483 | 0 | -0.04303 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.009865 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11838 | 12 | -0.043185 | -0.51822
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.009686 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.04843 | 0 | -0.043364 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.009686 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20341 | 0 | -0.043364 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.62926 | 0 | -0.043369 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.63895 | 0 | -0.043369 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67767 | 0 | -0.043369 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6099 | 0 | -0.043369 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60022 | 0 | -0.043369 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0068 | 0 | -0.043369 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57118 | 0 | -0.043369 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.009674 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.11609 | 12 | -0.043376 | -0.52051
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.009662 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 7.1789 | 743 | -0.043388 | -32.2373
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.009572 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5028 | 0 | -0.043478 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.00952 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6374 | 172 | -0.04353 | -7.4872
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.00952 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6374 | 172 | -0.04353 | -7.4872
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.00952 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6374 | 172 | -0.04353 | -7.4872
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4952 | 0 | -0.043866 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4823 | 0 | -0.043866 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4593 | 0 | -0.043866 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4723 | 0 | -0.043866 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.009063 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 3.6071 | 398 | -0.043987 | -17.5068
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.4961 | 56 | -0.044191 | -2.4747
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.52268 | 59 | -0.044191 | -2.6073
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.4961 | 56 | -0.044191 | -2.4747
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.4961 | 56 | -0.044191 | -2.4747
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.52268 | 59 | -0.044191 | -2.6073
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.4961 | 56 | -0.044191 | -2.4747
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.006885 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1911 | 0 | -0.046165 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.006885 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0741 | 0 | -0.046165 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.006885 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0603 | 0 | -0.046165 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.006885 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0603 | 0 | -0.046165 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.006885 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1154 | 0 | -0.046165 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.05305 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.05305 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.05305 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.05305 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.05305 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.05305 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.05305 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.05305 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.087362 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -49.709 | 569 | -0.14041 | -79.8944
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.087362 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -50.7573 | 581 | -0.14041 | -81.5794

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3668 RNDROCK1 - 3670 RNDRCKNE_ctg1 C:SANDOW__5-L_AUSTRO5_1Y C:L_AUSTRO5_1Y-SAND_TXU_59 [3429 - 7040 ckt1] and [7040 - 13429 ckt2] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.087362 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -49.709 | 0 | -0.14041 | 0 | 0 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.087362 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -50.7573 | 0 | -0.14041 | 0 | 0 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.05305 | 0 | 0 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.05305 | 0 | 0 | 0 | Weighted Shift Factors
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.05305 | 0 | 0 | 0 | South | 0.05305
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.05305 | 0 | 0 | 0 | North | -0.041314
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.05305 | 0 | 0 | 0 |  | 0.094364
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.05305 | 0 | 0 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.05305 | 0 | 0 | 0 | Line Rating | 247.95
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.05305 | 0 | 0 | 0 | Conc Gen | 342
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.006885 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1911 | 0 | -0.046165 | 0 | 0 | 0 | Weighted Imp. | 15.1133
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.006885 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0741 | 0 | -0.046165 | 0 | 0 | 0 | PTDF | 0.044191
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.006885 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0603 | 0 | -0.046165 | 0 | 0 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.006885 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0603 | 0 | -0.046165 | 0 | 0 | 0 | Concentration | 0.4683
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.006885 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1154 | 0 | -0.046165 | 0 | 0 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.4961 | 56 | -0.044191 | -2.4747 | 56 | 2.4747
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.52268 | 59 | -0.044191 | -2.6073 | 115 | 5.082
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.4961 | 56 | -0.044191 | -2.4747 | 171 | 7.5567
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.4961 | 56 | -0.044191 | -2.4747 | 227 | 10.0314
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.52268 | 59 | -0.044191 | -2.6073 | 286 | 12.6386
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.008859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.4961 | 56 | -0.044191 | -2.4747 | 342 | 15.1133
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.009063 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 3.6071 | 398 | -0.043987 | -17.5068
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4952 | 0 | -0.043866 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4823 | 0 | -0.043866 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4593 | 0 | -0.043866 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4723 | 0 | -0.043866 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.00952 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6374 | 172 | -0.04353 | -7.4872
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.00952 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6374 | 172 | -0.04353 | -7.4872
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.00952 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6374 | 172 | -0.04353 | -7.4872
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.009572 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5028 | 0 | -0.043478 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.009662 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 7.1789 | 743 | -0.043388 | -32.2373
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.009674 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.11609 | 0 | -0.043376 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.62926 | 0 | -0.043369 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.63895 | 0 | -0.043369 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67767 | 0 | -0.043369 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6099 | 0 | -0.043369 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60022 | 0 | -0.043369 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0068 | 0 | -0.043369 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.009681 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57118 | 0 | -0.043369 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.009686 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.04843 | 0 | -0.043364 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.009686 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20341 | 0 | -0.043364 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.009865 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11838 | 12 | -0.043185 | -0.51822
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34068 | 0 | -0.04303 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34769 | 0 | -0.04303 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32765 | 0 | -0.04303 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.45992 | 0 | -0.04303 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17735 | 0 | -0.04303 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20441 | 0 | -0.04303 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1994 | 0 | -0.04303 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3507 | 0 | -0.04303 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18036 | 0 | -0.04303 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.85571 | 0 | -0.04303 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.01002 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.483 | 0 | -0.04303 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.010136 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 7.45 | 735 | -0.042914 | -31.5418
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.0711 | 104 | -0.042751 | -4.4461
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.0711 | 104 | -0.042751 | -4.4461
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.55615 | 54 | -0.042751 | -2.3086
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.54585 | 53 | -0.042751 | -2.2658
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.55615 | 54 | -0.042751 | -2.3086
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.58704 | 57 | -0.042751 | -2.4368
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.55615 | 54 | -0.042751 | -2.3086
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.55615 | 54 | -0.042751 | -2.3086
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.59734 | 58 | -0.042751 | -2.4796
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.010299 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.59734 | 58 | -0.042751 | -2.4796
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.010755 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8606 | 0 | -0.042295 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.010755 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4519 | 0 | -0.042295 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.01083 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.45486 | 42 | -0.04222 | -1.7732
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.01083 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.45486 | 42 | -0.04222 | -1.7732
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.01083 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.41154 | 38 | -0.04222 | -1.6044
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.01083 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.41154 | 38 | -0.04222 | -1.6044
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.010849 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4755 | 0 | -0.042201 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79044 | 0 | -0.041917 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80158 | 0 | -0.041917 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.43419 | 0 | -0.041917 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.011133 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33399 | 0 | -0.041917 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.011309 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.0356 | 0 | -0.041741 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.011309 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7936 | 0 | -0.041741 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.011309 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7755 | 0 | -0.041741 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.011314 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.5796 | 228 | -0.041736 | -9.5158
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.011318 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72435 | 0 | -0.041732 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.011318 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7153 | 0 | -0.041732 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.011318 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.93487 | 0 | -0.041732 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.011318 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.833 | 0 | -0.041732 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.011321 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1834 | 0 | -0.041729 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.011324 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.412 | 213 | -0.041726 | -8.8876
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.691 | 0 | -0.041701 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.011349 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.73882 | 0 | -0.041701 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.011357 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.8739 | 165 | -0.041693 | -6.8793
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.011367 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.921 | 169 | -0.041683 | -7.0444
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.011374 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13649 | 12 | -0.041676 | -0.50011
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.011374 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.041676 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.011498 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.40243 | 0 | -0.041552 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8967 | 0 | -0.041428 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8258 | 0 | -0.041428 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8305 | 0 | -0.041428 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8247 | 0 | -0.041428 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.011622 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.1263 | 0 | -0.041428 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.011761 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.91736 | 0 | -0.041289 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.011761 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.94088 | 0 | -0.041289 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.54542 | 46 | -0.041193 | -1.8949
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.54542 | 46 | -0.041193 | -1.8949
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.54542 | 46 | -0.041193 | -1.8949
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65214 | 55 | -0.041193 | -2.2656
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65214 | 55 | -0.041193 | -2.2656
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.011857 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.64028 | 54 | -0.041193 | -2.2244
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.012284 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.79846 | 0 | -0.040766 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.012284 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.73704 | 0 | -0.040766 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.012284 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.79846 | 0 | -0.040766 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.012284 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.79846 | 0 | -0.040766 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1434 | 0 | -0.040485 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1007 | 0 | -0.040485 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0932 | 0 | -0.040485 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68479 | 0 | -0.040485 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.012565 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15329 | 0 | -0.040485 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.013284 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.039766 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.013882 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.6941 | 50 | -0.039168 | -1.9584
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.014688 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0399 | 0 | -0.038362 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.014688 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.97969 | 0 | -0.038362 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.014688 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77846 | 0 | -0.038362 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.2502 | 0 | -0.038362 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.2546 | 0 | -0.038362 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.237 | 0 | -0.038362 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.41 | 0 | -0.038362 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.014688 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.5839 | 0 | -0.038362 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.014688 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58752 | 0 | -0.038362 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.014698 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4742 | 0 | -0.038352 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.014698 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3654 | 0 | -0.038352 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.014698 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5095 | 0 | -0.038352 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.014698 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4992 | 0 | -0.038352 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.014698 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.47034 | 0 | -0.038352 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.014698 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.44094 | 0 | -0.038352 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.016556 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.6655 | 161 | -0.036494 | -5.8755
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.016556 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.7483 | 166 | -0.036494 | -6.058
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.016556 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.1059 | 248 | -0.036494 | -9.0505
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.016556 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 9.0396 | 546 | -0.036494 | -19.9257
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.016556 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 10.6455 | 0 | -0.036494 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.016556 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.21523 | 13 | -0.036494 | -0.47442
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.016774 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55354 | 0 | -0.036276 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.017164 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.7977 | 0 | -0.035886 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.017164 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.7977 | 0 | -0.035886 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.017164 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 4.2052 | 0 | -0.035886 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.017194 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 11.1933 | 0 | -0.035856 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.017194 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 9.6974 | 0 | -0.035856 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.017194 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 10.3164 | 0 | -0.035856 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.017319 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79841 | 0 | -0.035731 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.020946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.325 | 0 | -0.032104 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.020946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.325 | 0 | -0.032104 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.020946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.4926 | 0 | -0.032104 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.020946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.2936 | 0 | -0.032104 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.022003 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5622 | 0 | -0.031047 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.022003 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22003 | 0 | -0.031047 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.446 | 0 | -0.029728 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6652 | 0 | -0.029728 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.0495 | 0 | -0.029728 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.3555 | 0 | -0.029728 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.0057 | 0 | -0.029728 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.0523 | 0 | -0.029728 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1661 | 0 | -0.029728 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4198 | 0 | -0.029728 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.1923 | 0 | -0.029728 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6325 | 0 | -0.029728 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4693 | 0 | -0.029728 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6792 | 0 | -0.029728 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5113 | 0 | -0.029728 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.3555 | 0 | -0.029728 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.2622 | 0 | -0.029728 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.4022 | 0 | -0.029728 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.7725 | 0 | -0.029728 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8658 | 0 | -0.029728 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8658 | 0 | -0.029728 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.023322 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.9881 | 0 | -0.029728 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.028439 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 1.877 | 66 | -0.024611 | -1.6243
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.2792 | 76 | -0.02306 | -1.7526
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.2792 | 76 | -0.02306 | -1.7526
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.149 | 105 | -0.02306 | -2.4213
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.2193 | 74 | -0.02306 | -1.7064
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 2.2193 | 74 | -0.02306 | -1.7064
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.02999 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 3.059 | 102 | -0.02306 | -2.3521
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.030179 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.99591 | 0 | -0.022871 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.030179 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.75448 | 0 | -0.022871 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.030179 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.022871 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.030529 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 40.6952 | 0 | -0.022521 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.030529 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 40.5425 | 0 | -0.022521 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.060383 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.019069 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.060383 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.019069 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.06006 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.018746 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.06006 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -47.2672 | 787 | -0.018746 | -14.7529
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.057767 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -14.7306 | 255 | -0.016453 | -4.1954
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.057767 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.6073 | 149 | -0.016453 | -2.4515
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.057767 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -8.8384 | 153 | -0.016453 | -2.5173
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.037154 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.22292 | 0 | -0.015896 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.055886 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.3829 | 150 | -0.014572 | -2.1858
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.055886 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.4709 | 80 | -0.014572 | -1.1657
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.038776 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.014274 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.053277 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.79915 | 0 | -0.011963 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.053277 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.79915 | 0 | -0.011963 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.5291 | 0 | -0.008378 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.6184 | 0 | -0.008378 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.5291 | 0 | -0.008378 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.5738 | 0 | -0.008378 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.5023 | 0 | -0.008378 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.1168 | 0 | -0.008378 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.0549 | 0 | -0.008378 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2508 | 0 | -0.008378 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.9477 | 0 | -0.008378 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.044672 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.3057 | 0 | -0.008378 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.045069 | south | 7 | N | N | Nsouth | Nsouth | -1 | 2.1633 | 0 | -0.007981 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.298 | 0 | -0.006693 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3245 | 0 | -0.006693 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8079 | 0 | -0.006693 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.69535 | 0 | -0.006693 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3245 | 0 | -0.006693 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.69535 | 0 | -0.006693 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8079 | 0 | -0.006693 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.046357 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8079 | 0 | -0.006693 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.04656 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.37248 | 0 | -0.00649 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.046896 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.70344 | 0 | -0.006154 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.046896 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.0786 | 0 | -0.006154 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.047321 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0411 | 22 | -0.005729 | -0.12604
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.047321 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.52053 | 11 | -0.005729 | -0.063019
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.047321 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.52053 | 11 | -0.005729 | -0.063019
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.047752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2778 | 47.7 | -0.005298 | -0.25272
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.047752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.7811 | 37.3 | -0.005298 | -0.19762
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.047752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.1966 | 46 | -0.005298 | -0.24371
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.047752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 2.2921 | 48 | -0.005298 | -0.25431
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.047827 | south | 7 | N | N | Nsouth | Nsouth | -1 | 3.4914 | 0 | -0.005223 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -1 | 7.6214 | 0 | -0.004813 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -1 | 7.3803 | 0 | -0.004813 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -1 | 4.8237 | 0 | -0.004813 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -1 | 6.9944 | 0 | -0.004813 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -1 | 7.0908 | 0 | -0.004813 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.048237 | south | 8 | N | N | Nsouth | Nsouth | -1 | 6.1261 | 0 | -0.004813 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.048237 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.57884 | 0 | -0.004813 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.048364 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 6.9644 | 144 | -0.004686 | -0.67479
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.048364 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.0924 | 188 | -0.004686 | -0.88097
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.211 | 0 | -0.004608 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.211 | 0 | -0.004608 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.211 | 0 | -0.004608 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.77507 | 0 | -0.004608 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.211 | 0 | -0.004608 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.211 | 0 | -0.004608 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.211 | 0 | -0.004608 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.048442 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.72663 | 0 | -0.004608 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.048753 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 16.381 | 336 | -0.004297 | -1.4438
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.048753 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.7755 | 180 | -0.004297 | -0.77346
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.048759 | south | 8 | N | N | Nsouth | Nsouth | -1 | 7.231 | 0 | -0.004291 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.048759 | south | 8 | N | N | Nsouth | Nsouth | -1 | 7.2456 | 0 | -0.004291 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.048759 | south | 8 | N | N | Nsouth | Nsouth | -1 | 7.4601 | 0 | -0.004291 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.048768 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.7782 | 180 | -0.004282 | -0.77076
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.048867 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 16.3216 | 334 | -0.004183 | -1.3971
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.048867 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 16.6148 | 340 | -0.004183 | -1.4222
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.048867 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.7961 | 180 | -0.004183 | -0.75294
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.048867 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.7961 | 180 | -0.004183 | -0.75294
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.048884 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2221 | 0 | -0.004166 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.048884 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.2221 | 0 | -0.004166 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.048934 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8595 | 0 | -0.004116 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.048936 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.8596 | 0 | -0.004114 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.049179 | south | 7 | N | N | Nsouth | Nsouth | -1 | 1.4262 | 0 | -0.003871 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.6307 | 0 | -0.003787 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.0198 | 0 | -0.003787 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.872 | 0 | -0.003787 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.936 | 0 | -0.003787 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 4.6307 | 0 | -0.003787 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.7735 | 0 | -0.003787 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.1183 | 0 | -0.003787 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 1.0838 | 0 | -0.003787 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.2909 | 0 | -0.003787 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.4632 | 0 | -0.003787 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.7095 | 0 | -0.003787 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.049263 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 2.4632 | 0 | -0.003787 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.049298 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8733 | 38 | -0.003752 | -0.14258
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.049298 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.95145 | 19.3 | -0.003752 | -0.072414
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.049298 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.73947 | 15 | -0.003752 | -0.05628
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.049298 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.317 | 47 | -0.003752 | -0.17635
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.049298 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.003752 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.049398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.1133 | 144 | -0.003652 | -0.52589
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.049398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.1133 | 144 | -0.003652 | -0.52589
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.049398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.4471 | 171 | -0.003652 | -0.6245
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.049399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 10.2256 | 207 | -0.003651 | -0.75576
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.049399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 10.7048 | 216.7 | -0.003651 | -0.79118
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.049399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.9546 | 242 | -0.003651 | -0.88355
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.049504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.2523 | 146.5 | -0.003546 | -0.51949
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.049504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 7.3216 | 147.9 | -0.003546 | -0.52446
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.049504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.5642 | 173 | -0.003546 | -0.61346
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.050128 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.002922 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.050159 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.60191 | 0 | -0.002891 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.050159 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.55175 | 0 | -0.002891 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.050159 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.60191 | 0 | -0.002891 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.050786 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.002264 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.050815 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 31.9626 | 0 | -0.002235 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.051577 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.001473 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.042648 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.1649 | 168 | -0.0013337 | -0.22407
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.042648 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.8383 | 90 | -0.0013337 | -0.12004
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.042387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.4947 | 224 | -0.0010727 | -0.24029
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.042387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.5795 | 226 | -0.0010727 | -0.24244
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.042387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.986 | 212 | -0.0010727 | -0.22742
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.042387 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.9437 | 211 | -0.0010727 | -0.22635
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.042271 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.1474 | 216.4 | -0.00095673 | -0.20704
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.042271 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.1348 | 216.1 | -0.00095673 | -0.20675
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.052098 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.43762 | 8.4 | -0.00095202 | -0.007997
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.052152 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.00089802 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.052157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.2157 | 100 | -0.00089302 | -0.089302
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.052157 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 5.2157 | 100 | -0.00089302 | -0.089302
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.052157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.00089302 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.052157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.00089302 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.052157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.00089302 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.052157 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.00089302 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.052646 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2635 | 24 | -0.00040402 | -0.0096966
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.052646 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 1.2635 | 24 | -0.00040402 | -0.0096966
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.052646 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 1.2109 | 23 | -0.00040402 | -0.0092926
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.041367 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.8957 | 70 | -5.2734e-05 | -0.0036914
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.041367 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.8543 | 69 | -5.2734e-05 | -0.0036386
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.041367 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.8543 | 69 | -5.2734e-05 | -0.0036386
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.041367 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.813 | 68 | -5.2734e-05 | -0.0035859
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.040914 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -16.161 | 395 | 0.00040027 | 0.15811
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.040914 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -17.7976 | 435 | 0.00040027 | 0.17412
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.040873 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.0111 | 196 | 0.00044127 | 0.086488
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.040873 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.5369 | 111 | 0.00044127 | 0.048981
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.040858 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -17.7732 | 435 | 0.00045627 | 0.19848
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.040731 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -2.9734 | 73 | 0.00058327 | 0.042578
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.040731 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.847 | 119 | 0.00058327 | 0.069409
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.040731 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.3499 | 205 | 0.00058327 | 0.11957
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.040731 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -4.1546 | 102 | 0.00058327 | 0.059493
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.040731 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -3.9102 | 96 | 0.00058327 | 0.055994
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.040709 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00060527 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.040569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.8156 | 217.3 | 0.00074527 | 0.16195
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.040569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.3166 | 205 | 0.00074527 | 0.15278
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.040569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.051 | 272.4 | 0.00074527 | 0.20301
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.040463 | north | 3 | N | N | Nnorth | Nnorth | 1 | -46.8157 | 0 | 0.00085127 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.040463 | north | 3 | N | N | Nnorth | Nnorth | 1 | -46.8562 | 0 | 0.00085127 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.040423 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.72761 | 18 | 0.00089127 | 0.016043
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.040423 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.72761 | 18 | 0.00089127 | 0.016043
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.040423 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -1.5361 | 38 | 0.00089127 | 0.033868
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.040267 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0010473 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.040267 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0010473 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.040267 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0010473 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.040131 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.4079 | 0 | 0.0011833 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.040084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -11.5442 | 288 | 0.0012303 | 0.35432
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.040084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.8923 | 147 | 0.0012303 | 0.18085
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.040084 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.8923 | 147 | 0.0012303 | 0.18085
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.040016 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.7219 | 118 | 0.0012983 | 0.1532
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.040016 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -4.6018 | 115 | 0.0012983 | 0.1493
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.040016 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -22.2489 | 556 | 0.0012983 | 0.72184
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.039822 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.9201 | 224 | 0.0014923 | 0.33427
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.039815 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.3889 | 60 | 0.0014993 | 0.089956
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.039815 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.5083 | 63 | 0.0014993 | 0.094454
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.039756 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -4.4726 | 0 | 0.0015583 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.039696 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0016183 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.039684 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0016303 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.039535 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.5814 | 0 | 0.0017793 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.039535 | north | 5 | N | N | Nnorth | Nnorth | 1 | -1.5814 | 0 | 0.0017793 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.03953 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0017843 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.03953 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0017843 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.039506 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -6.716 | 170 | 0.0018083 | 0.30741
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.039506 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -20.5431 | 520 | 0.0018083 | 0.9403
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.03949 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.47388 | 0 | 0.0018243 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.03949 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.47388 | 0 | 0.0018243 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.039474 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -4.7369 | 0 | 0.0018403 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.039473 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -14.605 | 370 | 0.0018413 | 0.68127
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.5262 | 0 | 0.0018413 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.5657 | 0 | 0.0018413 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | 1 | -12.1972 | 0 | 0.0018413 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.6446 | 0 | 0.0018413 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.6841 | 0 | 0.0018413 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.039473 | north | 1 | N | N | Nnorth | Nnorth | 1 | -12.2366 | 0 | 0.0018413 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.039459 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.5784 | 40 | 0.0018553 | 0.074211
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3122 | 160 | 0.0018633 | 0.29812
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.1544 | 156 | 0.0018633 | 0.29067
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.7324 | 196 | 0.0018633 | 0.3652
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.1544 | 156 | 0.0018633 | 0.29067
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.1938 | 157 | 0.0018633 | 0.29253
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.039451 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.8113 | 198 | 0.0018633 | 0.36893
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.03944 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.1158 | 79 | 0.0018743 | 0.14807
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.03944 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -4.1806 | 106 | 0.0018743 | 0.19867
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.03944 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -5.7582 | 146 | 0.0018743 | 0.27364
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.03944 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -2.9974 | 76 | 0.0018743 | 0.14244
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.03943 | north | 8 | N | N | Nnorth | Nnorth | 1 | -2.9573 | 0 | 0.0018843 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.03943 | north | 8 | N | N | Nnorth | Nnorth | 1 | -3.1386 | 0 | 0.0018843 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.03943 | north | 8 | N | N | Nnorth | Nnorth | 1 | -3.4856 | 0 | 0.0018843 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.039415 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -21.9936 | 0 | 0.0018993 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.039415 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -22.8213 | 0 | 0.0018993 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.039415 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -31.8473 | 0 | 0.0018993 | 0
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.039415 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -15.293 | 388 | 0.0018993 | 0.73692
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.039415 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -20.2987 | 515 | 0.0018993 | 0.97812
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.039398 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.98495 | 25 | 0.0019163 | 0.047907
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.039398 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.6153 | 41 | 0.0019163 | 0.078567
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.039397 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.78794 | 20 | 0.0019173 | 0.038345
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.039322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.0217 | 204 | 0.0019923 | 0.40642
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.039322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -7.9037 | 201 | 0.0019923 | 0.40045
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.039322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.5159 | 242 | 0.0019923 | 0.48213
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3004 | 161 | 0.0021813 | 0.35118
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.4178 | 164 | 0.0021813 | 0.35773
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.4178 | 164 | 0.0021813 | 0.35773
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -16.2011 | 414 | 0.0021813 | 0.90304
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3395 | 162 | 0.0021813 | 0.35337
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3004 | 161 | 0.0021813 | 0.35118
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3787 | 163 | 0.0021813 | 0.35555
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.039133 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -16.0054 | 409 | 0.0021813 | 0.89214
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.055557 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 22.0006 | 0 | 0.002507 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.038466 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.76932 | 20 | 0.0028483 | 0.056965
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.038466 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.76932 | 20 | 0.0028483 | 0.056965
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.038466 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.76932 | 20 | 0.0028483 | 0.056965
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.038466 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.65392 | 17 | 0.0028483 | 0.048421
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.038451 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.3051 | 242 | 0.0028633 | 0.69291
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.038374 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -14.0449 | 366 | 0.0029403 | 1.0761
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.03802 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -29.8457 | 0 | 0.0032943 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.03802 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -30.2259 | 0 | 0.0032943 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.03802 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -29.6556 | 0 | 0.0032943 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.037855 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.6025 | 0 | 0.0034593 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.037855 | north | 1 | N | N | Nnorth | Nnorth | 1 | -4.9211 | 0 | 0.0034593 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.037855 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.489 | 0 | 0.0034593 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.037855 | north | 1 | N | N | Nnorth | Nnorth | 1 | -15.1041 | 0 | 0.0034593 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.056601 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.0188 | 0 | 0.003551 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.056601 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.0188 | 0 | 0.003551 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.056601 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.84901 | 0 | 0.003551 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.037709 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.0036053 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.037691 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.8845 | 0 | 0.0036233 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.037678 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -6.8574 | 182 | 0.0036363 | 0.6618
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.037678 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -18.2362 | 484 | 0.0036363 | 1.76
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.037401 | west | 4 | Y | N | Ywest | Nwest | 1 | -24.2994 | 0 | 0.0039133 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.037059 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.1147 | 0 | 0.0042553 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.057312 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.78517 | 0 | 0.004262 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.036644 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.648 | 0 | 0.0046703 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.036642 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.6568 | 0 | 0.0046723 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.058143 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.69772 | 0 | 0.005093 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.036047 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.1628 | 0 | 0.0052673 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.035915 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4411 | 151.5 | 0.0053993 | 0.81799
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.035915 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4699 | 152.3 | 0.0053993 | 0.82231
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.035915 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3749 | 177.5 | 0.0053993 | 0.95837
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.035832 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.3999 | 150.7 | 0.0054823 | 0.82618
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.035832 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.4106 | 151 | 0.0054823 | 0.82782
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.035832 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -6.3566 | 177.4 | 0.0054823 | 0.97255
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.058777 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 32.0922 | 0 | 0.005727 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.058777 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 44.0827 | 0 | 0.005727 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.035519 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.3278 | 0 | 0.0057953 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.035413 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -21.779 | 0 | 0.0059013 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.035413 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -20.7874 | 0 | 0.0059013 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.058961 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 3.4197 | 58 | 0.005911 | 0.34284
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.058961 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 5.2475 | 89 | 0.005911 | 0.52608
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.058961 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.5943 | 44 | 0.005911 | 0.26008
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.058961 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.5943 | 44 | 0.005911 | 0.26008
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.058961 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.5353 | 43 | 0.005911 | 0.25417
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.058961 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.6532 | 45 | 0.005911 | 0.26599
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.035394 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.3973 | 0 | 0.0059203 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.035394 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4773 | 0 | 0.0059203 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.035394 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8131 | 0 | 0.0059203 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.035394 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9726 | 0 | 0.0059203 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3257 | 0 | 0.0059623 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8003 | 0 | 0.0059623 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7725 | 0 | 0.0059623 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2069 | 0 | 0.0059623 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.712 | 0 | 0.0059623 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.035352 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8458 | 0 | 0.0059623 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.059099 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.1603 | 155 | 0.006049 | 0.93759
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.059099 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 10.0468 | 170 | 0.006049 | 1.0283
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.059099 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.1603 | 155 | 0.006049 | 0.93759
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.035202 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2803 | 0 | 0.0061123 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.035202 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.5554 | 0 | 0.0061123 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.035147 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.3934 | 0 | 0.0061673 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.035147 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.3934 | 0 | 0.0061673 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.059273 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 24.1241 | 407 | 0.006223 | 2.5328
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.035073 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9461 | 0 | 0.0062413 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.05933 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 12.4 | 209 | 0.00628 | 1.3125
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.05933 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 12.8153 | 216 | 0.00628 | 1.3565
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.05933 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.7292 | 46 | 0.00628 | 0.28888
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.05933 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.7885 | 47 | 0.00628 | 0.29516
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.05933 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.7292 | 46 | 0.00628 | 0.28888
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.05933 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.7292 | 46 | 0.00628 | 0.28888
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.059392 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 24.4695 | 412 | 0.006342 | 2.6129
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.059392 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 23.7568 | 400 | 0.006342 | 2.5368
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.034972 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4622 | 0 | 0.0063423 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.034972 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.1333 | 0 | 0.0063423 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.034972 | west | 7 | N | N | Nwest | Nwest | 1 | -0.8743 | 0 | 0.0063423 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.034972 | west | 7 | N | N | Nwest | Nwest | 1 | -1.5982 | 0 | 0.0063423 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.034972 | west | 7 | N | N | Nwest | Nwest | 1 | -1.5982 | 0 | 0.0063423 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.059403 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 25.1869 | 0 | 0.006353 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.059403 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 25.2463 | 0 | 0.006353 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.034961 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.9295 | 0 | 0.0063533 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.034961 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1953 | 0 | 0.0063533 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.03493 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2006 | 0 | 0.0063843 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.3026 | 66 | 0.0064263 | 0.42413
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4073 | 69 | 0.0064263 | 0.44341
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4073 | 69 | 0.0064263 | 0.44341
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.3375 | 67 | 0.0064263 | 0.43056
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.3375 | 67 | 0.0064263 | 0.43056
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.034888 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.2677 | 65 | 0.0064263 | 0.41771
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.059567 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.006517 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.059567 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.006517 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.059567 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.006517 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.034789 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.2184 | 0 | 0.0065253 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.034789 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.6536 | 0 | 0.0065253 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.034789 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9578 | 0 | 0.0065253 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.034789 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2408 | 0 | 0.0065253 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.0347 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.246 | 0 | 0.0066143 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.0347 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.246 | 0 | 0.0066143 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.03468 | west | 8 | N | N | Nwest | Nwest | 1 | -2.4276 | 0 | 0.0066343 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.03468 | west | 8 | N | N | Nwest | Nwest | 1 | -2.5455 | 0 | 0.0066343 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.03468 | west | 8 | N | N | Nwest | Nwest | 1 | -2.4415 | 0 | 0.0066343 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.034664 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.7994 | 0 | 0.0066503 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.034646 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1575 | 0 | 0.0066683 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.034646 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.0725 | 0 | 0.0066683 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.034646 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.8967 | 0 | 0.0066683 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.034592 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.151 | 0 | 0.0067223 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.034576 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.1491 | 0 | 0.0067383 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.059954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.9977 | 50 | 0.006904 | 0.3452
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.059954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.9977 | 50 | 0.006904 | 0.3452
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.059954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.9977 | 50 | 0.006904 | 0.3452
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.059954 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 2.9977 | 50 | 0.006904 | 0.3452
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.034359 | west | 8 | N | N | Nwest | Nwest | 1 | -0.88646 | 0 | 0.0069553 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.034317 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.3507 | 0 | 0.0069973 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.034234 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.4405 | 0 | 0.0070803 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.034225 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.985 | 0 | 0.0070893 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.034204 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.1306 | 0 | 0.0071103 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.3938 | 70 | 0.0071173 | 0.49821
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.3938 | 70 | 0.0071173 | 0.49821
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.1735 | 92.8 | 0.0071173 | 0.66048
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.7358 | 80 | 0.0071173 | 0.56938
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.7358 | 80 | 0.0071173 | 0.56938
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.034197 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.9327 | 115 | 0.0071173 | 0.81849
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.1184 | 208.2 | 0.0071243 | 1.4833
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.8584 | 142.1 | 0.0071243 | 1.0124
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.5268 | 132.4 | 0.0071243 | 0.94325
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.6498 | 136 | 0.0071243 | 0.9689
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.0259 | 147 | 0.0071243 | 1.0473
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.03419 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.1799 | 210 | 0.0071243 | 1.4961
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.034059 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8316 | 0 | 0.0072553 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.034059 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.0918 | 0 | 0.0072553 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.034059 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.335 | 0 | 0.0072553 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.034059 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.3057 | 0 | 0.0072553 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.033864 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.2235 | 0 | 0.0074503 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.033864 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.1615 | 0 | 0.0074503 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.033667 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.0164 | 0 | 0.0076473 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.9257 | 147 | 0.007669 | 1.1273
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.3792 | 138 | 0.007669 | 1.0583
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.5007 | 140 | 0.007669 | 1.0737
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.9257 | 147 | 0.007669 | 1.1273
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.0509 | 182 | 0.007669 | 1.3958
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.060719 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 12.0224 | 198 | 0.007669 | 1.5185
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.033549 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.1742 | 0 | 0.0077653 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.033549 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.0065 | 0 | 0.0077653 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.033525 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.6825 | 0 | 0.0077893 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.212 | 66 | 0.0077993 | 0.51475
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.1785 | 65 | 0.0077993 | 0.50695
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.2455 | 67 | 0.0077993 | 0.52255
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.2455 | 67 | 0.0077993 | 0.52255
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.033515 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.2455 | 67 | 0.0077993 | 0.52255
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.033515 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0077993 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.033515 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0077993 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.061624 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.1344 | 132 | 0.008574 | 1.1318
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.061624 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 8.2576 | 134 | 0.008574 | 1.1489
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.061624 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 19.9046 | 323 | 0.008574 | 2.7694
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.1105 | 0 | 0.009323 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 13.8468 | 0 | 0.009323 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 11.4766 | 0 | 0.009323 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 13.9716 | 0 | 0.009323 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 7.1729 | 0 | 0.009323 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.062444 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14987 | 0 | 0.009394 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.062444 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14987 | 0 | 0.009394 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.062882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 8.9292 | 142 | 0.009832 | 1.3961
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.062882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.1179 | 145 | 0.009832 | 1.4256
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.062882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 9.4952 | 151 | 0.009832 | 1.4846
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.062882 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 18.2358 | 290 | 0.009832 | 2.8513
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.062982 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.25193 | 0 | 0.009932 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.031024 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.14892 | 0 | 0.01029 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.063753 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 27.605 | 0 | 0.010703 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.063786 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 37.251 | 0 | 0.010736 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.063786 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 37.9527 | 0 | 0.010736 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.0639 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.15336 | 0 | 0.01085 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.0639 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.15336 | 0 | 0.01085 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.0639 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.17892 | 0 | 0.01085 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.029994 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3995 | 0 | 0.01132 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.029994 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3995 | 0 | 0.01132 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.029861 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -24.695 | 0 | 0.011453 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.029861 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -24.4562 | 0 | 0.011453 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.029716 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2287 | 0 | 0.011598 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.029716 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3773 | 0 | 0.011598 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.029716 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.1886 | 0 | 0.011598 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.029655 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3724 | 0 | 0.011659 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.029647 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3718 | 0 | 0.011667 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.029612 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4418 | 0 | 0.011702 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.029612 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4418 | 0 | 0.011702 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.065061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.5672 | 223.9 | 0.012011 | 2.6893
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.065061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.6387 | 225 | 0.012011 | 2.7025
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.065061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.6127 | 224.6 | 0.012011 | 2.6977
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.065061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.7493 | 226.7 | 0.012011 | 2.7229
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.028224 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2579 | 0 | 0.01309 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.027989 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.1412 | 0 | 0.013325 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.066408 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 28.0242 | 422 | 0.013358 | 5.6371
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.027756 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.3315 | 0 | 0.013558 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.067064 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.8778 | 0 | 0.014014 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.067064 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.9449 | 0 | 0.014014 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.025827 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -22.0821 | 0 | 0.015487 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.025827 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -22.0821 | 0 | 0.015487 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.025827 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.9335 | 0 | 0.015487 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.025827 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -3.9515 | 0 | 0.015487 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.070374 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.1191 | 158 | 0.017324 | 2.7372
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.070374 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.2598 | 160 | 0.017324 | 2.7718
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.070374 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 12.3155 | 175 | 0.017324 | 3.0317
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.07063 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.42378 | 0 | 0.01758 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.023201 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.1136 | 48 | 0.018113 | 0.86944
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.023201 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.0672 | 46 | 0.018113 | 0.83321
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.023201 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.4361 | 105 | 0.018113 | 1.9019
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.021425 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.019889 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.021425 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.019889 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.021425 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.36423 | 17 | 0.019889 | 0.33812
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.021425 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.019889 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.021425 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.019889 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.021257 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.68022 | 0 | 0.020057 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.073887 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.2678 | 152.5 | 0.020837 | 3.1776
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.073887 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 11.0461 | 149.5 | 0.020837 | 3.1151
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.073887 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 17.1861 | 232.6 | 0.020837 | 4.8467
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.020289 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.021025 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.074455 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3402 | 0 | 0.021405 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.074455 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.3402 | 0 | 0.021405 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.015554 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -7.2015 | 0 | 0.02576 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.013404 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.0106 | 0 | 0.02791 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.011613 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.7907 | 0 | 0.029701 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.011613 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.8116 | 0 | 0.029701 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.011613 | north | 1 | N | N | Nnorth | Nnorth | 1 | -1.8116 | 0 | 0.029701 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.011613 | north | 1 | N | N | Nnorth | Nnorth | 1 | -4.4129 | 0 | 0.029701 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.092702 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.2446 | 0 | 0.039652 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.092702 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.1519 | 0 | 0.039652 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.092702 | south | 5 | N | N | Nsouth | Nsouth | -1 | 3.2446 | 0 | 0.039652 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.041314 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.041314 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.7585 | 49 | 0.044062 | 2.159
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.4672 | 46 | 0.044062 | 2.0269
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.4672 | 46 | 0.044062 | 2.0269
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.5643 | 47 | 0.044062 | 2.0709
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.097112 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.9552 | 154 | 0.044062 | 6.7855
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.097112 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 14.3726 | 148 | 0.044062 | 6.5212
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.6614 | 48 | 0.044062 | 2.115
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.097112 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.6614 | 48 | 0.044062 | 2.115
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.099995 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.1998 | 42 | 0.046945 | 1.9717
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.099995 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.3998 | 44 | 0.046945 | 2.0656
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.099995 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.3998 | 44 | 0.046945 | 2.0656
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.099995 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 4.6998 | 47 | 0.046945 | 2.2064
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.10214 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 31.6631 | 310 | 0.049089 | 15.2176
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.10214 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 42.1834 | 413 | 0.049089 | 20.2737
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.10294 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.82354 | 0 | 0.049893 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.10294 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.82354 | 0 | 0.049893 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.034233 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.075547 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.062373 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 6.2373 | 0 | 0.10369 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 268
| 25 | 268
| 30 | 268
| 35 | 268
| 40 | 268
| 45 | 268
| 50 | 268
| 55 | 268
| 60 | 267
| 65 | 261
| 70 | 256
| 75 | 250
| 80 | 245
| 85 | 239
| 90 | 233
| 95 | 226
| 100 | 220
| 105 | 213
| 110 | 206
| 115 | 199
| Max | 268
| Min | 199
| Avg | 247.95