## test results
CRE test for: |  | TONKAWA_ - GRHAMSES 345kV [1048 - 1430] | [5 empty] | PASS
Line Rating: |  | 1340
Direcction |  | west | → | north |  | w-n
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | TONKAWA_ - GRHAMSES 345kV [1048 - 1430]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.020091
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.0037527
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.25825
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.010423
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | TONKAWA_ - GRHAMSES 345kV [1048 - 1430]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.021166
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.0033755
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.2789
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.010536
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | TONKAWA_ - GRHAMSES 345kV [1048 - 1430]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.016716
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.29899
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.0095557
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.28265
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.0066704
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.26878
PTDF tests
west | → | north | 0.81273 | 0.031872 | -0.031872 | -0.015519 | -0.81273 | 0.27941 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.27941 | -0.016716
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.12099
[6 empty] | Concentration |  | 0.43301 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.013316
[6 empty] | Concentration |  | 0.047656 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 204.2909
| Percent of line rating => | [6 empty] | 15.25% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 2.9087
[7 empty] | B1(N-S) | 0.0084948 | -0.040127 | -0.048622 | 0.0084948
[7 empty] | B2 (N-W) | 0.054908 | -0.81477 | -0.86967 | 0.054908
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.00882 | -0.018975 | -0.027795 | 0.00882
[7 empty] | B4 (S-W) | 0.046382 | -0.77577 | -0.82215 | 0.046382
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.00062189 | 0.020024 | 0.019402 | 0.00062189
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.011126 | 0.79294 | 0.78181 | 0.011126
[7 empty] | test | 0 | 0.81273 | 0.81273 | 0
[7 empty] | B1 | 1.045%
Deployment Error Percent | [6 empty] | B2 | 6.756%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 1.085%
[7 empty] | B4 | 5.707%
[7 empty] | B5 | 0.07652%
[7 empty] | B6 | 1.369%
[7 empty] | Max Abs Error | 6.756% | PASS

## Generation_sensitivity
Generator Sensitivities
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:COOKFIELD / LONGCREEK - GRAHAM8 [1430 - 1442] and [1430 - 1435] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:COOKFIELD / LONGCREEK - GRAHAM8 [1430 - 1442] and [1430 - 1435]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.012996 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -3.314
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.012996 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -1.9364
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.012655 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.18982
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.012655 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.18982
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.012996 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -1.9884
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.012252 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -1.8378
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.012252 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -0.98016
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.009415 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -0.68729
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.009415 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -1.1204
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.009415 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -1.9301
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.009415 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -0.96033
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.009415 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -0.90384
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.011139 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.13367
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.011139 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.13367
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.014641 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -2.4597
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.014641 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -1.3177
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.016756 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.30161
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.016756 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.30161
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.016756 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -0.63673
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.020209 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -5.8202
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.020209 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -2.9707
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.020209 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -2.9707
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.022542 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -2.536
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -0.022076 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -0.88304
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.022167 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -1.7512
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.022167 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -2.3497
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.022167 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -3.2364
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -0.022167 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -1.6847
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.02615 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -1.569
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.02615 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -1.6475
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.02208 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -0.4416
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.02208 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -0.552
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -0.02208 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -0.90528
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.014117 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -6.5362
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 18.8261
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 18.5409
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 19.1113
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 19.1113
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 19.1113
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.28524 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 32.5178
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.28524 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 146.9007
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 18.828
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 19.6838
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 19.6838
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 19.1133
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 19.1133
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 18.5427
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.29556 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 20.6888
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.29556 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 21.6937
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.29556 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 20.8071
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.2968 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 44.5204
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.2968 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 65.2967
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.26733 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 26.4656
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.26733 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 16.3071
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.2678 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 37.7591
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.26733 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 6.6832
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.26733 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 12.2169
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.26733 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 12.2169
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.2678 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 32.1354
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.27614 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 7.1245
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.28473 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 28.6158
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.27887 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 33.4646
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.28455 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 16.5038
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.28465 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 60.972
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.22877 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 34.315
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.26683 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 1.7611
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.26683 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 9.1522
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.22877 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 23.1055
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.27751 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 33.3011
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | -0.071097 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | -26.0215
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.021833 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -5.2836
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.23362 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 93.4468
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.23376 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 55.1667
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.23376 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 38.5699
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.040332 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -8.2277
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.040332 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -8.1067
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.040332 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -9.7603
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.020422 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.40844
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.020422 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.40844
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.020422 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.40844
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.020422 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -0.34717
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.017621 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -2.1145
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.019968 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 1.1981
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.022572 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -1.6929
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.022572 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -1.7967
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -0.022572 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -1.9954
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -3.62
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -3.5295
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -4.4345
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -3.5295
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -3.5521
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -4.4798
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.022811 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -3.8779
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -0.022811 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -11.8617
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022695 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -8.3971
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.022505 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -12.5578
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.022505 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -13.0304
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -0.022505 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -18.184
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.025877 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -2.8982
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.025877 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -2.5877
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.025877 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -9.7815
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.013615 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -2.9585
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.013615 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -2.7911
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.013615 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -3.7087
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.017429 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -13.4203
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.013956 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -0.97692
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.013956 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.96296
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.013956 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.96296
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.013956 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -0.94901
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.012429 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -14.3804
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.012429 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -14.3928
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.018901 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -4.2338
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.018901 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -4.2716
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.019813 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -4.2875
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.019813 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -4.2816
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.018901 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -4.007
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.018901 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -3.9881
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.022239 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -8.7844
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -0.022201 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -9.6574
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -0.022239 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -9.674
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.023489 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -3.2415
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.021191 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -2.5005
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.021191 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -2.437
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.021191 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -11.7822
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.021676 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -8.4103
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -0.021676 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -11.1631
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.020259 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -15.9033
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.020259 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -16.1059
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.020259 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -15.802
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.019881 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -3.6183
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.019881 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -9.6224
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.019172 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -4.2945
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.019913 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -0.99565
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.01993 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -0.83706
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.018032 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -11.0897
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.018032 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -10.5848
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.013949 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -7.4906
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.013949 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -10.9779
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.013328 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -0.9996
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.013328 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -2.9588
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.008509 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -4.8416
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.002434 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -0.50871
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.002434 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -0.52574
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.002294 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -0.93366
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.002434 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.11196
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.002434 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -0.1144
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.002434 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.11196
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.002434 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.11196
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.002513 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -1.0655
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.002513 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -1.068
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00187 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -0.10846
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00187 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -0.16643
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00187 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.08228
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00187 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.08228
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00187 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -0.08041
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00187 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -0.08415
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.002437 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -1.004
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.002437 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -0.9748
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.003048 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -1.6642
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.003048 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -2.286
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.002819 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -0.17196
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.002819 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -0.26781
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.002819 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -0.42567
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.002915 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.45182
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.002915 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -0.49555
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.002915 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.45182
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.004198 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.092356
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.004198 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.046178
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.004198 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.046178
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.004371 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -0.2085
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.004371 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -0.16304
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.004371 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -0.20107
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.004371 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -0.20981
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.000968 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.011616
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.000968 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.010648
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.006406 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.15374
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.006406 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.15374
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.006406 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.14734
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.002331 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -0.92308
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.008154 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -10.8693
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.008154 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -10.8285
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.003316 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -0.12601
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.003316 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.063999
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.003316 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.04974
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.003316 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -0.15585
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.26188 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 19.6413
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.21411 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 32.1159
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.20374 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 34.5339
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.16879 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 25.3183
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.27075 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 17.0571
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.067866 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 44.0925
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.022909 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.91636
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.022909 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.91636
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.004241 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 1.7897
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.005998 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -0.79174
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.005998 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -0.80373
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.005998 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -1.9374
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.00644 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -1.0175
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.00644 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -1.0304
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.00644 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -1.127
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.006477 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -3.7826
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.006477 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -3.8538
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.006475 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -2.8037
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.004191 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -0.93836
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.004191 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -0.94298
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.004191 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -0.9413
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.004191 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -0.9501
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.005179 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.041432
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.005179 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.041432
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.004468 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.080424
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.004468 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.080424
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.004468 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.06702
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.007118 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.097517
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.002043 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.036774
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.002043 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.036774
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.002943 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.103
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.002943 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -0.10006
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.002943 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.103
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.003673 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.10284
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.003673 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.10652
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.28476 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 9.9666
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.28476 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 8.5428
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.006291 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.31455
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.006291 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.31455
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.006291 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.31455
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.006291 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.31455
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.003686 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.022116
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.00395 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.00948
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.00395 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.00948
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.00395 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.01106
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.003569 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.014276
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.004325 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.01038
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.004325 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.01038
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.54463
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -0.51129
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -0.5187
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.54463
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -0.67431
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -0.73359
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.006006 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -0.91592
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.006006 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -0.8979
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.006006 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -1.397
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.00395 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -0.5609
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.00395 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -0.57275
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.00395 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -0.59645
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.00395 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -1.1455
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.066155 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 2.1831
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.066155 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 1.6539
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.000968 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.011616
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.004539 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -0.33135
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.40788
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -0.4182
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -0.13292
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.033229
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.40788
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -0.41304
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -0.40478
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -0.12907
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -0.2375
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.003677 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -2.3128
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.004449 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -0.64066
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.004449 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -0.83641
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.004313 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.051756
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.047167 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.283
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.00365 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -1.2264
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.003615 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -1.2074
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.003615 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -1.2291
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.00357 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -0.13566
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.003593 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.089825
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.003593 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.089825
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.003591 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -0.13646
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.003477 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -0.10083
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.003648 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -0.541
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.003648 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -0.54209
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.003648 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -0.55814
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -0.60498
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -0.58584
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -0.3829
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -0.5552
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -0.56286
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -0.48628
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.002822 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -0.41342
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.002822 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -0.41737
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.002822 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -0.48821
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.00313 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -0.64791
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.00313 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -0.67827
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.00313 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -0.75746
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.003131 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.45086
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.003131 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.45086
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.003131 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -0.5354
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.005392 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -1.6715
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.005392 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -2.2269
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.005576 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -0.23419
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.005576 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.24534
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.005576 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.24534
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.005576 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -0.26207
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.26122
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.24523
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.24523
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.25056
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.005331 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -0.82097
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.005331 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -0.78899
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.25589
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.25589
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 20.3927
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 20.3927
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 27.0349
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 23.3059
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 23.3059
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 33.5023
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 60.6412
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 41.3886
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 38.5634
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 39.6119
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 42.8158
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 61.1654
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.38029 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 79.4812
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.38029 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 48.1071
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.38029 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 94.693
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.38029 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 74.9177
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.2968 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 59.3606
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.2968 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 36.1803
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.28396 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 42.3094
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.27404 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 49.3276
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.27404 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 49.3276
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.27444 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 61.7492
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.29072 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 36.3399
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.29072 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 36.3399
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -3.1773
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -3.2
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -7.0128
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -3.2454
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -3.2681
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -7.0354
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.019373 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -3.7971
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.019373 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -2.1504
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -0.022991 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -3.4731
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -3.5378
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -3.5378
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -8.9308
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -3.4947
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -3.4731
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -3.5162
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -8.8229
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.021551 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -0.021551 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.020081 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -2.972
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.020081 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -2.6105
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.020081 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -2.9117
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.020081 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -8.0123
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.018334 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -2.7629
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.018334 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -2.7684
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.018334 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -3.2525
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.018397 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -2.7871
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.018397 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -2.8019
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.018397 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -3.2655
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.008509 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -4.9437
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.015678 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -13.4047
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.015678 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -13.4047
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.014101 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.45123
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.014071 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -0.67541
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.014071 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -0.64727
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.014111 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.16933
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.014111 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -0.71966
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.014111 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.23989
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.014111 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.31044
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.014111 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.35278
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.014071 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -1.4775
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.25745 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 21.6256
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.26155 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 20.9239
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.26133 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 39.2
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.26133 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 39.2
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010327 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.73115
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010327 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.68881
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010327 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.54733
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -1.5821
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -1.5852
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -1.5728
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.99139
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -2.5198
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.010327 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.41308
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.010325 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -1.0356
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.010325 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.95919
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.010325 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -1.0604
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.010325 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -1.0532
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.010325 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.3304
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.010325 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.30975
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009484 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -1.0527
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009484 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -1.0527
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009484 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -1.1286
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009484 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -1.0385
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.015678 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -2.3878
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.015678 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -2.3987
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.010829 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -1.4727
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.010046 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.33152
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.010827 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.45473
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.010827 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.45473
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.010827 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.41143
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.010827 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.41143
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.009332 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.66257
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.009332 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.09332
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.010026 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.6342
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.010026 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.6342
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.010026 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -2.4564
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.010639 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.69154
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.010639 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.63834
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.010639 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.69154
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.010639 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.69154
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.010761 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -1.6034
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.010761 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.70054
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.96487
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.92882
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.92246
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.57786
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.12936
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.010977 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -8.1559
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.010916 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -8.0233
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.010994 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.891
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.010994 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.891
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.010994 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -1.891
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.011333 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -1.9606
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.010841 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -1.8755
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.010841 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -1.4635
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.011037 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -1.7968
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.011037 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -1.7814
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.011037 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -1.7538
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.011037 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -2.9712
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.010765 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.68896
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.010765 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.68035
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.010765 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.88919
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.010765 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.7923
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -1.7498
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -1.6844
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -1.6887
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -1.6834
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -2.8842
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.010975 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.054875
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.010975 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.23048
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.013643 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -2.1038
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.013643 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -2.1283
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.013643 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -2.1283
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.013643 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -5.1843
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.011056 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -4.4003
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.49234
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.49234
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.49234
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.58866
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.58866
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.57796
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.016304 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -13.4834
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.016304 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -13.353
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.009973 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.45976
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.62996
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.62996
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -0.87035
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.61339
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.61339
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -0.84548
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.010766 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -1.9379
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.010766 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -1.7075
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.010766 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -1.6903
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.010742 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.37597
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.010509 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -4.8236
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.71344
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.72442
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.76832
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.69149
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.68051
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -1.1415
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.64758
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.011333 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -1.7679
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.011333 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -1.7453
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.011333 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -1.7453
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.011333 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -1.8359
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.01099 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -1.7254
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.010789 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.76602
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.010789 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.77681
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.010789 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.42077
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.010789 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.32367
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.010707 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.83515
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.010707 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.85656
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.010764 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.17438
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.01076 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -1.7754
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.010758 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -1.8181
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.010764 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -2.2927
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.010765 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -2.4544
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.010757 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.12908
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.010757 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.19363
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.010444 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.5222
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -1.1341
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -1.1341
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.58887
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.57796
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.58887
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.62159
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.58887
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.58887
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.63249
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.63249
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.010959 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.13151
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.6207
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.65396
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.6207
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.6207
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.65396
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.6207
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.008403 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -0.5546
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.010118 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -1.629
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.010118 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -1.6796
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.010118 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -2.5093
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.010118 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -5.5244
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.010118 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -6.5059
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.010022 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -6.5243
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.010022 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -5.6524
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.010022 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -6.0132
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.010118 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.13153
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.010976 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.13171
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.37165
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.37931
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.35744
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.50173
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.19348
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.22299
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.21753
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.38259
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.19676
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.93351
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -1.6178
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.56749
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -0.65352
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.41189
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.92445
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -0.78716
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -0.80546
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.45765
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.16475
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -0.86038
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -0.64071
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.57664
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -0.65902
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.59311
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.92445
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -0.88784
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -0.94276
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -0.69563
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.73224
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.73224
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -1.5652
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.068998
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.25093 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 19.196
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.26188 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 20.9507
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.26188 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 10.4754
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.26336 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 21.0689
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.2616 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 20.9278
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.25359 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 20.2873
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.25098 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 21.0822
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.26336 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 21.0689
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -0.19289
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.20724 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 24.8686
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.20724 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 48.2865
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.20724 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 35.2719
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -0.37562
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -0.31133
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -0.37901
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -0.19458
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -0.1692
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.168 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 10.0801
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.064415 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.21005 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.26998 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 1.2959
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 9.689
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 27.7751
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 34.8804
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 30.7464
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 27.1292
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 20.799
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.26217 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 39.3259
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.25514 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 28.7029
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.25514 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 38.143
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.25514 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 47.4555
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.25514 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 54.7269
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.003316 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.04275 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.002839 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -0.14456
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -0.22511
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -0.38206
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.31857
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -0.13895
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -0.12878
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.064391
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.31857
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -0.122
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -0.14573
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.074558
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.18513
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.071205
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.033229
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.071205
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.18513
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.18513
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -0.50157
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.16945
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -0.1864
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.16945
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003829 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.045948
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.004658 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.06987
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.004658 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.10713
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.005075 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -0.2436
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.004684 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.037472
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.003645 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -0.6561
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.00365 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -0.657
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.003615 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.6507
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.003615 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.6507
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.002835 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.2835
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.002835 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.2835
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.093825
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.093825
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.093825
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.060048
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.093825
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.093825
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.093825
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.056295
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.002835 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.002835 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 1.4175
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.002835 | south | #N/A | N | N | Nsouth | Nsouth | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 1.4175
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.002835 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.002611 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.066155 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.000805 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.002435 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [5 empty] | L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:COOKFIELD / LONGCREEK - GRAHAM8 [1430 - 1442] and [1430 - 1435] | [7 empty] | 204.2909
Number of Bus | Name of Bus | ID | Max MW | L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:COOKFIELD / LONGCREEK - GRAHAM8 [1430 - 1442] and [1430 - 1435] | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.012996 | north | 0.0070955 | -0.0092433 | -0.27124 | -0.0025729 | 0.0025729 | houston | Y | 0.0070955 | 1.1533
239 | BOSQUESW | 1 | 149 | -0.012996 | north | 0.0070955 | -0.0092433 | -0.27124 | -0.0025729 | 0.0025729 | houston | Y | 0.0070955 | 0.67387
244 | WHITNYDM | 1 | 15 | -0.012655 | north | 0.0074365 | -0.0089023 | -0.2709 | -0.0022319 | 0.0022319 | houston | Y | 0.0074365 | 0.07807
245 | WHITNYDM | 2 | 15 | -0.012655 | north | 0.0074365 | -0.0089023 | -0.2709 | -0.0022319 | 0.0022319 | houston | Y | 0.0074365 | 0.07807
247 | BOSQUESW | 2 | 153 | -0.012996 | north | 0.0070955 | -0.0092433 | -0.27124 | -0.0025729 | 0.0025729 | houston | Y | 0.0070955 | 0.69196
251 | BOSQUESW | 2 | 150 | -0.012252 | north | 0.0078395 | -0.0084993 | -0.2705 | -0.0018289 | 0.0018289 | houston | Y | 0.0078395 | 0.9016
253 | BOSQUESW | 2 | 80 | -0.012252 | north | 0.0078395 | -0.0084993 | -0.2705 | -0.0018289 | 0.0018289 | houston | Y | 0.0078395 | 0.48085
332 | RWMILLER | 1 | 73 | -0.009415 | north | 0.010676 | -0.0056623 | -0.26766 | 0.0010081 | 0.0010081 | houston | Y | 0.010676 | 0.70579
333 | RWMILLER | 2 | 119 | -0.009415 | north | 0.010676 | -0.0056623 | -0.26766 | 0.0010081 | 0.0010081 | houston | Y | 0.010676 | 1.1505
334 | RWMILLER | 3 | 205 | -0.009415 | north | 0.010676 | -0.0056623 | -0.26766 | 0.0010081 | 0.0010081 | houston | Y | 0.010676 | 1.982
335 | RWMILLER | 4 | 102 | -0.009415 | north | 0.010676 | -0.0056623 | -0.26766 | 0.0010081 | 0.0010081 | houston | Y | 0.010676 | 0.98617
336 | RWMILLER | 5 | 96 | -0.009415 | north | 0.010676 | -0.0056623 | -0.26766 | 0.0010081 | 0.0010081 | houston | Y | 0.010676 | 0.92816
344 | MRSSHPRD | 1 | 12 | -0.011139 | north | 0.0089525 | -0.0073863 | -0.26939 | -0.00071586 | 0.00071586 | houston | Y | 0.0089525 | 0.09884
345 | MRSSHPRD | 2 | 12 | -0.011139 | north | 0.0089525 | -0.0073863 | -0.26939 | -0.00071586 | 0.00071586 | houston | Y | 0.0089525 | 0.09884
366 | JNSNCNTY | 1 | 168 | -0.014641 | north | 0.0054505 | -0.010888 | -0.27289 | -0.0042179 | 0.0042179 | houston | Y | 0.0054505 | 0.20708
367 | JNSNCNTY | 2 | 90 | -0.014641 | north | 0.0054505 | -0.010888 | -0.27289 | -0.0042179 | 0.0042179 | houston | Y | 0.0054505 | 0.11094
503 | NTHTEXAS | 1 | 18 | -0.016756 | north | 0.0033355 | -0.013003 | -0.275 | -0.0063329 | 0.0033355 | North | N | 0.0033355 | 0
504 | NTHTEXAS | 2 | 18 | -0.016756 | north | 0.0033355 | -0.013003 | -0.275 | -0.0063329 | 0.0033355 | North | N | 0.0033355 | 0
505 | NTHTEXAS | 3 | 38 | -0.016756 | north | 0.0033355 | -0.013003 | -0.275 | -0.0063329 | 0.0033355 | North | N | 0.0033355 | 0
580 | JCKCNTY8 | 1 | 288 | -0.020209 | north | -0.0001175 | -0.016456 | -0.27846 | -0.0097859 | 0.0001175 | North | N | 0.0001175 | 0
581 | JCKCNTY8 | 2 | 147 | -0.020209 | north | -0.0001175 | -0.016456 | -0.27846 | -0.0097859 | 0.0001175 | North | N | 0.0001175 | 0
582 | JCKCNTY8 | 3 | 147 | -0.020209 | north | -0.0001175 | -0.016456 | -0.27846 | -0.0097859 | 0.0001175 | North | N | 0.0001175 | 0
728 | WOLFRIDG | 1 | 112.5 | -0.022542 | north | -0.0024505 | -0.018789 | -0.28079 | -0.012119 | 0.0024505 | North | N | 0.0024505 | 0
837 | NEWMAN_G | 1 | 40 | -0.022076 | north | -0.0019845 | -0.018323 | -0.28032 | -0.011653 | 0.0019845 | North | N | 0.0019845 | 0
842 | OLINGER_ | 1 | 79 | -0.022167 | north | -0.0020755 | -0.018414 | -0.28042 | -0.011744 | 0.0020755 | North | N | 0.0020755 | 0
843 | OLINGER_ | 1 | 106 | -0.022167 | north | -0.0020755 | -0.018414 | -0.28042 | -0.011744 | 0.0020755 | North | N | 0.0020755 | 0
844 | OLINGER_ | 1 | 146 | -0.022167 | north | -0.0020755 | -0.018414 | -0.28042 | -0.011744 | 0.0020755 | North | N | 0.0020755 | 0
845 | OLINGER_ | 1 | 76 | -0.022167 | north | -0.0020755 | -0.018414 | -0.28042 | -0.011744 | 0.0020755 | North | N | 0.0020755 | 0
923 | SPENCER_ | 1 | 60 | -0.02615 | north | -0.0060585 | -0.022397 | -0.2844 | -0.015727 | 0.0060585 | North | N | 0.0060585 | 0
924 | SPENCER_ | 1 | 63 | -0.02615 | north | -0.0060585 | -0.022397 | -0.2844 | -0.015727 | 0.0060585 | North | N | 0.0060585 | 0
948 | STEAM1 | 1 | 20 | -0.02208 | north | -0.0019885 | -0.018327 | -0.28033 | -0.011657 | 0.0019885 | North | N | 0.0019885 | 0
949 | STEAM2 | 1 | 25 | -0.02208 | north | -0.0019885 | -0.018327 | -0.28033 | -0.011657 | 0.0019885 | North | N | 0.0019885 | 0
950 | STEAM3 | 1 | 41 | -0.02208 | north | -0.0019885 | -0.018327 | -0.28033 | -0.011657 | 0.0019885 | North | N | 0.0019885 | 0
990 | GIBN_CRE | 1 | 463 | -0.014117 | north | 0.0059745 | -0.010364 | -0.27237 | -0.0036939 | 0.0036939 | houston | Y | 0.0059745 | 1.0559
1002 | PBCTAGE_ | A | 66 | 0.28524 | west | 0.30534 | 0.289 | 0.026996 | 0.29567 | 0.026996 | west | N | 0.026996 | 0
1003 | PBCTBGE_ | B | 65 | 0.28524 | west | 0.30534 | 0.289 | 0.026996 | 0.29567 | 0.026996 | west | N | 0.026996 | 0
1004 | PBCTCGE_ | C | 67 | 0.28524 | west | 0.30534 | 0.289 | 0.026996 | 0.29567 | 0.026996 | west | N | 0.026996 | 0
1005 | PBCTDGE_ | D | 67 | 0.28524 | west | 0.30534 | 0.289 | 0.026996 | 0.29567 | 0.026996 | west | N | 0.026996 | 0
1006 | PBCTEGE_ | E | 67 | 0.28524 | west | 0.30534 | 0.289 | 0.026996 | 0.29567 | 0.026996 | west | N | 0.026996 | 0
1007 | PB5GEN_6 | MB | 114 | 0.28524 | west | 0.30534 | 0.289 | 0.026996 | 0.29567 | 0.026996 | west | N | 0.026996 | 0
1008 | PB6GEN_7 | MB | 515 | 0.28524 | west | 0.30534 | 0.289 | 0.026996 | 0.29567 | 0.026996 | west | N | 0.026996 | 0
1039 | MRGNAG_1 | A | 66 | 0.28527 | west | 0.30536 | 0.28903 | 0.027025 | 0.2957 | 0.027025 | west | N | 0.027025 | 0
1040 | MRGNBG_2 | B | 69 | 0.28527 | west | 0.30536 | 0.28903 | 0.027025 | 0.2957 | 0.027025 | west | N | 0.027025 | 0
1041 | MRGNCG_3 | C | 69 | 0.28527 | west | 0.30536 | 0.28903 | 0.027025 | 0.2957 | 0.027025 | west | N | 0.027025 | 0
1042 | MRGNDG_4 | D | 67 | 0.28527 | west | 0.30536 | 0.28903 | 0.027025 | 0.2957 | 0.027025 | west | N | 0.027025 | 0
1043 | MRGNEG_5 | E | 67 | 0.28527 | west | 0.30536 | 0.28903 | 0.027025 | 0.2957 | 0.027025 | west | N | 0.027025 | 0
1044 | MRGNFG_6 | F | 65 | 0.28527 | west | 0.30536 | 0.28903 | 0.027025 | 0.2957 | 0.027025 | west | N | 0.027025 | 0
1045 | CALENG1G | 1 | 70 | 0.29556 | west | 0.31565 | 0.29931 | 0.037307 | 0.30598 | 0.037307 | west | N | 0.037307 | 0
1046 | CALENG2G | 2 | 73.4 | 0.29556 | west | 0.31565 | 0.29931 | 0.037307 | 0.30598 | 0.037307 | west | N | 0.037307 | 0
1047 | CALENG3G | 3 | 70.4 | 0.29556 | west | 0.31565 | 0.29931 | 0.037307 | 0.30598 | 0.037307 | west | N | 0.037307 | 0
1058 | LONGSHOR | 1 | 150 | 0.2968 | west | 0.31689 | 0.30056 | 0.038555 | 0.30723 | 0.038555 | west | N | 0.038555 | 0
1058 | LONGSHOR | 2 | 220 | 0.2968 | west | 0.31689 | 0.30056 | 0.038555 | 0.30723 | 0.038555 | west | N | 0.038555 | 0
1061 | CIELOGEN | 1 | 99 | 0.26733 | west | 0.28742 | 0.27108 | 0.0090809 | 0.27775 | 0.0090809 | west | N | 0.0090809 | 0
1062 | CIELOGEN | 1 | 61 | 0.26733 | west | 0.28742 | 0.27108 | 0.0090809 | 0.27775 | 0.0090809 | west | N | 0.0090809 | 0
1068 | SCURRYCW | 1 | 141 | 0.2678 | west | 0.28789 | 0.27155 | 0.0095469 | 0.27822 | 0.0095469 | west | N | 0.0095469 | 0
1069 | KINDERMG | 1 | 25 | 0.26733 | west | 0.28742 | 0.27108 | 0.0090809 | 0.27775 | 0.0090809 | west | N | 0.0090809 | 0
1070 | KINDERMG | 1 | 45.7 | 0.26733 | west | 0.28742 | 0.27108 | 0.0090809 | 0.27775 | 0.0090809 | west | N | 0.0090809 | 0
1071 | KINDERMG | 1 | 45.7 | 0.26733 | west | 0.28742 | 0.27108 | 0.0090809 | 0.27775 | 0.0090809 | west | N | 0.0090809 | 0
1073 | SCURRYCW | 2 | 120 | 0.2678 | west | 0.28789 | 0.27155 | 0.0095469 | 0.27822 | 0.0095469 | west | N | 0.0095469 | 0
1320 | BSP 1 | 1 | 25.8 | 0.27614 | west | 0.29623 | 0.2799 | 0.017895 | 0.28657 | 0.017895 | west | N | 0.017895 | 0
1326 | STANTONW | 1 | 100.5 | 0.28473 | west | 0.30483 | 0.28849 | 0.026486 | 0.29516 | 0.026486 | west | N | 0.026486 | 0
1327 | WILDHRSE | 1 | 120 | 0.27887 | west | 0.29896 | 0.28262 | 0.020624 | 0.2893 | 0.020624 | west | N | 0.020624 | 0
1328 | OCOTILLO | 1 | 58 | 0.28455 | west | 0.30464 | 0.2883 | 0.026301 | 0.29497 | 0.026301 | west | N | 0.026301 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.28465 | west | 0.30474 | 0.2884 | 0.026402 | 0.29507 | 0.026402 | west | N | 0.026402 | 0
1343 | TRENTIPP | 1 | 150 | 0.22877 | west | 0.24886 | 0.23252 | -0.029481 | 0.23919 | 0.029481 | west | N | 0.029481 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.26683 | west | 0.28692 | 0.27058 | 0.0085789 | 0.27725 | 0.0085789 | west | N | 0.0085789 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.26683 | west | 0.28692 | 0.27058 | 0.0085789 | 0.27725 | 0.0085789 | west | N | 0.0085789 | 0
1354 | AEPWIND_ | 1 | 101 | 0.22877 | west | 0.24886 | 0.23252 | -0.029481 | 0.23919 | 0.029481 | west | N | 0.029481 | 0
1360 | GUNSIGHT | 1 | 120 | 0.27751 | west | 0.2976 | 0.28126 | 0.019261 | 0.28793 | 0.019261 | west | N | 0.019261 | 0
1432 | GRHAMSES | 2 | 366 | -0.071097 | north | -0.051006 | -0.067344 | -0.32935 | -0.060674 | 0.051006 | North | N | 0.051006 | 0
1433 | GRHAMSES | 1 | 242 | -0.021833 | north | -0.0017415 | -0.01808 | -0.28008 | -0.01141 | 0.0017415 | North | N | 0.0017415 | 0
1437 | MESQUITW | 1 | 400 | 0.23362 | west | 0.25371 | 0.23737 | -0.024631 | 0.24404 | 0.024631 | west | N | 0.024631 | 0
1438 | MESQUITW | 1 | 236 | 0.23376 | west | 0.25385 | 0.23751 | -0.024491 | 0.24418 | 0.024491 | west | N | 0.024491 | 0
1442 | COKFIELD | 1 | 165 | 0.23376 | west | 0.25385 | 0.23751 | -0.024491 | 0.24418 | 0.024491 | west | N | 0.024491 | 0
1453 | WCPWRCO_ | 1 | 204 | -0.040332 | north | -0.020241 | -0.036579 | -0.29858 | -0.029909 | 0.020241 | North | N | 0.020241 | 0
1454 | WCPWRCO_ | 2 | 201 | -0.040332 | north | -0.020241 | -0.036579 | -0.29858 | -0.029909 | 0.020241 | North | N | 0.020241 | 0
1455 | WCPWRCO_ | 3 | 242 | -0.040332 | north | -0.020241 | -0.036579 | -0.29858 | -0.029909 | 0.020241 | North | N | 0.020241 | 0
1479 | WFCOGEN_ | 1 | 20 | -0.020422 | west | -0.0003305 | -0.016669 | -0.27867 | -0.0099989 | 0.0003305 | North | Y | 0.27867 | 5.5668
1479 | WFCOGEN_ | 2 | 20 | -0.020422 | west | -0.0003305 | -0.016669 | -0.27867 | -0.0099989 | 0.0003305 | North | Y | 0.27867 | 5.5668
1482 | WFCOGEN_ | 1 | 20 | -0.020422 | west | -0.0003305 | -0.016669 | -0.27867 | -0.0099989 | 0.0003305 | North | Y | 0.27867 | 5.5668
1482 | WFCOGEN_ | 2 | 17 | -0.020422 | west | -0.0003305 | -0.016669 | -0.27867 | -0.0099989 | 0.0003305 | North | Y | 0.27867 | 4.7318
1600 | BARTNWND | 1 | 120 | -0.017621 | north | 0.0024705 | -0.013868 | -0.27587 | -0.0071979 | 0.0024705 | North | N | 0.0024705 | 0
1643 | SLSTR1PP | 1 | 60 | 0.019968 | north | 0.040059 | 0.023721 | -0.23828 | 0.030391 | 0.023721 | south | Y | 0.040059 | 0.98033
1675 | PEC_1G | 1 | 75 | -0.022572 | north | -0.0024805 | -0.018819 | -0.28082 | -0.012149 | 0.0024805 | North | N | 0.0024805 | 0
1676 | PEC_2G | 2 | 79.6 | -0.022572 | north | -0.0024805 | -0.018819 | -0.28082 | -0.012149 | 0.0024805 | North | N | 0.0024805 | 0
1677 | PEC_3G | 3 | 88.4 | -0.022572 | north | -0.0024805 | -0.018819 | -0.28082 | -0.012149 | 0.0024805 | North | N | 0.0024805 | 0
1678 | LAMARPWR | 1 | 160 | -0.022625 | north | -0.0025335 | -0.018872 | -0.28087 | -0.012202 | 0.0025335 | North | N | 0.0025335 | 0
1679 | LAMARPWR | 2 | 156 | -0.022625 | north | -0.0025335 | -0.018872 | -0.28087 | -0.012202 | 0.0025335 | North | N | 0.0025335 | 0
1680 | LAMARPWR | 3 | 196 | -0.022625 | north | -0.0025335 | -0.018872 | -0.28087 | -0.012202 | 0.0025335 | North | N | 0.0025335 | 0
1681 | LAMARPWR | 4 | 156 | -0.022625 | north | -0.0025335 | -0.018872 | -0.28087 | -0.012202 | 0.0025335 | North | N | 0.0025335 | 0
1682 | LAMARPWR | 5 | 157 | -0.022625 | north | -0.0025335 | -0.018872 | -0.28087 | -0.012202 | 0.0025335 | North | N | 0.0025335 | 0
1683 | LAMARPWR | 6 | 198 | -0.022625 | north | -0.0025335 | -0.018872 | -0.28087 | -0.012202 | 0.0025335 | North | N | 0.0025335 | 0
1687 | VALLEY_1 | 1 | 170 | -0.022811 | north | -0.0027195 | -0.019058 | -0.28106 | -0.012388 | 0.0027195 | North | N | 0.0027195 | 0
1688 | VALLEY_2 | 2 | 520 | -0.022811 | north | -0.0027195 | -0.019058 | -0.28106 | -0.012388 | 0.0027195 | North | N | 0.0027195 | 0
1689 | VALLEY_3 | 3 | 370 | -0.022695 | north | -0.0026035 | -0.018942 | -0.28094 | -0.012272 | 0.0026035 | North | N | 0.0026035 | 0
1701 | MOSES_1G | 1 | 558 | -0.022505 | north | -0.0024135 | -0.018752 | -0.28075 | -0.012082 | 0.0024135 | North | N | 0.0024135 | 0
1702 | MOSES_2G | 2 | 579 | -0.022505 | north | -0.0024135 | -0.018752 | -0.28075 | -0.012082 | 0.0024135 | North | N | 0.0024135 | 0
1703 | MOSES_3G | 3 | 808 | -0.022505 | north | -0.0024135 | -0.018752 | -0.28075 | -0.012082 | 0.0024135 | North | N | 0.0024135 | 0
1861 | EAGLEMNT | MB | 112 | -0.025877 | north | -0.0057855 | -0.022124 | -0.28413 | -0.015454 | 0.0057855 | North | N | 0.0057855 | 0
1862 | EAGLEMNT | MB | 100 | -0.025877 | north | -0.0057855 | -0.022124 | -0.28413 | -0.015454 | 0.0057855 | North | N | 0.0057855 | 0
1863 | EAGLEMNT | MB | 378 | -0.025877 | north | -0.0057855 | -0.022124 | -0.28413 | -0.015454 | 0.0057855 | North | N | 0.0057855 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.013615 | north | 0.0064765 | -0.0098623 | -0.27186 | -0.0031919 | 0.0031919 | houston | Y | 0.0064765 | 0.71375
1878 | WLFHOLW_ | 2 | 205 | -0.013615 | north | 0.0064765 | -0.0098623 | -0.27186 | -0.0031919 | 0.0031919 | houston | Y | 0.0064765 | 0.67335
1879 | WLFHOLW_ | 3 | 272.4 | -0.013615 | north | 0.0064765 | -0.0098623 | -0.27186 | -0.0031919 | 0.0031919 | houston | Y | 0.0064765 | 0.89473
1889 | DECRDOVA | MB | 770 | -0.017429 | north | 0.0026625 | -0.013676 | -0.27568 | -0.0070059 | 0.0026625 | North | N | 0.0026625 | 0
1892 | DECRDOVA | A | 70 | -0.013956 | north | 0.0061355 | -0.010203 | -0.2722 | -0.0035329 | 0.0035329 | houston | Y | 0.0061355 | 0.18218
1893 | DECRDOVA | B | 69 | -0.013956 | north | 0.0061355 | -0.010203 | -0.2722 | -0.0035329 | 0.0035329 | houston | Y | 0.0061355 | 0.17958
1894 | DECRDOVA | C | 69 | -0.013956 | north | 0.0061355 | -0.010203 | -0.2722 | -0.0035329 | 0.0035329 | houston | Y | 0.0061355 | 0.17958
1895 | DECRDOVA | D | 68 | -0.013956 | north | 0.0061355 | -0.010203 | -0.2722 | -0.0035329 | 0.0035329 | houston | Y | 0.0061355 | 0.17698
1898 | COMCHEPK | 1 | 1157 | -0.012429 | north | 0.0076625 | -0.0086763 | -0.27068 | -0.0020059 | 0.0020059 | houston | Y | 0.0076625 | 6.5447
1899 | COMCHEPK | 2 | 1158 | -0.012429 | north | 0.0076625 | -0.0086763 | -0.27068 | -0.0020059 | 0.0020059 | houston | Y | 0.0076625 | 6.5504
1937 | MDLTHELP | 5 | 224 | -0.018901 | north | 0.0011905 | -0.015148 | -0.27715 | -0.0084779 | 0.0011905 | North | N | 0.0011905 | 0
1938 | MDLTHELP | 6 | 226 | -0.018901 | north | 0.0011905 | -0.015148 | -0.27715 | -0.0084779 | 0.0011905 | North | N | 0.0011905 | 0
1941 | MDLTHELP | 1 | 216.4 | -0.019813 | north | 0.0002785 | -0.01606 | -0.27806 | -0.0093899 | 0.0002785 | North | N | 0.0002785 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.019813 | north | 0.0002785 | -0.01606 | -0.27806 | -0.0093899 | 0.0002785 | North | N | 0.0002785 | 0
1943 | MDLTHELP | 3 | 212 | -0.018901 | north | 0.0011905 | -0.015148 | -0.27715 | -0.0084779 | 0.0011905 | North | N | 0.0011905 | 0
1944 | MDLTHELP | 4 | 211 | -0.018901 | north | 0.0011905 | -0.015148 | -0.27715 | -0.0084779 | 0.0011905 | North | N | 0.0011905 | 0
1947 | HANDLEY_ | 3 | 395 | -0.022239 | north | -0.0021475 | -0.018486 | -0.28049 | -0.011816 | 0.0021475 | North | N | 0.0021475 | 0
1948 | HANDLEY_ | 4 | 435 | -0.022201 | north | -0.0021095 | -0.018448 | -0.28045 | -0.011778 | 0.0021095 | North | N | 0.0021095 | 0
1949 | HANDLEY_ | 5 | 435 | -0.022239 | north | -0.0021475 | -0.018486 | -0.28049 | -0.011816 | 0.0021475 | North | N | 0.0021475 | 0
2371 | COLLIN_1 | MB | 138 | -0.023489 | north | -0.0033975 | -0.019736 | -0.28174 | -0.013066 | 0.0033975 | North | N | 0.0033975 | 0
2413 | MTCK6_G | 6 | 118 | -0.021191 | north | -0.0010995 | -0.017438 | -0.27944 | -0.010768 | 0.0010995 | North | N | 0.0010995 | 0
2414 | MTCK7_G | 7 | 115 | -0.021191 | north | -0.0010995 | -0.017438 | -0.27944 | -0.010768 | 0.0010995 | North | N | 0.0010995 | 0
2417 | MTCK8_G | 8 | 556 | -0.021191 | north | -0.0010995 | -0.017438 | -0.27944 | -0.010768 | 0.0010995 | North | N | 0.0010995 | 0
2451 | LKHB1_G | 1 | 388 | -0.021676 | north | -0.0015845 | -0.017923 | -0.27992 | -0.011253 | 0.0015845 | North | N | 0.0015845 | 0
2452 | LKHB2_G | 2 | 515 | -0.021676 | north | -0.0015845 | -0.017923 | -0.27992 | -0.011253 | 0.0015845 | North | N | 0.0015845 | 0
3097 | MARTLAKE | 1 | 785 | -0.020259 | north | -0.0001675 | -0.016506 | -0.27851 | -0.0098359 | 0.0001675 | North | N | 0.0001675 | 0
3098 | MARTLAKE | 2 | 795 | -0.020259 | north | -0.0001675 | -0.016506 | -0.27851 | -0.0098359 | 0.0001675 | North | N | 0.0001675 | 0
3099 | MARTLAKE | 3 | 780 | -0.020259 | north | -0.0001675 | -0.016506 | -0.27851 | -0.0098359 | 0.0001675 | North | N | 0.0001675 | 0
3107 | STRYKER_ | 1 | 182 | -0.019881 | north | 0.0002105 | -0.016128 | -0.27813 | -0.0094579 | 0.0002105 | North | N | 0.0002105 | 0
3108 | STRYKER_ | 2 | 484 | -0.019881 | north | 0.0002105 | -0.016128 | -0.27813 | -0.0094579 | 0.0002105 | North | N | 0.0002105 | 0
3126 | TRINIDAD | 1 | 224 | -0.019172 | north | 0.0009195 | -0.015419 | -0.27742 | -0.0087489 | 0.0009195 | North | N | 0.0009195 | 0
3309 | ASPN_G | 1 | 50 | -0.019913 | north | 0.0001785 | -0.01616 | -0.27816 | -0.0094899 | 0.0001785 | North | N | 0.0001785 | 0
3348 | CHAMPION | MB | 42 | -0.01993 | north | 0.0001615 | -0.016177 | -0.27818 | -0.0095069 | 0.0001615 | North | N | 0.0001615 | 0
3381 | BBRN_1G | 1 | 615 | -0.018032 | north | 0.0020595 | -0.014279 | -0.27628 | -0.0076089 | 0.0020595 | North | N | 0.0020595 | 0
3382 | BBRN_2G | 2 | 587 | -0.018032 | north | 0.0020595 | -0.014279 | -0.27628 | -0.0076089 | 0.0020595 | North | N | 0.0020595 | 0
3403 | THOUSE_1 | MB | 537 | -0.013949 | north | 0.0061425 | -0.010196 | -0.2722 | -0.0035259 | 0.0035259 | houston | Y | 0.0061425 | 1.4051
3404 | THOUSE_2 | 2 | 787 | -0.013949 | north | 0.0061425 | -0.010196 | -0.2722 | -0.0035259 | 0.0035259 | houston | Y | 0.0061425 | 2.0593
3416 | LAKE_CRK | MB | 75 | -0.013328 | north | 0.0067635 | -0.0095753 | -0.27158 | -0.0029049 | 0.0029049 | houston | Y | 0.0067635 | 0.2894
3417 | LAKE_CRK | MB | 222 | -0.013328 | north | 0.0067635 | -0.0095753 | -0.27158 | -0.0029049 | 0.0029049 | houston | Y | 0.0067635 | 0.85662
3432 | SANDOW_4 | 4 | 569 | -0.008509 | south | 0.011582 | -0.0047563 | -0.26676 | 0.0019141 | 0.0019141 | houston | Y | 0.0047563 | 1.6172
5026 | BRAUNIG_ | 1 | 209 | -0.002434 | south | 0.017657 | 0.0013187 | -0.26068 | 0.0079891 | 0.0013187 | south | N | 0.0013187 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.002434 | south | 0.017657 | 0.0013187 | -0.26068 | 0.0079891 | 0.0013187 | south | N | 0.0013187 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.002294 | south | 0.017797 | 0.0014587 | -0.26054 | 0.0081291 | 0.0014587 | south | N | 0.0014587 | 0
5031 | BRA_VHBC | 1 | 46 | -0.002434 | south | 0.017657 | 0.0013187 | -0.26068 | 0.0079891 | 0.0013187 | south | N | 0.0013187 | 0
5032 | BRA_VHBC | 2 | 47 | -0.002434 | south | 0.017657 | 0.0013187 | -0.26068 | 0.0079891 | 0.0013187 | south | N | 0.0013187 | 0
5033 | BRA_VHBC | 3 | 46 | -0.002434 | south | 0.017657 | 0.0013187 | -0.26068 | 0.0079891 | 0.0013187 | south | N | 0.0013187 | 0
5034 | BRA_VHBC | 4 | 46 | -0.002434 | south | 0.017657 | 0.0013187 | -0.26068 | 0.0079891 | 0.0013187 | south | N | 0.0013187 | 0
5111 | CALAVER_ | 1 | 424 | -0.002513 | south | 0.017578 | 0.0012397 | -0.26076 | 0.0079101 | 0.0012397 | south | N | 0.0012397 | 0
5112 | CALAVER_ | 2 | 425 | -0.002513 | south | 0.017578 | 0.0012397 | -0.26076 | 0.0079101 | 0.0012397 | south | N | 0.0012397 | 0
5264 | LEON_LCP | 3 | 58 | -0.00187 | south | 0.018221 | 0.0018827 | -0.26012 | 0.0085531 | 0.0018827 | south | N | 0.0018827 | 0
5265 | LEON_LCP | 4 | 89 | -0.00187 | south | 0.018221 | 0.0018827 | -0.26012 | 0.0085531 | 0.0018827 | south | N | 0.0018827 | 0
5266 | LEON_LCP | 1 | 44 | -0.00187 | south | 0.018221 | 0.0018827 | -0.26012 | 0.0085531 | 0.0018827 | south | N | 0.0018827 | 0
5267 | LEON_LCP | 2 | 44 | -0.00187 | south | 0.018221 | 0.0018827 | -0.26012 | 0.0085531 | 0.0018827 | south | N | 0.0018827 | 0
5268 | LEON_LCP | 3 | 43 | -0.00187 | south | 0.018221 | 0.0018827 | -0.26012 | 0.0085531 | 0.0018827 | south | N | 0.0018827 | 0
5269 | LEON_LCP | 4 | 45 | -0.00187 | south | 0.018221 | 0.0018827 | -0.26012 | 0.0085531 | 0.0018827 | south | N | 0.0018827 | 0
5396 | CALAVER_ | 1 | 412 | -0.002437 | south | 0.017654 | 0.0013157 | -0.26069 | 0.0079861 | 0.0013157 | south | N | 0.0013157 | 0
5397 | CALAVER_ | 2 | 400 | -0.002437 | south | 0.017654 | 0.0013157 | -0.26069 | 0.0079861 | 0.0013157 | south | N | 0.0013157 | 0
5401 | CALAVER_ | 1 | 546 | -0.003048 | south | 0.017043 | 0.00070472 | -0.2613 | 0.0073751 | 0.00070472 | south | N | 0.00070472 | 0
5402 | CALAVER_ | 2 | 750 | -0.003048 | south | 0.017043 | 0.00070472 | -0.2613 | 0.0073751 | 0.00070472 | south | N | 0.00070472 | 0
5436 | TUTTL_WB | MB | 61 | -0.002819 | south | 0.017272 | 0.00093372 | -0.26107 | 0.0076041 | 0.00093372 | south | N | 0.00093372 | 0
5438 | TUTTL_WB | MB | 95 | -0.002819 | south | 0.017272 | 0.00093372 | -0.26107 | 0.0076041 | 0.00093372 | south | N | 0.00093372 | 0
5439 | TUTTL_WB | MB | 151 | -0.002819 | south | 0.017272 | 0.00093372 | -0.26107 | 0.0076041 | 0.00093372 | south | N | 0.00093372 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.002915 | south | 0.017176 | 0.00083772 | -0.26116 | 0.0075081 | 0.00083772 | south | N | 0.00083772 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.002915 | south | 0.017176 | 0.00083772 | -0.26116 | 0.0075081 | 0.00083772 | south | N | 0.00083772 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.002915 | south | 0.017176 | 0.00083772 | -0.26116 | 0.0075081 | 0.00083772 | south | N | 0.00083772 | 0
5503 | RAYBURNG | 1 | 22 | -0.004198 | south | 0.015893 | -0.00044528 | -0.26245 | 0.0062251 | 0.00044528 | south | N | 0.00044528 | 0
5505 | RAYBURNG | 1 | 11 | -0.004198 | south | 0.015893 | -0.00044528 | -0.26245 | 0.0062251 | 0.00044528 | south | N | 0.00044528 | 0
5506 | RAYBURNG | 1 | 11 | -0.004198 | south | 0.015893 | -0.00044528 | -0.26245 | 0.0062251 | 0.00044528 | south | N | 0.00044528 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.004371 | south | 0.01572 | -0.00061828 | -0.26262 | 0.0060521 | 0.00061828 | south | N | 0.00061828 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.004371 | south | 0.01572 | -0.00061828 | -0.26262 | 0.0060521 | 0.00061828 | south | N | 0.00061828 | 0
5511 | RAYBURNC | 1 | 46 | -0.004371 | south | 0.01572 | -0.00061828 | -0.26262 | 0.0060521 | 0.00061828 | south | N | 0.00061828 | 0
5512 | RAYBURNC | 1 | 48 | -0.004371 | south | 0.01572 | -0.00061828 | -0.26262 | 0.0060521 | 0.00061828 | south | N | 0.00061828 | 0
5728 | FALCONHY | 2 | 12 | -0.000968 | south | 0.019123 | 0.0027847 | -0.25922 | 0.0094551 | 0.0027847 | south | N | 0.0027847 | 0
5729 | FALCONHY | 3 | 11 | -0.000968 | south | 0.019123 | 0.0027847 | -0.25922 | 0.0094551 | 0.0027847 | south | N | 0.0027847 | 0
5890 | PEARSALL | 1 | 24 | 0.006406 | south | 0.026497 | 0.010159 | -0.25184 | 0.016829 | 0.010159 | south | N | 0.010159 | 0
5891 | PEARSALL | 1 | 24 | 0.006406 | south | 0.026497 | 0.010159 | -0.25184 | 0.016829 | 0.010159 | south | N | 0.010159 | 0
5892 | PEARSALL | 1 | 23 | 0.006406 | south | 0.026497 | 0.010159 | -0.25184 | 0.016829 | 0.010159 | south | N | 0.010159 | 0
5903 | SANMIGUE | 1 | 396 | -0.002331 | south | 0.01776 | 0.0014217 | -0.26058 | 0.0080921 | 0.0014217 | south | N | 0.0014217 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.008154 | houston | 0.011937 | -0.0044013 | -0.2664 | 0.0022691 | 0.0022691 | houston | N | 0.0022691 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.008154 | houston | 0.011937 | -0.0044013 | -0.2664 | 0.0022691 | 0.0022691 | houston | N | 0.0022691 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | 0.020091 | 0.0037527 | -0.25825 | 0.010423 | 0.0037527 | south | Y | 0.020091 | 9.8033
5932 | SI_RAY9 | 9 | 38 | -0.003316 | south | 0.016775 | 0.00043672 | -0.26156 | 0.0071071 | 0.00043672 | south | N | 0.00043672 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.003316 | south | 0.016775 | 0.00043672 | -0.26156 | 0.0071071 | 0.00043672 | south | N | 0.00043672 | 0
5934 | SI_RAY5 | 5 | 15 | -0.003316 | south | 0.016775 | 0.00043672 | -0.26156 | 0.0071071 | 0.00043672 | south | N | 0.00043672 | 0
5935 | SI_RAY10 | 10 | 47 | -0.003316 | south | 0.016775 | 0.00043672 | -0.26156 | 0.0071071 | 0.00043672 | south | N | 0.00043672 | 0
6016 | SWMESA | 1 | 75 | 0.26188 | west | 0.28198 | 0.26564 | 0.0036359 | 0.27231 | 0.0036359 | west | N | 0.0036359 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | 0.020091 | 0.0037527 | -0.25825 | 0.010423 | 0.0037527 | south | Y | 0.25825 | 55.989
6144 | MCADOO1A | 1 | 150 | 0.21411 | west | 0.2342 | 0.21786 | -0.044142 | 0.22453 | 0.044142 | west | N | 0.044142 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.20374 | west | 0.22383 | 0.20749 | -0.054508 | 0.21416 | 0.054508 | west | N | 0.054508 | 0
6476 | LANGFORD | 1 | 150 | 0.16879 | west | 0.18888 | 0.17254 | -0.089459 | 0.17921 | 0.089459 | west | N | 0.089459 | 0
6637 | SNYDERW1 | 1 | 63 | 0.27075 | west | 0.29084 | 0.2745 | 0.012499 | 0.28117 | 0.012499 | west | N | 0.012499 | 0
6752 | OKLA0A | 1 | 649.7 | 0.067866 | west | 0.087957 | 0.071619 | -0.19038 | 0.078289 | 0.071619 | south | Y | 0.19038 | 77.1606
6948 | DENISNDM | 1 | 40 | -0.022909 | north | -0.0028175 | -0.019156 | -0.28116 | -0.012486 | 0.0028175 | North | N | 0.0028175 | 0
6948 | DENISNDM | 2 | 40 | -0.022909 | north | -0.0028175 | -0.019156 | -0.28116 | -0.012486 | 0.0028175 | North | N | 0.0028175 | 0
7000 | L_FERGUS | 1 | 422 | 0.004241 | south | 0.024332 | 0.0079937 | -0.25401 | 0.014664 | 0.0079937 | south | N | 0.0079937 | 0
7004 | L_SIMGID | 1 | 132 | -0.005998 | south | 0.014093 | -0.0022453 | -0.26425 | 0.0044251 | 0.0022453 | south | N | 0.0022453 | 0
7005 | L_SIMGID | 2 | 134 | -0.005998 | south | 0.014093 | -0.0022453 | -0.26425 | 0.0044251 | 0.0022453 | south | N | 0.0022453 | 0
7006 | L_SIMGID | 3 | 323 | -0.005998 | south | 0.014093 | -0.0022453 | -0.26425 | 0.0044251 | 0.0022453 | south | N | 0.0022453 | 0
7007 | L_LOSTPI | 1 | 158 | -0.00644 | south | 0.013651 | -0.0026873 | -0.26469 | 0.0039831 | 0.0026873 | south | N | 0.0026873 | 0
7008 | L_LOSTPI | 2 | 160 | -0.00644 | south | 0.013651 | -0.0026873 | -0.26469 | 0.0039831 | 0.0026873 | south | N | 0.0026873 | 0
7009 | L_LOSTPI | 3 | 175 | -0.00644 | south | 0.013651 | -0.0026873 | -0.26469 | 0.0039831 | 0.0026873 | south | N | 0.0026873 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.006477 | south | 0.013614 | -0.0027243 | -0.26473 | 0.0039461 | 0.0027243 | south | N | 0.0027243 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.006477 | south | 0.013614 | -0.0027243 | -0.26473 | 0.0039461 | 0.0027243 | south | N | 0.0027243 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.006475 | south | 0.013616 | -0.0027223 | -0.26472 | 0.0039481 | 0.0027223 | south | N | 0.0027223 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.004191 | south | 0.0159 | -0.00043828 | -0.26244 | 0.0062321 | 0.00043828 | south | N | 0.00043828 | 0
7015 | L_HAYSEN | 2 | 225 | -0.004191 | south | 0.0159 | -0.00043828 | -0.26244 | 0.0062321 | 0.00043828 | south | N | 0.00043828 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.004191 | south | 0.0159 | -0.00043828 | -0.26244 | 0.0062321 | 0.00043828 | south | N | 0.00043828 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.004191 | south | 0.0159 | -0.00043828 | -0.26244 | 0.0062321 | 0.00043828 | south | N | 0.00043828 | 0
7020 | L_AUSTPL | 1 | 8 | -0.005179 | south | 0.014912 | -0.0014263 | -0.26343 | 0.0052441 | 0.0014263 | south | N | 0.0014263 | 0
7020 | L_AUSTPL | 2 | 8 | -0.005179 | south | 0.014912 | -0.0014263 | -0.26343 | 0.0052441 | 0.0014263 | south | N | 0.0014263 | 0
7022 | L_BUCHAN | 1 | 18 | 0.004468 | south | 0.024559 | 0.0082207 | -0.25378 | 0.014891 | 0.0082207 | south | N | 0.0082207 | 0
7023 | L_BUCHAN | 2 | 18 | 0.004468 | south | 0.024559 | 0.0082207 | -0.25378 | 0.014891 | 0.0082207 | south | N | 0.0082207 | 0
7024 | L_BUCHAN | 3 | 15 | 0.004468 | south | 0.024559 | 0.0082207 | -0.25378 | 0.014891 | 0.0082207 | south | N | 0.0082207 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.007118 | south | 0.027209 | 0.010871 | -0.25113 | 0.017541 | 0.010871 | south | N | 0.010871 | 0
7028 | L_MARBFA | 1 | 18 | 0.002043 | south | 0.022134 | 0.0057957 | -0.25621 | 0.012466 | 0.0057957 | south | N | 0.0057957 | 0
7029 | L_MARBFA | 2 | 18 | 0.002043 | south | 0.022134 | 0.0057957 | -0.25621 | 0.012466 | 0.0057957 | south | N | 0.0057957 | 0
7031 | L_MARSFO | 1 | 35 | -0.002943 | south | 0.017148 | 0.00080972 | -0.26119 | 0.0074801 | 0.00080972 | south | N | 0.00080972 | 0
7032 | L_MARSFO | 2 | 34 | -0.002943 | south | 0.017148 | 0.00080972 | -0.26119 | 0.0074801 | 0.00080972 | south | N | 0.00080972 | 0
7033 | L_MARSFO | 3 | 35 | -0.002943 | south | 0.017148 | 0.00080972 | -0.26119 | 0.0074801 | 0.00080972 | south | N | 0.00080972 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.003673 | south | 0.023764 | 0.0074257 | -0.25458 | 0.014096 | 0.0074257 | south | N | 0.0074257 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.003673 | south | 0.023764 | 0.0074257 | -0.25458 | 0.014096 | 0.0074257 | south | N | 0.0074257 | 0
7038 | L_DELAWA | 1 | 35 | 0.28476 | west | 0.30485 | 0.28851 | 0.026513 | 0.29518 | 0.026513 | west | N | 0.026513 | 0
7038 | L_DELAWA | 2 | 30 | 0.28476 | west | 0.30485 | 0.28851 | 0.026513 | 0.29518 | 0.026513 | west | N | 0.026513 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.006291 | south | 0.0138 | -0.0025383 | -0.26454 | 0.0041321 | 0.0025383 | south | N | 0.0025383 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.006291 | south | 0.0138 | -0.0025383 | -0.26454 | 0.0041321 | 0.0025383 | south | N | 0.0025383 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.006291 | south | 0.0138 | -0.0025383 | -0.26454 | 0.0041321 | 0.0025383 | south | N | 0.0025383 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.006291 | south | 0.0138 | -0.0025383 | -0.26454 | 0.0041321 | 0.0025383 | south | N | 0.0025383 | 0
7487 | L_CANYHY | 1 | 6 | -0.003686 | south | 0.016405 | 6.6725e-05 | -0.26193 | 0.0067371 | 6.6725e-05 | south | N | 6.6725e-05 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.00395 | south | 0.016141 | -0.00019728 | -0.2622 | 0.0064731 | 0.00019728 | south | N | 0.00019728 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.00395 | south | 0.016141 | -0.00019728 | -0.2622 | 0.0064731 | 0.00019728 | south | N | 0.00019728 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.00395 | south | 0.016141 | -0.00019728 | -0.2622 | 0.0064731 | 0.00019728 | south | N | 0.00019728 | 0
7609 | L_SCHUMA | 1 | 4 | -0.003569 | south | 0.016522 | 0.00018372 | -0.26182 | 0.0068541 | 0.00018372 | south | N | 0.00018372 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.004325 | south | 0.015766 | -0.00057228 | -0.26257 | 0.0060981 | 0.00057228 | south | N | 0.00057228 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.004325 | south | 0.015766 | -0.00057228 | -0.26257 | 0.0060981 | 0.00057228 | south | N | 0.00057228 | 0
7800 | L_GUADGE | 1 | 147 | -0.003705 | south | 0.016386 | 4.7725e-05 | -0.26195 | 0.0067181 | 4.7725e-05 | south | N | 4.7725e-05 | 0
7801 | L_GUADGE | 2 | 138 | -0.003705 | south | 0.016386 | 4.7725e-05 | -0.26195 | 0.0067181 | 4.7725e-05 | south | N | 4.7725e-05 | 0
7802 | L_GUADGE | 3 | 140 | -0.003705 | south | 0.016386 | 4.7725e-05 | -0.26195 | 0.0067181 | 4.7725e-05 | south | N | 4.7725e-05 | 0
7803 | L_GUADGE | 4 | 147 | -0.003705 | south | 0.016386 | 4.7725e-05 | -0.26195 | 0.0067181 | 4.7725e-05 | south | N | 4.7725e-05 | 0
7804 | L_GUADGE | 5 | 182 | -0.003705 | south | 0.016386 | 4.7725e-05 | -0.26195 | 0.0067181 | 4.7725e-05 | south | N | 4.7725e-05 | 0
7805 | L_GUADGE | 6 | 198 | -0.003705 | south | 0.016386 | 4.7725e-05 | -0.26195 | 0.0067181 | 4.7725e-05 | south | N | 4.7725e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.006006 | south | 0.014085 | -0.0022533 | -0.26425 | 0.0044171 | 0.0022533 | south | N | 0.0022533 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.006006 | south | 0.014085 | -0.0022533 | -0.26425 | 0.0044171 | 0.0022533 | south | N | 0.0022533 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.006006 | south | 0.014085 | -0.0022533 | -0.26425 | 0.0044171 | 0.0022533 | south | N | 0.0022533 | 0
7810 | L_RIONOG | 1 | 142 | -0.00395 | south | 0.016141 | -0.00019728 | -0.2622 | 0.0064731 | 0.00019728 | south | N | 0.00019728 | 0
7811 | L_RIONOG | 2 | 145 | -0.00395 | south | 0.016141 | -0.00019728 | -0.2622 | 0.0064731 | 0.00019728 | south | N | 0.00019728 | 0
7812 | L_RIONOG | 3 | 151 | -0.00395 | south | 0.016141 | -0.00019728 | -0.2622 | 0.0064731 | 0.00019728 | south | N | 0.00019728 | 0
7813 | L_RIONOG | 4 | 290 | -0.00395 | south | 0.016141 | -0.00019728 | -0.2622 | 0.0064731 | 0.00019728 | south | N | 0.00019728 | 0
8032 | AMISTADH | 1 | 33 | 0.066155 | south | 0.086246 | 0.069908 | -0.19209 | 0.076578 | 0.069908 | south | N | 0.069908 | 0
8033 | AMISTADH | 2 | 25 | 0.066155 | south | 0.086246 | 0.069908 | -0.19209 | 0.076578 | 0.069908 | south | N | 0.069908 | 0
8048 | FALCONHY | 1 | 12 | -0.000968 | south | 0.019123 | 0.0027847 | -0.25922 | 0.0094551 | 0.0027847 | south | N | 0.0027847 | 0
8066 | DUP1V#1 | 1 | 73 | -0.004539 | south | 0.015552 | -0.00078628 | -0.26279 | 0.0058841 | 0.00078628 | south | N | 0.00078628 | 0
8134 | FOR69CG0 | 1 | 79 | -0.005163 | south | 0.014928 | -0.0014103 | -0.26341 | 0.0052601 | 0.0014103 | south | N | 0.0014103 | 0
8138 | FOR69CG0 | 2 | 81 | -0.005163 | south | 0.014928 | -0.0014103 | -0.26341 | 0.0052601 | 0.0014103 | south | N | 0.0014103 | 0
8139 | JOS #1 | MB | 255 | 0 | south | 0.020091 | 0.0037527 | -0.25825 | 0.010423 | 0.0037527 | south | N | 0.0037527 | 0
8147 | UCAR #2 | 10 | 28 | -0.004747 | south | 0.015344 | -0.00099428 | -0.263 | 0.0056761 | 0.00099428 | south | N | 0.00099428 | 0
8148 | UCAR #1 | 2 | 7 | -0.004747 | south | 0.015344 | -0.00099428 | -0.263 | 0.0056761 | 0.00099428 | south | N | 0.00099428 | 0
8153 | FOR69CG0 | 3 | 79 | -0.005163 | south | 0.014928 | -0.0014103 | -0.26341 | 0.0052601 | 0.0014103 | south | N | 0.0014103 | 0
8154 | FOR69CG0 | 4 | 80 | -0.005163 | south | 0.014928 | -0.0014103 | -0.26341 | 0.0052601 | 0.0014103 | south | N | 0.0014103 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.005163 | south | 0.014928 | -0.0014103 | -0.26341 | 0.0052601 | 0.0014103 | south | N | 0.0014103 | 0
8156 | FOR69CG0 | 6 | 25 | -0.005163 | south | 0.014928 | -0.0014103 | -0.26341 | 0.0052601 | 0.0014103 | south | N | 0.0014103 | 0
8157 | FOR69CG0 | 7 | 46 | -0.005163 | south | 0.014928 | -0.0014103 | -0.26341 | 0.0052601 | 0.0014103 | south | N | 0.0014103 | 0
8161 | COLETOU1 | 1 | 629 | -0.003677 | south | 0.016414 | 7.5725e-05 | -0.26193 | 0.0067461 | 7.5725e-05 | south | N | 7.5725e-05 | 0
8173 | VICEC51A | 5 | 144 | -0.004449 | south | 0.015642 | -0.00069628 | -0.2627 | 0.0059741 | 0.00069628 | south | N | 0.00069628 | 0
8174 | VICEC61A | 6 | 188 | -0.004449 | south | 0.015642 | -0.00069628 | -0.2627 | 0.0059741 | 0.00069628 | south | N | 0.00069628 | 0
8189 | CUERO 2 | 1 | 12 | -0.004313 | south | 0.015778 | -0.00056028 | -0.26256 | 0.0061101 | 0.00056028 | south | N | 0.00056028 | 0
8262 | ELPS | 1 | 6 | 0.047167 | south | 0.067258 | 0.05092 | -0.21108 | 0.05759 | 0.05092 | south | N | 0.05092 | 0
8285 | LAR #1 | MB | 32 | 0 | south | 0.020091 | 0.0037527 | -0.25825 | 0.010423 | 0.0037527 | south | N | 0.0037527 | 0
8287 | LAR #2 | MB | 32 | 0 | south | 0.020091 | 0.0037527 | -0.25825 | 0.010423 | 0.0037527 | south | N | 0.0037527 | 0
8288 | LAR #3 | MB | 105 | 0 | south | 0.020091 | 0.0037527 | -0.25825 | 0.010423 | 0.0037527 | south | N | 0.0037527 | 0
8388 | BATES0A | MB | 70 | 0 | south | 0.020091 | 0.0037527 | -0.25825 | 0.010423 | 0.0037527 | south | N | 0.0037527 | 0
8393 | BATES0B | MB | 110 | 0 | south | 0.020091 | 0.0037527 | -0.25825 | 0.010423 | 0.0037527 | south | N | 0.0037527 | 0
8442 | NBEC71A | 1 | 336 | -0.00365 | south | 0.016441 | 0.00010272 | -0.2619 | 0.0067731 | 0.00010272 | south | N | 0.00010272 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | 0.020091 | 0.0037527 | -0.25825 | 0.010423 | 0.0037527 | south | N | 0.0037527 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | 0.020091 | 0.0037527 | -0.25825 | 0.010423 | 0.0037527 | south | N | 0.0037527 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.003615 | south | 0.016476 | 0.00013772 | -0.26186 | 0.0068081 | 0.00013772 | south | N | 0.00013772 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.003615 | south | 0.016476 | 0.00013772 | -0.26186 | 0.0068081 | 0.00013772 | south | N | 0.00013772 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.00357 | south | 0.016521 | 0.00018272 | -0.26182 | 0.0068531 | 0.00018272 | south | N | 0.00018272 | 0
8506 | VAL #1 | 1 | 25 | -0.003593 | south | 0.016498 | 0.00015972 | -0.26184 | 0.0068301 | 0.00015972 | south | N | 0.00015972 | 0
8507 | VAL #2 | 2 | 25 | -0.003593 | south | 0.016498 | 0.00015972 | -0.26184 | 0.0068301 | 0.00015972 | south | N | 0.00015972 | 0
8511 | OXY_CC0A | 1 | 38 | -0.003591 | south | 0.0165 | 0.00016172 | -0.26184 | 0.0068321 | 0.00016172 | south | N | 0.00016172 | 0
8517 | CELANEBI | 1 | 29 | -0.003477 | south | 0.016614 | 0.00027572 | -0.26173 | 0.0069461 | 0.00027572 | south | N | 0.00027572 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.003648 | south | 0.016443 | 0.00010472 | -0.2619 | 0.0067751 | 0.00010472 | south | N | 0.00010472 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.003648 | south | 0.016443 | 0.00010472 | -0.2619 | 0.0067751 | 0.00010472 | south | N | 0.00010472 | 0
8562 | CNOPST1 | 3 | 153 | -0.003648 | south | 0.016443 | 0.00010472 | -0.2619 | 0.0067751 | 0.00010472 | south | N | 0.00010472 | 0
8926 | LGE_GT10 | 1 | 158 | -0.003829 | south | 0.016262 | -7.6275e-05 | -0.26208 | 0.0065941 | 7.6275e-05 | south | N | 7.6275e-05 | 0
8927 | LGE_GT20 | 2 | 153 | -0.003829 | south | 0.016262 | -7.6275e-05 | -0.26208 | 0.0065941 | 7.6275e-05 | south | N | 7.6275e-05 | 0
8928 | LGE_STG0 | 3 | 100 | -0.003829 | south | 0.016262 | -7.6275e-05 | -0.26208 | 0.0065941 | 7.6275e-05 | south | N | 7.6275e-05 | 0
8930 | ICPGN10A | 1 | 145 | -0.003829 | south | 0.016262 | -7.6275e-05 | -0.26208 | 0.0065941 | 7.6275e-05 | south | N | 7.6275e-05 | 0
8931 | ICPGN20A | 2 | 147 | -0.003829 | south | 0.016262 | -7.6275e-05 | -0.26208 | 0.0065941 | 7.6275e-05 | south | N | 7.6275e-05 | 0
8932 | ICPGN30A | 3 | 127 | -0.003829 | south | 0.016262 | -7.6275e-05 | -0.26208 | 0.0065941 | 7.6275e-05 | south | N | 7.6275e-05 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.002822 | south | 0.017269 | 0.00093072 | -0.26107 | 0.0076011 | 0.00093072 | south | N | 0.00093072 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.002822 | south | 0.017269 | 0.00093072 | -0.26107 | 0.0076011 | 0.00093072 | south | N | 0.00093072 | 0
8935 | FGNTS201 | 3 | 173 | -0.002822 | south | 0.017269 | 0.00093072 | -0.26107 | 0.0076011 | 0.00093072 | south | N | 0.00093072 | 0
8936 | MVGN#1 | 1 | 207 | -0.00313 | south | 0.016961 | 0.00062272 | -0.26138 | 0.0072931 | 0.00062272 | south | N | 0.00062272 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.00313 | south | 0.016961 | 0.00062272 | -0.26138 | 0.0072931 | 0.00062272 | south | N | 0.00062272 | 0
8938 | MVGN#3 | 3 | 242 | -0.00313 | south | 0.016961 | 0.00062272 | -0.26138 | 0.0072931 | 0.00062272 | south | N | 0.00062272 | 0
8981 | HECN1 | 1 | 144 | -0.003131 | south | 0.01696 | 0.00062172 | -0.26138 | 0.0072921 | 0.00062172 | south | N | 0.00062172 | 0
8982 | HECN2 | 2 | 144 | -0.003131 | south | 0.01696 | 0.00062172 | -0.26138 | 0.0072921 | 0.00062172 | south | N | 0.00062172 | 0
8983 | HECN3 | 3 | 171 | -0.003131 | south | 0.01696 | 0.00062172 | -0.26138 | 0.0072921 | 0.00062172 | south | N | 0.00062172 | 0
9000 | DECKR_G1 | 1 | 310 | -0.005392 | south | 0.014699 | -0.0016393 | -0.26364 | 0.0050311 | 0.0016393 | south | N | 0.0016393 | 0
9001 | DECKR_G2 | 2 | 413 | -0.005392 | south | 0.014699 | -0.0016393 | -0.26364 | 0.0050311 | 0.0016393 | south | N | 0.0016393 | 0
9002 | DECKR_G3 | 3 | 42 | -0.005576 | south | 0.014515 | -0.0018233 | -0.26382 | 0.0048471 | 0.0018233 | south | N | 0.0018233 | 0
9003 | DECKR_G4 | 4 | 44 | -0.005576 | south | 0.014515 | -0.0018233 | -0.26382 | 0.0048471 | 0.0018233 | south | N | 0.0018233 | 0
9004 | DECKR_G5 | 5 | 44 | -0.005576 | south | 0.014515 | -0.0018233 | -0.26382 | 0.0048471 | 0.0018233 | south | N | 0.0018233 | 0
9005 | DECKR_G6 | 6 | 47 | -0.005576 | south | 0.014515 | -0.0018233 | -0.26382 | 0.0048471 | 0.0018233 | south | N | 0.0018233 | 0
9016 | SANDH_G1 | 1 | 49 | -0.005331 | south | 0.01476 | -0.0015783 | -0.26358 | 0.0050921 | 0.0015783 | south | N | 0.0015783 | 0
9017 | SANDH_G2 | 2 | 46 | -0.005331 | south | 0.01476 | -0.0015783 | -0.26358 | 0.0050921 | 0.0015783 | south | N | 0.0015783 | 0
9018 | SANDH_G3 | 3 | 46 | -0.005331 | south | 0.01476 | -0.0015783 | -0.26358 | 0.0050921 | 0.0015783 | south | N | 0.0015783 | 0
9019 | SANDH_G4 | 4 | 47 | -0.005331 | south | 0.01476 | -0.0015783 | -0.26358 | 0.0050921 | 0.0015783 | south | N | 0.0015783 | 0
9020 | SANDHG5A | 5A | 154 | -0.005331 | south | 0.01476 | -0.0015783 | -0.26358 | 0.0050921 | 0.0015783 | south | N | 0.0015783 | 0
9021 | SANDHG5C | 5C | 148 | -0.005331 | south | 0.01476 | -0.0015783 | -0.26358 | 0.0050921 | 0.0015783 | south | N | 0.0015783 | 0
9022 | SANDH_G6 | 6 | 48 | -0.005331 | south | 0.01476 | -0.0015783 | -0.26358 | 0.0050921 | 0.0015783 | south | N | 0.0015783 | 0
9023 | SANDH_G7 | 7 | 48 | -0.005331 | south | 0.01476 | -0.0015783 | -0.26358 | 0.0050921 | 0.0015783 | south | N | 0.0015783 | 0
11001 | NAV1CT | 1 | 70 | 0.29132 | west | 0.31142 | 0.29508 | 0.033076 | 0.30175 | 0.033076 | west | N | 0.033076 | 0
11009 | NAV2CT | 1 | 70 | 0.29132 | west | 0.31142 | 0.29508 | 0.033076 | 0.30175 | 0.033076 | west | N | 0.033076 | 0
11011 | NAV3ST | 1 | 92.8 | 0.29132 | west | 0.31142 | 0.29508 | 0.033076 | 0.30175 | 0.033076 | west | N | 0.033076 | 0
11012 | NAV4CT | 1 | 80 | 0.29132 | west | 0.31142 | 0.29508 | 0.033076 | 0.30175 | 0.033076 | west | N | 0.033076 | 0
11013 | NAV5CT | 1 | 80 | 0.29132 | west | 0.31142 | 0.29508 | 0.033076 | 0.30175 | 0.033076 | west | N | 0.033076 | 0
11014 | NAV6ST | 1 | 115 | 0.29132 | west | 0.31142 | 0.29508 | 0.033076 | 0.30175 | 0.033076 | west | N | 0.033076 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.29126 | west | 0.31136 | 0.29502 | 0.033016 | 0.30169 | 0.033016 | west | N | 0.033016 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.29126 | west | 0.31136 | 0.29502 | 0.033016 | 0.30169 | 0.033016 | west | N | 0.033016 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.29126 | west | 0.31136 | 0.29502 | 0.033016 | 0.30169 | 0.033016 | west | N | 0.033016 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.29126 | west | 0.31136 | 0.29502 | 0.033016 | 0.30169 | 0.033016 | west | N | 0.033016 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.29126 | west | 0.31136 | 0.29502 | 0.033016 | 0.30169 | 0.033016 | west | N | 0.033016 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.29126 | west | 0.31136 | 0.29502 | 0.033016 | 0.30169 | 0.033016 | west | N | 0.033016 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.38029 | west | 0.40038 | 0.38405 | 0.12204 | 0.39072 | 0.12204 | west | N | 0.12204 | 0
11057 | CHAMPION | 1 | 126.5 | 0.38029 | west | 0.40038 | 0.38405 | 0.12204 | 0.39072 | 0.12204 | west | N | 0.12204 | 0
11058 | PYRON_1G | 1 | 249 | 0.38029 | west | 0.40038 | 0.38405 | 0.12204 | 0.39072 | 0.12204 | west | N | 0.12204 | 0
11059 | INADALE_ | 1 | 197 | 0.38029 | west | 0.40038 | 0.38405 | 0.12204 | 0.39072 | 0.12204 | west | N | 0.12204 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.2968 | west | 0.31689 | 0.30056 | 0.038555 | 0.30723 | 0.038555 | west | N | 0.038555 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.2968 | west | 0.31689 | 0.30056 | 0.038555 | 0.30723 | 0.038555 | west | N | 0.038555 | 0
11147 | NOTREES_ | 1 | 149 | 0.28396 | west | 0.30405 | 0.28771 | 0.025708 | 0.29438 | 0.025708 | west | N | 0.025708 | 0
11309 | BULLCREK | 1 | 180 | 0.27404 | west | 0.29413 | 0.27779 | 0.015794 | 0.28447 | 0.015794 | west | N | 0.015794 | 0
11310 | BULLCREK | 1 | 180 | 0.27404 | west | 0.29413 | 0.27779 | 0.015794 | 0.28447 | 0.015794 | west | N | 0.015794 | 0
11320 | COYOTE_1 | 1 | 225 | 0.27444 | west | 0.29453 | 0.27819 | 0.016193 | 0.28486 | 0.016193 | west | N | 0.016193 | 0
11415 | LORAINE_ | 1 | 125 | 0.29072 | west | 0.31081 | 0.29447 | 0.032471 | 0.30114 | 0.032471 | west | N | 0.032471 | 0
11416 | LORAINE_ | 1 | 125 | 0.29072 | west | 0.31081 | 0.29447 | 0.032471 | 0.30114 | 0.032471 | west | N | 0.032471 | 0
11691 | KMICHICT | 1 | 140 | -0.022695 | north | -0.0026035 | -0.018942 | -0.28094 | -0.012272 | 0.0026035 | North | N | 0.0026035 | 0
11692 | KMICHICT | 2 | 141 | -0.022695 | north | -0.0026035 | -0.018942 | -0.28094 | -0.012272 | 0.0026035 | North | N | 0.0026035 | 0
11693 | KMICHIST | 3 | 309 | -0.022695 | north | -0.0026035 | -0.018942 | -0.28094 | -0.012272 | 0.0026035 | North | N | 0.0026035 | 0
11694 | KMICHICT | 4 | 143 | -0.022695 | north | -0.0026035 | -0.018942 | -0.28094 | -0.012272 | 0.0026035 | North | N | 0.0026035 | 0
11695 | KMICHICT | 5 | 144 | -0.022695 | north | -0.0026035 | -0.018942 | -0.28094 | -0.012272 | 0.0026035 | North | N | 0.0026035 | 0
11696 | KMICHIST | 6 | 310 | -0.022695 | north | -0.0026035 | -0.018942 | -0.28094 | -0.012272 | 0.0026035 | North | N | 0.0026035 | 0
12322 | ENNSTRAC | 1 | 196 | -0.019373 | north | 0.0007185 | -0.01562 | -0.27762 | -0.0089499 | 0.0007185 | North | N | 0.0007185 | 0
12323 | ENNSTRAC | 2 | 111 | -0.019373 | north | 0.0007185 | -0.01562 | -0.27762 | -0.0089499 | 0.0007185 | North | N | 0.0007185 | 0
12357 | RNRTPL_1 | 1 | 0 | -0.022991 | north | -0.0028995 | -0.019238 | -0.28124 | -0.012568 | 0.0028995 | North | N | 0.0028995 | 0
12411 | FPLEFR1A | 1 | 161 | -0.021572 | north | -0.0014805 | -0.017819 | -0.27982 | -0.011149 | 0.0014805 | North | N | 0.0014805 | 0
12412 | FPLEFR1B | 2 | 164 | -0.021572 | north | -0.0014805 | -0.017819 | -0.27982 | -0.011149 | 0.0014805 | North | N | 0.0014805 | 0
12413 | FPLEFR1C | 3 | 164 | -0.021572 | north | -0.0014805 | -0.017819 | -0.27982 | -0.011149 | 0.0014805 | North | N | 0.0014805 | 0
12414 | FPLEFR1S | 4 | 414 | -0.021572 | north | -0.0014805 | -0.017819 | -0.27982 | -0.011149 | 0.0014805 | North | N | 0.0014805 | 0
12421 | FPLEFR2A | 1 | 162 | -0.021572 | north | -0.0014805 | -0.017819 | -0.27982 | -0.011149 | 0.0014805 | North | N | 0.0014805 | 0
12422 | FPLEFR2B | 2 | 161 | -0.021572 | north | -0.0014805 | -0.017819 | -0.27982 | -0.011149 | 0.0014805 | North | N | 0.0014805 | 0
12423 | FPLEFR2C | 3 | 163 | -0.021572 | north | -0.0014805 | -0.017819 | -0.27982 | -0.011149 | 0.0014805 | North | N | 0.0014805 | 0
12424 | FPLEFR2S | 4 | 409 | -0.021572 | north | -0.0014805 | -0.017819 | -0.27982 | -0.011149 | 0.0014805 | North | N | 0.0014805 | 0
12440 | PARKD_1S | 1 | 0 | -0.021551 | north | -0.0014595 | -0.017798 | -0.2798 | -0.011128 | 0.0014595 | North | N | 0.0014595 | 0
12449 | PARKD_2S | 1 | 0 | -0.021551 | north | -0.0014595 | -0.017798 | -0.2798 | -0.011128 | 0.0014595 | North | N | 0.0014595 | 0
13116 | TGATEWAY | 1 | 148 | -0.020081 | north | 1.0498e-05 | -0.016328 | -0.27833 | -0.0096579 | 1.0498e-05 | North | N | 1.0498e-05 | 0
13117 | TGATEWAY | 2 | 130 | -0.020081 | north | 1.0498e-05 | -0.016328 | -0.27833 | -0.0096579 | 1.0498e-05 | North | N | 1.0498e-05 | 0
13118 | TGATEWAY | 3 | 145 | -0.020081 | north | 1.0498e-05 | -0.016328 | -0.27833 | -0.0096579 | 1.0498e-05 | North | N | 1.0498e-05 | 0
13119 | TGATEWAY | 4 | 399 | -0.020081 | north | 1.0498e-05 | -0.016328 | -0.27833 | -0.0096579 | 1.0498e-05 | North | N | 1.0498e-05 | 0
13131 | CALFREST | 1 | 150.7 | -0.018334 | north | 0.0017575 | -0.014581 | -0.27658 | -0.0079109 | 0.0017575 | North | N | 0.0017575 | 0
13132 | CALFREST | 2 | 151 | -0.018334 | north | 0.0017575 | -0.014581 | -0.27658 | -0.0079109 | 0.0017575 | North | N | 0.0017575 | 0
13133 | CALFREST | 3 | 177.4 | -0.018334 | north | 0.0017575 | -0.014581 | -0.27658 | -0.0079109 | 0.0017575 | North | N | 0.0017575 | 0
13134 | CALFREST | 4 | 151.5 | -0.018397 | north | 0.0016945 | -0.014644 | -0.27665 | -0.0079739 | 0.0016945 | North | N | 0.0016945 | 0
13135 | CALFREST | 5 | 152.3 | -0.018397 | north | 0.0016945 | -0.014644 | -0.27665 | -0.0079739 | 0.0016945 | North | N | 0.0016945 | 0
13136 | CALFREST | 6 | 177.5 | -0.018397 | north | 0.0016945 | -0.014644 | -0.27665 | -0.0079739 | 0.0016945 | North | N | 0.0016945 | 0
13432 | SANDOW_5 | 5 | 581 | -0.008509 | south | 0.011582 | -0.0047563 | -0.26676 | 0.0019141 | 0.0019141 | houston | Y | 0.0047563 | 1.6513
13691 | OAKGROVE | 1 | 855 | -0.015678 | north | 0.0044135 | -0.011925 | -0.27393 | -0.0052549 | 0.0044135 | North | N | 0.0044135 | 0
13692 | OAKGROVE | 2 | 855 | -0.015678 | north | 0.0044135 | -0.011925 | -0.27393 | -0.0052549 | 0.0044135 | North | N | 0.0044135 | 0
32798 | BRYN_TAM | 1 | 32 | -0.014101 | north | 0.0059905 | -0.010348 | -0.27235 | -0.0036779 | 0.0036779 | houston | Y | 0.0059905 | 0.074004
32883 | BRYN_DNS | 1 | 48 | -0.014071 | north | 0.0060205 | -0.010318 | -0.27232 | -0.0036479 | 0.0036479 | houston | Y | 0.0060205 | 0.11389
32884 | BRYN_DNS | 1 | 46 | -0.014071 | north | 0.0060205 | -0.010318 | -0.27232 | -0.0036479 | 0.0036479 | houston | Y | 0.0060205 | 0.10914
32886 | BRYN_ATK | MB | 12 | -0.014111 | north | 0.0059805 | -0.010358 | -0.27236 | -0.0036879 | 0.0036879 | houston | Y | 0.0059805 | 0.027512
32887 | BRYN_ATK | MB | 51 | -0.014111 | north | 0.0059805 | -0.010358 | -0.27236 | -0.0036879 | 0.0036879 | houston | Y | 0.0059805 | 0.11692
32888 | BRYN_ATK | 1 | 17 | -0.014111 | north | 0.0059805 | -0.010358 | -0.27236 | -0.0036879 | 0.0036879 | houston | Y | 0.0059805 | 0.038975
32890 | BRYN_ATK | MB | 22 | -0.014111 | north | 0.0059805 | -0.010358 | -0.27236 | -0.0036879 | 0.0036879 | houston | Y | 0.0059805 | 0.050438
32891 | BRYN_ATK | MB | 25 | -0.014111 | north | 0.0059805 | -0.010358 | -0.27236 | -0.0036879 | 0.0036879 | houston | Y | 0.0059805 | 0.057316
32892 | BRYN_DNS | 1 | 105 | -0.014071 | north | 0.0060205 | -0.010318 | -0.27232 | -0.0036479 | 0.0036479 | houston | Y | 0.0060205 | 0.24913
36998 | RDCNYNG1 | 1 | 84 | 0.25745 | west | 0.27754 | 0.2612 | -0.00080012 | 0.26787 | 0.00080012 | west | N | 0.00080012 | 0
38332 | WDWRDU2 | 1 | 80 | 0.26155 | west | 0.28164 | 0.2653 | 0.0033009 | 0.27197 | 0.0033009 | west | N | 0.0033009 | 0
38437 | TNSRBNMS | 1 | 150 | 0.26133 | west | 0.28142 | 0.26509 | 0.0030849 | 0.27176 | 0.0030849 | west | N | 0.0030849 | 0
38438 | TNSRBNMS | 1 | 150 | 0.26133 | west | 0.28142 | 0.26509 | 0.0030849 | 0.27176 | 0.0030849 | west | N | 0.0030849 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.010327 | houston | 0.0097645 | -0.0065743 | -0.26858 | 9.6136e-05 | 9.6136e-05 | houston | N | 9.6136e-05 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.010327 | houston | 0.0097645 | -0.0065743 | -0.26858 | 9.6136e-05 | 9.6136e-05 | houston | N | 9.6136e-05 | 0
38600 | TNBP_CGN | 5 | 53 | -0.010327 | houston | 0.0097645 | -0.0065743 | -0.26858 | 9.6136e-05 | 9.6136e-05 | houston | N | 9.6136e-05 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.010327 | houston | 0.0097645 | -0.0065743 | -0.26858 | 9.6136e-05 | 9.6136e-05 | houston | N | 9.6136e-05 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.010327 | houston | 0.0097645 | -0.0065743 | -0.26858 | 9.6136e-05 | 9.6136e-05 | houston | N | 9.6136e-05 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.010327 | houston | 0.0097645 | -0.0065743 | -0.26858 | 9.6136e-05 | 9.6136e-05 | houston | N | 9.6136e-05 | 0
38614 | TNBPAMCG | 4 | 96 | -0.010327 | houston | 0.0097645 | -0.0065743 | -0.26858 | 9.6136e-05 | 9.6136e-05 | houston | N | 9.6136e-05 | 0
38615 | TNBPAMCG | 1 | 244 | -0.010327 | houston | 0.0097645 | -0.0065743 | -0.26858 | 9.6136e-05 | 9.6136e-05 | houston | N | 9.6136e-05 | 0
38690 | TNBP_CGN | 3 | 40 | -0.010327 | houston | 0.0097645 | -0.0065743 | -0.26858 | 9.6136e-05 | 9.6136e-05 | houston | N | 9.6136e-05 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.010325 | houston | 0.0097665 | -0.0065723 | -0.26857 | 9.8136e-05 | 9.8136e-05 | houston | N | 9.8136e-05 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.010325 | houston | 0.0097665 | -0.0065723 | -0.26857 | 9.8136e-05 | 9.8136e-05 | houston | N | 9.8136e-05 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.010325 | houston | 0.0097665 | -0.0065723 | -0.26857 | 9.8136e-05 | 9.8136e-05 | houston | N | 9.8136e-05 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.010325 | houston | 0.0097665 | -0.0065723 | -0.26857 | 9.8136e-05 | 9.8136e-05 | houston | N | 9.8136e-05 | 0
39470 | TNDOWCGN | 1 | 32 | -0.010325 | houston | 0.0097665 | -0.0065723 | -0.26857 | 9.8136e-05 | 9.8136e-05 | houston | N | 9.8136e-05 | 0
39480 | TNDOWCGN | 1 | 30 | -0.010325 | houston | 0.0097665 | -0.0065723 | -0.26857 | 9.8136e-05 | 9.8136e-05 | houston | N | 9.8136e-05 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.009484 | houston | 0.010607 | -0.0057313 | -0.26773 | 0.00093914 | 0.00093914 | houston | N | 0.00093914 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.009484 | houston | 0.010607 | -0.0057313 | -0.26773 | 0.00093914 | 0.00093914 | houston | N | 0.00093914 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.009484 | houston | 0.010607 | -0.0057313 | -0.26773 | 0.00093914 | 0.00093914 | houston | N | 0.00093914 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.009484 | houston | 0.010607 | -0.0057313 | -0.26773 | 0.00093914 | 0.00093914 | houston | N | 0.00093914 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.015678 | north | 0.0044135 | -0.011925 | -0.27393 | -0.0052549 | 0.0044135 | North | N | 0.0044135 | 0
39970 | TNTNPONE | 1 | 153 | -0.015678 | north | 0.0044135 | -0.011925 | -0.27393 | -0.0052549 | 0.0044135 | North | N | 0.0044135 | 0
48500 | APD_GT1_ | 1 | 136 | -0.010829 | houston | 0.0092625 | -0.0070763 | -0.26908 | -0.00040586 | 0.00040586 | houston | N | 0.00040586 | 0
48510 | AK_GT1__ | 1 | 33 | -0.010046 | houston | 0.010045 | -0.0062933 | -0.26829 | 0.00037714 | 0.00037714 | houston | N | 0.00037714 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.010827 | houston | 0.0092645 | -0.0070743 | -0.26908 | -0.00040386 | 0.00040386 | houston | N | 0.00040386 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.010827 | houston | 0.0092645 | -0.0070743 | -0.26908 | -0.00040386 | 0.00040386 | houston | N | 0.00040386 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.010827 | houston | 0.0092645 | -0.0070743 | -0.26908 | -0.00040386 | 0.00040386 | houston | N | 0.00040386 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.010827 | houston | 0.0092645 | -0.0070743 | -0.26908 | -0.00040386 | 0.00040386 | houston | N | 0.00040386 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.009332 | houston | 0.010759 | -0.0055793 | -0.26758 | 0.0010911 | 0.0010911 | houston | N | 0.0010911 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.009332 | houston | 0.010759 | -0.0055793 | -0.26758 | 0.0010911 | 0.0010911 | houston | N | 0.0010911 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.010026 | houston | 0.010065 | -0.0062733 | -0.26827 | 0.00039714 | 0.00039714 | houston | N | 0.00039714 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.010026 | houston | 0.010065 | -0.0062733 | -0.26827 | 0.00039714 | 0.00039714 | houston | N | 0.00039714 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.010026 | houston | 0.010065 | -0.0062733 | -0.26827 | 0.00039714 | 0.00039714 | houston | N | 0.00039714 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.010639 | houston | 0.0094525 | -0.0068863 | -0.26889 | -0.00021586 | 0.00021586 | houston | N | 0.00021586 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.010639 | houston | 0.0094525 | -0.0068863 | -0.26889 | -0.00021586 | 0.00021586 | houston | N | 0.00021586 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.010639 | houston | 0.0094525 | -0.0068863 | -0.26889 | -0.00021586 | 0.00021586 | houston | N | 0.00021586 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.010639 | houston | 0.0094525 | -0.0068863 | -0.26889 | -0.00021586 | 0.00021586 | houston | N | 0.00021586 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.010761 | houston | 0.0093305 | -0.0070083 | -0.26901 | -0.00033786 | 0.00033786 | houston | N | 0.00033786 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.010761 | houston | 0.0093305 | -0.0070083 | -0.26901 | -0.00033786 | 0.00033786 | houston | N | 0.00033786 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.010603 | houston | 0.0094885 | -0.0068503 | -0.26885 | -0.00017986 | 0.00017986 | houston | N | 0.00017986 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.010603 | houston | 0.0094885 | -0.0068503 | -0.26885 | -0.00017986 | 0.00017986 | houston | N | 0.00017986 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.010603 | houston | 0.0094885 | -0.0068503 | -0.26885 | -0.00017986 | 0.00017986 | houston | N | 0.00017986 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.010603 | houston | 0.0094885 | -0.0068503 | -0.26885 | -0.00017986 | 0.00017986 | houston | N | 0.00017986 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.010603 | houston | 0.0094885 | -0.0068503 | -0.26885 | -0.00017986 | 0.00017986 | houston | N | 0.00017986 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.010977 | houston | 0.0091145 | -0.0072243 | -0.26923 | -0.00055386 | 0.00055386 | houston | N | 0.00055386 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.010916 | houston | 0.0091755 | -0.0071633 | -0.26916 | -0.00049286 | 0.00049286 | houston | N | 0.00049286 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.010994 | houston | 0.0090975 | -0.0072413 | -0.26924 | -0.00057086 | 0.00057086 | houston | N | 0.00057086 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.010994 | houston | 0.0090975 | -0.0072413 | -0.26924 | -0.00057086 | 0.00057086 | houston | N | 0.00057086 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.010994 | houston | 0.0090975 | -0.0072413 | -0.26924 | -0.00057086 | 0.00057086 | houston | N | 0.00057086 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.011333 | houston | 0.0087585 | -0.0075803 | -0.26958 | -0.00090986 | 0.00090986 | houston | N | 0.00090986 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.010841 | houston | 0.0092505 | -0.0070883 | -0.26909 | -0.00041786 | 0.00041786 | houston | N | 0.00041786 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.010841 | houston | 0.0092505 | -0.0070883 | -0.26909 | -0.00041786 | 0.00041786 | houston | N | 0.00041786 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.011037 | houston | 0.0090545 | -0.0072843 | -0.26929 | -0.00061386 | 0.00061386 | houston | N | 0.00061386 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.011037 | houston | 0.0090545 | -0.0072843 | -0.26929 | -0.00061386 | 0.00061386 | houston | N | 0.00061386 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.011037 | houston | 0.0090545 | -0.0072843 | -0.26929 | -0.00061386 | 0.00061386 | houston | N | 0.00061386 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.011037 | houston | 0.0090545 | -0.0072843 | -0.26929 | -0.00061386 | 0.00061386 | houston | N | 0.00061386 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.010765 | houston | 0.0093265 | -0.0070123 | -0.26901 | -0.00034186 | 0.00034186 | houston | N | 0.00034186 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.010765 | houston | 0.0093265 | -0.0070123 | -0.26901 | -0.00034186 | 0.00034186 | houston | N | 0.00034186 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.010765 | houston | 0.0093265 | -0.0070123 | -0.26901 | -0.00034186 | 0.00034186 | houston | N | 0.00034186 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.010765 | houston | 0.0093265 | -0.0070123 | -0.26901 | -0.00034186 | 0.00034186 | houston | N | 0.00034186 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.010722 | houston | 0.0093695 | -0.0069693 | -0.26897 | -0.00029886 | 0.00029886 | houston | N | 0.00029886 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.010722 | houston | 0.0093695 | -0.0069693 | -0.26897 | -0.00029886 | 0.00029886 | houston | N | 0.00029886 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.010722 | houston | 0.0093695 | -0.0069693 | -0.26897 | -0.00029886 | 0.00029886 | houston | N | 0.00029886 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.010722 | houston | 0.0093695 | -0.0069693 | -0.26897 | -0.00029886 | 0.00029886 | houston | N | 0.00029886 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.010722 | houston | 0.0093695 | -0.0069693 | -0.26897 | -0.00029886 | 0.00029886 | houston | N | 0.00029886 | 0
48651 | EP_1_2 | 1 | 5 | -0.010975 | houston | 0.0091165 | -0.0072223 | -0.26922 | -0.00055186 | 0.00055186 | houston | N | 0.00055186 | 0
48651 | EP_1_2 | 2 | 21 | -0.010975 | houston | 0.0091165 | -0.0072223 | -0.26922 | -0.00055186 | 0.00055186 | houston | N | 0.00055186 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.013643 | north | 0.0064485 | -0.0098903 | -0.27189 | -0.0032199 | 0.0032199 | houston | Y | 0.0064485 | 0.49786
48672 | FTR_GT2_ | 2 | 156 | -0.013643 | north | 0.0064485 | -0.0098903 | -0.27189 | -0.0032199 | 0.0032199 | houston | Y | 0.0064485 | 0.50367
48673 | FTR_GT3_ | 3 | 156 | -0.013643 | north | 0.0064485 | -0.0098903 | -0.27189 | -0.0032199 | 0.0032199 | houston | Y | 0.0064485 | 0.50367
48674 | FTR_CN4_ | 4 | 380 | -0.013643 | north | 0.0064485 | -0.0098903 | -0.27189 | -0.0032199 | 0.0032199 | houston | Y | 0.0064485 | 1.2269
48690 | GBY_GN5_ | 5 | 398 | -0.011056 | houston | 0.0090355 | -0.0073033 | -0.2693 | -0.00063286 | 0.00063286 | houston | N | 0.00063286 | 0
48691 | GBY_7374 | A | 46 | -0.010703 | houston | 0.0093885 | -0.0069503 | -0.26895 | -0.00027986 | 0.00027986 | houston | N | 0.00027986 | 0
48691 | GBY_7374 | B | 46 | -0.010703 | houston | 0.0093885 | -0.0069503 | -0.26895 | -0.00027986 | 0.00027986 | houston | N | 0.00027986 | 0
48692 | GBY_8182 | C | 46 | -0.010703 | houston | 0.0093885 | -0.0069503 | -0.26895 | -0.00027986 | 0.00027986 | houston | N | 0.00027986 | 0
48692 | GBY_8182 | D | 55 | -0.010703 | houston | 0.0093885 | -0.0069503 | -0.26895 | -0.00027986 | 0.00027986 | houston | N | 0.00027986 | 0
48693 | GBY_8384 | E | 55 | -0.010703 | houston | 0.0093885 | -0.0069503 | -0.26895 | -0.00027986 | 0.00027986 | houston | N | 0.00027986 | 0
48693 | GBY_8384 | F | 54 | -0.010703 | houston | 0.0093885 | -0.0069503 | -0.26895 | -0.00027986 | 0.00027986 | houston | N | 0.00027986 | 0
48721 | LEG_1___ | 1 | 827 | -0.016304 | north | 0.0037875 | -0.012551 | -0.27455 | -0.0058809 | 0.0037875 | North | N | 0.0037875 | 0
48722 | LEG_2___ | 2 | 819 | -0.016304 | north | 0.0037875 | -0.012551 | -0.27455 | -0.0058809 | 0.0037875 | North | N | 0.0037875 | 0
48730 | MNS_GT | 1 | 46.1 | -0.009973 | houston | 0.010118 | -0.0062203 | -0.26822 | 0.00045014 | 0.00045014 | houston | N | 0.00045014 | 0
48731 | CBE_GT1 | 1 | 76 | -0.008289 | houston | 0.011802 | -0.0045363 | -0.26654 | 0.0021341 | 0.0021341 | houston | N | 0.0021341 | 0
48732 | CBE_GT2 | 1 | 76 | -0.008289 | houston | 0.011802 | -0.0045363 | -0.26654 | 0.0021341 | 0.0021341 | houston | N | 0.0021341 | 0
48733 | CBE_ST12 | 1 | 105 | -0.008289 | houston | 0.011802 | -0.0045363 | -0.26654 | 0.0021341 | 0.0021341 | houston | N | 0.0021341 | 0
48734 | CBE_GT3 | 1 | 74 | -0.008289 | houston | 0.011802 | -0.0045363 | -0.26654 | 0.0021341 | 0.0021341 | houston | N | 0.0021341 | 0
48735 | CBE_GT4 | 1 | 74 | -0.008289 | houston | 0.011802 | -0.0045363 | -0.26654 | 0.0021341 | 0.0021341 | houston | N | 0.0021341 | 0
48736 | CBE_ST34 | 1 | 102 | -0.008289 | houston | 0.011802 | -0.0045363 | -0.26654 | 0.0021341 | 0.0021341 | houston | N | 0.0021341 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.010766 | houston | 0.0093255 | -0.0070133 | -0.26901 | -0.00034286 | 0.00034286 | houston | N | 0.00034286 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.010766 | houston | 0.0093255 | -0.0070133 | -0.26901 | -0.00034286 | 0.00034286 | houston | N | 0.00034286 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.010766 | houston | 0.0093255 | -0.0070133 | -0.26901 | -0.00034286 | 0.00034286 | houston | N | 0.00034286 | 0
48761 | PR_GT1__ | 1 | 35 | -0.010742 | houston | 0.0093495 | -0.0069893 | -0.26899 | -0.00031886 | 0.00031886 | houston | N | 0.00031886 | 0
48772 | PHR_GN2_ | MB | 459 | -0.010509 | houston | 0.0095825 | -0.0067563 | -0.26876 | -8.5864e-05 | 8.5864e-05 | houston | N | 8.5864e-05 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.010976 | houston | 0.0091155 | -0.0072233 | -0.26922 | -0.00055286 | 0.00055286 | houston | N | 0.00055286 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.010976 | houston | 0.0091155 | -0.0072233 | -0.26922 | -0.00055286 | 0.00055286 | houston | N | 0.00055286 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.010976 | houston | 0.0091155 | -0.0072233 | -0.26922 | -0.00055286 | 0.00055286 | houston | N | 0.00055286 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.010976 | houston | 0.0091155 | -0.0072233 | -0.26922 | -0.00055286 | 0.00055286 | houston | N | 0.00055286 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.010976 | houston | 0.0091155 | -0.0072233 | -0.26922 | -0.00055286 | 0.00055286 | houston | N | 0.00055286 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.010976 | houston | 0.0091155 | -0.0072233 | -0.26922 | -0.00055286 | 0.00055286 | houston | N | 0.00055286 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.010976 | houston | 0.0091155 | -0.0072233 | -0.26922 | -0.00055286 | 0.00055286 | houston | N | 0.00055286 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.011333 | houston | 0.0087585 | -0.0075803 | -0.26958 | -0.00090986 | 0.00090986 | houston | N | 0.00090986 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.011333 | houston | 0.0087585 | -0.0075803 | -0.26958 | -0.00090986 | 0.00090986 | houston | N | 0.00090986 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.011333 | houston | 0.0087585 | -0.0075803 | -0.26958 | -0.00090986 | 0.00090986 | houston | N | 0.00090986 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.011333 | houston | 0.0087585 | -0.0075803 | -0.26958 | -0.00090986 | 0.00090986 | houston | N | 0.00090986 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.01099 | houston | 0.0091015 | -0.0072373 | -0.26924 | -0.00056686 | 0.00056686 | houston | N | 0.00056686 | 0
48820 | SHELLG1_ | 1 | 71 | -0.010789 | houston | 0.0093025 | -0.0070363 | -0.26904 | -0.00036586 | 0.00036586 | houston | N | 0.00036586 | 0
48821 | SHELLG2 | 2 | 72 | -0.010789 | houston | 0.0093025 | -0.0070363 | -0.26904 | -0.00036586 | 0.00036586 | houston | N | 0.00036586 | 0
48822 | SHELLG3_ | 1 | 39 | -0.010789 | houston | 0.0093025 | -0.0070363 | -0.26904 | -0.00036586 | 0.00036586 | houston | N | 0.00036586 | 0
48822 | SHELLG3_ | 2 | 30 | -0.010789 | houston | 0.0093025 | -0.0070363 | -0.26904 | -0.00036586 | 0.00036586 | houston | N | 0.00036586 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.010707 | houston | 0.0093845 | -0.0069543 | -0.26896 | -0.00028386 | 0.00028386 | houston | N | 0.00028386 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.010707 | houston | 0.0093845 | -0.0069543 | -0.26896 | -0.00028386 | 0.00028386 | houston | N | 0.00028386 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.010764 | houston | 0.0093275 | -0.0070113 | -0.26901 | -0.00034086 | 0.00034086 | houston | N | 0.00034086 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.01076 | houston | 0.0093315 | -0.0070073 | -0.26901 | -0.00033686 | 0.00033686 | houston | N | 0.00033686 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.010758 | houston | 0.0093335 | -0.0070053 | -0.26901 | -0.00033486 | 0.00033486 | houston | N | 0.00033486 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.010764 | houston | 0.0093275 | -0.0070113 | -0.26901 | -0.00034086 | 0.00034086 | houston | N | 0.00034086 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.010765 | houston | 0.0093265 | -0.0070123 | -0.26901 | -0.00034186 | 0.00034186 | houston | N | 0.00034186 | 0
48855 | SRB_GT21 | B2 | 12 | -0.010757 | houston | 0.0093345 | -0.0070043 | -0.26901 | -0.00033386 | 0.00033386 | houston | N | 0.00033386 | 0
48855 | SRB_GT21 | MB | 18 | -0.010757 | houston | 0.0093345 | -0.0070043 | -0.26901 | -0.00033386 | 0.00033386 | houston | N | 0.00033386 | 0
48865 | TECO_GT1 | 1 | 50 | -0.010444 | houston | 0.0096475 | -0.0066913 | -0.26869 | -2.0864e-05 | 2.0864e-05 | houston | N | 2.0864e-05 | 0
48873 | THW_ST3_ | 3 | 104 | -0.010905 | houston | 0.0091865 | -0.0071523 | -0.26915 | -0.00048186 | 0.00048186 | houston | N | 0.00048186 | 0
48874 | THW_ST4_ | 4 | 104 | -0.010905 | houston | 0.0091865 | -0.0071523 | -0.26915 | -0.00048186 | 0.00048186 | houston | N | 0.00048186 | 0
48875 | THW_3132 | A | 54 | -0.010905 | houston | 0.0091865 | -0.0071523 | -0.26915 | -0.00048186 | 0.00048186 | houston | N | 0.00048186 | 0
48875 | THW_3132 | B | 53 | -0.010905 | houston | 0.0091865 | -0.0071523 | -0.26915 | -0.00048186 | 0.00048186 | houston | N | 0.00048186 | 0
48877 | THW_3334 | C | 54 | -0.010905 | houston | 0.0091865 | -0.0071523 | -0.26915 | -0.00048186 | 0.00048186 | houston | N | 0.00048186 | 0
48877 | THW_3334 | D | 57 | -0.010905 | houston | 0.0091865 | -0.0071523 | -0.26915 | -0.00048186 | 0.00048186 | houston | N | 0.00048186 | 0
48879 | THW_4142 | E | 54 | -0.010905 | houston | 0.0091865 | -0.0071523 | -0.26915 | -0.00048186 | 0.00048186 | houston | N | 0.00048186 | 0
48879 | THW_4142 | F | 54 | -0.010905 | houston | 0.0091865 | -0.0071523 | -0.26915 | -0.00048186 | 0.00048186 | houston | N | 0.00048186 | 0
48881 | THW_4344 | G | 58 | -0.010905 | houston | 0.0091865 | -0.0071523 | -0.26915 | -0.00048186 | 0.00048186 | houston | N | 0.00048186 | 0
48881 | THW_4344 | H | 58 | -0.010905 | houston | 0.0091865 | -0.0071523 | -0.26915 | -0.00048186 | 0.00048186 | houston | N | 0.00048186 | 0
48883 | THW_GT1_ | B2 | 12 | -0.010959 | houston | 0.0091325 | -0.0072063 | -0.26921 | -0.00053586 | 0.00053586 | houston | N | 0.00053586 | 0
48885 | THW_5152 | A | 56 | -0.011084 | houston | 0.0090075 | -0.0073313 | -0.26933 | -0.00066086 | 0.00066086 | houston | N | 0.00066086 | 0
48885 | THW_5152 | B | 59 | -0.011084 | houston | 0.0090075 | -0.0073313 | -0.26933 | -0.00066086 | 0.00066086 | houston | N | 0.00066086 | 0
48886 | THW_5354 | C | 56 | -0.011084 | houston | 0.0090075 | -0.0073313 | -0.26933 | -0.00066086 | 0.00066086 | houston | N | 0.00066086 | 0
48886 | THW_5354 | D | 56 | -0.011084 | houston | 0.0090075 | -0.0073313 | -0.26933 | -0.00066086 | 0.00066086 | houston | N | 0.00066086 | 0
48887 | THW_5556 | E | 59 | -0.011084 | houston | 0.0090075 | -0.0073313 | -0.26933 | -0.00066086 | 0.00066086 | houston | N | 0.00066086 | 0
48887 | THW_5556 | F | 56 | -0.011084 | houston | 0.0090075 | -0.0073313 | -0.26933 | -0.00066086 | 0.00066086 | houston | N | 0.00066086 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.008403 | houston | 0.011688 | -0.0046503 | -0.26665 | 0.0020201 | 0.0020201 | houston | N | 0.0020201 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.010118 | houston | 0.0099735 | -0.0063653 | -0.26837 | 0.00030514 | 0.00030514 | houston | N | 0.00030514 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.010118 | houston | 0.0099735 | -0.0063653 | -0.26837 | 0.00030514 | 0.00030514 | houston | N | 0.00030514 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.010118 | houston | 0.0099735 | -0.0063653 | -0.26837 | 0.00030514 | 0.00030514 | houston | N | 0.00030514 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.010118 | houston | 0.0099735 | -0.0063653 | -0.26837 | 0.00030514 | 0.00030514 | houston | N | 0.00030514 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.010118 | houston | 0.0099735 | -0.0063653 | -0.26837 | 0.00030514 | 0.00030514 | houston | N | 0.00030514 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.010022 | houston | 0.010069 | -0.0062693 | -0.26827 | 0.00040114 | 0.00040114 | houston | N | 0.00040114 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.010022 | houston | 0.010069 | -0.0062693 | -0.26827 | 0.00040114 | 0.00040114 | houston | N | 0.00040114 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.010022 | houston | 0.010069 | -0.0062693 | -0.26827 | 0.00040114 | 0.00040114 | houston | N | 0.00040114 | 0
48929 | WAPGT21_ | B1 | 13 | -0.010118 | houston | 0.0099735 | -0.0063653 | -0.26837 | 0.00030514 | 0.00030514 | houston | N | 0.00030514 | 0
48940 | WARVUE_G | G1 | 12 | -0.010976 | houston | 0.0091155 | -0.0072233 | -0.26922 | -0.00055286 | 0.00055286 | houston | N | 0.00055286 | 0
49803 | EXN_15GT | 1 | 34 | -0.010931 | houston | 0.0091605 | -0.0071783 | -0.26918 | -0.00050786 | 0.00050786 | houston | N | 0.00050786 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.010931 | houston | 0.0091605 | -0.0071783 | -0.26918 | -0.00050786 | 0.00050786 | houston | N | 0.00050786 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.010931 | houston | 0.0091605 | -0.0071783 | -0.26918 | -0.00050786 | 0.00050786 | houston | N | 0.00050786 | 0
49826 | EXN938GT | 5 | 45.9 | -0.010931 | houston | 0.0091605 | -0.0071783 | -0.26918 | -0.00050786 | 0.00050786 | houston | N | 0.00050786 | 0
49828 | EXN941GT | 10 | 17.7 | -0.010931 | houston | 0.0091605 | -0.0071783 | -0.26918 | -0.00050786 | 0.00050786 | houston | N | 0.00050786 | 0
49829 | EXN942GT | 11 | 20.4 | -0.010931 | houston | 0.0091605 | -0.0071783 | -0.26918 | -0.00050786 | 0.00050786 | houston | N | 0.00050786 | 0
49830 | EXN943GT | 12 | 19.9 | -0.010931 | houston | 0.0091605 | -0.0071783 | -0.26918 | -0.00050786 | 0.00050786 | houston | N | 0.00050786 | 0
49831 | EXN944GT | 13 | 35 | -0.010931 | houston | 0.0091605 | -0.0071783 | -0.26918 | -0.00050786 | 0.00050786 | houston | N | 0.00050786 | 0
49832 | EXN945GT | 9 | 18 | -0.010931 | houston | 0.0091605 | -0.0071783 | -0.26918 | -0.00050786 | 0.00050786 | houston | N | 0.00050786 | 0
49837 | EXN_GT | 4 | 85.4 | -0.010931 | houston | 0.0091605 | -0.0071783 | -0.26918 | -0.00050786 | 0.00050786 | houston | N | 0.00050786 | 0
49838 | EXN_14GT | 14 | 148 | -0.010931 | houston | 0.0091605 | -0.0071783 | -0.26918 | -0.00050786 | 0.00050786 | houston | N | 0.00050786 | 0
49851 | DOW17000 | 37 | 62 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49858 | DOW38100 | 31 | 71.4 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49859 | DOW38200 | 33 | 45 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49860 | DOW38300 | 32 | 101 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49862 | DOW39100 | 36 | 86 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49863 | DOW39200 | 35 | 88 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49865 | DOW41000 | 41 | 50 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49866 | DOW42000 | 42 | 18 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49869 | DOW49000 | 45 | 94 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49870 | DOW61000 | 61 | 70 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49871 | DOW62000 | 62 | 63 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49872 | DOW63000 | 63 | 72 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49873 | DOW64000 | 64 | 64.8 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49876 | DOW65000 | 65 | 101 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49877 | DOW66000 | 66 | 97 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49878 | DOW67000 | 67 | 103 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49882 | DOW81000 | 81 | 76 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49884 | DOW82000 | 82 | 80 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49885 | DOW83000 | 83 | 80 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
49886 | DOW84000 | 84 | 171 | -0.009153 | houston | 0.010938 | -0.0054003 | -0.2674 | 0.0012701 | 0.0012701 | houston | N | 0.0012701 | 0
58909 | PEARSALL | 1 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58909 | PEARSALL | 2 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58909 | PEARSALL | 3 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58909 | PEARSALL | 4 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58909 | PEARSALL | 5 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58909 | PEARSALL | 6 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58919 | PEARSALL | 1 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58919 | PEARSALL | 2 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58919 | PEARSALL | 3 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58919 | PEARSALL | 4 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58919 | PEARSALL | 5 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58919 | PEARSALL | 6 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58929 | PEARSALL | 1 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58929 | PEARSALL | 2 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58929 | PEARSALL | 3 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58929 | PEARSALL | 4 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58929 | PEARSALL | 5 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58929 | PEARSALL | 6 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58949 | PEARSALL | 1 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58949 | PEARSALL | 2 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58949 | PEARSALL | 3 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58949 | PEARSALL | 4 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58949 | PEARSALL | 5 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
58949 | PEARSALL | 6 | 8.4 | 0.008214 | south | 0.028305 | 0.011967 | -0.25003 | 0.018637 | 0.011967 | south | N | 0.011967 | 0
60000 | DSKY2 | 1 | 76.5 | 0.25093 | west | 0.27102 | 0.25468 | -0.0073201 | 0.26135 | 0.0073201 | west | N | 0.0073201 | 0
60003 | KING_NE1 | 1 | 80 | 0.26188 | west | 0.28198 | 0.26564 | 0.0036359 | 0.27231 | 0.0036359 | west | N | 0.0036359 | 0
60005 | KING_SE1 | 1 | 40 | 0.26188 | west | 0.28198 | 0.26564 | 0.0036359 | 0.27231 | 0.0036359 | west | N | 0.0036359 | 0
60007 | KING_SW1 | 1 | 80 | 0.26336 | west | 0.28345 | 0.26711 | 0.0051129 | 0.27378 | 0.0051129 | west | N | 0.0051129 | 0
60016 | WOODWRD1 | 1 | 80 | 0.2616 | west | 0.28169 | 0.26535 | 0.0033499 | 0.27202 | 0.0033499 | west | N | 0.0033499 | 0
60017 | ORNNWP1 | 1 | 80 | 0.25359 | west | 0.27368 | 0.25734 | -0.0046571 | 0.26401 | 0.0046571 | west | N | 0.0046571 | 0
60018 | DSKY1 | 1 | 84 | 0.25098 | west | 0.27107 | 0.25473 | -0.0072701 | 0.2614 | 0.0072701 | west | N | 0.0072701 | 0
60019 | KING_NW1 | 1 | 80 | 0.26336 | west | 0.28345 | 0.26711 | 0.0051129 | 0.27378 | 0.0051129 | west | N | 0.0051129 | 0
60057 | CALLAHAN | 1 | 114 | -0.001692 | south | 0.018399 | 0.0020607 | -0.25994 | 0.0087311 | 0.0020607 | south | N | 0.0020607 | 0
60058 | BUFF_GAP | 1 | 120 | 0.20724 | west | 0.22733 | 0.21099 | -0.05101 | 0.21766 | 0.05101 | west | N | 0.05101 | 0
60060 | CIRELLO | 1 | 233 | 0.20724 | west | 0.22733 | 0.21099 | -0.05101 | 0.21766 | 0.05101 | west | N | 0.05101 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.20724 | west | 0.22733 | 0.21099 | -0.05101 | 0.21766 | 0.05101 | west | N | 0.05101 | 0
60066 | H_HOLLOW | 1 | 222 | -0.001692 | south | 0.018399 | 0.0020607 | -0.25994 | 0.0087311 | 0.0020607 | south | N | 0.0020607 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.001692 | south | 0.018399 | 0.0020607 | -0.25994 | 0.0087311 | 0.0020607 | south | N | 0.0020607 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.001692 | south | 0.018399 | 0.0020607 | -0.25994 | 0.0087311 | 0.0020607 | south | N | 0.0020607 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.001692 | south | 0.018399 | 0.0020607 | -0.25994 | 0.0087311 | 0.0020607 | south | N | 0.0020607 | 0
60074 | HORSH5 | 1 | 100 | -0.001692 | south | 0.018399 | 0.0020607 | -0.25994 | 0.0087311 | 0.0020607 | south | N | 0.0020607 | 0
60081 | WHRLWIND | 1 | 60 | 0.168 | west | 0.18809 | 0.17175 | -0.090246 | 0.17843 | 0.090246 | west | N | 0.090246 | 0
60201 | RIO DRCS | F | 0 | 0.064415 | south | 0.084506 | 0.068168 | -0.19383 | 0.074838 | 0.068168 | south | N | 0.068168 | 0
60202 | FRIEND_R | F | 0 | 0.21005 | west | 0.23014 | 0.2138 | -0.048201 | 0.22047 | 0.048201 | west | N | 0.048201 | 0
60203 | PRES0A | BT | 4.8 | 0.26998 | west | 0.29008 | 0.27374 | 0.011736 | 0.28041 | 0.011736 | west | N | 0.011736 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.25837 | west | 0.27846 | 0.26213 | 0.00012488 | 0.2688 | 0.00012488 | west | N | 0.00012488 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.25837 | west | 0.27846 | 0.26213 | 0.00012488 | 0.2688 | 0.00012488 | west | N | 0.00012488 | 0
71057 | L_SWEETW | W1 | 135 | 0.25837 | west | 0.27846 | 0.26213 | 0.00012488 | 0.2688 | 0.00012488 | west | N | 0.00012488 | 0
71059 | L_SWEETW | W1 | 119 | 0.25837 | west | 0.27846 | 0.26213 | 0.00012488 | 0.2688 | 0.00012488 | west | N | 0.00012488 | 0
71060 | L_SWEETW | W1 | 105 | 0.25837 | west | 0.27846 | 0.26213 | 0.00012488 | 0.2688 | 0.00012488 | west | N | 0.00012488 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.25837 | west | 0.27846 | 0.26213 | 0.00012488 | 0.2688 | 0.00012488 | west | N | 0.00012488 | 0
76031 | L_GASCCR | W1 | 150 | 0.26217 | west | 0.28226 | 0.26593 | 0.0039249 | 0.2726 | 0.0039249 | west | N | 0.0039249 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.25514 | west | 0.27523 | 0.25889 | -0.0031111 | 0.26556 | 0.0031111 | west | N | 0.0031111 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.25514 | west | 0.27523 | 0.25889 | -0.0031111 | 0.26556 | 0.0031111 | west | N | 0.0031111 | 0
76096 | L_CAPRSI | W1 | 186 | 0.25514 | west | 0.27523 | 0.25889 | -0.0031111 | 0.26556 | 0.0031111 | west | N | 0.0031111 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.25514 | west | 0.27523 | 0.25889 | -0.0031111 | 0.26556 | 0.0031111 | west | N | 0.0031111 | 0
80003 | MILHWYS | F | 0 | -0.003316 | south | 0.016775 | 0.00043672 | -0.26156 | 0.0071071 | 0.00043672 | south | N | 0.00043672 | 0
80010 | EPLVT1 | F | 0 | 0.04275 | south | 0.062841 | 0.046503 | -0.2155 | 0.053173 | 0.046503 | south | N | 0.046503 | 0
80012 | LAR | F | 0 | 0.002839 | south | 0.02293 | 0.0065917 | -0.25541 | 0.013262 | 0.0065917 | south | N | 0.0065917 | 0
80051 | FORPVCM0 | 8 | 28 | -0.005163 | south | 0.014928 | -0.0014103 | -0.26341 | 0.0052601 | 0.0014103 | south | N | 0.0014103 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.005163 | south | 0.014928 | -0.0014103 | -0.26341 | 0.0052601 | 0.0014103 | south | N | 0.0014103 | 0
80053 | FOR69CG0 | 10 | 74 | -0.005163 | south | 0.014928 | -0.0014103 | -0.26341 | 0.0052601 | 0.0014103 | south | N | 0.0014103 | 0
80080 | GWINDT11 | 1 | 94 | -0.003389 | south | 0.016702 | 0.00036372 | -0.26164 | 0.0070341 | 0.00036372 | south | N | 0.00036372 | 0
80080 | GWINDT11 | 2 | 41 | -0.003389 | south | 0.016702 | 0.00036372 | -0.26164 | 0.0070341 | 0.00036372 | south | N | 0.00036372 | 0
80080 | GWINDT11 | 3 | 38 | -0.003389 | south | 0.016702 | 0.00036372 | -0.26164 | 0.0070341 | 0.00036372 | south | N | 0.00036372 | 0
80080 | GWINDT11 | 4 | 19 | -0.003389 | south | 0.016702 | 0.00036372 | -0.26164 | 0.0070341 | 0.00036372 | south | N | 0.00036372 | 0
80081 | GWINDT21 | 1 | 94 | -0.003389 | south | 0.016702 | 0.00036372 | -0.26164 | 0.0070341 | 0.00036372 | south | N | 0.00036372 | 0
80081 | GWINDT21 | 2 | 36 | -0.003389 | south | 0.016702 | 0.00036372 | -0.26164 | 0.0070341 | 0.00036372 | south | N | 0.00036372 | 0
80081 | GWINDT21 | 3 | 43 | -0.003389 | south | 0.016702 | 0.00036372 | -0.26164 | 0.0070341 | 0.00036372 | south | N | 0.00036372 | 0
80081 | GWINDT21 | 4 | 22 | -0.003389 | south | 0.016702 | 0.00036372 | -0.26164 | 0.0070341 | 0.00036372 | south | N | 0.00036372 | 0
80137 | CSDR89 | 8 | 39 | -0.004747 | south | 0.015344 | -0.00099428 | -0.263 | 0.0056761 | 0.00099428 | south | N | 0.00099428 | 0
80137 | CSDR89 | 9 | 15 | -0.004747 | south | 0.015344 | -0.00099428 | -0.263 | 0.0056761 | 0.00099428 | south | N | 0.00099428 | 0
80138 | CSDR7 | 7 | 7 | -0.004747 | south | 0.015344 | -0.00099428 | -0.263 | 0.0056761 | 0.00099428 | south | N | 0.00099428 | 0
80139 | CSDR56 | 5 | 15 | -0.004747 | south | 0.015344 | -0.00099428 | -0.263 | 0.0056761 | 0.00099428 | south | N | 0.00099428 | 0
80139 | CSDR56 | 6 | 39 | -0.004747 | south | 0.015344 | -0.00099428 | -0.263 | 0.0056761 | 0.00099428 | south | N | 0.00099428 | 0
80140 | CSDR11 | 11 | 39 | -0.004747 | south | 0.015344 | -0.00099428 | -0.263 | 0.0056761 | 0.00099428 | south | N | 0.00099428 | 0
80180 | PNSCALT1 | 1 | 148 | -0.003389 | south | 0.016702 | 0.00036372 | -0.26164 | 0.0070341 | 0.00036372 | south | N | 0.00036372 | 0
80180 | PNSCALT1 | 2 | 50 | -0.003389 | south | 0.016702 | 0.00036372 | -0.26164 | 0.0070341 | 0.00036372 | south | N | 0.00036372 | 0
80181 | PNSCALT2 | 1 | 55 | -0.003389 | south | 0.016702 | 0.00036372 | -0.26164 | 0.0070341 | 0.00036372 | south | N | 0.00036372 | 0
80181 | PNSCALT2 | 2 | 50 | -0.003389 | south | 0.016702 | 0.00036372 | -0.26164 | 0.0070341 | 0.00036372 | south | N | 0.00036372 | 0
80223 | REYSHR G | 1 | 12 | -0.003829 | south | 0.016262 | -7.6275e-05 | -0.26208 | 0.0065941 | 7.6275e-05 | south | N | 7.6275e-05 | 0
80224 | VISTRONG | 1 | 15 | -0.004658 | south | 0.015433 | -0.00090528 | -0.26291 | 0.0057651 | 0.00090528 | south | N | 0.00090528 | 0
80225 | VISTRONG | 2 | 23 | -0.004658 | south | 0.015433 | -0.00090528 | -0.26291 | 0.0057651 | 0.00090528 | south | N | 0.00090528 | 0
80226 | ALCOA G | 1 | 48 | -0.005075 | south | 0.015016 | -0.0013223 | -0.26332 | 0.0053481 | 0.0013223 | south | N | 0.0013223 | 0
80227 | AIRCO G | 1 | 8 | -0.004684 | south | 0.015407 | -0.00093128 | -0.26293 | 0.0057391 | 0.00093128 | south | N | 0.00093128 | 0
80261 | NBEC81A | 1 | 180 | -0.003645 | south | 0.016446 | 0.00010772 | -0.26189 | 0.0067781 | 0.00010772 | south | N | 0.00010772 | 0
80262 | NBEC91A | 1 | 180 | -0.00365 | south | 0.016441 | 0.00010272 | -0.2619 | 0.0067731 | 0.00010272 | south | N | 0.00010272 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.003615 | south | 0.016476 | 0.00013772 | -0.26186 | 0.0068081 | 0.00013772 | south | N | 0.00013772 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.003615 | south | 0.016476 | 0.00013772 | -0.26186 | 0.0068081 | 0.00013772 | south | N | 0.00013772 | 0
80265 | LARECU40 | 4 | 100 | 0.002835 | south | 0.022926 | 0.0065877 | -0.25541 | 0.013258 | 0.0065877 | south | N | 0.0065877 | 0
80266 | LARECU50 | 5 | 100 | 0.002835 | south | 0.022926 | 0.0065877 | -0.25541 | 0.013258 | 0.0065877 | south | N | 0.0065877 | 0
80291 | PAPALOTE | 1 | 25 | -0.003753 | south | 0.016338 | -2.7525e-07 | -0.262 | 0.0066701 | 2.7525e-07 | south | N | 2.7525e-07 | 0
80291 | PAPALOTE | 2 | 25 | -0.003753 | south | 0.016338 | -2.7525e-07 | -0.262 | 0.0066701 | 2.7525e-07 | south | N | 2.7525e-07 | 0
80291 | PAPALOTE | 3 | 25 | -0.003753 | south | 0.016338 | -2.7525e-07 | -0.262 | 0.0066701 | 2.7525e-07 | south | N | 2.7525e-07 | 0
80291 | PAPALOTE | 4 | 16 | -0.003753 | south | 0.016338 | -2.7525e-07 | -0.262 | 0.0066701 | 2.7525e-07 | south | N | 2.7525e-07 | 0
80294 | PAPALOTE | 5 | 25 | -0.003753 | south | 0.016338 | -2.7525e-07 | -0.262 | 0.0066701 | 2.7525e-07 | south | N | 2.7525e-07 | 0
80294 | PAPALOTE | 6 | 25 | -0.003753 | south | 0.016338 | -2.7525e-07 | -0.262 | 0.0066701 | 2.7525e-07 | south | N | 2.7525e-07 | 0
80294 | PAPALOTE | 7 | 25 | -0.003753 | south | 0.016338 | -2.7525e-07 | -0.262 | 0.0066701 | 2.7525e-07 | south | N | 2.7525e-07 | 0
80294 | PAPALOTE | 8 | 15 | -0.003753 | south | 0.016338 | -2.7525e-07 | -0.262 | 0.0066701 | 2.7525e-07 | south | N | 2.7525e-07 | 0
86104 | CID-138 | EQ | 0 | 0.002835 | south | 0.022926 | 0.0065877 | -0.25541 | 0.013258 | 0.0065877 | south | N | 0.0065877 | 0
86105 | CID-230 | EQ | 500 | 0.002835 | south | 0.022926 | 0.0065877 | -0.25541 | 0.013258 | 0.0065877 | south | N | 0.0065877 | 0
86106 | CUF-230 | EQ | 500 | 0.002835 | south | 0.022926 | 0.0065877 | -0.25541 | 0.013258 | 0.0065877 | south | N | 0.0065877 | 0
86107 | CUF-138 | EQ | 0 | 0.002835 | south | 0.022926 | 0.0065877 | -0.25541 | 0.013258 | 0.0065877 | south | N | 0.0065877 | 0
88198 | BEEVILLE | F | 0 | -0.002611 | south | 0.01748 | 0.0011417 | -0.26086 | 0.0078121 | 0.0011417 | south | N | 0.0011417 | 0
88253 | HAMILTON | F | 0 | 0.066155 | south | 0.086246 | 0.069908 | -0.19209 | 0.076578 | 0.069908 | south | N | 0.069908 | 0
88299 | ZAPATA | F | 0 | 0.000805 | south | 0.020896 | 0.0045577 | -0.25744 | 0.011228 | 0.0045577 | south | N | 0.0045577 | 0
88508 | FALFURRI | F | 0 | -0.002435 | south | 0.017656 | 0.0013177 | -0.26068 | 0.0079881 | 0.0013177 | south | N | 0.0013177 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:COOKFIELD / LONGCREEK - GRAHAM8 [1430 - 1442] and [1430 - 1435] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.38029 | west | 6 | Y | N | Ywest | Nwest | 1 | 79.4812 | 209 | 0.40146 | 83.905 | 209 | 83.905
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.38029 | west | 6 | Y | N | Ywest | Nwest | 1 | 48.1071 | 126.5 | 0.40146 | 50.7846 | 335.5 | 134.6896
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.38029 | west | 6 | Y | N | Ywest | Nwest | 1 | 94.693 | 249 | 0.40146 | 99.9634 | 584.5 | 234.653
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.38029 | west | 6 | Y | N | Ywest | Nwest | 1 | 74.9177 | 197 | 0.40146 | 79.0875 | 781.5 | 313.7404 | Weighted Shift Factors
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.066155 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.1831 | 0 | -0.19209 | 0 | 781.5 | 313.7404 | west | 0.25825
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.066155 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.6539 | 0 | -0.19209 | 0 | 781.5 | 313.7404 | north | -0.021166
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.066155 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19209 | 0 | 781.5 | 313.7404 |  | 0.27941
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.047167 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.283 | 0 | -0.21108 | 0 | 781.5 | 313.7404
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.04275 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.2155 | 0 | 781.5 | 313.7404 | Line Rating | 1340
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 789.9 | 311.6401 | Conc Gen | 2593.1
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 798.3 | 309.5399 | Weighted Imp. | 313.7404
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 806.7 | 307.4396 | PTDF | 0.12099
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 815.1 | 305.3393
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 823.5 | 303.239 | Concentration | 0.43301
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 831.9 | 301.1387
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 840.3 | 299.0384
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 848.7 | 296.9381
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 857.1 | 294.8379
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 865.5 | 292.7376
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 873.9 | 290.6373
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 882.3 | 288.537
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 890.7 | 286.4367
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 899.1 | 284.3364
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 907.5 | 282.2361
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 915.9 | 280.1358
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 924.3 | 278.0356
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 932.7 | 275.9353
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 941.1 | 273.835
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 949.5 | 271.7347
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 957.9 | 269.6344
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 966.3 | 267.5341
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 974.7 | 265.4338
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003 | 983.1 | 263.3336
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.007118 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.097517 | 0 | -0.25113 | 0 | 983.1 | 263.3336
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.006406 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.15374 | 24 | -0.25184 | -6.0442 | 1007.1 | 257.2893
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.006406 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.15374 | 24 | -0.25184 | -6.0442 | 1031.1 | 251.2451
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.006406 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.14734 | 23 | -0.25184 | -5.7924 | 1054.1 | 245.4528
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.004468 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.080424 | 0 | -0.25378 | 0 | 1054.1 | 245.4528
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.004468 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.080424 | 0 | -0.25378 | 0 | 1054.1 | 245.4528
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.004468 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.06702 | 0 | -0.25378 | 0 | 1054.1 | 245.4528
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.004241 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7897 | 422 | -0.25401 | -107.191 | 1476.1 | 138.2618
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.003673 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10284 | 0 | -0.25458 | 0 | 1476.1 | 138.2618
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.003673 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10652 | 0 | -0.25458 | 0 | 1476.1 | 138.2618
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002839 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25541 | 0 | 1476.1 | 138.2618
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002835 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2835 | 100 | -0.25541 | -25.5413 | 1576.1 | 112.7204
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002835 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2835 | 100 | -0.25541 | -25.5413 | 1676.1 | 87.1791
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002835 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25541 | 0 | 1676.1 | 87.1791
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002835 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25541 | 0 | 1676.1 | 87.1791
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002835 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25541 | 0 | 1676.1 | 87.1791
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002835 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25541 | 0 | 1676.1 | 87.1791
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.002043 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.036774 | 0 | -0.25621 | 0 | 1676.1 | 87.1791
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.002043 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.036774 | 0 | -0.25621 | 0 | 1676.1 | 87.1791
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.000805 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25744 | 0 | 1676.1 | 87.1791
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25825 | 0 | 1676.1 | 87.1791
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25825 | 0 | 1676.1 | 87.1791
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25825 | 0 | 1676.1 | 87.1791
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25825 | 0 | 1676.1 | 87.1791
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25825 | 0 | 1676.1 | 87.1791
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25825 | 0 | 1676.1 | 87.1791
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25825 | 0 | 1676.1 | 87.1791
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25825 | 0 | 1676.1 | 87.1791
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.000968 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.011616 | 0 | -0.25922 | 0 | 1676.1 | 87.1791
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.000968 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010648 | 0 | -0.25922 | 0 | 1676.1 | 87.1791
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.000968 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.011616 | 0 | -0.25922 | 0 | 1676.1 | 87.1791
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.19289 | 114 | -0.25994 | -29.6332 | 1790.1 | 57.546
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.37562 | 222 | -0.25994 | -57.7067 | 2012.1 | 0.16075
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.31133 | 184 | -0.25994 | -47.829 | 2196.1 | 47.9897
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.37901 | 224 | -0.25994 | -58.2266 | 2420.1 | 106.2163
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.19458 | 115 | -0.25994 | -29.8931 | 2535.1 | 136.1094
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.00187 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.10846 | 58 | -0.26012 | -15.0869 | 2593.1 | 151.1963
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.00187 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.16643 | 89 | -0.26012 | -23.1505
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.00187 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08228 | 44 | -0.26012 | -11.4452
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.00187 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08228 | 44 | -0.26012 | -11.4452
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.00187 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08041 | 43 | -0.26012 | -11.1851
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.00187 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08415 | 45 | -0.26012 | -11.7053
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.2968 | west | 6 | Y | N | Ywest | Nwest | 1 | 44.5204 | 150 | 0.31797 | 47.6954
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.2968 | west | 6 | Y | N | Ywest | Nwest | 1 | 65.2967 | 220 | 0.31797 | 69.9532
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.2968 | west | 6 | Y | N | Ywest | Nwest | 1 | 59.3606 | 200 | 0.31797 | 63.5939
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.2968 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.1803 | 121.9 | 0.31797 | 38.7605
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.002294 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.93366 | 407 | -0.26054 | -106.0406
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.002331 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.92308 | 396 | -0.26058 | -103.1893
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.002434 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.50871 | 209 | -0.26068 | -54.4826
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.002434 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.52574 | 216 | -0.26068 | -56.3073
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.002434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.11196 | 46 | -0.26068 | -11.9914
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.002434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1144 | 47 | -0.26068 | -12.2521
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.002434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.11196 | 46 | -0.26068 | -11.9914
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.002434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.11196 | 46 | -0.26068 | -11.9914
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.002435 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.26068 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.002437 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.004 | 412 | -0.26069 | -107.4023
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.002437 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.9748 | 400 | -0.26069 | -104.274
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.002513 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.0655 | 424 | -0.26076 | -110.5627
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.002513 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.068 | 425 | -0.26076 | -110.8235
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.002611 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.26086 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.002819 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.26107 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.002819 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.26107 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.002819 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.26107 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.002822 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.41342 | 146.5 | -0.26107 | -38.2468
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.002822 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.41737 | 147.9 | -0.26107 | -38.6123
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.002822 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.48821 | 173 | -0.26107 | -45.1651
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.002915 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.45182 | 155 | -0.26116 | -40.4803
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.002915 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.49555 | 170 | -0.26116 | -44.3977
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.002915 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.45182 | 155 | -0.26116 | -40.4803
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.002943 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.103 | 0 | -0.26119 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.002943 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10006 | 0 | -0.26119 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.002943 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.103 | 0 | -0.26119 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.003048 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.6642 | 546 | -0.2613 | -142.6677
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.003048 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.286 | 750 | -0.2613 | -195.9721
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.00313 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64791 | 207 | -0.26138 | -54.1053
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.00313 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.67827 | 216.7 | -0.26138 | -56.6406
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.00313 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.75746 | 242 | -0.26138 | -63.2535
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.003131 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.45086 | 144 | -0.26138 | -37.6386
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.003131 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.45086 | 144 | -0.26138 | -37.6386
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.003131 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.5354 | 171 | -0.26138 | -44.6958
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.003316 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.26156 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.003316 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.12601 | 38 | -0.26156 | -9.9394
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.003316 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.063999 | 19.3 | -0.26156 | -5.0482
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.003316 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.04974 | 15 | -0.26156 | -3.9235
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.003316 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.15585 | 47 | -0.26156 | -12.2935
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.31857 | 94 | -0.26164 | -24.5939
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.13895 | 41 | -0.26164 | -10.7271
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.12878 | 38 | -0.26164 | -9.9422
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.064391 | 19 | -0.26164 | -4.9711
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.31857 | 94 | -0.26164 | -24.5939
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.122 | 36 | -0.26164 | -9.4189
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.14573 | 43 | -0.26164 | -11.2504
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.074558 | 22 | -0.26164 | -5.756
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.50157 | 148 | -0.26164 | -38.7223
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.16945 | 50 | -0.26164 | -13.0819
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.1864 | 55 | -0.26164 | -14.39
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.16945 | 50 | -0.26164 | -13.0819
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.29556 | west | 8 | N | N | Nwest | Nwest | 1 | 20.6888 | 0 | 0.31672 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.29556 | west | 8 | N | N | Nwest | Nwest | 1 | 21.6937 | 0 | 0.31672 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.29556 | west | 8 | N | N | Nwest | Nwest | 1 | 20.8071 | 0 | 0.31672 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.003477 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10083 | 0 | -0.26173 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.003569 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.014276 | 0 | -0.26182 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.00357 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.13566 | 0 | -0.26182 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.003591 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.13646 | 0 | -0.26184 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.003593 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.089825 | 0 | -0.26184 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.003593 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.089825 | 0 | -0.26184 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.003615 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2074 | 334 | -0.26186 | -87.4623
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.003615 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2291 | 340 | -0.26186 | -89.0335
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.003615 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.6507 | 180 | -0.26186 | -47.1354
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.003615 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.6507 | 180 | -0.26186 | -47.1354
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.003645 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.6561 | 180 | -0.26189 | -47.1408
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.003648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.541 | 0 | -0.2619 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.003648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.54209 | 0 | -0.2619 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.003648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.55814 | 0 | -0.2619 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.00365 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.2264 | 336 | -0.2619 | -87.9978
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.00365 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.657 | 180 | -0.2619 | -47.1417
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.003677 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.3128 | 629 | -0.26193 | -164.7509
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.003686 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.022116 | 0 | -0.26193 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.54463 | 147 | -0.26195 | -38.5071
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.51129 | 138 | -0.26195 | -36.1495
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.5187 | 140 | -0.26195 | -36.6734
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.54463 | 147 | -0.26195 | -38.5071
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.67431 | 182 | -0.26195 | -47.6755
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.73359 | 198 | -0.26195 | -51.8667
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.093825 | 25 | -0.262 | -6.55
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.093825 | 25 | -0.262 | -6.55
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.093825 | 25 | -0.262 | -6.55
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.060048 | 16 | -0.262 | -4.192
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.093825 | 25 | -0.262 | -6.55
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.093825 | 25 | -0.262 | -6.55
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.093825 | 25 | -0.262 | -6.55
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.056295 | 15 | -0.262 | -3.93
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.60498 | 0 | -0.26208 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.58584 | 0 | -0.26208 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.3829 | 0 | -0.26208 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.5552 | 0 | -0.26208 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.56286 | 0 | -0.26208 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.48628 | 0 | -0.26208 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.003829 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.045948 | 0 | -0.26208 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.00395 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00948 | 0 | -0.2622 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.00395 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00948 | 0 | -0.2622 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.00395 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.01106 | 0 | -0.2622 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.00395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.5609 | 142 | -0.2622 | -37.2321
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.00395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.57275 | 145 | -0.2622 | -38.0187
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.00395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.59645 | 151 | -0.2622 | -39.5919
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.00395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1455 | 290 | -0.2622 | -76.0375
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.004191 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.93836 | 223.9 | -0.26244 | -58.7601
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.004191 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.94298 | 225 | -0.26244 | -59.0488
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.004191 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.9413 | 224.6 | -0.26244 | -58.9438
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.004191 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.9501 | 226.7 | -0.26244 | -59.4949
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.004198 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.092356 | 22 | -0.26245 | -5.7738
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.004198 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.046178 | 11 | -0.26245 | -2.8869
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.004198 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.046178 | 11 | -0.26245 | -2.8869
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.004313 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.051756 | 0 | -0.26256 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.004325 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.01038 | 0 | -0.26257 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.004325 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.01038 | 0 | -0.26257 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.004371 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.2085 | 47.7 | -0.26262 | -12.5269
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.004371 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.16304 | 37.3 | -0.26262 | -9.7957
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.004371 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.20107 | 46 | -0.26262 | -12.0805
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.004371 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.20981 | 48 | -0.26262 | -12.6057
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.004449 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64066 | 144 | -0.2627 | -37.8284
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.004449 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.83641 | 188 | -0.2627 | -49.3871
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.004539 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.33135 | 0 | -0.26279 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.004658 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.06987 | 0 | -0.26291 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.004658 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10713 | 0 | -0.26291 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.004684 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.037472 | 0 | -0.26293 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.13292 | 0 | -0.263 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.033229 | 0 | -0.263 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.18513 | 0 | -0.263 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.071205 | 0 | -0.263 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.033229 | 0 | -0.263 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.071205 | 0 | -0.263 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.18513 | 0 | -0.263 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.18513 | 0 | -0.263 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.005075 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.2436 | 0 | -0.26332 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.40788 | 0 | -0.26341 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.4182 | 0 | -0.26341 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.40788 | 0 | -0.26341 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.41304 | 0 | -0.26341 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.40478 | 0 | -0.26341 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12907 | 0 | -0.26341 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.2375 | 0 | -0.26341 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14456 | 0 | -0.26341 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.22511 | 0 | -0.26341 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.38206 | 0 | -0.26341 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.005179 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.041432 | 0 | -0.26343 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.005179 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.041432 | 0 | -0.26343 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.26122 | 49 | -0.26358 | -12.9154
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.24523 | 46 | -0.26358 | -12.1246
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.24523 | 46 | -0.26358 | -12.1246
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.25056 | 47 | -0.26358 | -12.3882
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.005331 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.82097 | 154 | -0.26358 | -40.5912
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.005331 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.78899 | 148 | -0.26358 | -39.0097
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.25589 | 48 | -0.26358 | -12.6518
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.25589 | 48 | -0.26358 | -12.6518
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.005392 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.6715 | 310 | -0.26364 | -81.7284
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.005392 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2269 | 413 | -0.26364 | -108.8834
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.005576 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.23419 | 42 | -0.26382 | -11.0806
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.005576 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.24534 | 44 | -0.26382 | -11.6083
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.005576 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.24534 | 44 | -0.26382 | -11.6083
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.005576 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.26207 | 47 | -0.26382 | -12.3997
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.005998 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.79174 | 132 | -0.26425 | -34.8805
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.005998 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.80373 | 134 | -0.26425 | -35.409
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.005998 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.9374 | 323 | -0.26425 | -85.3515
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.006006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.91592 | 152.5 | -0.26425 | -40.2988
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.006006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.8979 | 149.5 | -0.26425 | -39.506
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.006006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.397 | 232.6 | -0.26425 | -61.4655
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.006291 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.31455 | 50 | -0.26454 | -13.227
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.006291 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.31455 | 50 | -0.26454 | -13.227
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.006291 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.31455 | 50 | -0.26454 | -13.227
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.006291 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.31455 | 50 | -0.26454 | -13.227
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.00644 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0175 | 158 | -0.26469 | -41.8207
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.00644 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0304 | 160 | -0.26469 | -42.3501
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.00644 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.127 | 175 | -0.26469 | -46.3204
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.006475 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.8037 | 433 | -0.26472 | -114.6251
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.006477 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -3.7826 | 584 | -0.26473 | -154.5995
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.006477 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -3.8538 | 595 | -0.26473 | -157.5114
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 1 | 20.3927 | 70 | 0.31249 | 21.8743
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 1 | 20.3927 | 70 | 0.31249 | 21.8743
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 1 | 27.0349 | 92.8 | 0.31249 | 28.9991
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 1 | 23.3059 | 80 | 0.31249 | 24.9992
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 1 | 23.3059 | 80 | 0.31249 | 24.9992
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 1 | 33.5023 | 115 | 0.31249 | 35.9364
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 1 | 60.6412 | 208.2 | 0.31243 | 65.048
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 1 | 41.3886 | 142.1 | 0.31243 | 44.3963
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 1 | 38.5634 | 132.4 | 0.31243 | 41.3658
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 1 | 39.6119 | 136 | 0.31243 | 42.4905
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 1 | 42.8158 | 147 | 0.31243 | 45.9273
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 1 | 61.1654 | 210 | 0.31243 | 65.6104
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.008154 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -10.8693 | 0 | -0.2664 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.008154 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -10.8285 | 0 | -0.2664 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.29072 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.3399 | 125 | 0.31189 | 38.9857
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.29072 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.3399 | 125 | 0.31189 | 38.9857
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.62996 | 76 | -0.26654 | -20.2568
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.62996 | 76 | -0.26654 | -20.2568
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.87035 | 105 | -0.26654 | -27.9864
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.61339 | 74 | -0.26654 | -19.7237
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.61339 | 74 | -0.26654 | -19.7237
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.84548 | 102 | -0.26654 | -27.1868
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.008403 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.5546 | 66 | -0.26665 | -17.599
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.008509 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -4.8416 | 569 | -0.26676 | -151.7848
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.008509 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -4.9437 | 581 | -0.26676 | -154.9859
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56749 | 0 | -0.2674 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65352 | 0 | -0.2674 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41189 | 0 | -0.2674 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92445 | 0 | -0.2674 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.78716 | 0 | -0.2674 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.80546 | 0 | -0.2674 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45765 | 0 | -0.2674 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16475 | 0 | -0.2674 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86038 | 0 | -0.2674 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64071 | 0 | -0.2674 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.57664 | 0 | -0.2674 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65902 | 0 | -0.2674 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59311 | 0 | -0.2674 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92445 | 0 | -0.2674 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88784 | 0 | -0.2674 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.94276 | 0 | -0.2674 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69563 | 0 | -0.2674 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73224 | 0 | -0.2674 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73224 | 0 | -0.2674 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5652 | 0 | -0.2674 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.009332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66257 | 0 | -0.26758 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.009332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09332 | 0 | -0.26758 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0527 | 0 | -0.26773 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0527 | 0 | -0.26773 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.009484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1286 | 0 | -0.26773 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.009484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0385 | 0 | -0.26773 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.009973 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45976 | 0 | -0.26822 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.010022 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -6.5243 | 651 | -0.26827 | -174.6438
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.010022 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.6524 | 564 | -0.26827 | -151.3043
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.010022 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -6.0132 | 600 | -0.26827 | -160.9621
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.010026 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6342 | 0 | -0.26827 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.010026 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6342 | 0 | -0.26827 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.010026 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4564 | 0 | -0.26827 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.010046 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.33152 | 0 | -0.26829 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.010118 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.629 | 161 | -0.26837 | -43.2069
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.010118 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.6796 | 166 | -0.26837 | -44.5488
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.010118 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.5093 | 248 | -0.26837 | -66.5548
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.010118 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -5.5244 | 546 | -0.26837 | -146.5279
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.010118 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -6.5059 | 0 | -0.26837 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.010118 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13153 | 13 | -0.26837 | -3.4888
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.010325 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0356 | 0 | -0.26857 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.010325 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.95919 | 0 | -0.26857 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.010325 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0604 | 0 | -0.26857 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.010325 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0532 | 0 | -0.26857 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.010325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3304 | 0 | -0.26857 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.010325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30975 | 0 | -0.26857 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.010327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73115 | 0 | -0.26858 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.010327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68881 | 0 | -0.26858 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.010327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.54733 | 0 | -0.26858 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5821 | 0 | -0.26858 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5852 | 0 | -0.26858 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5728 | 0 | -0.26858 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.99139 | 0 | -0.26858 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5198 | 0 | -0.26858 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.010327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41308 | 0 | -0.26858 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.010444 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.5222 | 50 | -0.26869 | -13.4346
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.010509 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.26876 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.96487 | 0 | -0.26885 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92882 | 0 | -0.26885 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92246 | 0 | -0.26885 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.57786 | 0 | -0.26885 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12936 | 0 | -0.26885 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.010639 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.69154 | 0 | -0.26889 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.010639 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.63834 | 0 | -0.26889 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.010639 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.69154 | 0 | -0.26889 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.010639 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.69154 | 0 | -0.26889 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.49234 | 46 | -0.26895 | -12.3718
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.49234 | 46 | -0.26895 | -12.3718
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.49234 | 46 | -0.26895 | -12.3718
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.58866 | 55 | -0.26895 | -14.7923
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.58866 | 55 | -0.26895 | -14.7923
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.57796 | 54 | -0.26895 | -14.5234
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.010707 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.83515 | 0 | -0.26896 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.010707 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.85656 | 0 | -0.26896 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7498 | 0 | -0.26897 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6844 | 0 | -0.26897 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6887 | 0 | -0.26897 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6834 | 0 | -0.26897 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8842 | 0 | -0.26897 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.010742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37597 | 0 | -0.26899 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.010757 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12908 | 12 | -0.26901 | -3.2281
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.010757 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.26901 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.010758 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.8181 | 169 | -0.26901 | -45.462
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.01076 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.7754 | 165 | -0.26901 | -44.3863
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.010761 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6034 | 0 | -0.26901 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.010761 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70054 | 0 | -0.26901 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.010764 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.2927 | 213 | -0.26901 | -57.2996
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.010764 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17438 | 0 | -0.26901 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.010765 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68896 | 0 | -0.26901 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.010765 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68035 | 0 | -0.26901 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.010765 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88919 | 0 | -0.26901 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.010765 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.7923 | 0 | -0.26901 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.010765 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.4544 | 228 | -0.26901 | -61.335
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.010766 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9379 | 0 | -0.26901 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.010766 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7075 | 0 | -0.26901 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.010766 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6903 | 0 | -0.26901 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.010789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.76602 | 0 | -0.26904 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.010789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.77681 | 0 | -0.26904 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.010789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42077 | 0 | -0.26904 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.010789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32367 | 0 | -0.26904 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.010827 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.45473 | 42 | -0.26908 | -11.3012
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.010827 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.45473 | 42 | -0.26908 | -11.3012
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.010827 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.41143 | 38 | -0.26908 | -10.2249
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.010827 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.41143 | 38 | -0.26908 | -10.2249
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.010829 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4727 | 0 | -0.26908 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.010841 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8755 | 0 | -0.26909 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.010841 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4635 | 0 | -0.26909 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1341 | 104 | -0.26915 | -27.9919
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1341 | 104 | -0.26915 | -27.9919
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.58887 | 54 | -0.26915 | -14.5343
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.57796 | 53 | -0.26915 | -14.2651
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.58887 | 54 | -0.26915 | -14.5343
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.62159 | 57 | -0.26915 | -15.3417
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.58887 | 54 | -0.26915 | -14.5343
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.58887 | 54 | -0.26915 | -14.5343
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.63249 | 58 | -0.26915 | -15.6109
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.63249 | 58 | -0.26915 | -15.6109
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.010916 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -8.0233 | 735 | -0.26916 | -197.8356
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37165 | 0 | -0.26918 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37931 | 0 | -0.26918 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35744 | 0 | -0.26918 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50173 | 0 | -0.26918 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19348 | 0 | -0.26918 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22299 | 0 | -0.26918 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21753 | 0 | -0.26918 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38259 | 0 | -0.26918 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19676 | 0 | -0.26918 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.93351 | 0 | -0.26918 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6178 | 0 | -0.26918 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.010959 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13151 | 12 | -0.26921 | -3.2305
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.010975 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.054875 | 0 | -0.26922 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.010975 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23048 | 0 | -0.26922 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71344 | 0 | -0.26922 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72442 | 0 | -0.26922 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.76832 | 0 | -0.26922 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69149 | 0 | -0.26922 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68051 | 0 | -0.26922 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1415 | 0 | -0.26922 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64758 | 0 | -0.26922 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.010976 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.13171 | 12 | -0.26922 | -3.2307
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.010977 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -8.1559 | 743 | -0.26923 | -200.0343
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.01099 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7254 | 0 | -0.26924 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.010994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.891 | 172 | -0.26924 | -46.3096
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.010994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.891 | 172 | -0.26924 | -46.3096
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.010994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.891 | 172 | -0.26924 | -46.3096
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.011037 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7968 | 0 | -0.26929 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.011037 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7814 | 0 | -0.26929 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.011037 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7538 | 0 | -0.26929 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.011037 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9712 | 0 | -0.26929 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.011056 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.4003 | 398 | -0.2693 | -107.183
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.6207 | 56 | -0.26933 | -15.0826
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.65396 | 59 | -0.26933 | -15.8906
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.6207 | 56 | -0.26933 | -15.0826
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.6207 | 56 | -0.26933 | -15.0826
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.65396 | 59 | -0.26933 | -15.8906
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.6207 | 56 | -0.26933 | -15.0826
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.011333 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9606 | 0 | -0.26958 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.011333 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7679 | 0 | -0.26958 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.011333 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7453 | 0 | -0.26958 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.011333 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7453 | 0 | -0.26958 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.011333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8359 | 0 | -0.26958 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 1 | 18.828 | 66 | 0.30644 | 20.225
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.6838 | 69 | 0.30644 | 21.1443
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.6838 | 69 | 0.30644 | 21.1443
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.1133 | 67 | 0.30644 | 20.5314
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.1133 | 67 | 0.30644 | 20.5314
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 1 | 18.5427 | 65 | 0.30644 | 19.9186
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 1 | 18.8261 | 66 | 0.30641 | 20.2231
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 1 | 18.5409 | 65 | 0.30641 | 19.9167
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.1113 | 67 | 0.30641 | 20.5295
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.1113 | 67 | 0.30641 | 20.5295
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.1113 | 67 | 0.30641 | 20.5295
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.28524 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30641 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.28524 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30641 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.28476 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9666 | 35 | 0.30593 | 10.7075
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.28476 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5428 | 30 | 0.30593 | 9.1778
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.28473 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.6158 | 100.5 | 0.3059 | 30.743
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.28465 | west | 6 | Y | N | Ywest | Nwest | 1 | 60.972 | 214.2 | 0.30582 | 65.5058
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.28455 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.5038 | 58 | 0.30572 | 17.7315
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.28396 | west | 6 | Y | N | Ywest | Nwest | 1 | 42.3094 | 149 | 0.30512 | 45.4632
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.27887 | west | 6 | Y | N | Ywest | Nwest | 1 | 33.4646 | 120 | 0.30004 | 36.0046
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.27751 | west | 6 | Y | N | Ywest | Nwest | 1 | 33.3011 | 120 | 0.29868 | 35.841
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.27614 | west | 8 | N | N | Nwest | Nwest | 1 | 7.1245 | 0 | 0.29731 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.27444 | west | 6 | Y | N | Ywest | Nwest | 1 | 61.7492 | 225 | 0.29561 | 66.5116
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.27404 | west | 6 | Y | N | Ywest | Nwest | 1 | 49.3276 | 180 | 0.29521 | 53.1375
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.27404 | west | 6 | Y | N | Ywest | Nwest | 1 | 49.3276 | 180 | 0.29521 | 53.1375
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.27075 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.0571 | 63 | 0.29191 | 18.3905
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.26998 | west | #N/A | N | N | Nwest | Nwest | 1 | 1.2959 | 0 | 0.29115 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.2678 | west | 6 | Y | N | Ywest | Nwest | 1 | 37.7591 | 141 | 0.28896 | 40.7435
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.2678 | west | 6 | Y | N | Ywest | Nwest | 1 | 32.1354 | 120 | 0.28896 | 34.6754
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.26733 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.4656 | 99 | 0.2885 | 28.561
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.26733 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.3071 | 61 | 0.2885 | 17.5982
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.26733 | west | 7 | N | N | Nwest | Nwest | 1 | 6.6832 | 0 | 0.2885 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.26733 | west | 7 | N | N | Nwest | Nwest | 1 | 12.2169 | 0 | 0.2885 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.26733 | west | 7 | N | N | Nwest | Nwest | 1 | 12.2169 | 0 | 0.2885 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.26683 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7611 | 6.6 | 0.28799 | 1.9008
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.26683 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1522 | 34.3 | 0.28799 | 9.8782
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.26336 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.0689 | 80 | 0.28453 | 22.7622
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.26336 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.0689 | 80 | 0.28453 | 22.7622
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.26217 | west | 6 | Y | N | Ywest | Nwest | 1 | 39.3259 | 150 | 0.28334 | 42.5009
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.26188 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.6413 | 75 | 0.28305 | 21.2288
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.26188 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9507 | 80 | 0.28305 | 22.644
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.26188 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.4754 | 40 | 0.28305 | 11.322
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.2616 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9278 | 80 | 0.28276 | 22.6211
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.26155 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9239 | 80 | 0.28272 | 22.6172
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.26133 | west | 6 | Y | N | Ywest | Nwest | 1 | 39.2 | 150 | 0.2825 | 42.3749
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.26133 | west | 6 | Y | N | Ywest | Nwest | 1 | 39.2 | 150 | 0.2825 | 42.3749
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.689 | 37.5 | 0.27954 | 10.4827
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.7751 | 107.5 | 0.27954 | 30.0505
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 1 | 34.8804 | 135 | 0.27954 | 37.7378
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.7464 | 119 | 0.27954 | 33.2652
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.1292 | 105 | 0.27954 | 29.3516
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.799 | 80.5 | 0.27954 | 22.5029
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.25745 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.6256 | 84 | 0.27861 | 23.4036
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.25514 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.7029 | 112.5 | 0.2763 | 31.0841
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.25514 | west | 6 | Y | N | Ywest | Nwest | 1 | 38.143 | 149.5 | 0.2763 | 41.3073
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.25514 | west | 6 | Y | N | Ywest | Nwest | 1 | 47.4555 | 186 | 0.2763 | 51.3924
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.25514 | west | 6 | Y | N | Ywest | Nwest | 1 | 54.7269 | 214.5 | 0.2763 | 59.2671
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.25359 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.2873 | 80 | 0.27476 | 21.9806
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.25098 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.0822 | 84 | 0.27214 | 22.8601
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.25093 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.196 | 76.5 | 0.27209 | 20.8152
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.23376 | west | 6 | Y | N | Ywest | Nwest | 1 | 55.1667 | 236 | 0.25492 | 60.1619
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.23376 | west | 6 | Y | N | Ywest | Nwest | 1 | 38.5699 | 165 | 0.25492 | 42.0623
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.23362 | west | 6 | Y | N | Ywest | Nwest | 1 | 93.4468 | 400 | 0.25478 | 101.9133
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.22877 | west | 6 | Y | N | Ywest | Nwest | 1 | 34.315 | 150 | 0.24993 | 37.49
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.22877 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.1055 | 101 | 0.24993 | 25.2433
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.21411 | west | 6 | Y | N | Ywest | Nwest | 1 | 32.1159 | 150 | 0.23527 | 35.2908
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.21005 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.23121 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.20724 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.8686 | 120 | 0.2284 | 27.4085
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.20724 | west | 6 | Y | N | Ywest | Nwest | 1 | 48.2865 | 233 | 0.2284 | 53.2182
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.20724 | west | 6 | Y | N | Ywest | Nwest | 1 | 35.2719 | 170.2 | 0.2284 | 38.8744
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.20374 | west | 6 | Y | N | Ywest | Nwest | 1 | 34.5339 | 169.5 | 0.22491 | 38.1216
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.16879 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.3183 | 150 | 0.18996 | 28.4933
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.168 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.0801 | 60 | 0.18917 | 11.3501
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.067866 | west | 4 | Y | N | Ywest | Nwest | 1 | 44.0925 | 649.7 | 0.089032 | 57.8443
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.064415 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.085581 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.019968 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.1981 | 60 | 0.041134 | 2.4681
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.021166 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.021166 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.1692 | 100 | 0.019474 | 1.9474
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.009415 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.68729 | 73 | 0.011751 | 0.85784
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.009415 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.1204 | 119 | 0.011751 | 1.3984
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.009415 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.9301 | 205 | 0.011751 | 2.409
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.009415 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.96033 | 102 | 0.011751 | 1.1986
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.009415 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.90384 | 96 | 0.011751 | 1.1281
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.011139 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.13367 | 0 | 0.010027 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.011139 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.13367 | 0 | 0.010027 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.012252 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.8378 | 150 | 0.0089143 | 1.3371
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.012252 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.98016 | 80 | 0.0089143 | 0.71314
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.012429 | north | 3 | N | N | Nnorth | Nnorth | 1 | -14.3804 | 0 | 0.0087373 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.012429 | north | 3 | N | N | Nnorth | Nnorth | 1 | -14.3928 | 0 | 0.0087373 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.012655 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.18982 | 0 | 0.0085113 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.012655 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.18982 | 0 | 0.0085113 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.012996 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.314 | 255 | 0.0081703 | 2.0834
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.012996 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.9364 | 149 | 0.0081703 | 1.2174
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.012996 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.9884 | 153 | 0.0081703 | 1.2501
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.013328 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0078383 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.013328 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0078383 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.013615 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9585 | 217.3 | 0.0075513 | 1.6409
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.013615 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7911 | 205 | 0.0075513 | 1.548
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.013615 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7087 | 272.4 | 0.0075513 | 2.057
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.013643 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.1038 | 0 | 0.0075233 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.013643 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.1283 | 0 | 0.0075233 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.013643 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.1283 | 0 | 0.0075233 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.013643 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.1843 | 0 | 0.0075233 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.013949 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0072173 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.013949 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.9779 | 787 | 0.0072173 | 5.68
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.013956 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.97692 | 70 | 0.0072103 | 0.50472
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.013956 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.96296 | 69 | 0.0072103 | 0.49751
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.013956 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.96296 | 69 | 0.0072103 | 0.49751
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.013956 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.94901 | 68 | 0.0072103 | 0.4903
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.014071 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.67541 | 48 | 0.0070953 | 0.34057
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.014071 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.64727 | 46 | 0.0070953 | 0.32638
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.014071 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4775 | 105 | 0.0070953 | 0.745
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.014101 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.45123 | 0 | 0.0070653 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.014111 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0070553 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.014111 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0070553 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.014111 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.23989 | 17 | 0.0070553 | 0.11994
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.014111 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0070553 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.014111 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0070553 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.014117 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -6.5362 | 463 | 0.0070493 | 3.2638
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.014641 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.4597 | 168 | 0.0065253 | 1.0962
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.014641 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.3177 | 90 | 0.0065253 | 0.58728
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.015678 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.4047 | 855 | 0.0054883 | 4.6925
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.015678 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.4047 | 855 | 0.0054883 | 4.6925
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.015678 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.3878 | 152.3 | 0.0054883 | 0.83587
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.015678 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.3987 | 153 | 0.0054883 | 0.83971
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.016304 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.4834 | 827 | 0.0048623 | 4.0211
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.016304 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.353 | 819 | 0.0048623 | 3.9822
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.016756 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.30161 | 18 | 0.0044103 | 0.079385
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.016756 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.30161 | 18 | 0.0044103 | 0.079385
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.016756 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.63673 | 38 | 0.0044103 | 0.16759
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.017429 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0037373 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.017621 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.1145 | 120 | 0.0035453 | 0.42543
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.018032 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -11.0897 | 615 | 0.0031343 | 1.9276
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.018032 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.5848 | 587 | 0.0031343 | 1.8398
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.018334 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7629 | 150.7 | 0.0028323 | 0.42682
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.018334 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7684 | 151 | 0.0028323 | 0.42767
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.018334 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2525 | 177.4 | 0.0028323 | 0.50245
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.018397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7871 | 151.5 | 0.0027693 | 0.41955
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.018397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.8019 | 152.3 | 0.0027693 | 0.42176
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.018397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2655 | 177.5 | 0.0027693 | 0.49155
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.018901 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.2338 | 224 | 0.0022653 | 0.50742
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.018901 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.2716 | 226 | 0.0022653 | 0.51195
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.018901 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.007 | 212 | 0.0022653 | 0.48024
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.018901 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.9881 | 211 | 0.0022653 | 0.47797
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.019172 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.2945 | 224 | 0.0019943 | 0.44672
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.019373 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7971 | 196 | 0.0017933 | 0.35148
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.019373 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.1504 | 111 | 0.0017933 | 0.19905
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.019813 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.2875 | 216.4 | 0.0013533 | 0.29285
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.019813 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.2816 | 216.1 | 0.0013533 | 0.29244
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.019881 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.6183 | 182 | 0.0012853 | 0.23392
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.019881 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.6224 | 484 | 0.0012853 | 0.62208
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.019913 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.99565 | 50 | 0.0012533 | 0.062664
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.01993 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.0012363 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.020081 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.972 | 0 | 0.0010853 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.020081 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.6105 | 0 | 0.0010853 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.020081 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.9117 | 0 | 0.0010853 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.020081 | north | 1 | N | N | Nnorth | Nnorth | 1 | -8.0123 | 0 | 0.0010853 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.020209 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.8202 | 288 | 0.00095728 | 0.2757
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.020209 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9707 | 147 | 0.00095728 | 0.14072
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.020209 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9707 | 147 | 0.00095728 | 0.14072
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.020259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.9033 | 785 | 0.00090728 | 0.71222
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.020259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -16.1059 | 795 | 0.00090728 | 0.72129
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.020259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.802 | 780 | 0.00090728 | 0.70768
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.020422 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.40844 | 20 | 0.00074428 | 0.014886
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.020422 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.40844 | 20 | 0.00074428 | 0.014886
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.020422 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.40844 | 20 | 0.00074428 | 0.014886
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.020422 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.34717 | 17 | 0.00074428 | 0.012653
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.021191 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.5005 | 118 | -2.4717e-05 | -0.0029167
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.021191 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.437 | 115 | -2.4717e-05 | -0.0028425
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.021191 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.7822 | 556 | -2.4717e-05 | -0.013743
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.021551 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.00038472 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.021551 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.00038472 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.4731 | 161 | -0.00040572 | -0.065321
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5378 | 164 | -0.00040572 | -0.066538
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5378 | 164 | -0.00040572 | -0.066538
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.9308 | 414 | -0.00040572 | -0.16797
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.4947 | 162 | -0.00040572 | -0.065726
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.4731 | 161 | -0.00040572 | -0.065321
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5162 | 163 | -0.00040572 | -0.066132
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.8229 | 409 | -0.00040572 | -0.16594
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.021676 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.4103 | 388 | -0.00050972 | -0.19777
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.021676 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.1631 | 515 | -0.00050972 | -0.2625
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.021833 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.2836 | 242 | -0.00066672 | -0.16135
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.022076 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.88304 | 40 | -0.00090972 | -0.036389
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.02208 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.4416 | 20 | -0.00091372 | -0.018274
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.02208 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.552 | 25 | -0.00091372 | -0.022843
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.02208 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.90528 | 41 | -0.00091372 | -0.037462
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.022167 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.7512 | 79 | -0.0010007 | -0.079057
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.022167 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.3497 | 106 | -0.0010007 | -0.10608
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.022167 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.2364 | 146 | -0.0010007 | -0.1461
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.022167 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6847 | 76 | -0.0010007 | -0.076055
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.022201 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -9.6574 | 435 | -0.0010347 | -0.4501
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.022239 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.7844 | 395 | -0.0010727 | -0.42372
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.022239 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -9.674 | 435 | -0.0010727 | -0.46663
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.022505 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.5578 | 558 | -0.0013387 | -0.747
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.022505 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.0304 | 579 | -0.0013387 | -0.77512
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.022505 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -18.184 | 808 | -0.0013387 | -1.0817
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.022542 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.536 | 112.5 | -0.0013757 | -0.15477
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.022572 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.6929 | 0 | -0.0014057 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.022572 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.7967 | 0 | -0.0014057 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.022572 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.9954 | 0 | -0.0014057 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.62 | 160 | -0.0014587 | -0.23339
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5295 | 156 | -0.0014587 | -0.22756
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.4345 | 196 | -0.0014587 | -0.28591
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5295 | 156 | -0.0014587 | -0.22756
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5521 | 157 | -0.0014587 | -0.22902
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.4798 | 198 | -0.0014587 | -0.28883
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.022695 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.3971 | 370 | -0.0015287 | -0.56563
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.1773 | 0 | -0.0015287 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2 | 0 | -0.0015287 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.0128 | 0 | -0.0015287 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2454 | 0 | -0.0015287 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2681 | 0 | -0.0015287 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.0354 | 0 | -0.0015287 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.022811 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.8779 | 170 | -0.0016447 | -0.2796
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.022811 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.8617 | 520 | -0.0016447 | -0.85525
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.022909 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.91636 | 0 | -0.0017427 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.022909 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.91636 | 0 | -0.0017427 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.022991 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0018247 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.023489 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0023227 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.025877 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0047107 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.025877 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0047107 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.025877 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0047107 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.02615 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.569 | 60 | -0.0049837 | -0.29902
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.02615 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.6475 | 63 | -0.0049837 | -0.31397
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.040332 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.2277 | 204 | -0.019166 | -3.9098
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.040332 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.1067 | 201 | -0.019166 | -3.8523
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.040332 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.7603 | 242 | -0.019166 | -4.6381
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.071097 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -26.0215 | 366 | -0.049931 | -18.2746

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: TONKAWA_ - GRHAMSES 345kV [1048 - 1430] C:COOKFIELD / LONGCREEK - GRAHAM8 [1430 - 1442] and [1430 - 1435] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.071097 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -26.0215 | 366 | -0.049931 | -18.2746 | 366 | 18.2746
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.040332 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.2277 | 204 | -0.019166 | -3.9098 | 570 | 22.1844
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.040332 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.1067 | 201 | -0.019166 | -3.8523 | 771 | 26.0368
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.040332 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -9.7603 | 242 | -0.019166 | -4.6381 | 1013 | 30.6749 | Weighted Shift Factors
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.02615 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.569 | 60 | -0.0049837 | -0.29902 | 1073 | 30.9739 | west | 0.25825
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.02615 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.6475 | 63 | -0.0049837 | -0.31397 | 1136 | 31.2879 | north | -0.021166
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.025877 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0047107 | 0 | 1136 | 31.2879 |  | 0.27941
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.025877 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0047107 | 0 | 1136 | 31.2879
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.025877 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0047107 | 0 | 1136 | 31.2879 | Line Rating | 1340
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.023489 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0023227 | 0 | 1136 | 31.2879 | Conc Gen | 2512
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.022991 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0018247 | 0 | 1136 | 31.2879 | Weighted Imp. | 33.4493
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.022909 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.91636 | 0 | -0.0017427 | 0 | 1136 | 31.2879 | PTDF | 0.013316
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.022909 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.91636 | 0 | -0.0017427 | 0 | 1136 | 31.2879
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.022811 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.8779 | 170 | -0.0016447 | -0.2796 | 1306 | 31.5675 | Concentration | 0.047656
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.022811 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.8617 | 520 | -0.0016447 | -0.85525 | 1826 | 32.4227
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.022695 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.3971 | 370 | -0.0015287 | -0.56563 | 2196 | 32.9883
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.1773 | 0 | -0.0015287 | 0 | 2196 | 32.9883
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2 | 0 | -0.0015287 | 0 | 2196 | 32.9883
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.0128 | 0 | -0.0015287 | 0 | 2196 | 32.9883
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2454 | 0 | -0.0015287 | 0 | 2196 | 32.9883
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | 1 | -3.2681 | 0 | -0.0015287 | 0 | 2196 | 32.9883
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.022695 | north | 1 | N | N | Nnorth | Nnorth | 1 | -7.0354 | 0 | -0.0015287 | 0 | 2196 | 32.9883
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.62 | 160 | -0.0014587 | -0.23339 | 2356 | 33.2217
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5295 | 156 | -0.0014587 | -0.22756 | 2512 | 33.4493
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.4345 | 196 | -0.0014587 | -0.28591
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5295 | 156 | -0.0014587 | -0.22756
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5521 | 157 | -0.0014587 | -0.22902
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.022625 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.4798 | 198 | -0.0014587 | -0.28883
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.022572 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.6929 | 0 | -0.0014057 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.022572 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.7967 | 0 | -0.0014057 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.022572 | north | 8 | N | N | Nnorth | Nnorth | 1 | -1.9954 | 0 | -0.0014057 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.022542 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.536 | 0 | -0.0013757 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.022505 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -12.5578 | 0 | -0.0013387 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.022505 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.0304 | 0 | -0.0013387 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.022505 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -18.184 | 0 | -0.0013387 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.022239 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.7844 | 395 | -0.0010727 | -0.42372
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.022239 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -9.674 | 435 | -0.0010727 | -0.46663
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.022201 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -9.6574 | 435 | -0.0010347 | -0.4501
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.022167 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.7512 | 79 | -0.0010007 | -0.079057
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.022167 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.3497 | 106 | -0.0010007 | -0.10608
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.022167 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -3.2364 | 146 | -0.0010007 | -0.1461
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.022167 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6847 | 76 | -0.0010007 | -0.076055
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.02208 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.4416 | 20 | -0.00091372 | -0.018274
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.02208 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.552 | 25 | -0.00091372 | -0.022843
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.02208 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.90528 | 41 | -0.00091372 | -0.037462
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.022076 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.88304 | 40 | -0.00090972 | -0.036389
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.021833 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.2836 | 242 | -0.00066672 | -0.16135
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.021676 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -8.4103 | 388 | -0.00050972 | -0.19777
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.021676 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.1631 | 515 | -0.00050972 | -0.2625
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.4731 | 161 | -0.00040572 | -0.065321
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5378 | 164 | -0.00040572 | -0.066538
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5378 | 164 | -0.00040572 | -0.066538
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.9308 | 414 | -0.00040572 | -0.16797
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.4947 | 162 | -0.00040572 | -0.065726
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.4731 | 161 | -0.00040572 | -0.065321
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.5162 | 163 | -0.00040572 | -0.066132
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.021572 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -8.8229 | 409 | -0.00040572 | -0.16594
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.021551 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.00038472 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.021551 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.00038472 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.021191 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -2.5005 | 118 | -2.4717e-05 | -0.0029167
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.021191 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -2.437 | 115 | -2.4717e-05 | -0.0028425
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.021191 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -11.7822 | 556 | -2.4717e-05 | -0.013743
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.020422 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.40844 | 20 | 0.00074428 | 0.014886
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.020422 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.40844 | 20 | 0.00074428 | 0.014886
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.020422 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.40844 | 20 | 0.00074428 | 0.014886
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.020422 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.34717 | 17 | 0.00074428 | 0.012653
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.020259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.9033 | 0 | 0.00090728 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.020259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -16.1059 | 0 | 0.00090728 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.020259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -15.802 | 0 | 0.00090728 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.020209 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -5.8202 | 288 | 0.00095728 | 0.2757
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.020209 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9707 | 147 | 0.00095728 | 0.14072
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.020209 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9707 | 147 | 0.00095728 | 0.14072
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.020081 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.972 | 0 | 0.0010853 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.020081 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.6105 | 0 | 0.0010853 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.020081 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.9117 | 0 | 0.0010853 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.020081 | north | 1 | N | N | Nnorth | Nnorth | 1 | -8.0123 | 0 | 0.0010853 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.01993 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.0012363 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.019913 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.99565 | 0 | 0.0012533 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.019881 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -3.6183 | 182 | 0.0012853 | 0.23392
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.019881 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.6224 | 484 | 0.0012853 | 0.62208
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.019813 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.2875 | 216.4 | 0.0013533 | 0.29285
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.019813 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.2816 | 216.1 | 0.0013533 | 0.29244
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.019373 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7971 | 196 | 0.0017933 | 0.35148
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.019373 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.1504 | 111 | 0.0017933 | 0.19905
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.019172 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.2945 | 224 | 0.0019943 | 0.44672
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.018901 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.2338 | 224 | 0.0022653 | 0.50742
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.018901 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.2716 | 226 | 0.0022653 | 0.51195
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.018901 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -4.007 | 212 | 0.0022653 | 0.48024
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.018901 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.9881 | 211 | 0.0022653 | 0.47797
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.018397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7871 | 151.5 | 0.0027693 | 0.41955
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.018397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.8019 | 152.3 | 0.0027693 | 0.42176
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.018397 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2655 | 177.5 | 0.0027693 | 0.49155
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.018334 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7629 | 150.7 | 0.0028323 | 0.42682
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.018334 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7684 | 151 | 0.0028323 | 0.42767
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.018334 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.2525 | 177.4 | 0.0028323 | 0.50245
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.018032 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -11.0897 | 0 | 0.0031343 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.018032 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -10.5848 | 0 | 0.0031343 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.017621 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.1145 | 0 | 0.0035453 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.017429 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0037373 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.016756 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.30161 | 18 | 0.0044103 | 0.079385
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.016756 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.30161 | 18 | 0.0044103 | 0.079385
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.016756 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.63673 | 38 | 0.0044103 | 0.16759
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.016304 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.4834 | 0 | 0.0048623 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.016304 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.353 | 0 | 0.0048623 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.015678 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.4047 | 0 | 0.0054883 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.015678 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -13.4047 | 0 | 0.0054883 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.015678 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.3878 | 0 | 0.0054883 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.015678 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -2.3987 | 0 | 0.0054883 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.014641 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.4597 | 168 | 0.0065253 | 1.0962
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.014641 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.3177 | 90 | 0.0065253 | 0.58728
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.014117 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -6.5362 | 0 | 0.0070493 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.014111 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0070553 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.014111 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0070553 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.014111 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.23989 | 17 | 0.0070553 | 0.11994
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.014111 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0070553 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.014111 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0070553 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.014101 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.45123 | 0 | 0.0070653 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.014071 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.67541 | 48 | 0.0070953 | 0.34057
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.014071 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.64727 | 46 | 0.0070953 | 0.32638
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.014071 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -1.4775 | 105 | 0.0070953 | 0.745
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.013956 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.97692 | 70 | 0.0072103 | 0.50472
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.013956 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.96296 | 69 | 0.0072103 | 0.49751
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.013956 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.96296 | 69 | 0.0072103 | 0.49751
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.013956 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.94901 | 68 | 0.0072103 | 0.4903
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.013949 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0072173 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.013949 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -10.9779 | 787 | 0.0072173 | 5.68
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.013643 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.1038 | 0 | 0.0075233 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.013643 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.1283 | 0 | 0.0075233 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.013643 | north | 1 | N | N | Nnorth | Nnorth | 1 | -2.1283 | 0 | 0.0075233 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.013643 | north | 1 | N | N | Nnorth | Nnorth | 1 | -5.1843 | 0 | 0.0075233 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.013615 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.9585 | 217.3 | 0.0075513 | 1.6409
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.013615 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7911 | 205 | 0.0075513 | 1.548
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.013615 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.7087 | 272.4 | 0.0075513 | 2.057
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.013328 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0078383 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.013328 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0078383 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.012996 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.314 | 255 | 0.0081703 | 2.0834
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.012996 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.9364 | 149 | 0.0081703 | 1.2174
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.012996 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.9884 | 153 | 0.0081703 | 1.2501
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.012655 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.18982 | 0 | 0.0085113 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.012655 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.18982 | 0 | 0.0085113 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.012429 | north | 3 | N | N | Nnorth | Nnorth | 1 | -14.3804 | 0 | 0.0087373 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.012429 | north | 3 | N | N | Nnorth | Nnorth | 1 | -14.3928 | 0 | 0.0087373 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.012252 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.8378 | 150 | 0.0089143 | 1.3371
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.012252 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.98016 | 80 | 0.0089143 | 0.71314
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.011139 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.13367 | 0 | 0.010027 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.011139 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.13367 | 0 | 0.010027 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.009415 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.68729 | 73 | 0.011751 | 0.85784
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.009415 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.1204 | 119 | 0.011751 | 1.3984
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.009415 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -1.9301 | 205 | 0.011751 | 2.409
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.009415 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.96033 | 102 | 0.011751 | 1.1986
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.009415 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.90384 | 96 | 0.011751 | 1.1281
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.1692 | 0 | 0.019474 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.021166 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.021166 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.019968 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.1981 | 0 | 0.041134 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.064415 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.085581 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.067866 | west | 4 | Y | N | Ywest | Nwest | 1 | 44.0925 | 0 | 0.089032 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.168 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.0801 | 0 | 0.18917 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.16879 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.3183 | 0 | 0.18996 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.20374 | west | 6 | Y | N | Ywest | Nwest | 1 | 34.5339 | 0 | 0.22491 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.20724 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.8686 | 0 | 0.2284 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.20724 | west | 6 | Y | N | Ywest | Nwest | 1 | 48.2865 | 0 | 0.2284 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.20724 | west | 6 | Y | N | Ywest | Nwest | 1 | 35.2719 | 0 | 0.2284 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.21005 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.23121 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.21411 | west | 6 | Y | N | Ywest | Nwest | 1 | 32.1159 | 0 | 0.23527 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.22877 | west | 6 | Y | N | Ywest | Nwest | 1 | 34.315 | 0 | 0.24993 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.22877 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.1055 | 0 | 0.24993 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.23362 | west | 6 | Y | N | Ywest | Nwest | 1 | 93.4468 | 0 | 0.25478 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.23376 | west | 6 | Y | N | Ywest | Nwest | 1 | 38.5699 | 0 | 0.25492 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.23376 | west | 6 | Y | N | Ywest | Nwest | 1 | 55.1667 | 0 | 0.25492 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.25093 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.196 | 0 | 0.27209 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.25098 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.0822 | 0 | 0.27214 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.25359 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.2873 | 0 | 0.27476 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.25514 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.7029 | 0 | 0.2763 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.25514 | west | 6 | Y | N | Ywest | Nwest | 1 | 38.143 | 0 | 0.2763 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.25514 | west | 6 | Y | N | Ywest | Nwest | 1 | 47.4555 | 0 | 0.2763 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.25514 | west | 6 | Y | N | Ywest | Nwest | 1 | 54.7269 | 0 | 0.2763 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.25745 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.6256 | 0 | 0.27861 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.689 | 0 | 0.27954 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.7751 | 0 | 0.27954 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 1 | 34.8804 | 0 | 0.27954 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 1 | 30.7464 | 0 | 0.27954 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.1292 | 0 | 0.27954 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.25837 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.799 | 0 | 0.27954 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.26133 | west | 6 | Y | N | Ywest | Nwest | 1 | 39.2 | 0 | 0.2825 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.26133 | west | 6 | Y | N | Ywest | Nwest | 1 | 39.2 | 0 | 0.2825 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.26155 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9239 | 0 | 0.28272 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.2616 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9278 | 0 | 0.28276 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.26188 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.6413 | 0 | 0.28305 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.26188 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.9507 | 0 | 0.28305 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.26188 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.4754 | 0 | 0.28305 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.26217 | west | 6 | Y | N | Ywest | Nwest | 1 | 39.3259 | 0 | 0.28334 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.26336 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.0689 | 0 | 0.28453 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.26336 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.0689 | 0 | 0.28453 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.26683 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7611 | 0 | 0.28799 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.26683 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1522 | 0 | 0.28799 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.26733 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.4656 | 0 | 0.2885 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.26733 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.3071 | 0 | 0.2885 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.26733 | west | 7 | N | N | Nwest | Nwest | 1 | 6.6832 | 0 | 0.2885 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.26733 | west | 7 | N | N | Nwest | Nwest | 1 | 12.2169 | 0 | 0.2885 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.26733 | west | 7 | N | N | Nwest | Nwest | 1 | 12.2169 | 0 | 0.2885 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.2678 | west | 6 | Y | N | Ywest | Nwest | 1 | 37.7591 | 0 | 0.28896 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.2678 | west | 6 | Y | N | Ywest | Nwest | 1 | 32.1354 | 0 | 0.28896 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.26998 | west | #N/A | N | N | Nwest | Nwest | 1 | 1.2959 | 0 | 0.29115 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.27075 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.0571 | 0 | 0.29191 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.27404 | west | 6 | Y | N | Ywest | Nwest | 1 | 49.3276 | 0 | 0.29521 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.27404 | west | 6 | Y | N | Ywest | Nwest | 1 | 49.3276 | 0 | 0.29521 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.27444 | west | 6 | Y | N | Ywest | Nwest | 1 | 61.7492 | 0 | 0.29561 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.27614 | west | 8 | N | N | Nwest | Nwest | 1 | 7.1245 | 0 | 0.29731 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.27751 | west | 6 | Y | N | Ywest | Nwest | 1 | 33.3011 | 0 | 0.29868 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.27887 | west | 6 | Y | N | Ywest | Nwest | 1 | 33.4646 | 0 | 0.30004 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.28396 | west | 6 | Y | N | Ywest | Nwest | 1 | 42.3094 | 0 | 0.30512 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.28455 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.5038 | 0 | 0.30572 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.28465 | west | 6 | Y | N | Ywest | Nwest | 1 | 60.972 | 0 | 0.30582 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.28473 | west | 6 | Y | N | Ywest | Nwest | 1 | 28.6158 | 0 | 0.3059 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.28476 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9666 | 0 | 0.30593 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.28476 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.5428 | 0 | 0.30593 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 1 | 18.8261 | 66 | 0.30641 | 20.2231
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 1 | 18.5409 | 65 | 0.30641 | 19.9167
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.1113 | 67 | 0.30641 | 20.5295
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.1113 | 67 | 0.30641 | 20.5295
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.28524 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.1113 | 67 | 0.30641 | 20.5295
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.28524 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30641 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.28524 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.30641 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 1 | 18.828 | 66 | 0.30644 | 20.225
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.6838 | 69 | 0.30644 | 21.1443
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.6838 | 69 | 0.30644 | 21.1443
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.1133 | 67 | 0.30644 | 20.5314
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 1 | 19.1133 | 67 | 0.30644 | 20.5314
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.28527 | west | 13 | Y | Y | Ywest | Ywest | 1 | 18.5427 | 65 | 0.30644 | 19.9186
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.011333 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9606 | 0 | -0.26958 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.011333 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7679 | 0 | -0.26958 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.011333 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7453 | 0 | -0.26958 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.011333 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7453 | 0 | -0.26958 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.011333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8359 | 0 | -0.26958 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.6207 | 56 | -0.26933 | -15.0826
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.65396 | 59 | -0.26933 | -15.8906
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.6207 | 56 | -0.26933 | -15.0826
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.6207 | 56 | -0.26933 | -15.0826
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.65396 | 59 | -0.26933 | -15.8906
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.011084 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.6207 | 56 | -0.26933 | -15.0826
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.011056 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.4003 | 398 | -0.2693 | -107.183
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.011037 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7968 | 0 | -0.26929 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.011037 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7814 | 0 | -0.26929 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.011037 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7538 | 0 | -0.26929 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.011037 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9712 | 0 | -0.26929 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.010994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.891 | 172 | -0.26924 | -46.3096
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.010994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.891 | 172 | -0.26924 | -46.3096
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.010994 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.891 | 172 | -0.26924 | -46.3096
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.01099 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7254 | 0 | -0.26924 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.010977 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -8.1559 | 743 | -0.26923 | -200.0343
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.010976 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.13171 | 0 | -0.26922 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71344 | 0 | -0.26922 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72442 | 0 | -0.26922 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.76832 | 0 | -0.26922 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69149 | 0 | -0.26922 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68051 | 0 | -0.26922 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1415 | 0 | -0.26922 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.010976 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64758 | 0 | -0.26922 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.010975 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.054875 | 0 | -0.26922 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.010975 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23048 | 0 | -0.26922 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.010959 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13151 | 12 | -0.26921 | -3.2305
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37165 | 0 | -0.26918 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37931 | 0 | -0.26918 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35744 | 0 | -0.26918 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50173 | 0 | -0.26918 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19348 | 0 | -0.26918 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22299 | 0 | -0.26918 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21753 | 0 | -0.26918 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38259 | 0 | -0.26918 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19676 | 0 | -0.26918 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.93351 | 0 | -0.26918 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.010931 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6178 | 0 | -0.26918 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.010916 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -8.0233 | 735 | -0.26916 | -197.8356
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1341 | 104 | -0.26915 | -27.9919
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1341 | 104 | -0.26915 | -27.9919
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.58887 | 54 | -0.26915 | -14.5343
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.57796 | 53 | -0.26915 | -14.2651
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.58887 | 54 | -0.26915 | -14.5343
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.62159 | 57 | -0.26915 | -15.3417
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.58887 | 54 | -0.26915 | -14.5343
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.58887 | 54 | -0.26915 | -14.5343
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.63249 | 58 | -0.26915 | -15.6109
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.010905 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.63249 | 58 | -0.26915 | -15.6109
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.010841 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8755 | 0 | -0.26909 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.010841 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4635 | 0 | -0.26909 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.010829 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4727 | 0 | -0.26908 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.010827 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.45473 | 42 | -0.26908 | -11.3012
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.010827 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.45473 | 42 | -0.26908 | -11.3012
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.010827 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.41143 | 38 | -0.26908 | -10.2249
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.010827 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.41143 | 38 | -0.26908 | -10.2249
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.010789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.76602 | 0 | -0.26904 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.010789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.77681 | 0 | -0.26904 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.010789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42077 | 0 | -0.26904 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.010789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32367 | 0 | -0.26904 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.010766 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9379 | 0 | -0.26901 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.010766 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7075 | 0 | -0.26901 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.010766 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6903 | 0 | -0.26901 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.010765 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.4544 | 228 | -0.26901 | -61.335
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.010765 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68896 | 0 | -0.26901 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.010765 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68035 | 0 | -0.26901 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.010765 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88919 | 0 | -0.26901 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.010765 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.7923 | 0 | -0.26901 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.010764 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17438 | 0 | -0.26901 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.010764 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.2927 | 213 | -0.26901 | -57.2996
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.010761 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6034 | 0 | -0.26901 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.010761 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.70054 | 0 | -0.26901 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.01076 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.7754 | 165 | -0.26901 | -44.3863
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.010758 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.8181 | 169 | -0.26901 | -45.462
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.010757 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12908 | 12 | -0.26901 | -3.2281
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.010757 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.26901 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.010742 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37597 | 0 | -0.26899 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7498 | 0 | -0.26897 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6844 | 0 | -0.26897 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6887 | 0 | -0.26897 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6834 | 0 | -0.26897 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.010722 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8842 | 0 | -0.26897 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.010707 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.83515 | 0 | -0.26896 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.010707 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.85656 | 0 | -0.26896 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.49234 | 46 | -0.26895 | -12.3718
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.49234 | 46 | -0.26895 | -12.3718
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.49234 | 46 | -0.26895 | -12.3718
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.58866 | 55 | -0.26895 | -14.7923
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.58866 | 55 | -0.26895 | -14.7923
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.010703 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.57796 | 54 | -0.26895 | -14.5234
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.010639 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.69154 | 0 | -0.26889 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.010639 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.63834 | 0 | -0.26889 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.010639 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.69154 | 0 | -0.26889 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.010639 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.69154 | 0 | -0.26889 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.96487 | 0 | -0.26885 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92882 | 0 | -0.26885 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92246 | 0 | -0.26885 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.57786 | 0 | -0.26885 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.010603 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12936 | 0 | -0.26885 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.010509 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.26876 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.010444 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.5222 | 50 | -0.26869 | -13.4346
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.010327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73115 | 0 | -0.26858 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.010327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68881 | 0 | -0.26858 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.010327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.54733 | 0 | -0.26858 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5821 | 0 | -0.26858 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5852 | 0 | -0.26858 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5728 | 0 | -0.26858 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.99139 | 0 | -0.26858 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.010327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5198 | 0 | -0.26858 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.010327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41308 | 0 | -0.26858 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.010325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3304 | 0 | -0.26857 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.010325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30975 | 0 | -0.26857 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.010325 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0356 | 0 | -0.26857 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.010325 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.95919 | 0 | -0.26857 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.010325 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0604 | 0 | -0.26857 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.010325 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0532 | 0 | -0.26857 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.010118 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.629 | 161 | -0.26837 | -43.2069
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.010118 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.6796 | 166 | -0.26837 | -44.5488
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.010118 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.5093 | 248 | -0.26837 | -66.5548
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.010118 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -5.5244 | 546 | -0.26837 | -146.5279
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.010118 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -6.5059 | 0 | -0.26837 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.010118 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13153 | 13 | -0.26837 | -3.4888
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.010046 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.33152 | 0 | -0.26829 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.010026 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6342 | 0 | -0.26827 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.010026 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6342 | 0 | -0.26827 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.010026 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4564 | 0 | -0.26827 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.010022 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -6.5243 | 0 | -0.26827 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.010022 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.6524 | 0 | -0.26827 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.010022 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -6.0132 | 0 | -0.26827 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.009973 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45976 | 0 | -0.26822 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0527 | 0 | -0.26773 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0527 | 0 | -0.26773 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.009484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.1286 | 0 | -0.26773 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.009484 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0385 | 0 | -0.26773 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.009332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66257 | 0 | -0.26758 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.009332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09332 | 0 | -0.26758 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56749 | 0 | -0.2674 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65352 | 0 | -0.2674 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41189 | 0 | -0.2674 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92445 | 0 | -0.2674 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.78716 | 0 | -0.2674 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.80546 | 0 | -0.2674 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45765 | 0 | -0.2674 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16475 | 0 | -0.2674 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.86038 | 0 | -0.2674 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64071 | 0 | -0.2674 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.57664 | 0 | -0.2674 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.65902 | 0 | -0.2674 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.59311 | 0 | -0.2674 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.92445 | 0 | -0.2674 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88784 | 0 | -0.2674 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.94276 | 0 | -0.2674 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69563 | 0 | -0.2674 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73224 | 0 | -0.2674 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73224 | 0 | -0.2674 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.009153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5652 | 0 | -0.2674 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.008509 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -4.8416 | 0 | -0.26676 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.008509 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -4.9437 | 0 | -0.26676 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.008403 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.5546 | 66 | -0.26665 | -17.599
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.62996 | 76 | -0.26654 | -20.2568
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.62996 | 76 | -0.26654 | -20.2568
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.87035 | 105 | -0.26654 | -27.9864
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.61339 | 74 | -0.26654 | -19.7237
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.61339 | 74 | -0.26654 | -19.7237
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.008289 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.84548 | 102 | -0.26654 | -27.1868
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.29072 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.3399 | 0 | 0.31189 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.29072 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.3399 | 0 | 0.31189 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.008154 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -10.8693 | 0 | -0.2664 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.008154 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -10.8285 | 0 | -0.2664 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 1 | 60.6412 | 208.2 | 0.31243 | 65.048
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 1 | 41.3886 | 142.1 | 0.31243 | 44.3963
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 1 | 38.5634 | 132.4 | 0.31243 | 41.3658
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 1 | 39.6119 | 136 | 0.31243 | 42.4905
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 1 | 42.8158 | 147 | 0.31243 | 45.9273
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.29126 | west | 9 | Y | Y | Ywest | Ywest | 1 | 61.1654 | 210 | 0.31243 | 65.6104
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 1 | 20.3927 | 70 | 0.31249 | 21.8743
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 1 | 20.3927 | 70 | 0.31249 | 21.8743
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 1 | 27.0349 | 92.8 | 0.31249 | 28.9991
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 1 | 23.3059 | 80 | 0.31249 | 24.9992
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 1 | 23.3059 | 80 | 0.31249 | 24.9992
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.29132 | west | 9 | Y | Y | Ywest | Ywest | 1 | 33.5023 | 115 | 0.31249 | 35.9364
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.006477 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -3.7826 | 0 | -0.26473 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.006477 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -3.8538 | 0 | -0.26473 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.006475 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.8037 | 0 | -0.26472 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.00644 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0175 | 158 | -0.26469 | -41.8207
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.00644 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0304 | 160 | -0.26469 | -42.3501
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.00644 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.127 | 175 | -0.26469 | -46.3204
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.006291 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.31455 | 50 | -0.26454 | -13.227
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.006291 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.31455 | 50 | -0.26454 | -13.227
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.006291 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.31455 | 50 | -0.26454 | -13.227
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.006291 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.31455 | 50 | -0.26454 | -13.227
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.006006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.91592 | 152.5 | -0.26425 | -40.2988
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.006006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.8979 | 149.5 | -0.26425 | -39.506
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.006006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.397 | 232.6 | -0.26425 | -61.4655
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.005998 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.79174 | 132 | -0.26425 | -34.8805
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.005998 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.80373 | 134 | -0.26425 | -35.409
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.005998 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.9374 | 323 | -0.26425 | -85.3515
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.005576 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.23419 | 42 | -0.26382 | -11.0806
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.005576 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.24534 | 44 | -0.26382 | -11.6083
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.005576 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.24534 | 44 | -0.26382 | -11.6083
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.005576 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.26207 | 47 | -0.26382 | -12.3997
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.005392 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.6715 | 310 | -0.26364 | -81.7284
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.005392 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2269 | 413 | -0.26364 | -108.8834
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.26122 | 49 | -0.26358 | -12.9154
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.24523 | 46 | -0.26358 | -12.1246
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.24523 | 46 | -0.26358 | -12.1246
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.25056 | 47 | -0.26358 | -12.3882
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.005331 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.82097 | 154 | -0.26358 | -40.5912
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.005331 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.78899 | 148 | -0.26358 | -39.0097
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.25589 | 48 | -0.26358 | -12.6518
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.005331 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.25589 | 48 | -0.26358 | -12.6518
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.005179 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.041432 | 0 | -0.26343 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.005179 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.041432 | 0 | -0.26343 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.40788 | 0 | -0.26341 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.4182 | 0 | -0.26341 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.40788 | 0 | -0.26341 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.41304 | 0 | -0.26341 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.40478 | 0 | -0.26341 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12907 | 0 | -0.26341 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.2375 | 0 | -0.26341 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14456 | 0 | -0.26341 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.22511 | 0 | -0.26341 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.005163 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.38206 | 0 | -0.26341 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.005075 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.2436 | 0 | -0.26332 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.13292 | 0 | -0.263 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.033229 | 0 | -0.263 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.18513 | 0 | -0.263 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.071205 | 0 | -0.263 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.033229 | 0 | -0.263 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.071205 | 0 | -0.263 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.18513 | 0 | -0.263 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.004747 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.18513 | 0 | -0.263 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.004684 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.037472 | 0 | -0.26293 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.004658 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.06987 | 0 | -0.26291 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.004658 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10713 | 0 | -0.26291 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.004539 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.33135 | 0 | -0.26279 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.004449 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64066 | 144 | -0.2627 | -37.8284
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.004449 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.83641 | 188 | -0.2627 | -49.3871
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.004371 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.2085 | 47.7 | -0.26262 | -12.5269
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.004371 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.16304 | 37.3 | -0.26262 | -9.7957
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.004371 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.20107 | 46 | -0.26262 | -12.0805
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.004371 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.20981 | 48 | -0.26262 | -12.6057
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.004325 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.01038 | 0 | -0.26257 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.004325 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.01038 | 0 | -0.26257 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.004313 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.051756 | 0 | -0.26256 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.004198 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.092356 | 22 | -0.26245 | -5.7738
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.004198 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.046178 | 11 | -0.26245 | -2.8869
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.004198 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.046178 | 11 | -0.26245 | -2.8869
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.004191 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.93836 | 223.9 | -0.26244 | -58.7601
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.004191 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.94298 | 225 | -0.26244 | -59.0488
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.004191 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.9413 | 224.6 | -0.26244 | -58.9438
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.004191 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.9501 | 226.7 | -0.26244 | -59.4949
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.00395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.5609 | 142 | -0.2622 | -37.2321
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.00395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.57275 | 145 | -0.2622 | -38.0187
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.00395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.59645 | 151 | -0.2622 | -39.5919
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.00395 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1455 | 290 | -0.2622 | -76.0375
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.00395 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00948 | 0 | -0.2622 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.00395 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00948 | 0 | -0.2622 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.00395 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.01106 | 0 | -0.2622 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.60498 | 0 | -0.26208 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.58584 | 0 | -0.26208 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.3829 | 0 | -0.26208 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.5552 | 0 | -0.26208 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.56286 | 0 | -0.26208 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.003829 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.48628 | 0 | -0.26208 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.003829 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.045948 | 0 | -0.26208 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.093825 | 0 | -0.262 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.093825 | 0 | -0.262 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.093825 | 0 | -0.262 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.060048 | 0 | -0.262 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.093825 | 0 | -0.262 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.093825 | 0 | -0.262 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.093825 | 0 | -0.262 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.003753 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.056295 | 0 | -0.262 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.54463 | 147 | -0.26195 | -38.5071
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.51129 | 138 | -0.26195 | -36.1495
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.5187 | 140 | -0.26195 | -36.6734
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.54463 | 147 | -0.26195 | -38.5071
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.67431 | 182 | -0.26195 | -47.6755
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.003705 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.73359 | 198 | -0.26195 | -51.8667
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.003686 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.022116 | 0 | -0.26193 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.003677 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.3128 | 0 | -0.26193 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.00365 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.2264 | 336 | -0.2619 | -87.9978
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.00365 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.657 | 180 | -0.2619 | -47.1417
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.003648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.541 | 0 | -0.2619 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.003648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.54209 | 0 | -0.2619 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.003648 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.55814 | 0 | -0.2619 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.003645 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.6561 | 180 | -0.26189 | -47.1408
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.003615 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2074 | 334 | -0.26186 | -87.4623
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.003615 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2291 | 340 | -0.26186 | -89.0335
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.003615 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.6507 | 180 | -0.26186 | -47.1354
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.003615 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.6507 | 180 | -0.26186 | -47.1354
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.003593 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.089825 | 0 | -0.26184 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.003593 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.089825 | 0 | -0.26184 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.003591 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.13646 | 0 | -0.26184 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.00357 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.13566 | 0 | -0.26182 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.003569 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.014276 | 0 | -0.26182 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.003477 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10083 | 0 | -0.26173 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.29556 | west | 8 | N | N | Nwest | Nwest | 1 | 20.6888 | 0 | 0.31672 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.29556 | west | 8 | N | N | Nwest | Nwest | 1 | 21.6937 | 0 | 0.31672 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.29556 | west | 8 | N | N | Nwest | Nwest | 1 | 20.8071 | 0 | 0.31672 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.31857 | 0 | -0.26164 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.13895 | 0 | -0.26164 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.12878 | 0 | -0.26164 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.064391 | 0 | -0.26164 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.31857 | 0 | -0.26164 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.122 | 0 | -0.26164 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.14573 | 0 | -0.26164 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.074558 | 0 | -0.26164 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.50157 | 0 | -0.26164 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.16945 | 0 | -0.26164 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.1864 | 0 | -0.26164 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.003389 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.16945 | 0 | -0.26164 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.003316 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.12601 | 38 | -0.26156 | -9.9394
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.003316 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.063999 | 19.3 | -0.26156 | -5.0482
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.003316 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.04974 | 15 | -0.26156 | -3.9235
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.003316 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.15585 | 47 | -0.26156 | -12.2935
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.003316 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.26156 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.003131 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.45086 | 144 | -0.26138 | -37.6386
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.003131 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.45086 | 144 | -0.26138 | -37.6386
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.003131 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.5354 | 171 | -0.26138 | -44.6958
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.00313 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64791 | 207 | -0.26138 | -54.1053
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.00313 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.67827 | 216.7 | -0.26138 | -56.6406
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.00313 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.75746 | 242 | -0.26138 | -63.2535
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.003048 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.6642 | 0 | -0.2613 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.003048 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.286 | 0 | -0.2613 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.002943 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.103 | 0 | -0.26119 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.002943 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10006 | 0 | -0.26119 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.002943 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.103 | 0 | -0.26119 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.002915 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.45182 | 155 | -0.26116 | -40.4803
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.002915 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.49555 | 170 | -0.26116 | -44.3977
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.002915 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.45182 | 155 | -0.26116 | -40.4803
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.002822 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.41342 | 146.5 | -0.26107 | -38.2468
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.002822 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.41737 | 147.9 | -0.26107 | -38.6123
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.002822 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.48821 | 173 | -0.26107 | -45.1651
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.002819 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.26107 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.002819 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.26107 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.002819 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.26107 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.002611 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.26086 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.002513 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.0655 | 0 | -0.26076 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.002513 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.068 | 0 | -0.26076 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.002437 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.004 | 412 | -0.26069 | -107.4023
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.002437 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.9748 | 400 | -0.26069 | -104.274
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.002435 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.26068 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.002434 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.50871 | 209 | -0.26068 | -54.4826
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.002434 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.52574 | 216 | -0.26068 | -56.3073
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.002434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.11196 | 46 | -0.26068 | -11.9914
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.002434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.1144 | 47 | -0.26068 | -12.2521
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.002434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.11196 | 46 | -0.26068 | -11.9914
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.002434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.11196 | 46 | -0.26068 | -11.9914
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.002331 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.92308 | 0 | -0.26058 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.002294 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.93366 | 407 | -0.26054 | -106.0406
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.2968 | west | 6 | Y | N | Ywest | Nwest | 1 | 44.5204 | 0 | 0.31797 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.2968 | west | 6 | Y | N | Ywest | Nwest | 1 | 65.2967 | 0 | 0.31797 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.2968 | west | 6 | Y | N | Ywest | Nwest | 1 | 59.3606 | 0 | 0.31797 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.2968 | west | 6 | Y | N | Ywest | Nwest | 1 | 36.1803 | 0 | 0.31797 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.00187 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.10846 | 58 | -0.26012 | -15.0869
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.00187 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.16643 | 89 | -0.26012 | -23.1505
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.00187 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08228 | 44 | -0.26012 | -11.4452
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.00187 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08228 | 44 | -0.26012 | -11.4452
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.00187 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08041 | 43 | -0.26012 | -11.1851
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.00187 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.08415 | 45 | -0.26012 | -11.7053
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.19289 | 0 | -0.25994 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.37562 | 0 | -0.25994 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.31133 | 0 | -0.25994 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.37901 | 0 | -0.25994 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.001692 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.19458 | 0 | -0.25994 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.000968 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.011616 | 0 | -0.25922 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.000968 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010648 | 0 | -0.25922 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.000968 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.011616 | 0 | -0.25922 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25825 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25825 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25825 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25825 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25825 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25825 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25825 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25825 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.000805 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25744 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.002043 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.036774 | 0 | -0.25621 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.002043 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.036774 | 0 | -0.25621 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002835 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2835 | 100 | -0.25541 | -25.5413
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002835 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2835 | 100 | -0.25541 | -25.5413
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002835 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25541 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002835 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25541 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002835 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25541 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002835 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25541 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002839 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.25541 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.003673 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10284 | 0 | -0.25458 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.003673 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10652 | 0 | -0.25458 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.004241 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7897 | 422 | -0.25401 | -107.191
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.004468 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.080424 | 0 | -0.25378 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.004468 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.080424 | 0 | -0.25378 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.004468 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.06702 | 0 | -0.25378 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.006406 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.15374 | 24 | -0.25184 | -6.0442
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.006406 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.15374 | 24 | -0.25184 | -6.0442
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.006406 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.14734 | 23 | -0.25184 | -5.7924
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.007118 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.097517 | 0 | -0.25113 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.008214 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.068998 | 8.4 | -0.25003 | -2.1003
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.04275 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.2155 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.047167 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.283 | 0 | -0.21108 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.066155 | south | 5 | N | N | Nsouth | Nsouth | -1 | 2.1831 | 0 | -0.19209 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.066155 | south | 5 | N | N | Nsouth | Nsouth | -1 | 1.6539 | 0 | -0.19209 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.066155 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.19209 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.38029 | west | 6 | Y | N | Ywest | Nwest | 1 | 79.4812 | 0 | 0.40146 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.38029 | west | 6 | Y | N | Ywest | Nwest | 1 | 48.1071 | 0 | 0.40146 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.38029 | west | 6 | Y | N | Ywest | Nwest | 1 | 94.693 | 0 | 0.40146 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.38029 | west | 6 | Y | N | Ywest | Nwest | 1 | 74.9177 | 0 | 0.40146 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
Average line rating
| Temp | Tonkawa - Graham
| 20 | 1340
| 25 | 1340
| 30 | 1340
| 35 | 1340
| 40 | 1340
| 45 | 1340
| 50 | 1340
| 55 | 1340
| 60 | 1307
| 65 | 1280
| 70 | 1251
| 75 | 1251
| 80 | 1223
| 85 | 1194
| 90 | 1163
| 95 | 1132
| 100 | 1098
| 105 | 1065
| 110 | 1031
| 115 | 994
| total | 24709
| avg | 1235.45